## Forecast
8 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2022-08-07 | Sunday
|  |  | Date (day): | 2022-08-07 |  | Sunday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 10522.6 | MW |  |  | (b) At Evening Peak Hour : |  | 12380 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2022-08-06 | 2022-08-07 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 300 | 0 | 0 | 0 |  | 365 | Under maint.
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 88 | 93 | 90 | 93 |  | 15 | Engine problem
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 410 | 394 | 412 | 412
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 343 | 267 | 300 | 330 | 30 |  | Gas shortage
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 225 | 225 | 225 |  | Gas shortage & GT-2 S/D
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 7 | 50 | 8 | 50 | 50 |  | Fuel shortage
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 0 | 0 | 0 | 0 |  | 102 | Under maint
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 30 | 30 | 30 | 30 |  | 25 | Engine problem
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 19 | 19 | 19 |  |  | Engine problem
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 97 | 95 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 8 | 50 | 8 | 50 | 50 |  | Fuel shortage
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 8 | 40 | 8 | 50 | 52 |  | Fuel shortage
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 35 | 54 | 35 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 50 | 125 | 50 | 132 |  | 17 | Engine problem
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 35 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 52 | 49 | 50 | 50 |  | 30 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 16 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 51 | 50 | 51 | 51
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 195 | 260 | 110 | 275 |  | 25 | Engine problem
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 0 | 300 |  | Fuel conservation
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Fuel conservation
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Fuel conservation
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 99 | 149 | 100 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 88 | 88 | 88 | 88 |  | 17 | Engine problem
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 17 | 54 | 17 | 104 |  |  | Fuel shortage
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 54 | 162 | 70 | 162
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 4 | 0 | 30 | 0
| 40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 55 | 55 | 55 | 55
|  | Dhaka area Total |  |  |  |  | 6263 | 5847 | 2546 | 2657 | 2084 | 2727 | 1838 | 1276
| 41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 100 | 100 | 100 | 80 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 25 | 0 | 25 | 25
| 43 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 0 | 0 | 20 | 0
| 44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 26 | 25 | 25 | 32 |  | 18 | Engine problem
| 45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 111 | 111 | 111 | 111 |  | 119 | Low Water Level
| 46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | S/D due to HGPI
| 47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint,Fuel conservation
| 48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 68 | 87 | 68 | 90
| 49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 26 | 24 | 26 | 26 | 72 |  | Fuel shortage
| 50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 17 | 51 | 17 | 51 | 51 |  | Fuel shortage
| 51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 56 | 56 | 56 | 56 | 44 |  | Fuel shortage
| 52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 21 | 90 | 21 | 90 |  | 10 | Engine problem
| 53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 11 | 15 | 17 | 17 |  | 5 | Engine problem
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 7 | 32 | 10 | 30
| 54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 89 | 81 | 90 | 95 |  | 13 | Engine problem
| 55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 3 | 0 | 5 | 0
| 56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 16 | 214 | 50 | 214 | 86 |  | Fuel shortage
| 57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 36 | 36 | 36 | 36 |  | 18 | Engine problem
| 58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 55 | 55 | 55 | 55 | 55 |  | Fuel shortage
| 59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 20 | 100 | 20 | 100
| 60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 108 | 108 | 108 | 108 |  | 8 | Engine problem
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 795 | 1185 | 860 | 1236 | 568 | 566
| 61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 208 | 202 | 210 | 210
| 63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 325 | 280 | 310 | 330 | 30 |  | Gas shortage
| 64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 320 | 305 | 305 | 320 | 40 |  | Gas shortage
|  | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+136*1 | 284 | 284 | 0 | 0 | 0 | 0 |  |  | On test.
| 65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 38 | 37 | 37 | 37 |  | 8 | Engine problem
| 66 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 55 | 53 | 55 | 55 | 55
| 67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 132 | 127 | 128 | 132 |  | 18 | Engine problem
| 70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 32 | 40 | 32 | 40 |  | 12 | Engine problem
| 71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 142 | 135 | 142 | 142 |  | 21 | Engine problem
| 72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 68 | 68 | 100 | 200
| 73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 9 | 10 | 10
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 110 | 164 | 143 | 166
| 75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 43 | 8 | 43 | 9 |  | Fuel shortage
| 77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 16 | 20 | 20 | 20 |  | 5 | Engine problem
| 78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel conservation
| 79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 114 | 17 | 114
| 80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 78 | 113 | 78 | 113
| 81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 35 | 35 | 35 | 35 |  | 19 | 33 kV feeder fault
| 82 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 58 | 75 | 60 | 60 | 55 |  | Fuel shortage
|  | Cumilla Area Total |  |  |  |  | 3193 | 3169 | 1765 | 1936 | 1804 | 2141 | 655 | 83
| 83 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 103 | 101 | 102 | 102 | 100 |  | Gas shortage
| 84 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 20 | 20
| 85 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0 |  | 8 | Under maint.
| 86 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 0 | 0 | 1.6 | 0
| 87 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 47 | 171 | 48 | 180 |  | 20 | Engine problem
| 88 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 49 | 78 | 49 | 79 |  | 36 | Engine problem
| 89 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 4 | 0 | 50 | 0
| 90 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 0 | 0 | 0 |  | 22 | Engine problem
|  | Mymensingh Area Total |  |  |  |  | 717 | 614 | 225 | 372 | 270.6 | 381 | 100 | 86
| 91 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 43 | 43 | 43 |  | 27 | Machine problem.
| 92 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 41 | 41 | 41 | 41 |  | 49 | Machine problem
| 93 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 110 | 110 | 110 | 110 |  | 53 | ST under maint.
| 94 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
| 95 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 31 | 50 | 33 | 53
| 96 | Fenchuganj 44MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 30 | 49 | 30 | 49
| 97 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 11 | 11 | 11
| 98 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 61 | 63 | 61 | 61
| 99 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 10 | 81 | 10 | 81
| 100 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
| 101 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 221 | 221 | 220 | 220
| 102 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Gas shortage
| 103 | Sylhet 50MW PP (EPL) |  | Gas | NENP | 27*2 | 50 | 50 | 31 | 32 | 31 | 32 | 18 |  | Gas shortage
| 104 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 8 | 16 | 8 | 16 | 9 |  | Gas shortage
| 105 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 305 | 290 | 290 | 290 |  |  | FGMO
| 106 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 399 | 403 | 400 | 400
| 107 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| 108 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 0 | 0 | 0 | 0 |  | 383 | Under maint.
|  | Sylhet Area Total |  |  |  |  | 2522 | 2477 | 1300 | 1420 | 1298 | 1417 | 47 | 942
| 109 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 913 | 914 | 930 | 930
| 110 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 16 | 16 | 16 | 16 | 99 |  | Fuel shortage
| 111 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 33 | 15 | 32 |  | 22 | Engine problem
| 112 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 35 | 0 | 0 | 230 |  | Fuel conservation
| 113 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 19 | 65 | 20 | 70 |  | 39 | Engine problem
| 114 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 170 | 150 | 180 | 185 | 225 |  | Gas shortage
| 115 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 8 | 0 | 8 | 32 |  | Fuel shortage
| 116 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Fuel conservation
| 117 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 53 | 0 | 35 | 70 |  | Fuel shortage
| 118 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 105 | 105 | 105 | 105
| 119 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 49 | 0 | 100 | 0
|  | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
|  | Khulna Area Total |  |  |  |  | 2388 | 2384 | 1272 | 1379 | 1366 | 1381 | 772 | 61
| 120 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 16 | 32 | 16 | 32 |  |  | Line O/L
| 121 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 23 | 32 | 23 | 30 |  | 10 | Engine problem
| 122 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 87 | 86 | 88 | 88 | 106 |  | Gas shortage
|  | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
| 123 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 930 | 1060 | 1110 | 1100 |  |  | Line O/L
| 124 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 219 | 220 | 225 | 220
| 125 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 0 | 0 |  |  | Line O/L
|  | Barisal Area Total |  |  |  |  | 1958 | 1958 | 1275 | 1430 | 1462 | 1470 | 106 | 10
| 126 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 127 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 24 | 24 | 32 |  | 20 | Engine problem
| 128 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 41 | 0 | 40 |  | 31 | Engine problem
| 129 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 130 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 34 | 42 | 42 | 42 |  | 8 | Engine problem
| 131 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 32 | 32 | 32 | 32 |  | 18 | Engine problem
| 132 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 189 | 178 | 188 | 190 | 20 |  | Gas shortage
| 133 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 140 | 216 | 0 | 0 | 220 |  | Fuel conservation
| 134 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 160 | 145 | 162 | 167 | 53 |  | Gas shortage
| 135 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 330 | 296 | 350 | 350 | 64 |  | Gas shortage
| 136 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 33 | 33 | 33 | 33 |  | 17 | Engine problem
| 137 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 20 | 22 | 21 | 21
| 138 | Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 139 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 140 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 52 | 8 | 52
| 141 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 79 | 90 | 80 | 86 |  | 18 | Engine problem
| 142 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel conservation
| 143 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 50 | 94 | 50 | 94 |  | 19 | Engine problem
| 144 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 55 | 95 | 55 | 95 |  | 18 | Engine problem
| 145 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 0 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2129 | 1141 | 1371 | 1062 | 1245 | 728 | 149
| 146 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
| 147 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 200 | 200 | 200 | 200 | 74 |  | Coal Shortage
| 148 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
| 149 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
| 150 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 56 | 92 | 56 | 92 |  | 21 | Engine problem
| 151 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 2 | 0 | 8 | 0
| 152 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 52 | 90 | 52 | 90 |  | 25 | Fuel shortage
|  | Rangpur Area Total |  |  |  |  | 800 | 720 | 310 | 382 | 316 | 382 | 199 | 131
|  | Total |  |  |  |  | 22482 | 21680 | 10629 | 12132 | 10522.6 | 12380 | 5013 | 3304
| A. |  | 2022-08-06 | (Yesterday) |  |  |  |  | Saturday
| 1 | Highest Generation : |  |  | 12170 | MW at | 22:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 10552 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 13800 | MW
| 3 | Day peak Generation : |  |  | 10629 | MW at | 9:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 12990.5 | MW
| 4 | Evening peak Generation : |  |  | 12132 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 1537 | MW
| 5 | Total Energy Generation : |  | 269.5539 | MKWHr | By Solar | 1.0424 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
|  | By Gas : | 135.237 | MKWHr |  | By Oil: | 73.9937 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 30.9188 | MKWHr |  | By Hydro: | 2.5995 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 5013 | MW | Dhaka | 4547.19 | 4167.19 |  | 380
|  |  |  | For Plants S/D or M/C prob = |  |  | 3304 | MW | Chittagong | 1499 | 1319 |  | 180 |  | 18:00 |  | 245.139
|  |  |  | Total = |  |  | 8317 | MW | Khulna | 1502 | 1302 |  | 200
| 7 | Total Gas Supplied : |  |  | 1000.91 | MMCFD |  |  | Rajshahi | 1361.4 | 1171.4 |  | 190 |  | 19:00 |  | 1059.8112
| 8 | Fuel Cost : | i) Gas : | Taka | 156674479.618 | ii) Oil : | Taka | 1027224821.63 | Comilla | 1207 | 1037 |  | 170 |  | 19:30 |  | 1310.4796
|  |  | iii) Coal : |  | 260458640 | Total | Taka | 1444357941.248 | Mymensingh | 1100 | 890 |  | 210 |  | 20:00 |  | 1550.0891
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0 | MKWHr. | Sylhet | 548 | 461 |  | 87 |  | 21:00 |  | 1537.1871
|  | ii) During Peak Demand : |  |  | 736 | MW (E to W) at | 21:00 | hrs | Barisal | 385.91 | 385.91 |  | 0 |  | 22:00 |  | 1410.0098
|  | iii) Maximum : |  |  | 454 | MW at | 5:00 | hrs | Rangpur | 840 | 720 |  | 120 |  | 23:00 |  | 1341.8132
| 10 | Maximum Temperature in Dhaka was |  |  |  | 34.0° C |  |  | Total | 12990.5 | 11453.5 |  | 1537
| B. |  | 2022-08-07 | (Today) |  |  |  | Sunday |  |  | Probable max. temperature in Dhaka |  |  | 35.8° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 14000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 1493.4046 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 12380 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 12300 | MW
| 4 | Reserve(Generation end) |  |  |  | - | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 310.0867 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 10290 | MW at | 8:00 | 451.2422 | 156.4271 | 213.3487 | 197.9019 | 164.1949 | 141.4381 | 57.6666 | 0 | 111.1853
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 22.08 | MKWHr. | ii) HVDC Flow at Peak Time |  | 914 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.6826 | MKWHr. | iii) Maximum HVDC Flow : |  | 914 | MW at | 1:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 93.01 |  | (b) Today: | 93.54 |  | (c) Rule Curve: |  | 90.92
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2022-08-06
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 300 | 90 | 0 | 408 | 333 |  | 0 | 225 | 0 | 7 | 0 | 30 | 0 | 0 | 95 | 8 | 8 | 49 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 25 | 25 | 33 | 50 | 0 | 78 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 0 | 26 | 51 | 56 | 89 | 25 | 17 | 42 | 0 | 0 | 0 | 350 | 335 | 206 | 8 | 142 | 36 | 55 | 0 | 51 | 0 | 32 | 8 | 22 | 10 | 33 | 20 | 168 | 100 | 0 | 20 | 0 | 43 | 41 | 31 | 30 | 110 | 0 | 60 | 10 | 0 | 221 | 0 | 32 | 10 | 305 | 8 | 0 | 0 | 200 | 0 | 0 | 47 | 0 | 97 | 0 | 21 | 133 | 127 | 404 | 49 | 92 | 87 | 0 | 16 | 36 | 54 | 17 | 90 | 53 | 0 | 17 | 0 | 162 | 108 | 0 | 35 | 0 | 74 | 55 | 0 |  | 914 | 0 | 170 | 0 | 16 | 0 | 0 | 0 | 17 | 56 | 8 | 85 | 32 | 32 | 0 | 0 | 0 | 32 | 41 | 86 | 0 | 42 | 32 | 8 | 33 | 21 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 190 | 0 | 0 | 172 | 0 | 0 | 159 | 0 | 336 | 0 | 0 | 50 | 105 | 56 | 0 | 0 | 55 | 1080 | 220 | 0 | 0 | 0 | 0 | 90 | 0 | 0 |  | 7050 | 4349 | 11399 | 3893 | 914 | 1941 | 0 | 2463 | 1280 | 113 | 172 | 627 | 168 | 0 | 1106.8116 | 92.91
2:00 | 0 | 0 | 0 | 180 | 300 | 90 | 0 | 406 | 332 |  | 0 | 225 | 0 | 8 | 0 | 30 | 0 | 0 | 97 | 8 | 8 | 50 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 26 | 25 | 33 | 50 | 0 | 78 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 0 | 26 | 51 | 56 | 89 | 26 | 17 | 42 | 0 | 0 | 0 | 330 | 330 | 207 | 8 | 142 | 36 | 54 | 0 | 51 | 0 | 31 | 8 | 22 | 10 | 33 | 20 | 170 | 101 | 0 | 20 | 0 | 43 | 41 | 31 | 30 | 110 | 0 | 60 | 10 | 0 | 221 | 0 | 30 | 10 | 310 | 8 | 0 | 0 | 195 | 0 | 0 | 47 | 0 | 97 | 0 | 21 | 70 | 120 | 403 | 49 | 105 | 87 | 0 | 16 | 36 | 53 | 17 | 84 | 20 | 0 | 17 | 0 | 162 | 108 | 0 | 35 | 0 | 70 | 55 | 0 |  | 913 | 0 | 175 | 0 | 16 | 0 | 0 | 0 | 17 | 56 | 8 | 87 | 31 | 32 | 0 | 0 | 0 | 32 | 41 | 86 | 0 | 42 | 24 | 8 | 33 | 21 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 189 | 0 | 0 | 150 | 0 | 0 | 160 | 0 | 356 | 0 | 0 | 50 | 105 | 56 | 0 | 0 | 55 | 1070 | 220 | 0 | 0 | 0 | 0 | 52 | 0 | 0 |  | 6926 | 4296 | 11222 | 3877 | 913 | 1961 | 0 | 2321 | 1270 | 113 | 150 | 597 | 170 | 0 | 1177.7729 | 92.93
3:00 | 0 | 0 | 0 | 180 | 300 | 90 | 0 | 407 | 332 |  | 0 | 225 | 0 | 7 | 0 | 30 | 0 | 0 | 97 | 8 | 8 | 50 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 27 | 25 | 33 | 50 | 0 | 79 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 0 | 26 | 51 | 56 | 83 | 26 | 17 | 42 | 0 | 0 | 0 | 350 | 335 | 207 | 8 | 144 | 36 | 55 | 0 | 51 | 0 | 40 | 8 | 22 | 10 | 33 | 20 | 168 | 101 | 0 | 20 | 0 | 43 | 41 | 30 | 30 | 110 | 0 | 60 | 10 | 0 | 221 | 0 | 30 | 10 | 320 | 8 | 0 | 0 | 195 | 0 | 0 | 47 | 0 | 97 | 0 | 21 | 70 | 132 | 397 | 49 | 105 | 87 | 0 | 16 | 36 | 52 | 17 | 84 | 20 | 0 | 17 | 0 | 162 | 108 | 0 | 35 | 0 | 75 | 55 | 0 |  | 914 | 0 | 175 | 0 | 16 | 0 | 0 | 0 | 17 | 56 | 8 | 85 | 31 | 16 | 0 | 0 | 0 | 32 | 41 | 86 | 0 | 42 | 24 | 8 | 33 | 21 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 189 | 0 | 0 | 150 | 0 | 0 | 158 | 0 | 360 | 0 | 0 | 50 | 105 | 56 | 0 | 0 | 55 | 1070 | 220 | 0 | 0 | 0 | 0 | 52 | 0 | 0 |  | 6976 | 4281 | 11257 | 3896 | 914 | 1975 | 0 | 2314 | 1270 | 114 | 150 | 606 | 168 | 0 | 1099.439 | 92.95
4:00 | 0 | 0 | 0 | 180 | 300 | 90 | 0 | 405 | 333 |  | 0 | 225 | 0 | 8 | 0 | 30 | 0 | 0 | 97 | 8 | 8 | 50 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 27 | 25 | 33 | 50 | 0 | 79 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 0 | 26 | 17 | 56 | 83 | 26 | 17 | 42 | 0 | 0 | 0 | 350 | 335 | 206 | 8 | 143 | 36 | 55 | 0 | 51 | 0 | 32 | 8 | 22 | 10 | 33 | 20 | 162 | 102 | 0 | 20 | 0 | 43 | 41 | 31 | 30 | 110 | 0 | 61 | 10 | 0 | 221 | 0 | 31 | 10 | 320 | 8 | 0 | 0 | 195 | 0 | 0 | 47 | 0 | 97 | 0 | 21 | 68 | 133 | 401 | 49 | 105 | 87 | 0 | 16 | 36 | 53 | 17 | 85 | 20 | 0 | 0 | 0 | 162 | 108 | 0 | 35 | 0 | 75 | 46 | 0 |  | 914 | 0 | 175 | 0 | 16 | 0 | 0 | 0 | 17 | 56 | 8 | 86 | 29 | 16 | 0 | 0 | 0 | 32 | 41 | 86 | 0 | 34 | 24 | 8 | 33 | 21 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 189 | 0 | 0 | 130 | 0 | 0 | 157 | 0 | 365 | 0 | 0 | 50 | 105 | 56 | 0 | 0 | 55 | 1050 | 222 | 0 | 0 | 0 | 0 | 52 | 0 | 0 |  | 6909 | 4238 | 11147 | 3898 | 914 | 1983 | 0 | 2282 | 1250 | 114 | 130 | 544 | 162 | 0 | 1108.6547 | 92.97
5:00 | 0 | 0 | 0 | 180 | 300 | 90 | 0 | 409 | 333 |  | 0 | 225 | 0 | 7 | 0 | 30 | 0 | 0 | 96 | 8 | 8 | 50 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 27 | 25 | 33 | 50 | 0 | 79 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 0 | 26 | 17 | 56 | 89 | 26 | 17 | 42 | 0 | 0 | 0 | 355 | 340 | 207 | 8 | 142 | 36 | 55 | 0 | 51 | 0 | 32 | 8 | 22 | 10 | 33 | 20 | 134 | 100 | 0 | 20 | 0 | 43 | 41 | 31 | 30 | 110 | 0 | 61 | 10 | 0 | 221 | 0 | 30 | 10 | 315 | 8 | 0 | 0 | 195 | 0 | 0 | 47 | 0 | 98 | 0 | 21 | 68 | 125 | 401 | 49 | 105 | 87 | 0 | 16 | 36 | 55 | 17 | 77 | 20 | 0 | 0 | 0 | 162 | 108 | 0 | 35 | 0 | 74 | 55 | 0 |  | 914 | 0 | 175 | 0 | 16 | 0 | 0 | 0 | 17 | 51 | 0 | 86 | 28 | 16 | 0 | 0 | 0 | 32 | 41 | 86 | 0 | 34 | 24 | 8 | 33 | 21 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 189 | 0 | 0 | 130 | 0 | 0 | 156 | 0 | 359 | 0 | 0 | 50 | 105 | 56 | 0 | 0 | 55 | 1050 | 220 | 0 | 0 | 0 | 0 | 52 | 0 | 0 |  | 6886 | 4215 | 11101 | 3908 | 914 | 1968 | 0 | 2274 | 1250 | 114 | 130 | 539 | 134 | 0 | 736.3384 | 92.99
6:00 | 0 | 0 | 0 | 180 | 300 | 90 | 0 | 409 | 332 |  | 0 | 225 | 0 | 8 | 0 | 30 | 0 | 0 | 97 | 8 | 8 | 50 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 27 | 25 | 33 | 51 | 0 | 78 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 0 | 26 | 17 | 56 | 89 | 26 | 14 | 40 | 0 | 0 | 0 | 315 | 310 | 209 | 8 | 142 | 36 | 56 | 0 | 51 | 0 | 32 | 8 | 22 | 10 | 33 | 20 | 124 | 103 | 0 | 20 | 0 | 43 | 41 | 31 | 30 | 110 | 0 | 61 | 10 | 0 | 221 | 0 | 31 | 10 | 305 | 8 | 0 | 0 | 195 | 0 | 0 | 47 | 0 | 97 | 1 | 21 | 68 | 130 | 401 | 49 | 105 | 87 | 0 | 16 | 36 | 55 | 17 | 76 | 20 | 0 | 0 | 0 | 54 | 108 | 0 | 35 | 0 | 63 | 55 | 0 |  | 913 | 0 | 175 | 0 | 16 | 0 | 0 | 0 | 0 | 20 | 0 | 88 | 22 | 16 | 0 | 0 | 0 | 32 | 0 | 79 | 0 | 34 | 24 | 8 | 33 | 21 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 189 | 0 | 0 | 130 | 0 | 0 | 159 | 0 | 364 | 0 | 0 | 50 | 95 | 56 | 0 | 0 | 55 | 990 | 222 | 0 | 0 | 0 | 1 | 52 | 0 | 0 |  | 6684 | 4055 | 10739 | 3846 | 913 | 1958 | 0 | 2150 | 1190 | 113 | 130 | 443 | 124 | 2 | 517.0036 | 93.01
7:00 | 0 | 0 | 0 | 180 | 300 | 90 | 0 | 411 | 303 |  | 0 | 225 | 0 | 7 | 0 | 30 | 0 | 0 | 98 | 8 | 8 | 50 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 27 | 25 | 33 | 51 | 0 | 77 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 0 | 26 | 17 | 56 | 89 | 26 | 14 | 39 | 0 | 0 | 0 | 310 | 310 | 210 | 8 | 143 | 36 | 57 | 0 | 51 | 0 | 32 | 8 | 22 | 10 | 31 | 20 | 120 | 104 | 0 | 20 | 0 | 43 | 41 | 31 | 30 | 110 | 0 | 60 | 10 | 0 | 221 | 0 | 31 | 10 | 300 | 8 | 0 | 0 | 195 | 0 | 0 | 47 | 0 | 98 | 5 | 21 | 68 | 135 | 401 | 49 | 105 | 82 | 1 | 16 | 36 | 55 | 17 | 77 | 20 | 0 | 15 | 0 | 54 | 108 | 0 | 35 | 0 | 61 | 55 | 0 |  | 914 | 0 | 180 | 0 | 16 | 0 | 0 | 0 | 0 | 19 | 0 | 88 | 21 | 16 | 0 | 0 | 0 | 0 | 0 | 79 | 0 | 34 | 24 | 8 | 33 | 21 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 189 | 0 | 0 | 130 | 0 | 0 | 164 | 0 | 363 | 0 | 0 | 50 | 105 | 56 | 0 | 1 | 55 | 990 | 223 | 0 | 0 | 0 | 7 | 52 | 0 | 0 |  | 6662 | 4049 | 10711 | 3854 | 914 | 1923 | 0 | 2174 | 1190 | 112 | 130 | 410 | 120 | 14 | 358.4927 | 93.03
8:00 | 0 | 0 | 0 | 180 | 300 | 88 | 0 | 410 | 303 |  | 0 | 225 | 0 | 8 | 0 | 30 | 0 | 0 | 95 | 8 | 8 | 50 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 27 | 25 | 33 | 51 | 0 | 76 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 0 | 26 | 17 | 56 | 89 | 25 | 17 | 13 | 0 | 0 | 0 | 310 | 305 | 211 | 8 | 142 | 37 | 56 | 0 | 51 | 0 | 32 | 8 | 22 | 10 | 33 | 20 | 124 | 104 | 0 | 22 | 0 | 43 | 41 | 31 | 30 | 110 | 0 | 65 | 10 | 0 | 221 | 0 | 31 | 10 | 280 | 8 | 0 | 0 | 195 | 0 | 0 | 47 | 0 | 97 | 0 | 21 | 68 | 128 | 363 | 49 | 88 | 68 | 2 | 16 | 36 | 55 | 17 | 78 | 20 | 0 | 18 | 1 | 54 | 108 | 0 | 35 | 1 | 58 | 55 | 0 |  | 913 | 0 | 180 | 0 | 16 | 0 | 0 | 0 | 0 | 19 | 0 | 88 | 21 | 16 | 0 | 0 | 0 | 0 | 0 | 79 | 0 | 34 | 32 | 8 | 33 | 21 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 188 | 0 | 0 | 130 | 0 | 0 | 162 | 0 | 340 | 0 | 0 | 50 | 105 | 56 | 0 | 2 | 55 | 960 | 223 | 0 | 0 | 0 | 16 | 52 | 0 | 0 |  | 6542 | 4010 | 10552 | 3817 | 913 | 1851 | 0 | 2136 | 1160 | 111 | 130 | 418 | 124 | 22 | 412.8656 | 93.05
9:00 | 0 | 0 | 0 | 180 | 300 | 88 | 0 | 410 | 343 |  | 0 | 225 | 0 | 7 | 0 | 30 | 0 | 0 | 97 | 8 | 8 | 50 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 27 | 25 | 16 | 51 | 0 | 76 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 0 | 26 | 17 | 56 | 89 | 26 | 11 | 7 | 0 | 0 | 0 | 325 | 320 | 208 | 8 | 142 | 38 | 53 | 0 | 51 | 0 | 32 | 8 | 22 | 11 | 33 | 16 | 110 | 103 | 0 | 22 | 0 | 43 | 41 | 31 | 30 | 110 | 0 | 61 | 10 | 0 | 221 | 0 | 31 | 10 | 305 | 8 | 0 | 0 | 195 | 0 | 0 | 47 | 0 | 99 | 0 | 21 | 68 | 132 | 399 | 49 | 88 | 68 | 3 | 16 | 36 | 55 | 17 | 78 | 20 | 0 | 17 | 4 | 54 | 108 | 0 | 35 | 4 | 58 | 55 | 0 |  | 913 | 0 | 170 | 0 | 16 | 0 | 0 | 0 | 0 | 19 | 0 | 87 | 23 | 16 | 0 | 0 | 0 | 0 | 0 | 79 | 0 | 34 | 32 | 8 | 33 | 20 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 189 | 0 | 0 | 140 | 0 | 0 | 160 | 0 | 330 | 0 | 0 | 50 | 105 | 56 | 0 | 2 | 55 | 930 | 219 | 0 | 0 | 0 | 49 | 52 | 0 | 0 |  | 6631 | 3998 | 10629 | 3840 | 913 | 1894 | 0 | 2141 | 1130 | 111 | 140 | 428 | 110 | 62 | 618.3768 | 93.07
10:00 | 0 | 0 | 0 | 180 | 300 | 82 | 0 | 410 | 337 |  | 0 | 225 | 0 | 8 | 0 | 30 | 0 | 0 | 97 | 8 | 8 | 50 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 0 | 25 | 27 | 25 | 17 | 51 | 0 | 74 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 0 | 26 | 42 | 56 | 89 | 25 | 15 | 2 | 0 | 0 | 0 | 295 | 305 | 208 | 8 | 142 | 34 | 52 | 0 | 51 | 0 | 32 | 8 | 16 | 11 | 33 | 17 | 148 | 94 | 0 | 22 | 0 | 43 | 41 | 31 | 30 | 110 | 0 | 60 | 10 | 0 | 221 | 0 | 29 | 10 | 275 | 8 | 0 | 0 | 195 | 0 | 0 | 47 | 0 | 97 | 19 | 21 | 68 | 117 | 402 | 49 | 88 | 68 | 3 | 50 | 17 | 55 | 17 | 77 | 20 | 0 | 17 | 17 | 50 | 108 | 0 | 0 | 13 | 58 | 55 | 0 |  | 913 | 0 | 160 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 21 | 16 | 0 | 0 | 0 | 0 | 0 | 73 | 0 | 34 | 32 | 8 | 33 | 19 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 188 | 0 | 0 | 130 | 0 | 0 | 154 | 0 | 305 | 0 | 0 | 50 | 105 | 50 | 0 | 3 | 55 | 910 | 217 | 0 | 0 | 0 | 53 | 52 | 0 | 0 |  | 6548 | 3895 | 10443 | 3748 | 913 | 1814 | 0 | 2075 | 1110 | 109 | 130 | 418 | 148 | 108 | 881.9473 | 93.09
11:00 | 0 | 0 | 0 | 180 | 300 | 85 | 0 | 408 | 327 |  | 0 | 225 | 0 | 7 | 0 | 30 | 0 | 0 | 93 | 8 | 8 | 50 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 0 | 25 | 27 | 25 | 25 | 51 | 0 | 75 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 0 | 26 | 51 | 56 | 88 | 25 | 15 | 2 | 0 | 0 | 0 | 365 | 330 | 211 | 8 | 142 | 34 | 51 | 0 | 51 | 0 | 31 | 8 | 19 | 9 | 31 | 17 | 150 | 80 | 0 | 22 | 2 | 43 | 41 | 31 | 30 | 110 | 0 | 61 | 10 | 0 | 220 | 0 | 29 | 9 | 280 | 8 | 0 | 0 | 195 | 0 | 0 | 47 | 0 | 99 | 20 | 21 | 34 | 123 | 401 | 49 | 88 | 68 | 2 | 52 | 17 | 55 | 17 | 77 | 20 | 0 | 17 | 23 | 54 | 108 | 0 | 0 | 18 | 56 | 55 | 0 |  | 914 | 0 | 160 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 18 | 16 | 0 | 0 | 0 | 0 | 0 | 73 | 0 | 34 | 32 | 8 | 33 | 18 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 187 | 0 | 0 | 137 | 0 | 0 | 145 | 0 | 297 | 17 | 0 | 50 | 88 | 56 | 0 | 3 | 55 | 880 | 217 | 0 | 0 | 2 | 71 | 52 | 0 | 0 |  | 6628 | 3878 | 10506 | 3823 | 914 | 1798 | 0 | 2057 | 1080 | 110 | 137 | 433 | 150 | 141 | 1008.2031 | 93.11
12:00 | 0 | 0 | 0 | 180 | 300 | 82 | 0 | 405 | 328 |  | 0 | 225 | 0 | 7 | 0 | 30 | 0 | 0 | 94 | 8 | 8 | 50 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 19 | 25 | 28 | 0 | 28 | 42 | 0 | 75 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 0 | 26 | 49 | 56 | 35 | 25 | 15 | 2 | 0 | 0 | 0 | 345 | 330 | 203 | 8 | 143 | 36 | 52 | 0 | 51 | 0 | 32 | 8 | 21 | 9 | 25 | 17 | 154 | 66 | 0 | 22 | 2 | 43 | 41 | 33 | 30 | 110 | 0 | 59 | 10 | 0 | 221 | 0 | 29 | 10 | 300 | 8 | 0 | 0 | 195 | 0 | 0 | 47 | 0 | 97 | 18 | 21 | 34 | 118 | 396 | 48 | 88 | 68 | 5 | 52 | 17 | 55 | 17 | 70 | 20 | 0 | 17 | 22 | 46 | 108 | 0 | 0 | 14 | 57 | 55 | 0 |  | 914 | 0 | 145 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 21 | 16 | 0 | 0 | 0 | 0 | 0 | 73 | 0 | 34 | 32 | 8 | 33 | 17 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 174 | 0 | 0 | 191 | 0 | 0 | 143 | 0 | 298 | 17 | 0 | 50 | 89 | 56 | 0 | 3 | 55 | 890 | 214 | 0 | 0 | 4 | 62 | 52 | 0 | 0 |  | 6512 | 3903 | 10415 | 3737 | 914 | 1820 | 0 | 1974 | 1090 | 110 | 191 | 486 | 154 | 130 | 1276.3814 | 93.13
13:00 | 0 | 0 | 0 | 180 | 300 | 85 | 0 | 399 | 322 |  | 0 | 225 | 0 | 8 | 0 | 30 | 0 | 0 | 94 | 8 | 8 | 50 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 0 | 25 | 27 | 0 | 28 | 42 | 0 | 77 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 0 | 26 | 49 | 56 | 12 | 25 | 15 | 4 | 0 | 0 | 0 | 345 | 330 | 205 | 8 | 142 | 36 | 52 | 0 | 51 | 0 | 32 | 8 | 22 | 9 | 25 | 17 | 154 | 66 | 0 | 22 | 1 | 43 | 41 | 33 | 30 | 110 | 0 | 60 | 10 | 0 | 221 | 0 | 29 | 10 | 310 | 8 | 0 | 0 | 195 | 0 | 0 | 47 | 0 | 95 | 7 | 21 | 34 | 122 | 403 | 49 | 88 | 82 | 4 | 52 | 17 | 55 | 17 | 67 | 20 | 0 | 17 | 47 | 50 | 108 | 0 | 0 | 35 | 53 | 55 | 0 |  | 913 | 0 | 145 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 25 | 16 | 0 | 0 | 0 | 0 | 5 | 73 | 0 | 34 | 32 | 8 | 33 | 17 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 176 | 0 | 0 | 212 | 0 | 0 | 140 | 0 | 287 | 17 | 0 | 50 | 89 | 56 | 0 | 3 | 55 | 930 | 212 | 0 | 0 | 4 | 1 | 52 | 0 | 0 |  | 6532 | 3897 | 10429 | 3720 | 913 | 1820 | 0 | 1966 | 1130 | 112 | 212 | 512 | 154 | 102 | 1171.3218 | 93.15
14:00 | 0 | 0 | 0 | 180 | 300 | 81 | 0 | 401 | 321 |  | 0 | 225 | 0 | 7 | 0 | 30 | 0 | 0 | 95 | 8 | 8 | 50 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 0 | 25 | 25 | 25 | 28 | 50 | 0 | 78 | 35 | 95 | 0 | 25 | 0 | 0 | 0 | 0 |  | 0 | 33 | 51 | 56 | 11 | 25 | 15 | 4 | 0 | 0 | 0 | 330 | 325 | 205 | 8 | 142 | 36 | 48 | 0 | 51 | 0 | 32 | 8 | 22 | 9 | 25 | 17 | 158 | 66 | 0 | 22 | 1 | 43 | 41 | 31 | 30 | 110 | 0 | 59 | 10 | 0 | 221 | 0 | 29 | 10 | 305 | 8 | 0 | 0 | 193 | 0 | 0 | 47 | 0 | 99 | 15 | 21 | 34 | 117 | 404 | 49 | 70 | 87 | 1 | 52 | 17 | 55 | 17 | 74 | 20 | 0 | 17 | 43 | 42 | 108 | 0 | 0 | 34 | 51 | 55 | 0 |  | 914 | 0 | 150 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 22 | 16 | 0 | 0 | 0 | 0 | 6 | 73 | 0 | 42 | 32 | 8 | 33 | 17 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 175 | 0 | 0 | 210 | 0 | 0 | 138 | 0 | 285 | 17 | 0 | 50 | 89 | 56 | 0 | 3 | 55 | 930 | 212 | 0 | 0 | 2 | 16 | 52 | 0 | 0 |  | 6518 | 3915 | 10433 | 3723 | 914 | 1799 | 0 | 1961 | 1130 | 113 | 210 | 520 | 158 | 115 | 1167.6355 | 93.17
15:00 | 0 | 0 | 0 | 180 | 300 | 84 | 0 | 397 | 318 |  | 0 | 225 | 0 | 8 | 0 | 30 | 0 | 0 | 94 | 8 | 8 | 48 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 19 | 25 | 25 | 25 | 28 | 42 | 0 | 78 | 35 | 95 | 0 | 25 | 0 | 0 | 0 | 0 |  | 0 | 33 | 51 | 56 | 12 | 23 | 15 | 4 | 0 | 0 | 0 | 320 | 315 | 203 | 8 | 142 | 36 | 50 | 0 | 51 | 0 | 39 | 8 | 22 | 9 | 33 | 20 | 146 | 66 | 0 | 22 | 1 | 43 | 41 | 31 | 30 | 110 | 0 | 58 | 10 | 0 | 221 | 0 | 31 | 10 | 315 | 8 | 0 | 0 | 195 | 0 | 0 | 47 | 0 | 97 | 14 | 21 | 34 | 112 | 394 | 49 | 70 | 87 | 2 | 52 | 17 | 55 | 17 | 74 | 20 | 0 | 17 | 36 | 46 | 108 | 0 | 0 | 20 | 66 | 55 | 0 |  | 913 | 0 | 145 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 24 | 16 | 0 | 0 | 0 | 16 | 7 | 73 | 0 | 42 | 32 | 8 | 33 | 17 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 176 | 0 | 0 | 209 | 0 | 0 | 140 | 0 | 285 | 17 | 0 | 50 | 67 | 57 | 0 | 3 | 55 | 950 | 210 | 0 | 0 | 2 | 43 | 90 | 0 | 0 |  | 6502 | 3991 | 10493 | 3712 | 913 | 1813 | 0 | 1984 | 1150 | 113 | 209 | 541 | 146 | 121 | 1037.6935 | 93.19
16:00 | 0 | 0 | 0 | 180 | 300 | 80 | 0 | 397 | 316 |  | 0 | 225 | 0 | 8 | 0 | 30 | 0 | 0 | 92 | 8 | 8 | 48 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 19 | 25 | 28 | 50 | 0 | 79 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 0 | 32 | 51 | 56 | 11 | 24 | 15 | 4 | 0 | 0 | 0 | 320 | 305 | 200 | 8 | 142 | 36 | 51 | 0 | 51 | 0 | 39 | 8 | 22 | 9 | 33 | 20 | 170 | 66 | 0 | 22 | 1 | 43 | 41 | 31 | 30 | 110 | 0 | 58 | 10 | 0 | 220 | 0 | 31 | 10 | 300 | 8 | 0 | 0 | 197 | 0 | 0 | 47 | 0 | 98 | 6 | 21 | 34 | 107 | 398 | 49 | 88 | 87 | 2 | 52 | 21 | 55 | 17 | 76 | 20 | 0 | 17 | 20 | 71 | 108 | 0 | 11 | 19 | 75 | 55 | 0 |  | 913 | 0 | 145 | 0 | 16 | 5 | 0 | 0 | 0 | 0 | 0 | 86 | 26 | 16 | 0 | 0 | 0 | 16 | 28 | 78 | 0 | 42 | 32 | 8 | 33 | 17 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 176 | 0 | 0 | 210 | 0 | 0 | 141 | 0 | 274 | 17 | 0 | 60 | 88 | 64 | 0 | 3 | 55 | 990 | 213 | 0 | 0 | 2 | 30 | 90 | 0 | 0 |  | 6561 | 4085 | 10646 | 3702 | 913 | 1787 | 0 | 2115 | 1190 | 114 | 215 | 567 | 170 | 83 | 804.535 | 93.21
17:00 | 0 | 0 | 0 | 180 | 140 | 85 | 0 | 405 | 317 |  | 0 | 225 | 0 | 7 | 0 | 30 | 0 | 0 | 92 | 8 | 8 | 110 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 24 | 25 | 28 | 50 | 0 | 79 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 0 | 24 | 51 | 56 | 11 | 25 | 15 | 14 | 0 | 0 | 0 | 335 | 330 | 191 | 8 | 141 | 36 | 54 | 0 | 51 | 0 | 39 | 8 | 22 | 9 | 33 | 17 | 168 | 67 | 0 | 22 | 1 | 43 | 41 | 33 | 30 | 110 | 0 | 57 | 10 | 0 | 220 | 0 | 31 | 10 | 270 | 8 | 0 | 0 | 247 | 0 | 0 | 47 | 0 | 98 | 3 | 21 | 41 | 113 | 374 | 49 | 88 | 87 | 2 | 52 | 36 | 55 | 114 | 94 | 20 | 0 | 17 | 7 | 162 | 108 | 0 | 32 | 10 | 75 | 55 | 0 |  | 913 | 0 | 145 | 0 | 16 | 5 | 0 | 0 | 0 | 0 | 8 | 83 | 25 | 16 | 0 | 0 | 0 | 24 | 38 | 78 | 0 | 42 | 32 | 8 | 33 | 17 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 175 | 0 | 0 | 148 | 0 | 0 | 141 | 0 | 280 | 17 | 0 | 92 | 88 | 94 | 0 | 3 | 55 | 990 | 213 | 0 | 0 | 1 | 30 | 90 | 0 | 0 |  | 6759 | 4111 | 10870 | 3554 | 913 | 1783 | 0 | 2509 | 1190 | 114 | 153 | 577 | 168 | 57 | 459.8659 | 93.23
18:00 | 0 | 0 | 0 | 180 | 0 | 92 | 0 | 396 | 316 |  | 0 | 225 | 0 | 12 | 0 | 30 | 0 | 0 | 91 | 8 | 8 | 125 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 24 | 25 | 28 | 50 | 0 | 79 | 35 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 24 | 51 | 56 | 34 | 25 | 15 | 20 | 0 | 0 | 0 | 280 | 310 | 200 | 8 | 137 | 36 | 54 | 0 | 51 | 0 | 39 | 8 | 22 | 9 | 33 | 20 | 152 | 67 | 0 | 22 | 0 | 43 | 41 | 33 | 30 | 110 | 0 | 58 | 10 | 0 | 220 | 0 | 31 | 10 | 300 | 8 | 0 | 0 | 262 | 0 | 0 | 168 | 0 | 127 | 1 | 21 | 68 | 115 | 403 | 78 | 88 | 87 | 0 | 52 | 36 | 55 | 114 | 102 | 20 | 0 | 17 | 1 | 162 | 108 | 0 | 35 | 2 | 75 | 55 | 0 |  | 914 | 0 | 145 | 0 | 16 | 5 | 0 | 0 | 3 | 0 | 8 | 86 | 24 | 16 | 0 | 0 | 0 | 24 | 40 | 88 | 0 | 42 | 32 | 8 | 33 | 18 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 176 | 0 | 0 | 130 | 0 | 0 | 141 | 0 | 279 | 17 | 0 | 94 | 105 | 92 | 0 | 2 | 95 | 980 | 213 | 0 | 0 | 0 | 6 | 90 | 0 | 0 |  | 6851 | 4133 | 10984 | 3371 | 914 | 1824 | 0 | 2823 | 1180 | 114 | 135 | 589 | 152 | 12 | 245.139 | 93.25
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
19:00 | 0 | 0 | 0 | 180 | 0 | 93 | 0 | 396 | 281 |  | 0 | 225 | 0 | 29 | 0 | 30 | 0 | 0 | 94 | 20 | 24 | 125 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 24 | 25 | 28 | 50 | 0 | 46 | 35 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 24 | 51 | 56 | 68 | 25 | 15 | 22 | 0 | 0 | 0 | 340 | 330 | 187 | 8 | 135 | 39 | 54 | 0 | 51 | 0 | 39 | 15 | 22 | 9 | 33 | 20 | 148 | 78 | 0 | 22 | 0 | 43 | 41 | 50 | 41 | 110 | 0 | 58 | 70 | 0 | 220 | 0 | 32 | 10 | 320 | 8 | 11 | 0 | 261 | 0 | 0 | 177 | 0 | 149 | 0 | 90 | 68 | 117 | 380 | 78 | 88 | 87 | 0 | 202 | 36 | 55 | 114 | 102 | 54 | 0 | 17 | 0 | 162 | 108 | 0 | 35 | 0 | 75 | 55 | 0 |  | 913 | 0 | 145 | 0 | 16 | 15 | 0 | 0 | 44 | 14 | 8 | 85 | 30 | 16 | 0 | 0 | 0 | 24 | 41 | 88 | 0 | 42 | 32 | 35 | 33 | 21 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 175 | 0 | 0 | 140 | 0 | 0 | 142 | 0 | 279 | 24 | 0 | 94 | 105 | 92 | 0 | 0 | 95 | 960 | 213 | 0 | 0 | 0 | 0 | 90 | 0 | 0 |  | 7328 | 4222 | 11550 | 3440 | 913 | 1910 | 0 | 3228 | 1160 | 81 | 155 | 655 | 148 | 0 | 1059.8112 | 93.31
19:30 | 0 | 0 | 0 | 180 | 0 | 93 | 0 | 397 | 266 |  | 0 | 225 | 0 | 50 | 0 | 30 | 0 | 0 | 97 | 50 | 50 | 125 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 24 | 25 | 28 | 50 | 0 | 46 | 35 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 24 | 51 | 56 | 80 | 25 | 15 | 20 | 0 | 0 | 0 | 300 | 325 | 190 | 8 | 135 | 39 | 54 | 0 | 51 | 0 | 40 | 43 | 22 | 9 | 33 | 20 | 152 | 94 | 0 | 22 | 0 | 44 | 41 | 50 | 48 | 110 | 0 | 61 | 78 | 0 | 222 | 0 | 32 | 10 | 310 | 8 | 11 | 0 | 262 | 0 | 0 | 180 | 0 | 149 | 0 | 90 | 68 | 121 | 400 | 78 | 88 | 87 | 0 | 204 | 36 | 55 | 114 | 113 | 90 | 0 | 51 | 0 | 162 | 108 | 0 | 35 | 0 | 75 | 55 | 0 |  | 913 | 0 | 145 | 0 | 16 | 15 | 0 | 0 | 39 | 30 | 8 | 86 | 31 | 16 | 0 | 0 | 0 | 24 | 41 | 90 | 0 | 42 | 32 | 52 | 33 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 176 | 0 | 0 | 197 | 0 | 0 | 142 | 0 | 283 | 45 | 0 | 94 | 105 | 92 | 0 | 0 | 95 | 1060 | 220 | 0 | 0 | 0 | 0 | 90 | 0 | 0 |  | 7533 | 4445 | 11978 | 3446 | 913 | 1911 | 0 | 3474 | 1260 | 81 | 212 | 726 | 152 | 0 | 1310.4796 | 0
20:00 | 0 | 0 | 0 | 180 | 0 | 93 | 0 | 395 | 267 |  | 0 | 225 | 0 | 50 | 0 | 30 | 0 | 0 | 91 | 50 | 50 | 125 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 24 | 25 | 16 | 50 | 0 | 46 | 35 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 24 | 51 | 56 | 81 | 25 | 15 | 27 | 0 | 0 | 0 | 280 | 305 | 202 | 8 | 135 | 39 | 54 | 0 | 51 | 0 | 40 | 43 | 22 | 9 | 33 | 20 | 152 | 95 | 0 | 22 | 0 | 43 | 41 | 50 | 48 | 110 | 0 | 63 | 78 | 0 | 222 | 0 | 32 | 10 | 280 | 8 | 11 | 0 | 260 | 0 | 0 | 170 | 0 | 149 | 0 | 90 | 68 | 122 | 403 | 78 | 88 | 87 | 0 | 210 | 36 | 55 | 114 | 109 | 90 | 0 | 44 | 0 | 162 | 108 | 0 | 35 | 0 | 75 | 55 | 0 |  | 913 | 0 | 145 | 0 | 16 | 15 | 0 | 0 | 39 | 70 | 8 | 88 | 31 | 32 | 0 | 0 | 0 | 24 | 41 | 90 | 0 | 42 | 32 | 52 | 33 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 174 | 0 | 0 | 207 | 0 | 0 | 142 | 0 | 295 | 47 | 0 | 94 | 105 | 92 | 0 | 0 | 95 | 1050 | 220 | 0 | 0 | 0 | 0 | 90 | 0 | 0 |  | 7453 | 4515 | 11968 | 3403 | 913 | 1901 | 0 | 3477 | 1250 | 81 | 222 | 776 | 152 | 0 | 1550.0891 | 93.29
21:00 | 0 | 0 | 0 | 180 | 0 | 93 | 0 | 394 | 267 |  | 0 | 225 | 0 | 50 | 0 | 30 | 0 | 0 | 95 | 50 | 40 | 125 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 24 | 25 | 33 | 50 | 0 | 76 | 35 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 24 | 51 | 56 | 81 | 25 | 15 | 32 | 0 | 0 | 0 | 280 | 305 | 202 | 8 | 135 | 37 | 55 | 0 | 51 | 0 | 40 | 43 | 22 | 9 | 33 | 20 | 164 | 101 | 0 | 22 | 0 | 43 | 41 | 50 | 49 | 110 | 0 | 63 | 81 | 0 | 221 | 0 | 32 | 10 | 290 | 16 | 11 | 0 | 260 | 0 | 0 | 171 | 0 | 149 | 0 | 90 | 68 | 127 | 403 | 78 | 88 | 87 | 0 | 214 | 36 | 55 | 114 | 113 | 100 | 0 | 54 | 0 | 162 | 108 | 0 | 35 | 0 | 75 | 55 | 0 |  | 914 | 0 | 150 | 0 | 16 | 35 | 0 | 0 | 33 | 65 | 8 | 86 | 32 | 32 | 0 | 0 | 0 | 24 | 41 | 90 | 0 | 42 | 32 | 52 | 33 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 178 | 0 | 0 | 216 | 0 | 0 | 145 | 0 | 296 | 53 | 0 | 94 | 105 | 92 | 0 | 0 | 95 | 1060 | 220 | 0 | 0 | 0 | 0 | 90 | 0 | 0 |  | 7570 | 4562 | 12132 | 3444 | 914 | 1923 | 0 | 3507 | 1260 | 111 | 251 | 774 | 164 | 0 | 1537.1871 | 93.31
22:00 | 0 | 0 | 0 | 180 | 0 | 93 | 0 | 394 | 267 |  | 0 | 225 | 0 | 48 | 0 | 30 | 0 | 0 | 57 | 50 | 40 | 125 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 24 | 25 | 33 | 50 | 0 | 76 | 35 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 24 | 51 | 56 | 81 | 26 | 15 | 35 | 0 | 0 | 0 | 280 | 310 | 208 | 8 | 135 | 34 | 55 | 0 | 51 | 0 | 40 | 43 | 22 | 9 | 33 | 20 | 166 | 101 | 0 | 0 | 0 | 43 | 41 | 50 | 49 | 110 | 0 | 63 | 81 | 0 | 220 | 0 | 32 | 10 | 280 | 10 | 11 | 0 | 243 | 0 | 0 | 171 | 0 | 149 | 0 | 90 | 68 | 132 | 403 | 78 | 88 | 87 | 0 | 214 | 36 | 55 | 114 | 112 | 100 | 0 | 60 | 0 | 162 | 108 | 0 | 35 | 0 | 75 | 55 | 0 |  | 913 | 0 | 150 | 0 | 32 | 118 | 0 | 0 | 33 | 59 | 8 | 88 | 32 | 32 | 0 | 0 | 0 | 24 | 40 | 87 | 0 | 42 | 32 | 52 | 33 | 22 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 177 | 0 | 0 | 218 | 0 | 0 | 145 | 0 | 306 | 53 | 0 | 94 | 105 | 92 | 0 | 0 | 95 | 1080 | 220 | 0 | 0 | 0 | 0 | 90 | 0 | 0 |  | 7498 | 4672 | 12170 | 3375 | 913 | 1926 | 0 | 3515 | 1280 | 111 | 336 | 766 | 166 | 0 | 1410.0098 | 93.33
23:00 | 0 | 0 | 0 | 180 | 0 | 93 | 0 | 400 | 287 |  | 0 | 225 | 0 | 50 | 0 | 30 | 0 | 0 | 95 | 50 | 40 | 125 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 26 | 25 | 33 | 50 | 0 | 76 | 35 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 26 | 51 | 56 | 42 | 25 | 15 | 38 | 0 | 0 | 0 | 320 | 335 | 205 | 8 | 135 | 37 | 54 | 0 | 51 | 0 | 40 | 43 | 22 | 10 | 33 | 20 | 164 | 102 | 0 | 0 | 0 | 44 | 41 | 50 | 49 | 110 | 0 | 62 | 81 | 0 | 220 | 0 | 32 | 10 | 310 | 12 | 11 | 0 | 245 | 0 | 0 | 171 | 0 | 149 | 0 | 90 | 68 | 133 | 402 | 78 | 88 | 87 | 0 | 52 | 36 | 55 | 114 | 113 | 100 | 0 | 55 | 0 | 162 | 108 | 0 | 35 | 0 | 75 | 55 | 0 |  | 913 | 0 | 160 | 0 | 32 | 120 | 0 | 0 | 33 | 59 | 8 | 84 | 30 | 32 | 0 | 0 | 0 | 24 | 40 | 87 | 0 | 42 | 32 | 52 | 33 | 22 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 177 | 0 | 0 | 217 | 0 | 0 | 146 | 0 | 298 | 53 | 0 | 94 | 105 | 92 | 0 | 0 | 95 | 1090 | 221 | 0 | 0 | 0 | 0 | 90 | 0 | 0 |  | 7463 | 4681 | 12144 | 3496 | 913 | 1969 | 0 | 3314 | 1290 | 111 | 337 | 767 | 164 | 0 | 1341.8132 | 93.35
24:00 | 0 | 0 | 0 | 180 | 0 | 93 | 0 | 404 | 311 |  | 0 | 225 | 0 | 11 | 0 | 30 | 0 | 0 | 0 | 15 | 8 | 84 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 25 | 27 | 25 | 33 | 50 | 0 | 76 | 35 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 18 | 51 | 56 | 11 | 25 | 15 | 38 | 0 | 0 | 0 | 300 | 310 | 192 | 8 | 135 | 37 | 55 | 0 | 51 | 0 | 40 | 43 | 22 | 10 | 33 | 20 | 166 | 101 | 0 | 0 | 0 | 43 | 41 | 53 | 49 | 110 | 0 | 61 | 81 | 0 | 221 | 0 | 32 | 10 | 315 | 16 | 11 | 0 | 243 | 0 | 0 | 48 | 0 | 149 | 0 | 90 | 68 | 133 | 404 | 48 | 88 | 87 | 0 | 52 | 36 | 55 | 17 | 57 | 100 | 0 | 18 | 0 | 162 | 108 | 0 | 35 | 0 | 76 | 55 | 0 |  | 913 | 0 | 160 | 0 | 32 | 150 | 0 | 0 | 33 | 60 | 8 | 86 | 33 | 32 | 0 | 0 | 0 | 24 | 40 | 80 | 0 | 42 | 32 | 8 | 33 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 177 | 0 | 0 | 217 | 0 | 0 | 147 | 0 | 297 | 0 | 0 | 50 | 105 | 56 | 0 | 0 | 95 | 1070 | 220 | 0 | 0 | 0 | 0 | 90 | 0 | 0 |  | 6805 | 4523 | 11328 | 3366 | 913 | 2003 | 0 | 2637 | 1270 | 111 | 367 | 712 | 166 | 0 | 1633.0309 | 92.89
KWH | 0 | 0 | 0 | 4347000 | 5116509 | 2066863 | 0 | 9797630 | 7488000 |  | 0 | 5036500 | 0 | 391680 | 0 | 744792 | 0 | 0 | 2356000 | 378240 | 355680 | 1709280 | 0 | 0 | 0 | 0 | 889920 | 1331942 | 954209 | 371160 | 600000 | 565200 | 589300 | 703700 | 1167902 | 0 | 1755490 | 844000 | 2400000 | 0 | 433251 | 0 | 0 | 0 | 0 |  | 0 | 614736 | 976181 | 1337640 | 1464960 | 610080 | 353184 | 596160 | 0 | 0 | 0 | 8040600 | 7815000 | 4934000 | 217454 | 3351740 | 859536 | 1289740 | 0 | 1217689 | 0 | 835272 | 391325 | 500112 | 234900 | 782600 | 488530 | 3682560 | 2053440 | 0 | 462276 | 8950 | 1024000 | 974760 | 852000 | 892656 | 2602554 | 0 | 1437312 | 666240 | 0 | 5375710 | 0 | 715820 | 239400 | 7437500 | 198696 | 57200 | 0 | 5151162 | 0 | 0 | 1828800 | 0 | 2711090 | 108540 | 887040 | 1515360 | 2979127 | 9543000 | 1344000 | 2204400 | 2021482 | 28080 | 1563164 | 777680 | 1313085 | 1079580 | 2056320 | 954240 | 0 | 515520 | 236380 | 2724480 | 2608200 | 0 | 646920 | 159232 | 1640640 | 1329840 | 0 |  | 22080000 | 0 | 4004352 | 0 | 419520 | 387443 | 0 | 0 | 287520 | 667904 | 96375 | 2071507 | 620717 | 509280 | 0 | 0 | 0 | 420448 | 495491 | 1918856 | 0 | 889248 | 621410 | 376200 | 790600 | 455400 | 0 | 216594 | 0 | 0 | 4870900 | 0 | 0 | 4588755 | 0 | 0 | 4299255 | 0 | 0 | 3837264 | 0 | 7582472 | 390240 | 0 | 1644768 | 2423952 | 1620105 | 0 | 29804 | 1602816 | 26047900 | 5208245 | 0 | 0 | 22140 | 449280 | 1693056 | 0 | 0 |  | 165914123 | 103639817 | 269553940 | 90051567 | 22080000 | 45185410 | 0 | 59969311 | 30918800 | 2599490 | 4686698 | 9337698 | 3682560 | 1042406 | 0
Fuel Cost | 0 | 0 | 0 | 6477030 | 5730490.08 | 2748927.79 | 0 | 10287511.5 | 8087040 |  | 0 | 5489785 | 0 | 4378982.4 | 0 | 9868494 | 0 | 0 | 4123000 | 5529868.8 | 5004417.6 | 27707428.8 | 0 | 0 | 0 | 0 | 11319782.4 | 17981217 | 12795942.69 | 278370 | 450000 | 0 | 0 | 0 | 19866013.02 | 0 | 473982.3 | 227880 | 4536000 | 0 | 7083653.85 | 0 | 0 | 0 | 0 |  | 0 | 10253796.48 | 16614600.62 | 18071516.4 | 18575692.8 | 7058625.6 | 448543.68 | 1985212.8 | 0 | 0 | 0 | 8925066 | 8518350 | 5723440 | 280515.66 | 4089122.8 | 971275.68 | 1921712.6 | 0 | 2033540.63 | 0 | 14425147.44 | 5263321.25 | 685153.44 | 176175 | 1369550 | 366397.5 | 26440780.8 | 2238249.6 | 0 | 628695.36 | 142663 | 1402880 | 1286683.2 | 1482480 | 1544294.88 | 2992937.1 | 0 | 2788385.28 | 1519027.2 | 0 | 5429467.1 | 0 | 1066571.8 | 474012 | 7437500 | 149022 | 43472 | 0 | 70313361.3 | 0 | 0 | 24652224 | 0 | 37548596.5 | 1268832.6 | 9154252.8 | 20699817.6 | 39533015.29 | 8779560 | 16343040 | 31875624 | 25571747.3 | 0 | 18351545.36 | 8468935.2 | 13958093.55 | 14649900.6 | 26505964.8 | 11240947.2 | 0 | 6675984 | 3415691 | 34573651.2 | 29681316 | 0 | 8448775.2 | 1902822.4 | 24560380.8 | 17513992.8 | 0 |  | 66240000 | 0 | 4484874.24 | 0 | 4367203.2 | 6392809.5 | 0 | 0 | 5178235.2 | 12022272 | 1384908.75 | 2320087.84 | 1204190.98 | 5551152 | 0 | 0 | 0 | 7050912.96 | 8666137.59 | 30010907.84 | 0 | 14725946.88 | 10508043.1 | 5127606 | 13337422 | 942678 | 0 | 163961.658 | 0 | 0 | 25767061 | 0 | 0 | 5322955.8 | 0 | 0 | 75064992.3 | 0 | 0 | 4451226.24 | 0 | 7506647.28 | 5244825.6 | 0 | 19457605.44 | 35026106.4 | 20575333.5 | 0 | 329334.2 | 19458186.24 | 234691579 | 5312409.9 | 0 | 0 | 250403.4 | 5270054.4 | 25954548.48 | 0 | 0 |  | 860957766.43 | 689362618.918 | 1550320385.348 | 102644995.998 | 66240000 | 54029483.62 | 0 | 789992115.8 | 260458640 | 701862.3 | 81457801.8 | 155774904.03 | 26440780.8 | 12579801 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 300 | 88 | 0 | 410 | 343 |  | 0 | 225 | 0 | 7 | 0 | 30 | 0 | 0 | 97 | 8 | 8 | 50 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 27 | 25 | 16 | 51 | 0 | 76 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 0 | 26 | 17 | 56 | 89 | 26 | 11 | 7 | 0 | 0 | 0 | 325 | 320 | 208 | 8 | 142 | 38 | 53 | 0 | 51 | 0 | 32 | 8 | 22 | 11 | 33 | 16 | 110 | 103 | 0 | 22 | 0 | 43 | 41 | 31 | 30 | 110 | 0 | 61 | 10 | 0 | 221 | 0 | 31 | 10 | 305 | 8 | 0 | 0 | 195 | 0 | 0 | 47 | 0 | 99 | 0 | 21 | 68 | 132 | 399 | 49 | 88 | 68 | 3 | 16 | 36 | 55 | 17 | 78 | 20 | 0 | 17 | 4 | 54 | 108 | 0 | 35 | 4 | 58 | 55 | 0 |  | 913 | 0 | 170 | 0 | 16 | 0 | 0 | 0 | 0 | 19 | 0 | 87 | 23 | 16 | 0 | 0 | 0 | 0 | 0 | 79 | 0 | 34 | 32 | 8 | 33 | 20 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 189 | 0 | 0 | 140 | 0 | 0 | 160 | 0 | 330 | 0 | 0 | 50 | 105 | 56 | 0 | 2 | 55 | 930 | 219 | 0 | 0 | 0 | 49 | 52 | 0 | 0 |  | 10629 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 0 | 93 | 0 | 394 | 267 | 0 | 0 | 225 | 0 | 50 | 0 | 30 | 0 | 0 | 95 | 50 | 40 | 125 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 24 | 25 | 33 | 50 | 0 | 76 | 35 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 51 | 56 | 81 | 25 | 15 | 32 | 0 | 0 | 0 | 280 | 305 | 202 | 8 | 135 | 37 | 55 | 0 | 51 | 0 | 40 | 43 | 22 | 9 | 33 | 20 | 164 | 101 | 0 | 22 | 0 | 43 | 41 | 50 | 49 | 110 | 0 | 63 | 81 | 0 | 221 | 0 | 32 | 10 | 290 | 16 | 11 | 0 | 260 | 0 | 0 | 171 | 0 | 149 | 0 | 90 | 68 | 127 | 403 | 78 | 88 | 87 | 0 | 214 | 36 | 55 | 114 | 113 | 100 | 0 | 54 | 0 | 162 | 108 | 0 | 35 | 0 | 75 | 55 | 0 |  | 914 | 0 | 150 | 0 | 16 | 35 | 0 | 0 | 33 | 65 | 8 | 86 | 32 | 32 | 0 | 0 | 0 | 24 | 41 | 90 | 0 | 42 | 32 | 52 | 33 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 178 | 0 | 0 | 216 | 0 | 0 | 145 | 0 | 296 | 53 | 0 | 94 | 105 | 92 | 0 | 0 | 95 | 1060 | 220 | 0 | 0 | 0 | 0 | 90 | 0 | 0 |  | 12132 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 0 | 93 | 0 | 412 | 330 | 0 | 0 | 225 | 0 | 50 | 0 | 30 | 0 | 0 | 0 | 50 | 50 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 25 | 25 | 33 | 51 | 0 | 76 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 51 | 56 | 95 | 32 | 17 | 30 | 0 | 0 | 0 | 330 | 320 | 210 | 8 | 142 | 37 | 55 | 0 | 51 | 0 | 40 | 43 | 22 | 10 | 33 | 20 | 166 | 102 | 0 | 20 | 0 | 43 | 41 | 53 | 49 | 110 | 0 | 61 | 81 | 0 | 220 | 0 | 32 | 10 | 290 | 16 | 11 | 0 | 275 | 0 | 0 | 180 | 0 | 149 | 0 | 90 | 200 | 132 | 400 | 79 | 88 | 90 | 0 | 214 | 36 | 55 | 114 | 113 | 100 | 0 | 104 | 0 | 162 | 108 | 0 | 35 |  | 60 | 55 |  |  | 930 | 0 | 185 | 0 | 16 | 0 | 0 | 0 | 32 | 70 | 8 | 88 | 30 | 32 | 0 | 0 | 0 | 32 | 40 | 86 | 0 | 42 | 32 | 52 | 33 | 21 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 350 | 35 | 0 | 94 | 105 | 92 | 0 | 0 | 95 | 1100 | 220 |  | 0 |  |  | 90
Forecast for Day | 0 | 0 | 0 | 180 | 0 | 90 | 0 | 412 | 300 | 0 | 0 | 225 | 0 | 8 | 0 | 30 | 0 | 0 | 0 | 8 | 8 | 50 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 25 | 25 | 33 | 51 | 0 | 76 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 17 | 56 | 90 | 25 | 17 | 10 | 0 | 0 | 0 | 310 | 305 | 210 | 8 | 142 | 37 | 55 | 0 | 51 | 0 | 32 | 8 | 22 | 10 | 33 | 20 | 143 | 102 | 0 | 20 | 1.6 | 43 | 41 | 33 | 30 | 110 | 0 | 61 | 10 | 0 | 220 | 0 | 31 | 10 | 290 | 8 | 11 | 0 | 110 | 0 | 0 | 48 | 0 | 100 | 20 | 21 | 100 | 128 | 400 | 49 | 88 | 68 | 5 | 50 | 36 | 55 | 17 | 78 | 20 | 0 | 17 | 50 | 70 | 108 | 0 | 35 | 30 | 60 | 55 |  |  | 930 | 0 | 180 | 0 | 16 | 0 | 0 | 0 | 15 | 20 | 0 | 88 | 23 | 16 | 0 | 0 | 0 | 24 | 0 | 80 | 0 | 42 | 32 | 8 | 33 | 21 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 188 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 350 | 0 | 0 | 50 | 105 | 56 | 0 | 8 | 55 | 1110 | 225 |  | 0 | 6 | 100 | 52
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 0 | 86 | 0 | 403 | 322 | 0 | 0 | 225 | 0 | 8 | 0 | 30 | 0 | 0 | 0 | 8 | 8 | 50 | 0 | 0 | 0 | 0 | 35 | 55 | 17 | 19 | 25 | 17 | 25 | 33 | 51 | 0 | 79 | 35 | 100 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 17 | 56 | 12 | 25 | 15 | 12 | 0 | 0 | 0 | 290 | 275 | 178 | 8 | 142 | 35 | 40 | 0 | 51 | 0 | 24 | 10 | 0 | 10 | 33 | 20 | 148 | 96 | 0 | 20 | 1 | 44 | 41 | 33 | 30 | 110 | 0 | 62 | 10 | 0 | 221 | 0 | 31 | 10 | 330 | 8 | 0 | 0 | 195 | 0 | 0 | 48 | 0 | 99 | 13 | 21 | 34 | 122 | 400 | 49 | 88 | 87 | 3 | 50 | 36 | 55 | 17 | 38 | 20 | 0 | 17 | 23 | 54 | 108 | 0 | 35 | 16 | 75 | 55 | 0 | 0 | 914 | 0 | 160 | 0 | 16 | 224 | 0 | 0 | 0 | 0 | 0 | 86 | 20 | 16 | 0 | 0 | 0 | 24 | 0 | 72 | 0 | 42 | 32 | 8 | 0 | 20 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 177 | 0 | 0 | 214 | 0 | 0 | 148 | 0 | 305 | 0 | 0 | 50 | 88 | 56 | 0 | 2 | 55 | 980 | 220 | 0 | 0 | 1 | 56 | 34 | 0 | 0 | 0 |  |  |  |  | 73993707 |  | 0
73993707
| Minimum Generation |  | 10552 | 8:00
| Highest Generation |  | 12170 | 22:00
| Day Peak Generation |  | 10629 | 9:00
| Evening Peak Generation |  | 12132 | 21:00
| HVDC Max Flow |  | 914 | 1:00
| HVDC EvPeak Flow |  | 914 | 21:00
| Load factor L.F |  | 92.29% | [159 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2022-08-07
Till now the maximum generation is : - |  |  | 14782 | 21:00 | Hrs on | 2022-04-16
The Summary of Yesterday's |  | 2022-08-06 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 10629 | MW Hour : | 9:00 | Min. Gen. at | 8:00 | 10290 | MW
Evening Peak Generation : |  | 12132 | MW Hour : | 21:00 | Available Max Generation : |  | 12380 | MW
E.P. Demand (at gen end) : |  | 13800 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 14000 | MW
Maximum Generation : |  | 12170 | MW Hour : | 22:00 | Reserve(Generation end) |  | - | MW
Total Gen. (MKWH) : |  | 269.5539 | System Load Factor : | 92.29% | Load Shed : |  | 1493.4046 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | 454 | MW at | 5:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2022-08-07
Actual : | 93.54 | Ft.(MSL) , | Rule curve : | 90.92 | Ft.( MSL )
Gas Consumed : | Total = | 1000.91 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 156674479.618
: |  | Coal : | 260458640 | Oil : | 1027224821.63 | Total : | 1444357941.248
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 380 | 9120:00 | 4483.4624 |  |  | 451.2422 | 10.06%
Chittagong Area | 180 | 4320:00 | 1269.5617 |  |  | 156.4271 | 12.32%
Khulna Area | 200 | 4800:00 | 1675.9763 |  |  | 213.3487 | 12.73%
Rajshahi Area | 190 | 4560:00 | 1487.6064 |  |  | 197.9019 | 13.3%
Cumilla Area | 170 | 4080:00 | 1265.6911 |  |  | 164.1949 | 12.97%
Mymensingh Area | 210 | 5040:00 | 1046.3563 |  |  | 141.4381 | 13.52%
Sylhet Area | 87 | 2088:00 | 467.0542 |  |  | 57.6666 | 12.35%
Barisal Area | 0 | 0:00 | 380.6105 |  |  | 0 | 0%
Rangpur Area | 120 | 2880:00 | 825.7312 |  |  | 111.1853 | 13.47%
Total | 1537 |  | 12902.05 |  |  | 1493.4046
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2
2) Ghorasal-3,4
3) Ashuganj-5
4) Baghabari-71,100 MW
5) Raozan unit-1,2
6) Siddhirganj 210 MW .
7) Sikalbaha 225 MW
8) Shajibazar 330 MW
9) Siddhirganj 335 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Kabirpur-Kodda 132 kV Ckt-1 was under shut down from 08:52 to 19:16 for D/W.
b) Sikalbaha 132/33 kV T-3 transformer was under shut down from 09:22 to 12:30 for D/W.
c) Aminbazar-Mirpur 132 kV Ckt-1 was under shut down from 11:04 to 18:19 for C/M.
d) Chowddagram 132/33 kV T-1 transformer & its associated 33 kV Bus were under shut down from 12:45 to | [5 empty] | About 22 MW power interruption occurred under
14:44 for C/M. | [5 empty] | Chowddagram S/S area from 12:45 to 14:44.
e) Aminbazar 230/132 kV T-02 transformer was under shut down from 12:25 to 17:54 for C/M.
f) Ghorashal Unit-7 was force shutdown at 17:21 due to air compressor problem.
g) Maniknagar-Siddhirganj 230 kV Ckt-1 & Maniknagar 230/132 kV T-01 was switched on at 21:16.
h) Aminbazar 132 kV main Bus was under shutdown from 17:34 to 19:44 for C/M.
i) Shahjadpur 132/33 kV T-3 transformer was under shut down from 23:55 to 00:15(07/08/2022) due to R/H | [5 empty] | About 10 MW power interruption occurred under
maintenance at 33 kV bushing. | [5 empty] | Shahjadpur S/S area from 23:55 to 00:15(07/08/2022).
j) Khulna GT-Goalpara 132 kV Ckt was opened at 00:50(07/08/2022) from Goalpara end due to O/L.
k) Hathazari 132/33 kV T-1 transformer tripped at 02:55(07/08/2022) showing Diff. At HT side & Lockout at LT
side and was switched on at 10:14(07/08/2022).
| Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2022-08-06 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4347000
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 5116509 | Under maint.
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 93 | 2066863 | Engine problem
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 394 | 9797630 | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 267 | 7488000 | Machine problem
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 5036500 | Gas shortage & GT-2 S/D.
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 50 | 391680 | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 0 | 0 | Under maint.
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 30 | 744792 | Engine problem
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 371160
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 95 | 2356000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 50 | 378240 | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 40 | 355680 | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 889920
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 125 | 1709280 | Engine problem
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 1331942
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 954209
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 49 | 1165200 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 589300 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 703700
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 50 | 1167902 | #REF!
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 260 | 5151162 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Fuel conservation
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 0 | 0 | Fuel conservation
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Fuel conservation
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 2711090
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 88 | 2204400 | Engine problem
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 54 | 515520 | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 2724480
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 159232
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 55 | 1329840
| Dhaka area Total |  |  |  | 5847 | 2657 | 61757231
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 100 | 2400000 | Machine problem
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 0 | 433251
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 108540
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 25 | 610080 | Engine problem
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 111 | 2599490 | Low water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | HGPI for 30 days.
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 87 | 2021482 | Engine problem
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 24 | 614736 | Fuel shortage
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 976181 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 56 | 1337640 | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 90 | 887040 | Engine problem
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 15 | 353184 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 32 | 596160
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 81 | 1464960 | Engine problem
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 28080
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 214 | 1563164 | Engine problem
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 36 | 777680 | Fuel shortage
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 55 | 1313085 | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 954240
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 108 | 2608200 | Engine problem
| Chattogram area Total |  |  |  | 2382 | 1185 | 21647193
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 202 | 4934000 | #REF!
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 280 | 8040600 | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 305 | 7815000 | Gas shortage
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+136*1 | 284 | 0 | 0 | On test.
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 37 | 859536 | Machine problem
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 55 | 1289740
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 217454 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1217689
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 127 | 2979127 | Engine problem
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 40 | 835272 | Engine problem
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 135 | 3351740 | Machine problem
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 68 | 1515360 | Fuel shortage
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 500112
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 9 | 234900 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 164 | 3682560
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 782600
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 43 | 391325 | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 20 | 488530 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Fuel conservation
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 1079580
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 113 | 2056320
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 35 | 646920 | 33 kV feeder problem.
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 75 | 1640640 | Fuel shortage
| Cumilla Area Total |  |  |  | 3169 | 1936 | 44559005
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 101 | 2053440 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 462276
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 8950
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 171 | 1828800 | Engine problem
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 78 | 1344000 | Engine problem
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 236380
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 0 | Engine problem
| Mymensingh Area Total |  |  |  | 614 | 372 | 5933846
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1024000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 41 | 974760 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 110 | 2602554 | ST under maint.
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 50 | 852000
| Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 49 | 892656
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 57200
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 63 | 1437312
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 666240 | Engine problem
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 221 | 5375710
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50MW PP (EPL) |  | NENP | 27*2 | 50 | 32 | 715820 | Gas shortage
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 198696 | Engine problem
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 7437500 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 403 | 9543000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 239400
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 0 | 0 | Under maint.
| Sylhet Area Total |  |  |  | 2477 | 1420 | 32016848
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 914 | 22080000
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 16 | 419520 | Fuel shortage
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 33 | 287520 | Engine problem
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 35 | 387443 | Fuel conservation
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 65 | 667904 | Line O/L
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 150 | 4004352 | Gas shortage.
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 8 | 96375 | Fuel shortage
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 53 | 390240 | Fuel shortage
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 105 | 2423952
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 449280
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 0 | 0 | 0 | On test.
| Khulna Area Total |  |  |  | 2384 | 1379 | 31206586
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 32 | 509280 | Line O/L
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 32 | 620717 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 86 | 2071507 | ST under S/D
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1060 | 26047900 | Line O/L
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 5208245
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Line O/L
| Barisal Area Total |  |  |  | 1958 | 1430 | 34457649
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 24 | 420448 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 41 | 495491 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contract Expired
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 42 | 889248 | Engine problem
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 621410 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 178 | 4588755 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 216 | 4299255
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 145 | 3837264 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 296 | 7582472 | Gas shortage
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 33 | 790600 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 455400
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | .
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 216594
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 376200
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 90 | 1918856 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Fuel conservation
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 94 | 1644768 | Engine problem
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 95 | 1602816 | Engine problem
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 22140
| Rajshahi Area Total |  |  |  | 2129 | 1371 | 29761717
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 200 | 4870900 | Coal shortage
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 92 | 1620105 | Engine problem
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 29804
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 90 | 1693056 | Fuel shortage
| Rangpur Area Total |  |  |  | 720 | 382 | 8213865
| Total |  |  |  | 21680 | 12132 | 269553940
| Eastern Grid Total |  |  |  | 14489 | 7570 | 165914123
| Western Grid Total |  |  |  | 7191 | 4562 | 103639817
| National Grid Total |  |  |  | 21680 | 12132 | 269553940
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2022-08-06
(a) ENTIRE EASTERN GRID : |  | 7874.19 | MW | (b) ENTIRE WESTERN GRID : |  | 3579.31 | MW
i) Dhaka area |  | 4167.19 | MW | i) Khulna area |  | 1302 | MW
ii) Chittagong area |  | 1319 | MW | ii) Rajshahi area |  | 1171.4 | MW
iii) Comilla area |  | 1037 | MW | iii) Barisal area |  | 385.91 | MW
iv) Mymensingh area |  | 890 | MW | iv) Rangpur area |  | 720 | MW
v) Sylhet area |  | 461 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 11453.5 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
AKS | 18 | 11:00 | Chowmuhani | 174 | 01:00 | Kaptai | 4.2 | 20:00 | Nawabganj | 36.9 | 19:00 | Siddhirganj | 108 | 22:00
AKSML | 110 | 13:00 | Chuadanga | 88 | 06:00 | Kazla | 86 | 17:00 | Netrakona | 96 | 19:00 | Sirajganj | 88 | 07:00
Aftabnagar | 33 | 20:00 | Coxsbazar | 124 | 20:00 | Keranigonj | 56 | 19:30 | New | 81 | 09:00 | Sonargaon | 80 | 12:00
Agargaon | 79 | 00:00 | Cumilla(N) | 142 | 19:00 | Khagrachori | 26 | 21:00 | Niamatpur | 64 | 06:00 | Sreemongol | 44 | 12:00
Agrabad | 72 | 19:30 | Cumilla(S) | 170 | 02:00 | Khulna | 74 | 21:00 | Noapara | 47 | 01:00 | Srinagar | 46.28 | 21:00
Amnura | 49 | 05:00 | Daudkandi | 116 | 00:00 | Khulshi | 168 | 14:00 | PHP | 11 | 10:00 | Sunamganj | 38 | 22:00
Ashuganj | 39 | 02:00 | Dhaka | 32 | 11:00 | Kishoreganj | 118 | 21:00 | Pabna | 89 | 00:00 | Sylhet | 136 | 00:00
BSRM | 153 | 02:00 | Dhamrai | 94 | 12:00 | Kodda | 299 | 09:00 | Palashbari | 108 | 23:00 | TK | 28.5 | 19:00
Bagerhat | 71 | 06:00 | Dhanmondi | 138 | 16:00 | Kulaura | 36 | 00:00 | Panchagarh | 46 | 08:00 | Tangail | 195 | 22:00
Bakulia | 106 | 19:30 | Dohazari | 96 | 20:00 | Kurigram | 53 | 19:00 | Patuakhali | 133 | 22:00 | Thakurgaon | 66 | 22:00
Banani | 49 | 14:00 | Faridpur | 120 | 18:30 | Kushtia | 128 | 18:30 | Payra | 1.02 | 16:00 | Tongi | 116 | 19:30
Bangabhaban | 8 | 10:00 | Fatullah | 67 | 16:00 | Lalbag | 98 | 13:00 | Purbachal | 20 | 21:00 | Ullon | 40 | 21:00
Barapukuria | 48 | 03:00 | Fenchuganj | 38 | 05:00 | Lalmonirhat | 42 | 19:00 | Purbasadipur | 96 | 05:00 | Uttara | 93 | 21:00
Barguna | 20 | 00:00 | Feni | 83 | 00:00 | Madanganj | 64 | 13:00 | Rahim | 26 | 08:00 | UttaraNew | 18 | 00:00
Barishal | 106 | 23:00 | GPH | 91 | 20:00 | Madaripur | 110 | 00:00 | Rajbari | 60 | 19:30 | Zigatola | 57 | 19:00
Barishal-230 | 78 | 21:00 | Ghorashal | 46 | 01:00 | Madartek | 89 | 23:00 | Rajendrapur | 92 | 05:00
Baroaulia | 72 | 19:00 | Goalpara | 26 | 19:00 | Madunaghat | 69 | 20:00 | Rajshahi | 132 | 22:00
Baroirhat | 64 | 21:00 | Gollamari | 52 | 19:00 | Magura | 42 | 04:00 | Rajshahi-230 | 26 | 02:00
Bashundhara | 164 | 19:00 | Gopalganj | 104 | 23:00 | Mahasthangarh | 64 | 04:00 | Ramganj | 88 | 19:00
BashundharaCement | 2 | 00:00 | Gulshan | 100 | 17:00 | Manikganj | 83 | 21:00 | Rampur | 16 | 00:00
Beanibazar | 54 | 03:00 | Halishahar | 88 | 09:00 | Maniknagar | 54 | 23:00 | Rangamati | 14 | 19:00
Benapole | 48 | 06:00 | HaripurSBU | 137 | 13:00 | Matarbari | 43 | 19:30 | Rangpur | 105 | 08:00
Bhaluka | 100 | 09:00 | Hasnabad | 87 | 23:00 | Matuail | 58 | 12:00 | Ruppur | 5 | 09:00
Bhandaria | 50 | 22:00 | Hathazari | 105 | 19:30 | Millgate | 58 | 09:00 | SSM | 3 | 05:00
Bhangura | 30 | 02:00 | Ishurdi | 68 | 19:00 | Mirpur | 131 | 19:00 | Saidpur | 93 | 08:00
Bheramara(GK) | 59 | 01:00 | Jaldhaka | 48 | 19:30 | Mirsorai | N/A | N/A | Satkhira | 95 | 06:00
Bhulta | 505 | 06:00 | Jamalpur | 116 | 19:00 | Mithapukur | 32 | 23:00 | Satmasjid | 101 | 19:00
Bog-Sherpur | 52 | 06:00 | Jashore | 120 | 21:00 | Modern | 0 | 00:00 | Savar | 156 | 09:00
Bogura | 146 | 07:00 | Jhenaidah | 105 | 07:00 | Mogbazar | 116 | 13:00 | Shahjadpur | 85 | 22:00
Borhanuddin | 44 | 23:00 | Joydebpur | 188 | 22:00 | Mongla | 32 | 14:00 | Shahjibazar | 95 | 00:00
Brahmanbaria | 136 | 04:00 | Joypurhat | 56 | 20:00 | Motijheel | 33 | 19:00 | Shahmirpur | 46.5 | 18:30
Cantonment | 151 | 19:00 | Juldah | 31 | 20:00 | Munshiganj | 88 | 19:00 | Shariatpur | 78 | 22:00
Chandpur | 55 | 00:00 | KSRM | 33.7 | 22:00 | Mymensingh | 203 | 18:00 | Sherpur | 100 | 19:00
Chandraghona | 32 | 19:00 | Kabirpur | 273 | 20:00 | Naogaon | 108 | 05:00 | Shikalbaha | 28 | 19:00
Chapai | 59 | 05:00 | Kachua | 62 | 03:00 | Narail | 39 | 05:00 | Shikalbaha-230 | N/A | N/A
Charsaidpur | 44 | 13:00 | Kallyanpur | 96 | 00:00 | Narinda | 43 | 14:00 | Shitalakhya | 114 | 12:00
Chauddagram | 49 | 01:00 | Kalurghat | 32 | 10:00 | Narshingdi | 165 | 19:00 | Sholosohor | N/A | N/A
Chhatak | 33 | 00:00 | Kamrangirchar | 60 | 11:00 | Natore | 109 | 00:00 | Shyampur | 144 | 01:00
Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
(1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2022-08-06 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Bhulta | 384 | 20:00 | 369 | 10:00 | Kaliakoir | 389 | 19:30 | 370 | 09:00
| Bibiana | 405 | 21:00 | 394 | 10:00 | Payra | 414 | 10:00 | 409 | 00:00
| BIPTC | 401 | 06:00 | 394 | 00:00 | Rahanpur_I
| Gopalganj_I | 409 | 11:00 | 394 | 07:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 220 | 06:00 | 208 | 10:00 | Hasnabad | 220 | 20:00 | 210 | 09:00
| AKSML | 233 | 19:00 | 219 | 12:00 | Hathazari | 235 | 19:00 | 223 | 12:00
| Aminbazar | 220 | 03:00 | 209 | 17:00 | Ishurdi | 235 | 20:00 | 227 | 05:00
| Ashuganj | 237 | 08:00 | 229 | 10:00 | Jhenaidah | 229 | 20:00 | 217 | 07:00
| Baghabari | 234 | 19:00 | 229 | 03:00 | Kaliakoir | 226 | 02:00 | 213 | 15:00
| Barapukuria | 224 | 11:00 | 210 | 05:00 | Keranigonj | 218 | 06:00 | 207 | 10:00
| Barishal | 245 | 11:00 | 238 | 01:00 | Khulna(S) | 235 | 20:00 | 222 | 07:00
| Bheramara | 232 | 20:00 | 222 | 06:00 | Maniknagar | 223 | 20:00 | 213 | 10:00
| Bhulta | 226 | 06:00 | 217 | 10:00 | Meghnaghat | 226 | 06:00 | 219 | 10:00
| Bibiana | 237 | 02:00 | 230 | 11:00 | Mirsorai
| BIPTC | 235 | 20:00 | 224 | 05:00 | Rajshahi | 234 | 19:00 | 225 | 05:00
| Bogura | 229 | 19:00 | 218 | 05:00 | Rampur
| Borhanuddin | 248 | 10:00 | 242 | 01:00 | Rampura | 224 | 04:00 | 215 | 10:00
| BSRM | 231 | 21:00 | 219 | 12:00 | Shikalbaha | 234 | 20:00 | 223 | 09:00
| Cumilla(N) | 228 | 21:00 | 220 | 10:00 | Shyampur | 219 | 06:00 | 209 | 10:00
| Fenchuganj | 242 | 21:00 | 236 | 12:00 | Siddhirganj | 225 | 06:00 | 213 | 23:00
| Ghorashal |  |  |  |  | Sirajgonj | 232 | 20:00 | 227 | 04:00
| GPH | 233 | 19:00 | 220 | 12:00 | Tongi | 226 | 05:00 | 215 | 08:00
| Haripur | 223 | 20:00 | 214 | 12:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 136 | 20:00 | 129 | 10:00 | Lalbag | 136 | 06:00 | 127 | 10:00
| Agargaon | 136 | 06:00 | 128 | 10:00 | Lalmonirhat | 133 | 11:00 | 123 | 06:00
| Agrabad | 137 | 00:00 | 129 | 12:00 | Madanganj | 132 | 20:00 | 125 | 10:00
| AKS | 137 | 00:00 | 126 | 17:00 | Madaripur | 137 | 10:00 | 132 | 00:00
| Aminbazar | 132 | 03:00 | 128 | 15:00 | Madartek | 136 | 06:00 | 128 | 10:00
| Amnura | 134 | 11:00 | 126 | 05:00 | Madunaghat | 140 | 19:00 | 130 | 12:00
| Ashuganj | 138 | 20:00 | 134 | 09:00 | Magura | 139 | 20:00 | 132 | 05:00
| Bagerhat | 137 | 20:00 | 122 | 05:00 | Mahasthangarh | 136 | 10:00 | 125 | 04:00
| Bakulia | 140 | 19:00 | 129 | 12:00 | Manikganj | 134 | 00:00 | 128 | 09:00
| Banani | 133 | 08:00 | 124 | 12:00 | Maniknagar | 134 | 22:00 | 125 | 10:00
| Bangabhaban | 133 | 22:00 | 125 | 12:00 | Matarbari | 134 | 19:00 | 117 | 20:00
| Barapukuria | 137 | 11:00 | 127 | 05:00 | Matuail | 131 | 03:00 | 125 | 10:00
| Barguna | 135 | 08:00 | 1 | 09:00 | Millgate | 132 | 07:00 | 124 | 17:00
| Barishal | 139 | 11:00 | 128 | 19:00 | Mirpur | 133 | 21:00 | 123 | 09:00
| Barishal-230 | 140 | 11:00 | 134 | 00:00 | Mithapukur | 136 | 11:00 | 120 | 04:00
| Baroaulia | 140 | 19:00 | 128 | 12:00 | Modern | 140 | 19:00 | 129 | 17:00
| Baroirhat | 135 | 19:00 | 127 | 06:00 | Mogbazar | 137 | 07:00 | 130 | 10:00
| Bashundhara | 133 | 21:00 | 124 | 11:00 | Mongla | 136 | 20:00 | 119 | 06:00
| BashundharaCement | 137 | 23:00 | 125 | 10:00 | Motijheel | 131 | 07:00 | 125 | 12:00
| Beanibazar | 132 | 08:00 | 129 | 01:00 | Munshiganj | 133 | 20:00 | 125 | 10:00
| Benapole | 136 | 11:00 | 127 | 06:00 | Mymensingh | 129 | 06:00 | 117 | 17:00
| Bhaluka | 128 | 02:00 | 117 | 12:00 | Naogaon | 136 | 11:00 | 124 | 04:00
| Bhandaria | 137 | 11:00 | 128 | 00:00 | Narail | 139 | 20:00 | 130 | 05:00
| Bhangura | 138 | 18:30 | 134 | 01:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bheramara | 137 | 20:00 | 133 | 04:00 | Narshingdi | 136 | 05:00 | 123 | 10:00
| Bheramara(GK) | 138 | 20:00 | 133 | 05:00 | Natore | 136 | 19:00 | 128 | 05:00
| Bhulta | 125 | 19:30 | 120 | 09:00 | Nawabganj | 135 | 06:00 | 127 | 12:00
| Bog-Sherpur | 137 | 19:00 | 129 | 05:00 | Netrakona | 128 | 00:00 | 117 | 12:00
| Bogura | 137 | 10:00 | 129 | 05:00 | New | 133 | 05:00 | 125 | 10:00
| Bogura-230 | 139 | 19:00 | 129 | 05:00 | Niamatpur | 134 | 18:00 | 119 | 05:00
| Brahmanbaria | 134 | 20:00 | 129 | 09:00 | Noapara | 138 | 20:00 | 127 | 05:00
| Cantonment | 135 | 06:00 | 126 | 10:00 | Pabna | 136 | 20:00 | 130 | 05:00
| Chandpur | 136 | 17:00 | 131 | 01:00 | Palashbari | 134 | 10:00 | 126 | 07:00
| Chandraghona | 138 | 00:00 | 131 | 17:00 | Panchagarh | 135 | 00:00 | 126 | 02:00
| Chapai | 134 | 19:00 | 125 | 05:00 | Patuakhali | 136 | 18:00 | 131 | 02:00
| Charsaidpur | 132 | 04:00 | 125 | 10:00 | Payra | 138 | 10:00 | 135 | 00:00
| Chauddagram | 135 | 18:00 | 127 | 05:00 | PHP | 136 | 19:00 | 127 | 04:00
| Chhatak | 132 | 04:00 | 129 | 18:30 | Postogola | 136 | 06:00 | 129 | 11:00
| Chowmuhani | 135 | 19:00 | 125 | 02:00 | Purbachal | 132 | 06:00 | 123 | 12:00
| Chuadanga | 137 | 20:00 | 125 | 06:00 | Purbasadipur | 133 | 01:00 | 119 | 05:00
| Coxsbazar | 131 | 19:00 | 114 | 20:00 | Rahim | 132 | 07:00 | 127 | 12:00
| Cumilla(N) | 135 | 20:00 | 129 | 12:00 | Rajbari | 135 | 20:00 | 120 | 07:00
| Cumilla(S) | 135 | 20:00 | 124 | 16:00 | Rajendrapur | 136 | 20:00 | 127 | 16:00
| Daudkandi | 132 | 20:00 | 125 | 10:00 | Rajshahi | 135 | 19:00 | 128 | 04:00
| Dhaka | 137 | 20:00 | 130 | 10:00 | Rajshahi-230 | 135 | 19:00 | 128 | 04:00
| Dhamrai | 131 | 08:00 | 122 | 12:00 | Ramganj | 134 | 18:00 | 128 | 12:00
| Dhanmondi | 131 | 05:00 | 124.7 | 10:00 | Rampur | 137 | 00:00 | 131 | 13:00
| Dohazari | 141 | 19:00 | 127 | 17:00 | Rampura | 136 | 07:00 | 129 | 10:00
| Faridpur | 135 | 19:30 | 13 | 01:00 | Rangamati | 138 | 19:00 | 130 | 12:00
| Fatullah | 134 | 06:00 | 127 | 10:00 | Rangpur | 134 | 11:00 | 119 | 05:00
| Fenchuganj | 138 | 06:00 | 133 | 03:00 | Ruppur | 136 | 00:00 | 133 | 05:00
| Feni | 137 | 19:00 | 128 | 01:00 | Saidpur | 134 | 10:00 | 124 | 06:00
| Ghorashal | 137 | 00:00 | 135 | 01:00 | Satkhira | 136 | 20:00 | 122 | 06:00
| Goalpara | 139 | 20:00 | 127 | 05:00 | Satmasjid | 136 | 06:00 | 128 | 10:00
| Gollamari | 138 | 20:00 | 127 | 05:00 | Savar | 133 | 20:00 | 122 | 10:00
| Gopalganj | 139 | 20:00 | 132 | 06:00 | Shahjadpur | 140 | 23:00 | 135 | 06:00
| Gopalganj_I | 138 | 11:00 | 133 | 07:00 | Shahjibazar | 136 | 20:00 | 131 | 17:00
| Gulshan | 136 | 06:00 | 129 | 10:00 | Shahmirpur | 137 | 00:00 | 130 | 12:00
| Halishahar | 138 | 00:00 | 129 | 12:00 | Shariatpur | 135 | 09:00 | 129 | 00:00
| Haripur | 132 | 07:00 | 127 | 12:00 | Sherpur | 135 | 19:30 | 117 | 15:00
| HaripurSBU | 138 | 15:00 | 127 | 10:00 | Shikalbaha | 139 | 00:00 | 132 | 12:00
| Hasnabad | 136 | 20:00 | 130 | 10:00 | Shikalbaha-230 | 138 | 20:00 | 132 | 09:00
| Hathazari | 139 | 19:00 | 132 | 12:00 | Shitalakhya | 135 | 20:00 | 126 | 10:00
| Ishurdi | 137 | 20:00 | 132 | 05:00 | Sholosohor | N/A | N/A | N/A | N/A
| Jaldhaka | 134 | 11:00 | 119 | 05:00 | Shyampur | 133 | 20:00 | 125 | 10:00
| Jamalpur | 135 | 19:00 | 118 | 17:00 | Shyampur-230 | 134 | 20:00 | 127 | 10:00
| Jashore | 138 | 20:00 | 127 | 06:00 | Siddhirganj | 132 | 21:00 | 126 | 10:00
| Jhenaidah | 141 | 20:00 | 131 | 07:00 | Sirajganj | 137 | 19:00 | 131 | 04:00
| Jhenaidah-230 | 140 | 19:30 | 131 | 07:00 | Sonargaon | 132 | 20:00 | 124 | 11:00
| Joydebpur | 140 | 21:00 | 133 | 09:00 | Sreemongol | 137 | 07:00 | 134 | 10:00
| Joypurhat | 136 | 11:00 | 125 | 06:00 | Srinagar | 135 | 05:00 | 126 | 10:00
| Juldah | 140 | 19:00 | 130 | 17:00 | SSM | 140 | 21:00 | 134 | 14:00
| Kabirpur | 138 | 21:00 | 120 | 10:00 | Sunamganj | 131 | 07:00 | 128 | 18:30
| Kachua | 136 | 20:00 | 129 | 05:00 | Sylhet | 134 | 08:00 | 132 | 00:00
| Kaliakoir | 138 | 04:00 | 133 | 09:00 | Tangail | 135 | 19:30 | 128 | 12:00
| Kallyanpur | 133 | 20:00 | 123 | 10:00 | Thakurgaon | 134 | 15:00 | 119 | 03:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2022-08-06
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 996 | 6805 | 4523 | 11328 |  |  |  | QF-LDC-11
0:30 | 818 | 6927.5 | 4436 | 11363.5 | Date: | 2022-08-06
1:00 | 640 | 7050 | 4349 | 11399
1:30 | 621 | 6988 | 4322.5 | 11310.5
2:00 | 602 | 6926 | 4296 | 11222
2:30 | 584 | 6951 | 4288.5 | 11239.5 | [5 empty] | Gen. at Eve. Peak | 12132 | 12132 MW (21:00 )
3:00 | 566 | 6976 | 4281 | 11257 | [6 empty] | 21:00
3:30 | 547 | 6942.5 | 4259.5 | 11202 | [5 empty] | Gen. at Day Peak | 10629 | 10629 MW (09:00 )
4:00 | 528 | 6909 | 4238 | 11147 | [6 empty] | 9:00
4:30 | 491 | 6897.5 | 4226.5 | 11124 | [5 empty] | Highest Generation | 12170
5:00 | 454 | 6886 | 4215 | 11101 | [6 empty] | 22:00
5:30 | 454 | 6785 | 4135 | 10920
6:00 | 454 | 6684 | 4055 | 10739
6:30 | 486 | 6673 | 4052 | 10725
7:00 | 518 | 6662 | 4049 | 10711
7:30 | 575 | 6602 | 4029.5 | 10631.5
8:00 | 632 | 6542 | 4010 | 10552
8:30 | 771 | 6586.5 | 4004 | 10590.5
9:00 | 910 | 6631 | 3998 | 10629
9:30 | 996 | 6589.5 | 3946.5 | 10536
10:00 | 1082 | 6548 | 3895 | 10443
10:30 | 1030 | 6588 | 3886.5 | 10474.5
11:00 | 978 | 6628 | 3878 | 10506
11:30 | 961 | 6570 | 3890.5 | 10460.5
12:00 | 944 | 6512 | 3903 | 10415
12:30 | 924 | 6522 | 3900 | 10422
13:00 | 904 | 6532 | 3897 | 10429
13:30 | 883 | 6525 | 3906 | 10431
14:00 | 862 | 6518 | 3915 | 10433
14:30 | 963 | 6510 | 3953 | 10463
15:00 | 1064 | 6502 | 3991 | 10493
15:30 | 1044 | 6531.5 | 4038 | 10569.5
16:00 | 1024 | 6561 | 4085 | 10646
16:30 | 1012 | 6660 | 4098 | 10758
17:00 | 1000 | 6759 | 4111 | 10870
17:30 | 978 | 6805 | 4122 | 10927
18:00 | 956 | 6851 | 4133 | 10984
18:30 | 875 | 7089.5 | 4177.5 | 11267
19:00 | 794 | 7328 | 4222 | 11550
19:30 | 754 | 7533 | 4445 | 11978
20:00 | 772 | 7453 | 4515 | 11968 |  |  |  | Executive Engineer
20:30 | 754 | 7511.5 | 4538.5 | 12050 |  |  |  | Network Operation Division
21:00 | 736 | 7570 | 4562 | 12132
21:30 | 799 | 7534 | 4617 | 12151
22:00 | 862 | 7498 | 4672 | 12170 |  |  |  |  | Page 6 of 7
22:30 | 902 | 7480.5 | 4676.5 | 12157
23:00 | 942 | 7463 | 4681 | 12144
23:30 | 969 | 7134 | 4602 | 11736
24:00 | 996 | 6805 | 4523 | 11328
12132 MW (21:00 )
10629 MW (09:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2022-08-06 |  | Energy |  | 269553940
[13 empty] | 2022-08-06 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 3366 | 913 | 2003 | 0 | 2637 | 1270 | 111 | 367 | 712 | 166 | 0 | 1633.0309
0:30 | 3629.5 | 913.5 | 1972 | 0 | 2550 | 1275 | 112 | 269.5 | 669.5 | 167 | 0 | 1369.9212 | Date: | 2022-08-06
1:00 | 3893 | 914 | 1941 | 0 | 2463 | 1280 | 113 | 172 | 627 | 168 | 0 | 1106.8116
1:30 | 3885 | 913.5 | 1951 | 0 | 2392 | 1275 | 113 | 161 | 612 | 169 | 0 | 1142.2922 | [8 empty] | Total Energy | 269.5539 | Total Energy Gen 269.554 MKWHr Energy Not Served 23.562 MKWHr Energy Requirement 293.116 MKWHr
2:00 | 3877 | 913 | 1961 | 0 | 2321 | 1270 | 113 | 150 | 597 | 170 | 0 | 1177.7729 | [8 empty] | Energy not Served | 23.5616
2:30 | 3886.5 | 913.5 | 1968 | 0 | 2317.5 | 1270 | 113.5 | 150 | 601.5 | 169 | 0 | 1138.6059 | [8 empty] | Energy Requirement | 293.1156
3:00 | 3896 | 914 | 1975 | 0 | 2314 | 1270 | 114 | 150 | 606 | 168 | 0 | 1099.439
3:30 | 3897 | 914 | 1979 | 0 | 2298 | 1260 | 114 | 140 | 575 | 165 | 0 | 1104.0469 | [6 empty] | Shortage
4:00 | 3898 | 914 | 1983 | 0 | 2282 | 1250 | 114 | 130 | 544 | 162 | 0 | 1108.6547
4:30 | 3903 | 914 | 1975.5 | 0 | 2278 | 1250 | 114 | 130 | 541.5 | 148 | 0 | 922.4966
5:00 | 3908 | 914 | 1968 | 0 | 2274 | 1250 | 114 | 130 | 539 | 134 | 0 | 736.3384
5:30 | 3877 | 913.5 | 1963 | 0 | 2212 | 1220 | 113.5 | 130 | 491 | 129 | 1 | 626.671
6:00 | 3846 | 913 | 1958 | 0 | 2150 | 1190 | 113 | 130 | 443 | 124 | 2 | 517.0036
6:30 | 3850 | 913.5 | 1940.5 | 0 | 2162 | 1190 | 112.5 | 130 | 426.5 | 122 | 8 | 437.7481 |  |  |  |  | Coal
7:00 | 3854 | 914 | 1923 | 0 | 2174 | 1190 | 112 | 130 | 410 | 120 | 14 | 358.4927
7:30 | 3835.5 | 913.5 | 1887 | 0 | 2155 | 1175 | 111.5 | 130 | 414 | 122 | 18 | 385.6791 |  |  |  | Oil |  |  |  | ,
8:00 | 3817 | 913 | 1851 | 0 | 2136 | 1160 | 111 | 130 | 418 | 124 | 22 | 412.8656
8:30 | 3828.5 | 913 | 1872.5 | 0 | 2138.5 | 1145 | 111 | 135 | 423 | 117 | 42 | 515.6212
9:00 | 3840 | 913 | 1894 | 0 | 2141 | 1130 | 111 | 140 | 428 | 110 | 62 | 618.3768
9:30 | 3794 | 913 | 1854 | 0 | 2108 | 1120 | 110 | 135 | 423 | 129 | 85 | 750.1621
10:00 | 3748 | 913 | 1814 | 0 | 2075 | 1110 | 109 | 130 | 418 | 148 | 108 | 881.9473
10:30 | 3785.5 | 913.5 | 1806 | 0 | 2066 | 1095 | 109.5 | 133.5 | 425.5 | 149 | 124.5 | 945.0752
11:00 | 3823 | 914 | 1798 | 0 | 2057 | 1080 | 110 | 137 | 433 | 150 | 141 | 1008.2031
11:30 | 3780 | 914 | 1809 | 0 | 2015.5 | 1085 | 110 | 164 | 459.5 | 152 | 135.5 | 1142.2922
12:00 | 3737 | 914 | 1820 | 0 | 1974 | 1090 | 110 | 191 | 486 | 154 | 130 | 1276.3814
12:30 | 3728.5 | 913.5 | 1820 | 0 | 1970 | 1110 | 111 | 201.5 | 499 | 154 | 116 | 1223.8516
13:00 | 3720 | 913 | 1820 | 0 | 1966 | 1130 | 112 | 212 | 512 | 154 | 102 | 1171.3218
13:30 | 3720 | 913 | 1820 | 0 | 1966 | 1130 | 112 | 212 | 512 | 154 | 102 | 1171.3218
14:00 | 3720 | 913 | 1820 | 0 | 1966 | 1130 | 112 | 212 | 512 | 154 | 102 | 1171.3218
14:30 | 3716 | 913 | 1816.5 | 0 | 1975 | 1140 | 112.5 | 210.5 | 526.5 | 150 | 111.5 | 1104.5076
15:00 | 3712 | 913 | 1813 | 0 | 1984 | 1150 | 113 | 209 | 541 | 146 | 121 | 1037.6935
15:30 | 3707 | 913 | 1800 | 0 | 2049.5 | 1170 | 113.5 | 212 | 554 | 158 | 102 | 921.1142
16:00 | 3702 | 913 | 1787 | 0 | 2115 | 1190 | 114 | 215 | 567 | 170 | 83 | 804.535
16:30 | 3554 | 913 | 1785 | 0 | 2312 | 1190 | 114 | 184 | 572 | 169 | 70 | 632.2004
17:00 | 3554 | 913 | 1783 | 0 | 2509 | 1190 | 114 | 153 | 577 | 168 | 57 | 459.8659
17:30 | 3462.5 | 913.5 | 1803.5 | 0 | 2666 | 1185 | 114 | 144 | 583 | 160 | 34.5 | 352.5024
18:00 | 3371 | 914 | 1824 | 0 | 2823 | 1180 | 114 | 135 | 589 | 152 | 12 | 245.139
18:30 | 3405.5 | 913.5 | 1867 | 0 | 3025.5 | 1170 | 97.5 | 145 | 622 | 150 | 6 | 652.4751
19:00 | 3440 | 913 | 1910 | 0 | 3228 | 1160 | 81 | 155 | 655 | 148 | 0 | 1059.8112
19:30 | 3446 | 913 | 1911 | 0 | 3474 | 1260 | 81 | 212 | 726 | 152 | 0 | 1310.4796
20:00 | 3403 | 913 | 1901 | 0 | 3477 | 1250 | 81 | 222 | 776 | 152 | 0 | 1550.0891
20:30 | 3423.5 | 913.5 | 1912 | 0 | 3492 | 1255 | 96 | 236.5 | 775 | 158 | 0 | 1543.6381
21:00 | 3444 | 914 | 1923 | 0 | 3507 | 1260 | 111 | 251 | 774 | 164 | 0 | 1537.1871
21:30 | 3409.5 | 913.5 | 1924.5 | 0 | 3511 | 1270 | 111 | 293.5 | 770 | 165 | 0 | 1473.5984
22:00 | 3375 | 913 | 1926 | 0 | 3515 | 1280 | 111 | 336 | 766 | 166 | 0 | 1410.0098
22:30 | 3435.5 | 913 | 1947.5 | 0 | 3414.5 | 1285 | 111 | 336.5 | 766.5 | 165 | 0 | 1375.9115
23:00 | 3496 | 913 | 1969 | 0 | 3314 | 1290 | 111 | 337 | 767 | 164 | 0 | 1341.8132
23:30 | 3431 | 913 | 1986 | 0 | 2975.5 | 1280 | 111 | 352 | 739.5 | 165 | 0 | 1487.4221 | Max Temp. in Dhaka |  | 24.7° C | 34.0° C
24:00 | 3366 | 913 | 2003 | 0 | 2637 | 1270 | 111 | 367 | 712 | 166 | 0 | 1633.0309
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 269.554 MKWHr Energy Not Served 23.562 MKWHr Energy Requirement 293.116 MKWHr
Note on W13: Author:

## Generation
g | 2022-08-06
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 78 | 78 | 79 | 79 | 79 | 78 | 77 | 76 | 76 | 74 | 75 | 75 | 77 | 78 | 78 | 79 | 79 | 79 |  | 46 | 46 | 46 | 76 | 76 | 76 | 76 | 1755490
2 | Karnaphuli Hydro PP Unit-4 & 5 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 844000
3 | Chattogram TPP-1 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 95 | 95 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2400000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 0 | [8 empty] | 433251
| Teknaf 20MW PP (Solartech) | [5 empty] | 1 | 5 |  |  | 19 | 20 | 18 | 7 | 15 | 14 | 6 | 3 | 1 |  | 0 | [6 empty] | 108540
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 51 | 51 | 51 | 17 | 17 | 17 | 17 | 17 | 17 | 42 | 51 | 49 | 49 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 976181
12 | Hathazari 100 MW peaking PP | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 33 | 33 | 32 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 26 | 18 | 614736
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 87 | 87 | 87 | 87 | 87 | 87 | 82 | 68 | 68 | 68 | 68 | 68 | 82 | 87 | 87 | 87 | 87 | 87 |  | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 2021482
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP | 32 | 31 | 40 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 31 | 32 | 32 | 32 | 39 | 39 | 39 | 39 |  | 39 | 40 | 40 | 40 | 40 | 40 | 40 | 835272
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 95 | 97 | 97 | 97 | 96 | 97 | 98 | 95 | 97 | 97 | 93 | 94 | 94 | 95 | 94 | 92 | 92 | 91 |  | 94 | 97 | 91 | 95 | 57 | 95 | 0 | 2356000
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 200 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 193 | 195 | 197 | 247 | 262 |  | 261 | 262 | 260 | 260 | 243 | 245 | 243 | 5151162
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 217454
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4347000
24
25 | Ghorasal 365 MW CCPP Unit-7 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 140 | 0 | [7 empty] | 0 | 5116509
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 37 | 38 | 34 | 34 | 36 | 36 | 36 | 36 | 36 | 36 | 36 |  | 39 | 39 | 39 | 37 | 34 | 37 | 37 | 859536
33 | Ashuganj 225 MW CCPP | 206 | 207 | 207 | 206 | 207 | 209 | 210 | 211 | 208 | 208 | 211 | 203 | 205 | 205 | 203 | 200 | 191 | 200 |  | 187 | 190 | 202 | 202 | 208 | 205 | 192 | 4934000
34 | Ashuganj 450 MW CCPP(South) | 335 | 330 | 335 | 335 | 340 | 310 | 310 | 305 | 320 | 305 | 330 | 330 | 330 | 325 | 315 | 305 | 330 | 310 |  | 330 | 325 | 305 | 305 | 310 | 335 | 310 | 7815000
| Ashuganj 450 MW CCPP(North) | 350 | 330 | 350 | 350 | 355 | 315 | 310 | 310 | 325 | 295 | 365 | 345 | 345 | 330 | 320 | 320 | 335 | 280 |  | 340 | 300 | 280 | 280 | 280 | 320 | 300 | 8040600
Ashuganj 420 MW CCPP(East)
35 | Ashuganj 55 MW PP (Precision) | 55 | 54 | 55 | 55 | 55 | 56 | 57 | 56 | 53 | 52 | 51 | 52 | 52 | 48 | 50 | 51 | 54 | 54 |  | 54 | 54 | 54 | 55 | 55 | 54 | 55 | 1289740
36 | Chandpur 150 MW CCPP | 142 | 142 | 144 | 143 | 142 | 142 | 143 | 142 | 142 | 142 | 142 | 143 | 142 | 142 | 142 | 142 | 141 | 137 |  | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 3351740
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 408 | 406 | 407 | 405 | 409 | 409 | 411 | 410 | 410 | 410 | 408 | 405 | 399 | 401 | 397 | 397 | 405 | 396 |  | 396 | 397 | 395 | 394 | 394 | 400 | 404 | 9797630
40 | Meghnaghat 450 MW CCPP(MPL) | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 |  | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 5036500
41 | Haripur 360MW CCPP(HPL) | 333 | 332 | 332 | 333 | 333 | 332 | 303 | 303 | 343 | 337 | 327 | 328 | 322 | 321 | 318 | 316 | 317 | 316 |  | 281 | 266 | 267 | 267 | 267 | 287 | 311 | 7488000
42 | RPCL 210MW CCPP | 100 | 101 | 101 | 102 | 100 | 103 | 104 | 104 | 103 | 94 | 80 | 66 | 66 | 66 | 66 | 66 | 67 | 67 |  | 78 | 94 | 95 | 101 | 101 | 102 | 101 | 2053440
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 0 | 1 | 4 | 17 | 23 | 22 | 47 | 43 | 36 | 20 | 7 | 1 |  | 0 | [6 empty] | 236380
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 44 | 43 | 43 | 43 | 44 | 43 | 1024000
45 | Fenchugonj CCPP Phase-2 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 |  | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 974760
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 60 | 60 | 60 | 61 | 61 | 61 | 60 | 65 | 61 | 60 | 61 | 59 | 60 | 59 | 58 | 58 | 57 | 58 |  | 58 | 61 | 63 | 63 | 63 | 62 | 61 | 1437312
48 | Shahjibazar 86MW PP (Shahjibazar) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 70 | 78 | 78 | 81 | 81 | 81 | 81 | 666240
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 221 | 221 | 221 | 221 | 221 | 221 | 221 | 221 | 221 | 221 | 220 | 221 | 221 | 221 | 221 | 220 | 220 | 220 |  | 220 | 222 | 222 | 221 | 220 | 220 | 221 | 5375710
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL) | 32 | 30 | 30 | 31 | 30 | 31 | 31 | 31 | 31 | 29 | 29 | 29 | 29 | 29 | 31 | 31 | 31 | 31 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 715820
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 9 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 239400
54 | Hobiganj 11MW PP Cofidence-E | [19 empty] | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 57200
55 | Fenchugonj 51 MW PP (Barakatullah) | 31 | 31 | 30 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 33 | 33 | 31 | 31 | 31 | 33 | 33 |  | 50 | 50 | 50 | 50 | 50 | 50 | 53 | 852000
56 | Shahjahanulla 25 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 16 | 10 | 12 | 16 | 198696
57 | Bibiana-II 341 MW CCPP (Summit) | 305 | 310 | 320 | 320 | 315 | 305 | 300 | 280 | 305 | 275 | 280 | 300 | 310 | 305 | 315 | 300 | 270 | 300 |  | 320 | 310 | 280 | 290 | 280 | 310 | 315 | 7437500
Bibiyana South 400 MW
58 | Nababganj 55 MW PP (Southern power ) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 954209
59 | Tangail Palli Power Gen 22 MW | [25 empty] | 0 | 0
60 | Barabkunda 22 MW PP (Regent) | 17 | 17 | 17 | 17 | 17 | 14 | 14 | 17 | 11 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 353184
61 | Narshingdi 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 0 | 0 | 19 | 0 | 0 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 371160
62 | Tangail 22 MW PP (Doreen) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 0 |  | 0 | 462276
63 | Impoprt (Tripura) | 168 | 170 | 168 | 162 | 134 | 124 | 120 | 124 | 110 | 148 | 150 | 154 | 154 | 158 | 146 | 170 | 168 | 152 |  | 148 | 152 | 152 | 164 | 166 | 164 | 166 | 3682560
64 | Malancha, Ctg. EPZ (United) | 42 | 42 | 42 | 42 | 42 | 40 | 39 | 13 | 7 | 2 | 2 | 2 | 4 | 4 | 4 | 4 | 14 | 20 |  | 22 | 20 | 27 | 32 | 35 | 38 | 38 | 596160
65 | Feni 22MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 16 | 19 | 21 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 500112
66 | Feni 11 MW PP (Doreen) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 11 | 11 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 10 | 10 | 234900
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 31 | 33 | 33 | 33 | 31 | 25 | 25 | 25 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 782600
68 | Cumilla 25 MW PP (Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 16 | 17 | 17 | 17 | 17 | 17 | 20 | 20 | 17 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 488530
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 25 | 26 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 28 | 27 | 25 | 25 | 19 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 26 | 27 | 565200
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 0 |  | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 589300
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 16 | 17 | 25 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 28 | 28 | 16 | 33 | 33 | 33 | 33 | 703700
73 | Ghorashal 108MW PP (Regent) | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 88 | 88 | 82 | 85 | 82 | 85 | 81 | 84 | 80 | 85 | 92 |  | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 2066863
| Feni Lanka Power | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 114 | 114 |  | 114 | 114 | 114 | 114 | 114 | 114 | 17 | 1079580
| Chowmuhani 113 MW | 90 | 84 | 84 | 85 | 77 | 76 | 77 | 78 | 78 | 77 | 77 | 70 | 67 | 74 | 74 | 76 | 94 | 102 |  | 102 | 113 | 109 | 113 | 112 | 113 | 57 | 2056320
| Manikgonj 162MW PP(MPGL) | 162 | 162 | 162 | 162 | 162 | 54 | 54 | 54 | 54 | 50 | 54 | 46 | 50 | 42 | 46 | 71 | 162 | 162 |  | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 2724480
77 | Siddhirganj 100 PP(Dutch Bangla) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 20 | 50 | 50 | 50 | 50 | 50 | 15 | 378240
78 | Gazipur 52 MW PP | 50 | 50 | 50 | 50 | 50 | 51 | 51 | 51 | 51 | 51 | 51 | 42 | 42 | 50 | 42 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1167902
79 | Kodda 150MW PP | 49 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 48 | 48 | 110 | 125 |  | 125 | 125 | 125 | 125 | 125 | 125 | 84 | 1709280
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 15 | 43 | 43 | 43 | 43 | 43 | 43 | 391325
| Gazipur 100 MW PP | 92 | 105 | 105 | 105 | 105 | 105 | 105 | 88 | 88 | 88 | 88 | 88 | 88 | 70 | 70 | 88 | 88 | 88 |  | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 2204400
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 2 | 3 | 3 | 2 | 5 | 4 | 1 | 2 | 2 | 2 | 0 | [8 empty] | 28080
| Jodiac Power | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 17 | 17 | 17 | 17 | 17 | 17 | 21 | 36 | 36 |  | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 777680
| Karnaphuli Power Ltd. | 54 | 53 | 52 | 53 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1313085
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL) | 7 | 8 | 7 | 8 | 7 | 8 | 7 | 8 | 7 | 8 | 7 | 7 | 8 | 7 | 8 | 8 | 7 | 12 |  | 29 | 50 | 50 | 50 | 48 | 50 | 11 | 391680
| Meghnaghat 104 MW PP (OPCL) | 17 | 17 | 17 |  |  |  | 15 | 18 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 51 | 44 | 54 | 60 | 55 | 18 | 515520
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 |  | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 1337640
92 | Fenchuganj 44MW (Energyprima) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 41 | 48 | 48 | 49 | 49 | 49 | 49 | 892656
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1217689
94 | Gagnagar 102 MW PP (Digital Power) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 24 | 50 | 50 | 40 | 40 | 40 | 8 | 355680
95 | Patenga 50MW PP (Baraka) | 25 | 26 | 26 | 26 | 26 | 26 | 26 | 25 | 26 | 25 | 25 | 25 | 25 | 25 | 23 | 24 | 25 | 25 |  | 25 | 25 | 25 | 25 | 26 | 25 | 25 | 610080
96 | Chattogram 108 MW PP (ECPV) | 89 | 89 | 83 | 83 | 89 | 89 | 89 | 89 | 89 | 89 | 88 | 35 | 12 | 11 | 12 | 11 | 11 | 34 |  | 68 | 80 | 81 | 81 | 81 | 42 | 11 | 1464960
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 744792
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1331942
101 | Kushiara 163 MW CCPP (KP) | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2602554
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 | 0 | 0 | 2 | 2 | 1 | 1 | 1 | 1 | 1 | 0 | [8 empty] | 8950
103 | Kamalaghat 54 MW PP(Banco Energy) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 35 | 889920
104 | Keranigonj 300 MW PP (APR) | [25 empty] | 0 | 0
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 168 |  | 177 | 180 | 170 | 171 | 171 | 171 | 48 | 1828800
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 97 | 97 | 97 | 97 | 98 | 97 | 98 | 97 | 99 | 97 | 99 | 97 | 95 | 99 | 97 | 98 | 98 | 127 |  | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 2711090
115 | Juldah 100 MW PP Unit-3 (Acorn) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 887040
116 | Chandpur 200MW (Desh energy) | 133 | 70 | 70 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 34 | 34 | 34 | 34 | 34 | 34 | 41 | 68 |  | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 1515360
117 | Ashuganj 150MW PP (Midland) | 127 | 120 | 132 | 133 | 125 | 130 | 135 | 128 | 132 | 117 | 123 | 118 | 122 | 117 | 112 | 107 | 113 | 115 |  | 117 | 121 | 122 | 127 | 132 | 133 | 133 | 2979127
118 | Bibiyana-III 400 MW CCPP | 404 | 403 | 397 | 401 | 401 | 401 | 401 | 363 | 399 | 402 | 401 | 396 | 403 | 404 | 394 | 398 | 374 | 403 |  | 380 | 400 | 403 | 403 | 403 | 402 | 404 | 9543000
| Jamalpur 115 MW PP (United) | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 48 | 49 | 49 | 49 | 49 | 49 | 78 |  | 78 | 78 | 78 | 78 | 78 | 78 | 48 | 1344000
| Anwara 300 MW PP (United) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 50 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 |  | 202 | 204 | 210 | 214 | 214 | 52 | 52 | 1563164
| Juldah unit-2 (Acorn) | 53 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 54 | 90 | 90 | 100 | 100 | 100 | 100 | 954240
| Anlima Energy Ltd. | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 |  | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 2608200
| Bhairob 54.5 MW | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | [5 empty] | 0 | 11 | 32 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 646920
| Spectra Solar Plant Ltd. | [5 empty] | 0 | 0 | 1 | 4 | 13 | 18 | 14 | 35 | 34 | 20 | 19 | 10 | 2 |  | 0 | [6 empty] | 159232
| Chandpur 115(Doreen) | 74 | 70 | 75 | 75 | 74 | 63 | 61 | 58 | 58 | 58 | 56 | 57 | 53 | 51 | 66 | 75 | 75 | 75 |  | 75 | 75 | 75 | 75 | 75 | 75 | 76 | 1640640
| Kanchan Purbachal Power Generation Ltd. | 55 | 55 | 55 | 46 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1329840
120 | Eastern Zone Total | 7050 | 6926 | 6976 | 6909 | 6886 | 6684 | 6662 | 6542 | 6631 | 6548 | 6628 | 6512 | 6532 | 6518 | 6502 | 6561 | 6759 | 6851 |  | 7328 | 7533 | 7453 | 7570 | 7498 | 7463 | 6805 | 165914123
121
122 | o
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 32 | 32 | 32 | 419520
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 17 | 17 | 17 | 17 | 17 | [12 empty] | 3 |  | 44 | 39 | 39 | 33 | 33 | 33 | 33 | 287520
| Khulna 225 MW CCPP | [15 empty] | 5 | 5 | 5 |  | 15 | 15 | 15 | 35 | 118 | 120 | 150 | 387443
129 | Rupsha 105 MW PP (Orion rupsha) | [10 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 24 | 45 | 47 | 53 | 53 | 53 | 0 | 390240
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 1 | 7 | 16 | 49 | 53 | 71 | 62 | 1 | 16 | 43 | 30 | 30 | 6 |  | 0 | [6 empty] | 449280
131
132 | United Payra Power Ltd. | [25 empty] | 0 | 0
133 | Bhola Nutan Biddut BD LTD (GAS) | 220 | 220 | 220 | 222 | 220 | 222 | 223 | 223 | 219 | 217 | 217 | 214 | 212 | 212 | 210 | 213 | 213 | 213 |  | 213 | 220 | 220 | 220 | 220 | 221 | 220 | 5208245
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 32 | 32 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 32 | 32 | 32 | 32 | 32 | 509280
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 85 | 87 | 85 | 86 | 86 | 88 | 88 | 88 | 87 | 87 | 88 | 85 | 85 | 85 | 84 | 86 | 83 | 86 |  | 85 | 86 | 88 | 86 | 88 | 84 | 86 | 2071507
140 | Bhola 33 MW PP (Venture) | 32 | 31 | 31 | 29 | 28 | 22 | 21 | 21 | 23 | 21 | 18 | 21 | 25 | 22 | 24 | 26 | 25 | 24 |  | 30 | 31 | 31 | 32 | 32 | 30 | 33 | 620717
141 | Noapara 100 MW PP (Bangla Trac) | [25 empty] | 0 | 0
142 | Noapara 40 MW PP (Khanjahan Ali) | 8 | 8 | 8 | 8 | [12 empty] | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 96375
143 | Gopalganj 100 MW Peaking PP | 56 | 56 | 56 | 56 | 51 | 20 | 19 | 19 | 19 | [10 empty] | 14 | 30 | 70 | 65 | 59 | 59 | 60 | 667904
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | 105 | 105 | 105 | 105 | 105 | 95 | 105 | 105 | 105 | 105 | 88 | 89 | 89 | 89 | 67 | 88 | 88 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2423952
146 | Bheramara HVDC | 914 | 913 | 914 | 914 | 914 | 913 | 914 | 913 | 913 | 913 | 914 | 914 | 913 | 914 | 913 | 913 | 913 | 914 |  | 913 | 913 | 913 | 914 | 913 | 913 | 913 | 22080000
147 | Bheramara 410 MW CCPP | 170 | 175 | 175 | 175 | 175 | 175 | 180 | 180 | 170 | 160 | 160 | 145 | 145 | 150 | 145 | 145 | 145 | 145 |  | 145 | 145 | 145 | 150 | 150 | 160 | 160 | 4004352
148 | Payra 1320 MW | 1080 | 1070 | 1070 | 1050 | 1050 | 990 | 990 | 960 | 930 | 910 | 880 | 890 | 930 | 930 | 950 | 990 | 990 | 980 |  | 960 | 1060 | 1050 | 1060 | 1080 | 1090 | 1070 | 26047900
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4870900
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 32 | 32 | 32 | 32 | 32 | 32 | [7 empty] | 0 | 16 | 16 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 420448
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 0 | 0 | 0 | 0 | 2 | 4 | 4 | 2 | 2 | 2 | 1 | 0 | [8 empty] | 22140
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 190 | 189 | 189 | 189 | 189 | 189 | 189 | 188 | 189 | 188 | 187 | 174 | 176 | 175 | 176 | 176 | 175 | 176 |  | 175 | 176 | 174 | 178 | 177 | 177 | 177 | 4588755
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
| Sirajgonj 225 MW CCPP Unit-2 (Oil) | 172 | 150 | 150 | 130 | 130 | 130 | 130 | 130 | 140 | 130 | 137 | 191 | 212 | 210 | 209 | 210 | 148 | 130 |  | 140 | 197 | 207 | 216 | 218 | 217 | 217 | 4299255
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 159 | 160 | 158 | 157 | 156 | 159 | 164 | 162 | 160 | 154 | 145 | 143 | 140 | 138 | 140 | 141 | 141 | 141 |  | 142 | 142 | 142 | 145 | 145 | 146 | 147 | 3837264
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 336 | 356 | 360 | 365 | 359 | 364 | 363 | 340 | 330 | 305 | 297 | 298 | 287 | 285 | 285 | 274 | 280 | 279 |  | 279 | 283 | 295 | 296 | 306 | 298 | 297 | 7582472
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | 41 | 41 | 41 | 41 | 41 | [7 empty] | 5 | 6 | 7 | 28 | 38 | 40 |  | 41 | 41 | 41 | 41 | 40 | 40 | 40 | 495491
162 | Bogra 22 MW PP (GBB) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 20 | 19 | 18 | 17 | 17 | 17 | 17 | 17 | 17 | 18 |  | 21 | 22 | 22 | 22 | 22 | 22 | 22 | 455400
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 0 |  | 11 | 216594
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | 42 | 42 | 42 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 42 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 889248
167 | Katakhali 50 MW Peaking PP | 32 | 24 | 24 | 24 | 24 | 24 | 24 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 621410
168 | Santahar 50 MW Peaking PP | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 790600
169 | Natore 52 MW PP (Rajlanka) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 35 | 52 | 52 | 52 | 52 | 52 | 8 | 376200
170 | Chapainawabganj 100 MW Peaking PP | 86 | 86 | 86 | 86 | 86 | 79 | 79 | 79 | 79 | 73 | 73 | 73 | 73 | 73 | 73 | 78 | 78 | 88 |  | 88 | 90 | 90 | 90 | 87 | 87 | 80 | 1918856
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 60 | 92 | 94 |  | 94 | 94 | 94 | 94 | 94 | 94 | 50 | 1644768
172 | Confidence Power Bogura Unit-1 113 MW | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 95 |  | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 1602816
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 50 | 56 | 56 | 56 | 56 | 57 | 64 | 94 | 92 |  | 92 | 92 | 92 | 92 | 92 | 92 | 56 | 1620105
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1 | 2 | 2 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 2 |  | 0 | [6 empty] | 29804
178 | Energypac Power Venture Thakurgaon Ltd. | 90 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 1693056
178