## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID COMPANY OF BANGLADESH LTD.
SYSTEM OPERATION DATA
Month:June 2022
Sl. | Items | Current Month |  | Previous Month |  | This Month Last Year |  | Max. Till-to-date
|  | 2022-06-01 |  | 2022-05-01 |  | 2021-06-01
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 14038 | 2022-06-08 | 13954 | 2022-05-16 | 13014 | 2021-06-02 | 14782 | 2022-04-16
|  |  | 23:00 |  | 21:00 |  | 21:00 |  | 21:00
2 | Minimum Generation (MW) | 8231 | 2022-06-17 | 4396 | 2022-05-21 | 7369 | 2021-06-18 | - | -
|  |  | 6:00 |  | 6:00 |  | 9:00 |  | -
3 | Maximum Evening Peak Generation (MW) | 14004 | 2022-06-06 | 13954 | 2022-05-16 | 13014 | 2021-06-02 | 14782 | 2022-04-16
|  |  | 21:00 |  | 21:00 |  | 21:00 |  | 21:00
4 | Maximum Day Peak Generation (MW) | 12226 | 2022-06-08 | 11993 | 2022-05-24 | 9351 | 2021-06-01 | 12895 | 2022-04-26
|  |  | 12:00 |  | 12:00 |  | 12:00 |  | 12:00
5 | Maximum Evening Peak Demand (MW) Estimated | 14038 | 2022-06-08 | 13954 | 2022-05-16 | 13014 | 2021-06-02 | 14782 | 2022-04-16
|  |  | 23:00 |  | 12:00 |  | 19:00 |  | 12:00
6 | Average Generation (MW) at Evening Peak | 13051.7667 |  | 12277.0968 |  | 11972.1667 |  | 13536.33 | 2022-04-27
7 | Average Generation (MW) at Day Peak | 11161.4333 |  | 10010.6129 |  | 10113.8333 |  | 11233.4 | 2022-04-27
8 | Maximum Power Import from India, BIPTC (MW) | 933 | 2022-06-07 | 934 | 2022-05-26 | 933 | 2021-04-29 18:00 | 956 | 27/3/2019
|  |  | 2:00 |  | 7:00 |  | 18:00 |  | 19:00
9 | Maximum Power Import from Tripura, India (MW) | 188 | 2022-06-08 | 174 | 2022-05-18 | 187 | 2021-04-18 | 194 | 12/06/19
|  |  | 21:00 |  | 18:00 |  | 18:00 |  | 19:00
10 | Maximum Load Shed (MW) at Evening Peak | - | - | - | - | - | - | 1459 | 04/05/2010
|  |  | - |  | - |  |  |  | 20:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | - | - | - | - | - | - | 13792 | 2021-04-27
|  | - | - | - | - | - | - |  | 20:00
12 | Minimum Load Shed (MW) at Evening Peak | - | - | - | - | - | -
13 | Generation During Min. Load Shed (MW) at Evening Peak | - | - | - | - | - | -
14 | Maximum Load Shed (MW) at Day Peak | - | - | - | - | - | -
15 | Generation During Max. Load Shed (MW) at Day Peak | - | - | - | - | - | -
16 | Minimum Load Shed (MW) at Day Peak | - | - | - | - | - | -
17 | Generation During Min. Load Shed (MW) at Day Peak | - | - | - | - | - | -
18 | Nos. of Days Load Shed at Evening Peak | - |  | - |  | -
19 | Nos. of Days Load Shed at Day Peak | - |  | - |  | -
20 | Gross Generation of BPDB (MKWH) | 1590.9771 |  | 1760.1344 |  | 1824.666 |  | 3805.72 | 2019-09-19
21 | Station Use of BPDB (MKWH) | 84.3577 |  | 75.5671 |  | 133.138
22 | Net Generation of BPDB (MKWH) | 1506.6194 |  | 1684.5673 |  | 1691.528
23 | Net Generation of IPP (MKWH) | 5289.635 |  | 4686.772 |  | 4415.8372
24 | Net Generation of REB (MKWH) | 122.8415 |  | 117.2486 |  | 133.1241
24 | Net Generation of Rental Power Plant (MKWH) | 624.4748 |  | 517.426 |  | 485.0104
25 | Total Net Generation (MKHWh) (BPDB, IPP, RPP & REB) | 7543.5707 |  | 7006.0139 |  | 6725.4996 |  | 7842.9924 | April'22
26 | Energy Generation by Gas (MKWH) | 4234.9012 |  | 4216.1115 |  | 4718.5487 |  | 4756.96 | Sep-19
27 | Energy Generation by Diesel (MKWH) | 491.7382 |  | 296.4446 |  | 291.9991 |  | 771.52 | July-18
28 | Energy Generation by Furnace Oil (MKWH) | 2164.1587 |  | 1740.5311 |  | 1394.2185 |  | 2365.7466 | April'22
29 | Energy Generation by Hydro (MKWH) | 52.8346 |  | 27.4557 |  | 17.4436 |  | 151.4 | August-19
30 | Energy Generation by Solar (MKWH) | 25.0967 |  | 33.0386 |  | 15.602 |  | 40.58 | March-22
31 | Energy Generation by Coal (MKWH) | 659.199 |  | 767.9994 |  | 420.8257 |  | 659.2 | June'22
32 | Enegry Import from India (BIPTC & AC) (MKWH) | 738.4142 |  | 725.8023 |  | 711.7673 |  | 775.9511 | August-20
33 | Monthly Load Factor (%) | 88.6952 |  | 83.2694 |  | 78.1871 |  | 88.7 | June'22

## QF-LDC-22
Page: 1/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month:June 2022
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quantity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 14038 | 2022-06-08 | 23:00
Generation Period
| Dhaka | MW | 5109.41
| Chattogram | MW | 1337 | [7 empty] | 5024.63
| Cumilla | MW | 1289
| Mymensingh | MW | 1014
| Sylhet | MW | 502
a) | Total supply in East zone | MW | 9251.41
| Khulna | MW | 1731.2
| Barisal | MW | 432
| Rajshahi | MW | 1349.6
| Rangpur | MW | 744
b) | Total supply in West zone | MW | 4256.8
c) | Total supply in both zone ( a+b) | MW | 13508.21
Ref: | 27.21.0000.603.16.087.20.529 | Date: 19/07/2022
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
Page: 2/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month:June 2022
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Daily Maximum power Export through EWI/ NO-1
| a) Ghorashal end | AMPS | 540 | 2022-06-27 | 23:00
| b) Ishurdi end | MW | 514 | 2022-06-14 | 19:30
18 | Daily Maximum power Import through EWI/ NO-1
| a) Ghorashal end | AMPS | 1180 | 2022-06-14 | 19:30 |  |  | 1.7815
| b) Ishurdi end | MW | 246 | 2022-06-27 | 22:00
19 | Daily Maximum Energy Export through EWI/NO-1 | [6 empty] | 0 | Ghorashal
| a) Ghorashal end | MKWH | - | - |  |  |  | 0
| b) Ishurdi end | MKWH | - | - |  |  |  | 0
20 | Daily Maximum Energy Import through EWI/ NO-1 | [6 empty] | 0
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
21 | Total Energy Export through EWI/ NO-1
| a) Ghorashal end | MKWH | 14.15 |  |  |  |  | #REF! | Imp | Exp
| b) Ishurdi end | MKWH | 104.07 |  |  |  |  | #REF! | #REF! | 0
22 | Total Energy Import through EWI/ NO-1 | [6 empty] | #REF! | #REF! | 0
| a) Ghorashal end | MKWH | - |  |  |  |  | 0
| b) Ishurdi end | MKWH | - |  |  |  |  | 0
23 | Transmission loss of EWI/ NO-1 | % | 3 |  |  |  |  | 0 |  |  |  | 5.91
24 | Daily Maximum power Export through EWI/ NO-2 | [6 empty] | 0 |  |  |  | 2.955
| a) Ashuganj end | MW | 320 | 2022-06-09 | 23:00 |  |  | 0
| b)Serajganj end | MW | 560 | 2022-06-14 | 19:30 |  |  |  | #REF! | 0
25 | Daily Maximum power Import through EWI/ NO-2
| a) Ashuganj end | MW | 490 | 2022-06-14 | 19:30
| b)Sirajganj end | MW | 290 | 2022-06-27 | 22:00
26 | Daily Maximum Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 1.85 | 2022-06-29 |  |  | 2366 | 4.732
| b)Sirajganj end | MKWH | - | -
27 | Daily Maximum Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | - | - | [6 empty] | %
| b)Sirajganj end | MKWH |  |  |  |  | 2370 | 4.74
28 | Total Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 19.81
| b)Sirajganj end | MKWH | 106.19
29 | Total Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | 101.97
| b)Sirajganj end | MKWH | 19.98 |  |  |  |  | 132.822 | 132822000 | 0.01099 | 1.099
30 | Transmission loss of EWI /NO-2 | % | 3.203'% |  |  |  |  | 134.298 | 134298000
* Total energy export from Ghorasal end and import from Ishurdi end and the transmission loss of EWI/NO-1 is taken | [7 empty] | 1.099 | 1476000 | 0.01099 | 1.099
from the calculation of GMD, PGCB, Ishwardi. | [8 empty] | 1.099
* *Total energy export from Ashuganj end and import from Sirajganj end and the transmission loss of EWI/NO-2 is taken | [10 empty] | 420
from the calculation of Sirajganj switching sub station.
* **The energy meter of Ghorasal end is out of order.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.
Ist East-West Interconnector Loss:
| Ghorasal End (KWH): | 109882206.4 | 1000000 | 109.8822 | 836363.65 | 0.83636
| Ishurdi End (KWH): | 106928443.1 | 1000000 | 106.9284 | 811272.74 | 0.81127
| Difference (-) : | 2953763.3 |  |  | 25090.91
| Loss : | 2.688% |  |  | 3%
| 2nd East-West Interconnector Loss: |  |  |  |  | 99387644.47
| Ashuganj End (KWH) | 245578000 | 1000000 | 245.578 |  | 96795991.85
| Sirajganj End (KWH) | 242062000 | 1000000 | 242.062 |  | 2308363.67
| Difference (-) : | 3516000 |  |  |  | 2239112.76
| Loss : | 1.432%

## QF-LDC-23
QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: June2022
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Mymensingh | 132/33 kV transformers T-1 & T2 | 2022-06-02 09:25 | 2022-06-02 09:35 | 0:10 | T | Due to 33 kV feeder fault | 170 | 28.3333 | Power interruption
Savar | 33 kV Bus-A | 2022-06-03 07:41 | 2022-06-03 09:14 | 1:33 | T | Due to red-hot maint by PBS | 0 | 0 | No interruption
Sherpur | 132/33 kV transformer T-3 | 2022-06-03 05:43 | 2022-06-03 06:49 | 1:06 | T | Due to bad weather | 12 | 13.2 | Power interruption
Kishoreganj | 132/33 kV transformers T-1 & T2 | 2022-06-05 21:20 | 2022-06-05 23:53 | 2:33 | T | Due to red-hot maint at 33 kV Bus | 70 | 178.5 | Power interruption
Tangail | 132/33 kV transformer T-2 | 2022-06-11 00:15 | 2022-06-11 01:45 | 1:30 | T | Due to red-hot maint by PDB | 90 | 135 | Power interruption
| 132/33 kV transformer T-2 | 2022-06-11 02:40 | 2022-06-11 03:58 | 1:18 | T | Due to red-hot maint by PDB | 70 | 91 | Power interruption
Mymensingh | 132/33 kV transformers T-1 & T2 | 2022-06-12 18:55 | 2022-06-12 19:10 | 0:15 | T | Due to 33 kV feeder fault | 120 | 30 | Power interruption
| 132/33 kV transformer T- with 33 kV Bus | 2022-06-13 10:42 | 2022-06-13 12:01 | 1:19 | T | Due to red-hot maint | 40 | 52.6667 | Power interruption
Kishoreganj | 132/33 kV transformers T-1 & T2 with 33 kV Bus | 2022-06-16 00:07 | 2022-06-16 01:36 | 1:29 | T | Due to red-hot maint | 90 | 133.5 | Power interruption
Kabirpur | 132/33 kV transformer T-3 | 2022-06-16 06:23 | 2022-06-16 07:59 | 1:36 | T | Due to red-hot maint at 33 kV Bus | 0 | 0 | No interruption
| 132/33 kV all transformers T-1 | 2022-06-17 15:02 | 2022-06-17 16:10 | 1:08 | T | Tripped showing O/C & E/F. relay | 0 | 0 | No interruption
| 132/33 kV all transformers T-2 | 2022-06-17 15:02 | 2022-06-17 16:01 | 0:59 | T |  | 50 | 49.1667 | Power interruption 15:02 to 16:01
| 132/33 kV all transformers T-3 | 2022-06-17 15:02 | 2022-06-17 18:50 | 3:48 | T
| 132/33 kV transformer T-1 | 2022-06-18 09:12 | 2022-06-18 21:14 | 12:02 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Netrakona | 132/33 kV transformer T-2 | 2022-06-20 07:58 | 2022-06-20 09:18 | 1:20 | T | Due to red-hot maint at 33 kV Bus | 10 | 13.3333 | Power interruption
Kabirpur | 132/33 kV transformers T-1 & T-2 | 2022-06-23 09:28 | 2022-06-23 09:59 | 0:31 | T | Tripped showing O/C . relay | 150 | 77.5 | Power interruption
Mymensingh | 132/33 kV transformer T-3 | 2022-06-26 21:27 | 2022-06-26 22:15 | 0:48 | T | Due to red-hot maint at 33 kV Bus | 0 | 0 | No interruption
Kodda | 132/33 kV transformer T-3 | 2022-06-29 20:30 | 2022-06-29 21:50 | 1:20 | T | Due to red-hot maint at 33 kV Bus | 20 | 26.6667 | Power interruption
| 132/33 kV transformer T-2 | 2022-06-29 20:45 | 2022-06-29 21:00 | 0:15 | T | Tripped showing O/C . relay at 33 kV feeder | 19 | 4.75 | Power interruption
|  |  | Total : | 35:00 |  | Unserved Energy: |  | 833.6167
Dhaka (South) Grid Circle :
Hasnabad | 33 kV main Bus | 2022-06-01 13:01 | 2022-06-01 18:10 | 5:09 | T | Due to red-hot maint.at 33 kV Bus | 0 | 0 | No interruption
| 230/132 kV transformer T-01 | 2022-06-02 14:30 | 2022-06-02 16:32 | 2:02 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Sonargaon | 132/33 kV transformers T-1 & T-2 | 2022-06-03 23:56 | 2022-06-04 00:13 | 0:17 | T | Due to 33 kV feeder fault | 60 | 17 | Power interruption
Munshiganj | 132/33 kV transformer T-1 & 33 kV Bus | 2022-06-05 15:38 | 2022-06-05 17:40 | 2:02 | T | Due to red-hot maint.at 33 kV Bus | 0 | 0 | No interruption
Keraniganj | 230/132 kV transformer T-02 | 2022-06-07 15:09 | 2022-06-07 17:18 | 2:09 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Bhulta | 132/33 kV transformer T-2 | 2022-06-14 07:28 | 2022-06-14 08:07 | 0:39 | T | Due to red-hot maint. | 0 | 0 | No interruption
Sreenagar | 132/33 kV transformer T-1 with 33 kV Bus-1 | 2022-06-16 15:03 | 2022-06-16 17:38 | 2:35 | T | Due to red-hot maint.at 33 kV Bus | 14 | 36.1667 | Power interruption
| 132/33 kV transformer T-1 | 2022-06-20 23:36 | 2022-06-21 00:04 | 0:28 | T |  | 0 | 0 | No interruption
| 132/33 kV transformer T-2 | 2022-06-22 11:13 | 2022-06-22 13:45 | 2:32 | T | Due to red-hot maint.at 33 kV Bus | 0 | 0 | No interruption
| 132/33 kV transformer T-1 | 2022-06-23 15:05 | 2022-06-23 16:30 | 1:25 | T | Due to red-hot maint. | 0 | 0 | No interruption
Bhulta | 132/33 kV transformers T-1 & T2 | 2022-06-25 11:42 | 2022-06-25 11:58 | 0:16 | T | Tripped showing E/F . relay | 248 | 66.1333 | Power interruption
| 132/33 kV transformer T-1 | 2022-06-27 08:07 | 2022-06-27 08:41 | 0:34 | T | Due to red-hot maint. | 0 | 0 | No interruption
Sonargaon | 132/33 kV transformer T-1 | 2022-06-28 07:49 | 2022-06-28 08:11 | 0:22 | T | Tripped showing E/F . relay at 33 kV feeder fault | 0 | 0 | No interruption
Hasnabad | 132/33 kV transformer T-2 | 2022-06-29 20:45 | 2022-06-29 21:00 | 0:15 | T | Tripped showing E/F . relay at 33 kV feeder fault | 19 | 4.75 | Power interruption
Bhulta | 132/33 kV transformer T-1 | 2022-06-30 08:07 | 2022-06-30 08:41 | 0:34 | T | Due to red-hot maint. | 0 | 0 | No interruption
Hasnabad | 132/33 kV transformer T-2 | 2022-06-30 16:10 | 2022-06-30 16:23 | 0:13 | T | Tripped showing O/C . relay at 33 kV feeder fault | 15 | 3.25 | Power interruption
|  |  | Total : | 21:32 |  | Unserved Energy: |  | 127.3
Chattogram Grid Circle :
Madunaghat | 132/33 kV transformers T1 & T2 | 2022-06-02 09:09 | 2022-06-02 10:07 | 0:58 | T | Due to 33 kV feeder fault | 42 | 40.6 | Power interruption
Dohazari | 132/33 kV transformer T-2 with 33 kV Bus-2 | 2022-06-04 07:20 | 2022-06-04 08:18 | 0:58 | T | Due to red-hot maint. | 0 | 0 | No interruption
Cox'sbazar | 132/33 kV transformers T1 & T2 | 2022-06-07 16:40 | 2022-06-07 16:45 | 0:05 | T | Due to 33 kV feeder fault | 20 | 1.6667 | Power interruption
| 132/33 kV transformers T1 & T2 | 2022-06-07 07:27 | 2022-06-07 07:30 | 0:03 | T | Due to 33 kV feeder fault | 48 | 2.4 | Power interruption
Madunaghat | 132/33 kV transformer T2 | 2022-06-14 16:01 | 2022-06-14 17:25 | 1:24 | T | Due to main prot.relay | 8 | 11.2 | Power interruption
Sikalbaha | 132/33 kV transformer T4 | 2022-06-16 11:45 | 2022-06-16 12:35 | 0:50 | T | Due to red-hot maint. | 0 | 0 | No interruption
Cox'sbazar | 132/33 kV transformer T3 | 2022-06-17 17:50 | 2022-06-17 18:48 | 0:58 | T | Due to red-hot maint. | 30 | 29 | Power interruption
Matarbari | 132/33 kV transformer T3 | 2022-06-18 12:12 | 2022-06-18 12:33 | 0:21 | E/O | Due to 33 kV feeder fault | 3 | 1.05 | Power interruption
Dohazari | 132/33 kV transformer T2 | 2022-06-19 08:34 | 2022-06-19 09:31 | 0:57 | T | Due to red-hot maint. | 0 | 0 | No interruption
Dohazari | 132/33 kV transformers T1 | 2022-06-20 10:52 | 2022-06-20 11:20 | 0:28 | T | Tripped showing PRD relay | 55 | 25.6667 | Power interruption
| 132/33 kV transformers T2 | 2022-06-20 10:52 | 2022-06-20 13:51 | 2:59 | T
Cox'sbazar | 132/33 kV transformerT2 | 2022-06-21 14:57 | 2022-06-21 16:10 | 1:13 | T | Due to red-hot maint. | 5 | 6.0833 | Power interruption
Sikalbaha | 132/33 kV transformer T-4 | 2022-06-21 15:36 | 2022-06-21 17:13 | 1:37 | T | Due to red-hot maint. | 15 | 1.75 | Power interruption 15:36 to 15:43
| 132/33 kV transformerT3 | 2022-06-26 10:02 | 2022-06-26 11:26 | 1:24 | T | Due to red-hot maint. | 0 | 0 | No interruption
Bakulia | 132/33 kV transformerT2 | 2022-06-28 17:31 | 2022-06-28 19:08 | 1:37 | T | Tripped showing O/C. relay at 33 kV side | 122 | 197.2333 | Power interruption
| 132/33 kV transformerT3 | 2022-06-28 17:35 | 2022-06-28 18:35 | 1:00 | T | Due to 33 kV feeder fault | 0 | 0 | No interruption
|  |  | Total : | 16:52 |  | Unserved Energy: |  | 316.65
Cumilla Grid Circle :
Baroierhat | 132/33 kV transformer T1 with 33 kV Bus | 2022-06-02 23:37 | 2022-06-03 00:41 | 1:04 | E/O | Due to red-hot maint | 20 | 21.3333 | Power interruption
Shahijibazar | 132/33 kV transformers T2 & T4 | 2022-06-03 12:50 | 2022-06-03 19:12 | 6:22 | T | Due to 33 kV feeder fault | 50 | 318.3333 | Power interruption
Cumilla (N) | 132/33 kV transformers T3 & T4 | 2022-06-04 11:09 | 2022-06-04 11:24 | 0:15 | T | Tripped showing O/C at 33 kV side | 0 | 0 | No interruption
Feni | 132/33 kV transformer T1 | 2022-06-05 07:58 | 2022-06-05 09:30 | 1:32 | E/O | Due to red-hot maint at 33 kV side | 20 | 30.6667 | Power interruption
Chaddagram | 132/33 kV transformer T1 | 2022-06-06 09:12 | 2022-06-06 10:25 | 1:13 | E/O | Due to red-hot maint at 33 kV side | 0 | 0 | No interruption
Kachua | 132/33 kV transformers T1 & T2 with 33 kV Bus | 2022-06-06 21:45 | 2022-06-06 22:22 | 0:37 | E/O | Due to red-hot maint at PBS feeder | 25 | 15.4167 | Power interruption
Sunamganj | 132/33 kV transformer T1 | 2022-06-06 22:28 | 2022-06-06 23:15 | 0:47 | E/O | Due to red-hot maint | 10 | 7.8333 | Power interruption
Baroierhat | 132/33 kV transformer T1 with 33 kV Bus | 2022-06-07 15:22 | 2022-06-07 17:07 | 1:45 | E/O | Due to red-hot maint at PBS feeder | 20 | 35 | Power interruption
Shahijibazar | 132/33 kV transformer T2 | 2022-06-11 05:02 | 2022-06-11 05:49 | 0:47 | T | Due to 33 kV feeder fault | 16 | 12.5333 | Power interruption
Daudkandi | 132/33 kV transformer T3 | 2022-06-11 07:54 | 2022-06-11 09:36 | 1:42 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Baroierhat | 132/33 kV transformer T1 | 2022-06-11 09:33 | 2022-06-11 11:28 | 1:55 | E/O | Due to red-hot maint | 26 | 49.8333 | Power interruption
Sunamganj | 132/33 kV transformers T1 & T2 | 2022-06-13 05:38 | 2022-06-13 07:15 | 1:37 | T | Due to 33 kV feeder fault | 25 | 40.4167 | Power interruption
Chatak | 132/33 kV transformer T2 | 2022-06-13 07:02 | 2022-06-13 07:40 | 0:38 | T | Due to 33 kV feeder fault | 5 | 3.1667 | Power interruption
Sreemongal | 132/33 kV transformers T2 & T3 | 2022-06-13 12:08 | 2022-06-13 12:24 | 0:16 | T | Due to 33 kV feeder fault | 13 | 3.4667 | Power interruption
B.Baria | 132/33 kV transformer T2 | 2022-06-13 20:40 | 2022-06-13 21:20 | 0:40 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Sreemongal | 132/33 kV transformer T2 | 2022-06-14 12:21 | 2022-06-14 13:34 | 1:13 | T | Due to 33 kV feeder fault | 14 | 17.0333 | Power interruption
Ramganj | 132/33 kV transformer T2 | 2022-06-19 21:38 | 2022-06-19 22:32 | 0:54 | E/O | Due to red-hot maint at 33 kV side | 30 | 27 | Power interruption
Chowmuhani | 132/33 kV transformer T1 | 2022-06-19 06:33 | 2022-06-19 09:48 | 3:15 | E/O |  | 30 | 97.5 | Power interruption
Sylhet | 132/33 kV transformer T1 | 2022-06-20 09:10 | 2022-06-20 16:49 | 7:39 | T | Tripped showing lockout relay | 30 | 27.5 | Power interruption 09:10 to 09:32
Cumilla(S) | 132/33 kV transformer T2 | 2022-06-20 15:38 | 2022-06-20 15:59 | 0:21 | T | Due to 33 kV feeder fault | 20 | 7 | Power interruption
Chandpur | 132/33 kV transformer T1 with 33 kV Bus | 2022-06-21 17:45 | 2022-06-21 18:18 | 0:33 | E/O | Due to bursting of CT | 0 | 0 | No interruption
Sylhet | 132/33 kV transformer T2 | 2022-06-22 12:24 | 2022-06-22 13:30 | 1:06 | T | Tripped showing lockout relay | 0 | 0 | No interruption
Kulaura | 132/33 kV transformer T1 | 2022-06-22 16:10 | 2022-06-22 17:40 | 1:30 | E/O | Due to red-hot maint by PBS | 15 | 27.5 | Power interruption
Ashuganj | 230/132 kV transformer OAT12 | 2022-06-22 23:34 | 2022-06-22 23:34 | 0:00 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Chatak | 132/33 kV transformer T1 | 2022-06-25 11:35 | 2022-06-25 11:40 | 0:05 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Shahijibazar | 132/33 kV transformer T4 | 2022-06-30 07:07 | 2022-06-30 07:56 | 0:49 | E/O | Due to red-hot maint at 33 kV side | 45 | 36.75 | Power interruption
|  |  | Total : | 38:35 |  |  |  | 778.2833
Khulna Grid Circle :
Barishal | 132/33 kV transformer T5 | 2022-06-01 12:02 | 2022-06-01 13:33 | 1:31 | T | Tripped showing PRD relay | 0 | 0 | No interruption
Mongla | 132/33 kV transformer T-1 | 2022-06-11 10:07 | 2022-06-11 11:06 | 0:59 | E/O | Due to red-hot maint | 10 | 9.8333 | Power interruption
Barishal(N) | 132/33 kV transformer T4 | 2022-06-11 10:13 | 2022-06-11 15:27 | 5:14 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Khulna© | 132/33 kV transformers T2 & T3 | 2022-06-12 07:11 | 2022-06-12 07:20 | 0:09 | T | Tripped showing E/F relay at 33 kV side | 60 | 9 | Power interruption
Mongla | 132/33 kV transformers T1 & T2 | 2022-06-12 19:07 | 2022-06-12 19:26 | 0:19 | E/O | Due to 33 kV feeder fault | 28 | 8.8667 | Power interruption
Shariatpur | 132/33 kV transformer T2 | 2022-06-12 14:03 | 2022-06-12 14:25 | 0:22 | E/O | Due to 33 kV feeder fault | 56 | 20.5333 | Power interruption
Khulna© | 132/33 kV transformer T2 | 2022-06-14 14:10 | 2022-06-14 14:40 | 0:30 | E/O | Due to 33 kV feeder fault | 25 | 12.5 | Power interruption
Barishal(N) | 132/33 kV transformers T4 & T5 | 2022-06-14 14:37 | 2022-06-14 14:43 | 0:06 | T | Tripped showing E/F relay | 41 | 4.1 | Power interruption
Gallamari | 132/33 kV transformer T2 | 2022-06-18 09:24 | 2022-06-18 09:45 | 0:21 | E/O | Due to 33 kV feeder fault | 26 | 9.1 | Power interruption
Bhandaria | 132/33 kV transformers T1 & T2 | 2022-06-18 09:58 | 2022-06-18 10:12 | 0:14 | T | Tripped showing O/C & E/F relay 33 kV side | 28 | 6.5333 | Power interruption
Noapara | 132/33 kV transformer T2 | 2022-06-22 08:34 | 2022-06-22 11:13 | 2:39 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Mongla | 132/33 kV transformers T1 & T2 | 2022-06-26 18:56 | 2022-06-26 19:06 | 0:10 | T | Tripped showing E/F relay | 36 | 6 | Power interruption
Barishal(N) | 132/33 kV transformers T1 & T2 | 2022-06-27 14:07 | 2022-06-27 14:22 | 0:15 | E/O | Due to 33 kV feeder fault | 110 | 27.5 | Power interruption
Noapara | 132/33 kV transformer T4 | 2022-06-30 08:33 | 2022-06-30 09:41 | 1:08 | E/O | Due to red-hot maint | 20 | 22.6667 | Power interruption
Rajbari | 132/33 kV transformer T1 | 2022-06-30 12:40 | 2022-06-30 14:16 | 1:36 | E/O | Due to red-hot maint | 10 | 16 | Power interruption
|  |  | Total : | 15:33 |  | Unserved Energy: |  | 152.6333
HVDC Grid Circle :
Shahjadpur | 132/33 kV transformerT2 | 2022-06-02 20:18 | 2022-06-02 23:05 | 2:47 | T | Tripped showing lockout relay | 0 | 0 | No interruption
Jhenaidah | 132/33 kV transformers T1 & T2 | 2022-06-06 06:57 | 2022-06-06 07:11 | 0:14 | T | Due to 33 kV feeder fault | 94 | 21.9333 | Power interruption
Shahjadpur | 132/33 kV transformerT3 | 2022-06-12 22:30 | 2022-06-12 23:03 | 0:33 | E/O | Due to red-hot maint at 33 kV Bus | 0 | 0 | No interruption
Ishurdi | 132/33 kV transformer T2 | 2022-06-21 02:16 | 2022-06-21 09:06 | 6:50 | E/O | Due to sparking & fire at 33 kV R-phase CT box | 25 | 170.8333 | Power interruption
Jhenaidah | 132/33 kV transformer T2 | 2022-06-21 07:18 | 2022-06-21 09:03 | 1:45 | E/O | Due to red-hot maint at 33 kV Bus | 32 | 56 | Power interruption
Bheramara | Bheramara HVDC 230 kV reactor 20DF24 | 2022-06-21 18:04 | 2022-06-21 18:04 | 0:00 | T | Tripped showing lockout relay | 0 | 0 | No interruption
Shahjadpur | 132/33 kV transformerT2 | 2022-06-22 15:15 | 2022-06-22 16:32 | 1:17 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Jassore | 132/33 kV transformer T1 | 2022-06-23 00:04 | 2022-06-23 01:56 | 1:52 | E/O | Due to red-hot maint | 2 | 3.7333 | Power interruption
| 132/33 kV transformer T2 | 2022-06-23 02:03 | 2022-06-23 03:03 | 1:00 | E/O | Due to red-hot maint at 33 kV Bus | 0 | 0 | No interruption
Benapole | 132/33 kV transformers T1 & T2 | 2022-06-25 18:38 | 2022-06-25 18:48 | 0:10 | T | Tripped showing E/F relay | 0 | 0 | No interruption
Shahjadpur | 132/33 kV transformer T3 | 2022-06-26 12:43 | 2022-06-26 14:19 | 1:36 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Jassore | 132/33 kV transformer T2 | 2022-06-28 17:38 | 2022-06-28 19:01 | 1:23 | E/O | Due to red-hot maint | 0 | 0 | No interruption
|  |  | Total : | 19:27 |  |  |  | 252.5
Bogura Grid Circle:
Purbasadipur | 132/33 kV transformer T1 | 2022-06-01 20:16 | 2022-06-01 20:30 | 0:14 | T | Tripped showing O/C relay | 55 | 12.8333 | Power interruption
| 132/33 kV transformer T1 | 2022-06-01 23:03 | 2022-06-01 23:15 | 0:12 | T |  | 60 | 12 | Power interruption
Bogura | 132/33 kV transformers T3 & T4 | 2022-06-06 07:17 | 2022-06-06 10:42 | 3:25 | T | Due to 33 kV Bus coupler flashing | 60 | 205 | Power interruption
Jaldhaka | 132/33 kV transformer T2 | 2022-06-06 13:48 | 2022-06-06 15:00 | 1:12 | E/O | Due to red-hot maint | 17 | 20.4 | Power interruption
Palashbari | 132/33 kV transformer T1 | 2022-06-08 06:40 | 2022-06-08 08:35 | 1:55 | E/O | Due to red-hot maint at 33 kV Bus | 0 | 0 | No interruption
Naogaon | 132/33 kV transformer T1 | 2022-06-10 00:20 | 2022-06-10 03:20 | 3:00 | E/O | Due to red-hot maint at 33 kV Bus | 30 | 90 | Power interruption
Jaldhaka | 132/33 kV transformer T2 | 2022-06-10 22:56 | 2022-06-11 00:12 | 1:16 | E/O | Due to red-hot maint | 20 | 25.3333 | Power interruption
Mohastangar | 132/33 kV transformer T2 | 2022-06-11 07:13 | 2022-06-11 07:13 | 0:00 | E/O | Due to red-hot maint by PBS | 0 | 0 | No interruption
Rajshahi(N) | 132/33 kV transformer T2 | 2022-06-13 23:37 | 2022-06-14 02:25 | 2:48 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Thaurgaon | 132/33 kV transformer T2 | 2022-06-14 23:11 | 2022-06-14 23:25 | 0:14 | T | Due to 33 kV feeder fault | 0 | 0 | No interruption
Rajshahi(N) | 132/33 kV transformer T2 | 2022-06-15 05:40 | 2022-06-15 05:55 | 0:15 | T | Due to 33 kV feeder fault | 106 | 26.5 | Power interruption
Thakurgaon | 132/33 kV transformer T2 | 2022-06-15 07:05 | 2022-06-15 07:13 | 0:08 | T | Due to 33 kV feeder fault | 0 | 0 | No interruption
Rajshahi(O) | 132/33 kV transformer T3 | 2022-06-16 07:04 | 2022-06-16 09:34 | 2:30 | T | Due to red-hot maint at 33 kV Bus | 40 | 100 | Power interruption
Purbasadipur | 33 kV full Bus | 2022-06-18 06:10 | 2022-06-18 12:30 | 6:20 | T | Due to red-hot maint by PDB | 50 | 316.6667 | Power interruption
Sirajganj | 132/33 kV transformers T1 | 2022-06-19 16:11 | 2022-06-19 18:40 | 2:29 | E/O | Due to auxiliary transformer burst | 0 | 0 | No interruption
| 132/33 kV transformers T2 | 2022-06-19 16:11 | 2022-06-19 16:50 | 0:39 | E/O |  | 0 | 0 | No interruption
| 132/33 kV transformer T3 | 2022-06-19 22:26 | 2022-06-19 22:45 | 0:19 | T | Due to 33 kV feeder fault | 30 | 9.5 | Power interruption
Barapukuria | 132/33 kV transformer T4 with 33 kV Bus | 2022-06-22 15:15 | 2022-06-22 17:40 | 2:25 | T | Due to red-hot maint by NESCO | 0 | 0 | No interruption
Naogaon | 132/33 kV transformer T2 | 2022-06-22 08:34 | 2022-06-22 11:13 | 2:39 | T | Due to red-hot maint by PBS | 0 | 0 | No interruption
Bogura | 132/33 kV transformer T4 | 2022-06-23 19:59 | 2022-06-23 20:45 | 0:46 | T | Due to 33 kV feeder fault | 0 | 0 | No interruption
| 132/33 kV transformers T3 & T4 | 2022-06-24 15:36 | 2022-06-24 17:13 | 1:37 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Rajshahi(O) | 132/33 kV transformer T3 | 2022-06-26 15:26 | 2022-06-26 16:44 | 1:18 | T | Due to red-hot maint at 33 kV Bus | 35 | 45.5 | Power interruption
Barapukuria | 132/33 kV transformer T3 | 2022-06-26 17:16 | 2022-06-26 17:59 | 0:43 | E/O | Due to red-hot maint at 33 kV | 10 | 7.1667 | Power interruption
Noapara | 132/33 kV transformer T4 | 2022-06-27 08:33 | 2022-06-27 09:41 | 1:08 | E/O | Due to red-hot maint | 20 | 22.6667 | Power interruption
|  |  | Total : | 37:32 |  |  |  | 893.5667
Others :Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0:00
Total outage period of Sub-station Equipment : |  |  |  | 192:07 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-24
Page: 1/2 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: june2022
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Tongi | Tongi-Tongi new 132 kV Ckt-1 | 2022-06-01 11:49 | 2022-06-01 12:10 | 0:21 | T | Tripped showing Dist. relay | 50 | 17.5 | Power interruption
Tangail | Tangail-RPCL 132 kV Ckt-1 | 2022-06-06 20:59 | 2022-06-06 21:26 | 0:27 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
| Tangail-RPCL 132 kV Ckt-2 | 2022-06-06 20:59 | 2022-06-06 21:25 | 0:26 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Mymensingh | Mymensingh-Bhaluka 132 kV Ckt-1 | 2022-06-06 21:56 | 2022-06-06 22:19 | 0:23 | T | Tripped showing Dist. relay
| Mymensingh-Bhaluka 132 kV Ckt-2 | 2022-06-06 21:56 | 2022-06-06 22:27 | 0:31 | T |  | 126 | 65.1 | Power interruption
Tangail | Tangail-RPCL 132 kV Ckt-1 | 2022-06-08 01:28 | 2022-06-08 01:40 | 0:12 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Mymensingh | Mymensingh-Jamalpur 132 kV Ckt-1 | 2022-06-08 01:31 | 2022-06-08 02:34 | 1:03 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Kodda | Kodda-Rajendrapur 132 kV Ckt-2 | 2022-06-08 08:46 | 2022-06-08 09:16 | 0:30 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
| Kodda-Rajendrapur 132 kV Ckt-2 | 2022-06-17 15:12 | 2022-06-17 16:06 | 0:54 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Tangail | Tangail-Kaliakoir 132 kV Ckt-1 & 2 | 2022-06-17 15:10 | 2022-06-17 15:31 | 0:21 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Mymensingh | Mymensingh-Kishoreganj 132 kV Ckt-2 | 2022-06-18 15:39 | 2022-06-18 15:45 | 0:06 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Tongi(N) | Tongi(N)-Tongi 132 kV Ckt-2 | 2022-06-19 17:55 | 2022-06-19 18:13 | 0:18 | E/O | Tripped showing CB fail | 0 | 0 | No interruption
Kabirpur | Kabirpur-Kodda 132 kV Ckt-2 | 2022-06-22 10:09 | 2022-06-22 10:32 | 0:23 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Mymensingh | Mymensingh-Kishoreganj 132 kV Ckt-2 | 2022-06-26 12:55 | 2022-06-26 12:58 | 0:03 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
|  |  | Total : | 5:58 |  | Unserved Energy: |  | 82.6
Dhaka (South) Grid Circle :
Haripur | Haripur-Bhulta 132 kV Ckt | 2022-06-07 12:48 | 2022-06-07 13:02 | 0:14 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Shyampur(N) | Shyampur(N)-Shyampur (O) 132 kV Ckt-2 | 2022-06-09 08:12 | 2022-06-09 16:07 | 7:55 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Haripur | Haripur-Narsingdi 132 kV Ckt | 2022-06-09 12:01 | 2022-06-09 12:30 | 0:29 | T | Tripped showing Dist. relay | 50 | 24.1667 | Power interruption
Ghorashal | Ghorashal-Ashuganj 132 kV Ckt-2 | 2022-06-09 23:30 | 2022-06-09 23:30 | 0:00 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Rampura | Rampura-Bashundhara 132 kV Ckt-1 | 2022-06-12 11:53 | 2022-06-12 12:10 | 0:17 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Bashundhara | Bashundhara -Purbachal 132 kV Ckt | 2022-06-12 11:53 | 2022-06-12 12:10 | 0:17 | T |  | 0 | 0 | No interruption
Keraniganj | Keraniganj-Nawabganj 132 kV Ckt-2 | 2022-06-16 17:00 | 2022-06-16 17:46 | 0:46 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Rampura | Rampura-Bashundhara 132 kV Ckt-1 | 2022-06-18 09:25 | 2022-06-18 09:34 | 0:09 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Keraniganj | Keraniganj-Nawabganj 132 kV Ckt-1 & 2 | 2022-06-22 06:50 | 2022-06-22 07:03 | 0:13 | T | Tripped showing Dist. relay | 30 | 6.5 | Power interruption
Siddhirganj | Siddhirganj-Matuail 132 kV Ckt | 2022-06-25 13:48 | 2022-06-25 14:18 | 0:30 | T | Tripped showing E/F. relay | 65 | 32.5 | Power interruption
| Siddhirganj-Siddhirganj peaking 132 kV Ckt | 2022-06-25 13:48 | 2022-06-25 14:05 | 0:17 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Keraniganj | Keraniganj-Nawabganj 132 kV Ckt-1 & 2 | 2022-06-27 02:09 | 2022-06-27 04:11 | 2:02 | T | Tripped showing O/C. relay | 45 | 91.5 | Power interruption
|  |  | Total : | 13:09 |  | Unserved Energy: |  | 154.6667
Chattogram Grid Circle :
Hathazari | Hathazari-Kaptai 132 kV Ckt-1 | 2022-06-02 09:22 | 2022-06-02 17:56 | 8:34 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Halishahar | Halishahar-Juldah 132 kV Ckt | 2022-06-03 11:06 | 2022-06-03 11:24 | 0:18 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-Madunaghat 132 kV Ckt-1 | 2022-06-03 11:06 | 2022-06-03 11:24 | 0:18 | T | Tripped showing O/C & E/F relay. | 0 | 0 | No interruption
Khulshi | Khulshi-Madunaghat 132 kV Ckt-2 | 2022-06-03 11:06 | 2022-06-03 11:25 | 0:19 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Baraulia | Baraulia-Khulshi 132 kV Ckt-2 | 2022-06-04 22:49 | 2022-06-04 22:49 | 0:00 | T | Tripped showing O/C relay. | 0 | 0 | No interruption
Sholoshahar | Sholoshahar-Madunaghat 132 kV Ckt-1 | 2022-06-08 00:49 | 2022-06-08 00:59 | 0:10 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'sbazar 132 kV Ckt-1 | 2022-06-13 22:02 | 2022-06-13 22:43 | 0:41 | T | Tripped showing Dist. relay | 45 | 30.75 | Power interruption
Kaptai | Kaptai-Hathazari 132 kV Ckt-1 & 2 | 2022-06-18 14:48 | 2022-06-18 14:56 | 0:08 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Halishahar | Halishahar-Khulshi 132 kV Ckt-3 | 2022-06-25 08:25 | 2022-06-25 10:40 | 2:15 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Madunaghat | Madunaghat-Sholoshahar 132 kV Ckt | 2022-06-27 00:45 | 2022-06-27 05:00 | 4:15 | E/O | Due to Oil leakage | 0 | 0 | No interruption
|  |  | Total : | 16:58 |  | Unserved Energy: |  | 30.75
Cumilla Grid Circle :
Sonargaon | Sonargaon-Daudkandi 132 kV Ckt-1 | 2022-06-01 14:23 | 2022-06-01 14:40 | 0:17 | T | Tripped showing Dist.& O/C & E/F relay. | 0 | 0 | No interruption
Ashuganj | Ashuganj-Ghorashal 230 kV Ckt-2 | 2022-06-12 16:18 | 2022-06-12 17:00 | 0:42 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Sreemongal | Sreemongal-Fenchuganj 132 kV Ckt-1 & 2 | 2022-06-14 14:32 | 2022-06-14 14:45 | 0:13 | T | Tripped showing Dist.& O/C & E/F relay. | 0 | 0 | No interruption
Rangamati | Rangamati-Kagrachari 132 k Ckt-1 | 2022-06-15 15:35 | 2022-06-15 15:51 | 0:16 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Sunamganj | Sunamganj-Chatak 132 kV Ckt-1 | 2022-06-15 12:15 | 2022-06-15 12:21 | 0:06 | T | Due to VT fail fuse relay | 0 | 0 | No interruption
Sonargaon | Sonargaon-Daudkandi 132 kV Ckt-1 | 2022-06-15 15:44 | 2022-06-15 15:53 | 0:09 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Feni | Feni-Chaddogram 132 kV Ckt-1 | 2022-06-15 18:32 | 2022-06-15 18:45 | 0:13 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Bibiyana | Bibiyana-Cumilla(N) 230 kV Ckt-2 | 2022-06-16 14:18 | 2022-06-16 14:29 | 0:11 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-BSRM 230 kV Ckt-1 | 2022-06-20 07:09 | 2022-06-20 09:50 | 2:41 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Shahjibazar | Shahjibazar-B.Baria 132 kV Ckt-2 | 2022-06-22 02:52 | 2022-06-22 05:24 | 2:32 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Chattak | Chattak-Sunamganj 132 kV Ckt | 2022-06-29 01:20 | 2022-06-29 01:40 | 0:20 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
|  |  | Total : | 7:40 |  | Unserved Energy: |  | 0
Khulna Grid Circle :
Rajbari | Rajbari-Bheramara 132 kV Ckt-2 | 2022-06-01 11:44 | 2022-06-01 11:59 | 0:15 | T | Tripped showing Dist. relay
Goalpara | Goalpara-NWPGCL 225 MW 132 kV Ckt | 2022-06-02 12:25 | 2022-06-02 14:20 | 1:55 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Orion rupsha P.P | Orion rupsha P.P-Bagerhat 132 kV Ckt | 2022-06-11 17:53 | 2022-06-11 18:17 | 0:24 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Barisal | Barisal-Bhandaria 132 kV Ckt | 2022-06-14 18:25 | 2022-06-14 21:22 | 2:57 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Rajbari | Rajbari-Bheramara 132 kV Ckt-2 | 2022-06-17 15:18 | 2022-06-17 15:59 | 0:41 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Barisal | Barisal-Bhola 230 kV Ckt-1 | 2022-06-18 13:52 | 2022-06-18 14:39 | 0:47 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
|  |  | Total : | 6:59 |  | Unserved Energy: |  | 0
HVDC Grid Circle :
Baghabari | Baghabari-Ishurdi 230 kV Ckt-1 | 2022-06-04 13:26 | 2022-06-04 14:33 | 1:07 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Jessore | Jessore-Jhenaidah 132 kV Ckt-1 | 2022-06-08 08:46 | 2022-06-08 11:47 | 3:01 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
| Jessore-Noapara 132 kV Ckt-1 | 2022-06-11 19:45 | 2022-06-11 20:07 | 0:22 | T | Tripped showing O/C. relay | 0 | 0 | No interruption
| Jessore-Noapara 132 kV Ckt-2 | 2022-06-11 19:45 | 2022-06-11 20:06 | 0:21 | T |  | 0 | 0 | No interruption
Jhenaidah | Jhenaidah-Magura 132 kV Ckt-2 | 2022-06-12 09:23 | 2022-06-12 10:47 | 1:24 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Bheramara | Bheramara-Bahrampur 132 kV Ckt-3 | 2022-06-12 22:35 | 2022-06-12 22:36 | 0:01 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Jhenaidah | Jhenaidah-Jessore 132 kV Ckt-1 | 2022-06-17 17:52 | 2022-06-17 18:02 | 0:10 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
| Jhenaidah-Bottail 132 kV Ckt-2 | 2022-06-17 15:44 | 2022-06-17 16:44 | 1:00 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Jessore | Jessore-Noapara 132 kV Ckt-1 | 2022-06-18 10:32 | 2022-06-18 12:12 | 1:40 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Jhenaidah(N) | Jhenaidah(N)-Jhenaidah (O) 132 kV Ckt-3 | 2022-06-27 15:11 | 2022-06-27 15:22 | 0:11 | T | Tripped showing Dir.Gen.trip relay | 0 | 0 | No interruption
| Jhenaidah(N)-HVDC 230 kV Ckt-2 | 2022-06-30 10:02 | 2022-06-30 10:43 | 0:41 | T | Tripped showing Gen.trip& lockout relay | 0 | 0 | No interruption
|  |  | Total : | 9:58 |  | Unserved Energy: |  | 0
Bogura Grid Circle:
Purbasadipur | Purbasadipur-Thakurgaon P/S 132 kV Ckt-1 & 2 | 2022-06-02 09:21 | 2022-06-02 09:34 | 0:13 | T | Due to bad weather | 90 | 19.5 | Power interruption
Sherpur | Sherpur-Bogura 132 kV Ckt 132 kV Ckt-1 | 2022-06-04 10:38 | 2022-06-04 11:05 | 0:27 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
| Sherpur-Bogura 132 kV Ckt 132 kV Ckt-2 | 2022-06-04 10:38 | 2022-06-04 11:07 | 0:29 | T |  | 0 | 0 | No interruption
Thakurgaon S/S | Thakurgaon S/S-Thakurgaon P/S 132 kV Ckt-1 | 2022-06-05 03:32 | 2022-06-05 05:15 | 1:43 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
| Thakurgaon S/S-Panchugar 132 kV Ckt | 2022-06-06 03:32 | 2022-06-06 03:54 | 0:22 | T | Tripped showing Dist. relay | 24 | 8.8 | Power interruption
Rajshahi | Rajshahi-Amnura 132 kV Ckt | 2022-06-06 07:07 | 2022-06-06 09:06 | 1:59 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Sirajganj | Sirajganj-Baghabari 132 kV Ckt | 2022-06-06 20:48 | 2022-06-06 22:24 | 1:36 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Mohastangar | Mohastangar-Palashbari 132 kV Ckt-1 | 2022-06-07 03:52 | 2022-06-07 03:52 | 0:00 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Rangpur | Rangpur-Lalmonirhat 132 kV Ckt-1 | 2022-06-08 01:58 | 2022-06-08 02:20 | 0:22 | T | Tripped showing Dist. relay | 38 | 13.9333 | Power interruption
Bogura | Bogura-Sherpur 132 kV Ckt-1 | 2022-06-11 16:34 | 2022-06-11 18:19 | 1:45 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
| Bogura-Sherpur 132 kV Ckt-2 | 2022-06-11 16:34 | 2022-06-11 17:04 | 0:30 | T |  | 0 | 0 | No interruption
Saidpur | Saidpur-Purbasdipur132 kV Ckt-2 | 2022-06-12 03:25 | 2022-06-12 04:15 | 0:50 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Mithapukur | Mithapukur-Rangpur confi.132 kV Ckt-1 | 2022-06-12 04:22 | 2022-06-12 04:56 | 0:34 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Purbasdipur | Purbasdipur-Thaurgaon 132 kV Ckt-2 | 2022-06-13 05:58 | 2022-06-13 06:56 | 0:58 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Sirajganj S/S | Sirajganj S/S-Sirajganj unit-4 132 kV Ckt | 2022-06-14 07:00 | 2022-06-14 08:40 | 1:40 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Mithapukur | Mithapukur-Rangpur confi.132 kV Ckt-1 | 2022-06-14 23:28 | 2022-06-15 18:14 | 18:46 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
| Mithapukur-Rangpur confi.132 kV Ckt-1 | 2022-06-17 05:22 | 2022-06-17 05:38 | 0:16 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Thakurgaon S/S | Thakurgaon S/S-Thakurgaon P/S 132 kV Ckt-2 | 2022-06-17 01:41 | 2022-06-17 01:56 | 0:00 | T | Tripped showing E/F. relay | 0 | 0 | No interruption
| Thakurgaon-Panchugar 132 kV Ckt | 2022-06-17 16:14 | 2022-06-17 16:27 | 0:13 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Bogura | Bogura-Naogaon 132 kV Ckt | 2022-06-19 22:30 | 2022-06-19 23:08 | 0:38 | T | Due to bad weathed around at Naogao S/S | 0 | 0 | No interruption
Naogaon | Naogaon-Santahar 132 kV Ckt | 2022-06-19 22:30 | 2022-06-19 22:50 | 0:20 | T |  | 0 | 0 | No interruption
C.nawabganj | C.nawabganj-Amnura 132 kV Ckt | 2022-06-30 15:42 | 2022-06-30 16:00 | 0:18 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
|  |  | Total : | 33:59 |  | Unserved Energy: |  | 42.2334
Others :
Ullon | Ullon-Dhanmondi 132 kV Cable -3 | 2022-06-16 03:50 | 2022-06-16 13:04 | 9:14 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Maniknagar | Maniknagar-Matuil 132 kV Ckt | 2022-06-25 13:49 | 2022-06-25 13:49 | 0:00 | T | Tripped showing E/F. relay | 0 | 0 | No interruption
|  |  | Total : | 9:14 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 103:55 | Hours
T = Tripping | [7 empty] | Executive Engineer
E/O = Emergency Outage | [7 empty] | Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-25
Page: 1/4 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: June 2022
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Tongi | 132/33 kV transformer T-2 | 2022-06-01 14:06 | 2022-06-01 15:22 | 1:16 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV transformer T-3 | 2022-06-01 16:46 | 2022-06-01 17:48 | 1:02 | S/O | Due to D/W work | 0 | 0 | No interruption
Aminbazar | 230/132 kV transformer T-03 | 2022-06-02 09:46 | 2022-06-02 15:16 | 5:30 | S/O | Due to C/M work | 0 | 0 | No interruption
Kodda | 132 kV main Bus | 2022-06-03 07:36 | 2022-06-03 07:36 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Kishoreganj | 132/33 kV transformer T-2 | 2022-06-08 12:18 | 2022-06-08 13:48 | 1:30 | S/O | Due to C/M work | 50 | 75 | Power interruption
Manikganj | 132/33 kV transformer T-4 | 2022-06-09 12:36 | 2022-06-09 12:58 | 0:22 | S/O | Due to C/M work | 0 | 0 | No interruption
Joydevpur | 132/33 kV transformers T-3 & T4 | 2022-06-10 08:19 | 2022-06-10 11:13 | 2:54 | S/O | Due to PBS work | 60 | 174 | Power interruption
Kishoreganj | 132/33 kV transformer T-1 | 2022-06-11 12:28 | 2022-06-11 12:45 | 0:17 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV transformer T-3 | 2022-06-12 15:35 | 2022-06-12 15:44 | 0:09 | S/O | Due to C/M work | 0 | 0 | No interruption
Tongi | 132 kV Bus-1 | 2022-06-14 10:25 | 2022-06-14 16:29 | 6:04 | S/O | Due to C/M work | 0 | 0 | No interruption
Savar | 132/33 kV transformer T-2 | 2022-06-15 09:04 | 2022-06-15 10:26 | 1:22 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | 230 kV Bus-1 | 2022-06-15 13:01 | 2022-06-15 15:35 | 2:34 | S/O | Due to C/M work | 0 | 0 | No interruption
Jamalpur | 132/33 kV transformer T-2 | 2022-06-18 08:28 | 2022-06-18 14:36 | 6:08 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-1 | 2022-06-19 08:30 | 2022-06-19 17:48 | 9:18 | S/O | Due to C/M work | 0 | 0 | No interruption
Bhaluka | 132/33 kV transformer T-2 | 2022-06-20 09:36 | 2022-06-20 10:02 | 0:26 | S/O | Due to D/W work | 15 | 6.5 | Power interruption
Kallyanpur | 132/33 kV transformer T-1 | 2022-06-20 08:14 | 2022-06-20 09:32 | 1:18 | S/O | Due to C/M work | 24 | 31.2 | Power interruption
Bhaluka | 132/33 kV transformer T-1 | 2022-06-20 10:10 | 2022-06-20 14:10 | 4:00 | S/O | Due to D/W work | 15 | 60 | Power interruption
Kabirpur | 132/33 kV transformer T-1 with 33 kV Bus | 2022-06-20 12:16 | 2022-06-20 13:58 | 1:42 | S/O | Due to C/M work | 80 | 136 | Power interruption
Aminbazar | 230/132 kV transformer T-02 | 2022-06-21 11:55 | 2022-06-21 21:27 | 9:32 | S/O | Due to D/W work | 0 | 0 | No interruption
Tangail | 132/33 kV transformer T-1 | 2022-06-21 10:01 | 2022-06-21 10:33 | 0:32 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV transformer T-1 | 2022-06-22 10:49 | 2022-06-22 10:57 | 0:08 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV transformer T-3 | 2022-06-22 11:12 | 2022-06-22 12:05 | 0:53 | S/O | Due to D/W work | 0 | 0 | No interruption
Kabirpur | 132 kV reserve Bus | 2022-06-23 06:13 | 2022-06-23 07:08 | 0:55 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-3 | 2022-06-23 12:25 | 2022-06-23 13:51 | 1:26 | S/O | Due to D/W work | 50 | 71.6667 | Power interruption
Netrakona | 132/33 kV transformer T-1 | 2022-06-26 10:10 | 2022-06-26 10:48 | 0:38 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV transformer T-3 | 2022-06-27 11:43 | 2022-06-27 12:13 | 0:30 | S/O | Due to C/M work |  | 0 | No interruption
| 132/33 kV transformer T-3 | 2022-06-30 11:43 | 2022-06-30 12:13 | 0:30 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 60:56 |  | Unserved Energy: |  | 554.3667
Dhaka (South) Grid Circle :
Maniknagar | 230/132 kV transformer T02 | 2022-06-03 09:40 | 2022-06-03 16:56 | 7:16 | S/O | Due to C/M work | 0 | 0 | No interruption
Haripur | 132/33 kV transformer T02 | 2022-06-06 11:58 | 2022-06-06 11:58 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Rampura | 230/132 kV transformer T02 | 2022-06-07 08:01 | 2022-06-07 08:58 | 0:57 | S/O | Due to C/M work | 0 | 0 | No interruption
Shyampur(O) | 132/33 kV transformer T-3 | 2022-06-17 09:16 | 2022-06-17 15:30 | 6:14 | S/O | Due to C/M work | 0 | 0 | No interruption
Hasnabad | 132/33 kV transformer T-1 | 2022-06-19 16:20 | 2022-06-19 16:37 | 0:17 | S/O | Due to C/M work | 0 | 0 | No interruption
Sonargaon | 132/33 kV transformer T-2 with 33 kV Bus | 2022-06-27 07:27 | 2022-06-27 10:32 | 3:05 | S/O | Due to C/M work | 20 | 61.6667 | Power interruption
|  |  | Total : | 17:49 |  | Unserved Energy: |  | 61.6667
Chattogram Grid Circle :
Bakulia | 132 kV Bus | 2022-06-02 09:46 | 2022-06-02 17:50 | 8:04 | S/O | Due to C/M work | 0 | 0 | No interruption
Hathazari | 132/33 kV transformer T-1 | 2022-06-11 15:22 | 2022-06-11 17:30 | 2:08 | S/O | Due to C/M work by PBS | 60 | 128 | Power interruption
Madunaghat | 132/33 kV transformer T-1 | 2022-06-11 16:11 | 2022-06-11 16:27 | 0:16 | S/O | Due to C/M work by 33 kV Bus | 10 | 2.6667 | Power interruption
Bakulia | 132/33 kV transformer T-3 | 2022-06-13 06:19 | 2022-06-13 08:50 | 2:31 | S/O | Due to C/M work | 20 | 50.3333 | Power interruption
Khulshi | 132/33 kV transformer T-2 | 2022-06-14 05:29 | 2022-06-14 06:54 | 1:25 | S/O | Due to C/M work | 0 | 0 | No interruption
Dohazari | 132/33 kV transformer T-2 | 2022-06-15 07:09 | 2022-06-15 07:58 | 0:49 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-1 with 33 kV Bus | 2022-06-21 08:12 | 2022-06-21 13:54 | 5:42 | S/O | Due to C/M work | 5 | 28.5 | Power interruption
| 132/33 kV transformer T-2 | 2022-06-22 07:01 | 2022-06-22 08:40 | 1:39 | S/O | Due to C/M work by PBS | 30 | 49.5 | Power interruption
Cox'sbazar | 132/33 kV transformerT2 | 2022-06-24 00:31 | 2022-06-24 02:55 | 2:24 | S/O | Due to D/W work | 60 | 144 | Power interruption
Dohazari | 132/33 kV transformer T-1 | 2022-06-24 08:35 | 2022-06-24 10:06 | 1:31 | S/O | Due to C/M work | 15 | 22.75 | Power interruption
Chanradhona | 132/33 kV transformerT2 | 2022-06-26 10:46 | 2022-06-26 16:17 | 5:31 | S/O | Due to D/W work | 0 | 0 | No interruption
Chandraghona | 132/33 kV transformer T1 | 2022-06-27 11:11 | 2022-06-27 17:46 | 6:35 | S/O | Due to D/W work | 0 | 0 | No interruption
Cox'sbazar | 132/33 kV transformers T1 & T2 | 2022-06-30 06:23 | 2022-06-30 07:35 | 1:12 | S/O | Due to C/M work | 36 | 43.2 | Power interruption
Sholohahar | 132/33 kV transformer T1 | 2022-06-30 11:51 | 2022-06-30 16:21 | 4:30 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 44:17 |  | Unserved Energy : |  | 468.95
Cumilla Grid Circle :
Barioerhat | 132/33 kV transformer T1 | 2022-06-02 10:04 | 2022-06-02 14:51 | 4:47 | S/O | Due to C/M work | 0 | 0 | No interruption
Feni | 132/33 kV transformer T1 | 2022-06-03 05:50 | 2022-06-03 05:50 | 0:00 | S/O |  | 0 | 0 | No interruption
Shahjibazar | 132/33 kV transformer T4 | 2022-06-03 08:46 | 2022-06-03 12:42 | 3:56 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer T2 | 2022-06-03 17:16 | 2022-06-03 18:02 | 0:46 | S/O | Due to maint.work | 0 | 0 | No interruption
Cumilla(N) | 132/33 kV transformer T2 | 2022-06-04 09:23 | 2022-06-04 11:47 | 2:24 | S/O | Due to C/M work | 0 | 0 | No interruption
Sunamganj | 132/33 kV transformer T1 | 2022-06-04 10:44 | 2022-06-04 18:21 | 7:37 | S/O | Due to C/M work | 0 | 0 | No interruption
Cumilla(S) | 132/33 kV transformer T4 | 2022-06-04 11:50 | 2022-06-04 13:20 | 1:30 | S/O | Due to C/M work | 0 | 0 | No interruption
Ashuganj | 400/230 kV transformer IBT1 | 2022-06-07 09:31 | 2022-06-07 13:57 | 4:26 | S/O | Due to C/M work | 0 | 0 | No interruption
Bianibazar | 132/33 kV transformer T1 | 2022-06-10 17:18 | 2022-06-10 17:54 | 0:36 | S/O | Due to C/M work | 0 | 0 | No interruption
Cumilla(N) | 132/33 kV transformer T3 | 2022-06-11 08:08 | 2022-06-11 12:16 | 4:08 | S/O | Due to D/W work | 60 | 248 | Power interruption
Chandpur | 132/33 kV transformer T2 |  | 2022-06-12 15:48 |  | S/O | Due to C/M work | 0 | 0 | No interruption
Kachua | 132/33 kV transformer T2 with 33 kV Bus | 2022-06-17 07:20 | 2022-06-17 09:18 | 1:58 | S/O | Due to maint.of 33 kV PBS feeder | 15 | 29.5 | Power interruption
Chowddagram | 132/33 kV transformer T1 with 33 kV Bus | 2022-06-17 07:36 | 2022-06-17 10:58 | 3:22 | S/O |  | 0 | 0 | No interruption
Sylhet | 132/33 kV transformer T2 |  | 2022-06-20 07:14 |  |  | After maint.work | 0 | 0 | No interruption
| 132/33 kV transformer T2 | 2022-06-21 15:57 | 2022-06-21 22:34 | 6:37 | S/O | Due to protection work | 0 | 0 | No interruption
Cumilla(N) | 132 kV reserve Bus | 2022-06-23 06:34 | 2022-06-23 09:32 | 2:58 | S/O | Due to C/M work | 55 | 163.1667 | Power interruption
Ashuganj | 132 kV Bus-2 | 2022-06-23 11:40 | 2022-06-23 13:33 | 1:53 | S/O | Due to winding tem.high | 0 | 0 | No interruption
|  |  | Total : | 46:58 |  | Unserved Energy : |  | 440.6667
Khulna Grid Circle :
Barishal(N) | 132/33 kV transformer T4 | 2022-06-01 10:49 | 2022-06-01 12:32 | 1:43 | S/O | Due to D/W work | 0 | 0 | No interruption
Gallamari | 132/33 kV transformer T2 | 2022-06-01 07:13 | 2022-06-01 07:13 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV transformer T2 | 2022-06-02 07:05 | 2022-06-02 07:05 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Shariatpur | 132/33 kV transformer T1 with 33 kV Bus | 2022-06-01 13:50 | 2022-06-01 14:34 | 0:44 | S/O | Due to D/W work | 10 | 7.3333 | Power interruption
Bagerhat | 132/33 kV transformer T-1 | 2022-06-02 08:22 | 2022-06-02 17:13 | 8:51 | S/O | Due to C/M work | 0 | 0 | No interruption
Rajbari | 132 kV Bus CB | 2022-06-02 15:34 | 2022-06-02 21:36 | 6:02 | S/O | Due to SAS work | 0 | 0 | No interruption
Gallamari | 132/33 kV transformer T2 | 2022-06-03 08:14 | 2022-06-03 17:41 | 9:27 | S/O | Due to D/W work | 0 | 0 | No interruption
Khulna© | 132/33 kV transformer T-3 | 2022-06-03 06:02 | 2022-06-03 07:59 | 1:57 | S/O | Due to C/M work | 0 | 0 | No interruption
Faripur | 132/33 kV transformer T1 | 2022-06-03 08:03 | 2022-06-03 08:03 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Rajbari | 132/33 kV transformer T-1 | 2022-06-03 08:56 | 2022-06-03 16:07 | 7:11 | S/O | Due to protection test | 0 | 0 | No interruption
Bagerhat | 132/33 kV transformer T-3 | 2022-06-03 07:38 | 2022-06-03 10:14 | 2:36 | S/O | Due to C/M work | 0 | 0 | No interruption
Gallamari | 132/33 kV transformer T2 | 2022-06-04 07:08 | 2022-06-04 07:08 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Faripur | 132 kV Bus-A | 2022-06-04 09:52 | 2022-06-04 12:09 | 2:17 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-3 | 2022-06-04 12:09 | 2022-06-04 12:09 | 0:00 | S/O | After maint.work | 0 | 0 | No interruption
Rajbari | 132/33 kV transformer T-2 | 2022-06-05 08:07 | 2022-06-05 15:12 | 7:05 | S/O | Due to D/W work | 0 | 0 | No interruption
Gallamari | 132/33 kV transformer T2 | 2022-06-06 06:02 | 2022-06-06 06:02 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Payra | 132/33 kV transformer T-3 | 2022-06-06 09:27 | 2022-06-06 13:26 | 3:59 | S/O | Due to C/M work | 0 | 0 | No interruption
Narial | 132/33 kV transformer T2 | 2022-06-06 22:16 | 2022-06-06 22:50 | 0:34 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV transformer T1 | 2022-06-07 06:14 | 2022-06-07 07:45 | 1:31 | S/O | Due to C/M work | 12 | 18.2 | Power interruption
Gallamari | 132/33 kV transformer T2 | 2022-06-07 06:20 | 2022-06-07 06:20 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV transformer T2 | 2022-06-08 06:09 | 2022-06-08 19:13 | 13:04 | S/O | Due to D/W work | 0 | 0 | No interruption
Payra | 400/132 kV transformer ATR1 | 2022-06-08 09:31 | 2022-06-08 13:55 | 4:24 | S/O | Due to C/M work | 0 | 0 | No interruption
Rajbari | 132/33 kV transformer T-1 | 2022-06-08 14:55 | 2022-06-08 16:52 | 1:57 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-2 | 2022-06-08 16:55 | 2022-06-08 18:07 | 1:12 | S/O | Due to C/M work | 0 | 0 | No interruption
Barisal(N) | 132/33 kV transformer T-5 | 2022-06-09 09:10 | 2022-06-09 15:34 | 6:24 | S/O | Due to C/M work | 0 | 0 | No interruption
Rajbari | 132/33 kV transformer T-2 | 2022-06-09 10:15 | 2022-06-09 18:05 | 7:50 | S/O | Due to C/M work | 0 | 0 | No interruption
Faripur | 132/33 kV transformer T-1 | 2022-06-09 13:45 | 2022-06-09 14:50 | 1:05 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-3 | 2022-06-10 09:19 | 2022-06-10 15:14 | 5:55 | S/O | Due to C/M work | 0 | 0 | No interruption
Rajbari | 132/33 kV transformer T-3 | 2022-06-10 09:35 | 2022-06-10 11:31 | 1:56 | S/O | Due to D/W work | 0 | 0 | No interruption
Khulna© | 132/33 kV transformer T-1 | 2022-06-12 06:27 | 2022-06-12 06:27 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Gopalganj | 132/33 kV transformer T-1 | 2022-06-14 10:52 | 2022-06-14 18:45 | 7:53 | S/O | Due to C/M work | 0 | 0 | No interruption
Khulna© | 132/33 kV transformer T-3 | 2022-06-15 08:26 | 2022-06-15 10:50 | 2:24 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-3 | 2022-06-15 08:06 | 2022-06-15 10:35 | 2:29 | S/O | Due to C/M work | 0 | 0 | No interruption
Gopalganj P/S | 132/33 kV transformer T-2 | 2022-06-15 10:52 | 2022-06-15 12:24 | 1:32 | S/O | Due to C/M work | 0 | 0 | No interruption
Payra | 400 kV Bus coupler | 2022-06-16 05:24 | 2022-06-16 05:24 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Faripur | 132/33 kV transformer T-1 | 2022-06-17 06:26 | 2022-06-17 06:26 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Gallamari | 132/33 kV transformer T1 | 2022-06-17 06:13 | 2022-06-17 06:13 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV transformer T1 | 2022-06-18 06:04 | 2022-06-18 06:04 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV transformer T1 | 2022-06-19 06:12 | 2022-06-19 06:12 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV transformer T1 | 2022-06-20 06:04 | 2022-06-20 06:04 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Matarbari | 132/33 kV transformer T-1 | 2022-06-18 11:15 | 2022-06-18 15:45 | 4:30 | S/O | Due to C/M work | 0 | 0 | No interruption
Khulna© | 132/33 kV transformer T-3 | 2022-06-22 06:50 | 2022-06-22 09:25 | 2:35 | S/O | Due to maint.work | 0 | 0 | No interruption
Gollamari | 132/33 kV transformer T-1 | 2022-06-22 09:31 | 2022-06-22 18:29 | 8:58 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV transformer T-1 | 2022-06-23 06:02 | 2022-06-23 06:02 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Gopalganj(O) | 132/33 kV transformer T-1 | 2022-06-23 10:47 | 2022-06-23 14:15 | 3:28 | S/O | Due to C/M work | 0 | 0 | No interruption
Gallamari | 132/33 kV transformer T1 | 2022-06-24 06:03 | 2022-06-24 06:03 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Payra | 132/33 kV transformer AT-R1 | 2022-06-26 16:05 | 2022-06-26 16:05 | 0:00 | S/O | Due to fire protection work | 0 | 0 | No interruption
Gallamari | 132/33 kV transformer T1 | 2022-06-26 06:09 | 2022-06-26 06:09 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV transformer T1 | 2022-06-27 06:12 | 2022-06-27 06:12 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Barishal(S) | 132/33 kV transformer T-1 | 2022-06-27 18:32 | 2022-06-27 19:14 | 0:42 | S/O | Due to C/M work | 27 | 18.9 | Power interruption
Gallamari | 132/33 kV transformer T1 | 2022-06-28 12:44 | 2022-06-28 19:08 | 6:24 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV transformer T1 | 2022-06-29 09:07 | 2022-06-29 18:14 | 9:07 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV transformer T1 | 2022-06-30 06:13 | 2022-06-30 06:13 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 147:46 |  | Unserved Energy : |  | 44.4333
HVDC Grid Circle
Bottail | 132/33 kV transformer T1 | 2022-06-02 07:05 | 2022-06-02 09:44 | 2:39 | S/O | Due to C/M work | 40 | 106 | Power interruption
Bheramara GK | 132/33 kV transformer T3 | 2022-06-02 08:20 | 2022-06-02 15:20 | 7:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Bheramara HVDC | 230 kV 20DF13 | 2022-06-05 10:15 | 2022-06-05 15:03 | 4:48 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV transformer T2 | 2022-06-08 06:12 | 2022-06-08 06:12 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Shahjadpur | 132/33 kV transformer T1 | 2022-06-11 10:55 | 2022-06-11 14:45 | 3:50 | S/O | Due to D/W work | 0 | 0 | No interruption
Bheramara GK | 132/33 kV transformer T3 | 2022-06-12 09:05 | 2022-06-12 16:30 | 7:25 | S/O | Due to C/M work | 0 | 0 | No interruption
HVDC | HVDC filter 20DF22 | 2022-06-22 11:40 | 2022-06-23 01:21 | 13:41 | S/O | Due to C/M work | 0 | 0 | No interruption
Kustia | 132/33 kV transformer T2 | 2022-06-24 07:11 | 2022-06-24 07:11 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Bheramara GK | 132/33 kV transformer T2 | 2022-06-28 10:23 | 2022-06-28 12:16 | 1:53 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 41:16 |  | Unserved Energy : |  | 106
Bogura Grid Circle:
Thakurgaon | 132/33 kV transformerT1 | 2022-06-01 06:48 | 2022-06-01 08:06 | 1:18 | S/O | Due to C/M work | 0 | 0 | No interruption
Bogura | 230/132 kV transformer T02 | 2022-06-05 09:31 | 2022-06-05 14:12 | 4:41 | S/O | Due to C/M work | 0 | 0 | No interruption
Jaldhaka | 132/33 kV transformer T2 with 33 kV Bus | 2022-06-05 21:20 | 2022-06-05 22:15 | 0:55 | S/O | Due to 33 kV feeder fault | 25 | 22.9167 | Power interruption
Natore | 132/33 kV transformer T1 | 2022-06-07 12:55 | 2022-06-07 13:10 | 0:15 | S/O | Due to C/M work | 0 | 0 | No interruption
Barapukuria | 230/132 kV transformer T6 | 2022-06-09 09:20 | 2022-06-09 14:14 | 4:54 | S/O | Due to C/M work | 0 | 0 | No interruption
Rajshahi | 132/33 kV transformer T2 | 2022-06-11 16:49 | 2022-06-11 20:13 | 3:24 | S/O | Due to C/M work by PBS | 0 | 0 | No interruption
Sherpur(Bogura) | 132/33 kV transformer T2 | 2022-06-13 07:26 | 2022-06-13 07:26 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer T1 | 2022-06-14 07:33 | 2022-06-14 10:39 | 3:06 | S/O | Due to C/M work | 0 | 0 | No interruption
Rangpur | 132/33 kV transformer T3 | 2022-06-14 08:26 | 2022-06-14 10:50 | 2:24 | S/O | Due to C/M work | 25 | 60 | Power interruption
Jaldhaka | 132/33 kV transformer T2 with 33 kV Bus | 2022-06-16 08:57 | 2022-06-16 10:18 | 1:21 | S/O | Due to C/M work | 13 | 17.55 | Power interruption
Natore | 132/33 kV transformer T4 | 2022-06-19 10:12 | 2022-06-19 18:40 | 8:28 | S/O | Due to C/M work | 0 | 0 | No interruption
C.nawabganj | 132/33 kV transformer T4 | 2022-06-19 20:14 | 2022-06-19 20:48 | 0:34 | S/O | Due to smoke generated from bushing. | 0 | 0 | No interruption
Rajshahi | 230 kV Bus-1 | 2022-06-20 09:16 | 2022-06-20 11:56 | 2:40 | S/O | Due to D/W work | 0 | 0 | No interruption
Bogura | 230/132 kV transformer T1 | 2022-06-20 08:36 | 2022-06-20 10:46 | 2:10 | S/O | Due to C/M work | 0 | 0 | No interruption
| 230/132 kV transformer T2 | 2022-06-20 12:34 | 2022-06-20 13:26 | 0:52 | S/O | Due to C/M work | 0 | 0 | No interruption
Sirajganj | 13233 kV transformer T4 |  | 2022-06-24 17:00 |  | S/O | After maint.work | 0 | 0 | No interruption
Bogura(O) | 132/33 kV transformer T1 with 33 kV Bus | 2022-06-24 09:43 | 2022-06-24 11:06 | 1:23 | S/O | Due to C/M work | 0 | 0 | No interruption
Sherpur(Bogura) | 132/33 kV transformer T2 | 2022-06-24 09:16 | 2022-06-24 12:00 | 2:44 | S/O | Due to C/M work | 0 | 0 | No interruption
Naogaon | 132/33 kV transformer T3 | 2022-06-24 07:15 | 2022-06-24 08:48 | 1:33 | S/O | Due to D/W work | 40 | 62 | Power interruption
| 132/33 kV transformer T3 | 2022-06-25 14:05 | 2022-06-25 15:55 | 1:50 | S/O | Due to changing work | 25 | 45.8333 | Power interruption
Natore | 132 kV main Bus | 2022-06-27 06:39 | 2022-06-27 09:01 | 2:22 | S/O | Due to replacement work | 85 | 201.1667 | Power interruption
C.nawabganj | 132/33 kV transformer T2 | 2022-06-28 12:59 | 2022-06-28 14:46 | 1:47 | S/O | Due to C/M work | 0 | 0 | No interruption
Natore | 132 kV main Bus | 2022-06-29 07:25 | 2022-06-29 09:10 | 1:45 | S/O | Due to C/M work | 85 | 148.75 | Power interruption
Niyamatput | 33 kV Bus-1 & 2 | 2022-06-30 09:15 | 2022-06-30 21:50 | 12:35 | S/O | Due to C/M work by 33 kV feeder | 55 | 692.0833 | Power interruption
|  |  | Total : | 63:01 |  | Unserved Energy : |  | 1250.3
Others :Nil
|  |  | Total | 0:00 |  | Unserved Energy : |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 422:03 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-26
Page: 1/5 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: June2022
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Tongi | Tongi-Uttara 3rd phase 132 kV Ckt | 2022-06-01 10:54 | 2022-06-01 12:19 | 1:25 | S/O | Due to D/W work | 0 | 0 | No interruption
| Tongi-Uttara 3rd phase 132 kV Ckt | 2022-06-07 11:48 | 2022-06-07 16:23 | 4:35 | S/O | Due to C/M work | 0 | 0 | No interruption
| Tongi-Uttara 3rd phase 132 kV Ckt | 2022-06-08 11:52 | 2022-06-08 22:37 | 10:45 | S/O | Due to C/M work | 0 | 0 | No interruption
Kallyanpur | Kallyanpur-Lalbagh 132 kV Ckt-1 | 2022-06-11 08:49 | 2022-06-11 14:47 | 5:58 | S/O | Due to C/M work | 0 | 0 | No interruption
| Tongi-Uttara 3rd phase 132 kV Ckt | 2022-06-12 09:01 | 2022-06-12 16:42 | 7:41 | S/O | Due to D/W work | 0 | 0 | No interruption
| Tongi-Bashundhara 132 kV Ckt-1 | 2022-06-13 10:52 | 2022-06-13 14:22 | 3:30 | S/O | Due to C/M work | 0 | 0 | No interruption
| Tongi-Bashundhara 132 kV Ckt-2 | 2022-06-14 14:24 | 2022-06-14 16:10 | 1:46 | S/O | Due to D/W work | 0 | 0 | No interruption
| Tongi-Tongi (N) 132 kV Ckt-1 | 2022-06-14 10:25 | 2022-06-14 16:31 | 6:06 | S/O | Due to C/M work | 0 | 0 | No interruption
Savar | Savar-Manikganj 132 kV Ckt-1 | 2022-06-15 06:29 | 2022-06-15 08:56 | 2:27 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Meghnaghat 230 kV Ckt-1 | 2022-06-15 09:14 | 2022-06-15 16:58 | 7:44 | S/O | Due to C/M work | 0 | 0 | No interruption
Tongi | Tongi-Uttara 3rd phase 132 kV Ckt | 2022-06-15 17:45 | 2022-06-15 21:09 | 3:24 | S/O | Due to CVT problem | 0 | 0 | No interruption
Aminbazar | Aminbazar-Meghnaghat 230 kV Ckt-2 | 2022-06-16 08:53 |  |  | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Kishoreganj 132 kV Ckt-2 | 2022-06-17 11:48 | 2022-06-17 12:20 | 0:32 | S/O | Due to C/M work | 0 | 0 | No interruption
| Mymensingh-Kishoreganj 132 kV Ckt-1 | 2022-06-18 11:48 | 2022-06-18 12:20 | 0:32 | S/O | Due to C/M work | 0 | 0 | No interruption
| Mymensingh-Kishoreganj 132 kV Ckt-2 | 2022-06-19 07:41 |  |  | S/O | Due to C/M work | 0 | 0 | No interruption
Tongi(N) | Tongi(N)-Tongi 132 kV Ckt-2 | 2022-06-19 10:33 | 2022-06-19 16:37 | 6:04 | S/O | Due to D/W work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kallyanpur 132 kV Ckt-1 | 2022-06-19 14:17 | 2022-06-19 16:10 | 1:53 | S/O | Due to D/W work | 0 | 0 | No interruption
| Aminbazar-Kallyanpur 132 kV Ckt-2 | 2022-06-20 10:12 | 2022-06-20 16:55 | 6:43 | S/O | Due to D/W work | 0 | 0 | No interruption
| Aminbazar-Kallyanpur 132 kV Ckt-2 | 2022-06-21 08:21 | 2022-06-21 16:12 | 7:51 | S/O | Due to D/W work | 0 | 0 | No interruption
Kodda | Kodda-joydevpur 132 kV Ckt-1 | 2022-06-24 08:10 | 2022-06-24 09:55 | 1:45 | S/O | Due to D/W work | 0 | 0 | No interruption
| Kodda-Kabirpur 132 kV Ckt-1 | 2022-06-24 12:49 | 2022-06-24 13:59 | 1:10 | S/O | Due to D/W work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Kishoreganj 132 kV Ckt-1 | 2022-06-26 08:51 | 2022-06-26 13:22 | 4:31 | S/O | Due to C/M work | 0 | 0 | No interruption
Tongi | Tongi-Uttara 3rd phase 132 kV Ckt | 2022-06-26 11:00 | 2022-06-26 13:22 | 2:22 | S/O | Due to protection work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kallyanpur 132 kV Ckt-1 | 2022-06-29 10:31 | 2022-06-29 15:19 | 4:48 | S/O | Due to D/W work | 0 | 0 | No interruption
| Aminbazar-Manikganj P/S 132 kV Ckt-1 | 2022-06-30 10:03 | 2022-06-30 13:25 | 3:22 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 96:54 |  | Unserved Energy: |  | 0
Dhaka (South) Grid Circle :
Keraniganj | Keraniganj-Hasnabad 230 kV Ckt-2 | 2022-06-05 11:00 | 2022-06-05 19:35 | 8:35 | S/O | Due to C/M work | 0 | 0 | No interruption
Maniknagar | Maniknagar-Siddhirganj 230 kV Ckt-2 |  | 2022-06-07 07:59 |  | S/O | After maint.work | 0 | 0 | No interruption
| Maniknagar-Siddhirganj 230 kV Ckt-2 | 2022-06-07 08:04 | 2022-06-11 08:26 | 96:22 | S/O | Due to D/W work | 0 | 0 | No interruption
Siddhirganj S.S | Siddhirganj S.S-Siddhirganj 335 MW 230 kVCkt | 2022-06-08 07:27 | 2022-06-08 10:57 | 3:30 | S/O | Due to C/M work | 0 | 0 | No interruption
Madanganj S/S | Madanganj S/S-Madanganj 100 MW 132 kV Ckt | 2022-06-10 01:32 | 2022-06-10 01:32 | 0:00 | S/O | Due to fire at Madanganj P/P | 0 | 0 | No interruption
Kallyanpur | Kallyanpur-Lalbag 132 kV Ckt-1 | 2022-06-10 17:28 | 2022-06-10 17:28 | 0:00 | S/O | Due to R-Q conductor detached | 0 | 0 | No interruption
Ghorashal | Ghorashal GIS-Ghorashal P/S 132 kV Ckt |  | 2022-06-10 11:08 |  | S/O | After maint.work | 0 | 0 | No interruption
Shyampur(O) | Shyampur(O)-Shyampur(New) 132 kV Ckt-2 | 2022-06-17 08:13 | 2022-06-17 15:17 | 7:04 | S/O | Due to C/M work | 0 | 0 | No interruption
Keraniganj | Keraniganj-Nawabganj 132 kV Ckt-2 | 2022-06-17 09:33 | 2022-06-17 11:09 | 1:36 | S/O | Due to C/M work | 0 | 0 | No interruption
Haripur | Haripur-Bhulta 230 kV Ckt-1 | 2022-06-17 10:07 | 2022-06-17 11:07 | 1:00 | S/O | Due to protection test | 0 | 0 | No interruption
Ghorashal | Ghorashal-Ishurdi 230 kV Ckt-1 & 2 | 2022-06-19 08:54 | 2022-06-19 18:36 | 9:42 | S/O | Due to D/W work | 0 | 0 | No interruption
| Ghorashal-Ishurdi 230 kV Ckt-1 & 2 | 2022-06-20 07:06 | 2022-06-20 07:06 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Kamrangirchar | Kamrangirchar-Keraniganj 132 kV Ckt | 2022-06-24 09:05 | 2022-06-24 18:04 | 8:59 | S/O | Due to C/M work | 0 | 0 | No interruption
Bashundhara | Bashundhara-Tongi 132 kV Ckt-1 | 2022-06-29 09:47 | 2022-06-29 11:42 | 1:55 | S/O | Due to C/M work | 0 | 0 | No interruption
Ghorashal | Ghorashal P/P-Ghoashal 230 kV GIS Ckt | 2022-06-29 12:30 | 2022-06-29 15:46 | 3:16 | S/O | Due to project work | 0 | 0 | No interruption
|  |  | Total : | 141:59 |  | Unserved Energy: |  | 0
Chattogram Grid Circle :
Chandraghona | Chandraghona-Kaptai 132 kV Ckt-1 | 2022-06-01 06:31 | 2022-06-01 09:13 | 2:42 | S/O | Due to C/M work | 0 | 0 | No interruption
Bakulia | Bakulia-Khulshi 132 kV Ckt-1 | 2022-06-02 09:21 | 2022-06-02 20:03 | 10:42 | S/O | Due to C/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Kaptai 132 kV Ckt-1 | 2022-06-02 09:22 | 2022-06-02 17:56 | 8:34 | S/O | Due to D/W work | 0 | 0 | No interruption
| Hathazari-Kaptai 132 kV Ckt-2 | 2022-06-02 10:12 | 2022-06-02 17:57 | 7:45 | S/O | Due to D/W work | 0 | 0 | No interruption
Bakulia | Bakulia-Khulshi 132 kV Ckt-1 | 2022-06-03 09:24 | 2022-06-03 20:49 | 11:25 | S/O | Due to C/M work | 0 | 0 | No interruption
Halishahar | Halishahar-Khulshi 132 kV Ckt-3 | 2022-06-04 10:53 | 2022-06-04 14:33 | 3:40 | S/O | Due to C/M work | 0 | 0 | No interruption
Baraulia | Baraulia-AKS 132 kV Ckt | 2022-06-05 00:51 | 2022-06-05 11:06 | 10:15 | S/O | Due to C/M work | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-intermidiate 230 kV Ckt-2 |  | 2022-06-09 16:27 |  |  | new connection | 0 | 0 | No interruption
Hathazari | Hathazari-Baroierhat 132 kV Ckt-2 | 2022-06-10 09:01 | 2022-06-10 16:50 | 7:49 | S/O | Due to C/M work | 0 | 0 | No interruption
| Hathazari-AKSM 230 kV Ckt | 2022-06-15 15:00 | 2022-06-15 17:08 | 2:08 | S/O | Due to B-phase PT out of order | 0 | 0 | No interruption
| Hathazari-AKSM 230 kV Ckt | 2022-06-17 09:08 | 2022-06-17 15:29 | 6:21 | S/O | Due to C/M work | 0 | 0 | No interruption
Khulshi | Khulshi-Madunaghat 132 kV Ckt | 2022-06-19 08:28 |  |  | S/O | Due to D/W work | 0 | 0 | No interruption
| Hathazari-Sikalbaha 230 kV Ckt-1 | 2022-06-22 09:54 |  |  | S/O | Due to D/W work | 0 | 0 | No interruption
Hathazari | Hathazari-Rampur 132 kV Ckt-1 | 2022-06-22 10:12 | 2022-06-22 17:41 | 7:29 | S/O | Due to D/W work | 0 | 0 | No interruption
| Hathazari-Sikalbaha 230 kV Ckt-1 | 2022-06-22 10:12 | 2022-06-22 17:29 | 7:17 | S/O | Due to D/W work | 0 | 0 | No interruption
Khulshi | Khulshi-Halishahar 132 kV Ckt-3 | 2022-06-24 08:29 | 2022-06-24 17:37 | 9:08 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 95:15 |  | Unserved Energy: |  | 0
Cumilla Grid Circle :
Kochua | Kochua-Chandpur 132 kV Ckt-1 | 2022-06-05 10:32 | 2022-06-05 15:06 | 4:34 | S/O | Due to D/W work | 0 | 0 | No interruption
Mirsoari | Mirsoari-BR Power 230 kV Ckt-2 | 2022-06-05 12:44 | 2022-06-05 12:49 | 0:05 | S/O | Due to D/W work | 0 | 0 | No interruption
Chandpur | Chandpur-Kachua 132 kV Ckt-2 | 2022-06-05 15:10 | 2022-06-05 17:32 | 2:22 | S/O | Due to D/W work | 0 | 0 | No interruption
Feni | Feni-Chaddagram 132 kV Ckt-2 | 2022-06-06 07:05 | 2022-06-06 09:55 | 2:50 | S/O | Due to C/M work | 0 | 0 | No interruption
Cumilla(S) | Cumilla(S)-Kochua 132 kV Ckt | 2022-06-06 09:51 | 2022-06-06 12:30 | 2:39 | S/O | Due to D/W work | 0 | 0 | No interruption
| Cumilla(S)-Kochua 132 kV Ckt | 2022-06-07 09:55 | 2022-06-07 20:14 | 10:19 | S/O | Due to D/W work | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Cumilla(S) 132 kV Ckt-3 | 2022-06-08 09:59 | 2022-06-08 16:24 | 6:25 | S/O | Due to D/W work | 0 | 0 | No interruption
Feni | Feni-Chowmuhani 132 kV Ckt-2 | 2022-06-08 16:16 | 2022-06-08 19:17 | 3:01 | S/O | Due to D/W work | 0 | 0 | No interruption
Mirsoari | Mirsoari-power gen.230 kV Ckt-1 | 2022-06-09 12:01 | 2022-06-09 14:48 | 2:47 | S/O | Due to D/W work | 0 | 0 | No interruption
Sreemongal | Sreemongal-Shahjibazar 132 kV Ckt-1 | 2022-06-13 19:27 | 2022-06-13 20:19 | 0:52 | S/O | Due to tree trimming | 0 | 0 | No interruption
Cumilla(S) | Cumilla(S)-Chuddagram 32 kV Ckt-1 | 2022-06-16 09:46 | 2022-06-16 15:54 | 6:08 | S/O | Due to D/W work | 0 | 0 | No interruption
Chatak | Chatak-Sylhet 132 kV Ckt-2 | 2022-06-17 00:31 | 2022-06-17 19:25 | 18:54 | S/O | Due to switchyard of Chattak under flood water | 0 | 0 | No interruption
| Chatak-Sunamganj 132 kV Ckt |  | 2022-06-17 19:35 |  | S/O | After maint.work | 0 | 0 | No interruption
Sylhet | Sylhet-Fenchuganj 132 kV Ckt | 2022-06-18 10:34 | 2022-06-19 11:10 | 24:36 | S/O | for flood level high. | 0 | 0 | No interruption
| Sylhet-Chatak 132 kV Ckt-1 |  | 2022-06-19 11:20 |  | S/O | After maint.work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV Ckt-1 | 2022-06-22 15:34 | 2022-06-22 17:41 | 2:07 | S/O | Due to removing work | 0 | 0 | No interruption
Feni | Feni-PHP 132 kV Ckt | 2022-06-30 09:32 | 2022-06-30 17:10 | 7:38 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 95:17 |  | Unserved Energy: |  | 0
Khulna Grid Circle :
Rajbari | Rajbari-Bheramara 132 kV Ckt-1 | 2022-06-01 09:02 | 2022-06-01 18:02 | 9:00 | S/O | Due to D/W work | 0 | 0 | No interruption
| Rajbari-Bheramara 132 kV Ckt-2 | 2022-06-02 06:16 | 2022-06-02 06:16 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Barisal(N) | Barisal(N)-Bhola 230 kV Ckt-1 | 2022-06-03 10:36 | 2022-06-03 11:18 | 0:42 | S/O | Due to C/M work | 0 | 0 | No interruption
| Barisal(N)-Faridpur 230 kV Ckt-1 | 2022-06-03 15:00 | 2022-06-03 15:10 | 0:10 | S/O | Due to Jumpering with Ckt-2 | 0 | 0 | No interruption
Bagerhat | Bagerhat-Mongla 132 kV Ckt | 2022-06-05 06:43 | 2022-06-05 06:43 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Faridpur | Faridpur-Rajbari 132 kV Ckt-2 | 2022-06-06 06:38 | 2022-06-06 06:38 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Goalpara | Goalpara-Khulna 225 MW P/S 132 kV Ckt | 2022-06-07 11:25 | 2022-06-07 14:32 | 3:07 | S/O | Due to C/M work | 0 | 0 | No interruption
Rajbari | Rajbari-Faridpur 132 kV Ckt-2 | 2022-06-09 10:04 | 2022-06-09 11:54 | 1:50 | S/O | Due to D/W work | 0 | 0 | No interruption
| Rajbari-Bheramara 132 kV Ckt-2 | 2022-06-09 10:05 | 2022-06-09 11:30 | 1:25 | S/O | Due to D/W work | 0 | 0 | No interruption
| Rajbari-Faridpur 132 kV Ckt-1 | 2022-06-09 11:57 | 2022-06-09 13:14 | 1:17 | S/O | Due to D/W work | 0 | 0 | No interruption
Goalpara | Goalpara-Khulna 225 MW P/S 132 kV Ckt |  | 2022-06-10 21:25 |  |  | After maint.work | 0 | 0 | No interruption
| Goalpara-Orion rupsha P.P 132 kV Ckt | 2022-06-12 08:18 | 2022-06-12 08:35 | 0:17 | S/O | Due to passing of KPCL Barge | 0 | 0 | No interruption
| Goalpara-Bagerhat 132 kV Ckt | 2022-06-12 08:25 | 2022-06-12 08:35 | 0:10 | S/O |  | 0 | 0 | No interruption
Faridpur | Faridpur-Gopalganj (N) 132 kV Ckt-1 | 2022-06-14 08:47 | 2022-06-14 12:10 | 3:23 | S/O | Due to C/M work | 0 | 0 | No interruption
Gopalganj | Gopalganj-Rampal 400 kV Ckt | 2022-06-16 05:45 | 2022-06-16 05:45 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Payra | Payra-Gopalganj 400 kV Ckt-1 | 2022-06-16 05:45 | 2022-06-16 22:46 | 17:01 | S/O | Due to high Voltage | 0 | 0 | No interruption
| Payra-Gopalganj 400 kV Ckt-1 | 2022-06-20 11:58 | 2022-06-20 13:12 | 1:14 | S/O | Due to test purpose | 0 | 0 | No interruption
Khulna(S) | Khulna(S)-Goalpara 330 MW 132 kV Ckt | 2022-06-21 15:56 | 2022-06-21 16:46 | 0:50 | S/O | Due to C/M work | 0 | 0 | No interruption
Payra | Payra-Gopalganj 400 kV Ckt-1 |  | 2022-06-20 13:55 |  | S/O | Due to high Voltage | 0 | 0 | No interruption
Gopalganj | Gopalganj-Rampal 400 kV Ckt-2 |  | 2022-06-26 13:22 |  | S/O | Due to new connection | 0 | 0 | No interruption
| Gopalganj-Rampal 400 kV Ckt-2 | 2022-06-26 13:47 | 2022-06-26 13:47 | 0:00 | S/O | Due to high Voltage | 0 | 0 | No interruption
|  |  | Total : | 40:26 |  | Unserved Energy: |  | 0
HVDC Grid Circle :
Jhenaidah(O) | Jhenaidah(O)-Jhenaidah(N) 132 kV Ckt-2 |  | 2022-06-01 17:27 |  | S/O | Due to D/W work | 0 | 0 | No interruption
Bheramara HVDC | Bheramara HVDC-Bheramara 230 kV Ckt-1 | 2022-06-05 08:20 | 2022-06-05 16:11 | 7:51 | S/O | Due to C/M work | 0 | 0 | No interruption
| Bheramara HVDC-Bheramara 230 kV Ckt-2 | 2022-06-06 09:11 | 2022-06-06 16:01 | 6:50 | S/O | Due to C/M work | 0 | 0 | No interruption
| Rajbari-Bheramara 132 kV Ckt-1 | 2022-06-08 12:41 | 2022-06-08 14:31 | 1:50 | S/O | Due to D/W work | 0 | 0 | No interruption
Goalpara | Goalpara-Rulsha Orion 132 kV Ckt | 2022-06-08 15:34 | 2022-06-08 16:38 | 1:04 | S/O | Due to C/M work | 0 | 0 | No interruption
Goalpara | Goalpara-Bagerhat 132 kV Ckt | 2022-06-08 15:36 | 2022-06-08 16:39 | 1:03 | S/O | Due to D/W work | 0 | 0 | No interruption
| Goalpara-Orion rupsha 132 kV Ckt | 2022-06-12 08:18 | 2022-06-12 08:25 | 0:07 | S/O | Due to passing of KPCL Barge | 0 | 0 | No interruption
| Goalpara-Bagerhat 132 kV Ckt | 2022-06-12 08:25 | 2022-06-12 08:35 | 0:10 | S/O |  | 0 | 0 | No interruption
Ishurdi | Ishurdi-Pabna 132 kV Ckt | 2022-06-23 10:11 | 2022-06-23 12:28 | 2:17 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 21:12 |  | Unserved Energy: |  | 0
Bogura Grid Circle :
Natore | Natore-Rajshahi 132 kV Ckt-1 | 2022-06-04 14:27 | 2022-06-04 14:27 | 0:00 | S/O | Due to changing work | 0 | 0 | No interruption
Saidpur | Saidpur-Purbasadipur 132 kV Ckt-1 | 2022-06-09 09:12 | 2022-06-09 16:29 | 7:17 | S/O | Due to D/W work | 0 | 0 | No interruption
Bogura | Bogura-Naogaon 132 kV Ckt-1 | 2022-06-09 12:50 | 2022-06-09 15:48 | 2:58 | S/O | Due to D/W work | 0 | 0 | No interruption
Palashbari | Palashbari-Mithapukur 132 kV CKt-1 & 2 | 2022-06-09 14:39 | 2022-06-09 15:24 | 0:45 | S/O | Due to D/W work | 0 | 0 | No interruption
Natore | Natore-Rajshahi 132 kV Ckt-1 | 2022-06-11 12:16 | 2022-06-11 14:50 | 2:34 | S/O | Due to C/M work | 0 | 0 | No interruption
Rajshahi | Rajshahi-Natore 132 kV Ckt-1 | 2022-06-12 12:34 | 2022-06-12 13:33 | 0:59 | S/O | Due to D/W work | 0 | 0 | No interruption
Naogaon | Naogaon-Joypurhat 132 kV Ckt | 2022-06-13 11:12 | 2022-06-13 12:14 | 1:02 | S/O | Due to remove rote under the line | 31 | 32.0333 | Power interruption
Rajshahi | Rajshahi-Katakhali P.P 132 kV Ckt | 2022-06-17 10:14 | 2022-06-17 14:36 | 4:22 | S/O | Due to C/M work | 0 | 0 | No interruption
Natore | Natore-Rajshahi 132 kV Ckt-2 | 2022-06-19 09:12 | 2022-06-19 09:12 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Bogura(O) | Bogura(O)-Bogura(N) 132 kV Ckt-1 | 2022-06-20 07:43 | 2022-06-20 08:12 | 0:29 | S/O | Due to C/M work | 0 | 0 | No interruption
| Bogura(O)-Bogura(N) 132 kV Ckt-2 | 2022-06-20 08:15 | 2022-06-20 08:32 | 0:17 | S/O | Due to C/M work | 0 | 0 | No interruption
Natore | Natore-Rajshahi 132 kV Ckt-2 |  | 2022-06-20 18:43 |  | S/O | After maint.work | 0 | 0 | No interruption
Sherpur | Sherpur-Sirajganj 132 kV Ckt-1 | 2022-06-24 07:11 | 2022-06-24 07:11 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Natore | Natore-Rajshahi 132 kV Ckt-2 | 2022-06-27 06:07 | 2022-06-27 06:07 | 0:00 | S/O | Due to replacement work | 0 | 0 | No interruption
| Natore-Rajshahi 132 kV Ckt-1 | 2022-06-27 07:01 | 2022-06-27 09:01 | 2:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Palashbari | Palashbari-Mithapukur 132 kV CKt-1 | 2022-06-29 08:33 | 2022-06-29 08:33 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
| Palashbari-Mithapukur 132 kV CKt-2 | 2022-06-29 08:34 | 2022-06-29 08:34 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 22:43 |  | Unserved Energy: |  | 32.0333
Others :Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 505:11 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month:June 2022
| Area | Previous Month (May' 2022) |  |  |  | Current Month (June '2022)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 27 | 3 | 37 | 67 | 31 | 2 | 52 | 85
2 | Dhaka (South) Grid Circle. | 27 | 6 | 28 | 61 | 26 | 2 | 15 | 43
3 | Chattogram Grid Circle. | 18 |  | 36 | 54 | 25 | 2 | 29 | 56
4 | Cumilla Grid Circle. | 49 | 10 | 41 | 100 | 21 | 16 | 34 | 71
5 | Khulna Grid Circle. | 20 | 11 | 54 | 85 | 9 | 12 | 72 | 93
6 | HVDC Grid Circle | 9 | 5 | 26 | 40 | 12 | 11 | 18 | 41
7 | Bogura Grid Circle. | 28 | 15 | 39 | 82 | 33 | 13 | 41 | 87
8 | Others | Total number of Total: 0; Total number of T: 2; Total number of Total: 2
9 | Total | 178 | 50 | 261 | 489 | 159 | 58 | 261 | 478
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month:June 2022
| Area | Previous Month (May' 2022) |  |  |  | Current Month (June '2022)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 574.1 |  | 435.5 | 1009.6 | 916.22 |  | 554.37 | 1470.59
2 | Dhaka (South) Grid Circle. | 284.03 | 160 | 73 | 517.03 | 281.97 |  | 61.67 | 343.64
3 | Chattogram Grid Circle. | 225.75 |  | 104.25 | 330 | 346.35 | 1.05 | 468.95 | 816.35
4 | Cumilla Grid Circle. | 145.22 | 667.94 | 403.42 | 1216.58 | 429.45 | 348.83 | 440.67 | 1218.95
5 | Khulna Grid Circle. | 48.55 | 176 | 353.1 | 577.65 | 25.63 | 127 | 44.43 | 197.06
6 | HVDC Grid Circle | 17.5 | 38.25 | 78.78 | 134.53 | 21.93 | 230.57 | 106 | 358.5
7 | Bogura Grid Circle. | 179.53 | 127.17 | 301.9833 | 608.6833 | 770.23 | 165.57 | 1282.33 | 2218.13
8 | Others | Energy unserved ( MWH ) due to Total: 0; Energy unserved ( MWH ) due to Total: 0
9 | Total | 1474.68 | 1169.36 | 1750.0333 | 4394.0733 | 2791.78 | 873.02 | 2958.42 | 6623.22
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-29
Page: 1/1 | [9 empty] | QF-LDC-29
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month:June 2022
A) Power Interruption
SL. | Name of | Total Capacity | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of the Sub-Station |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Dhaka (North) | 8801.6 | 13 | 7 | 21 | 6 | 1 | 14 | 1387.99
2 | Dhaka (South) | 5031.6 | 5 | 1 | 6 | 4 |  | 2 | 188.97
3 | Chattogram | 2042 | 10 | 8 | 18 | 5 | 2 | 11 | 785.6
4 | Khulna | 2434 | 12 | 3 | 15 | 9 | 3 | 3 | 197.07
5 | HVDC | 5954.3 | 4 | 1 | 5 | 1 |  | 4 | 358.5
6 | Bogura | 3145.6 | 14 | 7 | 21 | 4 | 1 | 16 | 2143.87
7 | Cumilla | 2981 | 18 | 3 | 21 | 2 | 6 | 13 | 1218.94
8 | Others | - | - | - | - | - | - | - | 0
| Total | 30390.1 | [6 empty] | 6280.94
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 99.92%
2 | Dhaka (South) | 99.95%
3 | Chattogram | 99.91%
4 | Khulna | 99.92%
5 | HVDC | 99.96% | [6 empty] | Executive Engineer
6 | Bogura | 99.84% | [6 empty] | Information Management Division
7 | Cumilla | 99.84% | [6 empty] | LDC, PGCB, Dhaka.

## QF-LDC-30
Page: 1/1 | [10 empty] | QF-LDC-30
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month:June 2022 | [12 empty] | 2043.54
4646.17
A) Power Interruption
SL. | Name of | Total length | No. of Section in | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of Transmission line | the Transmission |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | (Ckt-KM) | Line | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 2254.4715 | - | 2 |  | 2 | 1 | 1 | 1 | 82.6
2 | Dhaka (South) | 990.29 |  | 4 | - | 4 | 3 |  | 1 | 154.67
3 | Chattogram | 917 | - | 1 |  | 1 |  | 1 |  | 30.75
4 | Khulna | 1238.4 | - | - | - | - | - | - | - | - | -
5 | HVDC | 1325 | - | - | - | - | - | - | - | - | -
6 | Bogura | 1803.3 | - | 3 | 1 | 4 | 3 |  | 1 | 74.26
7 | Cumilla | 1648.16 | -
8 | Others | - |  | - | - | - | - | - | - | -
| Total | 10176.6215 | [7 empty] | 342.28
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 99.98%
2 | Dhaka (South) | 99.97% | [9 empty] | 5317.6567
3 | Chattogram | 99.92% | [9 empty] | 643.56
4 | Khulna | 99.98% | [9 empty] | 5961.2167
5 | Bheramara (HVDC) | 99.96% | [7 empty] | Executive Engineer
6 | Bogura | 99.91% | [7 empty] | Information Management Division
7 | Cumilla | 99.86% | [7 empty] | LDC, PGCB, Dhaka.

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month:June 2022
Type of | Power failure due to | [7 empty] | Partial |  | Total Grid failure
fault | Trouble In |  | Trouble In Grid S/S |  | Trouble In |  | Lightning in |  | Grid failure |  |  |  | Remarks
| Generation |  | Equipment |  | Transmission Line |  | Transmission Line/Thunder Storm
Period | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration
| No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min.
2022-06-01 | 17 | - | 5 | 05hr59 min | - | - | - | - | - | - | - | - | -
* Tripping of a generator is accounted in the category "Trouble in Generation ". Not all tripping cause power interruption.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-32
Page: 1/1 |  |  |  |  | QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the Systems
Month:June 2022
| Total Nos.of | Total | Unserved | Total | Remarks
Sub-station | Interruption | Duration of | Load | Unserved
|  | Interruption | (MW) | Energy
|  | Hrs./Mins. |  | (MWH)
Mymensingh | 1 | 0:10 | 170 | 28.3333 | Due to tripping of 132/33 kV transformers,T 1 & T2
Sherpur | 1 | 1:06 | 12 | 13.2 | Due to tripping of 132/33 kV transformer T-3
Kishoreganj | 1 | 2:33 | 70 | 178.5 | Due to tripping of 132/33 kV transformers,T 1 & T2
Tangail | 2 | 1:30 | 90 | 135 | Due to red-hot maint 132/33 kV Transformer T2
|  | 1:18 | 70 | 91 | Due to red-hot maint 132/33 kV Transformer T2
Mymensingh | 2 | 0:15 | 120 | 30 | Due to tripping of 33 kV feeder fault
|  | 1:19 | 40 | 52.6667 | Due to red-hot maint 132/33 kV Transformer T1
Kishoreganj |  | 1:29 | 90 | 133.5 | Due to red-hot maint 132/33 kV Transformers T1 & T2
Kabirpur | 1 | 0:59 | 50 | 49.1667 | Due to tripping of all 132/33 kV transformers
Netrakona | 1 | 1:20 | 10 | 13.3333 | Due to red-hot maint 132/33 kV Transformer T2
Kabirpur | 1 | 0:31 | 150 | 77.5 | Due to tripping of 132/33 kV transformers,T 1 & T2
Kodda | 2 | 1:20 | 20 | 26.6667 | Due to red-hot maint 132/33 kV Transformer T3
|  | 0:15 | 19 | 4.75 | Due to tripping of 132/33 kV transformer T-2
Tongi | 1 | 0:21 | 50 | 17.5 | Due to tripping of Tongi-Tongi new 132 kV Ckt-1
Mymensingh | 1 | 0:31 | 126 | 65.1 | Due to tripping of Mymensingh -Bhaluka132 kV Ckt-1 & 2
Kishoreganj | 1 | 1:30 | 50 | 75 | Due to S/D of 132/33 kV transformer T-2
Joydevpur | 1 | 2:54 | 60 | 174 | Due to S/D of 132/33 kV transformers T-3 & T4
Bhaluka | 1 | 0:26 | 15 | 6.5 | Due to S/D of 132/33 kV transformer T2
Kallyanpur | 1 | 1:18 | 24 | 31.2 | Due to S/D of 132/33 kV transformer T-1
Bhaluka | 1 | 4:00 | 15 | 60 | Due to S/D of 132/33 kV transformer T-1
Kabirpur | 1 | 1:42 | 80 | 136 | Due to S/D of 132/33 kV transformer T-1
|  | 1:26 | 50 | 71.6667 | Due to S/D of 132/33 kV transformer T3
Sonargaon | 1 | 0:17 | 60 | 17 | Due to 33 kV feeder fault
Sreenagar | 1 | 2:35 | 14 | 36.1667 | Due to red-hot maint 132/33 kV Transformer T1
Bhulta | 1 | 0:16 | 248 | 66.1333 | Due to tripping of 132/33 kV transformers T-1 ,& T 2
Hasnabad |  | 0:15 | 19 | 4.75 | Due to tripping of 132/33 kV transformer T-2
| 2 | 0:13 | 15 | 3.25 | Due to tripping of 132/33 kV transformer T2
Haripur |  | 0:29 | 50 | 24.1667 | Due to tripping of Haripur-Narsingdi 132 kV Ckt
Keraniganj | 2 | 0:13 | 30 | 6.5 | Due to tripping Keraniganj-Nawabganj 132 kV Ckt-1 & 2
Siddhirganj |  | 0:30 | 65 | 32.5 | Due to tripping Siddhirganj-Matuail 132 kV Ckt
Keraniganj | 1 | 2:02 | 45 | 91.5 | Due to tripping of Keraniganj-Nawabganj 132 kV Ckt-1 & 2
Sonargaon | 1 | 3:05 | 20 | 61.6667 | Due to S/D of 132/33 kV transformer T-2
Madunaghat | 1 | 0:58 | 42 | 40.6 | Due to tripping of 132/33 kV transformers T1 & T2
Cox'sbazar | 2 | 0:05 | 20 | 1.6667 | Due to 33 kV feeder fault
|  | 0:03 | 48 | 2.4
Madunaghat |  | 1:24 | 8 | 11.2 | Due to tripping 132/33 kV transformer T2
Cox'sbazar | 1 | 0:58 | 30 | 29 | Due to red-hot maint of 132/33 kV Transformer T3
Matarbari |  | 0:21 | 3 | 1.05 | Due to 33 kV feeder fault
Dohazari |  | 0:28 | 55 | 25.6667 | Due to tripping 132/33 kV transformer T1
Cox'sbazar |  | 1:13 | 5 | 6.0833 | Due to red-hot maint of 132/33 kV Transformer T2
Sikalbaha |  | 1:37 | 15 | 1.75 | Due to red-hot maint of 132/33 kV Transformer T4
Bakulia | 1 | 1:37 | 122 | 197.2333 | Due to tripping 132/33 kV transformer T2
Dohazari |  | 0:41 | 45 | 30.75 | Due to tripping of Dohazari-Cox'sbazar 132 kV Ckt-1
Hathazari |  | 2:08 | 60 | 128 | Due to S/D of 132/33 kV transformer T-1
Madunaghat | 2 | 0:16 | 10 | 2.6667
Bakulia |  | 2:31 | 20 | 50.3333 | Due to S/D of 132/33 kV transformer T-3
Dohazari | 2 | 5:42 | 5 | 28.5 | Due to S/D of 132/33 kV transformer T-1
|  | 1:39 | 30 | 49.5 | Due to S/D of 132/33 kV transformer T-2
Cox'sbazar | 1 | 2:24 | 60 | 144
Dohazari | 1 | 1:31 | 15 | 22.75 | Due to S/D of 132/33 kV transformer T-1
Cox'sbazar |  | 1:12 | 36 | 43.2 | Due to S/D of 132/33 kV transformersT-1 & T2
Baroierhat |  | 1:04 | 20 | 21.3333 | Due to red-hot maint of 132/33 kV Transformer T1
Shahijibazar | 1 | 6:22 | 50 | 318.3333 | Due to 33 kV feeder fault
Feni | 1 | 1:32 | 20 | 30.6667 | Due to red-hot maint of 132/33 kV Transformer T1
Kachua | 1 | 0:37 | 25 | 15.4167 | Due to red-hot maint of 132/33 kV Transformers T1 & T2
Sunamganj | 1 | 0:47 | 10 | 7.8333 | Due to red-hot maint of 132/33 kV Transformer T1
Baroierhat | 1 | 1:45 | 20 | 35
Shahijibazar | 1 | 0:47 | 16 | 12.5333 | Due to 33 kV feeder fault
Baroierhat |  | 1:55 | 26 | 49.8333 | Due to red-hot maint of 132/33 kV Transformer T1
Sunamganj | 1 | 1:37 | 25 | 40.4167 | Due to 33 kV feeder fault
Chatak | 1 | 0:38 | 5 | 3.1667
Page: 2/2 |  |  |  |  | QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the Systems
Month:June 2022
| Total Nos.of | Total | Unserved | Total | Remarks
Sub-station | Interruption | Duration of | Load | Unserved
|  | Interruption | (MW) | Energy
|  | Hrs./Mins. |  | (MWH)
Sreemongal | 1 | 0:16 | 13 | 3.4667 | Due to 33 kV feeder fault
Sreemongal | 1 | 1:13 | 14 | 17.0333
Ramganj | 1 | 0:54 | 30 | 27 | Due to red-hot maint of 132/33 kV Transformer T2
Chowmuhani | 1 | 3:15 | 30 | 97.5 | Due to red-hot maint of 132/33 kV Transformer T1
Sylhet | 1 | 7:39 | 30 | 27.5 | Due to tripping of 132/33 kV transformerT-1
Cumilla(S) | 1 | 0:21 | 20 | 7 | Due to 33 kV feeder fault
Kulaura | 1 | 1:30 | 15 | 27.5 | Due to red-hot maint of 132/33 kV Transformer T1
Shahijibazar | 1 | 0:49 | 45 | 36.75 | Due to red-hot maint of 132/33 kV Transformer T4
Cumilla(N) | 1 | 4:08 | 60 | 248 | Due to S/D of 132/33 kV transformer T-3
Kachua | 2 | 1:58 | 15 | 29.5 | Due to S/D of 132/33 kV transformer T-2
Cumilla(N) | 2 | 2:58 | 55 | 163.1667 | Due to 132 kV reserve Bus
Mongla | 1 | 0:59 | 10 | 9.8333 | Due to red-hot maint of 132/33 kV Transformer T1
Khulna© | 1 | 0:09 | 60 | 9 | Due to tripping of 132/33 kV transformers T2 & T3
Mongla | 1 | 0:19 | 28 | 8.8667 | Due to tripping of 132/33 kV transformers T1 & T2
Shariatpur | 1 | 0:22 | 56 | 20.5333 | Due to 33 kV feeder fault
Khulna© | 1 | 0:30 | 25 | 12.5 | Due to 33 kV feeder fault
Barishal(N) | 1 | 0:06 | 41 | 4.1 | Due to tripping of 132/33 kV transformers T4 & T5
Gallamari | 1 | 0:21 | 26 | 9.1 | Due to 33 kV feeder fault
Bhandaria | 1 | 0:14 | 28 | 6.5333 | Due to tripping of 132/33 kV transformers T1 & T2
Mongla | 1 | 0:10 | 36 | 6 | Due to tripping of 132/33 kV transformers T1 & T2
Barishal(N) | 1 | 0:15 | 110 | 27.5 | Due to 33 kV feeder fault
Noapara | 1 | 1:08 | 20 | 22.6667 | Due to red-hot maint of 132/33 kV Transformer T4
Rajbari | 1 | 1:36 | 10 | 16 | Due to red-hot maint of 132/33 kV Transformer T1
Shariatpur | 1 | 0:44 | 10 | 7.3333 | Due to S/D of 132/33 kV transformer T-1
Narial | 1 | 1:31 | 12 | 18.2 | Due to S/D of 132/33 kV transformer T-1
Barishal(S) | 1 | 0:42 | 27 | 18.9 | Due to S/D of 132/33 kV transformer T-1
Jhenaidah | 1 | 0:14 | 94 | 21.9333 | Due to 33 kV feeder fault
Ishurdi | 1 | 6:50 | 25 | 170.8333 | Due to tripping of 132/33 kV transformer T2
Jhenaidah | 1 | 1:45 | 32 | 56
Jassore | 1 | 1:52 | 2 | 3.7333 | Due to red-hot maint of 132/33 kV Transformer T2
Bottail | 1 | 2:39 | 40 | 106 | Due to S/D of 132/33 kV transformer T-1
Purbasadipur | 2 | 0:14 | 55 | 12.8333 | Due to tripping of 132/33 kV transformer T1
|  | 0:12 | 60 | 12
Bogura | 1 | 3:25 | 60 | 205 | Due to tripping of 132/33 kV transformers T3 & T4
Jaldhaka | 1 | 1:12 | 17 | 20.4 | Due to red-hot maint of 132/33 kV Transformer T2
Naogaon | 1 | 3:00 | 30 | 90 | Due to red-hot maint of 132/33 kV Transformer T1
Jaldhaka | 1 | 1:16 | 20 | 25.3333 | Due to red-hot maint of 132/33 kV Transformer T2
Rajshahi(N) | 1 | 0:15 | 106 | 26.5 | Due to 33 kV feeder fault
Rajshahi(O) | 1 | 2:30 | 40 | 100 | Due to red-hot maint of 132/33 kV Transformer T3
Purbasadipur | 1 | 6:20 | 50 | 316.6667 | Due to red-hot maint of 33 kV full Bus
Sirajganj | 1 | 0:19 | 30 | 9.5 | Due to 33 kV feeder fault
Rajshahi(O) | 1 | 1:18 | 35 | 45.5 | Due to red-hot maint of 132/33 kV Transformer T3
Barapukuria | 1 | 0:43 | 10 | 7.1667
Noapara | 1 | 1:08 | 20 | 22.6667 | Due to red-hot maint of 132/33 kV Transformer T4
Purbasadipur | 1 | 0:13 | 90 | 19.5 | Due to tripping of Purbasadipur-Thakurgaon P/S 132 kV Ckt-1 & 2
Thakurgaon S/S | 1 | 0:22 | 24 | 8.8 | Due to tripping of Thakurgaon S/S-Panchugar 132 kV Ckt
Rangpur | 1 | 0:22 | 38 | 13.9333 | Due to tripping of Rangpur-Lalmonirhat 132 kV Ckt-1
Jaldhaka | 1 | 0:55 | 25 | 22.9167 | Due to S/D of 132/33 kV transformer T-2
Rangpur | 1 | 2:24 | 25 | 60 | Due to S/D of 132/33 kV transformer T-3
Jaldhaka | 1 | 1:21 | 13 | 17.55 | Due to S/D of 132/33 kV transformer T-2
Naogaon | 2 | 1:33 | 40 | 62 | Due to S/D of 132/33 kV transformer T-3
|  | 1:50 | 25 | 45.8333
Natore | 2 | 2:22 | 85 | 201.1667 | Due to S/D of 132 kV main Bus
|  | 1:45 | 85 | 148.75
Niyamatput | 1 | 12:35 | 55 | 692.0833 | Due to S/D of 33 kV Bus
Naogaon | 1 | 1:02 | 31 | 32.0333 | Due to S/D of Naogaon-Joypurhat 132 kV Ckt
| Total Unserved energy : |  |  | 6623.2167 | MWH
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-33
Page: 1/3 |  |  |  | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month: June '2022
Sl. No | Name of the Sub-station | MW | Date and Time | Remarks
1 | AKS | 24 | 2022-06-27 06:00
2 | AKSML | 173 | 2022-06-16 18:00
3 | Aftabnagar | 35 | 2022-06-13 19:00
4 | Agargaon | 104 | 2022-06-13 13:00
5 | Agrabad | 96 | 2022-06-15 14:00
6 | Amnura | 56 | 2022-06-12 22:00
7 | Ashuganj | 48 | 2022-06-18 19:30
8 | BSRM | 169 | 2022-06-15 18:00
9 | Bagerhat | 117 | 2022-06-13 21:00
10 | Bakulia | 134 | 2022-06-07 19:30
11 | Banani | 62 | 2022-06-27 15:00
12 | Bangabhaban | 24 | 2022-06-05 10:00
13 | Barapukuria | 55 | 2022-06-01 22:00
14 | Barguna | 24 | 2022-06-12 23:00
15 | Barishal | 130 | 2022-06-13 19:30
16 | Barishal-230 | 80 | 2022-06-27 22:00
17 | Baroaulia | 82 | 2022-06-08 12:00
18 | Baroirhat | 79 | 2022-06-02 19:00
19 | Bashundhara | 189 | 2022-06-07 15:00
20 | BashundharaCement | 13 | 2022-06-01 15:00
21 | Beanibazar | 73 | 2022-06-27 19:00
22 | Benapole | 76 | 2022-06-02 22:00
23 | Bhaluka | 162 | 2022-06-26 19:30
24 | Bhandaria | 64 | 2022-06-06 22:00
25 | Bhangura | 38 | 2022-06-05 19:30
26 | Bheramara(GK) | 67 | 2022-06-28 21:00
27 | Bhulta | 267 | 2022-06-30 00:00
28 | Bog-Sherpur | 68 | 2022-06-28 20:00
29 | Bogura | 177 | 2022-06-11 23:00
30 | Borhanuddin | 48 | 2022-06-13 04:00
31 | Brahmanbaria | 184 | 2022-06-06 21:00
32 | Cantonment | 170 | 2022-06-13 13:00
33 | Chandpur | 79 | 2022-06-06 22:00
34 | Chandraghona | 36 | 2022-06-02 19:00
35 | Chapai | 88 | 2022-06-11 21:00
36 | Charsaidpur | 48 | 2022-06-30 00:00
37 | Chauddagram | 63 | 2022-06-02 23:00
38 | Chhatak | 35 | 2022-06-30 18:30
39 | Chowmuhani | 218 | 2022-06-08 23:00
40 | Chuadanga | 114 | 2022-06-28 21:00
41 | Coxsbazar | 121 | 2022-06-28 20:00
42 | Cumilla(N) | 174 | 2022-06-11 19:30
43 | Cumilla(S) | 188 | 2022-06-08 21:00
44 | Daudkandi | 158 | 2022-06-11 22:00
45 | Dhaka | 110 | 2022-06-16 12:00
46 | Dhamrai | 132 | 2022-06-11 15:00
47 | Dhanmondi | 185 | 2022-06-06 12:00
48 | Dohazari | 104 | 2022-06-26 20:00
49 | Faridpur | 160 | 2022-06-09 00:00
50 | Fatullah | 76 | 2022-06-07 16:00
51 | Fenchuganj | 49 | 2022-06-01 20:00
52 | Feni | 129 | 2022-06-26 19:30
53 | GPH | 99 | 2022-06-14 13:00
Page: 2/3 |  |  |  | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month: June '2022
Sl. No | Name of the Sub-station | MW | Date and Time | Remarks
54 | Ghorashal | 140 | 2022-06-26 10:00
56 | Goalpara | 34 | 2022-06-14 23:00
57 | Gollamari | 66 | 2022-06-12 07:00
58 | Gopalganj | 112.4 | 2022-06-13 22:00
59 | Gulshan | 136 | 2022-06-07 13:00
60 | Halishahar | 107 | 2022-06-05 11:00
61 | HaripurSBU | 143 | 2022-06-26 11:00
62 | Hasnabad | 108 | 2022-06-28 17:00
63 | Hathazari | 104 | 2022-06-06 21:00
64 | Ishurdi | 84 | 2022-06-05 21:00
65 | Jaldhaka | 71 | 2022-06-01 22:00
66 | Jamalpur | 160 | 2022-06-24 19:30
67 | Jashore | 139 | 2022-06-11 19:30
68 | Jhenaidah | 128 | 2022-06-06 21:00
69 | Joydebpur | 208 | 2022-06-13 16:00
70 | Joypurhat | 67 | 2022-06-15 21:00
71 | Juldah | 30 | 2022-06-29 09:00
72 | KSRM | 45.7 | 2022-06-28 14:00
73 | Kabirpur | 300 | 2022-06-08 12:00
74 | Kachua | 82 | 2022-06-06 22:00
75 | Kallyanpur | 123 | 2022-06-13 19:00
76 | Kalurghat | 37 | 2022-06-13 13:00
77 | Kamrangirchar | 97 | 2022-06-15 18:00
78 | Kaptai | 5 | 2022-06-05 19:00
79 | Kazla | 91 | 2022-06-04 10:00
80 | Keranigonj | 90 | 2022-06-11 23:00
81 | Khagrachori | 32 | 2022-06-10 19:30
82 | Khulna | 127 | 2022-06-13 19:00
83 | Khulshi | 210 | 2022-06-27 16:00
84 | Kishoreganj | 148 | 2022-06-09 00:00
85 | Kodda | 343 | 2022-06-07 15:00
86 | Kulaura | 50 | 2022-06-27 23:00
87 | Kurigram | 70 | 2022-06-08 23:00
88 | Kushtia | 152 | 2022-06-01 20:00
89 | Lalbag | 99 | 2022-06-14 13:00
90 | Lalmonirhat | 55 | 2022-06-01 20:00
91 | Madanganj | 204 | 2022-06-07 19:30
92 | Madaripur | 117 | 2022-06-12 22:00
93 | Madartek | 93 | 2022-06-08 21:00
94 | Madunaghat | 77 | 2022-06-11 17:00
95 | Magura | 64 | 2022-06-07 21:00
96 | Mahasthangarh | 74 | 2022-06-12 00:00
97 | Manikganj | 92 | 2022-06-08 22:00
98 | Maniknagar | 91 | 2022-06-13 13:00
99 | Matarbari | 127 | 2022-06-05 15:00
100 | Matuail | 68 | 2022-06-12 11:00
101 | Millgate | 68 | 2022-06-20 15:00
101 | Mirpur | 149.5 | 2022-06-08 19:00
102 | Mirsorai | N/A | N/A
Page: 3/3 |  |  |  | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month: June '2022
Sl. No | Name of the Sub-station | MW | Date and Time | Remarks
103 | Mithapukur | 42 | 2022-06-01 19:00
104 | Modern | 0 | 2022-06-01 00:00
105 | Mogbazar | 142 | 2022-06-06 17:00
106 | Mongla | 44 | 2022-06-25 11:00
107 | Motijheel | 43 | 2022-06-13 17:00
108 | Munshiganj | 113 | 2022-06-05 23:00
109 | Mymensingh | 239 | 2022-06-02 22:00
110 | Naogaon | 128 | 2022-06-14 21:00
111 | Narail | 59 | 2022-06-07 19:30
112 | Narinda | 80 | 2022-06-08 15:00
113 | Narshingdi | 193 | 2022-06-06 22:00
114 | Natore | 156 | 2022-06-11 22:00
115 | Nawabganj | 59 | 2022-06-08 23:00
116 | Netrakona | 129 | 2022-06-01 21:00
117 | New | 92.2 | 2022-06-01 17:00
118 | Niamatpur | 83 | 2022-06-03 22:00
119 | Noapara | 60 | 2022-06-08 23:00
120 | PHP | 10 | 2022-06-11 15:00
121 | Pabna | 120 | 2022-06-06 19:30
122 | Palashbari | 130 | 2022-06-01 20:00
123 | Panchagarh | 63 | 2022-06-01 19:30
124 | Patuakhali | 149 | 2022-06-05 02:00
125 | Payra | 2.5 | 2022-06-27 17:00
126 | Postogola | N/A | N/A
127 | Purbachal | 20 | 2022-06-05 19:00
128 | Purbasadipur | 130 | 2022-06-11 23:00
129 | Rahanpur_I | N/A | N/A
130 | Rahim | 35 | 2022-06-19 05:00
131 | Rajbari | 74 | 2022-06-04 19:30
132 | Rajendrapur | 122 | 2022-06-26 21:00
133 | Rajshahi | 182 | 2022-06-12 20:00
134 | Rajshahi-230 | 130 | 2022-06-11 03:00
135 | Ramganj | 124 | 2022-06-06 22:00
136 | Rampur | 23 | 2022-06-26 20:00
137 | Rangamati | 34 | 2022-06-18 06:00
138 | Rangpur | 155 | 2022-06-01 21:00
139 | Ruppur | 5.2 | 2022-06-27 11:00
140 | SSM | 22 | 2022-06-10 02:00
141 | Saidpur | 112 | 2022-06-02 20:00
142 | Satkhira | 138 | 2022-06-13 23:00
143 | Satmasjid | 109 | 2022-06-27 19:30
144 | Savar | 205 | 2022-06-23 16:00
145 | Shahjadpur | 111 | 2022-06-26 21:00
146 | Shahjibazar | 122 | 2022-06-06 21:00
147 | Shahmirpur | 50.5 | 2022-06-16 01:00
148 | Shariatpur | 84 | 2022-06-07 22:00
148 | Sherpur | 144 | 2022-06-01 21:00
148 | Shikalbaha | 38 | 2022-06-07 03:00
148 | Shikalbaha-230 | N/A | N/A
148 | Shitalakhya | 129 | 2022-06-13 12:00
148 | Sholosohor | N/A | N/A
148 | Shyampur | 188 | 2022-06-07 10:00
148 | Siddhirganj | 134 | 2022-06-08 15:00
148 | Sirajganj | 118 | 2022-06-15 21:00
148 | Sonargaon | 109 | 2022-06-08 01:00
148 | Sreemongol | 73 | 2022-06-01 19:00
148 | Srinagar | 47.3 | 2022-06-05 22:00
148 | Sunamganj | 56 | 2022-06-01 22:00
148 | Sylhet | 157 | 2022-06-01 19:00
148 | TK | 31.5 | 2022-06-06 22:00
148 | Tangail | 225 | 2022-06-10 22:00
148 | Thakurgaon | 101 | 2022-06-11 20:00
148 | Tongi | 147 | 2022-06-06 18:30
148 | Ullon | 135 | 2022-06-11 13:00
148 | Uttara | 105 | 2022-06-13 13:00
148 | UttaraNew | 30 | 2022-06-13 12:00
148 | Zigatola | 49 | 2022-06-08 20:00
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID COMPANY OF BANGLADESH LTD. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month:June 2022
Area | MW | Date | Hour | Remarks
Dhaka | 5340.15 | 2022-06-06 | 16:00
Chattogram | 1478.9 | 2022-07-06 | 19:00
Cumilla | 1371 | 2022-06-06 | 22:00
Mymensingh | 1108 | 2022-01-06 | 21:00
Sylhet | 574 | 2022-01-06 | 21:00
Khulna | 1763.4 | 2022-11-06 | 23:00
Barishal | 444 | 2022-08-06 | 22:00
Rajshahi | 1481.6 | 2022-03-06 | 23:00
Rangpur | 939 | 2022-01-06 | 20:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-35
| Page: 1/3 |  |  |  |  | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: June '2022
Sl | Substation name | base_kv | Max_kV | date_time | Min_kV | date_time
1 | Bhulta 400/230kV Grid Sub-Station | 400 | 404 | 2022-06-27 05:00 | 365 | 2022-06-07 12:00
2 | Bibiana 400/230kV Sub-Station | 400 | 416 | 2022-06-17 16:00 | 399 | 2022-06-16 12:00
3 | BIPTC | 400 | 407 | 2022-06-18 06:00 | 387 | 2022-06-12 23:00
4 | Gopalganj_I 400/132kV Grid Sub-Station | 400 | 423 | 2022-06-16 08:00 | 389 | 2022-06-21 22:00
5 | Kaliakoir 400/230/132kV Grid Sub-Station | 400 | 399 | 2022-06-24 14:00 | 378 | 2022-06-21 12:00
6 | Agargaon 230/132kV Grid Sub-Station | 230 | 233 | 2022-06-03 17:00 | 211 | 2022-06-13 11:00
7 | AKSML 230/33kV Grid Sub-Station | 230 | 241 | 2022-06-26 01:00 | 212 | 2022-06-17 10:00
8 | Aminbazar 230/132kV Grid Sub-Station | 230 | 231 | 2022-06-17 16:00 | 214 | 2022-06-13 09:00
9 | Baghabari 230/132kV Grid Sub-Station | 230 | 235 | 2022-06-04 18:00 | 223 | 2022-06-03 23:00
10 | Barapukuria 230/132/33kV Grid Sub-Station | 230 | 233 | 2022-06-13 07:00 | 209 | 2022-06-04
11 | Barishal 230/132kV Grid Sub-Station | 230 | 245 | 2022-06-10 09:00 | 222 | 2022-06-25 23:00
12 | Bheramara 230/132kV Grid Sub-Station | 230 | 257 | 2022-06-30 10:00 | 220 | 2022-06-11 19:30
13 | Bogura 230/132kV Grid Sub-Station | 230 | 235 | 2022-06-17 17:00 | 216 | 2022-06-01 21:00
14 | BSRM 230/33kV Grid Sub-Station | 230 | 237 | 2022-06-27 07:00 | 218 | 2022-06-17 10:00
15 | Cumilla(N) 230/132/33kV Grid Sub-Station | 230 | 233 | 2022-06-06 08:00 | 218 | 2022-06-13 12:00
16 | Fenchuganj 230/132/33kV Grid Sub-Station | 230 | 248 | 2022-06-17 15:00 | 234 | 2022-06-27 15:00
17 | GPH 230/33kV Grid Sub-Station | 230 | 238 | 2022-06-14 18:30 | 217 | 2022-06-17 11:00
18 | Haripur 230/132kV Grid Sub-Station | 230 | 231 | 2022-06-17 17:00 | 212 | 2022-06-13 12:00
19 | Hasnabad 230/132kV Grid Sub-Station | 230 | 230 | 2022-06-17 15:00 | 212 | 2022-06-13 12:00
20 | Hathazari 230/132/33kV Grid Sub-Station | 230 | 241 | 2022-06-15 17:00 | 217 | 2022-06-17 10:00
21 | Ishurdi 230/132kV Grid Sub-Station | 230 | 238 | 2022-06-17 17:00 | 213 | 2022-06-23 06:00
22 | Jhenaidah 230/132kV Grid Sub-Station | 230 | 238 | 2022-06-26 17:00 | 213 | 2022-06-17 23:00
23 | Keranigonj 230/132/33kV Grid Sub-Station | 230 | 230 | 2022-06-17 19:30 | 211 | 2022-06-16 12:00
24 | Khulna(S) 230/132kV Grid Sub-Station | 230 | 244 | 2022-06-27 10:00 | 213 | 2022-06-17 23:00
25 | Maniknagar 230/132kV Grid Sub-Station | 230 | 231 | 2022-06-17 19:30 | 200 | 2022-06-09
26 | Meghnaghat 230/132kV Grid Sub-Station | 230 | 233 | 2022-06-26 05:00 | 218 | 2022-06-13 11:00
27 | Rajshahi 230/132/33kV Grid Sub-Station | 230 | 240 | 2022-06-19 20:00 | 219 | 2022-06-20 23:00
28 | Rampura 230/132kV Grid Sub-Station | 230 | 232 | 2022-06-17 17:00 | 214 | 2022-06-06 12:00
29 | Shikalbaha 230/132kV Grid Sub-Station | 230 | 240 | 2022-06-01 08:00 | 216 | 2022-06-17 11:00
30 | Shyampur 230/132kV Grid Sub-Station | 230 | 233 | 2022-06-10 17:00 | 212 | 2022-06-14 16:00
31 | Siddhirganj 230/132kV Grid Sub-Station | 230 | 234 | 2022-06-25 02:00 | 216 | 2022-06-13 12:00
32 | Sirajgonj 230 kV Switching Station | 230 | 238 | 2022-06-08 06:00 | 222 | 2022-06-18 11:00
33 | Tongi 230/132/33kV Grid Sub-Station | 230 | 235 | 2022-06-17 16:00 | 212 | 2022-06-12 15:00
34 | Aftabnagar 132/33kV Grid Sub-Station | 132 | 137 | 2022-06-09 20:00 | 124 | 2022-06-13 12:00
35 | Agrabad 132/33kV Grid Sub-Station | 132 | 141 | 2022-06-15 17:00 | 125 | 2022-06-17 11:00
36 | AKS 132/33kV Grid Sub-Station | 132 | 140 | 2022-06-15 17:00 | 127 | 2022-06-17 09:00
37 | Amnura 132/33kV Grid Sub-Station | 132 | 138 | 2022-06-21 18:30 | 118 | 2022-06-16 02:00
38 | Ashuganj 230/132/33kV Sub-Station | 132 | 142 | 2022-06-17 14:00 | 132 | 2022-06-27 15:00
39 | Bagerhat 132/33kV Grid Sub-Station | 132 | 137 | 2022-06-18 11:00 | 118 | 2022-06-17 23:00
40 | Bakulia 132/33kV Grid Sub-Station | 132 | 141 | 2022-06-01 07:00 | 127 | 2022-06-17 11:00
41 | Banani 132/33kV Grid Sub-Station | 132 | 140 | 2022-06-17 19:30 | 121 | 2022-06-13 12:00
42 | Barguna 132/33kV Grid Sub-Station | 132 | 141 | 2022-06-14 08:00 | 127 | 2022-06-01 19:00
43 | Barishal 132/33kV Grid Sub-Station | 132 | 143 | 2022-06-09 15:00 | 124 | 2022-06-01 19:00
44 | Baroaulia 132/33kV Grid Sub-Station | 132 | 142 | 2022-06-11 08:00 | 128 | 2022-06-17 11:00
45 | Baroirhat 132/33kV Grid Sub-Station | 132 | 137 | 2022-06-01 18:00 | 120 | 2022-06-12 15:00
46 | Bashundhara 132/33kV Grid Sub-Station | 132 | 140 | 2022-06-17 17:00 | 120 | 2022-06-01 09:00
47 | BashundharaCement 132/33kV Sub-Station | 132 | 138 | 2022-06-09 19:30 | 120 | 2022-06-11 17:00
48 | Beanibazar 132/33kV Grid Sub-Station | 132 | 140 | 2022-06-18 13:00 | 124 | 2022-06-11 23:00
49 | Benapole 132/33kV Grid Sub-Station | 132 | 138 | 2022-06-19 23:00 | 119 | 2022-06-27 02:00
50 | Bhaluka 132/33kV Grid Sub-Station | 132 | 138 | 2022-06-17 14:00 | 113 | 2022-06-27 01:00
51 | Bhandaria 132/33kV Grid Sub-Station | 132 | 145 | 2022-06-09 15:00 | 121 | 2022-06-13 22:00
52 | Bhangura 132/33kV Grid Sub-Station | 132 | 141 | 2022-06-17 15:00 | 130 | 2022-06-01 21:00
53 | Bheramara(GK) 132/33kV Grid Sub-Station | 132 | 140 | 2022-06-02 18:00 | 130 | 2022-06-19 12:00
54 | Bhulta 132/33kV Grid Sub-Station | 132 | 127 | 2022-06-09 12:00 | 116 | 2022-06-07 12:00
55 | Bog-Sherpur 132/33kV Grid Sub-Station | 132 | 139 | 2022-06-09 09:00 | 123 | 2022-06-01 21:00
56 | Bogura 132/33kV Grid Sub-Station | 132 | 139 | 2022-06-17 17:00 | 123 | 2022-06-01 21:00
57 | Brahmanbaria 132/33kV Grid Sub-Station | 132 | 138 | 2022-06-04 13:00 | 125 | 2022-06-28 23:00
58 | Cantonment 132/33kV GIS Grid Sub-Station | 132 | 137 | 2022-06-17 17:00 | 119 | 2022-06-07 12:00
59 | Chandpur 132/33kV Grid Sub-Station | 132 | 142 | 2022-06-01 18:00 | 118 | 2022-06-09 01:00
60 | Chandraghona 132/33kV Grid Sub-Station | 132 | 142 | 2022-06-16 13:00 | 128 | 2022-06-17 11:00
61 | Chapai 132/33kV Grid Sub-Station | 132 | 136 | 2022-06-13 19:30 | 121 | 2022-06-18 15:00
62 | Charsaidpur 132/33kV Sub-Station | 132 | 138 | 2022-06-01 03:00 | 126 | 2022-06-13 12:00
63 | Chauddagram 132/33kV Grid Sub-Station | 132 | 137 | 2022-06-01 18:00 | 120 | 2022-06-12 15:00
64 | Chhatak 132/33kV Grid Sub-Station | 132 | 139 | 2022-06-17 03:00 | 123 | 2022-06-11 19:30
65 | Chowmuhani 132/33kV Grid Sub-Station | 132 | 136 | 2022-06-04 18:00 | 113 | 2022-06-09 01:00
66 | Chuadanga 132/33kV Grid Sub-Station | 132 | 137 | 2022-06-17 17:00 | 114 | 2022-06-07 22:00
67 | Coxsbazar 132/33kV Grid Sub-Station | 132 | 134 | 2022-06-03 16:00 | 113 | 2022-06-07 23:00
68 | Cumilla(S) 132/33kV Grid Sub-Station | 132 | 138 | 2022-06-09 19:30 | 124 | 2022-06-12 15:00
69 | Daudkandi 132/33kV Grid Sub-Station | 132 | 139 | 2022-06-14 19:30 | 123 | 2022-06-23 10:00
70 | Dhaka University 132/33kV Grid Sub-Station | 132 | 138 | 2022-06-09 21:00 | 124 | 2022-06-06 15:00
71 | Dhamrai 132/33kV Grid Sub-Station | 132 | 138 | 2022-06-17 17:00 | 121 | 2022-06-07 12:00
72 | Dhanmondi 132/33kV Grid Sub-Station | 132 | 137 | 2022-06-06 04:00 | 125 | 2022-06-12 11:00
73 | Dohazari 132/33kV Grid Sub-Station | 132 | 141 | 2022-06-15 17:00 | 122 | 2022-06-17 11:00
74 | Faridpur 132/33kV Grid Sub-Station | 132 | 138 | 2022-06-17 09:00 | 125 | 2022-06-07 23:00
75 | Fatullah 132/33kV Grid Sub-Station | 132 | 137 | 2022-06-17 17:00 | 122 | 2022-06-24 14:00
76 | Feni 132/33kV Grid Sub-Station | 132 | 139 | 2022-06-23 03:00 | 121 | 2022-06-09 01:00
77 | Ghorashal 132/33kV Sub-Station | 132 | 141 | 2022-06-09 20:00 | 129 | 2022-06-18 01:00
78 | Goalpara 132/33kV Grid Sub-Station | 132 | 142 | 2022-06-19 23:00 | 125 | 2022-06-20 12:00
79 | Gollamari 132/33kV Grid Sub-Station | 132 | 140 | 2022-06-05 18:00 | 122 | 2022-06-25 23:00
80 | Gopalganj 132/33kV Grid Sub-Station | 132 | 141 | 2022-06-03 18:30 | 124 | 2022-06-25 23:00
81 | Gulshan 132/33kV Grid Sub-Station | 132 | 137 | 2022-06-09 20:00 | 123 | 2022-06-13 12:00
82 | Halishahar 132/33kV Grid Sub-Station | 132 | 141 | 2022-06-14 18:30 | 126 | 2022-06-17 11:00
83 | HaripurSBU 132/33kV Sub-Station | 132 | 136 | 2022-06-09 19:30 | 127 | 2022-06-12 12:00
84 | Hasnabad 132/33kV Grid Substation | 132 | 139 | 2022-06-17 17:00 | 128 | 2022-06-07 11:00
85 | Ishurdi 132/33kV Grid Sub-Station | 132 | 143 | 2022-06-27 13:00 | 129 | 2022-06-11 19:30
86 | Jaldhaka 132/33kV Grid Sub-Station | 132 | 140 | 2022-06-12 04:00 | 113 | 2022-06-01 21:00
87 | Jamalpur 132/33kV Grid Sub-Station | 132 | 141 | 2022-06-09 09:00 | 119 | 2022-06-28 06:00
88 | Jashore 132/33kV Grid Sub-Station | 132 | 138 | 2022-06-17 18:00 | 123 | 2022-06-04 23:00
89 | Jhenaidah 132/33kV Grid Sub-Station | 132 | 138 | 2022-06-21 18:30 | 124 | 2022-06-04 23:00
90 | Joydebpur 132/33kV Grid Sub-Station | 132 | 145 | 2022-06-17 15:00 | 129 | 2022-06-19 09:00
91 | Joypurhat 132/33kV Grid Sub-Station | 132 | 138 | 2022-06-09 07:00 | 113 | 2022-06-01 23:00
92 | Juldah 132/33kV Grid Sub-Station | 132 | 143 | 2022-06-15 17:00 | 127 | 2022-06-17 10:00
93 | Kabirpur 132/33kV Grid Sub-Station | 132 | 140 | 2022-06-17 16:00 | 119 | 2022-06-08 12:00
94 | Kachua 132/33kV Grid Sub-Station | 132 | 139 | 2022-06-09 19:30 | 119 | 2022-06-09 01:00
95 | Kallyanpur 132/33kV Grid Sub-Station | 132 | 138 | 2022-06-26 03:00 | 123 | 2022-06-13 12:00
96 | Kalurghat 132/33kV Grid Sub-Station | 132 | 142 | 2022-06-16 21:00 | 127 | 2022-06-17 11:00
97 | Kamrangirchar 132/33kV Grid Sub-Station | 132 | 139 | 2022-06-17 17:00 | 121 | 2022-06-24 16:00
98 | Kaptai 132/33kV Sub-Station | 132 | 140 | 2022-06-20 19:30 | 130 | 2022-06-07 10:00
99 | Kazla 132/33kV Grid Sub-Station | 132 | 137 | 2022-06-17 17:00 | 123 | 2022-06-06 13:00
100 | Khagrachori 132/33kV Grid Sub-Station | 132 | 141 | 2022-06-14 18:30 | 129 | 2022-06-12 15:00
101 | Khulna (C) 132/33kV Grid Sub-Station | 132 | 140 | 2022-06-05 18:00 | 122 | 2022-06-25 19:00
102 | Khulshi 132/33kV Grid Sub-Station | 132 | 140 | 2022-06-16 13:00 | 125 | 2022-06-17 11:00
103 | Kishoreganj 132/33kV Grid Sub-Station | 132 | 139 | 2022-06-23 17:00 | 119 | 2022-06-01 22:00
104 | Kodda 132/33kV Grid Sub-Station | 132 | 145 | 2022-06-17 15:00 | 120 | 2022-06-25 08:00
105 | KSRM 132/33kV Grid Sub-Station | 132 | 141 | 2022-06-14 18:30 | 128.6 | 2022-06-27 15:00
106 | Kulaura 132/33kV Grid Sub-Station | 132 | 141 | 2022-06-17 15:00 | 132 | 2022-06-08 21:00
107 | Kurigram 132/33kV Grid Sub-Station | 132 | 138 | 2022-06-12 07:00 | 113 | 2022-06-01 21:00
108 | Kushtia 132/33kV Grid Sub-Station | 132 | 138 | 2022-06-17 17:00 | 126 | 2022-06-19 19:00
109 | Lalbag 132/33kV Grid Sub-Station | 132 | 139 | 2022-06-17 17:00 | 126 | 2022-06-16 12:00
110 | Lalmonirhat 132/33kV Grid Sub-Station | 132 | 137 | 2022-06-12 07:00 | 115 | 2022-06-01 01:00
111 | Madanganj 132/33kV Grid Sub-Station | 132 | 138 | 2022-06-09 19:30 | 126 | 2022-06-13 12:00
112 | Madaripur 132/33kV Grid Sub-Station | 132 | 142 | 2022-06-09 14:00 | 127 | 2022-06-13 22:00
113 | Madartek 132/33kV Grid Sub-Station | 132 | 137 | 2022-06-09 19:30 | 123 | 2022-06-13 12:00
114 | Madunaghat 132/33kV Grid Sub-Station | 132 | 141 | 2022-06-19 13:00 | 129 | 2022-06-17 10:00
115 | Magura 132/33kV Grid Sub-Station | 132 | 138 | 2022-06-17 18:30 | 120 | 2022-06-07 23:00
116 | Mahasthangarh 132/33kV Grid Sub-Station | 132 | 137 | 2022-06-06 08:00 | 121 | 2022-06-01 21:00
117 | Manikganj 132/33kV Grid Sub-Station | 132 | 139 | 2022-06-17 15:00 | 120 | 2022-06-25 23:00
118 | Maniknagar 132/33kV Grid Sub-Station | 132 | 136 | 2022-06-17 17:00 | 123 | 2022-06-07 12:00
119 | Matarbari 132/33kV Sub-Station | 132 | 138 | 2022-06-01 14:00 | 114 | 2022-06-27 19:00
120 | Matuail 132/33kV Grid Sub-Station | 132 | 139 | 2022-06-08 22:00 | 126 | 2022-06-06 10:00
121 | Millgate Tongi 132/33kV Grid Sub-Station | 132 | 140 | 2022-06-17 15:00 | 122 | 2022-06-07 14:00
122 | Mirpur 132/33kV Grid Sub-Station | 132 | 139 | 2022-06-25 23:00 | 121 | 2022-06-13 12:00
123 | Mithapukur 132/33kV Grid Sub-Station | 132 | 139 | 2022-06-29 06:00 | 118 | 2022-06-11 19:30
124 | Modern Steel 132/11kV Grid Sub-Station | 132 | 140 | 2022-06-10 19:30 | 126 | 2022-06-17 11:00
125 | Mogbazar 132/33kV Grid Sub-Station | 132 | 139 | 2022-06-09 22:00 | 125 | 2022-06-05 15:00
126 | Mongla 132/33kV Grid Sub-Station | 132 | 137 | 2022-06-10 18:30 | 119 | 2022-06-17 23:00
127 | Motijheel 132/33kV Grid Sub-Station | 132 | 138 | 2022-06-26 07:00 | 123 | 2022-06-06 15:00
128 | Munshiganj 132/33kV Grid Sub-Station | 132 | 139 | 2022-06-09 20:00 | 127 | 2022-06-12 15:00
129 | Mymensingh 132/33kV Grid Sub-Station | 132 | 139 | 2022-06-17 14:00 | 116 | 2022-06-01 21:00
130 | Naogaon 132/33kV Grid Sub-Station | 132 | 136 | 2022-06-09 07:00 | 116 | 2022-06-04
131 | Narail 132/33kV Grid Sub-Station | 132 | 137 | 2022-06-21 18:30 | 120 | 2022-06-04 23:00
132 | Narshingdi 132/33kV Grid Sub-Station | 132 | 140 | 2022-06-27 06:00 | 118 | 2022-06-07 12:00
133 | Natore 132/33kV Grid Sub-Station | 132 | 137 | 2022-06-09 08:00 | 124 | 2022-06-01 21:00
134 | Nawabganj 132/33kV Grid Sub-Station | 132 | 140 | 2022-06-17 17:00 | 125 | 2022-06-16 12:00
135 | Netrakona 132/33kV Grid Sub-Station | 132 | 137 | 2022-06-17 13:00 | 113 | 2022-06-01 22:00
136 | New Tongi 132/33kV Grid Sub-Station | 132 | 141 | 2022-06-17 15:00 | 123 | 2022-06-08 15:00
137 | Niamatpur 132/33kV Grid Sub-Station | 132 | 137 | 2022-06-09 07:00 | 113 | 2022-06-01 21:00
138 | Noapara 132/33kV Grid Sub-Station | 132 | 139 | 2022-06-18 09:00 | 124 | 2022-06-17 23:00
139 | Pabna 132/33kV Grid Sub-Station | 132 | 138 | 2022-06-09 09:00 | 126 | 2022-06-23 12:00
140 | Palashbari 132/33kV Grid Sub-Station | 132 | 136 | 2022-06-07 03:00 | 115 | 2022-06-01 21:00
141 | Panchagarh 132/33kV Grid Sub-Station | 132 | 139 | 2022-06-05 06:00 | 113 | 2022-06-01 20:00
142 | Patuakhali 132/33kV Grid Sub-Station | 132 | 140 | 2022-06-17 09:00 | 130 | 2022-06-01 19:00
143 | PHP 132/33kV Sub-Station | 132 | 137 | 2022-06-01 18:00 | 119 | 2022-06-12 15:00
144 | Purbachal 132/33kV Grid Sub-Station | 132 | 140 | 2022-06-17 16:00 | 121 | 2022-06-08 15:00
145 | Purbasadipur 132/33kV Grid Sub-Station | 132 | 140 | 2022-06-12 04:00 | 113 | 2022-06-11 19:00
146 | Rahim Steel 132/33kV Sub-Station | 132 | 138 | 2022-06-05 17:00 | 122 | 2022-06-10 02:00
147 | Rajbari 132/33kV Grid Sub-Station | 132 | 138 | 2022-06-17 09:00 | 120 | 2022-06-03 23:00
148 | Rajendrapur 132/33kV Grid Sub-Station | 132 | 141 | 2022-06-17 15:00 | 118 | 2022-06-25 11:00
149 | Rajshahi 132/33kV Grid Sub-Station | 132 | 135 | 2022-06-09 08:00 | 120 | 2022-06-20
150 | Ramganj 132/33kV Grid Sub-Station | 132 | 137 | 2022-06-05 09:00 | 114 | 2022-06-09 01:00
151 | Rangamati 132/33kV Grid Sub-Station | 132 | 141 | 2022-06-19 13:00 | 128 | 2022-06-17 11:00
152 | Rangpur 132/33kV Grid Sub-Station | 132 | 138 | 2022-06-12 07:00 | 115 | 2022-06-01 20:00
153 | Ruppur 132/11kV Grid Sub-Station | 132 | 139 | 2022-06-17 17:00 | 129 | 2022-06-19 14:00
154 | Saidpur 132/33kV Grid Sub-Station | 132 | 138 | 2022-06-12 04:00 | 113 | 2022-06-11 19:30
155 | Satkhira 132/33kV Grid Sub-Station | 132 | 139 | 2022-06-19 23:00 | 117 | 2022-06-17 23:00
156 | Satmasjid 132/33kV Grid Sub-Station | 132 | 138 | 2022-06-17 17:00 | 120 | 2022-06-27 09:00
157 | Savar 132/33kV Grid Sub-Station | 132 | 137 | 2022-06-05 05:00 | 122 | 2022-06-13 16:00
158 | Shahjadpur 132/33kV Grid Sub-Station | 132 | 143 | 2022-06-17 17:00 | 132 | 2022-06-05 15:00
159 | Shahjibazar 132/33kV Grid Sub-Station | 132 | 142 | 2022-06-13 13:00 | 129 | 2022-06-26 23:00
160 | Shahmirpur 132/33kV Grid Sub-Station | 132 | 141 | 2022-06-03 20:00 | 126 | 2022-06-17 11:00
161 | Shariatpur 132/33kV Grid Sub-Station | 132 | 141 | 2022-06-09 14:00 | 124 | 2022-06-13 23:00
162 | Sherpur 132/33kV Grid Sub-Station | 132 | 140 | 2022-06-09 09:00 | 114 | 2022-06-24 19:00
163 | Shikalbaha 132/33kV Sub-Station | 132 | 142 | 2022-06-14 18:30 | 125 | 2022-06-17 11:00
164 | Shitalakhya 132/33kV Grid Sub-Station | 132 | 139 | 2022-06-01 04:00 | 126 | 2022-06-13 12:00
165 | Shyampur 132/33kV Grid Sub-Station | 132 | 135 | 2022-06-03 21:00 | 125 | 2022-06-12 09:00
166 | Siddhirganj 132/33kV Grid Sub-Station | 132 | 136 | 2022-06-17 18:30 | 126 | 2022-06-07 12:00
167 | Sirajganj 132/33kV Grid Sub-Station | 132 | 140 | 2022-06-17 17:00 | 125 | 2022-06-01 20:00
168 | Sonargaon 132/33kV Grid Sub-Station | 132 | 138 | 2022-06-17 17:00 | 127 | 2022-06-06 12:00
169 | Sreemongol 132/33kV Grid Sub-Station | 132 | 142 | 2022-06-17 15:00 | 132 | 2022-06-01 23:00
170 | Srinagar 132/33kV Grid Sub-Station | 132 | 140 | 2022-06-17 17:00 | 126 | 2022-06-02 17:00
171 | SSM 132/33kV Grid Sub-Station | 132 | 143 | 2022-06-11 13:00 | 129 | 2022-06-18 18:00
172 | Sunamganj 132/33kV Grid Sub-Station | 132 | 139 | 2022-06-13 06:00 | 121 | 2022-06-11 21:00
173 | Sylhet 132/33kV Grid Sub-Station | 132 | 139 | 2022-06-17 15:00 | 128 | 2022-06-11 22:00
174 | Tangail 132/33kV Grid Sub-Station | 132 | 140 | 2022-06-06 21:00 | 122 | 2022-06-08 22:00
175 | Thakurgaon 132/33kV Grid Sub-Station | 132 | 138 | 2022-06-17 17:00 | 114 | 2022-06-07 22:00
176 | TK chemical 132kV Grid Sub-Station | 132 | 142 | 2022-06-19 13:00 | 126 | 2022-06-17 11:00
177 | Ullon 132/33kV Grid Sub-Station | 132 | 137 | 2022-06-09 20:00 | 119 | 2022-06-02 13:00
178 | Uttara 132/33kV Grid Sub-Station | 132 | 136 | 2022-06-17 17:00 | 121 | 2022-06-13 16:00
179 | UttaraNew 132/33kV Grid Sub-Station | 132 | 137 | 2022-06-25 01:00 | 120 | 2022-06-13 15:00
180 | Zigatola 132/33kV Grid Sub-Station | 132 | 139 | 2022-06-17 18:00 | 121 | 2022-06-24 12:00

## QF-LDC-36
Page: 1/2 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
Month: June 2022
Name of the | Auto transformer |  | Recorded maximum load
sub-station | Name | Capacity ( MVA ) | MW | Amps ( 230kV side ) | Date | Time | Remarks
| TR1 | 225 | 46 | 127
Hasnabad | TR2 | 225 | 46 | 127 | 17.06.2022 | 16:00
| TR3 | 225 | 46 | 127
| TR1 | 225 | 190 | 540
Tongi | TR2 | 225 | 190 | 540 | 08.06.2022 | 12:00
| TR3 | 225 | 190 | 540
Haripur | TR1 | 225 | 96 | 300
| TR2 | 225 | 96 | 300 | 01.06.2022 | 04:00
| TR3 | 225 | 96 | 300
| TR1 | 225 | 207 | 582
Rampura | TR2 | 225 | 207 | 582 | 06.06.2022 | 16:00
| TR3 | 225 | 207 | 582
Keraniganj | ATR1 | 300 | 123 | 359
| ATR2 | 300 | 123 | 359 | 01.06.2022 | 16:00
| ATR3 | 300 | 123 | 359
| TR1 | 225 | 142 | 404
Aminbazar | TR2 | 225 | 142 | 404 | 30.06.2022 | 12:00
| TR3 | 225 | 150 | 422
Agargaon | TR1 | 300 | 190 | 562
| TR2 | 300 | 190 | 562 | 13.06.2022 | 13:00
Maniknagar | TR1 | 300 | 159 | 490 | 08.06.2022 | 13:00
| TR2 | 300 | 159 | 490
Cumilla (N) | TR1 | 225 | 195 | 151 | 11.06.22 | 5:00
| TR2 | 225 | 192 | 544
Fenchuganj | AT2 | 300 | 210 | 562 | 11.06.22 | 19:30
| MT1 | 150 | 96 | 256
Hathazari | MT2 | 150 | 96 | 256
| MT3 | 150 | 96 | 256 | 12.06.22 | 21:00
| MT4 | 150 | 96 | 256
| TR1 | 225 | 106 | 286
Ishurdi | TR2 | 225 | 106 | 286 | 19.06.22 | 20:00
| TR3 | 225 | 106 | 286
Khulna(S) | TR1 | 225 | 94 | 243
| TR2 | 225 | 94 | 243 | 04.06.22 | 17:00
| TR3 | 300 | 117 | 315
Bogura | TR1 | 225 | 117 | 337 | 358
| TR2 | 225 | 117 | 337 | 26.06.22 | 23:00
| TR3 | 225 | 158 | 448
Baghabari | TR1 | 300 | 172 | 500 | 24.06.22 | 21:00
| TR2 | 225 | 124 | 350
Rajshahi | ATR-01 | 300 | 133 | 362
| ATR-02 | 300 | 133 | 362 | 24.06.22 | 22:00
Barapukuria | TR1 | 225 | 189 | 890 |  |  | Due to unavailability of 230 kV side meters
| TR2 | 225 | 154 | 740 | 28.06.22 | 22:00 | 132 kV current is being provided
| TR6 | 300 | 200 | 942
Bheramara | Transformer-1 | 225 | 87 | 226
| Transformer-2 | 225 | 87 | 226 | 19.06.2022 | 19:00
Shyampur | ATR-01 | 300 | 96 | 287
| ATR-02 | 300 | 96 | 287 | 01.06.2022 | 10:00
Kaliakoir | TR1 | 300 | 138 | 420 | 11.06.2022 | 15:00
Sikalbaha | ATR-1 | 300 | 181 | 567
| ATR-2 | 300 | 181 | 567 | 12.06.2022 | 19:00
Jhenaidah | T1(230/132 kV) | 300 | 168 | 479 | 04.06.2022 | 20:00
| T2(230/132 kV) | 300 | 168 | 479
Page: 2/2 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 400/230 & 400/132 kV Transformer
Month:June 2022
Name of the | Transformer |  | Recorded maximum load |  |  |  | Remarks
sub-station | Name | Capacity ( MVA ) | MW | Amps (400 kV side) | Date | Time
Kaliakoir | TR1(400/230 kV) | 520 | 241.5 | 386 | 19.06.2022 | 9:00
| TR2(400/230 kV) | 520 | 241.5 | 386
| TR1(400/132 kV) | 325 | 308.9 | 500 | 28.06.2022 | 1:45
| TR2(400/132 kV) | 325 | 308.9 | 500
Bibiyana | ICT1(400/230 kV) | 520 | 164 | 246 | 02.05.2022 | 12:00
| ICT2(400/230kV) | 520 | 159 | 240
Bhulta | ATR1(400/230 kV) | 520 | 466 | 748 | 24.06.2022 | 12:15
| ATR2(400/230kV) | 520 | 466 | 748
Ashuganj(N) | GSUT1(400/230 kV) | 567 | 368 | 565 | 18.06.2022 | 5:58
Gopalganj | ATR1(400/138 kV) | 325 | 311 | 460 | 13.06.2022 | 1:00
| ATR2(400/138kV) | 325 | 311 | 460
Payra | GSUT1 | 270 | 622 | 900 | 13.06.2022 | 15:28
| GSUT2 | 270 | 622 | 900 | 22.06.2022 | 12:11
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.
423

## QF-LDC-37
Page: 1/2 |  |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
[6 empty] | Report on load shedding | [13 empty] | Report on load shedding
Month:June 2022 | [6 empty] | (For Evening Peak) | [7 empty] | Month:June 2022 | [6 empty] | (For Day Peak)
| Peak Hour |  | Total load shed | [12 empty] | Peak Hour |  | Total load shed
Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks | Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur
2022-06-01 | 13797 | 13797 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-06-01 | 11886 | 11886 | - | - | - | - | - | - | - | - | - | - | - | -
2022-06-02 | 13474 | 13474 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-06-02 | 11829 | 11829 | - | - | - | - | - | - | - | - | - | - | - | -
2022-06-03 | 12725 | 12725 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-06-03 | 9939 | 9939 | - | - | - | - | - | - | - | - | - | - | - | -
2022-06-04 | 13036 | 13036 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-06-04 | 10222 | 10222 | - | - | - | - | - | - | - | - | - | - | - | -
2022-06-05 | 13833 | 13833 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-06-05 | 11791 | 11791 | - | - | - | - | - | - | - | - | - | - | - | -
2022-06-06 | 14004 | 14004 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-06-06 | 11848 | 11848 | - | - | - | - | - | - | - | - | - | - | - | -
2022-06-07 | 13587 | 13587 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-06-07 | 11900 | 11900 | - | - | - | - | - | - | - | - | - | - | - | -
2022-06-08 | 13985 | 13985 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-06-08 | 12226 | 12226 | - | - | - | - | - | - | - | - | - | - | - | -
2022-06-09 | 12051 | 12051 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-06-09 | 10677 | 10677 | - | - | - | - | - | - | - | - | - | - | - | -
2022-06-10 | 12700 | 12700 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-06-10 | 9695 | 9695 | - | - | - | - | - | - | - | - | - | - | - | -
2022-06-11 | 13803 | 13803 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-06-11 | 11160 | 11160 | - | - | - | - | - | - | - | - | - | - | - | -
2022-06-12 | 13492 | 13492 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-06-12 | 11802 | 11802 | - | - | - | - | - | - | - | - | - | - | - | -
2022-06-13 | 12914 | 12914 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-06-13 | 11768 | 11768 | - | - | - | - | - | - | - | - | - | - | - | -
2022-06-14 | 13200 | 13200 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-06-14 | 11633 | 11633 | - | - | - | - | - | - | - | - | - | - | - | -
2022-06-15 | 13264 | 13264 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-06-15 | 11406 | 11406 | - | - | - | - | - | - | - | - | - | - | - | -
2022-06-16 | 12989 | 12989 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-06-16 | 11489 | 11489 | - | - | - | - | - | - | - | - | - | - | - | -
2022-06-17 | 9530 | 9530 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-06-17 | 8231 | 8231 | - | - | - | - | - | - | - | - | - | - | - | -
2022-06-18 | 11850 | 11850 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-06-18 | 9978 | 9978 | - | - | - | - | - | - | - | - | - | - | - | -
2022-06-19 | 12133 | 12133 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-06-19 | 10591 | 10591 | - | - | - | - | - | - | - | - | - | - | - | -
2022-06-20 | 12439 | 12439 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-06-20 | 10336 | 10336 | - | - | - | - | - | - | - | - | - | - | - | -
2022-06-21 | 13023 | 13023 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-06-21 | 10785 | 10785 | - | - | - | - | - | - | - | - | - | - | - | -
2022-06-22 | 13082 | 13082 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-06-22 | 11018 | 11018 | - | - | - | - | - | - | - | - | - | - | - | -
2022-06-23 | 13194 | 13194 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-06-23 | 11338 | 11338 | - | - | - | - | - | - | - | - | - | - | - | -
2022-06-24 | 12570 | 12570 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-06-24 | 9942 | 9942 | - | - | - | - | - | - | - | - | - | - | - | -
2022-06-25 | 13319 | 13319 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-06-25 | 11756 | 11756 | - | - | - | - | - | - | - | - | - | - | - | -
2022-06-26 | 13696 | 13696 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-06-26 | 11933 | 11933 | - | - | - | - | - | - | - | - | - | - | - | -
2022-06-27 | 13523 | 13523 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-06-27 | 12067 | 12067 | - | - | - | - | - | - | - | - | - | - | - | -
2022-06-28 | 13332 | 13332 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-06-28 | 11825 | 11825 | - | - | - | - | - | - | - | - | - | - | - | -
2022-06-29 | 13485 | 13485 | - | - | [10 empty] | 2022-06-29 | 11705 | 11705
2022-06-30 | 13523 | 13523 | - | - | [10 empty] | 2022-06-30 | 12067 | 12067
[15 empty] | 0 | 0 | 2
| Max. L/S | - | - | - | [10 empty] | 0 | 0 | 3
Day Peak | Min. L/S | - | - | - | [10 empty] | 0 | 0 | 4
| No. of Days | - | - | - | [10 empty] | 0 | 0 | 5
[15 empty] | 0 | 0 | 6
| Max. L/S | - | - | - | [10 empty] | 0 | 0 | 7
Full Day | Min. L/S | - | - | - | [10 empty] | 0 | 0 | 8
| No. of Days | - | [12 empty] | 0 | 0 | 9
| Average L/S | #DIV/0! | [12 empty] | 0 | 0 | 10
[15 empty] | 0 | 0 | 11
[15 empty] | 0 | 0 | 12
[15 empty] | 0 | 0 | 13
[15 empty] | 0 | 0 | 14
[15 empty] | 0 | 0 | 15
[15 empty] | 0 | 0 | 16
[15 empty] | 0 | 0 | 17
[15 empty] | 0 | 0 | 18
[15 empty] | 0 | 0 | 19
[15 empty] | 0 | 0 | 20
[15 empty] | 0 | 0 | 21
[15 empty] | 0 | 0 | 22
[15 empty] | 0 | 0 | 23
[15 empty] | 0 | 0 | 24
[15 empty] | 0 | 0 | 25
[15 empty] | 0 | 0 | 26
[15 empty] | 0 | 0 | 27
[15 empty] | 0 | 0 | 28
[15 empty] | #REF! | #REF! | 29
[15 empty] | #REF! | #REF! | 30
[15 empty] | #REF! | #REF! | 31

## QF-LDC-38
Page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month:June 2022
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 14038 | 2022-06-08 | 23:00
2 | Maximum Day Peak Genaration | MW | 12226 | 2022-06-08 | 12:00
3 | Maximum Evening Peak Demand | MW | 14038 | 2022-06-08 | 23:00
4 | Minimum Generation | MW | 8231 | 2022-06-17 | 6:00
5 | Average of the daily evening peak Genaration | MW | 13051.7667
6 | Average of the daily day peak Genaration | MW | 11161.4333
7 | Maximum load shed | MW | 0 | - | -
8 | Minimum load shed | MW | 0 | - | -
9 | Total nos. of load shed days | Day | 0
10 | Average load shed ( Avg. of the 31 days in the month) | MW/Day | 0
11 | Total Generation | MkWh | 8366.3426
12 | Total Generation by BPDB | MkWh | 1590.9771 | % of total Gen. | 19.02%
13 | Total Generation by IPP | MkWh | 2989.6147 | '' | 35.73%
14 | A) Total Generation by Generation Companies | MkWh | 2300.0203 | '' | 27.49%
| B) Total Generation by REB | MkWh | 122.8415 | " | 1.468%
| C) Total Generation by RENTAL | MkWh | 624.4748 | " | 7.464%
| D) Total Imported from India (BIPTC) | MkWh | 655.2436 | " | 7.832%
| E) Total Imported from Tripura, India (A.C) | MkWh | 83.1706 | " | 0.9941%
15 | Fuel wise Generation.
| A) Gas | MkWh | 4234.9012 | % of total Gen. | 50.62%
| B) Oil | MkWh | 2655.8969 | '' | 31.75%
| C) Hydro | MkWh | 52.8346 | '' | 0.6315%
| D) Solar | MkWh | 25.0967 | '' | 0.3%
| E) Coal | MkWh | 659.199 | '' | 7.879%
| F) BIPTC (Import from India) | MkWh | 655.2436 | '' | 7.832%
| G) A.C (Import from Tripura, India) | MkWh | 83.1706 | '' | 0.9941%
16 | Maximun of the daily total Generation . | MkWh | 300.8757 | 2022-06-08
17 | Monthly Load factor | % | 88.6952
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 47739.5303
| A) Gas | M.Taka | 4793.6924
| B) Liquid fuel | M.Taka | 33842.587
| C) Coal | M.Taka | 5164.3437
| D) BIPTC (Import from India) | M.Taka | 3341.7425
| E) Tripura(Import from India) | M.Taka | 597.1646
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 1994.1249 | 2022-06-01
| A) Gas | M.Taka | 183.9161 | 2022-06-18
| B) Liquid fuel | M.Taka | 1595.7319 | 2022-06-01
| C) Coal | M.Taka | 268.9976 | 2022-06-06
| D) BIPTC (Import from India) | M.Taka | 114.0063 | 2022-06-12
20 | Average fuel cost of per unit Generation
| A) Including Hydro & Solar | Taka/kWhR | 5.2656
| B) Excluding Hydro & Solar | Taka/kWhR | 5.3146
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 83.73 | 30/06/2022 | 06:00
b) | Actual | FT (MSL) | 89.07 | 30/06/2022 | 06:00
22 | Peak Genaration of June 2021 | MW | 13014 | 2021-06-02 | 21:00
23 | Peak Demand of June 2021 | MW | 13014 | 2021-06-02 | 21:00
24 | Maximum peak Generation recorded upto 30/06/2022 | MW | 14782 | 16/04/2022 | 21:00
25 | Maximum peak Demand recorded upto 30/06/2022 | MW | 14782 | 16/04/2022 | 21:00
26 | Maximum load shed recorded upto 30/04/2022 | MW | 1459 | 04/05/2010 | 20:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## FGMO
Power Grid Company Of Bangladesh Ltd.
NLDC, Aftabnagar, Dhaka.
Monthly status of Free Governor Mode of Operation (FGMO) Power Plants
SL | Plant Name | Owner | Installed capacity | FGMO Status
|  |  | (MW) | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
1 | Bibiana-II 341 MW CCPP (Summit) | IPP | 341 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
2 | Shahjibazar GTPP Unit 8 & 9 | BPDB | 70
3 | Sirajgonj 400 MW CCPP Unit-4 | IPP | 414 | [22 empty] | √ | √ | √ | √ | √ | √ | √ | √
4 | Sirajgonj 225MW CCPP Unit-3 | NWPGCL | 220
5 | Sirajgonj 225MW CCPP Unit-2 | NWPGCL | 220
6 | Meghnaghat CCPP(Summit) | IPP | 335 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | [6 empty] | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
7 | Ashuganj 450 MW CCPP(North) | APSCL | 360 | [19 empty] | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
8 | Ashuganj 225 MW CCPP | APSCL | 221 | [10 empty] | √ |  |  | √ | √ | [6 empty] | √ | √ | √ | √ | √ | √ | √ | √ | √
9 | Bheramara 410 MW CCPP | NWPGCL | 410
10 | Haripur 412 MW CCPP | EGCB | 412
11 | Fenchugonj CCPP Phase-1 | BPDB | 97
12 | Chandpur 150 MW CCPP | BPDB | 163
13 | Siddhirganj 2x120 MW GTPP | EGCB | 210
14 | Shikalbaha 225 MW CCPP | BPDB | 225
15 | Shikalbaha Peaking GT | BPDB | 150
16 | Shahjibazar 330 MW CCPP | BPDB | 330
17 | Ashuganj 450 MW CCPP(South) | APSCL | 360 | [11 empty] | √ | √ | √ | √ | √ |  |  |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
18 | Fenchugonj CCPP Phase-2 | BPDB | 104
19 | Bhola 225 MW CCPP | BPDB | 194
20 | Ghorasal 365 MW CCPP Unit-7 | BPDB | 365
21 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | 210
22 | Siddhirganj 335 MW CCPP | EGCB | 335
23 | Bibiyana-III 400 MW CCPP | BPDB | 400
24 | Sylhet 225 MW CCPP | BPDB | 231
25 | RPCL 210 MW CCPP | IPP | 210
26 | Khulna 225 MW CCPP | NWPGCL | 230
27 | a) Baghabari 71 MW GTPP | BPDB | 71
| b) Baghabari 100 MW GTPP | BPDB | 100
28 | Karnaphuli Hydro PP Unit: 1 | BPDB | 40
| Karnaphuli Hydro PP Unit: 2 | BPDB | 40
| Karnaphuli Hydro PP Unit: 3 | BPDB | 50
| Karnaphuli Hydro PP Unit: 4 | BPDB | 50
| Karnaphuli Hydro PP Unit: 5 | BPDB | 50
29 | a) Ghorasal Repowered CCPP Unit-3 | BPDB | 416
| b) Ghorasal Repowered CCPP Unit-4 | BPDB | 410
30 | Bibiyana South 400 MW CCPP | BPDB | 383
31 | Barapukuria 275 MW TPP Unit-3 | BPDB | 274
32 | Shajibazar 100 MW PP | BPDB | 100
33 | Payra 1320 MW Unit-1 | BCPCL | 622
34 | Kushiara 163 MW CCPP (KP) | IPP | 163
35 | Haripur 360MW CCPP(HPL) | IPP | 360
36 | Meghnaghat 450 MW CCPP(MPL) | IPP | 450
due to gas shortage