## Forecast
8 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2022-08-07 | Sunday
|  |  | Date (day): | 2022-08-07 |  | Sunday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11729.6 | MW |  |  | (b) At Evening Peak Hour : |  | 13539 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2022-08-07 | 2022-08-07 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 200 | 200 | 200 |  | 165
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 86 | 81 | 90 | 93 |  | 15 | Engine problem
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 402 | 397 | 412 | 412
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 321 | 257 | 320 | 330 | 30 |  | Gas shortage
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 225 | 225 | 225 |  | Gas shortage & GT-2 S/D
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 7 | 48 | 8 | 48 | 52 |  | Fuel shortage
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 0 | 0 | 0 | 0 |  | 102 | Under maint
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 30 | 30 | 30 | 30 |  | 25 | Engine problem
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 22 | 19 | 19 |  |  | Engine problem
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 8 | 48 | 8 | 50 | 50 |  | Fuel shortage
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 8 | 50 | 8 | 30 | 72 |  | Fuel shortage
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 35 | 54 | 35 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 50 | 128 | 50 | 132 |  | 17 | Engine problem
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 55 | 35 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 45 | 52 | 50 | 50 |  | 30 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 16 | 30 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 42 | 49 | 51 | 51
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 195 | 242 | 110 | 275 |  | 25 | Engine problem
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 284 | 250 | 284 | 16
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 0 | 96 | 97 | 96 | 4
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 100 | 93 | 100 | 0
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 97 | 149 | 90 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 88 | 105 | 105 | 105 |  | 0
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 17 | 52 | 17 | 104 |  |  | Fuel shortage
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 54 | 162 | 70 | 162
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 20 | 0 | 30 | 0
| 40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 55 | 55 | 55 | 55
|  | Dhaka area Total |  |  |  |  | 6263 | 5847 | 2097 | 3239 | 2759 | 3410 | 1380 | 1059
| 41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 100 | 100 | 100 | 80 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 16 | 25 | 25 | 25
| 43 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 13 | 0 | 20 | 0
| 44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 25 | 25 | 25 | 32 |  | 18 | Engine problem
| 45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 111 | 116 | 118 | 118 |  | 112 | Low Water Level
| 46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | S/D due to HGPI
| 47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint,Fuel conservation
| 48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 87 | 105 | 68 | 90
| 49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 26 | 34 | 26 | 26 | 72 |  | Fuel shortage
| 50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 17 | 51 | 17 | 51 | 51 |  | Fuel shortage
| 51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 56 | 33 | 56 | 56 | 44 |  | Fuel shortage
| 52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 21 | 90 | 21 | 90 |  | 10 | Engine problem
| 53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 15 | 15 | 17 | 17 |  | 5 | Engine problem
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 30 | 10 | 10
| 54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 12 | 80 | 90 | 95 |  | 13 | Engine problem
| 55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
| 56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 50 | 214 | 50 | 214 | 86
| 57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 36 | 36 | 36 | 36 |  | 18 | Engine problem
| 58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 55 | 73 | 55 | 55 | 55 |  | Fuel shortage
| 59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 20 | 100 | 20 | 100
| 60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 108 | 108 | 108 | 108 |  | 8 | Engine problem
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 774 | 1235 | 867 | 1223 | 568 | 559
| 61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 166 | 208 | 210 | 210
| 63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 320 | 320 | 310 | 330 | 30 |  | Gas shortage
| 64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 330 | 305 | 305 | 320 | 40 |  | Gas shortage
|  | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+136*1 | 284 | 284 | 0 | 0 | 0 | 0 |  |  | On test.
| 65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 31 | 41 | 39 | 39 |  | 6 | Engine problem
| 66 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 55 | 40 | 40 | 55 | 55
| 67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 122 | 122 | 128 | 132 |  | 18 | Engine problem
| 70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 24 | 38 | 32 | 40 |  | 12 | Engine problem
| 71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 137 | 129 | 142 | 142 |  | 21 | Engine problem
| 72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 34 | 34 | 34 | 34
| 73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 19 | 22 | 22
| 74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 10 | 10 | 10 | 10
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 150 | 160 | 143 | 166
| 75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 21 | 33 | 33 | 33
| 76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 16 | 43 | 8 | 43 | 9 |  | Fuel shortage
| 77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 20 | 20 |  | 5 | Engine problem
| 78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 195 | 195 | 195 | 5 |  | Fuel conservation
| 79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 114 | 17 | 114
| 80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 38 | 115 | 78 | 113
| 81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 35 | 6 | 35 | 35 |  | 19 | 33 kV feeder fault
| 82 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 75 | 75 | 71 | 71 | 44 |  | Fuel shortage
|  | Cumilla Area Total |  |  |  |  | 3193 | 3169 | 1645 | 2086 | 1946 | 2183 | 449 | 81
| 83 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 81 | 100 | 102 | 102 | 100 |  | Gas shortage
| 84 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 20 | 20 | 20
| 85 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0 |  | 8 | Under maint.
| 86 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 87 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 48 | 154 | 48 | 180 |  | 20 | Engine problem
| 88 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 48 | 106 | 49 | 79 |  | 36 | Engine problem
| 89 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 41 | 0 | 50 | 0
| 90 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 6 | 11 | 11 |  | 11 | Engine problem
|  | Mymensingh Area Total |  |  |  |  | 717 | 614 | 242 | 386 | 281.6 | 392 | 100 | 75
| 91 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 44 | 43 | 43 |  | 27 | Machine problem.
| 92 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 41 | 41 | 41 | 41 |  | 49 | Machine problem
| 93 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 110 | 110 | 110 | 110 |  | 53 | ST under maint.
| 94 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
| 95 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 33 | 53 | 33 | 53
| 96 | Fenchuganj 44MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 30 | 48 | 30 | 49
| 97 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 11 | 11
| 98 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 60 | 56 | 61 | 61
| 99 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 10 | 81 | 10 | 81
| 100 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
| 101 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 220 | 221 | 220 | 220
| 102 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Gas shortage
| 103 | Sylhet 50MW PP (EPL) |  | Gas | NENP | 27*2 | 50 | 50 | 31 | 31 | 31 | 32 | 18 |  | Gas shortage
| 104 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 8 | 16 | 8 | 16 | 9 |  | Gas shortage
| 105 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 330 | 275 | 290 | 290 |  |  | FGMO
| 106 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 380 | 402 | 400 | 400
| 107 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 9 | 10 | 10
| 108 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 0 | 0 | 0 | 0 |  | 383 | Under maint.
|  | Sylhet Area Total |  |  |  |  | 2522 | 2477 | 1306 | 1387 | 1298 | 1417 | 47 | 942
| 109 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 914 | 909 | 931 | 931
| 110 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 16 | 32 | 16 | 16 | 99 |  | Fuel shortage
| 111 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 38 | 15 | 32 |  | 22 | Engine problem
| 112 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 221 | 228 | 225 | 225 | 5 |  | Fuel conservation
| 113 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 72 | 60 | 70 |  | 39 | Engine problem
| 114 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 150 | 150 | 160 | 185 | 225 |  | Gas shortage
| 115 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 8 | 0 | 8 | 32 |  | Fuel shortage
| 116 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 96 | 60 | 96 | 4 |  | Fuel conservation
| 117 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 53 | 0 | 35 | 70 |  | Fuel shortage
| 118 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 88 | 105 | 105 | 105
| 119 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 44 | 0 | 100 | 0
|  | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
|  | Khulna Area Total |  |  |  |  | 2388 | 2384 | 1433 | 1691 | 1672 | 1703 | 451 | 61
| 120 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 16 | 64 | 64 | 64 |  |  | Line O/L
| 121 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 21 | 33 | 23 | 30 |  | 10 | Engine problem
| 122 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 85 | 88 | 88 | 88 | 106 |  | Gas shortage
|  | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
| 123 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 940 | 800 | 600 | 600 |  |  | Coal Shortage
| 124 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 220 | 187 | 225 | 220
| 125 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 150 | 90 | 150
|  | Barisal Area Total |  |  |  |  | 1958 | 1958 | 1282 | 1322 | 1090 | 1152 | 106 | 10
| 126 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 127 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 24 | 32 | 32 | 32 |  | 20 | Engine problem
| 128 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 25 | 0 | 40 |  | 31 | Engine problem
| 129 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 130 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 42 | 42 |  | 8 | Engine problem
| 131 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 32 | 32 | 32 | 32 |  | 18 | Engine problem
| 132 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 178 | 170 | 188 | 190 | 20 |  | Gas shortage
| 133 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 213 | 213 | 210 | 210 | 10
| 134 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 146 | 143 | 162 | 167 | 53 |  | Gas shortage
| 135 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 290 | 286 | 350 | 350 | 64 |  | Gas shortage
| 136 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 34 | 33 | 33 |  | 17 | Engine problem
| 137 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 19 | 21 | 21 | 21
| 138 | Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 139 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 140 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 52 | 8 | 52
| 141 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 45 | 80 | 80 | 86 |  | 18 | Engine problem
| 142 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 172 | 170 | 172 | 28
| 143 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 50 | 94 | 50 | 94 |  | 19 | Engine problem
| 144 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 55 | 95 | 55 | 95 |  | 18 | Engine problem
| 145 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 3 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2129 | 1074 | 1460 | 1450 | 1627 | 346 | 149
| 146 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
| 147 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 200 | 240 | 250 | 250 | 24 |  | Coal Shortage
| 148 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
| 149 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
| 150 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 56 | 91 | 56 | 92 |  | 21 | Engine problem
| 151 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 6 | 0 | 8 | 0
| 152 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 34 | 90 | 52 | 90 |  | 25 | Fuel shortage
|  | Rangpur Area Total |  |  |  |  | 800 | 720 | 296 | 421 | 366 | 432 | 149 | 131
|  | Total |  |  |  |  | 22482 | 21680 | 10149 | 13227 | 11729.6 | 13539 | 3596 | 3067
| A. |  | 2022-08-07 | (Yesterday) |  |  |  |  | Sunday
| 1 | Highest Generation : |  |  | 13227 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 10149 | MW at | 9:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 14200 | MW
| 3 | Day peak Generation : |  |  | 10149 | MW at | 9:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 13500.54 | MW
| 4 | Evening peak Generation : |  |  | 13227 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 897 | MW
| 5 | Total Energy Generation : |  | 268.0395 | MKWHr | By Solar | 1.5612 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
|  | By Gas : | 125.5969 | MKWHr |  | By Oil: | 84.3572 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 27.8225 | MKWHr |  | By Hydro: | 2.7966 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 3596 | MW | Dhaka | 4991.78 | 4821.78 |  | 170
|  |  |  | For Plants S/D or M/C prob = |  |  | 3067 | MW | Chittagong | 1295.5 | 1245.5 |  | 50 |  | 18:00 |  | 755.6915
|  |  |  | Total = |  |  | 6663 | MW | Khulna | 1640 | 1480 |  | 160
| 7 | Total Gas Supplied : |  |  | 969.5 | MMCFD |  |  | Rajshahi | 1371.4 | 1251.4 |  | 120 |  | 19:00 |  | 1088
| 8 | Fuel Cost : | i) Gas : | Taka | 144451350.228 | ii) Oil : | Taka | 1216925561.2 | Comilla | 1268 | 1168 |  | 100 |  | 19:30 |  | 1072.7133
|  |  | iii) Coal : |  | 231624653 | Total | Taka | 1593001564.428 | Mymensingh | 1019 | 839 |  | 180 |  | 20:00 |  | 1207.2632
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0 | MKWHr. | Sylhet | 568 | 488 |  | 80 |  | 21:00 |  | 896.6925
|  | ii) During Peak Demand : |  |  | 736 | MW (E to W) at | 21:00 | hrs | Barisal | 401.86 | 401.86 |  | 0 |  | 22:00 |  | 808.2213
|  | iii) Maximum : |  |  | 454 | MW at | 5:00 | hrs | Rangpur | 945 | 908 |  | 37 |  | 23:00 |  | 834.947
| 10 | Maximum Temperature in Dhaka was |  |  |  | 35.4° C |  |  | Total | 13500.54 | 12603.54 |  | 897
| B. |  | 2022-08-07 | (Today) |  |  |  | Sunday |  |  | Probable max. temperature in Dhaka |  |  | 35.7° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 14200 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 609.6207 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 13539 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 12000 | MW
| 4 | Reserve(Generation end) |  |  |  | - | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 287.7569 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 11166 | MW at | 8:00 | 134.3836 | 66.8175 | 95.1112 | 93.0479 | 74.9066 | 67.7103 | 24.6777 | 0 | 52.9659
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 22.0247 | MKWHr. | ii) HVDC Flow at Peak Time |  | 909 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.8803 | MKWHr. | iii) Maximum HVDC Flow : |  | 914 | MW at | 1:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 93.54 |  | (b) Today: | 94.17 |  | (c) Rule Curve: |  | 91.24
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2022-08-07
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 0 | 93 | 0 | 402 | 331 |  | 0 | 225 | 0 | 7 | 0 | 30 | 0 | 0 | 0 | 8 | 8 | 50 | 0 | 0 | 0 | 0 | 35 | 55 | 17 | 19 | 25 | 27 | 25 | 33 | 50 | 0 | 78 | 35 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 26 | 51 | 56 | 11 | 25 | 15 | 38 | 0 | 0 | 0 | 345 | 330 | 171 | 8 | 135 | 37 | 55 | 0 | 51 | 0 | 41 | 8 | 22 | 10 | 33 | 20 | 172 | 101 | 0 | 0 | 0 | 44 | 41 | 53 | 48 | 110 | 0 | 62 | 81 | 0 | 222 | 0 | 32 | 10 | 320 | 8 | 0 | 0 | 225 | 0 | 0 | 48 | 0 | 136 | 0 | 30 | 42 | 132 | 402 | 49 | 88 | 87 | 0 | 16 | 36 | 55 | 17 | 45 | 65 | 0 | 17 | 0 | 162 | 108 | 0 | 35 | 0 | 74 | 55 | 0 |  | 914 | 0 | 160 | 0 | 16 | 216 | 0 | 0 | 22 | 60 | 8 | 87 | 32 | 32 | 0 | 0 | 0 | 24 | 40 | 80 | 0 | 42 | 24 | 8 | 33 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 177 | 0 | 0 | 215 | 0 | 0 | 148 | 0 | 286 | 0 | 0 | 50 | 105 | 56 | 0 | 0 | 95 | 1070 | 215 | 0 | 0 | 0 | 0 | 34 | 0 | 0 |  | 6549 | 4482 | 11031 | 3392 | 914 | 2010 | 0 | 2278 | 1270 | 113 | 431 | 666 | 172 | 0 | 1538.1087 | 93.4
2:00 | 0 | 0 | 0 | 180 | 0 | 93 | 0 | 403 | 331 |  | 0 | 225 | 0 | 8 | 0 | 30 | 0 | 0 | 0 | 8 | 8 | 50 | 0 | 0 | 0 | 0 | 35 | 55 | 17 | 19 | 25 | 20 | 0 | 17 | 50 | 0 | 78 | 35 | 100 | 0 | 7 | 0 | 0 | 0 | 0 |  | 0 | 26 | 51 | 56 | 11 | 25 | 15 | 38 | 0 | 0 | 0 | 305 | 290 | 184 | 8 | 135 | 37 | 40 | 0 | 51 | 0 | 41 | 8 | 22 | 10 | 33 | 20 | 172 | 101 | 0 | 20 | 0 | 44 | 41 | 53 | 49 | 110 | 0 | 62 | 81 | 0 | 220 | 0 | 31 | 10 | 320 | 8 | 0 | 0 | 200 | 0 | 0 | 48 | 0 | 99 | 0 | 20 | 34 | 128 | 402 | 49 | 88 | 87 | 0 | 16 | 36 | 55 | 17 | 36 | 20 | 0 | 17 | 0 | 162 | 108 | 0 | 35 | 0 | 75 | 55 | 0 |  | 914 | 0 | 160 | 0 | 16 | 223 | 0 | 0 | 17 | 57 | 8 | 86 | 30 | 32 | 0 | 0 | 0 | 24 | 40 | 80 | 0 | 42 | 24 | 8 | 33 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 178 | 0 | 0 | 214 | 0 | 0 | 148 | 0 | 290 | 0 | 0 | 50 | 105 | 56 | 0 | 0 | 55 | 1090 | 221 | 0 | 0 | 0 | 0 | 34 | 0 | 0 |  | 6309 | 4468 | 10777 | 3296 | 914 | 2003 | 0 | 2109 | 1290 | 113 | 437 | 657 | 172 | 0 | 1680.0312 | 93.43
3:00 | 0 | 0 | 0 | 180 | 0 | 93 | 0 | 406 | 327 |  | 0 | 225 | 0 | 7 | 0 | 30 | 0 | 0 | 0 | 8 | 8 | 50 | 0 | 0 | 0 | 0 | 35 | 55 | 17 | 19 | 25 | 25 | 0 | 17 | 50 | 0 | 78 | 35 | 100 | 0 | 16 | 0 | 0 | 0 | 0 |  | 0 | 26 | 51 | 56 | 11 | 25 | 15 | 37 | 0 | 0 | 0 | 340 | 320 | 182 | 8 | 141 | 37 | 40 | 0 | 51 | 0 | 41 | 8 | 22 | 10 | 33 | 20 | 170 | 102 | 0 | 20 | 0 | 43 | 41 | 53 | 49 | 110 | 0 | 60 | 10 | 0 | 220 | 0 | 30 | 10 | 320 | 8 | 0 | 0 | 200 | 0 | 0 | 48 | 0 | 99 | 0 | 21 | 34 | 137 | 402 | 49 | 88 | 87 | 0 | 16 | 36 | 55 | 17 | 36 | 20 | 0 | 0 | 0 | 162 | 108 | 0 | 35 | 0 | 75 | 55 | 0 |  | 913 | 0 | 160 | 0 | 16 | 226 | 0 | 0 | 17 | 57 | 8 | 87 | 30 | 32 | 0 | 0 | 0 | 24 | 40 | 80 | 0 | 42 | 24 | 8 | 33 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 177 | 0 | 0 | 215 | 0 | 0 | 148 | 0 | 302 | 0 | 0 | 50 | 105 | 56 | 0 | 0 | 55 | 1080 | 220 | 0 | 0 | 0 | 0 | 34 | 0 | 0 |  | 6306 | 4469 | 10775 | 3368 | 913 | 1937 | 0 | 2110 | 1280 | 113 | 441 | 658 | 170 | 0 | 1589.7169 | 93.45
4:00 | 0 | 0 | 0 | 180 | 0 | 93 | 0 | 405 | 326 |  | 0 | 225 | 0 | 8 | 0 | 30 | 0 | 0 | 0 | 8 | 8 | 50 | 0 | 0 | 0 | 0 | 35 | 55 | 17 | 19 | 25 | 20 | 8 | 17 | 51 | 0 | 78 | 35 | 100 | 0 | 16 | 0 | 0 | 0 | 0 |  | 0 | 26 | 17 | 56 | 11 | 25 | 15 | 38 | 0 | 0 | 0 | 335 | 320 | 179 | 8 | 142 | 37 | 40 | 0 | 51 | 0 | 41 | 8 | 22 | 10 | 33 | 20 | 168 | 102 | 0 | 20 | 0 | 43 | 41 | 42 | 30 | 110 | 0 | 61 | 10 | 0 | 220 | 0 | 32 | 10 | 330 | 8 | 0 | 0 | 195 | 0 | 0 | 48 | 0 | 99 | 0 | 21 | 34 | 137 | 401 | 49 | 88 | 81 | 0 | 16 | 36 | 55 | 17 | 36 | 20 | 0 | 0 | 0 | 162 | 108 | 0 | 35 | 0 | 74 | 55 | 0 |  | 913 | 0 | 165 | 0 | 16 | 226 | 0 | 0 | 17 | 57 | 8 | 87 | 27 | 32 | 0 | 0 | 0 | 24 | 40 | 80 | 0 | 42 | 24 | 8 | 33 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 178 | 0 | 0 | 215 | 0 | 0 | 149 | 0 | 306 | 0 | 0 | 50 | 105 | 56 | 0 | 0 | 55 | 1080 | 221 | 0 | 0 | 0 | 0 | 34 | 0 | 0 |  | 6237 | 4478 | 10715 | 3370 | 913 | 1921 | 0 | 2100 | 1280 | 113 | 441 | 624 | 168 | 0 | 1552.8539 | 93.48
5:00 | 0 | 0 | 0 | 180 | 0 | 92 | 0 | 407 | 327 |  | 0 | 225 | 0 | 7 | 0 | 30 | 0 | 0 | 0 | 8 | 8 | 50 | 0 | 0 | 0 | 0 | 35 | 55 | 17 | 19 | 25 | 25 | 25 | 33 | 51 | 0 | 79 | 35 | 100 | 0 | 16 | 0 | 0 | 0 | 0 |  | 0 | 26 | 17 | 56 | 11 | 25 | 15 | 38 | 0 | 0 | 0 | 345 | 330 | 189 | 8 | 142 | 37 | 40 | 0 | 51 | 0 | 41 | 8 | 22 | 10 | 33 | 20 | 164 | 102 | 0 | 22 | 0 | 43 | 41 | 42 | 30 | 110 | 0 | 60 | 10 | 0 | 220 | 0 | 31 | 10 | 310 | 8 | 0 | 0 | 198 | 0 | 0 | 48 | 0 | 99 | 0 | 21 | 34 | 132 | 402 | 49 | 88 | 87 | 0 | 16 | 36 | 55 | 17 | 36 | 20 | 0 | 0 | 0 | 162 | 108 | 0 | 35 | 0 | 75 | 55 | 0 |  | 914 | 0 | 165 | 0 | 16 | 226 | 0 | 0 | 17 | 57 | 0 | 85 | 27 | 32 | 0 | 0 | 0 | 24 | 40 | 80 | 0 | 42 | 24 | 8 | 33 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 178 | 0 | 0 | 215 | 0 | 0 | 151 | 0 | 307 | 0 | 0 | 50 | 105 | 56 | 0 | 0 | 55 | 1070 | 216 | 0 | 0 | 0 | 0 | 34 | 0 | 0 |  | 6289 | 4457 | 10746 | 3442 | 914 | 1896 | 0 | 2096 | 1270 | 114 | 441 | 624 | 164 | 0 | 1247.8126 | 93.51
6:00 | 0 | 0 | 0 | 180 | 0 | 90 | 0 | 404 | 327 |  | 0 | 225 | 0 | 7 | 0 | 30 | 0 | 0 | 0 | 8 | 8 | 50 | 0 | 0 | 0 | 0 | 35 | 55 | 17 | 19 | 25 | 25 | 25 | 33 | 51 | 0 | 79 | 35 | 100 | 0 | 16 | 0 | 0 | 0 | 0 |  | 0 | 26 | 17 | 56 | 11 | 25 | 15 | 38 | 0 | 0 | 0 | 315 | 290 | 188 | 8 | 142 | 35 | 40 | 0 | 51 | 0 | 41 | 8 | 22 | 10 | 33 | 20 | 150 | 101 | 0 | 22 | 0 | 43 | 41 | 42 | 30 | 110 | 0 | 60 | 10 | 0 | 220 | 0 | 31 | 10 | 320 | 8 | 0 | 0 | 195 | 0 | 0 | 48 | 0 | 99 | 1 | 21 | 34 | 132 | 400 | 49 | 88 | 80 | 0 | 16 | 36 | 54 | 17 | 36 | 20 | 0 | 5 | 4 | 66 | 108 | 0 | 35 | 1 | 75 | 44 | 0 |  | 914 | 0 | 160 | 0 | 16 | 226 | 0 | 0 | 0 | 0 | 0 | 85 | 24 | 32 | 0 | 0 | 0 | 24 | 0 | 72 | 0 | 42 | 24 | 8 | 33 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 177 | 0 | 0 | 213 | 0 | 0 | 151 | 0 | 324 | 0 | 0 | 50 | 105 | 56 | 0 | 0 | 55 | 1040 | 220 | 0 | 0 | 0 | 5 | 34 | 0 | 0 |  | 6097 | 4323 | 10420 | 3360 | 914 | 1922 | 0 | 1983 | 1240 | 114 | 439 | 500 | 150 | 11 | 1087.4585 | 93.54
7:00 | 0 | 0 | 0 | 180 | 0 | 90 | 0 | 405 | 325 |  | 0 | 225 | 0 | 8 | 0 | 30 | 0 | 0 | 0 | 8 | 8 | 50 | 0 | 0 | 0 | 0 | 35 | 55 | 17 | 19 | 25 | 17 | 25 | 33 | 51 | 0 | 77 | 35 | 100 | 0 | 16 | 0 | 0 | 0 | 0 |  | 0 | 26 | 17 | 56 | 11 | 25 | 15 | 38 | 0 | 0 | 0 | 350 | 335 | 183 | 8 | 142 | 35 | 40 | 0 | 51 | 0 | 24 | 8 | 22 | 10 | 33 | 20 | 140 | 102 | 0 | 20 | 0 | 43 | 41 | 42 | 30 | 110 | 0 | 60 | 10 | 0 | 220 | 0 | 31 | 10 | 320 | 8 | 0 | 0 | 195 | 0 | 0 | 48 | 0 | 99 | 3 | 21 | 34 | 128 | 390 | 49 | 88 | 87 | 1 | 16 | 36 | 54 | 17 | 37 | 20 | 0 | 18 | 15 | 54 | 108 | 0 | 35 | 8 | 75 | 55 | 0 |  | 913 | 0 | 160 | 0 | 16 | 225 | 0 | 0 | 0 | 0 | 0 | 87 | 21 | 32 | 0 | 0 | 0 | 24 | 0 | 72 | 0 | 42 | 24 | 8 | 33 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 178 | 0 | 0 | 214 | 0 | 0 | 148 | 0 | 313 | 0 | 0 | 50 | 88 | 56 | 0 | 1 | 55 | 1030 | 218 | 0 | 0 | 0 | 14 | 34 | 0 | 0 |  | 6161 | 4289 | 10450 | 3417 | 913 | 1904 | 0 | 1983 | 1230 | 112 | 439 | 484 | 140 | 42 | 967.6537 | 93.57
8:00 | 0 | 0 | 0 | 180 | 0 | 86 | 0 | 403 | 322 |  | 0 | 225 | 0 | 8 | 0 | 30 | 0 | 0 | 0 | 8 | 8 | 50 | 0 | 0 | 0 | 0 | 35 | 55 | 17 | 19 | 25 | 17 | 25 | 33 | 51 | 0 | 79 | 35 | 100 | 0 | 16 | 0 | 0 | 0 | 0 |  | 0 | 26 | 17 | 56 | 12 | 25 | 15 | 12 | 0 | 0 | 0 | 290 | 275 | 178 | 8 | 142 | 35 | 40 | 0 | 51 | 0 | 24 | 10 | 0 | 10 | 33 | 20 | 148 | 96 | 0 | 20 | 1 | 44 | 41 | 33 | 30 | 110 | 0 | 62 | 10 | 0 | 221 | 0 | 31 | 10 | 330 | 8 | 0 | 0 | 195 | 0 | 0 | 48 | 0 | 99 | 13 | 21 | 34 | 122 | 400 | 49 | 88 | 87 | 3 | 50 | 36 | 55 | 17 | 38 | 20 | 0 | 17 | 23 | 54 | 108 | 0 | 35 | 16 | 75 | 55 | 0 |  | 914 | 0 | 160 | 0 | 16 | 224 | 0 | 0 | 0 | 0 | 0 | 86 | 20 | 16 | 0 | 0 | 0 | 24 | 0 | 72 | 0 | 42 | 32 | 8 | 0 | 20 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 177 | 0 | 0 | 214 | 0 | 0 | 148 | 0 | 305 | 0 | 0 | 50 | 88 | 56 | 0 | 2 | 55 | 980 | 220 | 0 | 0 | 1 | 56 | 34 | 0 | 0 |  | 6059 | 4231 | 10290 | 3274 | 914 | 1863 | 0 | 1999 | 1180 | 114 | 438 | 459 | 148 | 115 | 1299.4207 | 93.6
9:00 | 0 | 0 | 0 | 180 | 0 | 86 | 0 | 402 | 321 |  | 0 | 225 | 0 | 7 | 0 | 30 | 0 | 0 | 0 | 8 | 8 | 50 | 0 | 0 | 0 | 0 | 35 | 55 | 17 | 19 | 25 | 20 | 25 | 16 | 42 | 0 | 76 | 35 | 100 | 0 | 16 | 0 | 0 | 0 | 0 |  | 0 | 26 | 17 | 56 | 12 | 25 | 15 | 2 | 0 | 0 | 0 | 320 | 330 | 166 | 8 | 137 | 31 | 40 | 0 | 51 | 0 | 24 | 16 | 0 | 10 | 21 | 20 | 150 | 81 | 0 | 22 | 2 | 43 | 41 | 33 | 30 | 110 | 0 | 60 | 10 | 0 | 220 | 0 | 31 | 10 | 330 | 8 | 0 | 0 | 195 | 0 | 0 | 48 | 0 | 97 | 13 | 21 | 34 | 122 | 380 | 48 | 88 | 87 | 4 | 50 | 36 | 55 | 17 | 38 | 20 | 0 | 17 | 41 | 54 | 108 | 0 | 35 | 20 | 75 | 55 | 0 |  | 914 | 0 | 150 | 0 | 16 | 221 | 0 | 0 | 0 | 0 | 0 | 85 | 21 | 16 | 0 | 0 | 0 | 24 | 0 | 45 | 0 | 0 | 32 | 8 | 0 | 19 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 178 | 0 | 0 | 213 | 0 | 0 | 146 | 0 | 290 | 0 | 0 | 50 | 88 | 56 | 0 | 6 | 55 | 940 | 220 | 0 | 0 | 3 | 44 | 34 | 0 | 0 |  | 6064 | 4085 | 10149 | 3262 | 914 | 1837 | 0 | 1950 | 1140 | 111 | 434 | 431 | 150 | 133 | 1613.6778 | 93.63
10:00 | 0 | 0 | 0 | 180 | 0 | 84 | 0 | 396 | 312 |  | 0 | 225 | 0 | 7 | 0 | 30 | 0 | 0 | 0 | 8 | 8 | 50 | 0 | 0 | 0 | 0 | 17 | 55 | 17 | 19 | 25 | 20 | 25 | 0 | 42 | 0 | 78 | 35 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 26 | 17 | 56 | 12 | 25 | 15 | 2 | 0 | 0 | 0 | 305 | 290 | 176 | 8 | 136 | 34 | 30 | 0 | 43 | 0 | 24 | 8 | 0 | 10 | 16 | 20 | 140 | 81 | 0 | 22 | 2 | 43 | 41 | 31 | 30 | 110 | 0 | 60 | 10 | 0 | 220 | 0 | 30 | 10 | 320 | 8 | 0 | 0 | 195 | 0 | 0 | 48 | 0 | 99 | 11 | 21 | 34 | 117 | 401 | 48 | 88 | 87 | 4 | 53 | 17 | 55 | 17 | 38 | 20 | 0 | 17 | 51 | 54 | 108 | 0 | 35 | 31 | 75 | 55 | 0 |  | 914 | 0 | 145 | 0 | 16 | 225 | 0 | 0 | 0 | 0 | 0 | 84 | 21 | 16 | 0 | 0 | 0 | 17 | 0 | 45 | 0 | 0 | 32 | 8 | 0 | 17 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 178 | 0 | 0 | 203 | 0 | 0 | 142 | 0 | 270 | 0 | 0 | 50 | 88 | 56 | 0 | 7 | 55 | 930 | 220 | 0 | 0 | 4 | 45 | 34 | 0 | 0 |  | 5923 | 4032 | 9955 | 3203 | 914 | 1773 | 0 | 1889 | 1129 | 113 | 428 | 414 | 140 | 155 | 1976.7784 | 93.66
11:00 | 0 | 0 | 0 | 180 | 0 | 83 | 0 | 397 | 312 |  | 0 | 225 | 0 | 7 | 0 | 30 | 0 | 0 | 0 | 8 | 8 | 50 | 0 | 0 | 0 | 0 | 17 | 55 | 17 | 19 | 25 | 20 | 25 | 30 | 42 | 0 | 79 | 35 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 26 | 17 | 56 | 12 | 25 | 15 | 2 | 0 | 0 | 0 | 335 | 330 | 201 | 8 | 135 | 38 | 10 | 0 | 43 | 0 | 24 | 8 | 0 | 10 | 25 | 20 | 162 | 81 | 0 | 22 | 1 | 43 | 41 | 33 | 30 | 110 | 0 | 60 | 10 | 0 | 205 | 0 | 30 | 10 | 320 | 8 | 0 | 0 | 195 | 0 | 0 | 48 | 0 | 99 | 14 | 21 | 34 | 118 | 385 | 48 | 88 | 87 | 5 | 53 | 17 | 55 | 17 | 38 | 20 | 0 | 17 | 50 | 54 | 108 | 0 | 35 | 34 | 75 | 55 | 0 |  | 914 | 0 | 130 | 0 | 16 | 227 | 0 | 0 | 0 | 0 | 0 | 83 | 22 | 16 | 0 | 0 | 0 | 24 | 0 | 45 | 0 | 0 | 32 | 8 | 0 | 17 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 175 | 0 | 0 | 200 | 0 | 0 | 140 | 0 | 280 | 0 | 0 | 50 | 88 | 56 | 0 | 7 | 55 | 930 | 216 | 0 | 0 | 5 | 81 | 34 | 0 | 0 |  | 6040 | 4062 | 10102 | 3289 | 914 | 1761 | 0 | 1890 | 1130 | 114 | 427 | 418 | 162 | 197 | 2025.6218 | 93.69
12:00 | 0 | 0 | 0 | 180 | 0 | 80 | 0 | 395 | 312 |  | 0 | 225 | 0 | 6 | 0 | 30 | 0 | 0 | 0 | 8 | 8 | 50 | 0 | 0 | 0 | 0 | 17 | 55 | 17 | 19 | 25 | 20 | 25 | 30 | 42 | 0 | 79 | 35 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 28 | 34 | 34 | 12 | 25 | 15 | 3 | 0 | 0 | 0 | 315 | 310 | 188 | 36 | 135 | 35 | 0 | 0 | 43 | 0 | 26 | 8 | 0 | 10 | 31 | 20 | 164 | 68 | 0 | 22 | 2 | 43 | 40 | 33 | 30 | 110 | 0 | 58 | 10 | 0 | 207 | 0 | 30 | 10 | 310 | 8 | 0 | 0 | 195 | 0 | 0 | 48 | 0 | 99 | 14 | 21 | 34 | 118 | 373 | 48 | 88 | 72 | 4 | 53 | 17 | 40 | 17 | 38 | 20 | 0 | 17 | 47 | 54 | 108 | 0 | 35 | 35 | 64 | 55 | 0 |  | 914 | 0 | 135 | 0 | 16 | 227 | 0 | 0 | 0 | 0 | 0 | 84 | 22 | 33 | 0 | 0 | 0 | 24 | 0 | 45 | 0 | 0 | 32 | 8 | 10 | 17 | 0 | 11 | 0 | 0 | 199 | 0 | 0 | 175 | 0 | 0 | 200 | 0 | 0 | 140 | 0 | 265 | 0 | 0 | 50 | 88 | 56 | 0 | 8 | 55 | 820 | 216 | 0 | 0 | 5 | 97 | 34 | 0 | 0 |  | 5925 | 3986 | 9911 | 3217 | 914 | 1752 | 0 | 1843 | 1019 | 114 | 427 | 449 | 164 | 212 | 2293.8002 | 93.72
13:00 | 0 | 0 | 0 | 180 | 0 | 82 | 0 | 401 | 311 |  | 0 | 225 | 0 | 23 | 0 | 30 | 0 | 0 | 0 | 22 | 16 | 50 | 0 | 0 | 0 | 0 | 17 | 55 | 17 | 19 | 25 | 25 | 25 | 30 | 42 | 0 | 80 | 35 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 26 | 51 | 33 | 15 | 25 | 13 | 3 | 0 | 0 | 0 | 310 | 305 | 204 | 55 | 129 | 38 | 0 | 0 | 43 | 0 | 31 | 8 | 0 | 10 | 31 | 20 | 168 | 68 | 0 | 22 | 3 | 43 | 40 | 33 | 30 | 110 | 0 | 61 | 10 | 0 | 208 | 0 | 31 | 10 | 300 | 8 | 0 | 0 | 195 | 0 | 0 | 47 | 0 | 99 | 19 | 76 | 34 | 115 | 403 | 48 | 88 | 74 | 3 | 52 | 29 | 53 | 17 | 76 | 32 | 0 | 31 | 56 | 54 | 108 | 0 | 35 | 35 | 76 | 55 | 0 |  | 913 | 0 | 140 | 0 | 16 | 230 | 0 | 0 | 0 | 0 | 0 | 85 | 24 | 33 | 0 | 0 | 0 | 24 | 5 | 45 | 0 | 0 | 32 | 8 | 33 | 17 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 173 | 0 | 0 | 170 | 0 | 0 | 139 | 0 | 265 | 1 | 0 | 50 | 88 | 55 | 0 | 7 | 55 | 820 | 216 | 0 | 0 | 4 | 68 | 34 | 0 | 0 |  | 6215 | 3961 | 10176 | 3266 | 913 | 1765 | 0 | 2037 | 1020 | 115 | 400 | 467 | 168 | 195 | 1957.4253 | 93.75
14:00 | 0 | 0 | 0 | 180 | 0 | 80 | 0 | 403 | 311 |  | 0 | 225 | 0 | 50 | 0 | 30 | 0 | 0 | 0 | 48 | 50 | 50 | 0 | 0 | 0 | 0 | 17 | 55 | 17 | 22 | 25 | 25 | 33 | 30 | 42 | 0 | 80 | 35 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 26 | 51 | 33 | 13 | 25 | 0 | 3 | 0 | 0 | 0 | 325 | 320 | 201 | 83 | 128 | 38 | 0 | 0 | 43 | 0 | 30 | 8 | 0 | 10 | 33 | 20 | 170 | 68 | 0 | 22 | 2 | 43 | 40 | 33 | 30 | 110 | 0 | 59 | 10 | 0 | 207 | 0 | 31 | 10 | 300 | 8 | 0 | 0 | 195 | 0 | 0 | 47 | 0 | 99 | 19 | 70 | 34 | 117 | 401 | 48 | 88 | 87 | 4 | 52 | 30 | 54 | 17 | 109 | 50 | 0 | 51 | 27 | 76 | 108 | 0 | 35 | 31 | 65 | 55 | 0 |  | 907 | 0 | 140 | 0 | 16 | 220 | 0 | 0 | 0 | 0 | 8 | 83 | 22 | 64 | 0 | 0 | 0 | 34 | 6 | 45 | 0 | 0 | 32 | 8 | 33 | 17 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 171 | 0 | 0 | 150 | 0 | 0 | 138 | 0 | 254 | 25 | 0 | 70 | 88 | 55 | 0 | 7 | 55 | 700 | 213 | 0 | 22 | 4 | 99 | 34 | 0 | 0 |  | 6410 | 3931 | 10341 | 3284 | 907 | 1775 | 0 | 2320 | 900 | 115 | 370 | 457 | 170 | 193 | 1898 | 93.78
15:00 | 0 | 0 | 0 | 180 | 0 | 87 | 0 | 401 | 307 |  | 0 | 225 | 0 | 56 | 0 | 30 | 0 | 0 | 0 | 48 | 50 | 50 | 0 | 0 | 0 | 0 | 35 | 55 | 17 | 22 | 25 | 25 | 33 | 30 | 42 | 0 | 80 | 35 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 26 | 51 | 33 | 15 | 25 | 13 | 2 | 0 | 0 | 0 | 320 | 305 | 202 | 83 | 128 | 37 | 0 | 0 | 43 | 0 | 30 | 12 | 21 | 10 | 33 | 20 | 182 | 68 | 0 | 22 | 2 | 43 | 41 | 32 | 30 | 110 | 0 | 60 | 10 | 0 | 207 | 0 | 31 | 10 | 300 | 8 | 0 | 0 | 193 | 100 | 0 | 46 | 0 | 98 | 15 | 76 | 34 | 113 | 404 | 48 | 88 | 87 | 4 | 52 | 33 | 55 | 17 | 110 | 50 | 0 | 47 | 34 | 105 | 108 | 0 | 35 | 26 | 66 | 55 | 0 |  | 907 | 0 | 135 | 0 | 16 | 221 | 0 | 0 | 0 | 0 | 8 | 85 | 26 | 64 | 0 | 0 | 0 | 32 | 6 | 45 | 0 | 0 | 32 | 8 | 33 | 17 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 170 | 0 | 0 | 130 | 0 | 0 | 137 | 0 | 255 | 35 | 0 | 70 | 88 | 54 | 0 | 6 | 55 | 650 | 213 | 0 | 45 | 4 | 67 | 34 | 0 | 0 |  | 6597 | 3859 | 10456 | 3296 | 907 | 1781 | 100 | 2411 | 850 | 115 | 351 | 435 | 182 | 158 | 1884 | 93.81
16:00 | 0 | 0 | 0 | 180 | 0 | 92 | 0 | 400 | 291 |  | 0 | 225 | 0 | 14 | 0 | 30 | 0 | 0 | 0 | 15 | 8 | 115 | 0 | 0 | 0 | 0 | 35 | 55 | 17 | 22 | 25 | 25 | 33 | 30 | 49 | 0 | 81 | 35 | 98 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 26 | 51 | 33 | 18 | 25 | 13 | 3 | 0 | 0 | 0 | 285 | 290 | 197 | 83 | 128 | 35 | 0 | 0 | 51 | 0 | 30 | 8 | 21 | 10 | 33 | 20 | 164 | 95 | 0 | 0 | 1 | 43 | 41 | 33 | 30 | 110 | 0 | 61 | 10 | 0 | 207 | 0 | 30 | 10 | 280 | 8 | 0 | 50 | 195 | 102 | 88 | 46 | 95 | 98 | 4 | 21 | 34 | 112 | 352 | 48 | 88 | 105 | 3 | 52 | 18 | 55 | 17 | 100 | 20 | 0 | 17 | 31 | 105 | 108 | 0 | 35 | 15 | 56 | 55 | 0 |  | 907 | 0 | 135 | 0 | 16 | 221 | 0 | 0 | 0 | 0 | 8 | 87 | 26 | 64 | 0 | 0 | 0 | 32 | 24 | 45 | 0 | 0 | 32 | 8 | 34 | 17 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 169 | 0 | 0 | 176 | 0 | 5 | 138 | 0 | 264 | 38 | 1 | 80 | 88 | 89 | 0 | 5 | 57 | 620 | 180 | 0 | 90 | 3 | 55 | 34 | 0 | 0 |  | 6483 | 3959 | 10442 | 3192 | 907 | 1735 | 341 | 2264 | 820 | 116 | 397 | 565 | 164 | 117 | 1804 | 93.84
17:00 | 0 | 0 | 0 | 180 | 0 | 93 | 0 | 401 | 288 |  | 0 | 225 | 0 | 11 | 0 | 30 | 0 | 0 | 0 | 8 | 8 | 124 | 0 | 0 | 0 | 0 | 54 | 55 | 17 | 22 | 25 | 26 | 33 | 30 | 49 | 0 | 83 | 35 | 98 | 0 | 13 | 0 | 0 | 0 | 0 |  | 0 | 25 | 51 | 33 | 15 | 25 | 13 | 3 | 0 | 0 | 0 | 280 | 275 | 198 | 83 | 128 | 37 | 0 | 0 | 51 | 0 | 30 | 8 | 0 | 10 | 33 | 20 | 160 | 96 | 0 | 20 | 0 | 44 | 41 | 33 | 30 | 110 | 0 | 60 | 10 | 0 | 207 | 0 | 29 | 10 | 290 | 8 | 0 | 50 | 195 | 153 | 94 | 47 | 98 | 141 | 5 | 21 | 34 | 110 | 403 | 48 | 88 | 105 | 2 | 69 | 17 | 55 | 98 | 102 | 20 | 0 | 17 | 14 | 114 | 108 | 0 | 35 | 9 | 56 | 55 | 0 |  | 907 | 0 | 135 | 0 | 20 | 226 | 0 | 0 | 0 | 0 | 8 | 85 | 24 | 64 | 0 | 0 | 0 | 32 | 33 | 45 | 0 | 0 | 32 | 8 | 34 | 17 | 0 | 11 | 0 | 0 | 201 | 0 | 0 | 168 | 0 | 0 | 209 | 0 | 20 | 140 | 0 | 263 | 24 | 50 | 93 | 89 | 81 | 0 | 4 | 57 | 600 | 189 | 0 | 120 | 1 | 6 | 72 | 0 | 0 |  | 6737 | 4068 | 10805 | 3227 | 907 | 1748 | 465 | 2497 | 801 | 118 | 435 | 615 | 160 | 41 | 1286 | 93.86
18:00 | 0 | 0 | 0 | 180 | 0 | 96 | 0 | 403 | 276 |  | 0 | 225 | 0 | 7 | 0 | 30 | 0 | 0 | 0 | 8 | 8 | 124 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 26 | 33 | 30 | 49 | 0 | 83 | 35 | 98 | 0 | 25 | 0 | 0 | 0 | 0 |  | 0 | 26 | 51 | 33 | 51 | 25 | 13 | 4 | 0 | 0 | 0 | 280 | 280 | 185 | 83 | 130 | 40 | 3 | 0 | 51 | 0 | 30 | 8 | 0 | 10 | 33 | 20 | 158 | 96 | 0 | 22 | 0 | 44 | 40 | 33 | 30 | 110 | 0 | 58 | 10 | 0 | 207 | 0 | 29 | 9 | 280 | 8 | 0 | 50 | 207 | 101 | 95 | 167 | 98 | 149 | 1 | 21 | 34 | 112 | 405 | 77 | 88 | 105 | 0 | 85 | 17 | 72 | 114 | 104 | 20 | 0 | 17 | 3 | 162 | 108 | 0 | 35 | 3 | 56 | 55 | 0 |  | 906 | 0 | 140 | 0 | 23 | 224 | 0 | 0 | 13 | 23 | 8 | 85 | 25 | 64 | 0 | 0 | 0 | 32 | 33 | 51 | 0 | 0 | 32 | 8 | 33 | 18 | 0 | 11 | 0 | 0 | 209 | 0 | 0 | 168 | 0 | 0 | 211 | 0 | 20 | 140 | 0 | 262 | 17 | 50 | 94 | 89 | 88 | 0 | 1 | 95 | 600 | 211 | 0 | 138 | 0 | 8 | 72 | 0 | 0 |  | 6978 | 4202 | 11180 | 3232 | 906 | 1755 | 414 | 2889 | 809 | 118 | 435 | 659 | 158 | 16 | 755.6915 | 93.88
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 904.0651 | 0
19:00 | 0 | 0 | 0 | 180 | 0 | 96 | 0 | 401 | 278 |  | 0 | 225 | 0 | 11 | 0 | 30 | 0 | 0 | 0 | 11 | 8 | 124 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 20 | 33 | 30 | 49 | 0 | 83 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 1 | 26 | 51 | 33 | 80 | 25 | 13 | 7 | 0 | 0 | 0 | 280 | 260 | 202 | 8 | 128 | 38 | 15 | 0 | 51 | 0 | 34 | 16 | 0 | 10 | 33 | 20 | 158 | 99 | 0 | 22 | 0 | 44 | 40 | 50 | 40 | 110 | 0 | 58 | 70 | 0 | 220 | 0 | 29 | 10 | 300 | 16 | 0 | 195 | 242 | 241 | 98 | 151 | 98 | 149 | 0 | 90 | 34 | 112 | 405 | 78 | 105 | 105 | 0 | 206 | 34 | 72 | 114 | 114 | 38 | 0 | 17 | 0 | 162 | 108 | 0 | 35 | 0 | 52 | 55 | 0 |  | 907 | 0 | 140 | 0 | 27 | 223 | 0 | 0 | 34 | 63 | 8 | 85 | 30 | 64 | 0 | 0 | 0 | 32 | 21 | 79 | 0 | 0 | 32 | 52 | 33 | 18 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 168 | 0 | 0 | 211 | 0 | 47 | 140 | 0 | 270 | 17 | 84 | 94 | 88 | 91 | 0 | 0 | 95 | 660 | 218 | 0 | 0 | 0 | 0 | 90 | 0 | 0 |  | 7637 | 4382 | 12019 | 3243 | 907 | 1825 | 763 | 3132 | 910 | 118 | 434 | 740 | 158 | 0 | 1088 | 93.94
19:30 | 0 | 0 | 0 | 180 | 0 | 96 | 0 | 396 | 276 |  | 0 | 225 | 0 | 41 | 0 | 30 | 0 | 0 | 0 | 50 | 42 | 128 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 26 | 33 | 30 | 49 | 0 | 83 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 2 | 34 | 51 | 33 | 76 | 25 | 13 | 7 | 0 | 0 | 0 | 280 | 260 | 204 | 8 | 127 | 41 | 35 | 0 | 51 | 0 | 38 | 43 | 10 | 10 | 33 | 20 | 160 | 100 | 0 | 22 | 0 | 44 | 40 | 53 | 47 | 110 | 0 | 58 | 81 | 0 | 220 | 0 | 29 | 9 | 270 | 16 | 0 | 150 | 242 | 200 | 60 | 151 | 51 | 149 | 0 | 90 | 34 | 116 | 404 | 78 | 105 | 105 | 0 | 210 | 36 | 73 | 114 | 115 | 100 | 0 | 51 | 0 | 162 | 108 | 0 | 35 | 0 | 75 | 55 | 0 |  | 909 | 0 | 145 | 0 | 30 | 226 | 0 | 0 | 36 | 78 | 8 | 88 | 31 | 64 | 0 | 0 | 0 | 32 | 21 | 80 | 0 | 0 | 32 | 52 | 33 | 20 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 169 | 0 | 0 | 213 | 0 | 95 | 141 | 0 | 281 | 53 | 155 | 94 | 105 | 91 | 0 | 0 | 95 | 780 | 213 | 0 | 0 | 0 | 0 | 90 | 0 | 0 |  | 7765 | 4721 | 12486 | 3268 | 909 | 1842 | 711 | 3446 | 1030 | 118 | 439 | 776 | 160 | 0 | 1072.7133 | 0
20:00 | 0 | 0 | 0 | 180 | 60 | 97 | 0 | 397 | 277 |  | 0 | 225 | 0 | 38 | 0 | 30 | 0 | 0 | 0 | 43 | 50 | 128 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 27 | 33 | 30 | 49 | 0 | 83 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 4 | 34 | 51 | 33 | 75 | 25 | 13 | 22 | 0 | 0 | 0 | 280 | 260 | 204 | 8 | 129 | 41 | 35 | 0 | 51 | 0 | 38 | 43 | 16 | 10 | 33 | 20 | 160 | 100 | 0 | 22 | 0 | 44 | 40 | 53 | 48 | 110 | 0 | 56 | 81 | 0 | 220 | 0 | 31 | 9 | 265 | 16 | 0 | 150 | 242 | 198 | 60 | 152 | 50 | 149 | 0 | 90 | 34 | 115 | 404 | 78 | 105 | 105 | 0 | 212 | 36 | 75 | 114 | 115 | 100 | 0 | 30 | 0 | 162 | 108 | 0 | 35 | 0 | 69 | 55 | 0 |  | 909 | 0 | 150 | 0 | 32 | 227 | 0 | 0 | 36 | 73 | 8 | 88 | 31 | 64 | 0 | 0 | 0 | 32 | 21 | 80 | 0 | 0 | 32 | 52 | 34 | 21 | 0 | 11 | 0 | 0 | 251 | 0 | 0 | 168 | 0 | 0 | 214 | 0 | 95 | 141 | 0 | 290 | 53 | 161 | 94 | 105 | 91 | 0 | 0 | 95 | 790 | 210 | 0 | 120 | 0 | 0 | 90 | 0 | 0 |  | 7821 | 4869 | 12690 | 3340 | 909 | 1864 | 714 | 3544 | 1041 | 118 | 441 | 773 | 160 | 0 | 1207.2632 | 93.92
21:00 | 0 | 0 | 0 | 180 | 200 | 81 | 0 | 397 | 257 |  | 0 | 225 | 0 | 48 | 0 | 30 | 0 | 0 | 0 | 48 | 50 | 128 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 27 | 33 | 30 | 49 | 0 | 81 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 6 | 34 | 51 | 33 | 80 | 25 | 15 | 30 | 0 | 0 | 0 | 320 | 305 | 208 | 8 | 129 | 41 | 40 | 0 | 51 | 0 | 38 | 43 | 19 | 10 | 33 | 20 | 160 | 100 | 0 | 20 | 0 | 44 | 41 | 53 | 48 | 110 | 0 | 56 | 81 | 0 | 221 | 0 | 31 | 9 | 275 | 16 | 0 | 195 | 242 | 284 | 96 | 154 | 100 | 149 | 0 | 90 | 34 | 122 | 402 | 106 | 105 | 105 | 0 | 214 | 36 | 73 | 114 | 115 | 100 | 0 | 52 | 0 | 162 | 108 | 0 | 6 | 0 | 75 | 55 | 0 |  | 909 | 0 | 150 | 0 | 32 | 228 | 0 | 0 | 38 | 72 | 8 | 88 | 33 | 64 | 0 | 0 | 0 | 32 | 25 | 80 | 0 | 0 | 32 | 52 | 34 | 21 | 0 | 11 | 0 | 0 | 240 | 0 | 0 | 170 | 0 | 0 | 213 | 0 | 96 | 143 | 0 | 286 | 53 | 172 | 94 | 105 | 91 | 0 | 0 | 95 | 800 | 187 | 0 | 150 | 0 | 0 | 90 | 0 | 0 |  | 8333 | 4894 | 13227 | 3576 | 909 | 1826 | 943 | 3652 | 1040 | 116 | 441 | 777 | 160 | 0 | 896.6925 | 93.94
22:00 | 0 | 0 | 0 | 180 | 200 | 84 | 0 | 398 | 247 |  | 0 | 225 | 0 | 48 | 0 | 30 | 0 | 0 | 0 | 48 | 50 | 128 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 27 | 33 | 17 | 49 | 0 | 81 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 7 | 34 | 51 | 33 | 80 | 25 | 15 | 35 | 0 | 0 | 0 | 320 | 320 | 206 | 8 | 129 | 42 | 49 | 0 | 51 | 0 | 38 | 43 | 21 | 10 | 33 | 20 | 170 | 100 | 0 | 20 | 0 | 43 | 40 | 53 | 48 | 110 | 0 | 61 | 81 | 0 | 221 | 0 | 31 | 9 | 300 | 16 | 0 | 140 | 242 | 292 | 50 | 181 | 50 | 149 | 0 | 90 | 34 | 125 | 404 | 87 | 105 | 105 | 0 | 214 | 36 | 74 | 114 | 113 | 100 | 0 | 52 | 0 | 162 | 108 | 0 | 35 | 0 | 75 | 55 | 0 |  | 909 | 0 | 150 | 0 | 32 | 227 | 0 | 0 | 42 | 72 | 8 | 88 | 34 | 64 | 0 | 0 | 0 | 32 | 28 | 80 | 0 | 0 | 32 | 52 | 34 | 22 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 173 | 0 | 0 | 212 | 0 | 96 | 145 | 0 | 291 | 53 | 169 | 94 | 105 | 91 | 0 | 0 | 95 | 790 | 221 | 0 | 150 | 0 | 0 | 90 | 0 | 0 |  | 8281 | 4942 | 13223 | 3590 | 909 | 1899 | 797 | 3692 | 1040 | 116 | 439 | 783 | 170 | 0 | 808.2213 | 93.96
23:00 | 0 | 0 | 0 | 180 | 200 | 88 | 0 | 399 | 247 |  | 0 | 225 | 0 | 48 | 0 | 30 | 0 | 0 | 0 | 48 | 50 | 128 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 27 | 33 | 33 | 49 | 0 | 81 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 8 | 34 | 51 | 33 | 44 | 25 | 15 | 37 | 0 | 0 | 0 | 320 | 320 | 205 | 8 | 128 | 42 | 51 | 0 | 51 | 0 | 38 | 43 | 21 | 10 | 33 | 20 | 162 | 100 | 0 | 20 | 0 | 43 | 41 | 53 | 48 | 110 | 0 | 61 | 81 | 0 | 221 | 0 | 30 | 9 | 320 | 16 | 0 | 196 | 242 | 297 | 95 | 180 | 99 | 134 | 0 | 90 | 34 | 130 | 381 | 78 | 105 | 105 | 0 | 53 | 36 | 75 | 114 | 114 | 100 | 0 | 50 | 0 | 162 | 108 | 0 | 35 | 0 | 60 | 55 | 0 |  | 909 | 0 | 155 | 0 | 32 | 227 | 0 | 0 | 32 | 66 | 8 | 82 | 30 | 64 | 0 | 0 | 0 | 32 | 26 | 80 | 0 | 0 | 32 | 43 | 34 | 21 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 175 | 0 | 0 | 211 | 0 | 96 | 145 | 0 | 287 | 36 | 170 | 94 | 105 | 91 | 0 | 0 | 95 | 790 | 220 | 0 | 38 | 0 | 0 | 90 | 0 | 0 |  | 8217 | 4777 | 12994 | 3584 | 909 | 1916 | 953 | 3323 | 1040 | 116 | 438 | 764 | 162 | 0 | 834.947 | 93.98
24:00 | 0 | 0 | 0 | 180 | 200 | 87 | 0 | 398 | 265 |  | 0 | 225 | 0 | 9 | 0 | 30 | 0 | 0 | 0 | 14 | 8 | 48 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 27 | 33 | 33 | 49 | 0 | 81 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 10 | 34 | 51 | 33 | 11 | 25 | 15 | 38 | 0 | 0 | 0 | 320 | 320 | 199 | 8 | 127 | 42 | 51 | 0 | 51 | 0 | 39 | 43 | 22 | 10 | 33 | 20 | 162 | 100 | 0 | 22 | 0 | 43 | 41 | 50 | 48 | 110 | 0 | 61 | 81 | 0 | 214 | 0 | 31 | 9 | 295 | 16 | 0 | 197 | 135 | 277 | 95 | 47 | 99 | 118 | 0 | 21 | 34 | 132 | 403 | 49 | 105 | 92 | 0 | 52 | 36 | 57 | 52 | 58 | 100 | 0 | 20 | 0 | 162 | 108 | 0 | 35 | 0 | 73 | 55 | 0 |  | 909 | 0 | 155 | 0 | 32 | 227 | 0 | 0 | 32 | 66 | 8 | 87 | 32 | 64 | 0 | 0 | 0 | 32 | 28 | 80 | 0 | 0 | 32 | 8 | 34 | 22 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 174 | 0 | 0 | 211 | 0 | 96 | 145 | 0 | 275 | 0 | 170 | 94 | 89 | 56 | 0 | 0 | 95 | 790 | 220 | 0 | 90 | 0 | 0 | 90 | 0 | 0 |  | 7455 | 4704 | 12159 | 3598 | 909 | 1898 | 934 | 2588 | 1040 | 116 | 438 | 687 | 162 | 0 | 0 | 94
KWH | 0 | 0 | 0 | 4315500 | 687100 | 2080454 | 0 | 9773060 | 7262000 |  | 0 | 4975150 | 0 | 463680 | 0 | 751006 | 0 | 0 | 0 | 461933 | 459216 | 1740480 | 0 | 0 | 0 | 0 | 894600 | 1308761 | 626577 | 456948 | 600000 | 539100 | 586000 | 649400 | 1141920 | 0 | 1956567 | 840000 | 2400000 | 0 | 317142 | 0 | 0 | 0 | 0 |  | 37680 | 655824 | 909799 | 1039320 | 650880 | 605760 | 331824 | 521280 | 0 | 0 | 0 | 7969400 | 7525000 | 4649000 | 669090 | 3203990 | 876024 | 702720 | 0 | 1156134 | 0 | 791304 | 422918 | 323856 | 238500 | 767300 | 487130 | 3880320 | 2149440 | 0 | 441756 | 16000 | 1015000 | 967424 | 997800 | 925488 | 2542336 | 0 | 1423008 | 857280 | 0 | 5156820 | 0 | 718000 | 231120 | 7541500 | 238560 | 0 | 1072896 | 4927852 | 1815668 | 686089 | 1812000 | 705761 | 2784960 | 116640 | 981120 | 850080 | 2944000 | 9456000 | 1368000 | 2208000 | 2221382 | 34439 | 1656000 | 769538 | 1441053 | 1089840 | 1700160 | 1045440 | 0 | 554880 | 400130 | 2822400 | 2608200 | 0 | 849960 | 257725 | 1683840 | 1312560 | 0 |  | 22024727 | 0 | 3726432 | 0 | 474240 | 5425920 | 0 | 0 | 304800 | 715392 | 118500 | 2063252 | 621013 | 1071648 | 0 | 0 | 0 | 654048 | 409522 | 1506936 | 0 | 334004 | 620200 | 391200 | 613170 | 446640 | 0 | 232254 | 0 | 0 | 5122600 | 0 | 0 | 4398755 | 0 | 0 | 5094618 | 0 | 578880 | 3678527 | 0 | 6858181 | 360960 | 1027096 | 1698432 | 2308032 | 1605427 | 0 | 61492 | 1647840 | 22699900 | 5164336 | 0 | 945600 | 38340 | 636480 | 1260288 | 0 | 0 |  | 161099792 | 106939682 | 268039474 | 81326360 | 22024727 | 44270522 | 5886390 | 59028829 | 27822500 | 2796567 | 10520538 | 8921475 | 3880320 | 1561246 | 0
Fuel Cost | 0 | 0 | 0 | 6430095 | 769552 | 2767003.82 | 0 | 10261713 | 7842960 |  | 0 | 5422913.5 | 0 | 5183942.4 | 0 | 9950829.5 | 0 | 0 | 0 | 6753460.46 | 6461169.12 | 28213180.8 | 0 | 0 | 0 | 0 | 11379312 | 17668273.5 | 8402397.57 | 342711 | 450000 | 0 | 0 | 0 | 19424059.2 | 0 | 528273.09 | 226800 | 4536000 | 0 | 5185271.7 | 0 | 0 | 0 | 0 |  | 491724 | 10939144.32 | 15484778.98 | 14041213.2 | 8253158.4 | 7008643.2 | 421416.48 | 1735862.4 | 0 | 0 | 0 | 8846034 | 8202250 | 5392840 | 863126.1 | 3908867.8 | 989907.12 | 1047052.8 | 0 | 1930743.78 | 0 | 13665820.08 | 5688247.1 | 443682.72 | 178875 | 1342775 | 365347.5 | 27860697.6 | 2342889.6 | 0 | 600788.16 | 255040 | 1390550 | 1276999.68 | 1736172 | 1601094.24 | 2923686.4 | 0 | 2760635.52 | 1954598.4 | 0 | 5208388.2 | 0 | 1069820 | 457617.6 | 7541500 | 178920 | 0 | 22487900.16 | 67265179.8 | 38056401.28 | 14181459.63 | 24425760 | 14588079.87 | 38571696 | 1363521.6 | 10125158.4 | 11612092.8 | 39066880 | 8699520 | 16634880 | 31927680 | 28100482.3 | 0 | 19441440 | 8380268.82 | 15318393.39 | 14789128.8 | 21915062.4 | 12315283.2 | 0 | 7185696 | 5781878.5 | 35816256 | 29681316 | 0 | 11100477.6 | 3079813.75 | 25207084.8 | 17286415.2 | 0 |  | 66074181 | 0 | 4173603.84 | 0 | 4936838.4 | 89527680 | 0 | 0 | 5489448 | 12877056 | 1702845 | 2310842.24 | 1204765.22 | 11680963.2 | 0 | 0 | 0 | 10968384.96 | 7162539.78 | 23568479.04 | 0 | 5531106.24 | 10487582 | 5332056 | 10344177.9 | 924544.8 | 0 | 175816.278 | 0 | 0 | 27098554 | 0 | 0 | 5102555.8 | 0 | 0 | 88952030.28 | 0 | 12144902.4 | 4267091.32 | 0 | 6789599.19 | 4851302.4 | 21538203.12 | 20092450.56 | 33351062.4 | 20388922.9 | 0 | 679486.6 | 20004777.6 | 204526099 | 5267622.72 | 0 | 6997440 | 433625.4 | 7465910.4 | 19320215.04 | 0 | 0 |  | 923006031.34 | 783744761.028 | 1706750792.368 | 91370667.258 | 66074181 | 53080682.97 | 122996946.46 | 766248312.6 | 231624653 | 755073.09 | 178479710.28 | 149200591.86 | 27860697.6 | 19059276.25 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 0 | 86 | 0 | 402 | 321 |  | 0 | 225 | 0 | 7 | 0 | 30 | 0 | 0 | 0 | 8 | 8 | 50 | 0 | 0 | 0 | 0 | 35 | 55 | 17 | 19 | 25 | 20 | 25 | 16 | 42 | 0 | 76 | 35 | 100 | 0 | 16 | 0 | 0 | 0 | 0 |  | 0 | 26 | 17 | 56 | 12 | 25 | 15 | 2 | 0 | 0 | 0 | 320 | 330 | 166 | 8 | 137 | 31 | 40 | 0 | 51 | 0 | 24 | 16 | 0 | 10 | 21 | 20 | 150 | 81 | 0 | 22 | 2 | 43 | 41 | 33 | 30 | 110 | 0 | 60 | 10 | 0 | 220 | 0 | 31 | 10 | 330 | 8 | 0 | 0 | 195 | 0 | 0 | 48 | 0 | 97 | 13 | 21 | 34 | 122 | 380 | 48 | 88 | 87 | 4 | 50 | 36 | 55 | 17 | 38 | 20 | 0 | 17 | 41 | 54 | 108 | 0 | 35 | 20 | 75 | 55 | 0 |  | 914 | 0 | 150 | 0 | 16 | 221 | 0 | 0 | 0 | 0 | 0 | 85 | 21 | 16 | 0 | 0 | 0 | 24 | 0 | 45 | 0 | 0 | 32 | 8 | 0 | 19 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 178 | 0 | 0 | 213 | 0 | 0 | 146 | 0 | 290 | 0 | 0 | 50 | 88 | 56 | 0 | 6 | 55 | 940 | 220 | 0 | 0 | 3 | 44 | 34 | 0 | 0 |  | 10149 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 200 | 81 | 0 | 397 | 257 | 0 | 0 | 225 | 0 | 48 | 0 | 30 | 0 | 0 | 0 | 48 | 50 | 128 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 27 | 33 | 30 | 49 | 0 | 81 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 6 | 34 | 51 | 33 | 80 | 25 | 15 | 30 | 0 | 0 | 0 | 320 | 305 | 208 | 8 | 129 | 41 | 40 | 0 | 51 | 0 | 38 | 43 | 19 | 10 | 33 | 20 | 160 | 100 | 0 | 20 | 0 | 44 | 41 | 53 | 48 | 110 | 0 | 56 | 81 | 0 | 221 | 0 | 31 | 9 | 275 | 16 | 0 | 195 | 242 | 284 | 96 | 154 | 100 | 149 | 0 | 90 | 34 | 122 | 402 | 106 | 105 | 105 | 0 | 214 | 36 | 73 | 114 | 115 | 100 | 0 | 52 | 0 | 162 | 108 | 0 | 6 | 0 | 75 | 55 | 0 |  | 909 | 0 | 150 | 0 | 32 | 228 | 0 | 0 | 38 | 72 | 8 | 88 | 33 | 64 | 0 | 0 | 0 | 32 | 25 | 80 | 0 | 0 | 32 | 52 | 34 | 21 | 0 | 11 | 0 | 0 | 240 | 0 | 0 | 170 | 0 | 0 | 213 | 0 | 96 | 143 | 0 | 286 | 53 | 172 | 94 | 105 | 91 | 0 | 0 | 95 | 800 | 187 | 0 | 150 | 0 | 0 | 90 | 0 | 0 |  | 13227 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 200 | 93 | 0 | 412 | 330 | 0 | 0 | 225 | 0 | 48 | 0 | 30 | 0 | 0 | 0 | 50 | 30 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 25 | 33 | 33 | 51 | 0 | 83 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 11 | 26 | 51 | 56 | 95 | 32 | 17 | 10 | 0 | 0 | 0 | 330 | 320 | 210 | 8 | 142 | 39 | 55 | 0 | 51 | 0 | 40 | 43 | 22 | 10 | 33 | 20 | 166 | 102 | 0 | 20 | 0 | 43 | 41 | 53 | 49 | 110 | 0 | 61 | 81 | 0 | 220 | 0 | 32 | 10 | 290 | 16 | 11 | 195 | 275 | 284 | 96 | 180 | 100 | 149 | 0 | 90 | 34 | 132 | 400 | 79 | 105 | 90 | 0 | 214 | 36 | 55 | 114 | 113 | 100 | 0 | 104 | 0 | 162 | 108 | 0 | 35 |  | 71 | 55 |  |  | 931 | 0 | 185 | 0 | 16 | 225 | 0 | 0 | 32 | 70 | 8 | 88 | 30 | 64 | 0 | 0 | 0 | 32 | 40 | 86 | 0 | 42 | 32 | 52 | 33 | 21 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 190 | 0 | 0 | 210 | 0 | 96 | 167 | 0 | 350 | 35 | 172 | 94 | 105 | 92 | 0 | 0 | 95 | 600 | 220 |  | 150 |  |  | 90
Forecast for Day | 0 | 0 | 0 | 180 | 200 | 90 | 0 | 412 | 320 | 0 | 0 | 225 | 0 | 8 | 0 | 30 | 0 | 0 | 0 | 8 | 8 | 50 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 25 | 33 | 33 | 51 | 0 | 83 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 11 | 26 | 17 | 56 | 90 | 25 | 17 | 10 | 0 | 0 | 0 | 310 | 305 | 210 | 8 | 142 | 39 | 55 | 0 | 51 | 0 | 32 | 8 | 22 | 10 | 33 | 20 | 143 | 102 | 0 | 20 | 1.6 | 43 | 41 | 33 | 30 | 110 | 0 | 61 | 10 | 0 | 220 | 0 | 31 | 10 | 290 | 8 | 11 | 195 | 110 | 250 | 97 | 48 | 93 | 90 | 20 | 21 | 34 | 128 | 400 | 49 | 105 | 68 | 5 | 50 | 36 | 55 | 17 | 78 | 20 | 0 | 17 | 50 | 70 | 108 | 0 | 35 | 30 | 71 | 55 |  |  | 931 | 0 | 160 | 0 | 16 | 225 | 0 | 0 | 15 | 60 | 0 | 88 | 23 | 64 | 0 | 0 | 0 | 32 | 0 | 80 | 0 | 42 | 32 | 8 | 33 | 21 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 188 | 0 | 0 | 210 | 0 | 60 | 162 | 0 | 350 | 0 | 170 | 50 | 105 | 56 | 0 | 8 | 55 | 600 | 225 |  | 90 | 6 | 100 | 52
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 200 | 84 | 0 | 410 | 320 | 0 | 0 | 225 | 0 | 8 | 0 | 30 | 0 | 0 | 0 | 8 | 8 | 48 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 20 | 33 | 32 | 50 | 0 | 83 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 11 | 26 | 17 | 33 | 16 | 25 | 15 | 4 | 0 | 0 | 0 | 320 | 320 | 206 | 8 | 134 | 39 | 49 | 0 | 51 | 0 | 30 | 8 | 21 | 10 | 33 | 20 | 142 | 95 | 0 | 22 | 0 | 43 | 41 | 31 | 30 | 110 | 0 | 59 | 10 | 0 | 220 | 0 | 31 | 9 | 300 | 8 | 0 | 195 | 95 | 250 | 97 | 48 | 93 | 89 | 0 | 21 | 34 | 118 | 400 | 49 | 105 | 70 | 1 | 50 | 36 | 55 | 17 | 39 | 20 | 0 | 17 | 10 | 35 | 108 | 0 | 35 | 8 | 71 | 55 | 0 | 0 | 914 | 0 | 160 | 0 | 16 | 237 | 0 | 0 | 21 | 60 | 0 | 87 | 19 | 64 | 0 | 0 | 0 | 32 | 0 | 51 | 0 | 0 | 32 | 8 | 33 | 20 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 179 | 0 | 0 | 216 | 0 | 60 | 150 | 0 | 312 | 0 | 169 | 50 | 75 | 56 | 0 | 1 | 55 | 600 | 220 | 0 | 90 | 1 | 47 | 34 | 0 | 0 | 0 |  |  |  |  | 84357232 |  | 0
84357232
| Minimum Generation |  | 10149 | 9:00
| Highest Generation |  | 13227 | 21:00
| Day Peak Generation |  | 10149 | 9:00
| Evening Peak Generation |  | 13227 | 21:00
| HVDC Max Flow |  | 914 | 1:00
| HVDC EvPeak Flow |  | 909 | 21:00
| Load factor L.F |  | 84.44% | [159 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2022-08-07
Till now the maximum generation is : - |  |  | 14782 | 21:00 | Hrs on | 2022-04-16
The Summary of Yesterday's |  | 2022-08-07 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 10149 | MW Hour : | 9:00 | Min. Gen. at | 8:00 | 11166 | MW
Evening Peak Generation : |  | 13227 | MW Hour : | 21:00 | Available Max Generation : |  | 13539 | MW
E.P. Demand (at gen end) : |  | 14200 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 14200 | MW
Maximum Generation : |  | 13227 | MW Hour : | 21:00 | Reserve(Generation end) |  | - | MW
Total Gen. (MKWH) : |  | 268.0395 | System Load Factor : | 84.44% | Load Shed : |  | 609.6207 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | 454 | MW at | 5:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2022-08-07
Actual : | 94.17 | Ft.(MSL) , | Rule curve : | 91.24 | Ft.( MSL )
Gas Consumed : | Total = | 969.5 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 144451350.228
: |  | Coal : | 231624653 | Oil : | 1216925561.2 | Total : | 1593001564.428
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 170 | 4080:00 | 4547.5118 |  |  | 134.3836 | 2.955%
Chittagong Area | 50 | 1200:00 | 1287.6983 |  |  | 66.8175 | 5.189%
Khulna Area | 160 | 3840:00 | 1699.9188 |  |  | 95.1112 | 5.595%
Rajshahi Area | 120 | 2880:00 | 1508.8579 |  |  | 93.0479 | 6.167%
Cumilla Area | 100 | 2400:00 | 1283.7724 |  |  | 74.9066 | 5.835%
Mymensingh Area | 180 | 4320:00 | 1061.3042 |  |  | 67.7103 | 6.38%
Sylhet Area | 80 | 1920:00 | 473.7264 |  |  | 24.6777 | 5.209%
Barisal Area | 0 | 0:00 | 386.0478 |  |  | 0 | 0%
Rangpur Area | 37 | 888:00 | 837.5274 |  |  | 52.9659 | 6.324%
Total | 897 |  | 13086.365 |  |  | 609.6207
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2
2) Ghorasal-3,4
3) Ashuganj-5
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
7) Sikalbaha 225 MW
8) Shajibazar 330 MW
9) Siddhirganj 335 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Aminbazar 230/132 kV T01 transformer was under shut down from 09:59 to 21:56 for C/M.
b) Haripur-Sonargaon 132 kV Ckt-2 was under shut down from 10:25 to 15:04 for C/M.
c) Mohastanghor 132/33 kV T-1 transformer was under shut down from 11:25 to 12:17 for C/M.
d) Tongi S/S-Tongi P/S 230 kV Ckt was under shut down from 12:55 to 17:29 for D/W.
e) Bogura Sherpur 132/33 kV T-1 transformer was under shut down from 08:20 to 09:46 for C/M. | [5 empty] | About 30 MW power interruption occurred under
Bogura Sherpur S/S area from 08:20 to 09:46.
f) Niamatpur 132/33 kV T-1 & T-2 transformer 33 kV bus was under shut down from 09:45 to 10:54 due to 33 kV | [5 empty] | About 25 MW power interruption occurred under
bus coupler Y phase pole problem. | [5 empty] | Niamatpur S/S area from 09:45 to 10:54.
g) Ghorasal #07 GT was synchronized at 19:52.
h) Haripur-Sonargaon 132 kV Ckt-1 was under shut down from 15:15 to 17:07 for D/W.
i) Ghorasal-Ishurdi 230 kV Ckt-1 tripped at 14:02 showing dist C phase Z1 at Ishurdi end & dist B phase Z1 at
Ghorasal end and was switched on at 14:23.
j) Chapainawabganj 132/33 kV T-1 transformer was under shut down from 22:05 to 00:59 due to 33 kV CT red
hot maintenance.
| Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2022-08-07 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4315500
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 200 | 687100
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 81 | 2080454 | Engine problem
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 397 | 9773060 | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 257 | 7262000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 4975150 | Gas shortage & GT-2 S/D.
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 48 | 463680 | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 0 | 0 | Under maint.
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 30 | 751006 | Engine problem
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 456948
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 48 | 461933 | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 50 | 459216 | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 894600
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 128 | 1740480 | Engine problem
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 1308761
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 626577 | Engine problem
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 52 | 1139100 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 586000 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 30 | 649400
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 49 | 1141920 | #REF!
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 242 | 4927852 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 284 | 1815668
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 96 | 686089
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 100 | 705761
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 2784960
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 2208000
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 52 | 554880 | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 2822400
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 257725
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 55 | 1312560
| Dhaka area Total |  |  |  | 5847 | 3239 | 57848780
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 100 | 2400000 | Machine problem
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 25 | 317142
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 116640
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 25 | 605760 | Engine problem
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 116 | 2796567 | Low water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | HGPI for 30 days.
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 105 | 2221382
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 34 | 655824 | Fuel shortage
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 909799 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 33 | 1039320 | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 90 | 981120 | Engine problem
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 15 | 331824 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 30 | 521280
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 80 | 650880 | Engine problem
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 34439
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 214 | 1656000 | Engine problem
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 36 | 769538 | Fuel shortage
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 73 | 1441053 | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 1045440
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 108 | 2608200 | Engine problem
| Chattogram area Total |  |  |  | 2382 | 1235 | 21102208
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 208 | 4649000 | #REF!
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 320 | 7969400 | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 305 | 7525000 | Gas shortage
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+136*1 | 284 | 0 | 0 | On test.
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 41 | 876024 | Machine problem
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 40 | 702720 | Gas shortage
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 669090
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1156134
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 122 | 2944000 | Engine problem
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 38 | 791304 | Engine problem
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 129 | 3203990 | Machine problem
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 34 | 850080 | Fuel shortage
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 323856
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 10 | 238500
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 160 | 3880320
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 767300
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 43 | 422918 | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 20 | 487130 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 195 | 1072896
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 1089840
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 115 | 1700160
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 6 | 849960 | 33 kV feeder problem.
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 75 | 1683840 | Fuel shortage
| Cumilla Area Total |  |  |  | 3169 | 2086 | 43853462
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 100 | 2149440 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 441756
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 16000
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 154 | 1812000 | Engine problem
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 106 | 1368000 | Engine problem
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 400130
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 37680 | Engine problem
| Mymensingh Area Total |  |  |  | 614 | 386 | 6225006
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 44 | 1015000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 41 | 967424 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 110 | 2542336 | ST under maint.
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 997800
| Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 48 | 925488
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 0 | 0
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 56 | 1423008
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 857280 | Engine problem
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 221 | 5156820
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50MW PP (EPL) |  | NENP | 27*2 | 50 | 31 | 718000 | Gas shortage
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 238560 | Engine problem
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 275 | 7541500 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 402 | 9456000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 9 | 231120
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 0 | 0 | Under maint.
| Sylhet Area Total |  |  |  | 2477 | 1387 | 32070336
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 909 | 22024727
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 32 | 474240 | Fuel shortage
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 38 | 304800 | Engine problem
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 228 | 5425920
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 72 | 715392 | Line O/L
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 150 | 3726432 | Gas shortage.
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 8 | 118500 | Fuel shortage
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 96 | 578880
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 53 | 360960 | Fuel shortage
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 105 | 2308032
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 636480
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 0 | 0 | 0 | On test.
| Khulna Area Total |  |  |  | 2384 | 1691 | 36674363
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 64 | 1071648 | Line O/L
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 33 | 621013 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 88 | 2063252 | ST under S/D
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 800 | 22699900 | Coal shortage
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 187 | 5164336
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 150 | 945600
| Barisal Area Total |  |  |  | 1958 | 1322 | 32565749
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 32 | 654048 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 25 | 409522 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contract Expired
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 334004 | Engine problem
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 620200 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 170 | 4398755 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 213 | 5094618
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 143 | 3678527 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 286 | 6858181 | Gas shortage
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 34 | 613170 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 21 | 446640
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | .
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 232254
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 391200
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 80 | 1506936 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 172 | 1027096 | Fuel conservation
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 94 | 1698432 | Engine problem
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 95 | 1647840 | Engine problem
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 38340
| Rajshahi Area Total |  |  |  | 2129 | 1460 | 29649763
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 240 | 5122600 | Coal shortage
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 91 | 1605427 | Engine problem
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 61492
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 90 | 1260288 | Fuel shortage
| Rangpur Area Total |  |  |  | 720 | 421 | 8049807
| Total |  |  |  | 21680 | 13227 | 268039474
| Eastern Grid Total |  |  |  | 14489 | 8333 | 161099792
| Western Grid Total |  |  |  | 7191 | 4894 | 106939682
| National Grid Total |  |  |  | 21680 | 13227 | 268039474
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2022-08-07
(a) ENTIRE EASTERN GRID : |  | 8562.28 | MW | (b) ENTIRE WESTERN GRID : |  | 4041.26 | MW
i) Dhaka area |  | 4821.78 | MW | i) Khulna area |  | 1480 | MW
ii) Chittagong area |  | 1245.5 | MW | ii) Rajshahi area |  | 1251.4 | MW
iii) Comilla area |  | 1168 | MW | iii) Barisal area |  | 401.86 | MW
iv) Mymensingh area |  | 839 | MW | iv) Rangpur area |  | 908 | MW
v) Sylhet area |  | 488 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 12603.54 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
AKS | 19 | 08:00 | Chowmuhani | 182 | 22:00 | Kaptai | 5 | 19:30 | Nawabganj | 36.9 | 19:00 | Siddhirganj | 108 | 22:00
AKSML | 127 | 07:00 | Chuadanga | 92 | 18:00 | Kazla | 92 | 19:30 | Netrakona | 96 | 19:00 | Sirajganj | 88 | 07:00
Aftabnagar | 35 | 20:00 | Coxsbazar | 122 | 20:00 | Keranigonj | 64 | 21:00 | New | 81 | 09:00 | Sonargaon | 80 | 12:00
Agargaon | 95 | 10:00 | Cumilla(N) | 154 | 23:00 | Khagrachori | 24 | 19:00 | Niamatpur | 64 | 06:00 | Sreemongol | 44 | 12:00
Agrabad | 72 | 17:00 | Cumilla(S) | 182 | 15:00 | Khulna | 88 | 22:00 | Noapara | 47 | 01:00 | Srinagar | 46.28 | 21:00
Amnura | 52 | 22:00 | Daudkandi | 159 | 19:00 | Khulshi | 170 | 19:00 | PHP | 11 | 10:00 | Sunamganj | 38 | 22:00
Ashuganj | 41 | 19:00 | Dhaka | 44 | 14:00 | Kishoreganj | 104 | 21:00 | Pabna | 89 | 00:00 | Sylhet | 136 | 00:00
BSRM | 137 | 11:00 | Dhamrai | 114 | 20:00 | Kodda | 327 | 18:30 | Palashbari | 108 | 23:00 | TK | 28.5 | 19:00
Bagerhat | 91 | 23:00 | Dhanmondi | 160.1 | 16:00 | Kulaura | 40 | 22:00 | Panchagarh | 46 | 08:00 | Tangail | 195 | 22:00
Bakulia | 107 | 20:00 | Dohazari | 90 | 22:00 | Kurigram | 58 | 21:00 | Patuakhali | 133 | 22:00 | Thakurgaon | 66 | 22:00
Banani | 57 | 13:00 | Faridpur | 135 | 22:00 | Kushtia | 132 | 18:00 | Payra | 1.02 | 16:00 | Tongi | 116 | 19:30
Bangabhaban | 22 | 10:00 | Fatullah | 69 | 10:00 | Lalbag | 80 | 00:00 | Purbachal | 20 | 21:00 | Ullon | 40 | 21:00
Barapukuria | 51 | 23:00 | Fenchuganj | 43 | 22:00 | Lalmonirhat | 54 | 21:00 | Purbasadipur | 96 | 05:00 | Uttara | 93 | 21:00
Barguna | 20 | 00:00 | Feni | 96 | 21:00 | Madanganj | 65 | 20:00 | Rahim | 26 | 08:00 | UttaraNew | 18 | 00:00
Barishal | 109 | 23:00 | GPH | 94 | 02:00 | Madaripur | 106 | 00:00 | Rajbari | 60 | 19:30 | Zigatola | 57 | 19:00
Barishal-230 | 76 | 21:00 | Ghorashal | 46 | 13:00 | Madartek | 90 | 23:00 | Rajendrapur | 92 | 05:00
Baroaulia | 70 | 08:00 | Goalpara | 26 | 00:00 | Madunaghat | 73 | 00:00 | Rajshahi | 132 | 22:00
Baroirhat | 68 | 21:00 | Gollamari | 46 | 18:30 | Magura | 52 | 18:00 | Rajshahi-230 | 26 | 02:00
Bashundhara | 169 | 19:30 | Gopalganj | 106.4 | 23:00 | Mahasthangarh | 60 | 19:00 | Ramganj | 88 | 19:00
BashundharaCement | 8 | 12:00 | Gulshan | 104 | 10:00 | Manikganj | 102 | 21:00 | Rampur | 16 | 00:00
Beanibazar | 50 | 22:00 | Halishahar | 86.5 | 17:00 | Maniknagar | 83 | 13:00 | Rangamati | 14 | 19:00
Benapole | 48 | 19:00 | HaripurSBU | 140 | 15:00 | Matarbari | 45 | 23:00 | Rangpur | 105 | 08:00
Bhaluka | 86 | 21:00 | Hasnabad | 101 | 21:00 | Matuail | 60 | 09:00 | Ruppur | 5 | 09:00
Bhandaria | 52 | 22:00 | Hathazari | 102 | 20:00 | Millgate | 53 | 08:00 | SSM | 3 | 05:00
Bhangura | 30 | 21:00 | Ishurdi | 72 | 19:00 | Mirpur | 126 | 22:00 | Saidpur | 93 | 08:00
Bheramara(GK) | 62 | 23:00 | Jaldhaka | 73 | 21:00 | Mirsorai | N/A | N/A | Satkhira | 95 | 06:00
Bhulta | 259 | 23:00 | Jamalpur | 102 | 21:00 | Mithapukur | 38 | 18:00 | Satmasjid | 101 | 19:00
Bog-Sherpur | 53 | 23:00 | Jashore | 122 | 21:00 | Modern | 0 | 00:00 | Savar | 156 | 09:00
Bogura | 150 | 19:30 | Jhenaidah | 108 | 18:00 | Mogbazar | 130 | 12:00 | Shahjadpur | 85 | 22:00
Borhanuddin | 43 | 00:00 | Joydebpur | 209 | 19:30 | Mongla | 36 | 11:00 | Shahjibazar | 95 | 00:00
Brahmanbaria | 154 | 21:00 | Joypurhat | 58 | 22:00 | Motijheel | 36 | 10:00 | Shahmirpur | 46.5 | 18:30
Cantonment | 150 | 22:00 | Juldah | 27 | 23:00 | Munshiganj | 104 | 21:00 | Shariatpur | 78 | 22:00
Chandpur | 69 | 19:00 | KSRM | 29.9 | 16:00 | Mymensingh | 208 | 19:30 | Sherpur | 100 | 19:00
Chandraghona | 32 | 20:00 | Kabirpur | 269 | 16:00 | Naogaon | 116 | 23:00 | Shikalbaha | 28 | 19:00
Chapai | 62 | 19:00 | Kachua | 64 | 22:00 | Narail | 44 | 22:00 | Shikalbaha-230 | N/A | N/A
Charsaidpur | 44 | 00:00 | Kallyanpur | 90 | 15:00 | Narinda | 72.2 | 16:00 | Shitalakhya | 114 | 12:00
Chauddagram | 54 | 21:00 | Kalurghat | 26 | 19:30 | Narshingdi | 208 | 23:00 | Sholosohor | N/A | N/A
Chhatak | 23 | 23:00 | Kamrangirchar | 58 | 13:00 | Natore | 122 | 23:00 | Shyampur | 144 | 01:00
Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
(1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2022-08-07 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Bhulta | 385 | 19:00 | 363 | 09:00 | Kaliakoir | 390 | 19:00 | 375 | 09:00
| Bibiana | 410 | 19:00 | 394 | 09:00 | Payra | 416 | 16:00 | 408 | 00:00
| BIPTC | 404 | 17:00 | 394 | 21:00 | Rahanpur_I
| Gopalganj_I | 412 | 15:00 | 393 | 02:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 220 | 19:30 | 208 | 09:00 | Hasnabad | 222 | 21:00 | 210 | 09:00
| AKSML | 235 | 19:00 | 221 | 05:00 | Hathazari | 237 | 19:00 | 221 | 04:00
| Aminbazar | 223 | 19:00 | 210 | 09:00 | Ishurdi | 237 | 16:00 | 225 | 09:00
| Ashuganj | 238 | 19:00 | 225 | 09:00 | Jhenaidah | 232 | 16:00 | 220 | 04:00
| Baghabari | 233 | 16:00 | 226 | 09:00 | Kaliakoir | 224 | 19:00 | 211 | 09:00
| Barapukuria | 223 | 17:00 | 209 | 21:00 | Keranigonj | 220 | 21:00 | 207 | 09:00
| Barishal | 245 | 17:00 | 238 | 00:00 | Khulna(S) | 239 | 16:00 | 226 | 07:00
| Bheramara | 233 | 15:00 | 220 | 09:00 | Maniknagar | 222 | 19:00 | 211 | 09:00
| Bhulta | 226 | 19:00 | 213 | 09:00 | Meghnaghat | 254 | 03:00 | 216 | 09:00
| Bibiana | 239 | 19:00 | 230 | 09:00 | Mirsorai
| BIPTC | 236 | 15:00 | 223 | 09:00 | Rajshahi | 233 | 16:00 | 222 | 09:00
| Bogura | 228 | 15:00 | 219 | 21:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 248 | 13:00 | 244 | 00:00 | Rampura | 224 | 21:00 | 220 | 20:00
| BSRM | 233 | 19:30 | 220 | 05:00 | Shikalbaha | 236 | 19:30 | 222 | 08:00
| Cumilla(N) | 228 | 19:30 | 215 | 09:00 | Shyampur | 221 | 21:00 | 209 | 09:00
| Fenchuganj | 243 | 19:00 | 235 | 11:00 | Siddhirganj | 223 | 19:30 | 213 | 09:00
| Ghorashal | N/A | N/A | N/A | N/A | Sirajgonj | 232 | 16:00 | 226 | 08:00
| GPH | 234 | 19:00 | 219 | 05:00 | Tongi | 224 | 19:00 | 210 | 09:00
| Haripur | 222 | 21:00 | 211 | 09:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 135 | 15:00 | 128 | 09:00 | Lalbag | 138 | 21:00 | 128 | 09:00
| Agargaon | 136 | 14:00 | 128 | 09:00 | Lalmonirhat | 132 | 23:00 | 113 | 20:00
| Agrabad | 135 | 14:00 | 128 | 08:00 | Madanganj | 132 | 19:30 | 125 | 09:00
| AKS | 136 | 18:00 | 126 | 09:00 | Madaripur | 138 | 13:00 | 133 | 00:00
| Aminbazar | 134 | 21:00 | 126 | 09:00 | Madartek | 136 | 21:00 | 128 | 09:00
| Amnura | 132 | 16:00 | 126 | 07:00 | Madunaghat | 140 | 19:00 | 130 | 07:00
| Ashuganj | 136 | 14:00 | 135 | 00:00 | Magura | 140 | 15:00 | 126 | 07:00
| Bagerhat | 137 | 15:00 | 128 | 05:00 | Mahasthangarh | 135 | 15:00 | 127 | 20:00
| Bakulia | 137 | 19:00 | 130 | 06:00 | Manikganj | 134 | 19:00 | 129 | 22:00
| Banani | 132 | 15:00 | 123 | 09:00 | Maniknagar | 132 | 20:00 | 125 | 03:00
| Bangabhaban | 132 | 19:00 | 125 | 11:00 | Matarbari | 135 | 19:00 | 115 | 21:00
| Barapukuria | 136 | 16:00 | 125 | 21:00 | Matuail | 131 | 19:30 | 125 | 09:00
| Barguna | 137 | 17:00 | 127 | 19:00 | Millgate | 133 | 19:00 | 125 | 09:00
| Barishal | 138 | 10:00 | 124 | 19:00 | Mirpur | 131 | 02:00 | 124 | 09:00
| Barishal-230 | 139 | 13:00 | 134 | 00:00 | Mithapukur | 134 | 16:00 | 121 | 21:00
| Baroaulia | 142 | 19:00 | 131 | 07:00 | Modern | 138 | 19:00 | 130 | 06:00
| Baroirhat | 135 | 18:00 | 126 | 05:00 | Mogbazar | 136 | 21:00 | 130 | 09:00
| Bashundhara | 132 | 15:00 | 123 | 09:00 | Mongla | 137 | 15:00 | 127 | 04:00
| BashundharaCement | 132 | 19:30 | 125 | 09:00 | Motijheel | 132 | 19:30 | 126 | 09:00
| Beanibazar | 133 | 15:00 | 130 | 05:00 | Munshiganj | 132 | 19:30 | 125 | 09:00
| Benapole | 136 | 15:00 | 129 | 03:00 | Mymensingh | 131 | 18:00 | 119 | 00:00
| Bhaluka | 131 | 18:00 | 118 | 00:00 | Naogaon | 134 | 15:00 | 126 | 03:00
| Bhandaria | 137 | 18:00 | 128 | 00:00 | Narail | 138 | 15:00 | 128 | 03:00
| Bhangura | 139 | 16:00 | 134 | 03:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bheramara | 137 | 15:00 | 132 | 03:00 | Narshingdi | 137 | 19:00 | 124 | 23:00
| Bheramara(GK) | 137 | 13:00 | 133 | 05:00 | Natore | 134 | 15:00 | 129 | 03:00
| Bhulta | 125 | 13:00 | 121 | 04:00 | Nawabganj | 137 | 21:00 | 127 | 11:00
| Bog-Sherpur | 137 | 16:00 | 130 | 04:00 | Netrakona | 129 | 10:00 | 118 | 00:00
| Bogura | 136 | 13:00 | 130 | 20:00 | New | 132 | 15:00 | 123 | 09:00
| Bogura-230 | 137 | 15:00 | 131 | 21:00 | Niamatpur | 133 | 16:00 | 123 | 21:00
| Brahmanbaria | 133 | 18:00 | 129 | 09:00 | Noapara | 140 | 18:00 | 130 | 07:00
| Cantonment | 134 | 19:30 | 126 | 09:00 | Pabna | 136 | 16:00 | 130 | 03:00
| Chandpur | 135 | 18:00 | 130 | 06:00 | Palashbari | 131 | 13:00 | 120 | 21:00
| Chandraghona | 140 | 19:00 | 132 | 04:00 | Panchagarh | 135 | 17:00 | 112 | 21:00
| Chapai | 131 | 00:00 | 127 | 03:00 | Patuakhali | 137 | 13:00 | 131 | 19:00
| Charsaidpur | 132 | 19:30 | 123 | 09:00 | Payra | 139 | 15:00 | 134 | 19:00
| Chauddagram | 134 | 18:00 | 126 | 08:00 | PHP | 135 | 19:30 | 125 | 05:00
| Chhatak | 132 | 05:00 | 129 | 06:00 | Postogola | 138 | 21:00 | 128 | 09:00
| Chowmuhani | 133 | 14:00 | 128 | 12:00 | Purbachal | 133 | 19:00 | 123 | 09:00
| Chuadanga | 136 | 15:00 | 127 | 18:30 | Purbasadipur | 134 | 00:00 | 115 | 20:00
| Coxsbazar | 131 | 19:00 | 110 | 20:00 | Rahim | 132 | 14:00 | 126 | 09:00
| Cumilla(N) | 135 | 19:30 | 129 | 06:00 | Rajbari | 136 | 16:00 | 127 | 06:00
| Cumilla(S) | 135 | 19:30 | 124 | 15:00 | Rajendrapur | 136 | 19:30 | 128 | 22:00
| Daudkandi | 135 | 19:30 | 125 | 00:00 | Rajshahi | 133 | 16:00 | 127 | 09:00
| Dhaka | 137 | 21:00 | 129 | 09:00 | Rajshahi-230 | 132 | 13:00 | 127 | 09:00
| Dhamrai | 129 | 15:00 | 122 | 09:00 | Ramganj | 133 | 15:00 | 124 | 06:00
| Dhanmondi | 131.5 | 21:00 | 124.3 | 09:00 | Rampur | 138 | 19:00 | 129 | 09:00
| Dohazari | 136 | 19:00 | 128 | 07:00 | Rampura | 136 | 21:00 | 127 | 09:00
| Faridpur | 136 | 16:00 | 128 | 03:00 | Rangamati | 138 | 19:00 | 131 | 06:00
| Fatullah | 136 | 21:00 | 126 | 09:00 | Rangpur | 132 | 16:00 | 117 | 21:00
| Fenchuganj | 138 | 19:30 | 134 | 04:00 | Ruppur | 138 | 19:00 | 131 | 09:00
| Feni | 136 | 19:30 | 127 | 04:00 | Saidpur | 133 | 00:00 | 120 | 21:00
| Ghorashal | 138 | 12:00 | 135 | 00:00 | Satkhira | 137 | 15:00 | 128 | 07:00
| Goalpara | 139 | 15:00 | 131 | 04:00 | Satmasjid | 135 | 19:30 | 128 | 09:00
| Gollamari | 137 | 13:00 | 131 | 07:00 | Savar | 133 | 19:30 | 125 | 11:00
| Gopalganj | 140 | 16:00 | 133 | 07:00 | Shahjadpur | 140 | 00:00 | 135 | 08:00
| Gopalganj_I | 141 | 15:00 | 133 | 02:00 | Shahjibazar | 135 | 16:00 | 131 | 02:00
| Gulshan | 136 | 21:00 | 127 | 09:00 | Shahmirpur | 141 | 19:00 | 130 | 08:00
| Halishahar | 140 | 19:00 | 129 | 09:00 | Shariatpur | 136 | 17:00 | 130 | 00:00
| Haripur | 132 | 14:00 | 126 | 09:00 | Sherpur | 135 | 18:00 | 118 | 00:00
| HaripurSBU | 132 | 19:00 | 125 | 10:00 | Shikalbaha | 140 | 19:30 | 129 | 07:00
| Hasnabad | 140 | 21:00 | 129 | 10:00 | Shikalbaha-230 | 139 | 19:30 | 131 | 08:00
| Hathazari | 138 | 19:00 | 129 | 08:00 | Shitalakhya | 138 | 21:00 | 125 | 10:00
| Ishurdi | 138 | 15:00 | 132 | 02:00 | Sholosohor
| Jaldhaka | 132 | 17:00 | 113 | 21:00 | Shyampur | 135 | 19:00 | 123 | 09:00
| Jamalpur | 137 | 18:00 | 120 | 00:00 | Shyampur-230 | 135 | 19:30 | 126 | 09:00
| Jashore | 136 | 15:00 | 129 | 05:00 | Siddhirganj | 131 | 14:00 | 125 | 09:00
| Jhenaidah | 141 | 16:00 | 133 | 05:00 | Sirajganj | 136 | 16:00 | 131 | 21:00
| Jhenaidah-230 | 141 | 15:00 | 133 | 07:00 | Sonargaon | 132 | 13:00 | 123 | 08:00
| Joydebpur | 142 | 17:00 | 134 | 09:00 | Sreemongol | 136 | 12:00 | 134 | 07:00
| Joypurhat | 134 | 16:00 | 125 | 04:00 | Srinagar | 138 | 19:00 | 127 | 11:00
| Juldah | 140 | 19:00 | 130 | 15:00 | SSM | 139 | 18:00 | 132 | 07:00
| Kabirpur | 137 | 19:00 | 120 | 09:00 | Sunamganj | 131 | 15:00 | 128 | 03:00
| Kachua | 134 | 17:00 | 128 | 05:00 | Sylhet | 134 | 01:00 | 132 | 22:00
| Kaliakoir | 138 | 19:00 | 128 | 14:00 | Tangail | 135 | 10:00 | 127 | 16:00
| Kallyanpur | 132 | 19:30 | 126 | 09:00 | Thakurgaon | 134 | 00:00 | 114 | 21:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2022-08-07
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 996 | 7455 | 4704 | 12159 |  |  |  | QF-LDC-11
0:30 | 818 | 7002 | 4593 | 11595 | Date: | 2022-08-07
1:00 | 640 | 6549 | 4482 | 11031
1:30 | 621 | 6429 | 4475 | 10904
2:00 | 602 | 6309 | 4468 | 10777
2:30 | 584 | 6307.5 | 4468.5 | 10776 | [5 empty] | Gen. at Eve. Peak | 13227 | 13227 MW (21:00 )
3:00 | 566 | 6306 | 4469 | 10775 | [6 empty] | 21:00
3:30 | 547 | 6271.5 | 4473.5 | 10745 | [5 empty] | Gen. at Day Peak | 10149 | 10149 MW (09:00 )
4:00 | 528 | 6237 | 4478 | 10715 | [6 empty] | 9:00
4:30 | 491 | 6263 | 4467.5 | 10730.5 | [5 empty] | Highest Generation | 13227
5:00 | 454 | 6289 | 4457 | 10746 | [6 empty] | 21:00
5:30 | 454 | 6193 | 4390 | 10583
6:00 | 454 | 6097 | 4323 | 10420
6:30 | 486 | 6129 | 4306 | 10435
7:00 | 518 | 6161 | 4289 | 10450
7:30 | 575 | 6110 | 4260 | 10370
8:00 | 632 | 6059 | 4231 | 10290
8:30 | 771 | 6061.5 | 4158 | 10219.5
9:00 | 910 | 6064 | 4085 | 10149
9:30 | 996 | 5993.5 | 4058.5 | 10052
10:00 | 1082 | 5923 | 4032 | 9955
10:30 | 1030 | 5981.5 | 4047 | 10028.5
11:00 | 978 | 6040 | 4062 | 10102
11:30 | 961 | 5982.5 | 4024 | 10006.5
12:00 | 944 | 5925 | 3986 | 9911
12:30 | 924 | 6070 | 3973.5 | 10043.5
13:00 | 904 | 6215 | 3961 | 10176
13:30 | 883 | 6312.5 | 3946 | 10258.5
14:00 | 862 | 6410 | 3931 | 10341
14:30 | 963 | 6503.5 | 3895 | 10398.5
15:00 | 1064 | 6597 | 3859 | 10456
15:30 | 1044 | 6540 | 3909 | 10449
16:00 | 1024 | 6483 | 3959 | 10442
16:30 | 1012 | 6610 | 4013.5 | 10623.5
17:00 | 1000 | 6737 | 4068 | 10805
17:30 | 978 | 6857.5 | 4135 | 10992.5
18:00 | 956 | 6978 | 4202 | 11180
18:30 | 875 | 7307.5 | 4292 | 11599.5
19:00 | 794 | 7637 | 4382 | 12019
19:30 | 754 | 7765 | 4721 | 12486
20:00 | 772 | 7821 | 4869 | 12690 |  |  |  | Executive Engineer
20:30 | 754 | 8077 | 4881.5 | 12958.5 |  |  |  | Network Operation Division
21:00 | 736 | 8333 | 4894 | 13227
21:30 | 799 | 8307 | 4918 | 13225
22:00 | 862 | 8281 | 4942 | 13223 |  |  |  |  | Page 6 of 7
22:30 | 902 | 8249 | 4859.5 | 13108.5
23:00 | 942 | 8217 | 4777 | 12994
23:30 | 969 | 7836 | 4740.5 | 12576.5
24:00 | 996 | 7455 | 4704 | 12159
13227 MW (21:00 )
10149 MW (09:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2022-08-07 |  | Energy |  | 268039474
[13 empty] | 2022-08-07 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 3598 | 909 | 1898 | 934 | 2588 | 1040 | 116 | 438 | 687 | 162 | 0 | 0
0:30 | 3495 | 911.5 | 1954 | 467 | 2433 | 1155 | 114.5 | 434.5 | 676.5 | 167 | 0 | 769.0543 | Date: | 2022-08-07
1:00 | 3392 | 914 | 2010 | 0 | 2278 | 1270 | 113 | 431 | 666 | 172 | 0 | 1538.1087
1:30 | 3344 | 914 | 2006.5 | 0 | 2193.5 | 1280 | 113 | 434 | 661.5 | 172 | 0 | 1609.0699 | [8 empty] | Total Energy | 268.0395 | Total Energy Gen 268.039 MKWHr Energy Not Served 31.983 MKWHr Energy Requirement 300.022 MKWHr
2:00 | 3296 | 914 | 2003 | 0 | 2109 | 1290 | 113 | 437 | 657 | 172 | 0 | 1680.0312 | [8 empty] | Energy not Served | 31.9825
2:30 | 3332 | 913.5 | 1970 | 0 | 2109.5 | 1285 | 113 | 439 | 657.5 | 171 | 0 | 1634.874 | [8 empty] | Energy Requirement | 300.022
3:00 | 3368 | 913 | 1937 | 0 | 2110 | 1280 | 113 | 441 | 658 | 170 | 0 | 1589.7169
3:30 | 3369 | 913 | 1929 | 0 | 2105 | 1280 | 113 | 441 | 641 | 169 | 0 | 1571.2854 | [6 empty] | Shortage
4:00 | 3370 | 913 | 1921 | 0 | 2100 | 1280 | 113 | 441 | 624 | 168 | 0 | 1552.8539
4:30 | 3406 | 913.5 | 1908.5 | 0 | 2098 | 1275 | 113.5 | 441 | 624 | 166 | 0 | 1400.3332
5:00 | 3442 | 914 | 1896 | 0 | 2096 | 1270 | 114 | 441 | 624 | 164 | 0 | 1247.8126
5:30 | 3401 | 914 | 1909 | 0 | 2039.5 | 1255 | 114 | 440 | 562 | 157 | 5.5 | 1167.6355
6:00 | 3360 | 914 | 1922 | 0 | 1983 | 1240 | 114 | 439 | 500 | 150 | 11 | 1087.4585
6:30 | 3388.5 | 913.5 | 1913 | 0 | 1983 | 1235 | 113 | 439 | 492 | 145 | 26.5 | 1027.5561 |  |  |  |  | Coal
7:00 | 3417 | 913 | 1904 | 0 | 1983 | 1230 | 112 | 439 | 484 | 140 | 42 | 967.6537
7:30 | 3345.5 | 913.5 | 1883.5 | 0 | 1991 | 1205 | 113 | 438.5 | 471.5 | 144 | 78.5 | 1133.5372 |  |  |  | Oil |  |  |  | ,
8:00 | 3274 | 914 | 1863 | 0 | 1999 | 1180 | 114 | 438 | 459 | 148 | 115 | 1299.4207
8:30 | 3268 | 914 | 1850 | 0 | 1974.5 | 1160 | 112.5 | 436 | 445 | 149 | 124 | 1456.5493
9:00 | 3262 | 914 | 1837 | 0 | 1950 | 1140 | 111 | 434 | 431 | 150 | 133 | 1613.6778
9:30 | 3232.5 | 914 | 1805 | 0 | 1919.5 | 1134.5 | 112 | 431 | 422.5 | 145 | 144 | 1795.2281
10:00 | 3203 | 914 | 1773 | 0 | 1889 | 1129 | 113 | 428 | 414 | 140 | 155 | 1976.7784
10:30 | 3246 | 914 | 1767 | 0 | 1889.5 | 1129.5 | 113.5 | 427.5 | 416 | 151 | 176 | 2001.2001
11:00 | 3289 | 914 | 1761 | 0 | 1890 | 1130 | 114 | 427 | 418 | 162 | 197 | 2025.6218
11:30 | 3253 | 914 | 1756.5 | 0 | 1866.5 | 1074.5 | 114 | 427 | 433.5 | 163 | 204.5 | 2159.711
12:00 | 3217 | 914 | 1752 | 0 | 1843 | 1019 | 114 | 427 | 449 | 164 | 212 | 2293.8002
12:30 | 3241.5 | 913.5 | 1758.5 | 0 | 1940 | 1019.5 | 114.5 | 413.5 | 458 | 166 | 203.5 | 2125.6127
13:00 | 3266 | 913 | 1765 | 0 | 2037 | 1020 | 115 | 400 | 467 | 168 | 195 | 1957.4253
13:30 | 3266 | 913 | 1765 | 0 | 2037 | 1020 | 115 | 400 | 467 | 168 | 195 | 1957.4253
14:00 | 3266 | 913 | 1765 | 0 | 2037 | 1020 | 115 | 400 | 467 | 168 | 195 | 1957.4253
14:30 | 3281 | 910 | 1773 | 50 | 2224 | 935 | 115 | 375.5 | 451 | 175 | 176.5 | 1920.7126
15:00 | 3296 | 907 | 1781 | 100 | 2411 | 850 | 115 | 351 | 435 | 182 | 158 | 1884
15:30 | 3244 | 907 | 1758 | 220.5 | 2337.5 | 835 | 115.5 | 374 | 500 | 173 | 137.5 | 1844
16:00 | 3192 | 907 | 1735 | 341 | 2264 | 820 | 116 | 397 | 565 | 164 | 117 | 1804
16:30 | 3227 | 907 | 1741.5 | 403 | 2380.5 | 810.5 | 117 | 416 | 590 | 162 | 79 | 1545
17:00 | 3227 | 907 | 1748 | 465 | 2497 | 801 | 118 | 435 | 615 | 160 | 41 | 1286
17:30 | 3229.5 | 906.5 | 1751.5 | 439.5 | 2693 | 805 | 118 | 435 | 637 | 159 | 28.5 | 1020.8458
18:00 | 3232 | 906 | 1755 | 414 | 2889 | 809 | 118 | 435 | 659 | 158 | 16 | 755.6915
18:30 | 3237.5 | 906.5 | 1790 | 588.5 | 3010.5 | 859.5 | 118 | 434.5 | 699.5 | 158 | 8 | 921.8458
19:00 | 3243 | 907 | 1825 | 763 | 3132 | 910 | 118 | 434 | 740 | 158 | 0 | 1088
19:30 | 3268 | 909 | 1842 | 711 | 3446 | 1030 | 118 | 439 | 776 | 160 | 0 | 1072.7133
20:00 | 3340 | 909 | 1864 | 714 | 3544 | 1041 | 118 | 441 | 773 | 160 | 0 | 1207.2632
20:30 | 3458 | 909 | 1845 | 828.5 | 3598 | 1040.5 | 117 | 441 | 775 | 160 | 0 | 1051.9779
21:00 | 3576 | 909 | 1826 | 943 | 3652 | 1040 | 116 | 441 | 777 | 160 | 0 | 896.6925
21:30 | 3583 | 909 | 1862.5 | 870 | 3672 | 1040 | 116 | 440 | 780 | 165 | 0 | 852.4569
22:00 | 3590 | 909 | 1899 | 797 | 3692 | 1040 | 116 | 439 | 783 | 170 | 0 | 808.2213
22:30 | 3587 | 909 | 1907.5 | 875 | 3507.5 | 1040 | 116 | 438.5 | 773.5 | 166 | 0 | 821.5841
23:00 | 3584 | 909 | 1916 | 953 | 3323 | 1040 | 116 | 438 | 764 | 162 | 0 | 834.947
23:30 | 3591 | 909 | 1907 | 943.5 | 2955.5 | 1040 | 116 | 438 | 725.5 | 162 | 0 | 417.4735 | Max Temp. in Dhaka |  | 24.7° C | 35.4° C
24:00 | 3598 | 909 | 1898 | 934 | 2588 | 1040 | 116 | 438 | 687 | 162 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 268.039 MKWHr Energy Not Served 31.983 MKWHr Energy Requirement 300.022 MKWHr
Note on W13: Author:
Note on Z14: Author:
Note on AA17: Author:
Note on AA19: Author:
Note on AA21: Author:

## Generation
g | 2022-08-07
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 78 | 78 | 78 | 78 | 79 | 79 | 77 | 79 | 76 | 78 | 79 | 79 | 80 | 80 | 80 | 81 | 83 | 83 |  | 83 | 83 | 83 | 81 | 81 | 81 | 81 | 1956567
2 | Karnaphuli Hydro PP Unit-4 & 5 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 840000
3 | Chattogram TPP-1 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 98 | 98 | 98 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2400000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 0 | 7 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 0 | [6 empty] | 13 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 317142
| Teknaf 20MW PP (Solartech) |  |  |  |  | 0 | 1 | 3 | 13 | 13 | 11 | 14 | 14 | 19 | 19 | 15 | 4 | 5 | 1 | [8 empty] | 116640
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 51 | 51 | 51 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 34 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 909799
12 | Hathazari 100 MW peaking PP | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 28 | 26 | 26 | 26 | 26 | 25 | 26 |  | 26 | 34 | 34 | 34 | 34 | 34 | 34 | 655824
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 87 | 87 | 87 | 81 | 87 | 80 | 87 | 87 | 87 | 87 | 87 | 72 | 74 | 87 | 87 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 92 | 2221382
| Daudkandi 200 MW PP (B.Trac) | [15 empty] | 50 | 50 | 50 |  | 195 | 150 | 150 | 195 | 140 | 196 | 197 | 1072896
14 | Titas 50 MW Peaking PP | 41 | 41 | 41 | 41 | 41 | 41 | 24 | 24 | 24 | 24 | 24 | 26 | 31 | 30 | 30 | 30 | 30 | 30 |  | 34 | 38 | 38 | 38 | 38 | 38 | 39 | 791304
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 225 | 200 | 200 | 195 | 198 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 193 | 195 | 195 | 207 |  | 242 | 242 | 242 | 242 | 242 | 242 | 135 | 4927852
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 36 | 55 | 83 | 83 | 83 | 83 | 83 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 669090
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4315500
24
25 | Ghorasal 365 MW CCPP Unit-7 | [21 empty] | 60 | 200 | 200 | 200 | 200 | 687100
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 37 | 37 | 37 | 37 | 37 | 35 | 35 | 35 | 31 | 34 | 38 | 35 | 38 | 38 | 37 | 35 | 37 | 40 |  | 38 | 41 | 41 | 41 | 42 | 42 | 42 | 876024
33 | Ashuganj 225 MW CCPP | 171 | 184 | 182 | 179 | 189 | 188 | 183 | 178 | 166 | 176 | 201 | 188 | 204 | 201 | 202 | 197 | 198 | 185 |  | 202 | 204 | 204 | 208 | 206 | 205 | 199 | 4649000
34 | Ashuganj 450 MW CCPP(South) | 330 | 290 | 320 | 320 | 330 | 290 | 335 | 275 | 330 | 290 | 330 | 310 | 305 | 320 | 305 | 290 | 275 | 280 |  | 260 | 260 | 260 | 305 | 320 | 320 | 320 | 7525000
| Ashuganj 450 MW CCPP(North) | 345 | 305 | 340 | 335 | 345 | 315 | 350 | 290 | 320 | 305 | 335 | 315 | 310 | 325 | 320 | 285 | 280 | 280 |  | 280 | 280 | 280 | 320 | 320 | 320 | 320 | 7969400
Ashuganj 420 MW CCPP(East)
35 | Ashuganj 55 MW PP (Precision) | 55 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 30 | 10 | 0 | [5 empty] | 3 |  | 15 | 35 | 35 | 40 | 49 | 51 | 51 | 702720
36 | Chandpur 150 MW CCPP | 135 | 135 | 141 | 142 | 142 | 142 | 142 | 142 | 137 | 136 | 135 | 135 | 129 | 128 | 128 | 128 | 128 | 130 |  | 128 | 127 | 129 | 129 | 129 | 128 | 127 | 3203990
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 402 | 403 | 406 | 405 | 407 | 404 | 405 | 403 | 402 | 396 | 397 | 395 | 401 | 403 | 401 | 400 | 401 | 403 |  | 401 | 396 | 397 | 397 | 398 | 399 | 398 | 9773060
40 | Meghnaghat 450 MW CCPP(MPL) | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 |  | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 4975150
41 | Haripur 360MW CCPP(HPL) | 331 | 331 | 327 | 326 | 327 | 327 | 325 | 322 | 321 | 312 | 312 | 312 | 311 | 311 | 307 | 291 | 288 | 276 |  | 278 | 276 | 277 | 257 | 247 | 247 | 265 | 7262000
42 | RPCL 210MW CCPP | 101 | 101 | 102 | 102 | 102 | 101 | 102 | 96 | 81 | 81 | 81 | 68 | 68 | 68 | 68 | 95 | 96 | 96 |  | 99 | 100 | 100 | 100 | 100 | 100 | 100 | 2149440
43 | Sutiakhali 50 MW Solar PP |  |  |  |  | 0 | 4 | 15 | 23 | 41 | 51 | 50 | 47 | 56 | 27 | 34 | 31 | 14 | 3 | [8 empty] | 400130
44 | Fenchugonj CCPP Phase-1 | 44 | 44 | 43 | 43 | 43 | 43 | 43 | 44 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 44 | 44 |  | 44 | 44 | 44 | 44 | 43 | 43 | 43 | 1015000
45 | Fenchugonj CCPP Phase-2 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 40 | 40 | 40 | 41 | 41 | 41 | 40 |  | 40 | 40 | 40 | 41 | 40 | 41 | 41 | 967424
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 62 | 62 | 60 | 61 | 60 | 60 | 60 | 62 | 60 | 60 | 60 | 58 | 61 | 59 | 60 | 61 | 60 | 58 |  | 58 | 58 | 56 | 56 | 61 | 61 | 61 | 1423008
48 | Shahjibazar 86MW PP (Shahjibazar) | 81 | 81 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 70 | 81 | 81 | 81 | 81 | 81 | 81 | 857280
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 222 | 220 | 220 | 220 | 220 | 220 | 220 | 221 | 220 | 220 | 205 | 207 | 208 | 207 | 207 | 207 | 207 | 207 |  | 220 | 220 | 220 | 221 | 221 | 221 | 214 | 5156820
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL) | 32 | 31 | 30 | 32 | 31 | 31 | 31 | 31 | 31 | 30 | 30 | 30 | 31 | 31 | 31 | 30 | 29 | 29 |  | 29 | 29 | 31 | 31 | 31 | 30 | 31 | 718000
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 9 |  | 10 | 9 | 9 | 9 | 9 | 9 | 9 | 231120
54 | Hobiganj 11MW PP Cofidence-E
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 53 | 53 | 42 | 42 | 42 | 42 | 33 | 33 | 31 | 33 | 33 | 33 | 33 | 32 | 33 | 33 | 33 |  | 50 | 53 | 53 | 53 | 53 | 53 | 50 | 997800
56 | Shahjahanulla 25 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 238560
57 | Bibiana-II 341 MW CCPP (Summit) | 320 | 320 | 320 | 330 | 310 | 320 | 320 | 330 | 330 | 320 | 320 | 310 | 300 | 300 | 300 | 280 | 290 | 280 |  | 300 | 270 | 265 | 275 | 300 | 320 | 295 | 7541500
Bibiyana South 400 MW
58 | Nababganj 55 MW PP (Southern power ) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 |  | 35 | 35 | 35 | 55 | 55 | 55 | 55 | 626577
59 | Tangail Palli Power Gen 22 MW | [19 empty] | 1 | 2 | 4 | 6 | 7 | 8 | 10 | 37680
60 | Barabkunda 22 MW PP (Regent) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 13 |  | 13 | 13 | 13 | 13 |  | 13 | 13 | 13 | 15 | 15 | 15 | 15 | 331824
61 | Narshingdi 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 456948
62 | Tangail 22 MW PP (Doreen) | 0 | 20 | 20 | 20 | 22 | 22 | 20 | 20 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 20 | 22 |  | 22 | 22 | 22 | 20 | 20 | 20 | 22 | 441756
63 | Impoprt (Tripura) | 172 | 172 | 170 | 168 | 164 | 150 | 140 | 148 | 150 | 140 | 162 | 164 | 168 | 170 | 182 | 164 | 160 | 158 |  | 158 | 160 | 160 | 160 | 170 | 162 | 162 | 3880320
64 | Malancha, Ctg. EPZ (United) | 38 | 38 | 37 | 38 | 38 | 38 | 38 | 12 | 2 | 2 | 2 | 3 | 3 | 3 | 2 | 3 | 3 | 4 |  | 7 | 7 | 22 | 30 | 35 | 37 | 38 | 521280
65 | Feni 22MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 0 | [6 empty] | 21 | 21 |  |  |  |  | 10 | 16 | 19 | 21 | 21 | 22 | 323856
66 | Feni 11 MW PP (Doreen) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 238500
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 21 | 16 | 25 | 31 | 31 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 767300
68 | Cumilla 25 MW PP (Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 487130
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 27 | 20 | 25 | 20 | 25 | 25 | 17 | 17 | 20 | 20 | 20 | 20 | 25 | 25 | 25 | 25 | 26 | 26 |  | 20 | 26 | 27 | 27 | 27 | 27 | 27 | 539100
71 | Maona 33 MW PP(Summit) | 25 | 0 | 0 | 8 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 586000
72 | Rupganj 33 MW PP(Summit) | 33 | 17 | 17 | 17 | 33 | 33 | 33 | 33 | 16 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 17 | 33 | 33 | 649400
73 | Ghorashal 108MW PP (Regent) | 93 | 93 | 93 | 93 | 92 | 90 | 90 | 86 | 86 | 84 | 83 | 80 | 82 | 80 | 87 | 92 | 93 | 96 |  | 96 | 96 | 97 | 81 | 84 | 88 | 87 | 2080454
| Feni Lanka Power | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 98 | 114 |  | 114 | 114 | 114 | 114 | 114 | 114 | 52 | 1089840
| Chowmuhani 113 MW | 45 | 36 | 36 | 36 | 36 | 36 | 37 | 38 | 38 | 38 | 38 | 38 | 76 | 109 | 110 | 100 | 102 | 104 |  | 114 | 115 | 115 | 115 | 113 | 114 | 58 | 1700160
| Manikgonj 162MW PP(MPGL) | 162 | 162 | 162 | 162 | 162 | 66 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 76 | 105 | 105 | 114 | 162 |  | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 2822400
77 | Siddhirganj 100 PP(Dutch Bangla) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 22 | 48 | 48 | 15 | 8 | 8 |  | 11 | 50 | 43 | 48 | 48 | 48 | 14 | 461933
78 | Gazipur 52 MW PP | 50 | 50 | 50 | 51 | 51 | 51 | 51 | 51 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 49 | 49 | 49 |  | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1141920
79 | Kodda 150MW PP | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 115 | 124 | 124 |  | 124 | 128 | 128 | 128 | 128 | 128 | 48 | 1740480
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 10 | 16 | 8 | 8 | 8 | 8 | 8 | 12 | 8 | 8 | 8 |  | 16 | 43 | 43 | 43 | 43 | 43 | 43 | 422918
| Gazipur 100 MW PP | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2208000
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 3 | 4 | 4 | 5 | 4 | 3 | 4 | 4 | 3 | 2 | [9 empty] | 34439
| Jodiac Power | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 17 | 17 | 17 | 29 | 30 | 33 | 18 | 17 | 17 |  | 34 | 36 | 36 | 36 | 36 | 36 | 36 | 769538
| Karnaphuli Power Ltd. | 55 | 55 | 55 | 55 | 55 | 54 | 54 | 55 | 55 | 55 | 55 | 40 | 53 | 54 | 55 | 55 | 55 | 72 |  | 72 | 73 | 75 | 73 | 74 | 75 | 57 | 1441053
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL) | 7 | 8 | 7 | 8 | 7 | 7 | 8 | 8 | 7 | 7 | 7 | 6 | 23 | 50 | 56 | 14 | 11 | 7 |  | 11 | 41 | 38 | 48 | 48 | 48 | 9 | 463680
| Meghnaghat 104 MW PP (OPCL) | 17 | 17 | 0 |  | 0 | 5 | 18 | 17 | 17 | 17 | 17 | 17 | 31 | 51 | 47 | 17 | 17 | 17 |  | 17 | 51 | 30 | 52 | 52 | 50 | 20 | 554880
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 34 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 1039320
92 | Fenchuganj 44MW (Energyprima) | 48 | 49 | 49 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 40 | 47 | 48 | 48 | 48 | 48 | 48 | 925488
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 43 | 43 | 43 | 43 | 43 | 43 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1156134
94 | Gagnagar 102 MW PP (Digital Power) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 16 | 50 | 50 | 8 | 8 | 8 |  | 8 | 42 | 50 | 50 | 50 | 50 | 8 | 459216
95 | Patenga 50MW PP (Baraka) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 605760
96 | Chattogram 108 MW PP (ECPV) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 12 | 12 | 12 | 12 | 12 | 15 | 13 | 15 | 18 | 15 | 51 |  | 80 | 76 | 75 | 80 | 80 | 44 | 11 | 650880
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 751006
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1308761
101 | Kushiara 163 MW CCPP (KP) | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2542336
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 1 | 2 | 2 | 1 | 2 | 3 | 2 | 2 | 1 | 0 | 0 | [8 empty] | 16000
103 | Kamalaghat 54 MW PP(Banco Energy) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 17 | 17 | 17 | 17 | 17 | 35 | 35 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 894600
104 | Keranigonj 300 MW PP (APR) | [14 empty] | 100 | 102 | 153 | 101 |  | 241 | 200 | 198 | 284 | 292 | 297 | 277 | 1815668
105 | Bramhangoan 100 MW PP (Aggreko) | [15 empty] | 88 | 94 | 95 |  | 98 | 60 | 60 | 96 | 50 | 95 | 95 | 686089
106 | Mymensingh 200 MW PP (United) | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 47 | 47 | 46 | 46 | 47 | 167 |  | 151 | 151 | 152 | 154 | 181 | 180 | 47 | 1812000
112 | Aurahati 100MW PP (Aggreko) | [15 empty] | 95 | 98 | 98 |  | 98 | 51 | 50 | 100 | 50 | 99 | 99 | 705761
114 | Kodda 149 MW PP Unit-1 (Summit) | 136 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 97 | 99 | 99 | 99 | 99 | 99 | 98 | 98 | 141 | 149 |  | 149 | 149 | 149 | 149 | 149 | 134 | 118 | 2784960
115 | Juldah 100 MW PP Unit-3 (Acorn) | 30 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 76 | 70 | 76 | 21 | 21 | 21 |  | 90 | 90 | 90 | 90 | 90 | 90 | 21 | 981120
116 | Chandpur 200MW (Desh energy) | 42 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 |  | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 850080
117 | Ashuganj 150MW PP (Midland) | 132 | 128 | 137 | 137 | 132 | 132 | 128 | 122 | 122 | 117 | 118 | 118 | 115 | 117 | 113 | 112 | 110 | 112 |  | 112 | 116 | 115 | 122 | 125 | 130 | 132 | 2944000
118 | Bibiyana-III 400 MW CCPP | 402 | 402 | 402 | 401 | 402 | 400 | 390 | 400 | 380 | 401 | 385 | 373 | 403 | 401 | 404 | 352 | 403 | 405 |  | 405 | 404 | 404 | 402 | 404 | 381 | 403 | 9456000
| Jamalpur 115 MW PP (United) | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 77 |  | 78 | 78 | 78 | 106 | 87 | 78 | 49 | 1368000
| Anwara 300 MW PP (United) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 50 | 50 | 53 | 53 | 53 | 52 | 52 | 52 | 52 | 69 | 85 |  | 206 | 210 | 212 | 214 | 214 | 53 | 52 | 1656000
| Juldah unit-2 (Acorn) | 65 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 32 | 50 | 50 | 20 | 20 | 20 |  | 38 | 100 | 100 | 100 | 100 | 100 | 100 | 1045440
| Anlima Energy Ltd. | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 |  | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 2608200
| Bhairob 54.5 MW | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 6 | 35 | 35 | 35 | 849960
| Spectra Solar Plant Ltd. |  |  |  |  | 0 | 1 | 8 | 16 | 20 | 31 | 34 | 35 | 35 | 31 | 26 | 15 | 9 | 3 | [8 empty] | 257725
| Chandpur 115(Doreen) | 74 | 75 | 75 | 74 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 64 | 76 | 65 | 66 | 56 | 56 | 56 |  | 52 | 75 | 69 | 75 | 75 | 60 | 73 | 1683840
| Kanchan Purbachal Power Generation Ltd. | 55 | 55 | 55 | 55 | 55 | 44 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1312560
120 | Eastern Zone Total | 6549 | 6309 | 6306 | 6237 | 6289 | 6097 | 6161 | 6059 | 6064 | 5923 | 6040 | 5925 | 6215 | 6410 | 6597 | 6483 | 6737 | 6978 |  | 7637 | 7765 | 7821 | 8333 | 8281 | 8217 | 7455 | 161099792
121
122 | o
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 20 | 23 |  | 27 | 30 | 32 | 32 | 32 | 32 | 32 | 474240
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 22 | 17 | 17 | 17 | 17 | 0 | [11 empty] | 13 |  | 34 | 36 | 36 | 38 | 42 | 32 | 32 | 304800
| Khulna 225 MW CCPP | 216 | 223 | 226 | 226 | 226 | 226 | 225 | 224 | 221 | 225 | 227 | 227 | 230 | 220 | 221 | 221 | 226 | 224 |  | 223 | 226 | 227 | 228 | 227 | 227 | 227 | 5425920
129 | Rupsha 105 MW PP (Orion rupsha) | [12 empty] | 1 | 25 | 35 | 38 | 24 | 17 |  | 17 | 53 | 53 | 53 | 53 | 36 | 0 | 360960
130 | Mongla Orion 100 MW Solar PP |  |  |  |  | 0 | 5 | 14 | 56 | 44 | 45 | 81 | 97 | 68 | 99 | 67 | 55 | 6 | 8 | [8 empty] | 636480
131
132 | United Payra Power Ltd. | [13 empty] | 22 | 45 | 90 | 120 | 138 |  |  |  | 120 | 150 | 150 | 38 | 90 | 945600
133 | Bhola Nutan Biddut BD LTD (GAS) | 215 | 221 | 220 | 221 | 216 | 220 | 218 | 220 | 220 | 220 | 216 | 216 | 216 | 213 | 213 | 180 | 189 | 211 |  | 218 | 213 | 210 | 187 | 221 | 220 | 220 | 5164336
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 16 | 16 | 16 | 16 | 33 | 33 | 64 | 64 | 64 | 64 | 64 |  | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 1071648
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 87 | 86 | 87 | 87 | 85 | 85 | 87 | 86 | 85 | 84 | 83 | 84 | 85 | 83 | 85 | 87 | 85 | 85 |  | 85 | 88 | 88 | 88 | 88 | 82 | 87 | 2063252
140 | Bhola 33 MW PP (Venture) | 32 | 30 | 30 | 27 | 27 | 24 | 21 | 20 | 21 | 21 | 22 | 22 | 24 | 22 | 26 | 26 | 24 | 25 |  | 30 | 31 | 31 | 33 | 34 | 30 | 32 | 621013
141 | Noapara 100 MW PP (Bangla Trac) | [9 empty] | 0 | [5 empty] | 5 | 20 | 20 |  | 47 | 95 | 95 | 96 | 96 | 96 | 96 | 578880
142 | Noapara 40 MW PP (Khanjahan Ali) | 8 | 8 | 8 | 8 | 0 | [8 empty] | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 118500
143 | Gopalganj 100 MW Peaking PP | 60 | 57 | 57 | 57 | 57 | 0 | [11 empty] | 23 |  | 63 | 78 | 73 | 72 | 72 | 66 | 66 | 715392
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | 105 | 105 | 105 | 105 | 105 | 105 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 89 | 89 |  | 88 | 105 | 105 | 105 | 105 | 105 | 89 | 2308032
146 | Bheramara HVDC | 914 | 914 | 913 | 913 | 914 | 914 | 913 | 914 | 914 | 914 | 914 | 914 | 913 | 907 | 907 | 907 | 907 | 906 |  | 907 | 909 | 909 | 909 | 909 | 909 | 909 | 22024727
147 | Bheramara 410 MW CCPP | 160 | 160 | 160 | 165 | 165 | 160 | 160 | 160 | 150 | 145 | 130 | 135 | 140 | 140 | 135 | 135 | 135 | 140 |  | 140 | 145 | 150 | 150 | 150 | 155 | 155 | 3726432
148 | Payra 1320 MW | 1070 | 1090 | 1080 | 1080 | 1070 | 1040 | 1030 | 980 | 940 | 930 | 930 | 820 | 820 | 700 | 650 | 620 | 600 | 600 |  | 660 | 780 | 790 | 800 | 790 | 790 | 790 | 22699900
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 199 | 200 | 199 | 200 | 200 | 200 | 200 | 201 | 209 |  | 250 | 250 | 251 | 240 | 250 | 250 | 250 | 5122600
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 17 | 24 | 24 | 24 | 34 | 32 | 32 | 32 | 32 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 654048
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 1 | 3 | 4 | 5 | 5 | 4 | 4 | 4 | 3 | 1 | 0 | [8 empty] | 38340
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 177 | 178 | 177 | 178 | 178 | 177 | 178 | 177 | 178 | 178 | 175 | 175 | 173 | 171 | 170 | 169 | 168 | 168 |  | 168 | 169 | 168 | 170 | 173 | 175 | 174 | 4398755
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
| Sirajgonj 225 MW CCPP Unit-2 (Oil) | 215 | 214 | 215 | 215 | 215 | 213 | 214 | 214 | 213 | 203 | 200 | 200 | 170 | 150 | 130 | 176 | 209 | 211 |  | 211 | 213 | 214 | 213 | 212 | 211 | 211 | 5094618
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 148 | 148 | 148 | 149 | 151 | 151 | 148 | 148 | 146 | 142 | 140 | 140 | 139 | 138 | 137 | 138 | 140 | 140 |  | 140 | 141 | 141 | 143 | 145 | 145 | 145 | 3678527
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 286 | 290 | 302 | 306 | 307 | 324 | 313 | 305 | 290 | 270 | 280 | 265 | 265 | 254 | 255 | 264 | 263 | 262 |  | 270 | 281 | 290 | 286 | 291 | 287 | 275 | 6858181
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | 40 | 40 | 40 | 40 | 40 | [7 empty] | 5 | 6 | 6 | 24 | 33 | 33 |  | 21 | 21 | 21 | 25 | 28 | 26 | 28 | 409522
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 19 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 18 |  | 18 | 20 | 21 | 21 | 22 | 21 | 22 | 446640
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 232254
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | [18 empty] | 334004
167 | Katakhali 50 MW Peaking PP | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 620200
168 | Santahar 50 MW Peaking PP | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  |  |  |  | 10 | 33 | 33 | 33 | 34 | 34 | 33 |  | 33 | 33 | 34 | 34 | 34 | 34 | 34 | 613170
169 | Natore 52 MW PP (Rajlanka) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 52 | 52 | 52 | 52 | 52 | 43 | 8 | 391200
170 | Chapainawabganj 100 MW Peaking PP | 80 | 80 | 80 | 80 | 80 | 72 | 72 | 72 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 51 |  | 79 | 80 | 80 | 80 | 80 | 80 | 80 | 1506936
171 | Baghabari 200 MW PP (Paramount) | [15 empty] | 1 | 50 | 50 |  | 84 | 155 | 161 | 172 | 169 | 170 | 170 | 1027096
| Bagura 113 MW PP (Confidence)-2 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 70 | 70 | 80 | 93 | 94 |  | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 1698432
172 | Confidence Power Bogura Unit-1 113 MW | 95 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 57 | 57 | 95 |  | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 1647840
173 | Rangpur 20 MW GTPP | [23 empty] | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | [23 empty] | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 55 | 55 | 54 | 89 | 81 | 88 |  | 91 | 91 | 91 | 91 | 91 | 91 | 56 | 1605427
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1 | 2 | 6 | 7 | 7 | 8 | 7 | 7 | 6 | 5 | 4 | 1 | [8 empty] | 61492
178 | Energypac Power Venture Thakurgaon Ltd. | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 72 | 72 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 1260288
178