## Forecast
8 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2022-08-09 | Tuesday
|  |  | Date (day): | 2022-08-09 |  | Tuesday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11359.6 | MW |  |  | (b) At Evening Peak Hour : |  | 13615 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2022-08-08 | 2022-08-09 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 300 | 305 | 305 |  | 60
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 83 | 82 | 86 | 86 |  | 22 | Engine problem
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 406 | 393 | 410 | 412
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 320 | 214 | 310 | 320 | 40 |  | Gas shortage
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 225 | 225 | 225 |  | Gas shortage & GT-2 S/D
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 7 | 31 | 8 | 32 | 68 |  | Fuel shortage
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 0 | 0 | 0 | 0 |  | 102 | Under maint
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 30 | 30 | 30 | 30 |  | 25 | Engine problem
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 0 | 19 | 19 |  |  | Engine problem
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 8 | 48 | 8 | 48 | 52 |  | Fuel shortage
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 8 | 32 | 8 | 32 | 70 |  | Fuel shortage
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 35 | 54 | 35 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 48 | 128 | 50 | 132 |  | 17 | Engine problem
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 35 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 52 | 48 | 50 | 50 |  | 30 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 30 | 28 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 50 | 49 | 51 | 51
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 95 | 258 | 110 | 275 |  | 25 | Engine problem
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 246 | 300 | 250 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 98 | 97 | 97 | 96 | 4 |  | Engine problem
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 93 | 97 | 50 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 90 | 149 | 90 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 88 | 105 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 17 | 32 | 17 | 52 |  |  | Fuel shortage
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 35 | 162 | 35 | 162
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 18 | 0 | 30 | 0
| 40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 55 | 55 | 35 | 55
|  | Dhaka area Total |  |  |  |  | 6263 | 5847 | 2459 | 3240 | 2750 | 3446 | 1390 | 961
| 41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 105 | 105 | 105 | 75 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 25 | 1 | 25 | 25
| 43 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 5 | 0 | 20 | 0
| 44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 25 | 37 | 25 | 35 |  | 15 | Engine problem
| 45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 117 | 115 | 118 | 118 |  | 112 | Low Water Level
| 46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | S/D due to HGPI
| 47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint,Fuel conservation
| 48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 69 | 105 | 68 | 105
| 49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 26 | 34 | 26 | 34 | 64 |  | Fuel shortage
| 50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 17 | 51 | 17 | 51 | 51 |  | Fuel shortage
| 51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 33 | 33 | 33 | 33 | 67 |  | Fuel shortage
| 52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 21 | 90 | 21 | 90 |  | 10 | Engine problem
| 53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 15 | 15 | 15 | 15 |  | 7 | Engine problem
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 3 | 21 | 5 | 20
| 54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 11 | 77 | 12 | 80 |  | 28 | Engine problem
| 55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 2 | 0 | 5 | 0
| 56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 52 | 214 | 52 | 210 | 90 |  | Fuel shortage
| 57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 36 | 36 | 17 | 36 |  | 18 | Engine problem
| 58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 55 | 55 | 55 | 55 | 55 |  | Fuel shortage
| 59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 20 | 100 | 20 | 100
| 60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 108 | 108 | 108 | 108 |  | 8 | Engine problem
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 740 | 1197 | 747 | 1220 | 582 | 573
| 61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 198 | 190 | 210 | 210 |  |  | Gas shortage
| 63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 320 | 320 | 320 | 320 | 40 |  | Gas shortage
| 64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 320 | 320 | 305 | 320 | 40 |  | Gas shortage
|  | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+136*1 | 284 | 284 | 0 | 0 | 0 | 0 |  |  | On test.
| 65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 39 | 38 | 39 | 39 |  | 6 | Engine problem
| 66 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 55 | 49 | 52 | 55 | 55
| 67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 120 | 128 | 123 | 145 |  | 5 | Engine problem
| 70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 30 | 38 | 38 | 38 |  | 14 | Engine problem
| 71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 135 | 121 | 142 | 142 |  | 21 | Engine problem
| 72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 34 | 34 | 17 | 34 |  |  | Fuel shortage
| 73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 22 | 22 | 22
| 74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 10 | 9 | 10 | 10
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 154 | 158 | 143 | 166
| 75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 43 | 8 | 43 | 9 |  | Fuel shortage
| 77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 20 | 20 |  | 5 | Engine problem
| 78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 196 | 200 | 120 | 200
| 79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 114 | 17 | 114
| 80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 38 | 115 | 38 | 113
| 81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 35 | 35 | 35 | 35 |  | 19 | 33 kV feeder fault
| 82 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 72 | 68 | 71 | 71 | 44 |  | Fuel shortage
|  | Cumilla Area Total |  |  |  |  | 3193 | 3169 | 1908 | 2117 | 1825 | 2189 | 454 | 70
| 83 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 70 | 96 | 95 | 100 | 102 |  | Gas shortage
| 84 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 85 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0 |  | 8 | Under maint.
| 86 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 87 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 48 | 180 | 48 | 180 |  | 20 | Engine problem
| 88 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 47 | 78 | 48 | 78 |  | 37 | Engine problem
| 89 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 21 | 0 | 50 | 0
| 90 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 11 | 12 | 12 | 12 |  | 10 | Engine problem
|  | Mymensingh Area Total |  |  |  |  | 717 | 614 | 221 | 388 | 276.6 | 392 | 102 | 75
| 91 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 44 | 43 | 43 | 43 |  | 27 | Machine problem.
| 92 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 41 | 41 | 41 | 41 |  | 49 | Machine problem
| 93 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 110 | 110 | 110 | 110 |  | 53 | ST under maint.
| 94 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
| 95 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 31 | 53 | 22 | 53
| 96 | Fenchuganj 44MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 30 | 49 | 20 | 49
| 97 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 11 | 11
| 98 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 60 | 62 | 62 | 62
| 99 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 10 | 81 | 10 | 81
| 100 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
| 101 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 220 | 221 | 220 | 220
| 102 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Gas shortage
| 103 | Sylhet 50MW PP (EPL) |  | Gas | NENP | 27*2 | 50 | 50 | 31 | 31 | 31 | 31 | 19 |  | Gas shortage
| 104 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 8 | 16 | 16 | 16 | 9 |  | Gas shortage
| 105 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 310 | 280 | 310 |  |  | FGMO
| 106 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 402 | 404 | 400 | 400
| 107 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 9 | 10 | 10 | 10
| 108 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 0 | 0 | 0 | 0 |  | 383 | Under maint.
|  | Sylhet Area Total |  |  |  |  | 2522 | 2477 | 1296 | 1431 | 1276 | 1437 | 48 | 942
| 109 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 915 | 914 | 928 | 928
| 110 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 16 | 22 | 16 | 32 | 83 |  | Fuel shortage
| 111 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 21 | 38 | 15 | 38 |  | 16 | Engine problem
| 112 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 237 | 229 | 225 | 225 | 5
| 113 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 60 | 63 | 60 | 70 |  | 39 | Engine problem
| 114 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 150 | 155 | 150 | 170 | 240 |  | Gas shortage
| 115 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 8 | 8 | 8 | 32 |  | Fuel shortage
| 116 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 55 | 79 | 60 | 96 | 4 |  | Engine problem
| 117 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 53 | 0 | 70 | 35 |  | Fuel shortage
| 118 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 89 | 89 | 105 | 105
| 119 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 74 | 0 | 100 | 0
|  | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
|  | Khulna Area Total |  |  |  |  | 2388 | 2384 | 1617 | 1650 | 1667 | 1742 | 415 | 55
| 120 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 48 | 48 | 64 | 64 |  |  | Line O/L
| 121 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 18 | 30 | 23 | 30 |  | 10 | Engine problem
| 122 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 88 | 87 | 88 | 88 | 106 |  | Gas shortage
|  | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
| 123 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 600 | 570 | 620 | 620 |  |  | Coal Shortage
| 124 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 220 | 222 | 225 | 220
| 125 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 90 | 54 | 0 | 54
|  | Barisal Area Total |  |  |  |  | 1958 | 1958 | 1064 | 1011 | 1020 | 1076 | 106 | 10
| 126 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 127 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 32 | 32 | 32 | 32 |  | 20 | Engine problem
| 128 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 17 | 0 | 40 |  | 31 | Engine problem
| 129 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 130 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 42 | 42 |  | 8 | Engine problem
| 131 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 32 | 32 | 32 | 32 |  | 18 | Engine problem
| 132 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 179 | 167 | 188 | 190 | 20 |  | Gas shortage
| 133 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 215 | 180 | 210 | 210 | 10
| 134 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 150 | 149 | 160 | 165 | 55 |  | Gas shortage
| 135 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 297 | 287 | 315 | 315 | 99 |  | Gas shortage
| 136 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 33 | 33 | 33 | 33 |  | 17 | Engine problem
| 137 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 19 | 21 | 21 | 21
| 138 | Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 139 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 140 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 52 | 8 | 52
| 141 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 51 | 80 | 80 | 86 |  | 18 | Engine problem
| 142 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 169 | 179 | 100 | 188 | 12
| 143 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 50 | 94 | 50 | 94 |  | 19 | Engine problem
| 144 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 50 | 95 | 55 | 95 |  | 18 | Engine problem
| 145 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 4 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2129 | 1300 | 1429 | 1343 | 1606 | 367 | 149
| 146 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 70 | 75 | 75 | 85 |  | Machine problem
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
| 147 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 250 | 250 | 250 | 250 | 24 |  | Machine problem
| 148 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
| 149 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
| 150 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 56 | 97 | 70 | 92 |  | 21 | Fuel shortage
| 151 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 1 | 0 | 8 | 0
| 152 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 34 | 90 | 52 | 90 |  | 25 | Fuel shortage
|  | Rangpur Area Total |  |  |  |  | 800 | 720 | 341 | 507 | 455 | 507 | 149 | 131
|  | Total |  |  |  |  | 22482 | 21680 | 10946 | 12970 | 11359.6 | 13615 | 3613 | 2966
| A. |  | 2022-08-08 | (Yesterday) |  |  |  |  | Monday
| 1 | Highest Generation : |  |  | 13047 | MW at | 22:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 10946 | MW at | 9:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 13900 | MW
| 3 | Day peak Generation : |  |  | 10946 | MW at | 9:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 13373.7671 | MW
| 4 | Evening peak Generation : |  |  | 12970 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 856.6371 | MW
| 5 | Total Energy Generation : |  | 278.4523 | MKWHr | By Solar | 1.262 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
|  | By Gas : | 129.9164 | MKWHr |  | By Oil: | 97.393 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 21.304 | MKWHr |  | By Hydro: | 2.7267 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 3613 | MW | Dhaka | 4788.37 | 4565.37 |  | 223
|  |  |  | For Plants S/D or M/C prob = |  |  | 2966 | MW | Chittagong | 1273.5 | 1273.5 |  | 0 |  | 18:00 |  | 573.2196
|  |  |  | Total = |  |  | 6579 | MW | Khulna | 1663.0209 | 1534.6 |  | 128.4209
| 7 | Total Gas Supplied : |  |  | 991.46 | MMCFD |  |  | Rajshahi | 1486.8 | 1339.8 |  | 147 |  | 19:00 |  | 440.5129
| 8 | Fuel Cost : | i) Gas : | Taka | 148589814.178 | ii) Oil : | Taka | 1510365860.01 | Comilla | 1264.2162 | 1164 |  | 100.2162 |  | 19:30 |  | 590.7296
|  |  | iii) Coal : |  | 168140565.45 | Total | Taka | 1827096239.638 | Mymensingh | 1042 | 901 |  | 141 |  | 20:00 |  | 897.6141
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0 | MKWHr. | Sylhet | 621 | 621 |  | 0 |  | 21:00 |  | 857.0648
|  | ii) During Peak Demand : |  |  | 736 | MW (E to W) at | 21:00 | hrs | Barisal | 379.86 | 379.86 |  | 0 |  | 22:00 |  | 786.1035
|  | iii) Maximum : |  |  | 454 | MW at | 5:00 | hrs | Rangpur | 855 | 738 |  | 117 |  | 23:00 |  | 863.5158
| 10 | Maximum Temperature in Dhaka was |  |  |  | 34.5° C |  |  | Total | 13373.7671 | 12517.13 |  | 856.6371
| B. |  | 2022-08-09 | (Today) |  |  |  | Tuesday |  |  | Probable max. temperature in Dhaka |  |  | 34.6° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 13600 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 13615 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 11500 | MW
| 4 | Reserve(Generation end) |  |  |  | 15 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 290.2545 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 10442 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 22.0975 | MKWHr. | ii) HVDC Flow at Peak Time |  | 914 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.7526 | MKWHr. | iii) Maximum HVDC Flow : |  | 915 | MW at | 9:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 94.17 |  | (b) Today: | 94.92 |  | (c) Rule Curve: |  | 91.56
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2022-08-08
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 200 | 87 | 0 | 399 | 281 |  | 0 | 225 | 0 | 7 | 0 | 30 | 0 | 0 | 0 | 8 | 8 | 48 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 22 | 25 | 27 | 33 | 33 | 49 | 0 | 81 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 11 | 26 | 51 | 33 | 12 | 25 | 15 | 38 | 0 | 0 | 0 | 320 | 320 | 195 | 8 | 127 | 42 | 52 | 0 | 51 | 0 | 39 | 8 | 21 | 10 | 33 | 20 | 162 | 100 | 0 | 22 | 0 | 43 | 41 | 50 | 48 | 110 | 0 | 60 | 81 | 0 | 221 | 0 | 31 | 0 | 310 | 16 | 0 | 197 | 112 | 298 | 95 | 47 | 96 | 97 | 0 | 21 | 34 | 133 | 403 | 48 | 105 | 87 | 0 | 16 | 23 | 56 | 17 | 42 | 55 | 0 | 0 | 0 | 51 | 108 | 0 | 35 | 0 | 76 | 55 | 0 |  | 914 | 0 | 150 | 0 | 26 | 224 | 0 | 0 | 21 | 60 | 8 | 84 | 30 | 64 | 0 | 0 | 0 | 32 | 27 | 72 | 0 | 0 | 24 | 8 | 34 | 22 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 173 | 0 | 0 | 206 | 0 | 96 | 145 | 0 | 274 | 0 | 169 | 50 | 89 | 56 | 0 | 0 | 95 | 660 | 210 | 0 | 90 | 0 | 0 | 34 | 0 | 0 |  | 7087 | 4408 | 11495 | 3591 | 914 | 1908 | 951 | 2079 | 910 | 116 | 430 | 640 | 162 | 0 | 1801.6791 | 94.02
2:00 | 0 | 0 | 0 | 180 | 200 | 87 | 0 | 402 | 291 |  | 0 | 225 | 0 | 7 | 0 | 30 | 0 | 0 | 0 | 8 | 8 | 48 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 22 | 25 | 24 | 33 | 33 | 49 | 0 | 83 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 11 | 26 | 51 | 33 | 12 | 20 | 15 | 38 | 0 | 0 | 0 | 320 | 320 | 193 | 8 | 127 | 42 | 52 | 0 | 51 | 0 | 39 | 8 | 21 | 10 | 33 | 20 | 162 | 100 | 0 | 22 | 0 | 43 | 41 | 50 | 45 | 110 | 0 | 60 | 40 | 0 | 220 | 0 | 31 | 9 | 325 | 16 | 0 | 197 | 97 | 296 | 97 | 48 | 96 | 97 | 0 | 21 | 34 | 133 | 398 | 48 | 105 | 87 | 0 | 16 | 36 | 56 | 17 | 38 | 20 | 0 | 0 | 0 | 35 | 108 | 0 | 35 | 0 | 76 | 55 | 0 |  | 914 | 0 | 155 | 0 | 16 | 226 | 0 | 0 | 21 | 55 | 0 | 88 | 29 | 64 | 0 | 0 | 0 | 32 | 27 | 65 | 0 | 0 | 24 | 8 | 34 | 22 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 172 | 0 | 0 | 208 | 0 | 96 | 145 | 0 | 276 | 0 | 168 | 50 | 89 | 55 | 0 | 0 | 57 | 650 | 220 | 0 | 90 | 0 | 0 | 34 | 0 | 0 |  | 7010 | 4351 | 11361 | 3591 | 914 | 1909 | 950 | 1961 | 900 | 118 | 434 | 630 | 162 | 0 | 1602.6189 | 94.05
3:00 | 0 | 0 | 0 | 180 | 200 | 88 | 0 | 410 | 293 |  | 0 | 225 | 0 | 8 | 0 | 30 | 0 | 0 | 0 | 8 | 8 | 48 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 22 | 25 | 27 | 33 | 33 | 49 | 0 | 83 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 11 | 26 | 51 | 33 | 12 | 23 | 15 | 38 | 0 | 0 | 0 | 320 | 320 | 194 | 8 | 128 | 42 | 52 | 0 | 51 | 0 | 39 | 8 | 21 | 10 | 33 | 20 | 168 | 102 | 0 | 22 | 0 | 43 | 41 | 31 | 30 | 110 | 0 | 60 | 10 | 0 | 220 | 0 | 31 | 7 | 300 | 16 | 0 | 197 | 97 | 298 | 98 | 48 | 95 | 98 | 0 | 21 | 34 | 135 | 398 | 48 | 105 | 87 | 0 | 16 | 36 | 56 | 17 | 38 | 20 | 0 | 0 | 0 | 35 | 108 | 0 | 35 | 0 | 75 | 55 | 0 |  | 914 | 0 | 160 | 0 | 16 | 227 | 0 | 0 | 21 | 55 | 0 | 88 | 30 | 64 | 0 | 0 | 0 | 32 | 32 | 64 | 0 | 0 | 24 | 8 | 34 | 22 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 172 | 0 | 0 | 215 | 0 | 96 | 145 | 0 | 291 | 0 | 168 | 50 | 89 | 56 | 0 | 0 | 57 | 650 | 220 | 0 | 90 | 0 | 0 | 34 | 0 | 0 |  | 6951 | 4385 | 11336 | 3611 | 914 | 1837 | 952 | 1968 | 900 | 118 | 442 | 641 | 168 | 0 | 1349.1858 | 94.08
4:00 | 0 | 0 | 0 | 180 | 200 | 90 | 0 | 407 | 302 |  | 0 | 225 | 0 | 7 | 0 | 30 | 0 | 0 | 0 | 8 | 8 | 48 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 22 | 25 | 27 | 33 | 33 | 49 | 0 | 83 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 11 | 26 | 17 | 33 | 12 | 25 | 15 | 38 | 0 | 0 | 0 | 320 | 320 | 201 | 8 | 128 | 40 | 53 | 0 | 51 | 0 | 39 | 8 | 21 | 10 | 33 | 20 | 168 | 101 | 0 | 22 | 0 | 43 | 41 | 31 | 30 | 110 | 0 | 55 | 10 | 0 | 220 | 0 | 31 | 7 | 315 | 16 | 0 | 197 | 97 | 301 | 98 | 48 | 96 | 98 | 0 | 21 | 34 | 135 | 402 | 48 | 105 | 87 | 0 | 16 | 36 | 55 | 17 | 38 | 20 | 0 | 0 | 0 | 35 | 108 | 0 | 35 | 0 | 75 | 55 | 0 |  | 914 | 0 | 160 | 0 | 16 | 226 | 0 | 0 | 21 | 55 | 0 | 86 | 27 | 64 | 0 | 0 | 0 | 32 | 0 | 59 | 0 | 0 | 24 | 8 | 34 | 22 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 175 | 0 | 0 | 213 | 0 | 96 | 147 | 0 | 297 | 0 | 169 | 50 | 90 | 56 | 0 | 0 | 55 | 620 | 220 | 0 | 90 | 0 | 0 | 34 | 0 | 0 |  | 6948 | 4321 | 11269 | 3614 | 914 | 1867 | 957 | 1967 | 870 | 118 | 439 | 568 | 168 | 0 | 1226.6163 | 94.11
5:00 | 0 | 0 | 0 | 180 | 200 | 90 | 0 | 405 | 318 |  | 0 | 225 | 0 | 7 | 0 | 30 | 0 | 0 | 0 | 8 | 8 | 48 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 22 | 25 | 27 | 33 | 33 | 49 | 0 | 83 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 11 | 26 | 17 | 33 | 12 | 25 | 15 | 32 | 0 | 0 | 0 | 320 | 320 | 204 | 8 | 127 | 40 | 52 | 0 | 51 | 0 | 39 | 8 | 21 | 10 | 33 | 20 | 160 | 102 | 0 | 22 | 0 | 43 | 41 | 31 | 30 | 110 | 0 | 55 | 10 | 0 | 220 | 0 | 31 | 9 | 330 | 16 | 0 | 197 | 97 | 298 | 99 | 48 | 94 | 98 | 0 | 21 | 34 | 135 | 402 | 48 | 105 | 87 | 0 | 16 | 36 | 55 | 17 | 38 | 20 | 0 | 0 | 0 | 35 | 92 | 0 | 35 | 0 | 74 | 55 | 0 |  | 914 | 0 | 160 | 0 | 16 | 227 | 0 | 0 | 21 | 55 | 0 | 88 | 27 | 64 | 0 | 0 | 0 | 32 | 0 | 59 | 0 | 0 | 24 | 8 | 33 | 22 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 177 | 0 | 0 | 209 | 0 | 96 | 148 | 0 | 303 | 0 | 169 | 50 | 89 | 56 | 0 | 0 | 55 | 620 | 220 | 0 | 90 | 0 | 0 | 34 | 0 | 0 |  | 6946 | 4327 | 11273 | 3620 | 914 | 1899 | 953 | 1949 | 870 | 118 | 436 | 563 | 160 | 0 | 946.4575 | 94.14
6:00 | 0 | 0 | 0 | 180 | 200 | 90 | 0 | 407 | 317 |  | 0 | 225 | 0 | 8 | 0 | 30 | 0 | 0 | 0 | 8 | 8 | 48 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 22 | 25 | 27 | 33 | 33 | 50 | 0 | 83 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 11 | 26 | 17 | 33 | 12 | 25 | 15 | 38 | 0 | 0 | 0 | 320 | 320 | 207 | 8 | 127 | 40 | 53 | 0 | 51 | 0 | 39 | 8 | 21 | 10 | 33 | 15 | 152 | 102 | 0 | 22 | 0 | 43 | 41 | 31 | 30 | 110 | 0 | 55 | 10 | 0 | 220 | 0 | 31 | 9 | 315 | 16 | 0 | 197 | 95 | 301 | 99 | 48 | 93 | 90 | 0 | 21 | 34 | 135 | 401 | 49 | 105 | 80 | 0 | 16 | 36 | 55 | 17 | 38 | 20 | 0 | 0 | 1 | 35 | 108 | 0 | 35 | 0 | 75 | 55 | 0 |  | 914 | 0 | 165 | 0 | 16 | 227 | 0 | 0 | 21 | 55 | 0 | 86 | 25 | 64 | 0 | 0 | 0 | 32 | 0 | 51 | 0 | 0 | 24 | 8 | 33 | 22 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 176 | 0 | 0 | 214 | 0 | 97 | 149 | 0 | 317 | 0 | 169 | 50 | 89 | 56 | 0 | 0 | 55 | 610 | 220 | 0 | 90 | 0 | 1 | 34 | 0 | 0 |  | 6934 | 4331 | 11265 | 3622 | 914 | 1902 | 956 | 1952 | 860 | 118 | 441 | 560 | 152 | 2 | 677.3576 | 94.17
7:00 | 0 | 0 | 0 | 180 | 200 | 89 | 0 | 406 | 321 |  | 0 | 225 | 0 | 7 | 0 | 30 | 0 | 0 | 0 | 8 | 8 | 48 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 22 | 25 | 27 | 33 | 33 | 42 | 0 | 83 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 11 | 26 | 17 | 33 | 12 | 25 | 15 | 28 | 0 | 0 | 0 | 320 | 320 | 206 | 8 | 135 | 36 | 53 | 0 | 51 | 0 | 30 | 8 | 21 | 10 | 33 | 15 | 136 | 102 | 0 | 22 | 0 | 43 | 41 | 31 | 30 | 110 | 0 | 60 | 10 | 0 | 221 | 0 | 31 | 9 | 325 | 8 | 0 | 197 | 95 | 301 | 98 | 48 | 93 | 88 | 0 | 21 | 34 | 135 | 401 | 49 | 105 | 84 | 1 | 16 | 36 | 55 | 17 | 38 | 20 | 0 | 5 | 1 | 35 | 108 | 0 | 35 | 5 | 75 | 55 | 0 |  | 914 | 0 | 165 | 0 | 16 | 227 | 0 | 0 | 21 | 55 | 0 | 86 | 20 | 64 | 0 | 0 | 0 | 32 | 0 | 51 | 0 | 0 | 24 | 8 | 33 | 22 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 175 | 0 | 0 | 213 | 0 | 97 | 150 | 0 | 318 | 0 | 169 | 50 | 71 | 56 | 0 | 1 | 55 | 600 | 219 | 0 | 90 | 0 | 10 | 34 | 0 | 0 |  | 6915 | 4307 | 11222 | 3622 | 914 | 1900 | 955 | 1932 | 850 | 118 | 440 | 550 | 136 | 18 | 532.6704 | 94.19
8:00 | 0 | 0 | 0 | 180 | 200 | 84 | 0 | 410 | 320 |  | 0 | 225 | 0 | 8 | 0 | 30 | 0 | 0 | 0 | 8 | 8 | 48 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 20 | 33 | 32 | 50 | 0 | 83 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 11 | 26 | 17 | 33 | 16 | 25 | 15 | 4 | 0 | 0 | 0 | 320 | 320 | 206 | 8 | 134 | 39 | 49 | 0 | 51 | 0 | 30 | 8 | 21 | 10 | 33 | 20 | 142 | 95 | 0 | 22 | 0 | 43 | 41 | 31 | 30 | 110 | 0 | 59 | 10 | 0 | 220 | 0 | 31 | 9 | 300 | 8 | 0 | 195 | 95 | 250 | 97 | 48 | 93 | 89 | 0 | 21 | 34 | 118 | 400 | 49 | 105 | 70 | 1 | 50 | 36 | 55 | 17 | 39 | 20 | 0 | 17 | 10 | 35 | 108 | 0 | 35 | 8 | 71 | 55 | 0 |  | 914 | 0 | 160 | 0 | 16 | 237 | 0 | 0 | 21 | 60 | 0 | 87 | 19 | 64 | 0 | 0 | 0 | 32 | 0 | 51 | 0 | 0 | 32 | 8 | 33 | 20 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 179 | 0 | 0 | 216 | 0 | 60 | 150 | 0 | 312 | 0 | 169 | 50 | 75 | 56 | 0 | 1 | 55 | 600 | 220 | 0 | 90 | 1 | 47 | 34 | 0 | 0 |  | 6836 | 4330 | 11166 | 3612 | 914 | 1833 | 864 | 1962 | 850 | 118 | 453 | 566 | 142 | 68 | 768.5935 | 94.22
9:00 | 0 | 0 | 0 | 180 | 0 | 83 | 0 | 406 | 320 |  | 0 | 225 | 0 | 7 | 0 | 30 | 0 | 0 | 0 | 8 | 8 | 48 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 27 | 33 | 30 | 50 | 0 | 82 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 11 | 26 | 17 | 33 | 11 | 25 | 15 | 3 | 0 | 0 | 0 | 320 | 320 | 198 | 8 | 135 | 39 | 49 | 0 | 51 | 0 | 30 | 8 | 21 | 10 | 33 | 20 | 154 | 70 | 0 | 22 | 2 | 44 | 41 | 31 | 30 | 110 | 0 | 60 | 10 | 0 | 220 | 0 | 31 | 9 | 300 | 8 | 0 | 196 | 95 | 246 | 98 | 48 | 93 | 90 | 5 | 21 | 34 | 120 | 402 | 47 | 88 | 69 | 2 | 52 | 36 | 55 | 17 | 38 | 20 | 0 | 17 | 21 | 35 | 108 | 0 | 35 | 18 | 72 | 55 | 0 |  | 915 | 0 | 150 | 0 | 16 | 237 | 0 | 0 | 21 | 60 | 0 | 88 | 18 | 48 | 0 | 0 | 0 | 32 | 0 | 51 | 0 | 0 | 32 | 8 | 33 | 19 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 179 | 0 | 0 | 215 | 0 | 55 | 150 | 0 | 297 | 0 | 169 | 50 | 89 | 56 | 0 | 1 | 50 | 600 | 220 | 0 | 90 | 4 | 74 | 34 | 0 | 0 |  | 6624 | 4322 | 10946 | 3376 | 915 | 1814 | 857 | 1934 | 850 | 117 | 452 | 565 | 154 | 127 | 1063.4976 | 94.25
10:00 | 0 | 0 | 0 | 180 | 30 | 86 | 0 | 403 | 318 |  | 0 | 225 | 0 | 7 | 0 | 30 | 0 | 0 | 0 | 8 | 8 | 64 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 19 | 25 | 28 | 33 | 30 | 47 | 0 | 81 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 6 | 26 | 17 | 33 | 12 | 25 | 15 | 2 | 0 | 0 | 0 | 320 | 320 | 199 | 8 | 135 | 39 | 47 | 0 | 43 | 0 | 30 | 8 | 21 | 10 | 28 | 20 | 136 | 71 | 0 | 22 | 1 | 44 | 41 | 31 | 30 | 110 | 0 | 55 | 10 | 0 | 215 | 0 | 30 | 9 | 310 | 8 | 0 | 196 | 95 | 300 | 98 | 46 | 95 | 89 | 10 | 21 | 34 | 120 | 403 | 47 | 88 | 69 | 4 | 52 | 17 | 55 | 17 | 39 | 20 | 0 | 17 | 53 | 35 | 108 | 0 | 35 | 32 | 75 | 55 | 0 |  | 914 | 0 | 145 | 0 | 16 | 234 | 0 | 0 | 21 | 59 | 0 | 86 | 17 | 0 | 0 | 0 | 0 | 32 | 0 | 44 | 0 | 0 | 16 | 8 | 14 | 18 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 175 | 0 | 0 | 213 | 0 | 94 | 147 | 0 | 286 | 0 | 169 | 50 | 71 | 56 | 0 | 2 | 55 | 300 | 220 | 0 | 0 | 5 | 42 | 34 | 0 | 0 |  | 6701 | 3804 | 10505 | 3378 | 914 | 1800 | 952 | 1740 | 550 | 116 | 447 | 536 | 136 | 149 | 1562.0696 | 94.28
11:00 | 0 | 0 | 0 | 180 | 70 | 84 | 0 | 400 | 255 |  | 0 | 225 | 0 | 7 | 0 | 30 | 0 | 0 | 0 | 8 | 8 | 50 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 19 | 25 | 28 | 33 | 30 | 42 | 0 | 80 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 7 | 26 | 17 | 65 | 12 | 25 | 15 | 2 | 0 | 0 | 0 | 320 | 320 | 194 | 8 | 128 | 39 | 51 | 0 | 43 | 0 | 30 | 8 | 19 | 10 | 21 | 20 | 150 | 69 | 0 | 22 | 2 | 43 | 41 | 33 | 30 | 110 | 0 | 60 | 10 | 0 | 221 | 0 | 30 | 9 | 320 | 8 | 0 | 198 | 95 | 300 | 97 | 46 | 96 | 89 | 3 | 21 | 34 | 120 | 390 | 47 | 88 | 69 | 5 | 52 | 17 | 55 | 17 | 39 | 0 | 0 | 17 | 35 | 35 | 95 | 0 | 35 | 33 | 75 | 55 | 0 |  | 914 | 0 | 140 | 0 | 16 | 238 | 0 | 0 | 21 | 59 | 0 | 84 | 14 | 0 | 0 | 0 | 0 | 32 | 0 | 44 | 0 | 0 | 24 | 8 | 14 | 17 | 0 | 11 | 0 | 0 | 251 | 0 | 0 | 172 | 0 | 0 | 207 | 0 | 95 | 144 | 0 | 281 | 17 | 168 | 50 | 71 | 56 | 0 | 4 | 55 | 370 | 214 | 0 | 18 | 5 | 88 | 34 | 0 | 0 |  | 6637 | 3936 | 10573 | 3376 | 914 | 1736 | 954 | 1770 | 621 | 115 | 445 | 524 | 150 | 175 | 1683.7175 | 94.31
12:00 | 0 | 0 | 0 | 180 | 157 | 81 | 0 | 393 | 240 |  | 0 | 225 | 0 | 8 | 0 | 30 | 0 | 0 | 0 | 8 | 8 | 50 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 19 | 25 | 28 | 33 | 30 | 47 | 0 | 80 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 8 | 26 | 17 | 65 | 12 | 25 | 15 | 3 | 0 | 0 | 0 | 320 | 320 | 192 | 8 | 128 | 36 | 50 | 0 | 43 | 0 | 30 | 8 | 19 | 10 | 20 | 20 | 160 | 69 | 0 | 22 | 2 | 42 | 41 | 33 | 30 | 110 | 0 | 59 | 10 | 0 | 201 | 0 | 30 | 9 | 320 | 8 | 0 | 198 | 95 | 300 | 96 | 46 | 97 | 89 | 3 | 0 | 17 | 118 | 384 | 47 | 88 | 69 | 3 | 52 | 17 | 55 | 17 | 38 | 0 | 0 | 17 | 51 | 35 | 90 | 0 | 35 | 35 | 75 | 55 | 0 |  | 914 | 0 | 140 | 0 | 16 | 229 | 0 | 0 | 21 | 15 | 0 | 82 | 18 | 16 | 0 | 0 | 0 | 30 | 4 | 44 | 0 | 0 | 24 | 8 | 33 | 17 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 173 | 0 | 0 | 180 | 0 | 95 | 144 | 0 | 280 | 17 | 169 | 50 | 71 | 56 | 0 | 3 | 55 | 480 | 214 | 0 | 0 | 3 | 10 | 34 | 0 | 0 |  | 6652 | 3906 | 10558 | 3421 | 914 | 1721 | 955 | 1729 | 730 | 115 | 409 | 474 | 160 | 110 | 1881.8561 | 94.34
13:00 | 0 | 0 | 0 | 180 | 300 | 86 | 0 | 396 | 224 |  | 0 | 225 | 0 | 9 | 0 | 30 | 0 | 0 | 0 | 8 | 8 | 50 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 22 | 25 | 22 | 33 | 16 | 47 | 0 | 80 | 35 | 95 | 0 | 25 | 0 | 0 | 0 | 0 |  | 11 | 26 | 17 | 65 | 18 | 25 | 15 | 2 | 0 | 0 | 0 | 320 | 320 | 169 | 8 | 128 | 36 | 52 | 0 | 43 | 0 | 30 | 10 | 19 | 10 | 18 | 20 | 168 | 69 | 0 | 22 | 2 | 43 | 41 | 33 | 30 | 110 | 0 | 60 | 10 | 0 | 200 | 0 | 31 | 9 | 320 | 8 | 0 | 198 | 95 | 300 | 95 | 46 | 97 | 93 | 4 | 0 | 17 | 117 | 402 | 46 | 88 | 69 | 1 | 52 | 17 | 55 | 17 | 39 | 0 | 0 | 17 | 56 | 42 | 90 | 0 | 35 | 29 | 75 | 55 | 0 |  | 914 | 0 | 145 | 0 | 32 | 230 | 0 | 0 | 21 | 15 | 8 | 87 | 12 | 16 | 0 | 0 | 0 | 24 | 0 | 44 | 0 | 0 | 24 | 8 | 33 | 17 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 172 | 0 | 0 | 180 | 0 | 96 | 144 | 0 | 275 | 25 | 168 | 50 | 71 | 50 | 0 | 4 | 55 | 520 | 214 | 0 | 0 | 5 | 43 | 34 | 0 | 0 |  | 6788 | 3997 | 10785 | 3548 | 914 | 1701 | 954 | 1777 | 770 | 115 | 410 | 464 | 168 | 144 | 1580.5011 | 94.37
14:00 | 0 | 0 | 0 | 180 | 300 | 79 | 0 | 400 | 250 |  | 0 | 225 | 0 | 9 | 0 | 30 | 0 | 0 | 0 | 8 | 8 | 50 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 22 | 25 | 28 | 33 | 28 | 41 | 0 | 81 | 35 | 95 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 17 | 65 | 16 | 25 | 15 | 3 | 0 | 0 | 0 | 320 | 320 | 146 | 8 | 128 | 34 | 52 | 0 | 51 | 0 | 32 | 8 | 19 | 10 | 16 | 20 | 176 | 66 | 0 | 22 | 2 | 43 | 41 | 33 | 30 | 110 | 0 | 61 | 10 | 0 | 213 | 0 | 31 | 9 | 310 | 8 | 0 | 198 | 95 | 303 | 97 | 46 | 99 | 88 | 12 | 21 | 17 | 113 | 402 | 49 | 88 | 69 | 4 | 52 | 17 | 55 | 17 | 39 | 20 | 0 | 17 | 48 | 102 | 90 | 0 | 35 | 34 | 74 | 55 | 0 |  | 915 | 0 | 145 | 0 | 32 | 230 | 0 | 0 | 21 | 18 | 8 | 86 | 20 | 16 | 0 | 0 | 0 | 24 | 0 | 44 | 0 | 0 | 24 | 8 | 33 | 17 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 172 | 0 | 0 | 180 | 0 | 96 | 143 | 0 | 275 | 35 | 168 | 50 | 86 | 50 | 0 | 5 | 55 | 510 | 214 | 0 | 0 | 5 | 25 | 34 | 0 | 0 |  | 6923 | 4005 | 10928 | 3552 | 915 | 1727 | 961 | 1887 | 760 | 116 | 410 | 469 | 176 | 135 | 1264.4009 | 94.4
15:00 | 0 | 0 | 0 | 180 | 300 | 82 | 0 | 396 | 247 |  | 0 | 225 | 0 | 7 | 0 | 30 | 0 | 0 | 0 | 8 | 8 | 50 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 22 | 25 | 28 | 33 | 28 | 50 | 0 | 81 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 30 | 33 | 14 | 25 | 15 | 2 | 0 | 0 | 0 | 320 | 320 | 170 | 8 | 121 | 31 | 51 | 0 | 51 | 0 | 38 | 8 | 21 | 10 | 25 | 20 | 158 | 66 | 0 | 20 | 2 | 44 | 41 | 33 | 30 | 110 | 0 | 62 | 10 | 0 | 221 | 0 | 31 | 9 | 320 | 8 | 0 | 197 | 95 | 305 | 94 | 46 | 96 | 79 | 12 | 21 | 17 | 113 | 391 | 49 | 88 | 69 | 0 | 52 | 17 | 65 | 17 | 43 | 20 | 0 | 17 | 46 | 102 | 99 | 0 | 35 | 17 | 67 | 55 | 0 |  | 915 | 0 | 140 | 0 | 32 | 231 | 0 | 0 | 21 | 18 | 8 | 86 | 22 | 16 | 0 | 0 | 0 | 24 | 0 | 47 | 0 | 0 | 24 | 8 | 33 | 17 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 168 | 0 | 0 | 180 | 0 | 96 | 143 | 0 | 267 | 35 | 168 | 50 | 88 | 55 | 0 | 5 | 55 | 500 | 217 | 0 | 0 | 1 | 6 | 34 | 0 | 0 |  | 6925 | 3971 | 10896 | 3566 | 915 | 1732 | 956 | 1892 | 750 | 116 | 411 | 491 | 158 | 89 | 1386.0488 | 94.43
16:00 | 0 | 0 | 0 | 180 | 300 | 82 | 0 | 400 | 236 |  | 0 | 225 | 0 | 7 | 0 | 30 | 0 | 0 | 0 | 8 | 8 | 100 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 22 | 25 | 26 | 33 | 28 | 50 | 0 | 81 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 51 | 33 | 14 | 29 | 15 | 5 | 0 | 0 | 0 | 320 | 320 | 174 | 8 | 123 | 31 | 50 | 0 | 43 | 0 | 38 | 8 | 21 | 10 | 25 | 20 | 162 | 66 | 0 | 22 | 1 | 43 | 41 | 33 | 30 | 110 | 0 | 62 | 10 | 0 | 220 | 0 | 30 | 10 | 290 | 16 | 0 | 195 | 95 | 302 | 95 | 47 | 96 | 89 | 13 | 21 | 17 | 113 | 403 | 49 | 88 | 69 | 0 | 52 | 23 | 74 | 34 | 66 | 20 | 0 | 17 | 27 | 102 | 108 | 0 | 35 | 12 | 71 | 43 | 0 |  | 915 | 0 | 140 | 0 | 32 | 229 | 0 | 0 | 21 | 19 | 8 | 88 | 22 | 16 | 0 | 0 | 0 | 32 | 0 | 43 | 0 | 0 | 30 | 8 | 33 | 17 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 168 | 0 | 0 | 180 | 0 | 96 | 143 | 0 | 274 | 50 | 115 | 65 | 88 | 54 | 0 | 5 | 55 | 520 | 214 | 0 | 0 | 2 | 46 | 34 | 0 | 0 |  | 7024 | 4023 | 11047 | 3596 | 915 | 1689 | 899 | 1992 | 770 | 116 | 409 | 573 | 162 | 106 | 1154.7335 | 94.46
17:00 | 0 | 0 | 0 | 180 | 300 | 77 | 0 | 399 | 225 |  | 0 | 225 | 0 | 8 | 0 | 30 | 0 | 0 | 0 | 8 | 8 | 128 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 24 | 33 | 28 | 41 | 0 | 81 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 51 | 33 | 14 | 31 | 15 | 3 | 0 | 0 | 0 | 320 | 320 | 158 | 8 | 121 | 34 | 50 | 0 | 51 | 0 | 38 | 8 | 21 | 9 | 33 | 20 | 160 | 67 | 0 | 22 | 0 | 43 | 41 | 33 | 30 | 110 | 0 | 63 | 10 | 0 | 220 | 0 | 30 | 9 | 290 | 16 | 0 | 100 | 110 | 200 | 95 | 47 | 97 | 96 | 3 | 21 | 17 | 113 | 403 | 49 | 92 | 82 | 0 | 85 | 36 | 74 | 84 | 101 | 20 | 0 | 17 | 14 | 120 | 108 | 0 | 35 | 3 | 74 | 37 | 0 |  | 914 | 0 | 145 | 0 | 16 | 228 | 0 | 0 | 21 | 19 | 8 | 88 | 20 | 16 | 0 | 0 | 0 | 32 | 3 | 43 | 0 | 0 | 32 | 8 | 33 | 17 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 168 | 0 | 0 | 180 | 0 | 96 | 144 | 0 | 278 | 47 | 90 | 92 | 88 | 97 | 0 | 3 | 55 | 530 | 200 | 0 | 0 | 1 | 21 | 72 | 0 | 0 |  | 6999 | 4066 | 11065 | 3593 | 914 | 1666 | 678 | 2279 | 780 | 116 | 408 | 606 | 160 | 45 | 953.8301 | 94.49
18:00 | 0 | 0 | 0 | 180 | 300 | 77 | 0 | 395 | 222 |  | 0 | 225 | 0 | 7 | 0 | 30 | 0 | 0 | 0 | 8 | 8 | 128 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 23 | 33 | 28 | 49 | 0 | 82 | 35 | 105 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 51 | 33 | 33 | 31 | 15 | 19 | 0 | 0 | 0 | 320 | 320 | 169 | 8 | 121 | 37 | 51 | 0 | 51 | 0 | 37 | 8 | 21 | 9 | 30 | 20 | 156 | 67 | 0 | 22 | 0 | 43 | 41 | 35 | 30 | 110 | 0 | 61 | 10 | 0 | 220 | 0 | 30 | 10 | 270 | 16 | 0 | 20 | 205 | 34 | 25 | 174 | 25 | 149 | 0 | 21 | 17 | 118 | 403 | 76 | 105 | 105 | 0 | 88 | 36 | 60 | 114 | 101 | 20 | 0 | 17 | 4 | 162 | 108 | 0 | 35 | 2 | 75 | 55 | 0 |  | 914 | 0 | 145 | 0 | 16 | 229 | 0 | 0 | 21 | 25 | 8 | 85 | 20 | 16 | 0 | 0 | 0 | 32 | 5 | 50 | 0 | 0 | 32 | 8 | 33 | 18 | 0 | 11 | 11 | 0 | 250 | 0 | 0 | 167 | 0 | 0 | 130 | 0 | 70 | 145 | 0 | 274 | 68 | 20 | 94 | 88 | 98 | 0 | 2 | 95 | 520 | 215 | 0 | 0 | 0 | 5 | 90 | 0 | 0 |  | 7068 | 4010 | 11078 | 3599 | 914 | 1675 | 194 | 2830 | 781 | 117 | 359 | 570 | 156 | 13 | 573.2196 | 94.52
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 300 | 79 | 0 | 393 | 217 |  | 0 | 225 | 0 | 8 | 0 | 30 | 0 | 0 | 0 | 22 | 32 | 128 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 23 | 33 | 28 | 49 | 0 | 82 | 35 | 105 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 34 | 51 | 33 | 72 | 31 | 15 | 19 | 0 | 0 | 0 | 320 | 320 | 177 | 8 | 120 | 36 | 52 | 0 | 51 | 0 | 38 | 14 | 21 | 9 | 30 | 20 | 164 | 95 | 0 | 22 | 0 | 44 | 41 | 36 | 40 | 110 | 0 | 61 | 50 | 0 | 221 | 0 | 32 | 10 | 310 | 16 | 0 | 188 | 258 | 282 | 95 | 179 | 94 | 149 | 0 | 76 | 22 | 133 | 403 | 78 | 88 | 105 | 0 | 206 | 36 | 55 | 114 | 109 | 30 | 0 | 17 | 0 | 162 | 108 | 0 | 35 | 0 | 75 | 55 | 0 |  | 915 | 0 | 145 | 0 | 31 | 227 | 0 | 0 | 36 | 50 | 8 | 88 | 26 | 16 | 0 | 0 | 0 | 32 | 6 | 80 | 0 | 0 | 32 | 43 | 33 | 20 | 0 | 11 | 47 | 0 | 251 | 0 | 0 | 168 | 0 | 0 | 143 | 0 | 85 | 146 | 0 | 282 | 53 | 54 | 94 | 88 | 98 | 0 | 0 | 95 | 520 | 217 | 0 | 0 | 0 | 0 | 90 | 0 | 0 |  | 8092 | 4230 | 12322 | 3638 | 915 | 1784 | 798 | 3198 | 818 | 117 | 370 | 663 | 164 | 0 | 440.5129 | 0
19:30 | 0 | 0 | 0 | 180 | 300 | 82 | 0 | 392 | 214 |  | 0 | 225 | 0 | 33 | 0 | 30 | 0 | 0 | 0 | 50 | 32 | 128 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 23 | 33 | 28 | 49 | 0 | 82 | 35 | 105 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12 | 34 | 51 | 33 | 77 | 0 | 15 | 3 | 0 | 0 | 0 | 320 | 320 | 177 | 8 | 121 | 38 | 52 | 0 | 51 | 0 | 38 | 43 | 21 | 9 | 31 | 20 | 158 | 96 | 0 | 22 | 0 | 43 | 41 | 53 | 48 | 110 | 0 | 63 | 81 | 0 | 221 | 0 | 31 | 10 | 265 | 16 | 0 | 150 | 258 | 244 | 94 | 179 | 97 | 149 | 0 | 76 | 34 | 129 | 402 | 78 | 88 | 105 | 0 | 210 | 36 | 55 | 114 | 115 | 100 | 0 | 30 | 0 | 162 | 108 | 0 | 35 | 0 | 70 | 55 | 0 |  | 914 | 0 | 155 | 0 | 30 | 230 | 0 | 0 | 48 | 57 | 8 | 87 | 28 | 16 | 0 | 0 | 0 | 32 | 7 | 80 | 0 | 0 | 32 | 52 | 33 | 20 | 0 | 11 | 66 | 0 | 251 | 0 | 0 | 167 | 0 | 0 | 180 | 0 | 50 | 149 | 0 | 289 | 53 | 161 | 94 | 88 | 98 | 0 | 0 | 95 | 580 | 217 | 0 | 54 | 0 | 0 | 90 | 0 | 0 |  | 8137 | 4522 | 12659 | 3653 | 914 | 1787 | 796 | 3387 | 897 | 117 | 410 | 720 | 158 | 0 | 590.7296 | 0
20:00 | 0 | 0 | 0 | 180 | 300 | 82 | 0 | 392 | 214 |  | 0 | 225 | 0 | 30 | 0 | 30 | 0 | 0 | 0 | 48 | 32 | 128 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 23 | 33 | 28 | 49 | 0 | 83 | 35 | 105 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12 | 34 | 51 | 33 | 77 | 7 | 15 | 20 | 0 | 0 | 0 | 320 | 320 | 184 | 8 | 120 | 38 | 52 | 0 | 51 | 0 | 38 | 43 | 22 | 9 | 33 | 20 | 160 | 95 | 0 | 22 | 0 | 44 | 41 | 53 | 49 | 110 | 0 | 63 | 81 | 0 | 220 | 0 | 30 | 10 | 260 | 16 | 0 | 150 | 260 | 250 | 95 | 180 | 98 | 149 | 0 | 90 | 34 | 127 | 403 | 78 | 88 | 105 | 0 | 210 | 29 | 55 | 114 | 114 | 100 | 0 | 33 | 0 | 162 | 108 | 0 | 35 | 0 | 58 | 55 | 0 |  | 915 | 0 | 155 | 0 | 32 | 230 | 0 | 0 | 38 | 68 | 8 | 87 | 27 | 45 | 0 | 0 | 0 | 32 | 7 | 80 | 0 | 0 | 32 | 52 | 35 | 20 | 0 | 11 | 66 | 0 | 250 | 0 | 0 | 166 | 0 | 0 | 180 | 0 | 50 | 148 | 0 | 296 | 53 | 165 | 94 | 89 | 97 | 0 | 0 | 95 | 590 | 210 | 0 | 44 | 0 | 0 | 90 | 0 | 0 |  | 8169 | 4557 | 12726 | 3660 | 915 | 1798 | 808 | 3408 | 906 | 118 | 410 | 723 | 160 | 0 | 897.6141 | 94.58
21:00 | 0 | 0 | 0 | 180 | 300 | 82 | 0 | 393 | 214 |  | 0 | 225 | 0 | 31 | 0 | 30 | 0 | 0 | 0 | 48 | 32 | 128 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 23 | 33 | 28 | 49 | 0 | 80 | 35 | 105 | 0 | 1 | 0 | 0 | 0 | 0 |  | 12 | 34 | 51 | 33 | 77 | 37 | 15 | 21 | 0 | 0 | 0 | 320 | 320 | 190 | 8 | 121 | 38 | 52 | 0 | 51 | 0 | 38 | 43 | 22 | 9 | 33 | 20 | 158 | 96 | 0 | 22 | 0 | 43 | 41 | 53 | 49 | 110 | 0 | 62 | 81 | 0 | 221 | 0 | 31 | 10 | 310 | 16 | 0 | 200 | 258 | 300 | 97 | 180 | 97 | 149 | 0 | 90 | 34 | 128 | 404 | 78 | 105 | 105 | 0 | 214 | 36 | 55 | 114 | 115 | 100 | 0 | 32 | 0 | 162 | 108 | 0 | 35 | 0 | 68 | 55 | 0 |  | 914 | 0 | 155 | 0 | 22 | 229 | 0 | 0 | 38 | 63 | 8 | 87 | 30 | 48 | 0 | 0 | 0 | 32 | 17 | 80 | 0 | 0 | 32 | 52 | 33 | 21 | 0 | 11 | 70 | 0 | 250 | 0 | 0 | 167 | 0 | 0 | 180 | 0 | 79 | 149 | 0 | 287 | 53 | 179 | 94 | 89 | 97 | 0 | 0 | 95 | 570 | 222 | 0 | 54 | 0 | 0 | 90 | 0 | 0 |  | 8373 | 4597 | 12970 | 3649 | 914 | 1857 | 952 | 3480 | 890 | 115 | 409 | 726 | 158 | 0 | 857.0648 | 0
22:00 | 0 | 0 | 0 | 180 | 300 | 83 | 0 | 399 | 220 |  | 0 | 225 | 0 | 24 | 0 | 30 | 0 | 0 | 0 | 48 | 32 | 130 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 24 | 33 | 28 | 49 | 0 | 81 | 35 | 105 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 27 | 51 | 33 | 77 | 43 | 15 | 28 | 0 | 0 | 0 | 320 | 320 | 195 | 8 | 120 | 38 | 53 | 0 | 51 | 0 | 36 | 43 | 22 | 10 | 33 | 20 | 156 | 98 | 0 | 22 | 0 | 43 | 41 | 53 | 49 | 110 | 0 | 63 | 81 | 0 | 220 | 0 | 29 | 10 | 300 | 16 | 0 | 200 | 258 | 302 | 97 | 180 | 98 | 142 | 0 | 90 | 34 | 133 | 403 | 78 | 88 | 105 | 0 | 214 | 36 | 55 | 114 | 114 | 100 | 0 | 33 | 0 | 162 | 108 | 0 | 35 | 0 | 73 | 55 | 0 |  | 915 | 0 | 155 | 0 | 32 | 229 | 0 | 0 | 38 | 53 | 8 | 87 | 31 | 48 | 0 | 0 | 0 | 32 | 0 | 80 | 0 | 0 | 32 | 52 | 33 | 21 | 0 | 11 | 71 | 0 | 250 | 0 | 0 | 170 | 0 | 0 | 199 | 0 | 96 | 149 | 0 | 300 | 35 | 181 | 94 | 105 | 97 | 0 | 0 | 95 | 570 | 223 | 0 | 72 | 0 | 0 | 90 | 0 | 0 |  | 8393 | 4654 | 13047 | 3665 | 915 | 1875 | 974 | 3515 | 891 | 116 | 428 | 711 | 156 | 0 | 786.1035 | 94.64
23:00 | 0 | 0 | 0 | 180 | 300 | 83 | 0 | 406 | 232 |  | 0 | 225 | 0 | 17 | 0 | 30 | 0 | 0 | 0 | 48 | 32 | 130 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 0 | 25 | 24 | 33 | 30 | 49 | 0 | 81 | 35 | 105 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 34 | 51 | 33 | 43 | 29 | 15 | 30 | 0 | 0 | 0 | 320 | 320 | 195 | 8 | 120 | 38 | 53 | 0 | 51 | 0 | 40 | 43 | 22 | 10 | 33 | 20 | 152 | 101 | 0 | 22 | 0 | 43 | 41 | 53 | 49 | 110 | 0 | 62 | 81 | 0 | 221 | 0 | 31 | 10 | 300 | 16 | 0 | 200 | 273 | 301 | 97 | 180 | 97 | 141 | 0 | 90 | 34 | 137 | 397 | 78 | 88 | 105 | 0 | 52 | 36 | 55 | 114 | 114 | 100 | 0 | 33 | 0 | 162 | 108 | 0 | 35 | 0 | 75 | 55 | 0 |  | 914 | 0 | 155 | 0 | 16 | 228 | 0 | 0 | 37 | 53 | 8 | 86 | 31 | 48 | 0 | 0 | 0 | 32 | 0 | 80 | 0 | 0 | 32 | 52 | 33 | 21 | 0 | 11 | 71 | 0 | 251 | 0 | 0 | 169 | 0 | 0 | 214 | 0 | 96 | 151 | 0 | 291 | 35 | 181 | 94 | 105 | 98 | 0 | 0 | 95 | 590 | 220 | 0 | 72 | 0 | 0 | 90 | 0 | 0 |  | 8203 | 4660 | 12863 | 3671 | 914 | 1879 | 972 | 3283 | 912 | 116 | 442 | 736 | 152 | 0 | 863.5158 | 94.67
24:00 | 0 | 0 | 0 | 180 | 300 | 83 | 0 | 405 | 241 |  | 0 | 225 | 0 | 9 | 0 | 30 | 0 | 0 | 0 | 23 | 8 | 48 | 0 | 0 | 0 | 0 | 54 | 55 | 0 | 22 | 25 | 24 | 33 | 30 | 49 | 0 | 81 | 35 | 105 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 34 | 51 | 33 | 12 | 26 | 15 | 30 | 0 | 0 | 0 | 300 | 320 | 195 | 8 | 121 | 38 | 54 | 0 | 51 | 0 | 40 | 43 | 22 | 10 | 33 | 20 | 128 | 102 | 0 | 22 | 0 | 43 | 41 | 53 | 49 | 110 | 0 | 63 | 81 | 0 | 220 | 0 | 31 | 10 | 310 | 16 | 0 | 200 | 132 | 270 | 97 | 48 | 98 | 85 | 0 | 90 | 34 | 137 | 402 | 49 | 88 | 91 | 0 | 52 | 36 | 56 | 60 | 113 | 100 | 0 | 29 | 0 | 162 | 108 | 0 | 35 | 0 | 75 | 55 | 0 |  | 914 | 0 | 155 | 0 | 16 | 228 | 0 | 0 | 35 | 53 | 8 | 88 | 32 | 48 | 0 | 0 | 0 | 32 | 0 | 80 | 0 | 0 | 32 | 52 | 34 | 22 | 0 | 11 | 71 | 0 | 250 | 0 | 0 | 169 | 0 | 0 | 212 | 0 | 96 | 150 | 0 | 291 | 17 | 180 | 94 | 105 | 70 | 0 | 0 | 95 | 590 | 215 | 0 | 90 | 0 | 0 | 90 | 0 | 0 |  | 7539 | 4625 | 12164 | 3680 | 914 | 1896 | 941 | 2699 | 911 | 116 | 440 | 651 | 128 | 0 | 1415.5392 | 94.7
KWH | 0 | 0 | 0 | 4347000 | 5429336 | 1970681 | 0 | 9748480 | 6318000 |  | 0 | 4942400 | 0 | 269760 | 0 | 736753 | 0 | 0 | 0 | 386726 | 300096 | 1745760 | 0 | 0 | 0 | 0 | 894240 | 1284846 | 964333 | 418572 | 600000 | 583740 | 792500 | 705100 | 1141440 | 0 | 1886749 | 840000 | 2400000 | 0 | 540190 | 0 | 0 | 0 | 0 |  | 273120 | 640176 | 816342 | 1382880 | 624000 | 639360 | 356496 | 403680 | 0 | 0 | 0 | 8003000 | 7876000 | 4554000 | 217454 | 3024910 | 890928 | 1237440 | 0 | 1169784 | 0 | 858496 | 396653 | 493344 | 235620 | 715300 | 469940 | 3752640 | 1993920 | 0 | 491724 | 14550 | 1022000 | 927944 | 913800 | 922608 | 2595027 | 0 | 1436736 | 776640 | 0 | 5225520 | 0 | 718400 | 212400 | 7547500 | 295464 | 0 | 4430016 | 3327053 | 6660161 | 2229976 | 1896000 | 2243877 | 2572704 | 73440 | 807360 | 707520 | 3032654 | 9584000 | 1317600 | 2278800 | 2058291 | 24121 | 1658509 | 757113 | 1391703 | 1147980 | 1543920 | 884160 | 0 | 372480 | 379390 | 2069280 | 2514109 | 0 | 885960 | 202236 | 1770240 | 1299240 | 0 |  | 22097454 | 0 | 3796992 | 0 | 484800 | 5519040 | 0 | 0 | 570240 | 1054720 | 102375 | 2074016 | 563305 | 967584 | 0 | 0 | 0 | 731632 | 128941 | 1367056 | 0 | 0 | 564800 | 426240 | 754460 | 444960 | 0 | 233334 | 371345 | 0 | 6080800 | 0 | 0 | 4340491 | 0 | 0 | 4908091 | 0 | 2214720 | 3763018 | 0 | 6918400 | 517920 | 3773965 | 1681056 | 2076192 | 1627171 | 0 | 37274 | 1615872 | 14851900 | 5214518 | 0 | 1236000 | 34860 | 496080 | 1318272 | 0 | 0 |  | 173492391 | 104959894 | 278452285 | 86829425 | 22097454 | 43086997 | 21552715 | 56180555 | 21304045 | 2726749 | 10427131 | 9232623 | 3752640 | 1261951 | 0
Fuel Cost | 0 | 0 | 0 | 6477030 | 6080856.32 | 2621005.73 | 0 | 10235904 | 6823440 |  | 0 | 5387216 | 0 | 3015916.8 | 0 | 9761977.25 | 0 | 0 | 0 | 5653934.12 | 4222350.72 | 28298769.6 | 0 | 0 | 0 | 0 | 11374732.8 | 17345421 | 12931705.53 | 313929 | 450000 | 0 | 0 | 0 | 19415894.4 | 0 | 509422.23 | 226800 | 4536000 | 0 | 8832106.5 | 0 | 0 | 0 | 0 |  | 3564216 | 10678135.68 | 13894140.84 | 18682708.8 | 7912320 | 7397395.2 | 452749.92 | 1344254.4 | 0 | 0 | 0 | 8883330 | 8584840 | 5282640 | 280515.66 | 3690390.2 | 1006748.64 | 1843785.6 | 0 | 1953539.28 | 0 | 14826225.92 | 5334982.85 | 675881.28 | 176715 | 1251775 | 352455 | 26943955.2 | 2173372.8 | 0 | 668744.64 | 231927 | 1400140 | 1224886.08 | 1590012 | 1596111.84 | 2984281.05 | 0 | 2787267.84 | 1770739.2 | 0 | 5277775.2 | 0 | 1070416 | 420552 | 7547500 | 221598 | 0 | 92853135.36 | 45414273.45 | 139596974.56 | 46093603.92 | 25558080 | 46380937.59 | 35631950.4 | 858513.6 | 8331955.2 | 9664723.2 | 40243318.58 | 8817280 | 16022016 | 32951448 | 26037381.15 | 0 | 19470895.66 | 8244960.57 | 14793802.89 | 15578088.6 | 19901128.8 | 10415404.8 | 0 | 4823616 | 5482185.5 | 26259163.2 | 28610560.42 | 0 | 11570637.6 | 2416720.2 | 26500492.8 | 17110990.8 | 0 |  | 66292362 | 0 | 4252631.04 | 0 | 5046768 | 91064160 | 0 | 0 | 10270022.4 | 18984960 | 1471128.75 | 2322897.92 | 1092811.7 | 10546665.6 | 0 | 0 | 0 | 12269468.64 | 2255178.09 | 21380755.84 | 0 | 0 | 9550768 | 5809651.2 | 12727740.2 | 921067.2 | 0 | 176633.838 | 2157514.45 | 0 | 32167432 | 0 | 0 | 5034969.56 | 0 | 0 | 85695268.86 | 0 | 46464825.6 | 4365100.88 | 0 | 6849216 | 6960844.8 | 79140046.05 | 19886892.48 | 30000974.4 | 20665071.7 | 0 | 411877.7 | 19616686.08 | 133815619 | 5318808.36 | 0 | 9146400 | 394266.6 | 5819018.4 | 20209109.76 | 0 | 0 |  | 1126127674.97 | 810555613.098 | 1936683288.068 | 97174542.158 | 66292362 | 51415272.02 | 450529523.08 | 727940742.86 | 168140565.45 | 736222.23 | 176759428.86 | 155136165.21 | 26943955.2 | 15614509 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 0 | 83 | 0 | 406 | 320 |  | 0 | 225 | 0 | 7 | 0 | 30 | 0 | 0 | 0 | 8 | 8 | 48 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 27 | 33 | 30 | 50 | 0 | 82 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 11 | 26 | 17 | 33 | 11 | 25 | 15 | 3 | 0 | 0 | 0 | 320 | 320 | 198 | 8 | 135 | 39 | 49 | 0 | 51 | 0 | 30 | 8 | 21 | 10 | 33 | 20 | 154 | 70 | 0 | 22 | 2 | 44 | 41 | 31 | 30 | 110 | 0 | 60 | 10 | 0 | 220 | 0 | 31 | 9 | 300 | 8 | 0 | 196 | 95 | 246 | 98 | 48 | 93 | 90 | 5 | 21 | 34 | 120 | 402 | 47 | 88 | 69 | 2 | 52 | 36 | 55 | 17 | 38 | 20 | 0 | 17 | 21 | 35 | 108 | 0 | 35 | 18 | 72 | 55 | 0 |  | 915 | 0 | 150 | 0 | 16 | 237 | 0 | 0 | 21 | 60 | 0 | 88 | 18 | 48 | 0 | 0 | 0 | 32 | 0 | 51 | 0 | 0 | 32 | 8 | 33 | 19 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 179 | 0 | 0 | 215 | 0 | 55 | 150 | 0 | 297 | 0 | 169 | 50 | 89 | 56 | 0 | 1 | 50 | 600 | 220 | 0 | 90 | 4 | 74 | 34 | 0 | 0 |  | 10946 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 300 | 82 | 0 | 393 | 214 | 0 | 0 | 225 | 0 | 31 | 0 | 30 | 0 | 0 | 0 | 48 | 32 | 128 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 23 | 33 | 28 | 49 | 0 | 80 | 35 | 105 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 12 | 34 | 51 | 33 | 77 | 37 | 15 | 21 | 0 | 0 | 0 | 320 | 320 | 190 | 8 | 121 | 38 | 52 | 0 | 51 | 0 | 38 | 43 | 22 | 9 | 33 | 20 | 158 | 96 | 0 | 22 | 0 | 43 | 41 | 53 | 49 | 110 | 0 | 62 | 81 | 0 | 221 | 0 | 31 | 10 | 310 | 16 | 0 | 200 | 258 | 300 | 97 | 180 | 97 | 149 | 0 | 90 | 34 | 128 | 404 | 78 | 105 | 105 | 0 | 214 | 36 | 55 | 114 | 115 | 100 | 0 | 32 | 0 | 162 | 108 | 0 | 35 | 0 | 68 | 55 | 0 |  | 914 | 0 | 155 | 0 | 22 | 229 | 0 | 0 | 38 | 63 | 8 | 87 | 30 | 48 | 0 | 0 | 0 | 32 | 17 | 80 | 0 | 0 | 32 | 52 | 33 | 21 | 0 | 11 | 70 | 0 | 250 | 0 | 0 | 167 | 0 | 0 | 180 | 0 | 79 | 149 | 0 | 287 | 53 | 179 | 94 | 89 | 97 | 0 | 0 | 95 | 570 | 222 | 0 | 54 | 0 | 0 | 90 | 0 | 0 |  | 12970 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 305 | 86 | 0 | 412 | 320 | 0 | 0 | 225 | 0 | 32 | 0 | 30 | 0 | 0 | 0 | 48 | 32 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 25 | 33 | 33 | 51 | 0 | 83 | 35 | 105 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 12 | 34 | 51 | 33 | 80 | 35 | 15 | 20 | 0 | 0 | 0 | 320 | 320 | 210 | 8 | 142 | 39 | 55 | 0 | 51 | 0 | 38 | 43 | 22 | 10 | 33 | 20 | 166 | 100 | 0 | 22 | 0 | 43 | 41 | 53 | 49 | 110 | 0 | 62 | 81 | 0 | 220 | 0 | 31 | 10 | 310 | 16 | 11 | 200 | 275 | 300 | 96 | 180 | 100 | 149 | 0 | 90 | 34 | 145 | 400 | 78 | 105 | 105 | 0 | 210 | 36 | 55 | 114 | 113 | 100 | 0 | 52 | 0 | 162 | 108 | 0 | 35 |  | 71 | 55 |  |  | 928 | 0 | 170 | 0 | 32 | 225 | 0 | 0 | 38 | 70 | 8 | 88 | 30 | 64 | 0 | 0 | 0 | 32 | 40 | 86 | 0 | 42 | 32 | 52 | 33 | 21 | 0 | 11 | 75 | 0 | 250 | 0 | 0 | 190 | 0 | 0 | 210 | 0 | 96 | 165 | 0 | 315 | 70 | 188 | 94 | 105 | 92 | 0 | 0 | 95 | 620 | 220 |  | 54 |  |  | 90
Forecast for Day | 0 | 0 | 0 | 180 | 305 | 86 | 0 | 410 | 310 | 0 | 0 | 225 | 0 | 8 | 0 | 30 | 0 | 0 | 0 | 8 | 8 | 50 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 25 | 33 | 33 | 51 | 0 | 83 | 35 | 105 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 12 | 26 | 17 | 33 | 12 | 25 | 15 | 5 | 0 | 0 | 0 | 320 | 305 | 210 | 8 | 142 | 39 | 55 | 0 | 51 | 0 | 38 | 8 | 22 | 10 | 33 | 20 | 143 | 95 | 0 | 22 | 1.6 | 43 | 41 | 22 | 20 | 110 | 0 | 62 | 10 | 0 | 220 | 0 | 31 | 10 | 280 | 16 | 11 | 120 | 110 | 250 | 97 | 48 | 50 | 90 | 20 | 21 | 17 | 123 | 400 | 48 | 105 | 68 | 5 | 52 | 17 | 55 | 17 | 38 | 20 | 0 | 17 | 50 | 35 | 108 | 0 | 35 | 30 | 71 | 35 |  |  | 928 | 0 | 150 | 0 | 16 | 225 | 0 | 0 | 15 | 60 | 8 | 88 | 23 | 64 | 0 | 0 | 0 | 32 | 0 | 80 | 0 | 42 | 32 | 8 | 33 | 21 | 0 | 11 | 75 | 0 | 250 | 0 | 0 | 188 | 0 | 0 | 210 | 0 | 60 | 160 | 0 | 315 | 0 | 100 | 50 | 105 | 70 | 0 | 8 | 55 | 620 | 225 |  | 0 | 6 | 100 | 52
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 305 | 86 | 0 | 409 | 303 | 0 | 0 | 225 | 0 | 7 | 0 | 30 | 0 | 0 | 0 | 8 | 8 | 49 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 0 | 25 | 26 | 25 | 28 | 42 | 0 | 83 | 35 | 105 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 12 | 26 | 17 | 33 | 12 | 25 | 15 | 8 | 0 | 0 | 0 | 320 | 305 | 204 | 8 | 136 | 39 | 54 | 0 | 51 | 0 | 39 | 8 | 22 | 10 | 33 | 0 | 104 | 95 | 0 | 22 | 1 | 43 | 41 | 22 | 20 | 110 | 0 | 63 | 10 | 0 | 221 | 0 | 30 | 10 | 280 | 16 | 0 | 120 | 97 | 215 | 50 | 48 | 50 | 32 | 2 | 21 | 17 | 123 | 402 | 48 | 88 | 69 | 3 | 50 | 17 | 55 | 17 | 38 | 20 | 0 | 6 | 22 | 35 | 108 | 0 | 35 | 17 | 71 | 35 | 0 | 0 | 911 | 0 | 165 | 0 | 16 | 229 | 0 | 0 | 0 | 0 | 8 | 88 | 14 | 0 | 0 | 0 | 0 | 32 | 0 | 23 | 0 | 0 | 32 | 8 | 33 | 20 | 0 | 11 | 74 | 0 | 250 | 0 | 0 | 177 | 0 | 0 | 213 | 0 | 50 | 153 | 0 | 315 | 0 | 100 | 50 | 105 | 70 | 0 | 3 | 55 | 510 | 218 | 0 | 0 | 2 | 20 | 0 | 0 | 0 | 0 |  |  |  |  | 97393024 |  | 0
97393024
| Minimum Generation |  | 10946 | 9:00
| Highest Generation |  | 13047 | 22:00
| Day Peak Generation |  | 10946 | 9:00
| Evening Peak Generation |  | 12970 | 21:00
| HVDC Max Flow |  | 915 | 9:00
| HVDC EvPeak Flow |  | 914 | 21:00
| Load factor L.F |  | 88.93% | [159 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2022-08-09
Till now the maximum generation is : - |  |  | 14782 | 21:00 | Hrs on | 2022-04-16
The Summary of Yesterday's |  | 2022-08-08 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 10946 | MW Hour : | 9:00 | Min. Gen. at | 8:00 | 10442 | MW
Evening Peak Generation : |  | 12970 | MW Hour : | 21:00 | Available Max Generation : |  | 13615 | MW
E.P. Demand (at gen end) : |  | 13900 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 13600 | MW
Maximum Generation : |  | 13047 | MW Hour : | 22:00 | Reserve(Generation end) |  | 15 | MW
Total Gen. (MKWH) : |  | 278.4523 | System Load Factor : | 88.93% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | 454 | MW at | 5:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2022-08-09
Actual : | 94.92 | Ft.(MSL) , | Rule curve : | 91.56 | Ft.( MSL )
Gas Consumed : | Total = | 991.46 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 148589814.178
: |  | Coal : | 168140565.45 | Oil : | 1510365860.01 | Total : | 1827096239.638
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 223 | 5352:00 | 4355.3635 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1233.2885 |  |  | 0 | 0%
Khulna Area | 128.4209 | 3082:06 | 1628.0913 |  |  | 0 | 0%
Rajshahi Area | 147 | 3528:00 | 1445.1033 |  |  | 0 | 0%
Cumilla Area | 100.2162 | 2405:11 | 1229.5285 |  |  | 0 | 0%
Mymensingh Area | 141 | 3384:00 | 1016.4604 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 453.7098 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 369.7359 |  |  | 0 | 0%
Rangpur Area | 117 | 2808:00 | 802.1389 |  |  | 0 | 0%
Total | 856.6371 |  | 12533.42 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-2 |  | 10) Payra unit-2
2) Ghorasal-3,4
3) Ashuganj-5
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
7) Sikalbaha 225 MW
8) Shajibazar 330 MW
9) Siddhirganj 335 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Mymensing-Netrokona 132 kV Ckt-1 was under shut down from 09:30 to 12:14 for C/M.
b) Munshiganj-Madanganj132 kV Ckt-2 was under shut down from 09:51 to 17:19 for C/M.
c) Mithapukur 132/33 kV T-2 transformer was under shut down from 10:37 to 12:32 for C/M.
d) Aminbazar 230/132 kV T03 transformer was under shut down from 10:32 to 16:37 for C/M.
e) Rampura-Aftabnagar 132 kV Ckt-2 was under shut down from 10:47 to 16:48 for D/W. | [5 empty] | About 30 MW power interruption occurred under
f) Rampura 132/33 kV T-2 transformer was under shut down from 11:10 to 16:38 for D/W. | [5 empty] | Bogura Sherpur S/S area from 08:20 to 09:46.
g) Bogura 132/33 kV T-1 & T-2 transformer tripped at 09:21 from 33 kV end showing O/C relays & 33 kV Bogura | [5 empty] | About 55 MW power interruption occurred under
Oil feeder fault and was switched on at 09:57. | [5 empty] | Bogura S/S area from 09:21 to 09:57.
h) Payra uni-2 was shut down at 12:42 due to coal shortage.
i) Ashuganj 230/132 kV T01 transformer tripped at 09:21 from 132 kV end showing O/C relays and was
switched on at 15:21.
j) Gopalganj(N)-Rampal 400 kV Ckt tripped at 09:36 from showing O/V relay at Gopalganj(N) end.
k) Gopalganj(N)-Payra P/P 400 kV Ckt tripped at 09:36 from showing O/V relay at Gopalganj(N) end.
l) Payra S/S-Payra P/P 400 kV Ckt-1 & 2 tripped at 09:36 from showing O/V relay and was switched on at 10:40.
m) Chandpur 132/33 kV T2 transformer was switched on at 15:27.
n) Tongi 132/33 kV T3 transformer was under shut down from 16:12 to 16:44 for TRTUD work.
o) Aminbazar-Manikganj P/P 132 kV Ckt-2 was under shut down from 16:50 to 21:09 for relay work.
p) Madunaghat 132/33 kV T-1 & T-2 transformers tripped at 19:03 33 kV end showing DMT, Gen trip O/C | [5 empty] | About 70 MW power interruption occurred under
relays and was switched on at 20:00. | [5 empty] | Madunaghat S/S area from 19:03 to 20:00.
q) Barapukuria unit-1 was synchronized at 17:14.
r) Kabirpur-Kodda 132 kV Ckt-1 was shut down at 06:52(09-08-2022) for C/M.
s) Purbasadipur 132/33 kV T-2 transformer was shut down at 06:04(09-08-2022) for C/M. | [5 empty] | About 45 MW power interruption occurred under
Purbasadipur S/S area from 06:04(09-08-22) to till.
t) Rangpur 132/33 kV T-1 transformer was under shut down from 07:55(09-08-2022) to 10:10 for R/H | [5 empty] | About 30 MW power interruption occurred under
maintenance at Bus isolator. | [5 empty] | Rangpur S/S area from 07:55(09-08-22) to 10:01.
| Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2022-08-08 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4347000
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 300 | 5429336 | Gas shortage
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 82 | 1970681 | Engine problem
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 393 | 9748480 | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 214 | 6318000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 4942400 | Gas shortage & GT-2 S/D.
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 31 | 269760 | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 0 | 0 | Under maint.
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 30 | 736753 | Engine problem
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 418572 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 48 | 386726 | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 32 | 300096 | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 894240
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 128 | 1745760 | Engine problem
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 1284846
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 964333
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 48 | 1183740 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 792500
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 28 | 705100 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 49 | 1141440 | #REF!
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 258 | 3327053 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 300 | 6660161
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 97 | 2229976
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 97 | 2243877
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 2572704
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 2278800
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 32 | 372480 | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 2069280
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 202236
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 55 | 1299240
| Dhaka area Total |  |  |  | 5847 | 3240 | 66835570
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 105 | 2400000 | Machine problem
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 1 | 540190 | Engine problem
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 73440
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 37 | 639360 | Engine problem
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 115 | 2726749 | Low water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | HGPI for 30 days.
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 105 | 2058291
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 34 | 640176 | Fuel shortage
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 816342 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 33 | 1382880 | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 90 | 807360 | Engine problem
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 15 | 356496 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 21 | 403680
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 77 | 624000 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 24121
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 214 | 1658509 | Fuel shortage
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 36 | 757113 | Fuel shortage
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 55 | 1391703 | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 884160
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 108 | 2514109 | Engine problem
| Chattogram area Total |  |  |  | 2382 | 1197 | 20698679
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 190 | 4554000 | #REF!
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 320 | 8003000 | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 320 | 7876000 | Gas shortage
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+136*1 | 284 | 0 | 0 | On test.
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 38 | 890928 | Machine problem
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 52 | 1237440
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 217454
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1169784
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 128 | 3032654 | Engine problem
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 38 | 858496 | Engine problem
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 121 | 3024910 | Machine problem
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 34 | 707520 | Fuel shortage
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 493344
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 9 | 235620
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 158 | 3752640
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 715300
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 43 | 396653 | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 20 | 469940 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 200 | 4430016
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 1147980
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 115 | 1543920
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 35 | 885960 | 33 kV feeder problem.
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 68 | 1770240 | Fuel shortage
| Cumilla Area Total |  |  |  | 3169 | 2117 | 47413799
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 96 | 1993920 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 491724
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 14550
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 180 | 1896000 | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 78 | 1317600 | Engine problem
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 379390
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 273120 | Engine problem
| Mymensingh Area Total |  |  |  | 614 | 388 | 6366304
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1022000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 41 | 927944 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 110 | 2595027 | ST under maint.
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 913800
| Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 49 | 922608
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 0 | 0 | Engine problem
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 62 | 1436736
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 776640
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 221 | 5225520
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50MW PP (EPL) |  | NENP | 27*2 | 50 | 31 | 718400 | Gas shortage
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 295464 | Engine problem
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7547500 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 404 | 9584000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 212400
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 0 | 0 | Under maint.
| Sylhet Area Total |  |  |  | 2477 | 1431 | 32178039
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 914 | 22097454
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 22 | 484800 | Fuel shortage
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 38 | 570240 | Engine problem
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 229 | 5519040
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 63 | 1054720 | Line O/L
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 155 | 3796992 | Gas shortage.
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 8 | 102375 | Fuel shortage
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 79 | 2214720
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 53 | 517920 | Fuel shortage
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 89 | 2076192 | Engine problem
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 496080
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 0 | 0 | 0 | On test.
| Khulna Area Total |  |  |  | 2384 | 1650 | 38930533
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 48 | 967584 | Line O/L
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 30 | 563305 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 87 | 2074016 | ST under S/D
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 570 | 14851900 | Coal shortage
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 222 | 5214518
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 54 | 1236000 | Line O/L
| Barisal Area Total |  |  |  | 1958 | 1011 | 24907323
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 32 | 731632 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 17 | 128941 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contract Expired
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Fuel shortage
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 564800 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 167 | 4340491 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 180 | 4908091
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 149 | 3763018 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 287 | 6918400 | Gas shortage
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 33 | 754460 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 21 | 444960
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | .
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 233334
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 426240
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 80 | 1367056 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 179 | 3773965
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 94 | 1681056 | Engine problem
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 95 | 1615872 | Engine problem
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 34860
| Rajshahi Area Total |  |  |  | 2129 | 1429 | 31687176
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 70 | 371345 | Engine problem
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 250 | 6080800 | Coal shortage
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 97 | 1627171 | Engine problem
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 37274
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 90 | 1318272 | Fuel shortage
| Rangpur Area Total |  |  |  | 720 | 507 | 9434862
| Total |  |  |  | 21680 | 12970 | 278452285
| Eastern Grid Total |  |  |  | 14489 | 8373 | 173492391
| Western Grid Total |  |  |  | 7191 | 4597 | 104959894
| National Grid Total |  |  |  | 21680 | 12970 | 278452285
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2022-08-08
(a) ENTIRE EASTERN GRID : |  | 8524.87 | MW | (b) ENTIRE WESTERN GRID : |  | 3992.26 | MW
i) Dhaka area |  | 4565.37 | MW | i) Khulna area |  | 1534.6 | MW
ii) Chittagong area |  | 1273.5 | MW | ii) Rajshahi area |  | 1339.8 | MW
iii) Comilla area |  | 1164 | MW | iii) Barisal area |  | 379.86 | MW
iv) Mymensingh area |  | 901 | MW | iv) Rangpur area |  | 738 | MW
v) Sylhet area |  | 621 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 12517.13 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
AKS | 18 | 00:00 | Chowmuhani | 171 | 23:00 | Kaptai | 4 | 18:00 | Nawabganj | 36.9 | 19:00 | Siddhirganj | 108 | 22:00
AKSML | 132 | 01:00 | Chuadanga | 102 | 21:00 | Kazla | 88 | 00:00 | Netrakona | 96 | 19:00 | Sirajganj | 88 | 07:00
Aftabnagar | 34 | 00:00 | Coxsbazar | 107 | 18:30 | Keranigonj | 60 | 00:00 | New | 81 | 09:00 | Sonargaon | 80 | 12:00
Agargaon | 98 | 13:00 | Cumilla(N) | 138 | 00:00 | Khagrachori | 24 | 19:00 | Niamatpur | 64 | 06:00 | Sreemongol | 44 | 12:00
Agrabad | 82 | 17:00 | Cumilla(S) | 176 | 14:00 | Khulna | 83 | 20:00 | Noapara | 47 | 01:00 | Srinagar | 46.28 | 21:00
Amnura | 53 | 05:00 | Daudkandi | 154 | 21:00 | Khulshi | 175 | 16:00 | PHP | 11 | 10:00 | Sunamganj | 38 | 22:00
Ashuganj | 45 | 00:00 | Dhaka | 40 | 11:00 | Kishoreganj | 110 | 22:00 | Pabna | 89 | 00:00 | Sylhet | 136 | 00:00
BSRM | 156 | 02:00 | Dhamrai | 100 | 08:00 | Kodda | 264 | 18:30 | Palashbari | 108 | 23:00 | TK | 28.5 | 19:00
Bagerhat | 92 | 22:00 | Dhanmondi | 151 | 14:00 | Kulaura | 52 | 21:00 | Panchagarh | 46 | 08:00 | Tangail | 195 | 22:00
Bakulia | 107 | 19:30 | Dohazari | 104 | 20:00 | Kurigram | 61 | 18:00 | Patuakhali | 133 | 22:00 | Thakurgaon | 66 | 22:00
Banani | 50 | 17:00 | Faridpur | 157 | 21:00 | Kushtia | 130 | 18:00 | Payra | 1.02 | 16:00 | Tongi | 116 | 19:30
Bangabhaban | 22 | 10:00 | Fatullah | 71 | 10:00 | Lalbag | 81 | 16:00 | Purbachal | 20 | 21:00 | Ullon | 40 | 21:00
Barapukuria | 52 | 19:00 | Fenchuganj | 51 | 22:00 | Lalmonirhat | 44 | 22:00 | Purbasadipur | 96 | 05:00 | Uttara | 93 | 21:00
Barguna | 20 | 00:00 | Feni | 96 | 22:00 | Madanganj | 67 | 16:00 | Rahim | 26 | 08:00 | UttaraNew | 18 | 00:00
Barishal | 104 | 00:00 | GPH | 51 | 23:00 | Madaripur | 96 | 22:00 | Rajbari | 60 | 19:30 | Zigatola | 57 | 19:00
Barishal-230 | 88 | 23:00 | Ghorashal | 50 | 19:00 | Madartek | 84 | 00:00 | Rajendrapur | 92 | 05:00
Baroaulia | 71 | 23:00 | Goalpara | 26 | 12:00 | Madunaghat | 54 | 22:00 | Rajshahi | 132 | 22:00
Baroirhat | 57 | 20:00 | Gollamari | 56 | 13:00 | Magura | 54 | 22:00 | Rajshahi-230 | 26 | 02:00
Bashundhara | 159 | 19:00 | Gopalganj | 89.8 | 22:00 | Mahasthangarh | 68 | 19:30 | Ramganj | 88 | 19:00
BashundharaCement | 13 | 04:00 | Gulshan | 104 | 12:00 | Manikganj | 78 | 19:00 | Rampur | 16 | 00:00
Beanibazar | 76 | 22:00 | Halishahar | 90 | 15:00 | Maniknagar | 80 | 12:00 | Rangamati | 14 | 19:00
Benapole | 54 | 19:00 | HaripurSBU | 139 | 20:00 | Matarbari | 40 | 21:00 | Rangpur | 105 | 08:00
Bhaluka | 102 | 22:00 | Hasnabad | 87 | 19:00 | Matuail | 63 | 17:00 | Ruppur | 5 | 09:00
Bhandaria | 51 | 00:00 | Hathazari | 106 | 22:00 | Millgate | 59 | 17:00 | SSM | 3 | 05:00
Bhangura | 30 | 19:00 | Ishurdi | 68 | 00:00 | Mirpur | 128 | 19:00 | Saidpur | 93 | 08:00
Bheramara(GK) | 60 | 22:00 | Jaldhaka | 48 | 00:00 | Mirsorai | N/A | N/A | Satkhira | 95 | 06:00
Bhulta | 231 | 07:00 | Jamalpur | 116 | 20:00 | Mithapukur | 34 | 10:00 | Satmasjid | 101 | 19:00
Bog-Sherpur | 58 | 21:00 | Jashore | 128 | 23:00 | Modern | 0 | 00:00 | Savar | 156 | 09:00
Bogura | 159 | 23:00 | Jhenaidah | 104 | 21:00 | Mogbazar | 133 | 15:00 | Shahjadpur | 85 | 22:00
Borhanuddin | 43 | 01:00 | Joydebpur | 186 | 18:00 | Mongla | 36 | 10:00 | Shahjibazar | 95 | 00:00
Brahmanbaria | 150 | 23:00 | Joypurhat | 60 | 21:00 | Motijheel | 38 | 14:00 | Shahmirpur | 46.5 | 18:30
Cantonment | 146 | 00:00 | Juldah | 31 | 04:00 | Munshiganj | 92 | 19:00 | Shariatpur | 78 | 22:00
Chandpur | 60 | 21:00 | KSRM | 31 | 16:00 | Mymensingh | 214 | 19:00 | Sherpur | 100 | 19:00
Chandraghona | 34 | 19:00 | Kabirpur | 274 | 20:00 | Naogaon | 117 | 23:00 | Shikalbaha | 28 | 19:00
Chapai | 61 | 21:00 | Kachua | 64 | 21:00 | Narail | 47 | 19:30 | Shikalbaha-230 | N/A | N/A
Charsaidpur | 46 | 23:00 | Kallyanpur | 96 | 22:00 | Narinda | 72 | 13:00 | Shitalakhya | 114 | 12:00
Chauddagram | 59 | 20:00 | Kalurghat | 32 | 09:00 | Narshingdi | 157 | 00:00 | Sholosohor | N/A | N/A
Chhatak | 36 | 21:00 | Kamrangirchar | 59 | 16:00 | Natore | 123 | 21:00 | Shyampur | 144 | 01:00
Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
(1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2022-08-08 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Bhulta | 386 | 19:00 | 367 | 11:00 | Kaliakoir | 390 | 19:00 | 379 | 00:00
| Bibiana | 408 | 19:00 | 395 | 03:00 | Payra | 418 | 03:00 | 410 | 23:00
| BIPTC | 402 | 06:00 | 395 | 23:00 | Rahanpur_I | N/A | N/A | N/A | N/A
| Gopalganj_I | 412 | 10:00 | 398 | 23:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 222 | 19:30 | 211 | 17:00 | Hasnabad | 220 | 19:00 | 214 | 09:00
| AKSML | 233 | 19:00 | 213 | 09:00 | Hathazari | 235 | 19:00 | 218 | 08:00
| Aminbazar | 224 | 19:00 | 214 | 11:00 | Ishurdi | 235 | 19:30 | 229 | 07:00
| Ashuganj | 238 | 20:00 | 227 | 11:00 | Jhenaidah | 231 | 15:00 | 222 | 23:00
| Baghabari | 234 | 18:30 | 229 | 09:00 | Kaliakoir | 233 | 19:30 | 215 | 09:00
| Barapukuria | 223 | 18:00 | 212 | 06:00 | Keranigonj | 221 | 19:30 | 212 | 11:00
| Barishal | 246 | 17:00 | 239 | 22:00 | Khulna(S) | 242 | 15:00 | 230 | 07:00
| Bheramara | 233 | 18:30 | 226 | 07:00 | Maniknagar | 224 | 19:00 | 215 | 11:00
| Bhulta | 227 | 19:00 | 216 | 11:00 | Meghnaghat | 226 | 19:30 | 216 | 12:00
| Bibiana | 242 | 19:30 | 232 | 09:00 | Mirsorai | N/A | N/A | N/A | N/A
| BIPTC | 234 | 03:00 | 227 | 07:00 | Rajshahi | 234 | 18:30 | 225 | 07:00
| Bogura | 229 | 19:00 | 219 | 07:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 250 | 18:00 | 240 | 23:00 | Rampura | 225 | 19:30 | 215 | 11:00
| BSRM | 232 | 19:00 | 219 | 01:00 | Shikalbaha | 232 | 19:30 | 219 | 09:00
| Cumilla(N) | 229 | 19:00 | 218 | 09:00 | Shyampur | 222 | 19:30 | 214 | 09:00
| Fenchuganj | 241 | 20:00 | 236 | 07:00 | Siddhirganj | 225 | 19:00 | 216 | 09:00
| Ghorashal | N/A | N/A | N/A | N/A | Sirajgonj | 232 | 18:30 | 228 | 07:00
| GPH | 234 | 19:00 | 218 | 09:00 | Tongi | 228 | 19:30 | 215 | 11:00
| Haripur | 223 | 22:00 | 212 | 04:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 136 | 19:30 | 130 | 12:00 | Lalbag | 138 | 19:30 | 130 | 04:00
| Agargaon | 136 | 19:30 | 130 | 11:00 | Lalmonirhat | 130 | 18:30 | 119 | 06:00
| Agrabad | 138 | 19:00 | 127 | 08:00 | Madanganj | 131 | 20:00 | 126 | 11:00
| AKS | 137 | 18:30 | 126 | 08:00 | Madaripur | 139 | 09:00 | 132 | 23:00
| Aminbazar | 135 | 19:00 | 128 | 00:00 | Madartek | 137 | 19:30 | 131 | 01:00
| Amnura | 132 | 18:30 | 125 | 07:00 | Madunaghat | 138 | 20:00 | 129 | 08:00
| Ashuganj | 138 | 10:00 | 134 | 07:00 | Magura | 140 | 15:00 | 132 | 22:00
| Bagerhat | 137 | 08:00 | 128 | 23:00 | Mahasthangarh | 137 | 18:30 | 127 | 06:00
| Bakulia | 139 | 19:00 | 127 | 09:00 | Manikganj | 134 | 12:00 | 128 | 01:00
| Banani | 133 | 19:30 | 125 | 09:00 | Maniknagar | 132 | 07:00 | 127 | 11:00
| Bangabhaban | 132 | 19:30 | 127 | 10:00 | Matarbari | 131 | 16:00 | 119 | 07:00
| Barapukuria | 137 | 23:00 | 127 | 06:00 | Matuail | 131 | 20:00 | 126 | 12:00
| Barguna | 139 | 10:00 | 128 | 13:00 | Millgate | 134 | 19:30 | 126 | 08:00
| Barishal | 142 | 20:00 | 128 | 12:00 | Mirpur | 133 | 22:00 | 125 | 11:00
| Barishal-230 | 140 | 09:00 | 134 | 21:00 | Mithapukur | 135 | 18:30 | 122 | 05:00
| Baroaulia | 140 | 19:00 | 129 | 09:00 | Modern | 139 | 18:30 | 129 | 12:00
| Baroirhat | 135 | 19:00 | 126 | 04:00 | Mogbazar | 137 | 20:00 | 130 | 12:00
| Bashundhara | 133 | 19:30 | 125 | 09:00 | Mongla | 136 | 15:00 | 127 | 23:00
| BashundharaCement | 131 | 20:00 | 126 | 11:00 | Motijheel | 132 | 19:30 | 127 | 10:00
| Beanibazar | 133 | 08:00 | 126 | 22:00 | Munshiganj | 132 | 19:30 | 126 | 11:00
| Benapole | 137 | 15:00 | 129 | 23:00 | Mymensingh | 128 | 18:00 | 118 | 01:00
| Bhaluka | 129 | 18:00 | 118 | 01:00 | Naogaon | 135 | 18:30 | 124 | 06:00
| Bhandaria | 139 | 10:00 | 128 | 00:00 | Narail | 137 | 10:00 | 130 | 23:00
| Bhangura | 138 | 18:30 | 134 | 09:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bheramara | 136 | 00:00 | 134 | 06:00 | Narshingdi | 135 | 02:00 | 123 | 15:00
| Bheramara(GK) | 138 | 00:00 | 134 | 20:00 | Natore | 136 | 21:00 | 128 | 07:00
| Bhulta | 124 | 06:00 | 117 | 16:00 | Nawabganj | 138 | 20:00 | 131 | 18:00
| Bog-Sherpur | 137 | 18:00 | 129 | 07:00 | Netrakona | 125 | 19:00 | 115 | 05:00
| Bogura | 138 | 19:00 | 129 | 06:00 | New | 132 | 19:00 | 125 | 11:00
| Bogura-230 | 138 | 18:00 | 127 | 10:00 | Niamatpur | 132 | 18:30 | 119 | 05:00
| Brahmanbaria | 133 | 20:00 | 130 | 01:00 | Noapara | 139 | 15:00 | 132 | 23:00
| Cantonment | 135 | 19:30 | 129 | 11:00 | Pabna | 135 | 00:00 | 131 | 07:00
| Chandpur | 135 | 18:30 | 128 | 12:00 | Palashbari | 131 | 17:00 | 120 | 06:00
| Chandraghona | 139 | 19:00 | 130 | 05:00 | Panchagarh | 133 | 17:00 | 115 | 07:00
| Chapai | 132 | 18:30 | 126 | 06:00 | Patuakhali | 138 | 20:00 | 130 | 19:00
| Charsaidpur | 132 | 20:00 | 126 | 11:00 | Payra | 138 | 00:00 | 134 | 13:00
| Chauddagram | 135 | 19:00 | 125 | 08:00 | PHP | 135 | 18:00 | 125 | 07:00
| Chhatak | 132 | 00:00 | 130 | 12:00 | Postogola | 140 | 19:30 | 133 | 12:00
| Chowmuhani | 134 | 18:30 | 123 | 06:00 | Purbachal | 133 | 20:00 | 125 | 09:00
| Chuadanga | 135 | 03:00 | 125 | 23:00 | Purbasadipur | 134 | 17:00 | 117 | 06:00
| Coxsbazar | 130 | 14:00 | 116 | 08:00 | Rahim | 132 | 19:00 | 127 | 11:00
| Cumilla(N) | 135 | 19:00 | 129 | 09:00 | Rajbari | 135 | 03:00 | 130 | 22:00
| Cumilla(S) | 135 | 19:00 | 124 | 22:00 | Rajendrapur | 133 | 18:00 | 127 | 07:00
| Daudkandi | 133 | 00:00 | 127 | 18:00 | Rajshahi | 132 | 19:30 | 128 | 05:00
| Dhaka | 138 | 20:00 | 130 | 09:00 | Rajshahi-230 | 134 | 18:30 | 127 | 07:00
| Dhamrai | 130 | 19:30 | 125 | 01:00 | Ramganj | 133 | 21:00 | 123 | 05:00
| Dhanmondi | 130.6 | 20:00 | 125 | 11:00 | Rampur | 136 | 19:30 | 129 | 07:00
| Dohazari | 134 | 19:30 | 125 | 04:00 | Rampura | 136 | 19:30 | 130 | 11:00
| Faridpur | 135 | 03:00 | 129 | 23:00 | Rangamati | 137 | 19:00 | 129 | 09:00
| Fatullah | 135 | 19:30 | 129 | 18:30 | Rangpur | 133 | 18:30 | 122 | 06:00
| Fenchuganj | 137 | 00:00 | 134 | 15:00 | Ruppur | 137 | 10:00 | 134 | 08:00
| Feni | 136 | 19:00 | 127 | 02:00 | Saidpur | 132 | 00:00 | 119 | 07:00
| Ghorashal | 137 | 19:00 | 135 | 01:00 | Satkhira | 135 | 15:00 | 126 | 23:00
| Goalpara | 140 | 15:00 | 132 | 23:00 | Satmasjid | 136 | 19:30 | 130 | 11:00
| Gollamari | 138 | 08:00 | 131 | 11:00 | Savar | 133 | 22:00 | 125 | 11:00
| Gopalganj | 140 | 01:00 | 135 | 20:00 | Shahjadpur | 142 | 03:00 | 136 | 07:00
| Gopalganj_I | 141 | 10:00 | 134 | 23:00 | Shahjibazar | 135 | 19:30 | 133 | 03:00
| Gulshan | 136 | 19:30 | 129 | 11:00 | Shahmirpur | 139 | 19:00 | 127 | 08:00
| Halishahar | 138 | 19:00 | 128 | 08:00 | Shariatpur | 137 | 03:00 | 131 | 21:00
| Haripur | 132 | 19:00 | 127 | 11:00 | Sherpur | 133 | 18:00 | 116 | 01:00
| HaripurSBU | 132 | 20:00 | 127 | 12:00 | Shikalbaha | 140 | 19:00 | 128 | 08:00
| Hasnabad | 140 | 19:30 | 133 | 11:00 | Shikalbaha-230 | 136 | 19:30 | 128 | 09:00
| Hathazari | 138 | 19:00 | 128 | 08:00 | Shitalakhya | 140 | 22:00 | 131 | 16:00
| Ishurdi | 137 | 19:30 | 133 | 09:00 | Sholosohor | N/A | N/A | N/A | N/A
| Jaldhaka | 132 | 18:30 | 117 | 07:00 | Shyampur | 133 | 19:00 | 126 | 17:00
| Jamalpur | 137 | 18:00 | 118 | 02:00 | Shyampur-230 | 134 | 19:30 | 129 | 10:00
| Jashore | 136 | 15:00 | 130 | 23:00 | Siddhirganj | 131 | 19:30 | 127 | 09:00
| Jhenaidah | 140 | 10:00 | 134 | 22:00 | Sirajganj | 136 | 18:30 | 130 | 07:00
| Jhenaidah-230 | 141 | 15:00 | 134 | 23:00 | Sonargaon | 131 | 02:00 | 125 | 14:00
| Joydebpur | 141 | 19:30 | 136 | 15:00 | Sreemongol | 136 | 00:00 | 134 | 09:00
| Joypurhat | 135 | 18:30 | 124 | 05:00 | Srinagar | 138 | 19:30 | 131 | 09:00
| Juldah | 140 | 19:00 | 128 | 07:00 | SSM | 141 | 19:00 | 131 | 11:00
| Kabirpur | 135 | 21:00 | 124 | 08:00 | Sunamganj | 132 | 03:00 | 130 | 00:00
| Kachua | 134 | 18:30 | 127 | 05:00 | Sylhet | 133 | 00:00 | 130 | 20:00
| Kaliakoir | 137 | 19:00 | 127 | 08:00 | Tangail | 134 | 12:00 | 129 | 01:00
| Kallyanpur | 134 | 19:30 | 126 | 12:00 | Thakurgaon | 134 | 18:00 | 114 | 06:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2022-08-08
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 996 | 7539 | 4625 | 12164 |  |  |  | QF-LDC-11
0:30 | 818 | 7313 | 4516.5 | 11829.5 | Date: | 2022-08-08
1:00 | 640 | 7087 | 4408 | 11495
1:30 | 621 | 7048.5 | 4379.5 | 11428
2:00 | 602 | 7010 | 4351 | 11361
2:30 | 584 | 6980.5 | 4368 | 11348.5 | [5 empty] | Gen. at Eve. Peak | 12970 | 12970 MW (21:00 )
3:00 | 566 | 6951 | 4385 | 11336 | [6 empty] | 21:00
3:30 | 547 | 6949.5 | 4353 | 11302.5 | [5 empty] | Gen. at Day Peak | 10946 | 10946 MW (09:00 )
4:00 | 528 | 6948 | 4321 | 11269 | [6 empty] | 9:00
4:30 | 491 | 6947 | 4324 | 11271 | [5 empty] | Highest Generation | 13047
5:00 | 454 | 6946 | 4327 | 11273 | [6 empty] | 22:00
5:30 | 454 | 6940 | 4329 | 11269
6:00 | 454 | 6934 | 4331 | 11265
6:30 | 486 | 6924.5 | 4319 | 11243.5
7:00 | 518 | 6915 | 4307 | 11222
7:30 | 575 | 6875.5 | 4318.5 | 11194
8:00 | 632 | 6836 | 4330 | 11166
8:30 | 771 | 6730 | 4326 | 11056
9:00 | 910 | 6624 | 4322 | 10946
9:30 | 996 | 6662.5 | 4063 | 10725.5
10:00 | 1082 | 6701 | 3804 | 10505
10:30 | 1030 | 6669 | 3870 | 10539
11:00 | 978 | 6637 | 3936 | 10573
11:30 | 961 | 6644.5 | 3921 | 10565.5
12:00 | 944 | 6652 | 3906 | 10558
12:30 | 924 | 6720 | 3951.5 | 10671.5
13:00 | 904 | 6788 | 3997 | 10785
13:30 | 883 | 6855.5 | 4001 | 10856.5
14:00 | 862 | 6923 | 4005 | 10928
14:30 | 963 | 6924 | 3988 | 10912
15:00 | 1064 | 6925 | 3971 | 10896
15:30 | 1044 | 6974.5 | 3997 | 10971.5
16:00 | 1024 | 7024 | 4023 | 11047
16:30 | 1012 | 7011.5 | 4044.5 | 11056
17:00 | 1000 | 6999 | 4066 | 11065
17:30 | 978 | 7033.5 | 4038 | 11071.5
18:00 | 956 | 7068 | 4010 | 11078
18:30 | 875 | 7580 | 4120 | 11700
19:00 | 794 | 8092 | 4230 | 12322
19:30 | 754 | 8137 | 4522 | 12659
20:00 | 772 | 8169 | 4557 | 12726 |  |  |  | Executive Engineer
20:30 | 754 | 8271 | 4577 | 12848 |  |  |  | Network Operation Division
21:00 | 736 | 8373 | 4597 | 12970
21:30 | 799 | 8383 | 4625.5 | 13008.5
22:00 | 862 | 8393 | 4654 | 13047 |  |  |  |  | Page 6 of 7
22:30 | 902 | 8298 | 4657 | 12955
23:00 | 942 | 8203 | 4660 | 12863
23:30 | 969 | 7871 | 4642.5 | 12513.5
24:00 | 996 | 7539 | 4625 | 12164
12970 MW (21:00 )
10946 MW (09:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2022-08-08 |  | Energy |  | 278452285
[13 empty] | 2022-08-08 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 3680 | 914 | 1896 | 941 | 2699 | 911 | 116 | 440 | 651 | 128 | 0 | 1415.5392
0:30 | 3635.5 | 914 | 1902 | 946 | 2389 | 910.5 | 116 | 435 | 645.5 | 145 | 0 | 1608.6092 | Date: | 2022-08-08
1:00 | 3591 | 914 | 1908 | 951 | 2079 | 910 | 116 | 430 | 640 | 162 | 0 | 1801.6791
1:30 | 3591 | 914 | 1908.5 | 950.5 | 2020 | 905 | 117 | 432 | 635 | 162 | 0 | 1702.149 | [8 empty] | Total Energy | 278.4523 | Total Energy Gen 180.187 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 180.187 MKWHr
2:00 | 3591 | 914 | 1909 | 950 | 1961 | 900 | 118 | 434 | 630 | 162 | 0 | 1602.6189 | [8 empty] | Energy not Served | 27.1239
2:30 | 3601 | 914 | 1873 | 951 | 1964.5 | 900 | 118 | 438 | 635.5 | 165 | 0 | 1475.9024 | [8 empty] | Energy Requirement | 305.5762
3:00 | 3611 | 914 | 1837 | 952 | 1968 | 900 | 118 | 442 | 641 | 168 | 0 | 1349.1858
3:30 | 3612.5 | 914 | 1852 | 954.5 | 1967.5 | 885 | 118 | 440.5 | 604.5 | 168 | 0 | 1287.9011 | [6 empty] | Shortage
4:00 | 3614 | 914 | 1867 | 957 | 1967 | 870 | 118 | 439 | 568 | 168 | 0 | 1226.6163
4:30 | 3617 | 914 | 1883 | 955 | 1958 | 870 | 118 | 437.5 | 565.5 | 164 | 0 | 1086.5369
5:00 | 3620 | 914 | 1899 | 953 | 1949 | 870 | 118 | 436 | 563 | 160 | 0 | 946.4575
5:30 | 3621 | 914 | 1900.5 | 954.5 | 1950.5 | 865 | 118 | 438.5 | 561.5 | 156 | 1 | 811.9076
6:00 | 3622 | 914 | 1902 | 956 | 1952 | 860 | 118 | 441 | 560 | 152 | 2 | 677.3576
6:30 | 3622 | 914 | 1901 | 955.5 | 1942 | 855 | 118 | 440.5 | 555 | 144 | 10 | 605.014 |  |  |  |  | Coal
7:00 | 3622 | 914 | 1900 | 955 | 1932 | 850 | 118 | 440 | 550 | 136 | 18 | 532.6704
7:30 | 3617 | 914 | 1866.5 | 909.5 | 1947 | 850 | 118 | 446.5 | 558 | 139 | 43 | 650.6319 |  |  |  | Oil |  |  |  | ,
8:00 | 3612 | 914 | 1833 | 864 | 1962 | 850 | 118 | 453 | 566 | 142 | 68 | 768.5935
8:30 | 3494 | 914.5 | 1823.5 | 860.5 | 1948 | 850 | 117.5 | 452.5 | 565.5 | 148 | 97.5 | 916.0455
9:00 | 3376 | 915 | 1814 | 857 | 1934 | 850 | 117 | 452 | 565 | 154 | 127 | 1063.4976
9:30 | 3377 | 914.5 | 1807 | 904.5 | 1837 | 700 | 116.5 | 449.5 | 550.5 | 145 | 138 | 1312.7836
10:00 | 3378 | 914 | 1800 | 952 | 1740 | 550 | 116 | 447 | 536 | 136 | 149 | 1562.0696
10:30 | 3377 | 914 | 1768 | 953 | 1755 | 585.5 | 115.5 | 446 | 530 | 143 | 162 | 1622.8936
11:00 | 3376 | 914 | 1736 | 954 | 1770 | 621 | 115 | 445 | 524 | 150 | 175 | 1683.7175
11:30 | 3398.5 | 914 | 1728.5 | 954.5 | 1749.5 | 675.5 | 115 | 427 | 499 | 155 | 142.5 | 1782.7868
12:00 | 3421 | 914 | 1721 | 955 | 1729 | 730 | 115 | 409 | 474 | 160 | 110 | 1881.8561
12:30 | 3484.5 | 914 | 1711 | 954.5 | 1753 | 750 | 115 | 409.5 | 469 | 164 | 127 | 1731.1786
13:00 | 3548 | 914 | 1701 | 954 | 1777 | 770 | 115 | 410 | 464 | 168 | 144 | 1580.5011
13:30 | 3548 | 914 | 1701 | 954 | 1777 | 770 | 115 | 410 | 464 | 168 | 144 | 1580.5011
14:00 | 3548 | 914 | 1701 | 954 | 1777 | 770 | 115 | 410 | 464 | 168 | 144 | 1580.5011
14:30 | 3557 | 914.5 | 1716.5 | 955 | 1834.5 | 760 | 115.5 | 410.5 | 477.5 | 163 | 116.5 | 1483.275
15:00 | 3566 | 915 | 1732 | 956 | 1892 | 750 | 116 | 411 | 491 | 158 | 89 | 1386.0488
15:30 | 3581 | 915 | 1710.5 | 927.5 | 1942 | 760 | 116 | 410 | 532 | 160 | 97.5 | 1270.3911
16:00 | 3596 | 915 | 1689 | 899 | 1992 | 770 | 116 | 409 | 573 | 162 | 106 | 1154.7335
16:30 | 3593 | 914.5 | 1677.5 | 788.5 | 2135.5 | 775 | 116 | 408.5 | 589.5 | 161 | 75.5 | 1054.2818
17:00 | 3593 | 914 | 1666 | 678 | 2279 | 780 | 116 | 408 | 606 | 160 | 45 | 953.8301
17:30 | 3596 | 914 | 1670.5 | 436 | 2554.5 | 780.5 | 116.5 | 383.5 | 588 | 158 | 29 | 763.5249
18:00 | 3599 | 914 | 1675 | 194 | 2830 | 781 | 117 | 359 | 570 | 156 | 13 | 573.2196
18:30 | 3618.5 | 914.5 | 1729.5 | 496 | 3014 | 799.5 | 117 | 364.5 | 616.5 | 160 | 6.5 | 506.8663
19:00 | 3638 | 915 | 1784 | 798 | 3198 | 818 | 117 | 370 | 663 | 164 | 0 | 440.5129
19:30 | 3653 | 914 | 1787 | 796 | 3387 | 897 | 117 | 410 | 720 | 158 | 0 | 590.7296
20:00 | 3660 | 915 | 1798 | 808 | 3408 | 906 | 118 | 410 | 723 | 160 | 0 | 897.6141
20:30 | 3654.5 | 914.5 | 1827.5 | 880 | 3444 | 898 | 116.5 | 409.5 | 724.5 | 159 | 0 | 877.3394
21:00 | 3649 | 914 | 1857 | 952 | 3480 | 890 | 115 | 409 | 726 | 158 | 0 | 857.0648
21:30 | 3657 | 914.5 | 1866 | 963 | 3497.5 | 890.5 | 115.5 | 418.5 | 718.5 | 157 | 0 | 821.5841
22:00 | 3665 | 915 | 1875 | 974 | 3515 | 891 | 116 | 428 | 711 | 156 | 0 | 786.1035
22:30 | 3668 | 914.5 | 1877 | 973 | 3399 | 901.5 | 116 | 435 | 723.5 | 154 | 0 | 824.8096
23:00 | 3671 | 914 | 1879 | 972 | 3283 | 912 | 116 | 442 | 736 | 152 | 0 | 863.5158
23:30 | 3675.5 | 914 | 1887.5 | 956.5 | 2991 | 911.5 | 116 | 441 | 693.5 | 140 | 0 | 1139.5275 | Max Temp. in Dhaka |  | 24.7° C | 34.5° C
24:00 | 3680 | 914 | 1896 | 941 | 2699 | 911 | 116 | 440 | 651 | 128 | 0 | 1415.5392
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 180.187 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 180.187 MKWHr
Note on W13: Author:

## Generation
g | 2022-08-08
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 81 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 82 | 81 | 80 | 80 | 80 | 81 | 81 | 81 | 81 | 82 |  | 82 | 82 | 83 | 80 | 81 | 81 | 81 | 1886749
2 | Karnaphuli Hydro PP Unit-4 & 5 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 840000
3 | Chattogram TPP-1 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 95 | 95 | 100 | 100 | 100 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2400000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 0 |  | 1 | 25 | 25 | 25 | 540190
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 0 |  | 5 | 10 | 3 | 3 | 4 | 12 | 12 | 13 | 3 | 0 | [8 empty] | 73440
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 51 | 51 | 51 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 30 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 816342
12 | Hathazari 100 MW peaking PP | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 |  | 34 | 34 | 34 | 34 | 27 | 34 | 34 | 640176
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 87 | 87 | 87 | 87 | 87 | 80 | 84 | 70 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 82 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 91 | 2058291
| Daudkandi 200 MW PP (B.Trac) | 197 | 197 | 197 | 197 | 197 | 197 | 197 | 195 | 196 | 196 | 198 | 198 | 198 | 198 | 197 | 195 | 100 | 20 |  | 188 | 150 | 150 | 200 | 200 | 200 | 200 | 4430016
14 | Titas 50 MW Peaking PP | 39 | 39 | 39 | 39 | 39 | 39 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 32 | 38 | 38 | 38 | 37 |  | 38 | 38 | 38 | 38 | 36 | 40 | 40 | 858496
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 112 | 97 | 97 | 97 | 97 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 110 | 205 |  | 258 | 258 | 260 | 258 | 258 | 273 | 132 | 3327053
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 217454
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4347000
24
25 | Ghorasal 365 MW CCPP Unit-7 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 0 | 30 | 70 | 157 | 300 | 300 | 300 | 300 | 300 | 300 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 5429336
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 42 | 42 | 42 | 40 | 40 | 40 | 36 | 39 | 39 | 39 | 39 | 36 | 36 | 34 | 31 | 31 | 34 | 37 |  | 36 | 38 | 38 | 38 | 38 | 38 | 38 | 890928
33 | Ashuganj 225 MW CCPP | 195 | 193 | 194 | 201 | 204 | 207 | 206 | 206 | 198 | 199 | 194 | 192 | 169 | 146 | 170 | 174 | 158 | 169 |  | 177 | 177 | 184 | 190 | 195 | 195 | 195 | 4554000
34 | Ashuganj 450 MW CCPP(South) | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 |  | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 7876000
| Ashuganj 450 MW CCPP(North) | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 |  | 320 | 320 | 320 | 320 | 320 | 320 | 300 | 8003000
Ashuganj 420 MW CCPP(East)
35 | Ashuganj 55 MW PP (Precision) | 52 | 52 | 52 | 53 | 52 | 53 | 53 | 49 | 49 | 47 | 51 | 50 | 52 | 52 | 51 | 50 | 50 | 51 |  | 52 | 52 | 52 | 52 | 53 | 53 | 54 | 1237440
36 | Chandpur 150 MW CCPP | 127 | 127 | 128 | 128 | 127 | 127 | 135 | 134 | 135 | 135 | 128 | 128 | 128 | 128 | 121 | 123 | 121 | 121 |  | 120 | 121 | 120 | 121 | 120 | 120 | 121 | 3024910
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 399 | 402 | 410 | 407 | 405 | 407 | 406 | 410 | 406 | 403 | 400 | 393 | 396 | 400 | 396 | 400 | 399 | 395 |  | 393 | 392 | 392 | 393 | 399 | 406 | 405 | 9748480
40 | Meghnaghat 450 MW CCPP(MPL) | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 |  | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 4942400
41 | Haripur 360MW CCPP(HPL) | 281 | 291 | 293 | 302 | 318 | 317 | 321 | 320 | 320 | 318 | 255 | 240 | 224 | 250 | 247 | 236 | 225 | 222 |  | 217 | 214 | 214 | 214 | 220 | 232 | 241 | 6318000
42 | RPCL 210MW CCPP | 100 | 100 | 102 | 101 | 102 | 102 | 102 | 95 | 70 | 71 | 69 | 69 | 69 | 66 | 66 | 66 | 67 | 67 |  | 95 | 96 | 95 | 96 | 98 | 101 | 102 | 1993920
43 | Sutiakhali 50 MW Solar PP |  |  |  |  | 0 | 1 | 1 | 10 | 21 | 53 | 35 | 51 | 56 | 48 | 46 | 27 | 14 | 4 | [8 empty] | 379390
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 44 | 44 | 43 | 42 | 43 | 43 | 44 | 43 | 43 | 43 |  | 44 | 43 | 44 | 43 | 43 | 43 | 43 | 1022000
45 | Fenchugonj CCPP Phase-2 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 |  | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 927944
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 60 | 60 | 60 | 55 | 55 | 55 | 60 | 59 | 60 | 55 | 60 | 59 | 60 | 61 | 62 | 62 | 63 | 61 |  | 61 | 63 | 63 | 62 | 63 | 62 | 63 | 1436736
48 | Shahjibazar 86MW PP (Shahjibazar) | 81 | 40 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 50 | 81 | 81 | 81 | 81 | 81 | 81 | 776640
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 221 | 220 | 220 | 220 | 220 | 220 | 221 | 220 | 220 | 215 | 221 | 201 | 200 | 213 | 221 | 220 | 220 | 220 |  | 221 | 221 | 220 | 221 | 220 | 221 | 220 | 5225520
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL) | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 30 | 30 | 30 | 31 | 31 | 31 | 30 | 30 | 30 |  | 32 | 31 | 30 | 31 | 29 | 31 | 31 | 718400
53 | Sylhet 10MW PP (Desh) | 0 | 9 | 7 | 7 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 10 | 9 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 212400
54 | Hobiganj 11MW PP Cofidence-E
55 | Fenchugonj 51 MW PP (Barakatullah) | 50 | 50 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 35 |  | 36 | 53 | 53 | 53 | 53 | 53 | 53 | 913800
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 295464
57 | Bibiana-II 341 MW CCPP (Summit) | 310 | 325 | 300 | 315 | 330 | 315 | 325 | 300 | 300 | 310 | 320 | 320 | 320 | 310 | 320 | 290 | 290 | 270 |  | 310 | 265 | 260 | 310 | 300 | 300 | 310 | 7547500
Bibiyana South 400 MW
58 | Nababganj 55 MW PP (Southern power ) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 55 |  | 55 | 55 | 55 | 55 | 55 | 35 | 0 | 964333
59 | Tangail Palli Power Gen 22 MW | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 6 | 7 | 8 | 11 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 273120
60 | Barabkunda 22 MW PP (Regent) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 356496
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 19 | 19 | 19 | 19 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 |  |  | 0 | 22 | 418572
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 491724
63 | Impoprt (Tripura) | 162 | 162 | 168 | 168 | 160 | 152 | 136 | 142 | 154 | 136 | 150 | 160 | 168 | 176 | 158 | 162 | 160 | 156 |  | 164 | 158 | 160 | 158 | 156 | 152 | 128 | 3752640
64 | Malancha, Ctg. EPZ (United) | 38 | 38 | 38 | 38 | 32 | 38 | 28 | 4 | 3 | 2 | 2 | 3 | 2 | 3 | 2 | 5 | 3 | 19 |  | 19 | 3 | 20 | 21 | 28 | 30 | 30 | 403680
65 | Feni 22MW PP (Doreen) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 19 | 19 | 19 | 19 | 21 | 21 | 21 | 21 |  | 21 | 21 | 22 | 22 | 22 | 22 | 22 | 493344
66 | Feni 11 MW PP (Doreen) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 9 | 9 |  | 9 | 9 | 9 | 9 | 10 | 10 | 10 | 235620
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 28 | 21 | 20 | 18 | 16 | 25 | 25 | 33 | 30 |  | 30 | 31 | 33 | 33 | 33 | 33 | 33 | 715300
68 | Cumilla 25 MW PP (Summit) | 20 | 20 | 20 | 20 | 20 | 15 | 15 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 469940
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 27 | 24 | 27 | 27 | 27 | 27 | 27 | 20 | 27 | 28 | 28 | 28 | 22 | 28 | 28 | 26 | 24 | 23 |  | 23 | 23 | 23 | 23 | 24 | 24 | 24 | 583740
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 792500
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 32 | 30 | 30 | 30 | 30 | 16 | 28 | 28 | 28 | 28 | 28 |  | 28 | 28 | 28 | 28 | 28 | 30 | 30 | 705100
73 | Ghorashal 108MW PP (Regent) | 87 | 87 | 88 | 90 | 90 | 90 | 89 | 84 | 83 | 86 | 84 | 81 | 86 | 79 | 82 | 82 | 77 | 77 |  | 79 | 82 | 82 | 82 | 83 | 83 | 83 | 1970681
| Feni Lanka Power | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 34 | 84 | 114 |  | 114 | 114 | 114 | 114 | 114 | 114 | 60 | 1147980
| Chowmuhani 113 MW | 42 | 38 | 38 | 38 | 38 | 38 | 38 | 39 | 38 | 39 | 39 | 38 | 39 | 39 | 43 | 66 | 101 | 101 |  | 109 | 115 | 114 | 115 | 114 | 114 | 113 | 1543920
| Manikgonj 162MW PP(MPGL) | 51 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 42 | 102 | 102 | 102 | 120 | 162 |  | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 2069280
77 | Siddhirganj 100 PP(Dutch Bangla) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 22 | 50 | 48 | 48 | 48 | 48 | 23 | 386726
78 | Gazipur 52 MW PP | 49 | 49 | 49 | 49 | 49 | 50 | 42 | 50 | 50 | 47 | 42 | 47 | 47 | 41 | 50 | 50 | 41 | 49 |  | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1141440
79 | Kodda 150MW PP | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 64 | 50 | 50 | 50 | 50 | 50 | 100 | 128 | 128 |  | 128 | 128 | 128 | 128 | 130 | 130 | 48 | 1745760
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 10 | 8 | 8 | 8 | 8 | 8 |  | 14 | 43 | 43 | 43 | 43 | 43 | 43 | 396653
| Gazipur 100 MW PP | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 92 | 105 |  | 88 | 88 | 88 | 105 | 88 | 88 | 88 | 2278800
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 1 | 2 | 4 | 5 | 3 | 1 | 4 | 0 | 0 | [10 empty] | 24121
| Jodiac Power | 23 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 17 | 17 | 17 | 17 | 17 | 17 | 23 | 36 | 36 |  | 36 | 36 | 29 | 36 | 36 | 36 | 36 | 757113
| Karnaphuli Power Ltd. | 56 | 56 | 56 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 65 | 74 | 74 | 60 |  | 55 | 55 | 55 | 55 | 55 | 55 | 56 | 1391703
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL) | 7 | 7 | 8 | 7 | 7 | 8 | 7 | 8 | 7 | 7 | 7 | 8 | 9 | 9 | 7 | 7 | 8 | 7 |  | 8 | 33 | 30 | 31 | 24 | 17 | 9 | 269760
| Meghnaghat 104 MW PP (OPCL) | 0 | [5 empty] | 5 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 30 | 33 | 32 | 33 | 33 | 29 | 372480
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 65 | 65 | 65 | 65 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 1382880
92 | Fenchuganj 44MW (Energyprima) | 48 | 45 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 40 | 48 | 49 | 49 | 49 | 49 | 49 | 922608
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 43 | 43 | 43 | 43 | 51 | 51 | 43 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1169784
94 | Gagnagar 102 MW PP (Digital Power) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 32 | 32 | 32 | 32 | 32 | 32 | 8 | 300096
95 | Patenga 50MW PP (Baraka) | 25 | 20 | 23 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 29 | 31 | 31 |  | 31 |  | 7 | 37 | 43 | 29 | 26 | 639360
96 | Chattogram 108 MW PP (ECPV) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 16 | 11 | 12 | 12 | 12 | 18 | 16 | 14 | 14 | 14 | 33 |  | 72 | 77 | 77 | 77 | 77 | 43 | 12 | 624000
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 736753
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1284846
101 | Kushiara 163 MW CCPP (KP) | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2595027
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 | 2 | 1 | 2 | 2 | 2 | 2 | 2 | 1 | 0 | 0 | [8 empty] | 14550
103 | Kamalaghat 54 MW PP(Banco Energy) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 17 | 17 | 17 | 17 | 17 | 35 | 35 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 894240
104 | Keranigonj 300 MW PP (APR) | 298 | 296 | 298 | 301 | 298 | 301 | 301 | 250 | 246 | 300 | 300 | 300 | 300 | 303 | 305 | 302 | 200 | 34 |  | 282 | 244 | 250 | 300 | 302 | 301 | 270 | 6660161
105 | Bramhangoan 100 MW PP (Aggreko) | 95 | 97 | 98 | 98 | 99 | 99 | 98 | 97 | 98 | 98 | 97 | 96 | 95 | 97 | 94 | 95 | 95 | 25 |  | 95 | 94 | 95 | 97 | 97 | 97 | 97 | 2229976
106 | Mymensingh 200 MW PP (United) | 47 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 46 | 46 | 46 | 46 | 46 | 46 | 47 | 47 | 174 |  | 179 | 179 | 180 | 180 | 180 | 180 | 48 | 1896000
112 | Aurahati 100MW PP (Aggreko) | 96 | 96 | 95 | 96 | 94 | 93 | 93 | 93 | 93 | 95 | 96 | 97 | 97 | 99 | 96 | 96 | 97 | 25 |  | 94 | 97 | 98 | 97 | 98 | 97 | 98 | 2243877
114 | Kodda 149 MW PP Unit-1 (Summit) | 97 | 97 | 98 | 98 | 98 | 90 | 88 | 89 | 90 | 89 | 89 | 89 | 93 | 88 | 79 | 89 | 96 | 149 |  | 149 | 149 | 149 | 149 | 142 | 141 | 85 | 2572704
115 | Juldah 100 MW PP Unit-3 (Acorn) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  |  | 21 | 21 | 21 | 21 | 21 |  | 76 | 76 | 90 | 90 | 90 | 90 | 90 | 807360
116 | Chandpur 200MW (Desh energy) | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 22 | 34 | 34 | 34 | 34 | 34 | 34 | 707520
117 | Ashuganj 150MW PP (Midland) | 133 | 133 | 135 | 135 | 135 | 135 | 135 | 118 | 120 | 120 | 120 | 118 | 117 | 113 | 113 | 113 | 113 | 118 |  | 133 | 129 | 127 | 128 | 133 | 137 | 137 | 3032654
118 | Bibiyana-III 400 MW CCPP | 403 | 398 | 398 | 402 | 402 | 401 | 401 | 400 | 402 | 403 | 390 | 384 | 402 | 402 | 391 | 403 | 403 | 403 |  | 403 | 402 | 403 | 404 | 403 | 397 | 402 | 9584000
| Jamalpur 115 MW PP (United) | 48 | 48 | 48 | 48 | 48 | 49 | 49 | 49 | 47 | 47 | 47 | 47 | 46 | 49 | 49 | 49 | 49 | 76 |  | 78 | 78 | 78 | 78 | 78 | 78 | 49 | 1317600
| Anwara 300 MW PP (United) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 50 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 85 | 88 |  | 206 | 210 | 210 | 214 | 214 | 52 | 52 | 1658509
| Juldah unit-2 (Acorn) | 55 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  |  |  | 20 | 20 | 20 | 20 | 20 |  | 30 | 100 | 100 | 100 | 100 | 100 | 100 | 884160
| Anlima Energy Ltd. | 108 | 108 | 108 | 108 | 92 | 108 | 108 | 108 | 108 | 108 | 95 | 90 | 90 | 90 | 99 | 108 | 108 | 108 |  | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 2514109
| Bhairob 54.5 MW | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 885960
| Spectra Solar Plant Ltd. | [5 empty] | 0 | 5 | 8 | 18 | 32 | 33 | 35 | 29 | 34 | 17 | 12 | 3 | 2 | [8 empty] | 202236
| Chandpur 115(Doreen) | 76 | 76 | 75 | 75 | 74 | 75 | 75 | 71 | 72 | 75 | 75 | 75 | 75 | 74 | 67 | 71 | 74 | 75 |  | 75 | 70 | 58 | 68 | 73 | 75 | 75 | 1770240
| Kanchan Purbachal Power Generation Ltd. | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 43 | 37 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1299240
120 | Eastern Zone Total | 7087 | 7010 | 6951 | 6948 | 6946 | 6934 | 6915 | 6836 | 6624 | 6701 | 6637 | 6652 | 6788 | 6923 | 6925 | 7024 | 6999 | 7068 |  | 8092 | 8137 | 8169 | 8373 | 8393 | 8203 | 7539 | 173492391
121
122 | o
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | 26 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 32 | 32 | 32 | 32 | 16 | 16 |  | 31 | 30 | 32 | 22 | 32 | 16 | 16 | 484800
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 36 | 48 | 38 | 38 | 38 | 37 | 35 | 570240
| Khulna 225 MW CCPP | 224 | 226 | 227 | 226 | 227 | 227 | 227 | 237 | 237 | 234 | 238 | 229 | 230 | 230 | 231 | 229 | 228 | 229 |  | 227 | 230 | 230 | 229 | 229 | 228 | 228 | 5519040
129 | Rupsha 105 MW PP (Orion rupsha) | [9 empty] | 0 | 17 | 17 | 25 | 35 | 35 | 50 | 47 | 68 |  | 53 | 53 | 53 | 53 | 35 | 35 | 17 | 517920
130 | Mongla Orion 100 MW Solar PP |  |  |  |  | 0 | 1 | 10 | 47 | 74 | 42 | 88 | 10 | 43 | 25 | 6 | 46 | 21 | 5 | [8 empty] | 496080
131
132 | United Payra Power Ltd. | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | 18 | [9 empty] | 54 | 44 | 54 | 72 | 72 | 90 | 1236000
133 | Bhola Nutan Biddut BD LTD (GAS) | 210 | 220 | 220 | 220 | 220 | 220 | 219 | 220 | 220 | 220 | 214 | 214 | 214 | 214 | 217 | 214 | 200 | 215 |  | 217 | 217 | 210 | 222 | 223 | 220 | 215 | 5214518
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 48 |  |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 45 | 48 | 48 | 48 | 48 | 967584
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 84 | 88 | 88 | 86 | 88 | 86 | 86 | 87 | 88 | 86 | 84 | 82 | 87 | 86 | 86 | 88 | 88 | 85 |  | 88 | 87 | 87 | 87 | 87 | 86 | 88 | 2074016
140 | Bhola 33 MW PP (Venture) | 30 | 29 | 30 | 27 | 27 | 25 | 20 | 19 | 18 | 17 | 14 | 18 | 12 | 20 | 22 | 22 | 20 | 20 |  | 26 | 28 | 27 | 30 | 31 | 31 | 32 | 563305
141 | Noapara 100 MW PP (Bangla Trac) | 96 | 96 | 96 | 96 | 96 | 97 | 97 | 60 | 55 | 94 | 95 | 95 | 96 | 96 | 96 | 96 | 96 | 70 |  | 85 | 50 | 50 | 79 | 96 | 96 | 96 | 2214720
142 | Noapara 40 MW PP (Khanjahan Ali) | 8 | 0 | [10 empty] | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 102375
143 | Gopalganj 100 MW Peaking PP | 60 | 55 | 55 | 55 | 55 | 55 | 55 | 60 | 60 | 59 | 59 | 15 | 15 | 18 | 18 | 19 | 19 | 25 |  | 50 | 57 | 68 | 63 | 53 | 53 | 53 | 1054720
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | 89 | 89 | 89 | 90 | 89 | 89 | 71 | 75 | 89 | 71 | 71 | 71 | 71 | 86 | 88 | 88 | 88 | 88 |  | 88 | 88 | 89 | 89 | 105 | 105 | 105 | 2076192
146 | Bheramara HVDC | 914 | 914 | 914 | 914 | 914 | 914 | 914 | 914 | 915 | 914 | 914 | 914 | 914 | 915 | 915 | 915 | 914 | 914 |  | 915 | 914 | 915 | 914 | 915 | 914 | 914 | 22097454
147 | Bheramara 410 MW CCPP | 150 | 155 | 160 | 160 | 160 | 165 | 165 | 160 | 150 | 145 | 140 | 140 | 145 | 145 | 140 | 140 | 145 | 145 |  | 145 | 155 | 155 | 155 | 155 | 155 | 155 | 3796992
148 | Payra 1320 MW | 660 | 650 | 650 | 620 | 620 | 610 | 600 | 600 | 600 | 300 | 370 | 480 | 520 | 510 | 500 | 520 | 530 | 520 |  | 520 | 580 | 590 | 570 | 570 | 590 | 590 | 14851900
149
150 | Barapukuria TPP Unit-1 | [17 empty] | 11 |  | 47 | 66 | 66 | 70 | 71 | 71 | 71 | 371345
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 251 | 250 | 250 | 250 | 250 | 250 | 250 | 250 |  | 251 | 251 | 250 | 250 | 250 | 251 | 250 | 6080800
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 30 | 24 | 24 | 24 | 32 | 32 | 32 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 731632
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 0 | 1 | 4 | 5 | 5 | 3 | 5 | 5 | 1 | 2 | 1 | 0 | [8 empty] | 34860
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 173 | 172 | 172 | 175 | 177 | 176 | 175 | 179 | 179 | 175 | 172 | 173 | 172 | 172 | 168 | 168 | 168 | 167 |  | 168 | 167 | 166 | 167 | 170 | 169 | 169 | 4340491
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
| Sirajgonj 225 MW CCPP Unit-2 (Oil) | 206 | 208 | 215 | 213 | 209 | 214 | 213 | 216 | 215 | 213 | 207 | 180 | 180 | 180 | 180 | 180 | 180 | 130 |  | 143 | 180 | 180 | 180 | 199 | 214 | 212 | 4908091
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 145 | 145 | 145 | 147 | 148 | 149 | 150 | 150 | 150 | 147 | 144 | 144 | 144 | 143 | 143 | 143 | 144 | 145 |  | 146 | 149 | 148 | 149 | 149 | 151 | 150 | 3763018
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 274 | 276 | 291 | 297 | 303 | 317 | 318 | 312 | 297 | 286 | 281 | 280 | 275 | 275 | 267 | 274 | 278 | 274 |  | 282 | 289 | 296 | 287 | 300 | 291 | 291 | 6918400
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | 27 | 27 | 32 | 0 | [7 empty] | 4 |  |  |  |  | 3 | 5 |  | 6 | 7 | 7 | 17 | 0 |  | 0 | 128941
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 19 | 18 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 18 |  | 20 | 20 | 20 | 21 | 21 | 21 | 22 | 444960
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 233334
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 32 | 32 | 16 | 24 | 24 | 24 | 24 | 24 | 30 | 32 | 32 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 564800
168 | Santahar 50 MW Peaking PP | 34 | 34 | 34 | 34 | 33 | 33 | 33 | 33 | 33 | 14 | 14 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 35 | 33 | 33 | 33 | 34 | 754460
169 | Natore 52 MW PP (Rajlanka) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 43 | 52 | 52 | 52 | 52 | 52 | 52 | 426240
170 | Chapainawabganj 100 MW Peaking PP | 72 | 65 | 64 | 59 | 59 | 51 | 51 | 51 | 51 | 44 | 44 | 44 | 44 | 44 | 47 | 43 | 43 | 50 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1367056
171 | Baghabari 200 MW PP (Paramount) | 169 | 168 | 168 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 168 | 169 | 168 | 168 | 168 | 115 | 90 | 20 |  | 54 | 161 | 165 | 179 | 181 | 181 | 180 | 3773965
| Bagura 113 MW PP (Confidence)-2 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 65 | 92 | 94 |  | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 1681056
172 | Confidence Power Bogura Unit-1 113 MW | 95 | 57 | 57 | 55 | 55 | 55 | 55 | 55 | 50 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 95 |  | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 1615872
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 56 | 55 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 50 | 50 | 55 | 54 | 97 | 98 |  | 98 | 98 | 97 | 97 | 97 | 98 | 70 | 1627171
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1 | 1 | 1 | 2 | 4 | 3 | 4 | 5 | 5 | 5 | 3 | 2 | [8 empty] | 37274
178 | Energypac Power Venture Thakurgaon Ltd. | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 72 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 1318272
178