## Forecast
8 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2022-08-12 | Friday
|  |  | Date (day): | 2022-08-12 |  | Friday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 10931.6 | MW |  |  | (b) At Evening Peak Hour : |  | 12925 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2022-08-11 | 2022-08-12 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 300 | 290 | 300 | 300 |  | 65 | Engine problem
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 82 | 80 | 83 | 83 |  | 25 | Engine problem
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 258 | 391 | 350 | 390 | 22 |  | Gas shortage
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 307 | 206 | 300 | 300 | 60 |  | Gas shortage
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 225 | 225 | 225 |  | Gas shortage & GT-2 S/D
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 7 | 32 | 15 | 32 | 68 |  | Fuel shortage
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 0 | 0 | 0 | 0 |  | 102 | Under maint
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 30 | 30 | 30 | 30 |  | 25 | Engine problem
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 22 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 8 | 49 | 8 | 50 | 50 |  | Fuel shortage
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 8 | 32 | 8 | 32 | 70 |  | Fuel shortage
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 54 | 17 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 32 | 127 | 36 | 130 |  | 19 | Engine problem
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 35 | 35 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 51 | 47 | 50 | 50 |  | 30 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 30 | 16 | 30 | 30
| 29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 42 | 42 | 42 | 42 |  | 10 | Engine problem
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 82 | 277 | 82 | 285 |  | 15 | Engine problem
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 300 | 300 | 300 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 90 | 98 | 90 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 90 | 98 | 0 | 0 | 100 |  | Fuel shortage
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 43 | 149 | 43 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 70 | 88 | 88 | 88 |  | 17 | Engine problem
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 17 | 33 | 17 | 33 | 71 |  | Fuel shortage
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 35 | 162 | 35 | 162
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 21 | 0 | 30 | 0
| 40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 55 | 55 | 55 | 55
|  | Dhaka area Total |  |  |  |  | 6263 | 5847 | 2522 | 3206 | 2559 | 3265 | 1597 | 988
| 41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 110 | 110 | 110 | 110 | 70 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 25 | 25 | 25 | 25
| 43 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 11 | 0 | 20 | 0
| 44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 19 | 45 | 19 | 45 |  | 5 | Engine problem
| 45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 107 | 107 | 107 | 107 |  | 123 | Low Water Level
| 46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | S/D due to HGPI
| 47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
| 48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 69 | 105 | 68 | 105
| 49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 25 | 34 | 25 | 34 | 64 |  | Fuel shortage
| 50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 17 | 51 | 17 | 51 | 51 |  | Fuel shortage
| 51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 33 | 33 | 33 | 33 | 67 |  | Fuel shortage
| 52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 21 | 90 | 21 | 90 |  | 10 | Engine problem
| 53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 15 | 15 | 15 | 15 |  | 7 | Engine problem
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 8 | 32 | 15 | 30
| 54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 7 | 90 | 12 | 90 |  | 18 | Engine problem
| 55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 2 | 0 | 5 | 0
| 56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 51 | 214 | 52 | 214 | 86 |  | Fuel shortage
| 57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 36 | 36 | 36 | 36 |  | 18 | Engine problem
| 58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 55 | 55 | 55 | 55 | 55 |  | Fuel shortage
| 59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 20 | 98 | 20 | 100
| 60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 108 | 108 | 108 | 108 |  | 8 | Engine problem
|  | Mirsharai 150 MW |  | Gas/HSD | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 739 | 1248 | 763 | 1248 | 573 | 564
| 61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 183 | 188 | 190 | 190 | 31 |  | Gas shortage
| 63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 280 | 300 | 280 | 320 | 40 |  | Gas shortage
| 64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 260 | 270 | 280 | 310 | 50 |  | Gas shortage
|  | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+136*1 | 284 | 284 | 0 | 0 | 0 | 0 |  |  | On test.
| 65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 36 | 42 | 42 | 42 |  | 3 | Engine problem
| 66 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 55 | 50 | 55 | 55 | 55
| 67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 51 | 51 | 51
| 69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 117 | 140 | 118 | 142 |  | 8 | Engine problem
| 70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 47 | 47 | 47 | 47 |  | 5 | Engine problem
| 71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 124 | 123 | 130 | 130 |  | 33 | Engine problem
| 72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 34 | 200 | 34 | 200
| 73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 22 | 22 | 22
| 74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 9 | 10 | 10 | 10
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 90 | 78 | 143 | 166
| 75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 21 | 33 | 33 | 33
| 76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 8 | 8 | 8 | 44 |  | Fuel shortage
| 77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 20 | 20 |  | 5 | Engine problem
| 78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel shortage
| 79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 114 | 17 | 114
| 80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 39 | 105 | 38 | 105 |  | 8 | Engine problem
| 81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 35 | 35 | 35 | 35 |  | 19 | 33 kV feeder fault
| 82 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 73 | 74 | 74 | 75 | 40 |  | Fuel shortage
|  | Cumilla Area Total |  |  |  |  | 3193 | 3169 | 1513 | 1923 | 1635 | 2083 | 726 | 81
| 83 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 63 | 98 | 60 | 90 | 112 |  | Gas shortage
| 84 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 22 | 22 | 22
| 85 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0 |  | 8 | Under maint.
| 86 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 87 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 48 | 180 | 48 | 180 |  | 20 | Engine problem
| 88 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 49 | 78 | 48 | 78 |  | 37 | Engine problem
| 89 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 53 | 0 | 50 | 0
| 90 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 12 | 12 |  | 10 | Engine problem
|  | Mymensingh Area Total |  |  |  |  | 717 | 614 | 247 | 390 | 241.6 | 382 | 112 | 75
| 91 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 43 | 43 | 43 |  | 27 | Machine problem.
| 92 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 41 | 41 | 0 | 0 |  | 90 | Machine problem
| 93 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | ST under maint.
| 94 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
| 95 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Gas shortage
| 96 | Fenchuganj 44MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Gas shortage
| 97 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 11 | 11
| 98 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 59 | 62 | 62 | 64
| 99 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 10 | 81 | 10 | 80
| 100 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
| 101 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 221 | 221 | 220 | 220
| 102 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Gas shortage
| 103 | Sylhet 50MW PP (EPL) |  | Gas | NENP | 27*2 | 50 | 50 | 0 | 0 | 30 | 30 | 20 |  | Gas shortage
| 104 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 0 | 8 | 12 | 12 | 13 |  | Gas shortage
| 105 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 280 | 300 | 320 |  |  | FGMO
| 106 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 395 | 403 | 400 | 400
| 107 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 9 | 9 | 10 | 10
| 108 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 382 | 388 | 400 | 400
|  | Sylhet Area Total |  |  |  |  | 2522 | 2477 | 1460 | 1536 | 1498 | 1590 | 154 | 710
| 109 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 906 | 907 | 920 | 920
| 110 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 16 | 16 | 16 | 32 | 83 |  | Fuel shortage
| 111 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 45 | 0 | 43 |  | 11 | Engine problem
| 112 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 228 | 230 | 225 | 225
| 113 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 72 | 0 | 70 |  | 39 | Engine problem
| 114 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 155 | 145 | 155 | 155 | 255 |  | Gas shortage
| 115 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 8 | 8 | 8 | 8 | 32 |  | Fuel shortage
| 116 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 94 | 96 | 94 | 94 |  | 6 | Engine problem
| 117 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 17 | 53 | 17 | 52 | 53 |  | Fuel shortage
| 118 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 67 | 105 | 105 | 105
| 119 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 60 | 0 | 100 | 0
|  | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
|  | Khulna Area Total |  |  |  |  | 2388 | 2384 | 1551 | 1677 | 1640 | 1704 | 439 | 56
| 120 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 110 | 16 | 110 |  |  | Line O/L
| 121 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 16 | 27 | 15 | 20 |  | 20 | Engine problem
| 122 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 88 | 88 | 88 | 88 | 106 |  | Gas shortage
|  | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
| 123 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 490 | 70 | 620 | 620 |  |  | Coal Shortage
| 124 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 218 | 220 | 225 | 0
| 125 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 116 | 50 | 116
|  | Barisal Area Total |  |  |  |  | 1958 | 1958 | 812 | 631 | 1014 | 954 | 106 | 20
| 126 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 127 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 31 | 31 | 32 | 32 |  | 20 | Engine problem
| 128 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 34 | 41 | 40 | 40 |  | 31 | Engine problem
| 129 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 130 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 42 | 42 | 42 |  | 8 | Engine problem
| 131 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 32 | 40 | 32 | 40 |  | 10 | Engine problem
| 132 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 152 | 152 | 150 | 150 | 60 |  | Gas shortage
| 133 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 209 | 218 | 220 | 220
| 134 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 147 | 148 | 150 | 150 | 70 |  | Gas shortage
| 135 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 279 | 308 | 300 | 300 | 114 |  | Gas shortage
| 136 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 34 | 33 | 33 | 34 |  | 16 | Engine problem
| 137 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 18 | 21 | 21 | 21
| 138 | Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 139 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 140 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 16 | 8 | 16 | 36 |  | Fuel shortage
| 141 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 46 | 80 | 50 | 80 |  | 24 | Engine problem
| 142 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 177 | 133 | 50 | 0 | 200 |  | Fuel shortage
| 143 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 50 | 94 | 50 | 90 |  | 23 | Engine problem
| 144 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 55 | 95 | 55 | 95 |  | 18 | Engine problem
| 145 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2129 | 1288 | 1463 | 1250 | 1321 | 651 | 150
| 146 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Machine problem
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
| 147 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 250 | 251 | 250 | 250 | 24 |  | Machine problem
| 148 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
| 149 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
| 150 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 56 | 55 | 56 | 56 |  | 57 | Engine problem
| 151 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 4 | 0 | 8 | 0
| 152 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 17 | 72 | 17 | 72 |  | 43 | Fuel shortage
|  | Rangpur Area Total |  |  |  |  | 800 | 720 | 327 | 378 | 331 | 378 | 149 | 185
|  | Total |  |  |  |  | 22482 | 21680 | 10459 | 12452 | 10931.6 | 12925 | 4507 | 2829
| A. |  | 2022-08-11 | (Yesterday) |  |  |  |  | Thursday
| 1 | Highest Generation : |  |  | 12452 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 10280 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 13450 | MW
| 3 | Day peak Generation : |  |  | 10459 | MW at | 10:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 12957.15 | MW
| 4 | Evening peak Generation : |  |  | 12452 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 920 | MW
| 5 | Total Energy Generation : |  | 263.4185 | MKWHr | By Solar | 1.0943 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
|  | By Gas : | 130.5835 | MKWHr |  | By Oil: | 90.4288 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 14.8206 | MKWHr |  | By Hydro: | 2.5445 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 4507 | MW | Dhaka | 4611.55 | 4421.55 |  | 190 |  | 18:00 |  | 662.6124
|  |  |  | For Plants S/D or M/C prob = |  |  | 2829 | MW | Chittagong | 1245.75 | 1245.75 |  | 0 |  | 19:00 |  | 1018.3404
|  |  |  | Total = |  |  | 7336 | MW | Khulna | 1539 | 1364 |  | 175 |  | 19:30 |  | 869.9668
| 7 | Total Gas Supplied : |  |  | 963.93 | MMCFD |  |  | Rajshahi | 1341 | 1191 |  | 150 |  | 20:00 |  | 974.1048
| 8 | Fuel Cost : | i) Gas : | Taka | 146727448.788 | ii) Oil : | Taka | 1377368341.84 | Comilla | 1280 | 1105 |  | 175 |  | 21:00 |  | 919.7319
|  |  | iii) Coal : |  | 110843838 | Total | Taka | 1634939628.628 | Mymensingh | 1081 | 891 |  | 190 |  | 22:00 |  | 1035.8503
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0 | MKWHr. | Sylhet | 595 | 555 |  | 40 |  | 23:00 |  | 1134.4588
|  | ii) During Peak Demand : |  |  | 206 | MW (E to W) at | 21:00 | hrs | Barisal | 355.85 | 355.85 |  | 0 |  | 24:00 |  | 1761.1298
|  | iii) Maximum : |  |  | 98 | MW at | 19:00 | hrs | Rangpur | 908 | 908 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 33° C |  |  | Total | 12957.15 | 12037.15 |  | 920
| B. |  | 2022-08-12 | (Today) |  |  |  | Friday |  |  | Probable max. temperature in Dhaka |  |  | 33.5° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 14200 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 1175 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 12925 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 11700 | MW
| 4 | Reserve(Generation end) |  |  |  | - | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 300.3969 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 9620 | MW at | 8:00 | 267 | 140 | 176 | 158 | 105 | 155 | 56 | 0 | 118
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.8953 | MKWHr. | ii) HVDC Flow at Peak Time |  | 907 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.0515 | MKWHr. | iii) Maximum HVDC Flow : |  | 907 | MW at | 1:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 95.69 |  | (b) Today: | 95.79 |  | (c) Rule Curve: |  | 92.52
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2022-08-11
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 300 | 86 | 0 | 274 | 240 |  | 0 | 225 | 0 | 8 | 0 | 30 | 0 | 0 | 0 | 8 | 8 | 32 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 27 | 33 | 30 | 36 | 0 | 35 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 25 | 51 | 33 | 12 | 19 | 15 | 38 | 0 | 0 | 0 | 310 | 300 | 207 | 8 | 123 | 38 | 53 | 0 | 51 | 0 | 48 | 8 | 22 | 9 | 33 | 20 | 78 | 102 | 0 | 22 | 0 | 43 | 41 | 0 | 0 | 0 | 0 | 61 | 10 | 0 | 221 | 0 | 30 | 9 | 310 | 8 | 0 | 0 | 82 | 302 | 90 | 48 | 90 | 43 | 0 | 21 | 34 | 133 | 403 | 49 | 88 | 84 | 0 | 16 | 36 | 55 | 27 | 47 | 47 | 391 | 0 | 0 | 56 | 108 | 0 | 35 | 0 | 73 | 55 | 0 | 0 | 0 |  | 907 | 0 | 160 | 0 | 16 | 217 | 0 | 0 | 30 | 60 | 8 | 88 | 25 | 16 | 0 | 0 | 0 | 31 | 26 | 81 | 0 | 0 | 32 | 8 | 34 | 22 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 165 | 0 | 0 | 215 | 0 | 94 | 153 | 0 | 319 | 0 | 178 | 50 | 89 | 65 | 0 | 0 | 55 | 600 | 220 | 0 | 0 | 0 | 0 | 52 | 0 | 0 |  | 6709 | 4277 | 10986 | 3944 | 907 | 1646 | 754 | 1820 | 850 | 105 | 432 | 665 | 78 | 0 | 1395.2645 | 95.61
2:00 | 0 | 0 | 0 | 180 | 300 | 86 | 0 | 274 | 240 |  | 0 | 225 | 0 | 8 | 0 | 30 | 0 | 0 | 0 | 8 | 8 | 32 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 27 | 33 | 30 | 36 | 0 | 35 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 25 | 51 | 33 | 12 | 19 | 15 | 38 | 0 | 0 | 0 | 320 | 310 | 191 | 8 | 122 | 38 | 54 | 0 | 51 | 0 | 48 | 8 | 22 | 9 | 33 | 20 | 68 | 102 | 0 | 22 | 0 | 43 | 41 | 0 | 0 | 0 | 0 | 60 | 10 | 0 | 221 | 0 | 30 | 9 | 315 | 8 | 0 | 0 | 80 | 302 | 90 | 48 | 90 | 43 | 0 | 21 | 34 | 138 | 403 | 49 | 88 | 87 | 0 | 16 | 36 | 55 | 17 | 38 | 20 | 392 | 0 | 0 | 35 | 108 | 0 | 35 | 0 | 73 | 55 | 0 | 0 | 0 |  | 907 | 0 | 160 | 0 | 16 | 218 | 0 | 0 | 30 | 40 | 8 | 88 | 23 | 16 | 0 | 0 | 0 | 31 | 26 | 81 | 0 | 0 | 32 | 8 | 33 | 22 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 165 | 0 | 0 | 217 | 0 | 94 | 153 | 0 | 318 | 0 | 178 | 50 | 105 | 55 | 0 | 0 | 55 | 560 | 220 | 0 | 0 | 0 | 0 | 34 | 0 | 0 |  | 6647 | 4204 | 10851 | 3947 | 907 | 1649 | 754 | 1747 | 810 | 105 | 435 | 646 | 68 | 0 | 1151.0472 | 95.63
3:00 | 0 | 0 | 0 | 180 | 300 | 86 | 0 | 268 | 243 |  | 0 | 225 | 0 | 7 | 0 | 30 | 0 | 0 | 0 | 8 | 8 | 32 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 27 | 33 | 30 | 42 | 0 | 35 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 25 | 51 | 33 | 12 | 18 | 15 | 38 | 0 | 0 | 0 | 300 | 290 | 191 | 8 | 122 | 38 | 54 | 0 | 51 | 0 | 48 | 8 | 22 | 9 | 33 | 20 | 64 | 102 | 0 | 22 | 0 | 43 | 41 | 0 | 0 | 0 | 0 | 60 | 10 | 0 | 221 | 0 | 31 | 9 | 310 | 8 | 0 | 0 | 82 | 302 | 90 | 48 | 90 | 43 | 0 | 21 | 34 | 137 | 403 | 49 | 88 | 87 | 0 | 16 | 36 | 55 | 17 | 38 | 20 | 398 | 0 | 0 | 35 | 108 | 0 | 35 | 0 | 73 | 55 | 0 | 0 | 0 |  | 902 | 0 | 165 | 0 | 16 | 218 | 0 | 0 | 30 | 40 | 8 | 88 | 22 | 0 | 0 | 0 | 0 | 31 | 26 | 45 | 0 | 0 | 24 | 8 | 33 | 22 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 164 | 0 | 0 | 218 | 0 | 94 | 155 | 0 | 335 | 0 | 178 | 50 | 105 | 55 | 0 | 0 | 55 | 540 | 220 | 0 | 0 | 0 | 0 | 34 | 0 | 0 |  | 6607 | 4142 | 10749 | 3913 | 902 | 1664 | 754 | 1736 | 790 | 105 | 436 | 603 | 64 | 0 | 1106.8116 | 95.65
4:00 | 0 | 0 | 0 | 180 | 300 | 86 | 0 | 267 | 247 |  | 0 | 225 | 0 | 8 | 0 | 30 | 0 | 0 | 0 | 8 | 8 | 32 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 18 | 33 | 30 | 42 | 0 | 35 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 25 | 51 | 33 | 12 | 18 | 15 | 38 | 0 | 0 | 0 | 280 | 270 | 198 | 8 | 122 | 38 | 54 | 0 | 51 | 0 | 47 | 8 | 22 | 9 | 33 | 20 | 78 | 102 | 0 | 22 | 0 | 43 | 41 | 0 | 0 | 0 | 0 | 61 | 10 | 0 | 220 | 0 | 30 | 9 | 305 | 8 | 0 | 0 | 82 | 301 | 90 | 48 | 90 | 44 | 0 | 21 | 34 | 135 | 402 | 49 | 88 | 87 | 0 | 16 | 36 | 55 | 17 | 39 | 20 | 398 | 10 | 0 | 35 | 108 | 0 | 35 | 0 | 64 | 55 | 0 | 0 | 0 |  | 905 | 0 | 165 | 0 | 16 | 218 | 0 | 0 | 30 | 40 | 8 | 89 | 19 | 0 | 0 | 0 | 0 | 31 | 26 | 45 | 0 | 0 | 24 | 8 | 33 | 22 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 164 | 0 | 0 | 219 | 0 | 94 | 156 | 0 | 335 | 0 | 177 | 50 | 105 | 55 | 0 | 0 | 55 | 540 | 220 | 0 | 0 | 0 | 0 | 34 | 0 | 0 |  | 6575 | 4144 | 10719 | 3871 | 905 | 1659 | 752 | 1738 | 790 | 105 | 437 | 603 | 78 | 0 | 904.0651 | 95.67
5:00 | 0 | 0 | 0 | 180 | 300 | 86 | 0 | 269 | 255 |  | 0 | 225 | 0 | 8 | 0 | 30 | 0 | 0 | 0 | 8 | 8 | 32 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 27 | 33 | 30 | 42 | 0 | 35 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 25 | 51 | 33 | 12 | 19 | 15 | 38 | 0 | 0 | 0 | 280 | 270 | 210 | 8 | 136 | 38 | 54 | 0 | 51 | 0 | 47 | 8 | 22 | 9 | 33 | 20 | 84 | 103 | 0 | 22 | 0 | 43 | 41 | 0 | 0 | 0 | 0 | 61 | 10 | 0 | 220 | 0 | 30 | 9 | 285 | 8 | 0 | 0 | 82 | 300 | 90 | 48 | 90 | 43 | 0 | 21 | 34 | 138 | 400 | 49 | 88 | 87 | 0 | 16 | 36 | 46 | 17 | 38 | 20 | 400 | 0 | 0 | 35 | 108 | 0 | 35 | 0 | 73 | 23 | 0 | 0 | 0 |  | 905 | 0 | 165 | 0 | 16 | 218 | 0 | 0 | 30 | 40 | 8 | 89 | 18 | 0 | 0 | 0 | 0 | 31 | 40 | 45 | 0 | 0 | 24 | 8 | 33 | 22 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 164 | 0 | 0 | 220 | 0 | 94 | 157 | 0 | 331 | 0 | 177 | 50 | 105 | 56 | 0 | 0 | 55 | 540 | 221 | 0 | 0 | 0 | 0 | 34 | 0 | 0 |  | 6566 | 4157 | 10723 | 3910 | 905 | 1643 | 751 | 1699 | 790 | 105 | 438 | 618 | 84 | 0 | 255.2763 | 95.68
6:00 | 0 | 0 | 0 | 180 | 300 | 86 | 0 | 226 | 274 |  | 0 | 225 | 0 | 7 | 0 | 30 | 0 | 0 | 0 | 8 | 8 | 32 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 27 | 33 | 32 | 42 | 0 | 35 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 25 | 17 | 33 | 12 | 19 | 15 | 41 | 0 | 0 | 0 | 345 | 330 | 205 | 8 | 135 | 35 | 54 | 0 | 51 | 0 | 47 | 8 | 22 | 9 | 33 | 20 | 76 | 101 | 0 | 20 | 0 | 43 | 41 | 0 | 0 | 0 | 0 | 60 | 10 | 0 | 221 | 0 | 30 | 9 | 270 | 8 | 0 | 0 | 80 | 101 | 90 | 48 | 90 | 43 | 1 | 21 | 34 | 137 | 400 | 49 | 88 | 87 | 0 | 16 | 36 | 55 | 17 | 38 | 20 | 387 | 0 | 1 | 35 | 108 | 0 | 35 | 1 | 73 | 55 | 0 | 0 | 0 |  | 905 | 0 | 170 | 0 | 16 | 215 | 0 | 0 | 0 | 40 | 8 | 86 | 13 | 0 | 0 | 0 | 0 | 31 | 35 | 45 | 0 | 0 | 24 | 8 | 33 | 22 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 163 | 0 | 0 | 220 | 0 | 0 | 157 | 0 | 340 | 0 | 50 | 50 | 105 | 56 | 0 | 0 | 55 | 500 | 217 | 0 | 0 | 0 | 3 | 34 | 0 | 0 |  | 6430 | 3862 | 10292 | 3969 | 905 | 1650 | 331 | 1736 | 750 | 105 | 435 | 549 | 76 | 6 | 191.6876 | 95.69
7:00 | 0 | 0 | 0 | 180 | 300 | 86 | 0 | 21 | 320 |  | 0 | 225 | 0 | 7 | 0 | 30 | 0 | 0 | 0 | 8 | 8 | 32 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 0 | 25 | 27 | 33 | 32 | 42 | 0 | 35 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 25 | 17 | 33 | 9 | 19 | 13 | 40 | 0 | 0 | 0 | 310 | 305 | 178 | 8 | 128 | 35 | 54 | 0 | 51 | 0 | 40 | 8 | 22 | 9 | 33 | 20 | 86 | 80 | 0 | 20 | 0 | 43 | 41 | 0 | 0 | 0 | 0 | 59 | 10 | 0 | 221 | 0 | 30 | 9 | 315 | 8 | 0 | 0 | 80 | 302 | 90 | 48 | 90 | 43 | 3 | 21 | 34 | 133 | 402 | 49 | 88 | 69 | 0 | 16 | 36 | 55 | 17 | 38 | 20 | 400 | 0 | 13 | 35 | 108 | 0 | 35 | 7 | 73 | 55 | 0 | 0 | 0 |  | 905 | 0 | 165 | 0 | 16 | 230 | 0 | 0 | 0 | 40 | 8 | 88 | 12 | 0 | 0 | 0 | 0 | 31 | 36 | 45 | 0 | 0 | 24 | 8 | 34 | 22 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 164 | 0 | 0 | 215 | 0 | 20 | 154 | 0 | 329 | 0 | 71 | 50 | 105 | 56 | 0 | 1 | 55 | 500 | 220 | 0 | 0 | 0 | 7 | 34 | 0 | 0 |  | 6374 | 3906 | 10280 | 3637 | 905 | 1731 | 573 | 1693 | 750 | 105 | 445 | 539 | 86 | 31 | 294.904 | 95.7
8:00 | 0 | 0 | 0 | 180 | 300 | 83 | 0 | 49 | 326 |  | 0 | 225 | 0 | 8 | 0 | 30 | 0 | 0 | 0 | 8 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 0 | 25 | 24 | 33 | 21 | 42 | 0 | 37 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 25 | 17 | 33 | 11 | 19 | 13 | 15 | 0 | 0 | 0 | 280 | 275 | 165 | 8 | 128 | 33 | 54 | 0 | 51 | 0 | 47 | 8 | 19 | 9 | 33 | 20 | 84 | 66 | 0 | 20 | 0 | 43 | 41 | 0 | 0 | 0 | 0 | 58 | 10 | 0 | 221 | 0 | 30 | 9 | 280 | 8 | 0 | 0 | 82 | 262 | 90 | 48 | 90 | 43 | 5 | 21 | 34 | 115 | 402 | 49 | 88 | 69 | 1 | 50 | 36 | 55 | 17 | 39 | 20 | 395 | 17 | 29 | 35 | 108 | 0 | 35 | 10 | 74 | 55 | 0 | 0 | 0 |  | 906 | 0 | 170 | 0 | 16 | 229 | 0 | 0 | 0 | 40 | 8 | 88 | 15 | 0 | 0 | 0 | 0 | 31 | 36 | 46 | 0 | 0 | 32 | 8 | 34 | 22 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 164 | 0 | 0 | 220 | 0 | 94 | 153 | 0 | 318 | 0 | 178 | 50 | 105 | 56 | 0 | 1 | 55 | 490 | 223 | 0 | 0 | 1 | 27 | 34 | 0 | 0 |  | 6246 | 4111 | 10357 | 3557 | 906 | 1669 | 714 | 1733 | 740 | 107 | 449 | 544 | 84 | 74 | 408 | 95.7
9:00 | 0 | 0 | 0 | 180 | 300 | 85 | 0 | 149 | 317 |  | 0 | 225 | 0 | 8 | 0 | 30 | 0 | 0 | 0 | 8 | 8 | 32 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 19 | 25 | 24 | 33 | 32 | 42 | 0 | 36 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 25 | 17 | 33 | 8 | 19 | 15 | 8 | 0 | 0 | 0 | 280 | 260 | 139 | 8 | 129 | 35 | 53 | 0 | 51 | 0 | 47 | 8 | 19 | 9 | 21 | 20 | 86 | 64 | 0 | 20 | 2 | 44 | 41 | 0 | 0 | 0 | 0 | 55 | 10 | 0 | 221 | 0 | 30 | 9 | 320 | 8 | 0 | 0 | 82 | 301 | 90 | 48 | 90 | 43 | 1 | 21 | 34 | 122 | 400 | 49 | 88 | 69 | 2 | 51 | 36 | 55 | 17 | 38 | 20 | 397 | 17 | 42 | 35 | 108 | 0 | 35 | 23 | 74 | 55 | 0 | 0 | 0 |  | 907 | 0 | 155 | 0 | 16 | 229 | 0 | 0 | 0 | 7 | 8 | 88 | 15 | 0 | 0 | 0 | 0 | 31 | 36 | 46 | 0 | 0 | 32 | 8 | 34 | 18 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 150 | 0 | 0 | 212 | 0 | 94 | 149 | 0 | 298 | 17 | 177 | 50 | 105 | 56 | 0 | 4 | 55 | 490 | 222 | 0 | 0 | 4 | 15 | 17 | 0 | 0 |  | 6434 | 4006 | 10440 | 3602 | 907 | 1669 | 752 | 1737 | 740 | 106 | 441 | 519 | 86 | 93 | 516 | 95.71
10:00 | 0 | 0 | 0 | 180 | 300 | 82 | 0 | 258 | 307 |  | 0 | 225 | 0 | 7 | 0 | 30 | 0 | 0 | 0 | 8 | 8 | 32 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 19 | 25 | 26 | 33 | 30 | 42 | 0 | 37 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 25 | 17 | 33 | 7 | 19 | 15 | 8 | 0 | 0 | 0 | 280 | 260 | 183 | 8 | 124 | 36 | 50 | 0 | 43 | 0 | 47 | 8 | 19 | 9 | 21 | 20 | 90 | 63 | 0 | 20 | 2 | 43 | 41 | 0 | 0 | 0 | 0 | 59 | 10 | 0 | 221 | 0 | 0 | 9 | 300 | 0 | 0 | 0 | 82 | 300 | 90 | 48 | 90 | 43 | 11 | 21 | 34 | 117 | 395 | 49 | 70 | 69 | 2 | 51 | 36 | 55 | 17 | 39 | 20 | 382 | 17 | 53 | 35 | 108 | 0 | 35 | 21 | 73 | 55 | 0 | 0 | 0 |  | 906 | 0 | 155 | 0 | 16 | 228 | 0 | 0 | 0 | 0 | 8 | 88 | 16 | 0 | 0 | 0 | 0 | 31 | 34 | 46 | 0 | 0 | 32 | 8 | 34 | 18 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 152 | 0 | 0 | 209 | 0 | 94 | 147 | 0 | 279 | 17 | 177 | 50 | 67 | 56 | 0 | 4 | 55 | 490 | 218 | 0 | 0 | 5 | 60 | 17 | 0 | 0 |  | 6481 | 3978 | 10459 | 3725 | 906 | 1573 | 751 | 1674 | 740 | 107 | 437 | 507 | 90 | 158 | 821 | 95.71
11:00 | 0 | 0 | 0 | 180 | 300 | 82 | 0 | 376 | 253 |  | 0 | 225 | 0 | 8 | 0 | 30 | 0 | 0 | 0 | 8 | 8 | 32 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 19 | 25 | 20 | 33 | 14 | 42 | 0 | 37 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 25 | 17 | 33 | 9 | 19 | 15 | 8 | 0 | 0 | 0 | 280 | 260 | 202 | 8 | 124 | 36 | 48 | 0 | 43 | 0 | 47 | 8 | 19 | 9 | 16 | 12 | 88 | 64 | 0 | 20 | 2 | 43 | 41 | 0 | 0 | 0 | 0 | 59 | 10 | 0 | 221 | 0 | 0 | 9 | 280 | 0 | 0 | 0 | 82 | 205 | 90 | 48 | 90 | 43 | 6 | 21 | 34 | 112 | 404 | 49 | 70 | 69 | 6 | 52 | 36 | 55 | 17 | 39 | 20 | 386 | 17 | 57 | 35 | 108 | 0 | 35 | 34 | 73 | 55 | 0 | 0 | 0 |  | 907 | 0 | 150 | 0 | 16 | 228 | 0 | 0 | 0 | 0 | 8 | 88 | 10 | 0 | 0 | 0 | 0 | 31 | 31 | 46 | 0 | 0 | 32 | 8 | 34 | 18 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 152 | 0 | 0 | 208 | 0 | 50 | 146 | 0 | 286 | 17 | 175 | 50 | 67 | 56 | 0 | 6 | 55 | 490 | 222 | 0 | 0 | 5 | 51 | 17 | 0 | 0 |  | 6439 | 3921 | 10360 | 3835 | 907 | 1502 | 610 | 1673 | 740 | 107 | 436 | 503 | 88 | 167 | 1143 | 95.72
12:00 | 0 | 0 | 0 | 180 | 300 | 80 | 0 | 400 | 243 |  | 0 | 225 | 0 | 8 | 0 | 15 | 0 | 0 | 0 | 8 | 8 | 30 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 0 | 25 | 23 | 33 | 28 | 42 | 0 | 35 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 17 | 33 | 12 | 19 | 15 | 6 | 0 | 0 | 0 | 280 | 260 | 203 | 8 | 125 | 36 | 50 | 0 | 43 | 0 | 47 | 8 | 19 | 9 | 16 | 11 | 98 | 60 | 0 | 20 | 2 | 43 | 41 | 0 | 0 | 0 | 0 | 58 | 10 | 0 | 220 | 0 | 0 | 9 | 320 | 0 | 0 | 0 | 82 | 304 | 90 | 47 | 90 | 43 | 13 | 21 | 34 | 110 | 404 | 49 | 70 | 69 | 1 | 52 | 36 | 55 | 17 | 39 | 20 | 395 | 17 | 46 | 35 | 108 | 0 | 35 | 28 | 74 | 55 | 0 | 0 | 0 |  | 906 | 0 | 140 | 0 | 16 | 226 | 0 | 0 | 0 | 0 | 8 | 86 | 15 | 0 | 0 | 0 | 0 | 31 | 31 | 46 | 0 | 0 | 32 | 2 | 34 | 17 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 152 | 0 | 0 | 209 | 0 | 94 | 143 | 0 | 255 | 10 | 176 | 50 | 67 | 55 | 0 | 7 | 55 | 490 | 212 | 0 | 0 | 3 | 17 | 17 | 0 | 0 |  | 6570 | 3863 | 10433 | 3846 | 906 | 1493 | 754 | 1645 | 740 | 105 | 435 | 503 | 98 | 117 | 1260 | 95.72
13:00 | 0 | 0 | 0 | 180 | 300 | 80 | 0 | 400 | 237 |  | 0 | 225 | 0 | 8 | 0 | 22 | 0 | 0 | 0 | 8 | 8 | 30 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 0 | 25 | 8 | 33 | 28 | 42 | 0 | 35 | 70 | 113 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 17 | 33 | 12 | 19 | 15 | 6 | 0 | 0 | 0 | 280 | 260 | 204 | 8 | 125 | 36 | 46 | 0 | 51 | 0 | 37 | 8 | 19 | 9 | 16 | 11 | 104 | 60 | 0 | 20 | 2 | 43 | 41 | 0 | 0 | 0 | 0 | 55 | 10 | 0 | 220 | 0 | 0 | 9 | 285 | 0 | 0 | 0 | 80 | 300 | 90 | 47 | 90 | 43 | 6 | 21 | 34 | 110 | 396 | 49 | 70 | 69 | 3 | 68 | 36 | 55 | 17 | 39 | 20 | 392 | 10 | 37 | 108 | 108 | 0 | 35 | 24 | 73 | 30 | 0 | 0 | 0 |  | 906 | 0 | 145 | 0 | 16 | 229 | 0 | 0 | 0 | 0 | 8 | 88 | 15 | 16 | 0 | 0 | 0 | 31 | 31 | 46 | 0 | 0 | 32 | 8 | 34 | 17 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 151 | 0 | 0 | 212 | 0 | 95 | 143 | 0 | 257 | 17 | 176 | 50 | 67 | 55 | 0 | 7 | 55 | 490 | 208 | 0 | 0 | 3 | 71 | 17 | 0 | 0 |  | 6543 | 3957 | 10500 | 3827 | 906 | 1454 | 751 | 1735 | 740 | 105 | 441 | 496 | 104 | 153 | 1106 | 95.73
14:00 | 0 | 0 | 0 | 180 | 295 | 78 | 0 | 397 | 232 |  | 0 | 225 | 0 | 7 | 0 | 25 | 0 | 0 | 0 | 8 | 8 | 30 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 19 | 25 | 8 | 33 | 28 | 42 | 0 | 36 | 70 | 25 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 17 | 33 | 12 | 19 | 15 | 7 | 0 | 0 | 0 | 300 | 300 | 192 | 8 | 122 | 35 | 46 | 0 | 51 | 0 | 38 | 8 | 19 | 9 | 16 | 12 | 108 | 60 | 0 | 20 | 2 | 43 | 41 | 0 | 0 | 0 | 0 | 55 | 10 | 0 | 208 | 0 | 0 | 9 | 290 | 0 | 0 | 0 | 82 | 250 | 50 | 47 | 50 | 43 | 4 | 21 | 54 | 107 | 402 | 48 | 88 | 69 | 4 | 69 | 36 | 55 | 17 | 38 | 20 | 366 | 0 | 56 | 108 | 108 | 0 | 35 | 14 | 69 | 55 | 0 | 0 | 0 |  | 907 | 0 | 135 | 0 | 16 | 226 | 0 | 0 | 0 | 0 | 8 | 88 | 11 | 16 | 0 | 0 | 0 | 31 | 35 | 52 | 0 | 0 | 32 | 8 | 34 | 17 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 152 | 0 | 0 | 211 | 0 | 65 | 142 | 0 | 257 | 17 | 177 | 50 | 67 | 55 | 0 | 7 | 55 | 490 | 218 | 0 | 0 | 2 | 63 | 17 | 0 | 0 |  | 6411 | 3922 | 10333 | 3753 | 907 | 1459 | 592 | 1784 | 740 | 106 | 437 | 506 | 108 | 152 | 1351.9505 | 95.73
15:00 | 0 | 0 | 0 | 180 | 295 | 78 | 0 | 397 | 233 |  | 0 | 225 | 0 | 8 | 0 | 25 | 0 | 0 | 0 | 8 | 8 | 30 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 19 | 25 | 8 | 33 | 20 | 42 | 0 | 33 | 70 | 95 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 27 | 17 | 33 | 12 | 19 | 15 | 6 | 0 | 0 | 0 | 300 | 305 | 187 | 8 | 122 | 42 | 48 | 0 | 51 | 0 | 37 | 8 | 22 | 9 | 18 | 12 | 102 | 61 | 0 | 20 | 2 | 43 | 41 | 0 | 0 | 0 | 0 | 60 | 10 | 0 | 215 | 0 | 0 | 9 | 310 | 0 | 0 | 0 | 82 | 300 | 90 | 47 | 81 | 46 | 5 | 21 | 96 | 110 | 405 | 48 | 88 | 69 | 4 | 52 | 36 | 55 | 17 | 38 | 20 | 378 | 0 | 44 | 108 | 108 | 0 | 35 | 15 | 72 | 55 | 0 | 0 | 0 |  | 906 | 0 | 135 | 0 | 0 | 224 | 0 | 0 | 0 | 0 | 8 | 88 | 13 | 49 | 0 | 0 | 0 | 31 | 35 | 52 | 0 | 0 | 24 | 8 | 14 | 17 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 152 | 0 | 0 | 207 | 0 | 95 | 141 | 0 | 243 | 17 | 178 | 50 | 67 | 55 | 0 | 6 | 55 | 0 | 222 | 0 | 36 | 4 | 27 | 17 | 0 | 0 |  | 6672 | 3437 | 10109 | 3854 | 906 | 1473 | 744 | 1872 | 250 | 103 | 431 | 474 | 102 | 107 | 1453.3238 | 95.73
16:00 | 0 | 0 | 0 | 180 | 280 | 78 | 0 | 397 | 226 |  | 0 | 225 | 0 | 7 | 0 | 25 | 0 | 0 | 0 | 8 | 8 | 78 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 0 | 25 | 20 | 33 | 24 | 42 | 0 | 34 | 70 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 17 | 33 | 12 | 19 | 15 | 8 | 0 | 0 | 0 | 300 | 300 | 180 | 8 | 121 | 41 | 53 | 0 | 51 | 0 | 37 | 8 | 22 | 9 | 25 | 20 | 106 | 63 | 0 | 20 | 2 | 43 | 41 | 0 | 0 | 0 | 0 | 60 | 10 | 0 | 208 | 0 | 0 | 9 | 310 | 0 | 0 | 0 | 97 | 300 | 80 | 47 | 81 | 59 | 3 | 21 | 133 | 124 | 399 | 48 | 88 | 69 | 3 | 52 | 36 | 50 | 17 | 40 | 20 | 377 | 0 | 16 | 108 | 108 | 0 | 35 | 8 | 72 | 55 | 0 | 0 | 0 |  | 906 | 0 | 135 | 0 | 0 | 224 | 0 | 0 | 0 | 0 | 8 | 88 | 16 | 80 | 0 | 0 | 0 | 31 | 35 | 52 | 0 | 0 | 24 | 8 | 26 | 17 | 0 | 11 | 0 | 0 | 251 | 0 | 0 | 153 | 0 | 0 | 210 | 0 | 92 | 141 | 0 | 246 | 25 | 178 | 77 | 71 | 54 | 0 | 4 | 90 | 0 | 220 | 0 | 64 | 2 | 11 | 17 | 0 | 0 |  | 6764 | 3567 | 10331 | 3831 | 906 | 1477 | 731 | 2116 | 251 | 104 | 434 | 536 | 106 | 49 | 1215.5574 | 95.74
17:00 | 0 | 0 | 0 | 180 | 285 | 78 | 0 | 393 | 225 |  | 0 | 225 | 0 | 8 | 0 | 15 | 0 | 0 | 0 | 7 | 8 | 110 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 24 | 33 | 15 | 42 | 0 | 35 | 70 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 17 | 33 | 12 | 19 | 15 | 15 | 0 | 0 | 0 | 300 | 270 | 173 | 8 | 122 | 40 | 51 | 0 | 51 | 0 | 46 | 8 | 22 | 9 | 25 | 20 | 104 | 68 | 0 | 20 | 1 | 44 | 41 | 0 | 0 | 0 | 0 | 60 | 10 | 0 | 210 | 0 | 0 | 9 | 305 | 0 | 0 | 0 | 225 | 0 | 95 | 47 | 50 | 76 | 2 | 21 | 158 | 127 | 402 | 48 | 88 | 74 | 1 | 52 | 36 | 55 | 17 | 100 | 20 | 385 | 17 | 14 | 128 | 108 | 0 | 35 | 2 | 73 | 55 | 0 | 0 | 0 |  | 907 | 0 | 140 | 0 | 0 | 227 | 0 | 0 | 0 | 0 | 8 | 88 | 17 | 80 | 0 | 0 | 0 | 31 | 35 | 52 | 0 | 8 | 32 | 8 | 33 | 18 | 0 | 11 | 0 | 0 | 251 | 0 | 0 | 152 | 0 | 0 | 170 | 0 | 96 | 141 | 0 | 252 | 36 | 178 | 94 | 89 | 55 | 0 | 2 | 95 | 0 | 219 | 0 | 81 | 1 | 11 | 17 | 0 | 0 |  | 6766 | 3635 | 10401 | 3835 | 907 | 1483 | 419 | 2484 | 251 | 105 | 397 | 552 | 104 | 34 | 966.7322 | 95.74
18:00 | 0 | 0 | 0 | 180 | 285 | 78 | 0 | 391 | 224 |  | 0 | 225 | 0 | 7 | 0 | 25 | 0 | 0 | 0 | 7 | 8 | 110 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 24 | 33 | 16 | 42 | 0 | 36 | 70 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 17 | 33 | 22 | 13 | 15 | 8 | 0 | 0 | 0 | 300 | 265 | 180 | 8 | 120 | 40 | 53 | 0 | 51 | 0 | 47 | 8 | 22 | 9 | 33 | 20 | 78 | 70 | 0 | 20 | 0 | 44 | 41 | 0 | 0 | 0 | 0 | 60 | 10 | 0 | 210 | 0 | 0 | 9 | 290 | 0 | 0 | 0 | 241 | 0 | 50 | 130 | 50 | 132 | 0 | 21 | 181 | 125 | 400 | 77 | 88 | 105 | 0 | 52 | 36 | 51 | 17 | 113 | 20 | 378 | 17 | 2 | 162 | 108 | 0 | 35 | 1 | 73 | 55 | 0 | 0 | 0 |  | 906 | 0 | 145 | 0 | 0 | 227 | 0 | 0 | 9 | 0 | 8 | 88 | 16 | 80 | 0 | 0 | 0 | 31 | 38 | 52 | 0 | 8 | 32 | 8 | 33 | 18 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 152 | 0 | 0 | 170 | 0 | 10 | 141 | 0 | 264 | 36 | 80 | 94 | 98 | 55 | 0 | 1 | 95 | 0 | 220 | 0 | 81 | 0 | 1 | 72 | 0 | 0 |  | 6951 | 3530 | 10481 | 3840 | 906 | 1474 | 190 | 2840 | 250 | 106 | 397 | 565 | 78 | 5 | 662.6124 | 95.74
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 285 | 78 | 0 | 390 | 217 |  | 0 | 225 | 0 | 11 | 0 | 30 | 0 | 0 | 0 | 18 | 16 | 110 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 24 | 33 | 16 | 42 | 0 | 36 | 70 | 105 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 51 | 33 | 90 | 25 | 15 | 20 | 0 | 0 | 0 | 300 | 305 | 175 | 8 | 120 | 41 | 52 | 0 | 51 | 0 | 45 | 8 | 22 | 9 | 33 | 20 | 82 | 72 | 0 | 20 | 0 | 44 | 41 | 0 | 0 | 0 | 0 | 62 | 60 | 0 | 221 | 0 | 0 | 9 | 310 | 0 | 0 | 0 | 250 | 295 | 96 | 177 | 98 | 145 | 0 | 90 | 198 | 130 | 391 | 78 | 88 | 105 | 0 | 207 | 36 | 53 | 114 | 110 | 51 | 393 | 17 | 0 | 162 | 108 | 0 | 35 | 0 | 73 | 55 | 0 | 0 | 0 |  | 906 | 0 | 140 | 0 | 16 | 226 | 0 | 0 | 39 | 34 | 8 | 88 | 24 | 80 | 0 | 0 | 0 | 31 | 38 | 80 | 0 | 42 | 40 | 16 | 33 | 20 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 152 | 0 | 0 | 177 | 0 | 25 | 143 | 0 | 268 | 53 | 68 | 94 | 105 | 55 | 0 | 0 | 95 | 0 | 222 | 0 | 85 | 0 | 0 | 72 | 0 | 0 |  | 8059 | 3736 | 11795 | 3898 | 906 | 1564 | 582 | 3477 | 250 | 106 | 403 | 704 | 82 | 0 | 1018.3404 | 95.75
19:30 | 0 | 0 | 0 | 180 | 285 | 79 | 0 | 395 | 217 |  | 0 | 225 | 0 | 32 | 0 | 30 | 0 | 0 | 0 | 37 | 32 | 110 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 24 | 33 | 16 | 42 | 0 | 37 | 70 | 105 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 33 | 51 | 33 | 90 | 40 | 15 | 21 | 0 | 0 | 0 | 300 | 270 | 180 | 8 | 120 | 42 | 52 | 0 | 51 | 0 | 47 | 8 | 22 | 9 | 33 | 20 | 72 | 72 | 0 | 22 | 0 | 43 | 41 | 0 | 0 | 0 | 0 | 61 | 78 | 0 | 221 | 0 | 0 | 9 | 265 | 8 | 0 | 0 | 260 | 198 | 97 | 177 | 98 | 145 | 0 | 90 | 200 | 137 | 403 | 77 | 88 | 105 | 0 | 212 | 36 | 55 | 114 | 105 | 95 | 398 | 34 | 0 | 162 | 108 | 0 | 35 | 0 | 74 | 55 | 0 | 0 | 0 |  | 905 | 0 | 140 | 0 | 16 | 229 | 0 | 0 | 50 | 40 | 8 | 88 | 27 | 96 | 0 | 0 | 0 | 31 | 40 | 80 | 0 | 42 | 40 | 16 | 33 | 21 | 0 | 11 | 0 | 0 | 251 | 0 | 0 | 152 | 0 | 0 | 216 | 0 | 96 | 146 | 0 | 281 | 53 | 100 | 94 | 105 | 55 | 0 | 0 | 95 | 0 | 219 | 0 | 116 | 0 | 0 | 72 | 0 | 0 |  | 8092 | 3964 | 12056 | 3902 | 905 | 1553 | 589 | 3677 | 251 | 107 | 445 | 771 | 72 | 0 | 869.9668 | 0
20:00 | 0 | 0 | 0 | 180 | 285 | 79 | 0 | 398 | 208 |  | 0 | 225 | 0 | 31 | 0 | 30 | 0 | 0 | 0 | 49 | 32 | 127 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 22 | 33 | 16 | 42 | 0 | 37 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 34 | 34 | 33 | 90 | 38 | 15 | 17 | 0 | 0 | 0 | 300 | 270 | 183 | 8 | 122 | 42 | 54 | 0 | 51 | 0 | 47 | 8 | 22 | 9 | 33 | 20 | 80 | 85 | 0 | 22 | 0 | 43 | 41 | 0 | 0 | 0 | 0 | 64 | 78 | 0 | 221 | 0 | 0 | 9 | 260 | 8 | 0 | 0 | 261 | 208 | 98 | 180 | 98 | 149 | 0 | 90 | 200 | 135 | 402 | 78 | 88 | 105 | 0 | 214 | 36 | 55 | 114 | 105 | 96 | 400 | 34 | 0 | 162 | 108 | 0 | 35 | 0 | 73 | 55 | 0 | 0 | 0 |  | 906 | 0 | 145 | 0 | 16 | 231 | 0 | 0 | 45 | 67 | 8 | 88 | 28 | 96 | 0 | 0 | 0 | 31 | 40 | 80 | 0 | 42 | 40 | 16 | 33 | 21 | 0 | 11 | 0 | 0 | 251 | 0 | 0 | 152 | 0 | 0 | 217 | 0 | 96 | 146 | 0 | 286 | 53 | 100 | 94 | 105 | 55 | 0 | 0 | 95 | 0 | 219 | 0 | 116 | 0 | 0 | 72 | 0 | 0 |  | 8142 | 4001 | 12143 | 3935 | 906 | 1543 | 600 | 3695 | 251 | 107 | 448 | 795 | 80 | 0 | 974.1048 | 95.75
21:00 | 0 | 0 | 0 | 180 | 290 | 80 | 0 | 391 | 206 |  | 0 | 225 | 0 | 32 | 0 | 30 | 0 | 0 | 0 | 49 | 32 | 127 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 22 | 33 | 16 | 42 | 0 | 37 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 34 | 51 | 33 | 90 | 45 | 15 | 32 | 0 | 0 | 0 | 300 | 270 | 188 | 8 | 123 | 42 | 55 | 0 | 51 | 0 | 47 | 8 | 22 | 10 | 33 | 20 | 78 | 98 | 0 | 22 | 0 | 43 | 41 | 0 | 0 | 0 | 0 | 62 | 81 | 0 | 221 | 0 | 0 | 9 | 280 | 8 | 0 | 0 | 277 | 300 | 98 | 180 | 98 | 149 | 0 | 90 | 200 | 140 | 403 | 78 | 88 | 105 | 0 | 214 | 36 | 55 | 114 | 105 | 98 | 388 | 33 | 0 | 162 | 108 | 0 | 35 | 0 | 74 | 55 | 0 | 0 | 0 |  | 907 | 0 | 145 | 0 | 16 | 230 | 0 | 0 | 45 | 72 | 8 | 88 | 27 | 110 | 0 | 0 | 0 | 31 | 41 | 80 | 0 | 42 | 40 | 16 | 33 | 21 | 0 | 11 | 0 | 0 | 251 | 0 | 0 | 152 | 0 | 0 | 218 | 0 | 96 | 148 | 0 | 308 | 53 | 133 | 94 | 105 | 55 | 0 | 0 | 95 | 70 | 220 | 0 | 116 | 0 | 0 | 72 | 0 | 0 |  | 8303 | 4149 | 12452 | 3942 | 907 | 1603 | 725 | 3720 | 321 | 107 | 448 | 819 | 78 | 0 | 919.7319 | 95.75
22:00 | 0 | 0 | 0 | 180 | 290 | 80 | 0 | 377 | 205 |  | 0 | 225 | 0 | 20 | 0 | 30 | 0 | 0 | 0 | 48 | 32 | 127 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 24 | 33 | 16 | 42 | 0 | 37 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 34 | 51 | 33 | 83 | 0 | 15 | 32 | 0 | 0 | 0 | 300 | 275 | 177 | 8 | 82 | 42 | 55 | 0 | 51 | 0 | 48 | 8 | 22 | 10 | 33 | 20 | 82 | 98 | 0 | 22 | 0 | 43 | 41 | 0 | 0 | 0 | 0 | 62 | 81 | 0 | 221 | 0 | 0 | 9 | 310 | 8 | 0 | 0 | 278 | 188 | 70 | 180 | 50 | 149 | 0 | 90 | 200 | 142 | 403 | 79 | 88 | 105 | 0 | 214 | 36 | 55 | 114 | 115 | 100 | 393 | 33 | 0 | 162 | 108 | 0 | 35 | 0 | 73 | 55 | 0 | 0 | 0 |  | 907 | 0 | 155 | 0 | 16 | 230 | 0 | 0 | 43 | 71 | 8 | 88 | 28 | 110 | 0 | 0 | 0 | 31 | 41 | 80 | 0 | 42 | 40 | 16 | 33 | 21 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 152 | 0 | 0 | 215 | 0 | 60 | 149 | 0 | 302 | 54 | 140 | 94 | 105 | 55 | 0 | 0 | 95 | 170 | 220 | 0 | 127 | 0 | 0 | 72 | 0 | 0 |  | 8045 | 4231 | 12276 | 3899 | 907 | 1627 | 508 | 3682 | 420 | 107 | 445 | 814 | 82 | 0 | 1035.8503 | 95.76
23:00 | 0 | 0 | 0 | 180 | 300 | 82 | 0 | 372 | 205 |  | 0 | 225 | 0 | 16 | 0 | 30 | 0 | 0 | 0 | 48 | 32 | 127 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 24 | 33 | 16 | 42 | 0 | 38 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 34 | 34 | 33 | 48 | 3 | 15 | 38 | 0 | 0 | 0 | 300 | 330 | 162 | 8 | 82 | 42 | 55 | 0 | 51 | 0 | 48 | 8 | 22 | 10 | 33 | 20 | 76 | 98 | 0 | 22 | 0 | 43 | 41 | 0 | 0 | 0 | 0 | 59 | 81 | 0 | 221 | 0 | 0 | 9 | 305 | 8 | 0 | 0 | 278 | 301 | 98 | 181 | 95 | 149 | 0 | 90 | 200 | 142 | 403 | 79 | 88 | 105 | 0 | 52 | 36 | 55 | 114 | 115 | 100 | 386 | 29 | 0 | 162 | 108 | 0 | 35 | 0 | 73 | 55 | 0 | 0 | 0 |  | 906 | 0 | 160 | 0 | 16 | 228 | 0 | 0 | 42 | 71 | 8 | 0 | 29 | 110 | 0 | 0 | 0 | 31 | 30 | 80 | 0 | 42 | 40 | 16 | 33 | 21 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 152 | 0 | 0 | 216 | 0 | 80 | 149 | 0 | 303 | 54 | 159 | 94 | 105 | 55 | 0 | 0 | 95 | 210 | 10 | 0 | 145 | 0 | 0 | 72 | 0 | 0 |  | 8046 | 4023 | 12069 | 3851 | 906 | 1422 | 733 | 3499 | 460 | 108 | 444 | 786 | 76 | 0 | 1134.4588 | 95.76
24:00 | 0 | 0 | 0 | 180 | 300 | 85 | 0 | 379 | 220 |  | 0 | 225 | 0 | 8 | 0 | 30 | 0 | 0 | 0 | 14 | 8 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 24 | 33 | 16 | 42 | 0 | 38 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 34 | 51 | 33 | 11 | 6 | 15 | 38 | 0 | 0 | 0 | 300 | 300 | 148 | 8 | 82 | 42 | 55 | 0 | 51 | 0 | 48 | 8 | 22 | 10 | 33 | 20 | 84 | 99 | 0 | 22 | 0 | 43 | 41 | 0 | 0 | 0 | 0 | 61 | 78 | 0 | 221 | 0 | 0 | 9 | 320 | 8 | 0 | 0 | 130 | 302 | 98 | 48 | 97 | 53 | 0 | 90 | 200 | 137 | 404 | 49 | 88 | 37 | 0 | 52 | 36 | 55 | 114 | 60 | 100 | 390 | 17 | 0 | 150 | 108 | 0 | 35 | 0 | 74 | 55 | 0 | 0 | 0 |  | 907 | 0 | 155 | 0 | 16 | 228 | 0 | 0 | 36 | 68 | 8 | 0 | 28 | 110 | 0 | 0 | 0 | 31 | 25 | 80 | 0 | 42 | 40 | 8 | 33 | 21 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 152 | 0 | 0 | 212 | 0 | 96 | 150 | 0 | 323 | 35 | 177 | 50 | 105 | 55 | 0 | 0 | 55 | 230 | 0 | 0 | 146 | 0 | 0 | 0 | 0 | 0 |  | 7306 | 3883 | 11189 | 3818 | 907 | 1461 | 770 | 2659 | 480 | 108 | 440 | 674 | 84 | 0 | 1761.1298 | 95.76
KWH | 0 | 0 | 0 | 4347000 | 7007373 | 1937227 | 0 | 7630840 | 5944000 |  | 0 | 5125250 | 0 | 270720 | 0 | 700616 | 0 | 0 | 0 | 371520 | 298368 | 1351680 | 0 | 0 | 0 | 0 | 857160 | 1329281 | 961028 | 359244 | 600000 | 523080 | 783000 | 594200 | 994560 | 0 | 856495 | 1688000 | 2500000 | 0 | 602789 | 0 | 0 | 0 | 0 |  | 298080 | 632544 | 753896 | 790440 | 611520 | 451200 | 352 | 572640 | 0 | 0 | 0 | 7519700 | 7069000 | 4495000 | 200727 | 2864100 | 911952 | 1257600 | 0 | 1201175 | 0 | 1080864 | 203947 | 494928 | 234540 | 690000 | 464340 | 2051520 | 1888320 | 0 | 470520 | 15900 | 1018000 | 979838 | 0 | 0 | 0 | 0 | 1416864 | 668160 | 0 | 5225890 | 0 | 306760 | 199980 | 7391000 | 133128 | 0 | 0 | 3158944 | 6056032 | 2102871 | 1920000 | 2041405 | 1746576 | 66285 | 882240 | 2284320 | 3064436 | 9560000 | 1347600 | 2043600 | 1984690 | 30721 | 1630909 | 912923 | 1316430 | 998640 | 1463280 | 949440 | 9276100 | 305280 | 389610 | 2093760 | 2608200 | 0 | 889560 | 169284 | 1764480 | 1282680 | 0 | 0 | 0 |  | 21895272 | 0 | 3774816 | 0 | 318720 | 5433600 | 0 | 0 | 387360 | 733440 | 187875 | 1961000 | 444592 | 944256 | 0 | 0 | 0 | 742192 | 742244 | 1364440 | 0 | 242380 | 676290 | 223344 | 739079 | 441600 | 0 | 262854 | 0 | 0 | 6099400 | 0 | 0 | 3946091 | 0 | 0 | 5229527 | 0 | 1925760 | 3808200 | 0 | 7080654 | 479520 | 3797363 | 1686432 | 2278368 | 1333478 | 0 | 45440 | 1639104 | 8721200 | 5001873 | 0 | 967200 | 35820 | 341280 | 948288 | 0 | 0 |  | 166538152 | 96880352 | 263418504 | 92810270 | 21895272 | 37773238 | 15923431 | 54638182 | 14820600 | 2544495 | 10663127 | 9204029 | 2051520 | 1094340 | 0
Fuel Cost | 0 | 0 | 0 | 6477030 | 7848257.76 | 2576511.91 | 0 | 8012382 | 6419520 |  | 0 | 5586522.5 | 0 | 3026649.6 | 0 | 9283162 | 0 | 0 | 0 | 5431622.4 | 4198037.76 | 21910732.8 | 0 | 0 | 0 | 0 | 10903075.2 | 17945293.5 | 12887385.48 | 269433 | 450000 | 0 | 0 | 0 | 16917465.6 | 0 | 231253.65 | 455760 | 4725000 | 0 | 9855600.15 | 0 | 0 | 0 | 0 |  | 3889944 | 10550833.92 | 12831309.92 | 10678844.4 | 7754073.6 | 5220384 | 447.04 | 1906891.2 | 0 | 0 | 0 | 8346867 | 7705210 | 5214200 | 258937.83 | 3494202 | 1030505.76 | 1873824 | 0 | 2005962.25 | 0 | 18666521.28 | 2743087.15 | 678051.36 | 175905 | 1207500 | 348255 | 14729913.6 | 2058268.8 | 0 | 639907.2 | 253446 | 1394660 | 1293386.16 | 0 | 0 | 0 | 0 | 2748716.16 | 1523404.8 | 0 | 5278148.9 | 0 | 457072.4 | 395960.4 | 7391000 | 99846 | 0 | 0 | 43119585.6 | 126934430.72 | 43466343.57 | 25881600 | 42195841.35 | 24190077.6 | 774871.65 | 9104716.8 | 31203811.2 | 40665065.72 | 8795200 | 16386816 | 29550456 | 25106328.5 | 0 | 19146871.66 | 9941731.47 | 13993650.9 | 13551544.8 | 18861679.2 | 11184403.2 | 8534012 | 3953376 | 5629864.5 | 26569814.4 | 29681316 | 0 | 11617653.6 | 2022943.8 | 26414265.6 | 16892895.6 | 0 | 0 | 0 |  | 65685816 | 0 | 4227793.92 | 0 | 3317875.2 | 89654400 | 0 | 0 | 6976353.6 | 13201920 | 2699763.75 | 2196320 | 862508.48 | 10292390.4 | 0 | 0 | 0 | 12446559.84 | 12981847.56 | 21339841.6 | 0 | 4013812.8 | 11436063.9 | 3044178.72 | 12468262.73 | 914112 | 0 | 198980.478 | 0 | 0 | 32265826 | 0 | 0 | 4577465.56 | 0 | 0 | 91307541.42 | 0 | 40402444.8 | 4417512 | 0 | 7009847.46 | 6444748.8 | 79630702.11 | 19950490.56 | 32922417.6 | 16935170.6 | 0 | 502112 | 19898722.56 | 78578012 | 5101910.46 | 0 | 7157280 | 405124.2 | 4003214.4 | 14537255.04 | 0 | 0 |  | 985627349.88 | 744006598.548 | 1729633948.428 | 102443463.098 | 65685816 | 44283985.69 | 332629762.55 | 708966390.72 | 110843838 | 687013.65 | 180961941.42 | 154810247.15 | 14729913.6 | 13591576.55 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 300 | 82 | 0 | 258 | 307 |  | 0 | 225 | 0 | 7 | 0 | 30 | 0 | 0 | 0 | 8 | 8 | 32 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 19 | 25 | 26 | 33 | 30 | 42 | 0 | 37 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 25 | 17 | 33 | 7 | 19 | 15 | 8 | 0 | 0 | 0 | 280 | 260 | 183 | 8 | 124 | 36 | 50 | 0 | 43 | 0 | 47 | 8 | 19 | 9 | 21 | 20 | 90 | 63 | 0 | 20 | 2 | 43 | 41 | 0 | 0 | 0 | 0 | 59 | 10 | 0 | 221 | 0 | 0 | 9 | 300 | 0 | 0 | 0 | 82 | 300 | 90 | 48 | 90 | 43 | 11 | 21 | 34 | 117 | 395 | 49 | 70 | 69 | 2 | 51 | 36 | 55 | 17 | 39 | 20 | 382 | 17 | 53 | 35 | 108 | 0 | 35 | 21 | 73 | 55 | 0 | 0 | 0 |  | 906 | 0 | 155 | 0 | 16 | 228 | 0 | 0 | 0 | 0 | 8 | 88 | 16 | 0 | 0 | 0 | 0 | 31 | 34 | 46 | 0 | 0 | 32 | 8 | 34 | 18 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 152 | 0 | 0 | 209 | 0 | 94 | 147 | 0 | 279 | 17 | 177 | 50 | 67 | 56 | 0 | 4 | 55 | 490 | 218 | 0 | 0 | 5 | 60 | 17 | 0 | 0 |  | 10459 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 290 | 80 | 0 | 391 | 206 | 0 | 0 | 225 | 0 | 32 | 0 | 30 | 0 | 0 | 0 | 49 | 32 | 127 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 22 | 33 | 16 | 42 | 0 | 37 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 12 | 34 | 51 | 33 | 90 | 45 | 15 | 32 | 0 | 0 | 0 | 300 | 270 | 188 | 8 | 123 | 42 | 55 | 0 | 51 | 0 | 47 | 8 | 22 | 10 | 33 | 20 | 78 | 98 | 0 | 22 | 0 | 43 | 41 | 0 | 0 | 0 | 0 | 62 | 81 | 0 | 221 | 0 | 0 | 9 | 280 | 8 | 0 | 0 | 277 | 300 | 98 | 180 | 98 | 149 | 0 | 90 | 200 | 140 | 403 | 78 | 88 | 105 | 0 | 214 | 36 | 55 | 114 | 105 | 98 | 388 | 33 | 0 | 162 | 108 | 0 | 35 | 0 | 74 | 55 | 0 | 0 | 0 |  | 907 | 0 | 145 | 0 | 16 | 230 | 0 | 0 | 45 | 72 | 8 | 88 | 27 | 110 | 0 | 0 | 0 | 31 | 41 | 80 | 0 | 42 | 40 | 16 | 33 | 21 | 0 | 11 | 0 | 0 | 251 | 0 | 0 | 152 | 0 | 0 | 218 | 0 | 96 | 148 | 0 | 308 | 53 | 133 | 94 | 105 | 55 | 0 | 0 | 95 | 70 | 220 | 0 | 116 | 0 | 0 | 72 | 0 | 0 |  | 12452 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 300 | 83 | 0 | 390 | 300 | 0 | 0 | 225 | 0 | 32 | 0 | 30 | 0 | 0 | 0 | 50 | 32 | 130 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 25 | 33 | 30 | 42 | 0 | 37 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 12 | 34 | 51 | 33 | 90 | 45 | 15 | 30 | 0 | 0 | 0 | 320 | 310 | 190 | 8 | 130 | 42 | 55 | 0 | 51 | 0 | 47 | 8 | 22 | 10 | 33 | 20 | 166 | 90 | 0 | 22 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 64 | 80 | 0 | 220 | 0 | 30 | 10 | 320 | 12 | 11 | 0 | 285 | 300 | 100 | 180 | 0 | 149 | 0 | 90 | 200 | 142 | 400 | 78 | 88 | 105 | 0 | 214 | 36 | 55 | 114 | 105 | 100 | 400 | 33 | 0 | 162 | 108 | 0 | 35 |  | 75 | 55 |  |  |  |  | 920 | 0 | 155 | 0 | 32 | 225 | 0 | 0 | 43 | 70 | 8 | 88 | 20 | 110 | 0 | 0 | 0 | 32 | 40 | 80 | 0 | 42 | 40 | 16 | 34 | 21 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 150 | 0 | 0 | 220 | 0 | 94 | 150 | 0 | 300 | 52 | 0 | 90 | 105 | 56 | 0 | 0 | 95 | 620 | 0 |  | 116 |  |  | 72
Forecast for Day | 0 | 0 | 0 | 180 | 300 | 83 | 0 | 350 | 300 | 0 | 0 | 225 | 0 | 15 | 0 | 30 | 0 | 0 | 0 | 8 | 8 | 36 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 22 | 25 | 25 | 33 | 30 | 42 | 0 | 37 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 12 | 25 | 17 | 33 | 12 | 19 | 15 | 15 | 0 | 0 | 0 | 280 | 280 | 190 | 8 | 130 | 42 | 55 | 0 | 51 | 0 | 47 | 8 | 22 | 10 | 33 | 20 | 143 | 60 | 0 | 22 | 1.6 | 43 | 0 | 0 | 0 | 0 | 0 | 62 | 10 | 0 | 220 | 0 | 30 | 10 | 300 | 12 | 11 | 0 | 82 | 300 | 90 | 48 | 0 | 43 | 20 | 21 | 34 | 118 | 400 | 48 | 88 | 68 | 5 | 52 | 36 | 55 | 17 | 38 | 20 | 400 | 17 | 50 | 35 | 108 | 0 | 35 | 30 | 74 | 55 |  |  |  |  | 920 | 0 | 155 | 0 | 16 | 225 | 0 | 0 | 0 | 0 | 8 | 88 | 15 | 16 | 0 | 0 | 0 | 32 | 40 | 50 | 0 | 42 | 32 | 8 | 33 | 21 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 150 | 0 | 0 | 220 | 0 | 94 | 150 | 0 | 300 | 17 | 50 | 50 | 105 | 56 | 0 | 8 | 55 | 620 | 225 |  | 50 | 6 | 100 | 17
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 300 | 92 | 0 | 370 | 268 | 0 | 0 | 225 | 0 | 8 | 0 | 30 | 0 | 0 | 0 | 8 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 22 | 25 | 25 | 33 | 33 | 42 | 0 | 37 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 12 | 25 | 17 | 33 | 13 | 6 | 15 | 38 | 0 | 0 | 0 | 280 | 260 | 190 | 8 | 0 | 43 | 51 | 0 | 51 | 0 | 47 | 8 | 22 | 10 | 33 | 20 | 70 | 84 | 0 | 20 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 60 | 25 | 0 | 221 | 0 | 0 | 9 | 310 | 0 | 0 | 0 | 80 | 300 | 90 | 48 | 0 | 35 | 1 | 21 | 50 | 135 | 401 | 49 | 88 | 17 | 3 | 50 | 36 | 55 | 17 | 28 | 20 | 400 | 6 | 10 | 35 | 108 | 0 | 35 | 14 | 0 | 55 | 0 | 0 | 0 | 0 | 903 | 0 | 175 | 0 | 0 | 228 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 110 | 0 | 0 | 0 | 30 | 0 | 45 | 0 | 42 | 0 | 8 | 14 | 21 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 152 | 0 | 0 | 190 | 0 | 90 | 162 | 0 | 354 | 0 | 140 | 50 | 105 | 56 | 0 | 2 | 55 | 0 | 0 | 0 | 146 | 2 | 17 | 0 | 0 | 0 | 0 |  |  |  |  | 90428769 |  | 0
90428769
| Minimum Generation |  | 10280 | 7:00
| Highest Generation |  | 12452 | 21:00
| Day Peak Generation |  | 10459 | 10:00
| Evening Peak Generation |  | 12452 | 21:00
| HVDC Max Flow |  | 907 | 1:00
| HVDC EvPeak Flow |  | 907 | 21:00
| Load factor L.F |  | 88.14% | [161 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2022-08-12
Till now the maximum generation is : - |  |  | 14782 | 21:00 | Hrs on | 2022-04-16
The Summary of Yesterday's |  | 2022-08-11 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 10459 | MW Hour : | 10:00 | Min. Gen. at | 8:00 | 9620 | MW
Evening Peak Generation : |  | 12452 | MW Hour : | 21:00 | Available Max Generation : |  | 12925 | MW
E.P. Demand (at gen end) : |  | 13450 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 14200 | MW
Maximum Generation : |  | 12452 | MW Hour : | 21:00 | Reserve(Generation end) |  | - | MW
Total Gen. (MKWH) : |  | 263.4185 | System Load Factor : | 88.14% | Load Shed : |  | 1175 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | 98 | MW at | 19:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2022-08-12
Actual : | 95.79 | Ft.(MSL) , | Rule curve : | 92.52 | Ft.( MSL )
Gas Consumed : | Total = | 963.93 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 146727448.788
: |  | Coal : | 110843838 | Oil : | 1377368341.84 | Total : | 1634939628.628
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 190 | 4560:00 | 4547.5118 |  |  | 267 | 4.398%
Chittagong Area | 0 | 0:00 | 1287.6983 |  |  | 140 | 6.213%
Khulna Area | 175 | 4200:00 | 1699.9188 |  |  | 176 | 5.412%
Rajshahi Area | 150 | 3600:00 | 1508.8579 |  |  | 158 | 5.633%
Cumilla Area | 175 | 4200:00 | 1283.7724 |  |  | 105 | 7.011%
Mymensingh Area | 190 | 4560:00 | 1061.3042 |  |  | 155 | 9.422%
Sylhet Area | 40 | 960:00 | 473.7264 |  |  | 56 | 6.333%
Barisal Area | 0 | 0:00 | 386.0478 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 837.5274 |  |  | 118 | 7.164%
Total | 920 |  | 13086.365 |  |  | 1175
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-2 |  | 10) Payra unit-2
2) Ghorasal-3,4
3) Ashuganj-5
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
7) Sikalbaha 225 MW
8) Shajibazar 330 MW
9) Siddhirganj 335 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Norail 132/33 kV T-1 transformer was under shut down from 09:56 to 11:55 due to R/H maintenance.
b) Chapainawabganj-Rohanpur 132 kV Ckt was shut down at 09:31 for D/W.
c) Ghorashal 230 kV GIS Bus Coupler was under shut down from 11:54 to 15:49 for D/W.
d) Madanganj-Munshiganj 132 kV Ckt-1 was under shut down from 12:05 to 13:26 for D/W.
e) Agargaon-Satmosjid 132 kV Ckt-1 was under shut down from 12:35 to 22:38 for D/W.
f) Raozan Unit-1 tripped at 13:29 due to problem at control system.
g) Payra 1320 MW unit-1 tripped at 13:59 due to zero power protection and was synchronized at 20:12.
h) Bhola Natun Bidyut ST was shutdown at 22:50 & GT at 23:05 due to gas field work.
i) Purbasadipur 132/33 T-1 & T-2 transformers tripped at 00:05(12/08/2022) due to Kaharol 33 kV PBS feeder | [5 empty] | About 79 MW power interruption occurred under
fault and were switched on at 00:28(12/08/2022). | [5 empty] | Purbasadipur S/S area from 00:05(12/08/2022) to 00:28.
j) Kabirpur-Kodda 132 kV Ckt-2 was shut down at 06:40(12/08/2022) for C/M.
k) Aminbazar-Mirpur 132 kV Ckt-2 was shut down at 06:44(12/08/2022) for C/M.
l) Payra 1320 MW unit-1 tripped at 04:01(12/08/2022) showing Differential protection(87T) at unit transformer.
m) Chandpur Desh P.P.-Ramganj 132 kV Ckt tripped at 07:13(12/08/2022).
n) Norail 132/33 kV T-1 & T-2 transformers were shutdown at 07:08(12/08/2022) & 07:13(12/08/2022) due to | [5 empty] | About 22 MW power interruption has been running under
R/H maintenance at 33 kV Bus. | [5 empty] | Norail S/S area since 07:08(12/08/2022).
o) Chandpur 132/33 kV T-1 transformer was under shut down from 07:15(12/08/2022) to 09:46(12/08/2022) for | [5 empty] | About 10 MW power interruption occurred under
C/M. | [5 empty] | Chandpur S/S area from 07:15(12/08/2022) to 09:46.
p) Bhulta 400/230 kV ATR-1 transformer was under shut down from 07:32(12/08/2022) to 10:07(12/08/2022) for
C/M.
| Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2022-08-11 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4347000
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 290 | 7007373 | Gas shortage
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 80 | 1937227 | Engine problem
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 391 | 7630840 | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 206 | 5944000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 5125250 | Gas shortage & GT-2 S/D.
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 32 | 270720 | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 0 | 0 | Under maint.
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 30 | 700616 | Engine problem
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 359244
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 49 | 371520 | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 32 | 298368 | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 857160
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 127 | 1351680 | Engine problem
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 1329281
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 961028
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 47 | 1123080 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 783000
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 16 | 594200 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 42 | 994560 | #REF!
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 277 | 3158944 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 300 | 6056032
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 98 | 2102871
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 98 | 2041405
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 1746576
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 88 | 2043600 | Engine problem
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 33 | 305280 | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 2093760
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 169284
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 55 | 1282680
| Dhaka area Total |  |  |  | 5847 | 3206 | 62986579
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 110 | 2500000 | Machine problem
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 25 | 602789
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 66285
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 45 | 451200 | Engine problem
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 107 | 2544495 | Low water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | HGPI for 30 days.
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 105 | 1984690
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 34 | 632544 | Fuel shortage
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 753896 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 33 | 790440 | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 90 | 882240 | Engine problem
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 15 | 352 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 32 | 572640
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 90 | 611520 | Engine problem
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 30721
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 214 | 1630909 | Fuel shortage
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 36 | 912923 | Fuel shortage
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 55 | 1316430 | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 98 | 949440 | Engine problem
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 108 | 2608200 | Engine problem
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Chattogram area Total |  |  |  | 2382 | 1248 | 19841714
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 188 | 4495000 | #REF!
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 300 | 7519700 | gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 270 | 7069000 | Gas shortage
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+136*1 | 284 | 0 | 0 | On test.
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 42 | 911952
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 55 | 1257600
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 200727 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1201175
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 140 | 3064436 | Engine problem
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 47 | 1080864
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 123 | 2864100 | Machine problem
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 200 | 2284320
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 494928
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 10 | 234540
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 78 | 2051520
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 690000
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 8 | 203947 | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 20 | 464340 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Fuel shortage
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 998640
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 105 | 1463280 | Engine problem
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 35 | 889560 | 33 kV feeder problem.
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 74 | 1764480 | Fuel shortage
| Cumilla Area Total |  |  |  | 3169 | 1923 | 41204109
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 98 | 1888320 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 470520
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 15900
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 180 | 1920000 | Engine problem
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 78 | 1347600 | Engine problem
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 389610
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 298080 | Engine problem
| Mymensingh Area Total |  |  |  | 614 | 390 | 6330030
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1018000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 41 | 979838 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | ST under maint.
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 0 | 0 | Gas shortage
| Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 0 | 0 | Gas shortage
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 0 | 0 | Engine problem
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 62 | 1416864
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 668160
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 221 | 5225890
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50MW PP (EPL) |  | NENP | 27*2 | 50 | 0 | 306760 | Gas shortage
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 8 | 133128 | Gas shortage
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 280 | 7391000 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 403 | 9560000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 9 | 199980
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 388 | 9276100
| Sylhet Area Total |  |  |  | 2477 | 1536 | 36175720
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 907 | 21895272
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 16 | 318720 | Fuel shortage
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 45 | 387360 | Engine problem
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 230 | 5433600
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 72 | 733440 | Line O/L
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 145 | 3774816 | Gas shortage.
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 8 | 187875 | Fuel shortage
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 96 | 1925760
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 53 | 479520 | Fuel shortage
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 105 | 2278368
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 341280
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 0 | 0 | 0 | On test.
| Khulna Area Total |  |  |  | 2384 | 1677 | 37756011
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 110 | 944256 | Line O/L
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 27 | 444592 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 88 | 1961000 | ST under S/D
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 70 | 8721200 | Coal shortage, Unit-2 S/D
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 5001873
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 116 | 967200 | Line O/L
| Barisal Area Total |  |  |  | 1958 | 631 | 18040121
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 31 | 742192 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 41 | 742244 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contract Expired
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 42 | 242380 | Engine problem
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 40 | 676290 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 152 | 3946091 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 218 | 5229527
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 148 | 3808200 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 308 | 7080654 | Gas shortage
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 33 | 739079 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 21 | 441600
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | .
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 262854
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 16 | 223344 | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 80 | 1364440 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 133 | 3797363 | Engine problem
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 94 | 1686432 | Engine problem
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 95 | 1639104 | Engine problem
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 35820
| Rajshahi Area Total |  |  |  | 2129 | 1463 | 32657614
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 251 | 6099400 | Coal shortage
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 55 | 1333478 | Engine problem
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 45440
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 72 | 948288 | Fuel shortage
| Rangpur Area Total |  |  |  | 720 | 378 | 8426606
| Total |  |  |  | 21680 | 12452 | 263418504
| Eastern Grid Total |  |  |  | 14489 | 8303 | 166538152
| Western Grid Total |  |  |  | 7191 | 4149 | 96880352
| National Grid Total |  |  |  | 21680 | 12452 | 263418504
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2022-08-11
(a) ENTIRE EASTERN GRID : |  | 8218.3 | MW | (b) ENTIRE WESTERN GRID : |  | 3818.85 | MW
i) Dhaka area |  | 4421.55 | MW | i) Khulna area |  | 1364 | MW
ii) Chittagong area |  | 1245.75 | MW | ii) Rajshahi area |  | 1191 | MW
iii) Comilla area |  | 1105 | MW | iii) Barisal area |  | 355.85 | MW
iv) Mymensingh area |  | 891 | MW | iv) Rangpur area |  | 908 | MW
v) Sylhet area |  | 555 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 12037.15 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
AKS | 21 | 08:00 | Chowmuhani | 168 | 21:00 | Kaptai | 4.5 | 19:30 | Nawabganj | 36.9 | 19:00 | Siddhirganj | 108 | 22:00
AKSML | 142 | 23:00 | Chuadanga | 87 | 00:00 | Kazla | 84 | 10:00 | Netrakona | 96 | 19:00 | Sirajganj | 88 | 07:00
Aftabnagar | 30 | 15:00 | Coxsbazar | 110 | 20:00 | Keranigonj | 56 | 19:00 | New | 81 | 09:00 | Sonargaon | 80 | 12:00
Agargaon | 89 | 13:00 | Cumilla(N) | 159 | 21:00 | Khagrachori | 28 | 19:30 | Niamatpur | 64 | 06:00 | Sreemongol | 44 | 12:00
Agrabad | 74 | 14:00 | Cumilla(S) | 161 | 14:00 | Khulna | 89 | 21:00 | Noapara | 47 | 01:00 | Srinagar | 46.28 | 21:00
Amnura | 49 | 22:00 | Daudkandi | 137 | 22:00 | Khulshi | 170 | 20:00 | PHP | 11 | 10:00 | Sunamganj | 38 | 22:00
Ashuganj | 39 | 23:00 | Dhaka | 36 | 11:00 | Kishoreganj | 112 | 22:00 | Pabna | 89 | 00:00 | Sylhet | 136 | 00:00
BSRM | 151 | 02:00 | Dhamrai | 90 | 08:00 | Kodda | 276 | 21:00 | Palashbari | 108 | 23:00 | TK | 28.5 | 19:00
Bagerhat | 82 | 21:00 | Dhanmondi | 132 | 12:00 | Kulaura | 48 | 21:00 | Panchagarh | 46 | 08:00 | Tangail | 195 | 22:00
Bakulia | 100 | 19:00 | Dohazari | 92 | 21:00 | Kurigram | 66 | 21:00 | Patuakhali | 133 | 22:00 | Thakurgaon | 66 | 22:00
Banani | 55 | 14:00 | Faridpur | 122 | 20:00 | Kushtia | 122 | 00:00 | Payra | 1.02 | 16:00 | Tongi | 116 | 19:30
Bangabhaban | 20 | 10:00 | Fatullah | 69 | 00:00 | Lalbag | 72 | 18:00 | Purbachal | 20 | 21:00 | Ullon | 40 | 21:00
Barapukuria | 54 | 21:00 | Fenchuganj | 46 | 20:00 | Lalmonirhat | 50 | 21:00 | Purbasadipur | 96 | 05:00 | Uttara | 93 | 21:00
Barguna | 16 | 19:00 | Feni | 90 | 19:00 | Madanganj | 67 | 10:00 | Rahim | 26 | 08:00 | UttaraNew | 18 | 00:00
Barishal | 94 | 19:30 | GPH | 93 | 19:00 | Madaripur | 90 | 21:00 | Rajbari | 60 | 19:30 | Zigatola | 57 | 19:00
Barishal-230 | 72 | 22:00 | Ghorashal | 49 | 23:00 | Madartek | 78 | 23:00 | Rajendrapur | 92 | 05:00
Baroaulia | 75 | 19:00 | Goalpara | 23 | 00:00 | Madunaghat | 58 | 19:30 | Rajshahi | 132 | 22:00
Baroirhat | 53 | 19:00 | Gollamari | 40 | 23:00 | Magura | 44 | 00:00 | Rajshahi-230 | 26 | 02:00
Bashundhara | 157 | 19:30 | Gopalganj | 94.8 | 22:00 | Mahasthangarh | 60 | 22:00 | Ramganj | 88 | 19:00
BashundharaCement | 7 | 00:00 | Gulshan | 106 | 17:00 | Manikganj | 76 | 05:00 | Rampur | 16 | 00:00
Beanibazar | 57 | 20:00 | Halishahar | 84 | 17:00 | Maniknagar | 74 | 13:00 | Rangamati | 14 | 19:00
Benapole | 46 | 19:00 | HaripurSBU | 147 | 23:00 | Matarbari | 38 | 21:00 | Rangpur | 105 | 08:00
Bhaluka | 94 | 21:00 | Hasnabad | 88 | 23:00 | Matuail | 64 | 10:00 | Ruppur | 5 | 09:00
Bhandaria | 43 | 19:30 | Hathazari | 96 | 19:00 | Millgate | 54 | 12:00 | SSM | 3 | 05:00
Bhangura | 28 | 19:00 | Ishurdi | 61 | 19:30 | Mirpur | 122 | 19:30 | Saidpur | 93 | 08:00
Bheramara(GK) | 54 | 00:00 | Jaldhaka | 66 | 21:00 | Mirsorai | N/A | N/A | Satkhira | 95 | 06:00
Bhulta | 233 | 09:00 | Jamalpur | 119 | 21:00 | Mithapukur | 32 | 21:00 | Satmasjid | 101 | 19:00
Bog-Sherpur | 48 | 07:00 | Jashore | 114 | 19:00 | Modern | 0 | 00:00 | Savar | 156 | 09:00
Bogura | 147 | 22:00 | Jhenaidah | 96 | 00:00 | Mogbazar | 121 | 16:00 | Shahjadpur | 85 | 22:00
Borhanuddin | 38 | 22:00 | Joydebpur | 192 | 21:00 | Mongla | 30 | 11:00 | Shahjibazar | 95 | 00:00
Brahmanbaria | 150 | 22:00 | Joypurhat | 52 | 23:00 | Motijheel | 33 | 10:00 | Shahmirpur | 46.5 | 18:30
Cantonment | 144 | 19:00 | Juldah | 22 | 14:00 | Munshiganj | 90 | 23:00 | Shariatpur | 78 | 22:00
Chandpur | 57 | 21:00 | KSRM | 33.25 | 07:00 | Mymensingh | 209 | 22:00 | Sherpur | 100 | 19:00
Chandraghona | 30 | 19:00 | Kabirpur | 247 | 21:00 | Naogaon | 108 | 19:00 | Shikalbaha | 28 | 19:00
Chapai | 59 | 08:00 | Kachua | 56 | 22:00 | Narail | 34 | 00:00 | Shikalbaha-230 | N/A | N/A
Charsaidpur | 22 | 00:00 | Kallyanpur | 90 | 23:00 | Narinda | 68 | 13:00 | Shitalakhya | 114 | 12:00
Chauddagram | 52 | 22:00 | Kalurghat | 34 | 12:00 | Narshingdi | 150 | 04:00 | Sholosohor | N/A | N/A
Chhatak | 25 | 21:00 | Kamrangirchar | 57 | 21:00 | Natore | 106 | 22:00 | Shyampur | 144 | 01:00
Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
(1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2022-08-11 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Bhulta | 387 | 19:00 | 367 | 11:00 | Kaliakoir | 390 | 19:00 | 375 | 12:00
| Bibiana | 406 | 20:00 | 394 | 10:00 | Payra | 420 | 16:00 | 410 | 01:00
| BIPTC | 405 | 06:00 | 396 | 20:00 | Rahanpur_I
| Gopalganj_I | 418 | 17:00 | 400 | 01:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 224 | 20:00 | 212 | 11:00 | Hasnabad | 221 | 01:00 | 214 | 13:00
| AKSML | 235 | 20:00 | 215 | 11:00 | Hathazari | 235 | 20:00 | 219 | 11:00
| Aminbazar | 221 | 00:00 | 213 | 11:00 | Ishurdi | 238 | 17:00 | 229 | 21:00
| Ashuganj | 240 | 20:00 | 228 | 08:00 | Jhenaidah | 233 | 17:00 | 224 | 21:00
| Baghabari | 236 | 18:30 | 230 | 07:00 | Kaliakoir | 226 | 19:00 | 214 | 12:00
| Barapukuria | 224 | 14:00 | 207 | 21:00 | Keranigonj | 223 | 19:30 | 211 | 12:00
| Barishal | 246 | 14:00 | 230 | 23:00 | Khulna(S) | 243 | 17:00 | 232 | 01:00
| Bheramara | 234 | 17:00 | 225 | 21:00 | Maniknagar | 225 | 20:00 | 212 | 12:00
| Bhulta | 228 | 19:00 | 216 | 11:00 | Meghnaghat | 230 | 00:00 | 220 | 09:00
| Bibiana | 236 | 19:30 | 228 | 10:00 | Mirsorai
| BIPTC | 236 | 17:00 | 226 | 21:00 | Rajshahi | 236 | 17:00 | 226 | 11:00
| Bogura | 228 | 17:00 | 218 | 21:00 | Rampur
| Borhanuddin | 249 | 07:00 | 239 | 23:00 | Rampura | 226 | 20:00 | 214 | 11:00
| BSRM | 233 | 20:00 | 218 | 11:00 | Shikalbaha | 236 | 21:00 | 218 | 14:00
| Cumilla(N) | 229 | 20:00 | 216 | 11:00 | Shyampur | 224 | 20:00 | 212 | 12:00
| Fenchuganj | 236 | 00:00 | 230 | 11:00 | Siddhirganj | 224 | 19:00 | 214 | 11:00
| Ghorashal |  |  |  |  | Sirajgonj | 233 | 17:00 | 228 | 07:00
| GPH | 233 | 23:00 | 216 | 14:00 | Tongi | 228 | 19:30 | 212 | 11:00
| Haripur | 223 | 19:30 | 212 | 12:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 140 | 20:00 | 129 | 11:00 | Lalbag | 139 | 19:30 | 132 | 08:00
| Agargaon | 138 | 20:00 | 130 | 12:00 | Lalmonirhat | 127 | 14:00 | 112 | 21:00
| Agrabad | 138 | 20:00 | 126 | 11:00 | Madanganj | 132 | 19:30 | 122 | 12:00
| AKS | 137 | 20:00 | 126 | 17:00 | Madaripur | 139 | 06:00 | 136 | 00:00
| Aminbazar | 134 | 00:00 | 127 | 11:00 | Madartek | 138 | 20:00 | 129 | 11:00
| Amnura | 134 | 18:30 | 126 | 08:00 | Madunaghat | 137 | 19:30 | 129 | 11:00
| Ashuganj | 137 | 18:00 | 132 | 11:00 | Magura | 140 | 17:00 | 135 | 21:00
| Bagerhat | 138 | 14:00 | 131 | 00:00 | Mahasthangarh | 136 | 14:00 | 125 | 21:00
| Bakulia | 137 | 19:30 | 26 | 14:00 | Manikganj | 135 | 19:30 | 126 | 03:00
| Banani | 133 | 20:00 | 125 | 10:00 | Maniknagar | 134 | 19:30 | 126 | 10:00
| Bangabhaban | 134 | 19:30 | 120 | 16:00 | Matarbari | 129 | 00:00 | 115 | 14:00
| Barapukuria | 137 | 14:00 | 124 | 21:00 | Matuail | 131.8 | 20:00 | 124.8 | 12:00
| Barguna | 137 | 15:00 | 128 | 12:00 | Millgate | 134 | 19:00 | 125 | 09:00
| Barishal | 140 | 16:00 | 126 | 03:00 | Mirpur | 133 | 00:00 | 125 | 12:00
| Barishal-230 | 140 | 17:00 | 131 | 23:00 | Mithapukur | 134 | 14:00 | 120 | 21:00
| Baroaulia | 139 | 20:00 | 128 | 11:00 | Modern | 138 | 20:00 | 128 | 07:00
| Baroirhat | 134 | 20:00 | 124 | 03:00 | Mogbazar | 139 | 20:00 | 129 | 12:00
| Bashundhara | 133 | 19:30 | 125 | 08:00 | Mongla | 137 | 17:00 | 129 | 01:00
| BashundharaCement | 132 | 19:30 | 122 | 12:00 | Motijheel | 134 | 19:30 | 120 | 14:00
| Beanibazar | 130 | 00:00 | 126 | 21:00 | Munshiganj | 132 | 00:00 | 124 | 11:00
| Benapole | 138 | 17:00 | 132 | 06:00 | Mymensingh | 132 | 20:00 | 116 | 06:00
| Bhaluka | 132 | 18:00 | 115 | 06:00 | Naogaon | 135 | 17:00 | 122 | 21:00
| Bhandaria | 140 | 08:00 | 129 | 23:00 | Narail | 139 | 16:00 | 133 | 22:00
| Bhangura | 140 | 17:00 | 134 | 21:00 | Narinda
| Bheramara | 137 | 14:00 | 134 | 01:00 | Narshingdi | 127 | 19:30 | 117 | 08:00
| Bheramara(GK) | 139 | 17:00 | 135 | 11:00 | Natore | 136 | 19:00 | 129 | 21:00
| Bhulta | 124 | 20:00 | 117 | 14:00 | Nawabganj | 139 | 20:00 | 130 | 11:00
| Bog-Sherpur | 138 | 17:00 | 128 | 21:00 | Netrakona | 130 | 20:00 | 117 | 02:00
| Bogura | 138 | 17:00 | 128 | 21:00 | New | 133 | 19:00 | 125 | 14:00
| Bogura-230 | 138 | 18:30 | 130 | 21:00 | Niamatpur | 134 | 17:00 | 119 | 21:00
| Brahmanbaria | 133 | 18:00 | 128 | 12:00 | Noapara | 140 | 14:00 | 134 | 06:00
| Cantonment | 136 | 05:00 | 129 | 11:00 | Pabna | 137 | 17:00 | 132 | 21:00
| Chandpur | 138 | 18:30 | 124 | 02:00 | Palashbari | 132 | 14:00 | 117 | 21:00
| Chandraghona | 139 | 20:00 | 130 | 06:00 | Panchagarh | 132 | 17:00 | 113 | 21:00
| Chapai | 132 | 14:00 | 125 | 11:00 | Patuakhali | 139 | 16:00 | 131 | 00:00
| Charsaidpur | 133 | 19:30 | 123 | 12:00 | Payra | 140 | 17:00 | 135 | 00:00
| Chauddagram | 134 | 19:00 | 124 | 02:00 | PHP | 135 | 20:00 | 123 | 03:00
| Chhatak | 130 | 00:00 | 126 | 21:00 | Postogola | 141 | 19:00 | 133 | 12:00
| Chowmuhani | 134 | 18:30 | 125 | 06:00 | Purbachal | 134 | 19:00 | 124 | 10:00
| Chuadanga | 138 | 14:00 | 131 | 01:00 | Purbasadipur | 133 | 17:00 | 114 | 01:00
| Coxsbazar | 126 | 00:00 | 115 | 18:00 | Rahim | 132 | 19:30 | 125 | 12:00
| Cumilla(N) | 133 | 19:00 | 127 | 02:00 | Rajbari | 137 | 16:00 | 132 | 00:00
| Cumilla(S) | 136 | 03:00 | 126 | 02:00 | Rajendrapur | 140 | 19:30 | 124 | 12:00
| Daudkandi | 129 | 19:00 | 122 | 12:00 | Rajshahi | 134 | 17:00 | 128 | 11:00
| Dhaka | 139 | 20:00 | 130 | 09:00 | Rajshahi-230 | 135 | 17:00 | 18 | 07:00
| Dhamrai | 131 | 19:00 | 124 | 09:00 | Ramganj | 134 | 18:00 | 120 | 03:00
| Dhanmondi | 131 | 19:30 | 123 | 12:00 | Rampur | 137 | 21:00 | 127 | 12:00
| Dohazari | 135 | 00:00 | 126 | 11:00 | Rampura | 137 | 20:00 | 129 | 11:00
| Faridpur | 137 | 17:00 | 132 | 00:00 | Rangamati | 137 | 20:00 | 129 | 08:00
| Fatullah | 135 | 19:30 | 128 | 14:00 | Rangpur | 130 | 12:00 | 116 | 21:00
| Fenchuganj | 135 | 07:00 | 131 | 21:00 | Ruppur | 137 | 17:00 | 134 | 01:00
| Feni | 137 | 19:30 | 126 | 08:00 | Saidpur | 134 | 17:00 | 116 | 21:00
| Ghorashal | 140 | 20:00 | 136 | 08:00 | Satkhira | 136 | 14:00 | 129 | 22:00
| Goalpara | 139 | 17:00 | 134 | 01:00 | Satmasjid | 138 | 20:00 | 129 | 12:00
| Gollamari | 138 | 17:00 | 133 | 00:00 | Savar | 136 | 20:00 | 125 | 11:00
| Gopalganj | 140 | 16:00 | 136 | 11:00 | Shahjadpur | 140 | 17:00 | 137 | 01:00
| Gopalganj_I | 141 | 17:00 | 14 | 23:00 | Shahjibazar | 135 | 19:30 | 130 | 12:00
| Gulshan | 138 | 20:00 | 128 | 12:00 | Shahmirpur | 139 | 20:00 | 128 | 08:00
| Halishahar | 138 | 20:00 | 127 | 11:00 | Shariatpur | 138 | 16:00 | 134 | 00:00
| Haripur | 132 | 19:30 | 125 | 12:00 | Sherpur | 137 | 18:00 | 114 | 06:00
| HaripurSBU | 132 | 19:00 | 125 | 13:00 | Shikalbaha | 139 | 19:30 | 127 | 08:00
| Hasnabad | 142 | 20:00 | 135 | 10:00 | Shikalbaha-230 | 139 | 21:00 | 129 | 12:00
| Hathazari | 138 | 03:00 | 128 | 11:00 | Shitalakhya | 141 | 20:00 | 131 | 11:00
| Ishurdi | 138 | 17:00 | 134 | 07:00 | Sholosohor
| Jaldhaka | 132 | 14:00 | 113 | 21:00 | Shyampur | 135 | 20:00 | 128 | 09:00
| Jamalpur | 139 | 18:00 | 117 | 07:00 | Shyampur-230 | 135 | 19:30 | 128 | 09:00
| Jashore | 138 | 17:00 | 133 | 01:00 | Siddhirganj | 132 | 20:00 | 125 | 11:00
| Jhenaidah | 142 | 14:00 | 136 | 11:00 | Sirajganj | 136 | 16:00 | 130 | 21:00
| Jhenaidah-230 | 142 | 17:00 | 137 | 01:00 | Sonargaon | 132 | 19:00 | 125 | 07:00
| Joydebpur | 144 | 19:00 | 133 | 12:00 | Sreemongol | 135 | 19:00 | 131 | 12:00
| Joypurhat | 135 | 17:00 | 122 | 21:00 | Srinagar | 139 | 20:00 | 130 | 11:00
| Juldah | 139 | 20:00 | 127 | 11:00 | SSM | 140 | 00:00 | 132 | 09:00
| Kabirpur | 138 | 19:00 | 123 | 14:00 | Sunamganj | 128 | 00:00 | 125 | 21:00
| Kachua | 135 | 19:00 | 124 | 02:00 | Sylhet | 132 | 09:00 | 129 | 21:00
| Kaliakoir | 139 | 19:00 | 131 | 12:00 | Tangail | 136 | 19:30 | 127 | 05:00
| Kallyanpur | 135 | 19:30 | 126 | 12:00 | Thakurgaon | 133 | 18:00 | 113 | 21:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2022-08-11
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 586 | 7306 | 3883 | 11189 |  |  |  | QF-LDC-11
0:30 | 651 | 7007.5 | 4080 | 11087.5 | Date: | 2022-08-11
1:00 | 716 | 6709 | 4277 | 10986
1:30 | 739 | 6678 | 4240.5 | 10918.5
2:00 | 762 | 6647 | 4204 | 10851
2:30 | 763 | 6627 | 4173 | 10800 | [5 empty] | Gen. at Eve. Peak | 12452 | 12452 MW (21:00 )
3:00 | 764 | 6607 | 4142 | 10749 | [6 empty] | 21:00
3:30 | 775 | 6591 | 4143 | 10734 | [5 empty] | Gen. at Day Peak | 10459 | 10459 MW (10:00 )
4:00 | 786 | 6575 | 4144 | 10719 | [6 empty] | 10:00
4:30 | 797 | 6570.5 | 4150.5 | 10721 | [5 empty] | Highest Generation | 12452
5:00 | 808 | 6566 | 4157 | 10723 | [6 empty] | 21:00
5:30 | 772 | 6498 | 4009.5 | 10507.5
6:00 | 736 | 6430 | 3862 | 10292
6:30 | 778 | 6402 | 3884 | 10286
7:00 | 820 | 6374 | 3906 | 10280
7:30 | 901 | 6310 | 4008.5 | 10318.5
8:00 | 982 | 6246 | 4111 | 10357
8:30 | 980 | 6340 | 4058.5 | 10398.5
9:00 | 978 | 6434 | 4006 | 10440
9:30 | 1025 | 6457.5 | 3992 | 10449.5
10:00 | 1072 | 6481 | 3978 | 10459
10:30 | 1017 | 6460 | 3949.5 | 10409.5
11:00 | 962 | 6439 | 3921 | 10360
11:30 | 986 | 6504.5 | 3892 | 10396.5
12:00 | 1010 | 6570 | 3863 | 10433
12:30 | 991 | 6556.5 | 3910 | 10466.5
13:00 | 972 | 6543 | 3957 | 10500
13:30 | 938 | 6477 | 3939.5 | 10416.5
14:00 | 904 | 6411 | 3922 | 10333
14:30 | 736 | 6541.5 | 3679.5 | 10221
15:00 | 568 | 6672 | 3437 | 10109
15:30 | 635 | 6718 | 3502 | 10220
16:00 | 702 | 6764 | 3567 | 10331
16:30 | 731 | 6765 | 3601 | 10366
17:00 | 760 | 6766 | 3635 | 10401
17:30 | 614 | 6858.5 | 3582.5 | 10441
18:00 | 468 | 6951 | 3530 | 10481
18:30 | 283 | 7505 | 3633 | 11138
19:00 | 98 | 8059 | 3736 | 11795
19:30 | 184 | 8092 | 3964 | 12056
20:00 | 106 | 8142 | 4001 | 12143 |  |  |  | Executive Engineer
20:30 | 156 | 8222.5 | 4075 | 12297.5 |  |  |  | Network Operation Division
21:00 | 206 | 8303 | 4149 | 12452
21:30 | 280 | 8174 | 4190 | 12364
22:00 | 354 | 8045 | 4231 | 12276 |  |  |  |  | Page 6 of 7
22:30 | 339 | 8045.5 | 4127 | 12172.5
23:00 | 324 | 8046 | 4023 | 12069
23:30 | 455 | 7676 | 3953 | 11629
24:00 | 586 | 7306 | 3883 | 11189
12452 MW (21:00 )
10459 MW (10:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2022-08-11 |  | Energy |  | 263418504
[13 empty] | 2022-08-11 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 3818 | 907 | 1461 | 770 | 2659 | 480 | 108 | 440 | 674 | 84 | 0 | 1761.1298
0:30 | 3881 | 907 | 1553.5 | 762 | 2239.5 | 665 | 106.5 | 436 | 669.5 | 81 | 0 | 1578.1972 | Date: | 2022-08-11
1:00 | 3944 | 907 | 1646 | 754 | 1820 | 850 | 105 | 432 | 665 | 78 | 0 | 1395.2645
1:30 | 3945.5 | 907 | 1647.5 | 754 | 1783.5 | 830 | 105 | 433.5 | 655.5 | 73 | 0 | 1273.1559 | [8 empty] | Total Energy | 263.4185 | Total Energy Gen 263.419 MKWHr Energy Not Served 23.959 MKWHr Energy Requirement 287.377 MKWHr
2:00 | 3947 | 907 | 1649 | 754 | 1747 | 810 | 105 | 435 | 646 | 68 | 0 | 1151.0472 | [8 empty] | Energy not Served | 23.9588
2:30 | 3930 | 904.5 | 1656.5 | 754 | 1741.5 | 800 | 105 | 435.5 | 624.5 | 66 | 0 | 1128.9294 | [8 empty] | Energy Requirement | 287.3773
3:00 | 3913 | 902 | 1664 | 754 | 1736 | 790 | 105 | 436 | 603 | 64 | 0 | 1106.8116
3:30 | 3892 | 903.5 | 1661.5 | 753 | 1737 | 790 | 105 | 436.5 | 603 | 71 | 0 | 1005.4383 | [6 empty] | Shortage
4:00 | 3871 | 905 | 1659 | 752 | 1738 | 790 | 105 | 437 | 603 | 78 | 0 | 904.0651
4:30 | 3890.5 | 905 | 1651 | 751.5 | 1718.5 | 790 | 105 | 437.5 | 610.5 | 81 | 0 | 579.6707
5:00 | 3910 | 905 | 1643 | 751 | 1699 | 790 | 105 | 438 | 618 | 84 | 0 | 255.2763
5:30 | 3939.5 | 905 | 1646.5 | 541 | 1717.5 | 770 | 105 | 436.5 | 583.5 | 80 | 3 | 223.4819
6:00 | 3969 | 905 | 1650 | 331 | 1736 | 750 | 105 | 435 | 549 | 76 | 6 | 191.6876
6:30 | 3803 | 905 | 1690.5 | 452 | 1714.5 | 750 | 105 | 440 | 544 | 81 | 18.5 | 243.2958 |  |  |  |  | Coal
7:00 | 3637 | 905 | 1731 | 573 | 1693 | 750 | 105 | 445 | 539 | 86 | 31 | 294.904
7:30 | 3597 | 905.5 | 1700 | 643.5 | 1713 | 745 | 106 | 447 | 541.5 | 85 | 52.5 | 326.452 |  |  |  | Oil |  |  |  | ,
8:00 | 3557 | 906 | 1669 | 714 | 1733 | 740 | 107 | 449 | 544 | 84 | 74 | 358
8:30 | 3579.5 | 906.5 | 1669 | 733 | 1735 | 740 | 106.5 | 445 | 531.5 | 85 | 83.5 | 518.5
9:00 | 3602 | 907 | 1669 | 752 | 1737 | 740 | 106 | 441 | 519 | 86 | 93 | 679
9:30 | 3663.5 | 906.5 | 1621 | 751.5 | 1705.5 | 740 | 106.5 | 439 | 513 | 88 | 125.5 | 827.5
10:00 | 3725 | 906 | 1573 | 751 | 1674 | 740 | 107 | 437 | 507 | 90 | 158 | 976
10:30 | 3780 | 906.5 | 1537.5 | 680.5 | 1673.5 | 740 | 107 | 436.5 | 505 | 89 | 162.5 | 1172.5
11:00 | 3835 | 907 | 1502 | 610 | 1673 | 740 | 107 | 436 | 503 | 88 | 167 | 1369
11:30 | 3840.5 | 906.5 | 1497.5 | 682 | 1659 | 740 | 106 | 435.5 | 503 | 93 | 142 | 1444
12:00 | 3846 | 906 | 1493 | 754 | 1645 | 740 | 105 | 435 | 503 | 98 | 117 | 1519
12:30 | 3836.5 | 906 | 1473.5 | 752.5 | 1690 | 740 | 105 | 438 | 499.5 | 101 | 135 | 1468.5
13:00 | 3827 | 906 | 1454 | 751 | 1735 | 740 | 105 | 441 | 496 | 104 | 153 | 1418
13:30 | 3827 | 906 | 1454 | 751 | 1735 | 740 | 105 | 441 | 496 | 104 | 153 | 1461
14:00 | 3827 | 906 | 1454 | 751 | 1735 | 740 | 105 | 441 | 496 | 104 | 153 | 1504
14:30 | 3840.5 | 906 | 1463.5 | 747.5 | 1803.5 | 495 | 104 | 436 | 485 | 103 | 130 | 1515
15:00 | 3854 | 906 | 1473 | 744 | 1872 | 250 | 103 | 431 | 474 | 102 | 107 | 1526
15:30 | 3842.5 | 906 | 1475 | 737.5 | 1994 | 250.5 | 103.5 | 432.5 | 505 | 104 | 78 | 1490
16:00 | 3831 | 906 | 1477 | 731 | 2116 | 251 | 104 | 434 | 536 | 106 | 49 | 1454
16:30 | 3835 | 906.5 | 1480 | 575 | 2300 | 251 | 104.5 | 415.5 | 544 | 105 | 41.5 | 1210.3661
17:00 | 3835 | 907 | 1483 | 419 | 2484 | 251 | 105 | 397 | 552 | 104 | 34 | 966.7322
17:30 | 3837.5 | 906.5 | 1478.5 | 304.5 | 2662 | 250.5 | 105.5 | 397 | 558.5 | 91 | 19.5 | 814.6723
18:00 | 3840 | 906 | 1474 | 190 | 2840 | 250 | 106 | 397 | 565 | 78 | 5 | 662.6124
18:30 | 3869 | 906 | 1519 | 386 | 3158.5 | 250 | 106 | 400 | 634.5 | 80 | 2.5 | 840.4764
19:00 | 3898 | 906 | 1564 | 582 | 3477 | 250 | 106 | 403 | 704 | 82 | 0 | 1018.3404
19:30 | 3902 | 905 | 1553 | 589 | 3677 | 251 | 107 | 445 | 771 | 72 | 0 | 869.9668
20:00 | 3935 | 906 | 1543 | 600 | 3695 | 251 | 107 | 448 | 795 | 80 | 0 | 974.1048
20:30 | 3938.5 | 906.5 | 1573 | 662.5 | 3707.5 | 286 | 107 | 448 | 807 | 79 | 0 | 946.9183
21:00 | 3942 | 907 | 1603 | 725 | 3720 | 321 | 107 | 448 | 819 | 78 | 0 | 919.7319
21:30 | 3920.5 | 907 | 1615 | 616.5 | 3701 | 370.5 | 107 | 446.5 | 816.5 | 80 | 0 | 1016.3659
22:00 | 3899 | 907 | 1627 | 508 | 3682 | 420 | 107 | 445 | 814 | 82 | 0 | 1113
22:30 | 3875 | 906.5 | 1524.5 | 620.5 | 3590.5 | 440 | 107.5 | 444.5 | 800 | 79 | 0 | 1059.5
23:00 | 3851 | 906 | 1422 | 733 | 3499 | 460 | 108 | 444 | 786 | 76 | 0 | 1006
23:30 | 3834.5 | 906.5 | 1441.5 | 751.5 | 3079 | 470 | 108 | 442 | 730 | 80 | 0 | 1127.5 | Max Temp. in Dhaka |  | 24.7° C | 33° C
24:00 | 3818 | 907 | 1461 | 770 | 2659 | 480 | 108 | 440 | 674 | 84 | 0 | 1249
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 263.419 MKWHr Energy Not Served 23.959 MKWHr Energy Requirement 287.377 MKWHr
Note on W13: Author:

## Generation
g | 2022-08-11
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 37 | 36 | 37 | 37 | 35 | 35 | 36 | 33 | 34 | 35 | 36 |  | 36 | 37 | 37 | 37 | 37 | 38 | 38 | 856495
2 | Karnaphuli Hydro PP Unit-4 & 5 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1688000
3 | Chattogram TPP-1 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 113 | 25 | 95 | 100 | 100 | 100 |  | 105 | 105 | 110 | 110 | 110 | 110 | 110 | 2500000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 602789
| Teknaf 20MW PP (Solartech) |  |  |  |  | 0 | 1 | 3 | 5 | 1 | 11 | 6 | 13 | 6 | 4 | 5 | 3 | 2 | 0 | [8 empty] | 66285
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 51 | 51 | 51 | 51 | 51 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 51 | 51 | 34 | 51 | 51 | 34 | 51 | 753896
12 | Hathazari 100 MW peaking PP | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 26 | 26 | 26 | 27 | 26 | 26 | 26 |  | 26 | 33 | 34 | 34 | 34 | 34 | 34 | 632544
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 84 | 87 | 87 | 87 | 87 | 87 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 74 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 37 | 1984690
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP | 48 | 48 | 48 | 47 | 47 | 47 | 40 | 47 | 47 | 47 | 47 | 47 | 37 | 38 | 37 | 37 | 46 | 47 |  | 45 | 47 | 47 | 47 | 48 | 48 | 48 | 1080864
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 82 | 80 | 82 | 82 | 82 | 80 | 80 | 82 | 82 | 82 | 82 | 82 | 80 | 82 | 82 | 97 | 225 | 241 |  | 250 | 260 | 261 | 277 | 278 | 278 | 130 | 3158944
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 200727
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4347000
24
25 | Ghorasal 365 MW CCPP Unit-7 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 295 | 295 | 280 | 285 | 285 |  | 285 | 285 | 285 | 290 | 290 | 300 | 300 | 7007373
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 38 | 38 | 38 | 38 | 38 | 35 | 35 | 33 | 35 | 36 | 36 | 36 | 36 | 35 | 42 | 41 | 40 | 40 |  | 41 | 42 | 42 | 42 | 42 | 42 | 42 | 911952
33 | Ashuganj 225 MW CCPP | 207 | 191 | 191 | 198 | 210 | 205 | 178 | 165 | 139 | 183 | 202 | 203 | 204 | 192 | 187 | 180 | 173 | 180 |  | 175 | 180 | 183 | 188 | 177 | 162 | 148 | 4495000
34 | Ashuganj 450 MW CCPP(South) | 300 | 310 | 290 | 270 | 270 | 330 | 305 | 275 | 260 | 260 | 260 | 260 | 260 | 300 | 305 | 300 | 270 | 265 |  | 305 | 270 | 270 | 270 | 275 | 330 | 300 | 7069000
| Ashuganj 450 MW CCPP(North) | 310 | 320 | 300 | 280 | 280 | 345 | 310 | 280 | 280 | 280 | 280 | 280 | 280 | 300 | 300 | 300 | 300 | 300 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 7519700
Ashuganj 420 MW CCPP(East)
35 | Ashuganj 55 MW PP (Precision) | 53 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 53 | 50 | 48 | 50 | 46 | 46 | 48 | 53 | 51 | 53 |  | 52 | 52 | 54 | 55 | 55 | 55 | 55 | 1257600
36 | Chandpur 150 MW CCPP | 123 | 122 | 122 | 122 | 136 | 135 | 128 | 128 | 129 | 124 | 124 | 125 | 125 | 122 | 122 | 121 | 122 | 120 |  | 120 | 120 | 122 | 123 | 82 | 82 | 82 | 2864100
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 274 | 274 | 268 | 267 | 269 | 226 | 21 | 49 | 149 | 258 | 376 | 400 | 400 | 397 | 397 | 397 | 393 | 391 |  | 390 | 395 | 398 | 391 | 377 | 372 | 379 | 7630840
40 | Meghnaghat 450 MW CCPP(MPL) | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 |  | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 5125250
41 | Haripur 360MW CCPP(HPL) | 240 | 240 | 243 | 247 | 255 | 274 | 320 | 326 | 317 | 307 | 253 | 243 | 237 | 232 | 233 | 226 | 225 | 224 |  | 217 | 217 | 208 | 206 | 205 | 205 | 220 | 5944000
42 | RPCL 210MW CCPP | 102 | 102 | 102 | 102 | 103 | 101 | 80 | 66 | 64 | 63 | 64 | 60 | 60 | 60 | 61 | 63 | 68 | 70 |  | 72 | 72 | 85 | 98 | 98 | 98 | 99 | 1888320
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 1 | 13 | 29 | 42 | 53 | 57 | 46 | 37 | 56 | 44 | 16 | 14 | 2 | [8 empty] | 389610
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 44 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 44 | 44 |  | 44 | 43 | 43 | 43 | 43 | 43 | 43 | 1018000
45 | Fenchugonj CCPP Phase-2 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 |  | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 979838
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 61 | 60 | 60 | 61 | 61 | 60 | 59 | 58 | 55 | 59 | 59 | 58 | 55 | 55 | 60 | 60 | 60 | 60 |  | 62 | 61 | 64 | 62 | 62 | 59 | 61 | 1416864
48 | Shahjibazar 86MW PP (Shahjibazar) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 60 | 78 | 78 | 81 | 81 | 81 | 78 | 668160
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 221 | 221 | 221 | 220 | 220 | 221 | 221 | 221 | 221 | 221 | 221 | 220 | 220 | 208 | 215 | 208 | 210 | 210 |  | 221 | 221 | 221 | 221 | 221 | 221 | 221 | 5225890
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL) | 30 | 30 | 31 | 30 | 30 | 30 | 30 | 30 | 30 | [17 empty] | 306760
53 | Sylhet 10MW PP (Desh) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 199980
54 | Hobiganj 11MW PP Cofidence-E
55 | Fenchugonj 51 MW PP (Barakatullah) | [26 empty] | 0
56 | Shahjahanulla 25 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | [11 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 133128
57 | Bibiana-II 341 MW CCPP (Summit) | 310 | 315 | 310 | 305 | 285 | 270 | 315 | 280 | 320 | 300 | 280 | 320 | 285 | 290 | 310 | 310 | 305 | 290 |  | 310 | 265 | 260 | 280 | 310 | 305 | 320 | 7391000
| Bibiyana South 400 MW | 391 | 392 | 398 | 398 | 400 | 387 | 400 | 395 | 397 | 382 | 386 | 395 | 392 | 366 | 378 | 377 | 385 | 378 |  | 393 | 398 | 400 | 388 | 393 | 386 | 390 | 9276100
58 | Nababganj 55 MW PP (Southern power ) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 55 | 55 |  | 55 | 55 | 55 | 35 | 35 | 35 | 35 | 961028
59 | Tangail Palli Power Gen 22 MW | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 298080
60 | Barabkunda 22 MW PP (Regent) | 15 | 15 | 15 | 15 | 15 | 15 | 13 | 13 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 352
61 | Narshingdi 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 0 |  | 19 | 19 | 19 |  |  | 19 | 19 |  | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 359244
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 22 | 22 | 22 | 22 | 22 | 22 | 470520
63 | Impoprt (Tripura) | 78 | 68 | 64 | 78 | 84 | 76 | 86 | 84 | 86 | 90 | 88 | 98 | 104 | 108 | 102 | 106 | 104 | 78 |  | 82 | 72 | 80 | 78 | 82 | 76 | 84 | 2051520
64 | Malancha, Ctg. EPZ (United) | 38 | 38 | 38 | 38 | 38 | 41 | 40 | 15 | 8 | 8 | 8 | 6 | 6 | 7 | 6 | 8 | 15 | 8 |  | 20 | 21 | 17 | 32 | 32 | 38 | 38 | 572640
65 | Feni 22MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 494928
66 | Feni 11 MW PP (Doreen) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 10 | 10 | 10 | 10 | 234540
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 21 | 21 | 16 | 16 | 16 | 16 | 18 | 25 | 25 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 690000
68 | Cumilla 25 MW PP (Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 12 | 11 | 11 | 12 | 12 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 464340
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 27 | 27 | 27 | 18 | 27 | 27 | 27 | 24 | 24 | 26 | 20 | 23 | 8 | 8 | 8 | 20 | 24 | 24 |  | 24 | 24 | 22 | 22 | 24 | 24 | 24 | 523080
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 783000
72 | Rupganj 33 MW PP(Summit) | 30 | 30 | 30 | 30 | 30 | 32 | 32 | 21 | 32 | 30 | 14 | 28 | 28 | 28 | 20 | 24 | 15 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 594200
73 | Ghorashal 108MW PP (Regent) | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 83 | 85 | 82 | 82 | 80 | 80 | 78 | 78 | 78 | 78 | 78 |  | 78 | 79 | 79 | 80 | 80 | 82 | 85 | 1937227
| Feni Lanka Power | 27 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 998640
| Chowmuhani 113 MW | 47 | 38 | 38 | 39 | 38 | 38 | 38 | 39 | 38 | 39 | 39 | 39 | 39 | 38 | 38 | 40 | 100 | 113 |  | 110 | 105 | 105 | 105 | 115 | 115 | 60 | 1463280
| Manikgonj 162MW PP(MPGL) | 56 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 108 | 108 | 108 | 108 | 128 | 162 |  | 162 | 162 | 162 | 162 | 162 | 162 | 150 | 2093760
77 | Siddhirganj 100 PP(Dutch Bangla) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 7 | 7 |  | 18 | 37 | 49 | 49 | 48 | 48 | 14 | 371520
78 | Gazipur 52 MW PP | 36 | 36 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 994560
79 | Kodda 150MW PP | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 16 | 32 | 32 | 32 | 30 | 30 | 30 | 30 | 78 | 110 | 110 |  | 110 | 110 | 127 | 127 | 127 | 127 | 16 | 1351680
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 203947
| Gazipur 100 MW PP | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 70 | 70 | 70 | 70 | 88 | 88 | 88 | 88 | 88 |  | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 2043600
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 0 | 1 | 2 | 2 | 6 | 1 | 3 | 4 | 4 | 3 | 1 | [9 empty] | 30721
| Jodiac Power | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 |  | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 912923
| Karnaphuli Power Ltd. | 55 | 55 | 55 | 55 | 46 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 50 | 55 | 51 |  | 53 | 55 | 55 | 55 | 55 | 55 | 55 | 1316430
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL) | 8 | 8 | 7 | 8 | 8 | 7 | 7 | 8 | 8 | 7 | 8 | 8 | 8 | 7 | 8 | 7 | 8 | 7 |  | 11 | 32 | 31 | 32 | 20 | 16 | 8 | 270720
| Meghnaghat 104 MW PP (OPCL) |  |  | 0 | 10 | 0 |  |  | 17 | 17 | 17 | 17 | 17 | 10 |  |  |  | 17 | 17 |  | 17 | 34 | 34 | 33 | 33 | 29 | 17 | 305280
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 790440
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 43 | 43 | 43 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1201175
94 | Gagnagar 102 MW PP (Digital Power) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 16 | 32 | 32 | 32 | 32 | 32 | 8 | 298368
95 | Patenga 50MW PP (Baraka) | 19 | 19 | 18 | 18 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 13 |  | 25 | 40 | 38 | 45 | 0 | 3 | 6 | 451200
96 | Chattogram 108 MW PP (ECPV) | 12 | 12 | 12 | 12 | 12 | 12 | 9 | 11 | 8 | 7 | 9 | 12 | 12 | 12 | 12 | 12 | 12 | 22 |  | 90 | 90 | 90 | 90 | 83 | 48 | 11 | 611520
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 15 | 22 | 25 | 25 | 25 | 15 | 25 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 700616
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1329281
101 | Kushiara 163 MW CCPP (KP)
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 0 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 0 | [8 empty] | 15900
103 | Kamalaghat 54 MW PP(Banco Energy) | 35 | 35 | 35 | 35 | 35 | 35 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 857160
104 | Keranigonj 300 MW PP (APR) | 302 | 302 | 302 | 301 | 300 | 101 | 302 | 262 | 301 | 300 | 205 | 304 | 300 | 250 | 300 | 300 |  |  |  | 295 | 198 | 208 | 300 | 188 | 301 | 302 | 6056032
105 | Bramhangoan 100 MW PP (Aggreko) | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 50 | 90 | 80 | 95 | 50 |  | 96 | 97 | 98 | 98 | 70 | 98 | 98 | 2102871
106 | Mymensingh 200 MW PP (United) | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 47 | 47 | 47 | 47 | 47 | 47 | 130 |  | 177 | 177 | 180 | 180 | 180 | 181 | 48 | 1920000
112 | Aurahati 100MW PP (Aggreko) | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 50 | 81 | 81 | 50 | 50 |  | 98 | 98 | 98 | 98 | 50 | 95 | 97 | 2041405
114 | Kodda 149 MW PP Unit-1 (Summit) | 43 | 43 | 43 | 44 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 46 | 59 | 76 | 132 |  | 145 | 145 | 149 | 149 | 149 | 149 | 53 | 1746576
115 | Juldah 100 MW PP Unit-3 (Acorn) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 882240
116 | Chandpur 200MW (Desh energy) | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 54 | 96 | 133 | 158 | 181 |  | 198 | 200 | 200 | 200 | 200 | 200 | 200 | 2284320
117 | Ashuganj 150MW PP (Midland) | 133 | 138 | 137 | 135 | 138 | 137 | 133 | 115 | 122 | 117 | 112 | 110 | 110 | 107 | 110 | 124 | 127 | 125 |  | 130 | 137 | 135 | 140 | 142 | 142 | 137 | 3064436
118 | Bibiyana-III 400 MW CCPP | 403 | 403 | 403 | 402 | 400 | 400 | 402 | 402 | 400 | 395 | 404 | 404 | 396 | 402 | 405 | 399 | 402 | 400 |  | 391 | 403 | 402 | 403 | 403 | 403 | 404 | 9560000
| Jamalpur 115 MW PP (United) | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 48 | 48 | 48 | 48 | 77 |  | 78 | 77 | 78 | 78 | 79 | 79 | 49 | 1347600
| Anwara 300 MW PP (United) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 50 | 51 | 51 | 52 | 52 | 68 | 69 | 52 | 52 | 52 | 52 |  | 207 | 212 | 214 | 214 | 214 | 52 | 52 | 1630909
| Juldah unit-2 (Acorn) | 47 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 51 | 95 | 96 | 98 | 100 | 100 | 100 | 949440
| Anlima Energy Ltd. | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 |  | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 2608200
| Bhairob 54.5 MW | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 889560
| Spectra Solar Plant Ltd. | [5 empty] | 1 | 7 | 10 | 23 | 21 | 34 | 28 | 24 | 14 | 15 | 8 | 2 | 1 | [8 empty] | 169284
| Chandpur 115(Doreen) | 73 | 73 | 73 | 64 | 73 | 73 | 73 | 74 | 74 | 73 | 73 | 74 | 73 | 69 | 72 | 72 | 73 | 73 |  | 73 | 74 | 73 | 74 | 73 | 73 | 74 | 1764480
| Kanchan Purbachal Power Generation Ltd. | 55 | 55 | 55 | 55 | 23 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 30 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1282680
Mirsharai 150 MW (Oil)
Mirsharai 150 MW (Gas)
120 | Eastern Zone Total | 6709 | 6647 | 6607 | 6575 | 6566 | 6430 | 6374 | 6246 | 6434 | 6481 | 6439 | 6570 | 6543 | 6411 | 6672 | 6764 | 6766 | 6951 | 0 | 8059 | 8092 | 8142 | 8303 | 8045 | 8046 | 7306 | 166538152
121
122 | o
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 0 |  |  |  |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 318720
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 30 | 30 | 30 | 30 | 30 | 0 | [11 empty] | 9 |  | 39 | 50 | 45 | 45 | 43 | 42 | 36 | 387360
| Khulna 225 MW CCPP | 217 | 218 | 218 | 218 | 218 | 215 | 230 | 229 | 229 | 228 | 228 | 226 | 229 | 226 | 224 | 224 | 227 | 227 |  | 226 | 229 | 231 | 230 | 230 | 228 | 228 | 5433600
129 | Rupsha 105 MW PP (Orion rupsha) | [8 empty] | 17 | 17 | 17 | 10 | 17 | 17 | 17 | 25 | 36 | 36 |  | 53 | 53 | 53 | 53 | 54 | 54 | 35 | 479520
130 | Mongla Orion 100 MW Solar PP |  |  |  |  | 0 | 3 | 7 | 27 | 15 | 60 | 51 | 17 | 71 | 63 | 27 | 11 | 11 | 1 | [8 empty] | 341280
131
132 | United Payra Power Ltd. | [14 empty] | 36 | 64 | 81 | 81 |  | 85 | 116 | 116 | 116 | 127 | 145 | 146 | 967200
133 | Bhola Nutan Biddut BD LTD (GAS) | 220 | 220 | 220 | 220 | 221 | 217 | 220 | 223 | 222 | 218 | 222 | 212 | 208 | 218 | 222 | 220 | 219 | 220 |  | 222 | 219 | 219 | 220 | 220 | 10 | 0 | 5001873
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 16 | 16 | 0 | [9 empty] | 16 | 16 | 49 | 80 | 80 | 80 |  | 80 | 96 | 96 | 110 | 110 | 110 | 110 | 944256
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 88 | 88 | 88 | 89 | 89 | 86 | 88 | 88 | 88 | 88 | 88 | 86 | 88 | 88 | 88 | 88 | 88 | 88 |  | 88 | 88 | 88 | 88 | 88 | 0 | 0 | 1961000
140 | Bhola 33 MW PP (Venture) | 25 | 23 | 22 | 19 | 18 | 13 | 12 | 15 | 15 | 16 | 10 | 15 | 15 | 11 | 13 | 16 | 17 | 16 |  | 24 | 27 | 28 | 27 | 28 | 29 | 28 | 444592
141 | Noapara 100 MW PP (Bangla Trac) | 94 | 94 | 94 | 94 | 94 | 0 | 20 | 94 | 94 | 94 | 50 | 94 | 95 | 65 | 95 | 92 | 96 | 10 |  | 25 | 96 | 96 | 96 | 60 | 80 | 96 | 1925760
142 | Noapara 40 MW PP (Khanjahan Ali) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 187875
143 | Gopalganj 100 MW Peaking PP | 60 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 7 | [10 empty] | 34 | 40 | 67 | 72 | 71 | 71 | 68 | 733440
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | 89 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 67 | 67 | 67 | 67 | 67 | 67 | 71 | 89 | 98 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2278368
146 | Bheramara HVDC | 907 | 907 | 902 | 905 | 905 | 905 | 905 | 906 | 907 | 906 | 907 | 906 | 906 | 907 | 906 | 906 | 907 | 906 |  | 906 | 905 | 906 | 907 | 907 | 906 | 907 | 21895272
147 | Bheramara 410 MW CCPP | 160 | 160 | 165 | 165 | 165 | 170 | 165 | 170 | 155 | 155 | 150 | 140 | 145 | 135 | 135 | 135 | 140 | 145 |  | 140 | 140 | 145 | 145 | 155 | 160 | 155 | 3774816
148 | Payra 1320 MW | 600 | 560 | 540 | 540 | 540 | 500 | 500 | 490 | 490 | 490 | 490 | 490 | 490 | 490 | [8 empty] | 70 | 170 | 210 | 230 | 8721200
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 251 | 251 | 250 |  | 250 | 251 | 251 | 251 | 250 | 250 | 250 | 6099400
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 |  | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 742192
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 0 | 1 | 4 | 5 | 5 | 3 | 3 | 2 | 4 | 2 | 1 | 0 | [8 empty] | 35820
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 165 | 165 | 164 | 164 | 164 | 163 | 164 | 164 | 150 | 152 | 152 | 152 | 151 | 152 | 152 | 153 | 152 | 152 |  | 152 | 152 | 152 | 152 | 152 | 152 | 152 | 3946091
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
| Sirajgonj 225 MW CCPP Unit-2 (Oil) | 215 | 217 | 218 | 219 | 220 | 220 | 215 | 220 | 212 | 209 | 208 | 209 | 212 | 211 | 207 | 210 | 170 | 170 |  | 177 | 216 | 217 | 218 | 215 | 216 | 212 | 5229527
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 153 | 153 | 155 | 156 | 157 | 157 | 154 | 153 | 149 | 147 | 146 | 143 | 143 | 142 | 141 | 141 | 141 | 141 |  | 143 | 146 | 146 | 148 | 149 | 149 | 150 | 3808200
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 319 | 318 | 335 | 335 | 331 | 340 | 329 | 318 | 298 | 279 | 286 | 255 | 257 | 257 | 243 | 246 | 252 | 264 |  | 268 | 281 | 286 | 308 | 302 | 303 | 323 | 7080654
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | 26 | 26 | 26 | 26 | 40 | 35 | 36 | 36 | 36 | 34 | 31 | 31 | 31 | 35 | 35 | 35 | 35 | 38 |  | 38 | 40 | 40 | 41 | 41 | 30 | 25 | 742244
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 18 | 18 | 18 | 17 | 17 | 17 | 17 | 17 | 18 | 18 |  | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 441600
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 262854
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | [16 empty] | 8 | 8 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 242380
167 | Katakhali 50 MW Peaking PP | 32 | 32 | 24 | 24 | 24 | 24 | 24 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 24 | 24 | 32 | 32 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 676290
168 | Santahar 50 MW Peaking PP | 34 | 33 | 33 | 33 | 33 | 33 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 14 | 26 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 739079
169 | Natore 52 MW PP (Rajlanka) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 2 | 8 | 8 | 8 | 8 | 8 | 8 |  | 16 | 16 | 16 | 16 | 16 | 16 | 8 | 223344
170 | Chapainawabganj 100 MW Peaking PP | 81 | 81 | 45 | 45 | 45 | 45 | 45 | 46 | 46 | 46 | 46 | 46 | 46 | 52 | 52 | 52 | 52 | 52 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1364440
171 | Baghabari 200 MW PP (Paramount) | 178 | 178 | 178 | 177 | 177 | 50 | 71 | 178 | 177 | 177 | 175 | 176 | 176 | 177 | 178 | 178 | 178 | 80 |  | 68 | 100 | 100 | 133 | 140 | 159 | 177 | 3797363
| Bagura 113 MW PP (Confidence)-2 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 77 | 94 | 94 |  | 94 | 94 | 94 | 94 | 94 | 94 | 50 | 1686432
172 | Confidence Power Bogura Unit-1 113 MW | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 90 | 95 | 95 |  | 95 | 95 | 95 | 95 | 95 | 95 | 55 | 1639104
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 65 | 55 | 55 | 55 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 55 | 55 | 55 | 55 | 54 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1333478
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1 | 1 | 4 | 4 | 6 | 7 | 7 | 7 | 6 | 4 | 2 | 1 | [8 empty] | 45440
178 | Energypac Power Venture Thakurgaon Ltd. | 52 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 72 |  | 72 | 72 | 72 | 72 | 72 | 72 | 0 | 948288
178