## Forecast
8 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2022-08-15 | Monday
|  |  | Date (day): | 2022-08-15 |  | Monday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11469.6 | MW |  |  | (b) At Evening Peak Hour : |  | 13830 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2022-08-14 | 2022-08-15 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 300 | 300 | 300 | 300 |  | 65 | Engine problem
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 86 | 80 | 80 | 80 |  | 28 | Engine problem
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 407 | 407 | 412 | 412
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 333 | 336 | 330 | 330 | 30 |  | Gas shortage
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 225 | 225 | 225 |  | Gas shortage & GT-2 S/D
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 8 | 50 | 30 | 50 | 50 |  | Fuel shortage
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 0 | 0 | 0 | 0 |  | 102 | Under maint
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 30 | 30 | 30 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 19 | 19 | 19 |  | 3 | Engine problem
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 93 | 37 | 95 | 95 | 115 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 8 | 49 | 8 | 50 | 50 |  | Fuel shortage
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 8 | 50 | 8 | 50 | 52 |  | Fuel shortage
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 18 | 35 | 17 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 16 | 128 | 16 | 128 |  | 21 | Engine problem
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 35 | 35 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 51 | 45 | 45 | 45 |  | 35 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 28 | 30 | 30 | 30
| 29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 41 | 41 | 41 | 41 |  | 11 | Engine problem
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 80 | 278 | 80 | 275 |  | 25 | Engine problem
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 11 | 303 | 300 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 91 | 30 | 60 | 96
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 94 | 70 | 50 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 35 | 142 | 43 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 88 | 105 | 88 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 17 | 53 | 17 | 50 | 54 |  | Fuel shortage
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 35 | 162 | 35 | 162
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 3 | 0 | 30 | 0
| 40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 55 | 55 | 55 | 55
|  | Dhaka area Total |  |  |  |  | 6263 | 5847 | 2464 | 3363 | 2747 | 3579 | 1297 | 970
| 41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 110 | 110 | 110 | 110 | 70 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 25 | 25 | 25 | 25
| 43 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 7 | 0 | 20 | 0
| 44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 42 | 19 | 42 |  | 8 | Engine problem
| 45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 101 | 101 | 101 | 101 |  | 129 | Low Water Level
| 46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | S/D due to HGPI
| 47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
| 48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 17 | 105 | 17 | 105
| 49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 26 | 26 | 26 | 26 | 72 |  | Fuel shortage
| 50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 17 | 51 | 17 | 51 | 51 |  | Fuel shortage
| 51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 33 | 33 | 33 | 33 | 67 |  | Fuel shortage
| 52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 21 | 90 | 21 | 90 |  | 10 | Engine problem
| 53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 15 | 15 | 15 | 15 |  | 7 | Engine problem
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 6 | 26 | 30 | 30
| 54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 11 | 85 | 12 | 85 |  | 23 | Fuel shortage
| 55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 2 | 0 | 5 | 0
| 56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 123 | 214 | 118 | 300
| 57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 36 | 36 | 36 | 36 |  | 18 | Engine problem
| 58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 35 | 55 | 55 | 55 | 55 |  | Fuel shortage
| 59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 20 | 100 | 20 | 100
| 60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 107 | 107 | 107 | 107 |  | 9 | Engine problem
|  | Mirsharai 150 MW |  | Gas/HSD | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 712 | 1221 | 787 | 1311 | 495 | 579
| 61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 195 | 211 | 200 | 211
| 63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 280 | 325 | 300 | 325 | 35 |  | Gas shortage
| 64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 280 | 270 | 280 | 300 | 60 |  | Gas shortage
|  | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+136*1 | 284 | 284 | 0 | 0 | 0 | 0 |  |  | On test.
| 65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 39 | 35 | 35 | 35 |  | 10 | Engine problem
| 66 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 55 | 53 | 52 | 55 | 55
| 67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 130 | 132 | 100 | 132 |  | 18 | Engine problem
| 70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 37 | 39 | 40 | 40 |  | 12 | Engine problem
| 71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 30 | 136 | 130 | 136 |  | 27 | Engine problem, Gas shortage
| 72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 200 | 200 | 200 | 200
| 73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 21 | 22 | 22
| 74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 10 | 10 | 10 | 10
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 128 | 162 | 143 | 166
| 75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 30 | 33 | 33 | 33
| 76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 | 52 |  | Fuel shortage
| 77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 21 | 20 | 21 |  | 4 | Engine problem
| 78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 52 | 30 | 100 | 200
| 79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 0 | 0 | 114 |  | Fuel shortage
| 80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 29 | 57 | 30 | 57 | 56 |  | Fuel shortage
| 81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 35 | 35 | 35 | 35 |  | 19 | 33 kV feeder fault
| 82 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 61 | 73 | 74 | 75 | 40 |  | Fuel shortage
|  | Cumilla Area Total |  |  |  |  | 3193 | 3169 | 1687 | 1901 | 1866 | 2112 | 678 | 90
| 83 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 65 | 99 | 100 | 100 | 102 |  | Gas shortage
| 84 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 22 | 22 | 22
| 85 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0 |  | 8 | Under maint.
| 86 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 0 | 0 | 1.6 | 0
| 87 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 78 | 186 | 48 | 180 |  | 20 | Engine problem
| 88 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 69 | 79 | 78 | 100 |  | 15 | Engine problem
| 89 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 37 | 0 | 50 | 0
| 90 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 9 | 12 | 12 | 12 |  | 10 | Engine problem
|  | Mymensingh Area Total |  |  |  |  | 717 | 614 | 278 | 398 | 311.6 | 414 | 102 | 53
| 91 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 43 | 43 | 43 |  | 27 | Machine problem.
| 92 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 30 | 30 |  | 60 | Machine problem
| 93 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | ST under maint.
| 94 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
| 95 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 11 | 11 | 0 | 0 | 51 |  | Gas shortage
| 96 | Fenchuganj 44MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 10 | 10 | 10 | 10 | 40 |  | Gas shortage
| 97 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0
| 98 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 61 | 64 | 62 | 64
| 99 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 10 | 78 | 25 | 80
| 100 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
| 101 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 220 | 220 | 200 | 220
| 102 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Gas shortage
| 103 | Sylhet 50MW PP (EPL) |  | Gas | NENP | 27*2 | 50 | 50 | 11 | 17 | 11 | 17 | 33 |  | Gas shortage
| 104 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 8 | 8 | 8 | 8 | 17 |  | Gas shortage
| 105 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 280 | 270 | 300 | 300 |  |  | FGMO
| 106 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 400 | 402 | 400 | 400
| 107 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 7 | 9 | 9 | 9
| 108 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 375 | 391 | 400 | 400
|  | Sylhet Area Total |  |  |  |  | 2522 | 2477 | 1436 | 1523 | 1498 | 1581 | 161 | 680
| 109 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 895 | 892 | 912 | 912
| 110 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 0 | 16 | 16 | 66 | 49 |  | Fuel shortage
| 111 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 36 | 0 | 36 |  | 18 | Engine problem
| 112 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 229 | 231 | 225 | 225
| 113 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 70 | 0 | 70 |  | 39 | Engine problem
| 114 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 170 | 165 | 170 | 170 | 240 |  | Gas shortage
| 115 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 8 | 32 | 32 | 8 |  | Fuel shortage
| 116 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 20 | 10 | 90 | 90 |  | 10 | Engine problem
| 117 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 10 | 53 | 17 | 52 | 53 |  | Fuel shortage
| 118 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 89 | 70 | 90 | 105
| 119 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 24 | 0 | 100 | 0
|  | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
|  | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
|  | Khulna Area Total |  |  |  |  | 2388 | 2384 | 1437 | 1551 | 1652 | 1758 | 366 | 67
| 120 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 48 | 110 | 110 |  |  | Line O/L
| 121 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 12 | 23 | 15 | 23 |  | 17 | Engine problem
| 122 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 55 | 87 | 144 | 144
|  | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
| 123 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 460 | 490 | 620 | 620 |  |  | Line O/L
| 124 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 206 | 70 | 0 | 0
| 125 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 35 | 50 | 110 |  |  | Line O/L
|  | Barisal Area Total |  |  |  |  | 1958 | 1958 | 733 | 753 | 939 | 1007 | 0 | 17
| 126 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 127 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 24 | 32 | 32 |  | 20 | Engine problem
| 128 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 28 | 0 | 40 |  | 31 | Engine problem
| 129 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 130 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 34 | 42 | 42 | 42 |  | 8 | Engine problem
| 131 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 16 | 40 | 16 | 40 |  | 10 | Engine problem
| 132 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 152 | 153 | 150 | 160 | 50 |  | Gas shortage
| 133 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 130 | 130 | 220 | 220
| 134 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 156 | 147 | 150 | 150 | 70 |  | Gas shortage
| 135 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 333 | 328 | 330 | 330 | 84 |  | Gas shortage
| 136 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 33 | 33 | 33 |  | 17 | Engine problem
| 137 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 19 | 22 | 21 | 22
| 138 | Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 139 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 140 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 8 | 8 | 8 | 44 |  | Fuel shortage
| 141 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 45 | 80 | 50 | 80 |  | 24 | Engine problem
| 142 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 127 | 30 | 80 | 175 | 25 |  | Fuel shortage
| 143 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 50 | 94 | 50 | 94 |  | 19 | Engine problem
| 144 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 55 | 95 | 55 | 95 |  | 18 | Engine problem
| 145 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 4 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2129 | 1140 | 1265 | 1254 | 1532 | 444 | 147
| 146 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 70 | 83 | 70 | 83 | 85 |  | Machine problem
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
| 147 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 250 | 240 | 250 | 250 | 24 |  | Machine problem
| 148 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
| 149 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
| 150 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 69 | 112 | 70 | 113
| 151 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 3 | 0 | 8 | 0
| 152 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 0 | 72 | 17 | 90 |  | 25 | Fuel shortage
|  | Rangpur Area Total |  |  |  |  | 800 | 720 | 392 | 507 | 415 | 536 | 149 | 110
|  | Total |  |  |  |  | 22482 | 21680 | 10279 | 12482 | 11469.6 | 13830 | 3692 | 2713
| A. |  | 2022-08-14 | (Yesterday) |  |  |  |  | Sunday
| 1 | Highest Generation : |  |  | 12486 | MW at | 23:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 20:00 | hrs.
| 2 | Minimum Generation : |  |  | 10268 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 12750 | MW
| 3 | Day peak Generation : |  |  | 10279 | MW at | 9:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 12330.7 | MW
| 4 | Evening peak Generation : |  |  | 12482 | MW at | 20:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 247 | MW
| 5 | Total Energy Generation : |  | 266.6104 | MKWHr | By Solar | 0.6913 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
|  | By Gas : | 135.6987 | MKWHr |  | By Oil: | 82.3493 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 20.2616 | MKWHr |  | By Hydro: | 2.4165 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 3692 | MW | Dhaka | 4347.79 | 4287.79 |  | 60 |  | 18:00 |  | 223.0212
|  |  |  | For Plants S/D or M/C prob = |  |  | 2713 | MW | Chittagong | 1328.65 | 1328.65 |  | 0 |  | 19:00 |  | 508.7094
|  |  |  | Total = |  |  | 6405 | MW | Khulna | 1342.6 | 1342.6 |  | 0 |  | 19:30 |  | 363.1005
| 7 | Total Gas Supplied : |  |  | 1014.68 | MMCFD |  |  | Rajshahi | 1250 | 1250 |  | 0 |  | 20:00 |  | 246.9821
| 8 | Fuel Cost : | i) Gas : | Taka | 153530052.134 | ii) Oil : | Taka | 1217483631.51 | Comilla | 1223 | 1223 |  | 0 |  | 21:00 |  | 294.904
|  |  | iii) Coal : |  | 156299393.03 | Total | Taka | 1527313076.674 | Mymensingh | 1117 | 930 |  | 187 |  | 22:00 |  | 229.4722
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 14654.487 | MKWHr. | Sylhet | 601 | 601 |  | 0 |  | 23:00 |  | 197.217
|  | ii) During Peak Demand : |  |  | 182 | MW (E to W) at | 20:00 | hrs | Barisal | 267.66 | 267.66 |  | 0 |  | 24:00 |  | 410.1009
|  | iii) Maximum : |  |  | 182 | MW at | 20:00 | hrs | Rangpur | 853 | 853 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 31.8° C |  |  | Total | 12330.7 | 12083.7 |  | 247
| B. |  | 2022-08-15 | (Today) |  |  |  | Monday |  |  | Probable max. temperature in Dhaka |  |  | 34.0° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 13600 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 13830 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 11000 | MW
| 4 | Reserve(Generation end) |  |  |  | 230 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 290.3974 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 9926 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.6189 | MKWHr. | ii) HVDC Flow at Peak Time |  | 892 | MW at | 20:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.5741 | MKWHr. | iii) Maximum HVDC Flow : |  | 896 | MW at | 3:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 95.95 |  | (b) Today: | 95.95 |  | (c) Rule Curve: |  | 93.48
.

## YesterdayGen
2022-08-14
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 300 | 87 | 0 | 404 | 339 |  | 0 | 225 | 0 | 7 | 0 | 30 | 0 | 0 | 95 | 8 | 8 | 16 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 22 | 25 | 26 | 33 | 33 | 41 | 0 | 38 | 65 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 51 | 33 | 12 | 6 | 15 | 30 | 0 | 0 | 0 | 290 | 290 | 187 | 8 | 49 | 40 | 41 | 0 | 51 | 0 | 40 | 0 | 22 | 10 | 33 | 20 | 160 | 102 | 0 | 21 | 0 | 43 | 0 | 31 | 10 | 0 | 0 | 64 | 81 | 0 | 214 | 0 | 11 | 7 | 300 | 8 | 0 | 100 | 80 | 0 | 90 | 49 | 99 | 35 | 0 | 21 | 200 | 137 | 403 | 49 | 88 | 17 | 0 | 52 | 36 | 55 | 0 | 30 | 50 | 400 | 0 | 0 | 76 | 89 | 0 | 35 | 0 | 67 | 55 | 0 | 0 | 0 |  | 895 | 0 | 160 | 0 | 16 | 226 | 0 | 0 | 20 | 65 | 8 | 60 | 23 | 16 | 0 | 0 | 0 | 16 | 28 | 45 | 0 | 34 | 24 | 8 | 33 | 21 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 152 | 0 | 0 | 191 | 0 | 91 | 150 | 0 | 313 | 0 | 174 | 50 | 105 | 70 | 0 | 0 | 55 | 580 | 221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6873 | 4111 | 10984 | 3972 | 895 | 1799 | 554 | 1890 | 830 | 103 | 417 | 555 | 160 | 0 | 1581.4227 | 95.95
2:00 | 0 | 0 | 0 | 180 | 300 | 87 | 0 | 408 | 338 |  | 0 | 225 | 0 | 8 | 0 | 30 | 0 | 0 | 94 | 8 | 8 | 16 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 22 | 25 | 27 | 33 | 33 | 41 | 0 | 36 | 65 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 51 | 33 | 12 | 6 | 15 | 30 | 0 | 0 | 0 | 290 | 290 | 182 | 8 | 50 | 40 | 42 | 0 | 51 | 0 | 40 | 0 | 22 | 10 | 33 | 20 | 160 | 102 | 0 | 21 | 0 | 43 | 0 | 31 | 10 | 0 | 0 | 64 | 81 | 0 | 214 | 0 | 11 | 7 | 305 | 8 | 0 | 50 | 80 | 0 | 90 | 49 | 95 | 35 | 0 | 21 | 200 | 137 | 401 | 50 | 88 | 17 | 0 | 52 | 36 | 52 | 0 | 29 | 20 | 400 | 0 | 0 | 35 | 89 | 0 | 35 | 0 | 74 | 55 | 0 | 0 | 0 |  | 895 | 0 | 160 | 0 | 16 | 227 | 0 | 0 | 20 | 65 | 8 | 60 | 16 | 16 | 0 | 0 | 0 | 16 | 28 | 45 | 0 | 34 | 16 | 8 | 33 | 21 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 152 | 0 | 0 | 216 | 0 | 91 | 150 | 0 | 312 | 0 | 174 | 50 | 105 | 70 | 0 | 0 | 55 | 570 | 221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6754 | 4111 | 10865 | 3970 | 895 | 1796 | 500 | 1824 | 820 | 101 | 443 | 572 | 160 | 0 | 1506.7751 | 95.95
3:00 | 0 | 0 | 0 | 180 | 300 | 88 | 0 | 408 | 339 |  | 0 | 225 | 0 | 8 | 0 | 30 | 0 | 0 | 97 | 8 | 8 | 16 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 22 | 25 | 27 | 33 | 33 | 41 | 0 | 35 | 65 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 24 | 33 | 12 | 6 | 15 | 30 | 0 | 0 | 0 | 290 | 290 | 182 | 8 | 50 | 38 | 42 | 0 | 51 | 0 | 40 | 0 | 22 | 10 | 33 | 20 | 158 | 94 | 0 | 21 | 0 | 43 | 0 | 31 | 10 | 0 | 0 | 63 | 10 | 0 | 221 | 0 | 11 | 7 | 300 | 8 | 0 | 50 | 80 | 0 | 50 | 49 | 95 | 34 | 0 | 21 | 200 | 137 | 402 | 50 | 88 | 17 | 0 | 52 | 36 | 50 | 0 | 29 | 20 | 393 | 0 | 0 | 35 | 89 | 0 | 35 | 0 | 74 | 55 | 0 | 0 | 0 |  | 896 | 0 | 160 | 0 | 16 | 224 | 0 | 0 | 20 | 65 | 8 | 60 | 10 | 16 | 0 | 0 | 0 | 16 | 28 | 44 | 0 | 34 | 16 | 8 | 33 | 21 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 152 | 0 | 0 | 215 | 0 | 90 | 150 | 0 | 336 | 0 | 174 | 50 | 85 | 70 | 0 | 0 | 55 | 570 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6600 | 4103 | 10703 | 3963 | 896 | 1739 | 459 | 1801 | 820 | 100 | 439 | 543 | 158 | 0 | 1379.5978 | 95.95
4:00 | 0 | 0 | 0 | 180 | 300 | 88 | 0 | 407 | 332 |  | 0 | 225 | 0 | 8 | 0 | 30 | 0 | 0 | 97 | 8 | 8 | 16 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 22 | 25 | 27 | 33 | 33 | 41 | 0 | 36 | 65 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 17 | 33 | 13 | 6 | 15 | 30 | 0 | 0 | 0 | 290 | 290 | 188 | 8 | 50 | 38 | 40 | 0 | 51 | 0 | 40 | 0 | 22 | 10 | 33 | 20 | 154 | 95 | 0 | 21 | 0 | 43 | 0 | 31 | 10 | 0 | 0 | 64 | 10 | 0 | 221 | 0 | 11 | 7 | 320 | 8 | 0 | 50 | 80 | 0 | 92 | 49 | 95 | 28 | 0 | 21 | 200 | 137 | 402 | 50 | 88 | 17 | 0 | 52 | 36 | 45 | 0 | 28 | 20 | 400 | 14 | 0 | 35 | 89 | 0 | 35 | 0 | 74 | 55 | 0 | 0 | 0 |  | 896 | 0 | 170 | 0 | 16 | 226 | 0 | 0 | 20 | 60 | 8 | 60 | 11 | 16 | 0 | 0 | 0 | 16 | 28 | 44 | 0 | 34 | 16 | 8 | 0 | 21 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 152 | 0 | 0 | 213 | 0 | 90 | 150 | 0 | 345 | 0 | 174 | 50 | 85 | 69 | 0 | 0 | 55 | 570 | 221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6660 | 4085 | 10745 | 3987 | 896 | 1761 | 501 | 1803 | 820 | 101 | 439 | 496 | 154 | 0 | 1156.5766 | 95.95
5:00 | 0 | 0 | 0 | 180 | 300 | 88 | 0 | 408 | 334 |  | 0 | 225 | 0 | 8 | 0 | 30 | 0 | 0 | 97 | 8 | 8 | 16 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 22 | 25 | 27 | 33 | 33 | 41 | 0 | 36 | 65 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 17 | 33 | 12 | 6 | 15 | 37 | 0 | 0 | 0 | 280 | 260 | 198 | 8 | 50 | 38 | 40 | 0 | 51 | 0 | 40 | 0 | 22 | 10 | 33 | 20 | 146 | 101 | 0 | 21 | 0 | 43 | 0 | 31 | 10 | 0 | 0 | 63 | 10 | 0 | 221 | 0 | 11 | 7 | 290 | 8 | 0 | 50 | 80 | 0 | 92 | 49 | 93 | 32 | 0 | 21 | 200 | 137 | 402 | 50 | 88 | 17 | 0 | 52 | 36 | 55 | 0 | 28 | 20 | 400 | 0 | 0 | 35 | 94 | 0 | 35 | 0 | 74 | 55 | 0 | 0 | 0 |  | 894 | 0 | 175 | 0 | 16 | 226 | 0 | 0 | 20 | 22 | 0 | 60 | 13 | 0 | 0 | 0 | 0 | 16 | 24 | 44 | 0 | 34 | 16 | 8 | 0 | 21 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 152 | 0 | 0 | 217 | 0 | 91 | 151 | 0 | 345 | 0 | 174 | 50 | 85 | 70 | 0 | 0 | 55 | 560 | 221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6609 | 4021 | 10630 | 3969 | 894 | 1742 | 500 | 1784 | 810 | 101 | 443 | 458 | 146 | 0 | 986.0853 | 95.95
6:00 | 0 | 0 | 0 | 180 | 300 | 88 | 0 | 407 | 333 |  | 0 | 225 | 0 | 7 | 0 | 30 | 0 | 0 | 92 | 8 | 8 | 16 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 22 | 25 | 27 | 33 | 33 | 41 | 0 | 33 | 65 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 17 | 33 | 14 | 6 | 15 | 37 | 0 | 0 | 0 | 280 | 260 | 209 | 8 | 50 | 38 | 40 | 0 | 51 | 0 | 40 | 0 | 22 | 10 | 33 | 20 | 138 | 103 | 0 | 21 | 0 | 43 | 0 | 31 | 10 | 0 | 0 | 64 | 10 | 0 | 221 | 0 | 11 | 7 | 280 | 8 | 0 | 50 | 80 | 0 | 50 | 49 | 50 | 35 | 0 | 21 | 200 | 137 | 401 | 49 | 88 | 17 | 0 | 52 | 36 | 55 | 0 | 28 | 20 | 400 | 0 | 1 | 35 | 95 | 0 | 35 | 0 | 74 | 55 | 0 | 0 | 0 |  | 895 | 0 | 175 | 0 | 0 | 228 | 0 | 0 | 0 | 0 | 0 | 60 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 0 | 34 | 16 | 8 | 0 | 21 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 152 | 0 | 0 | 215 | 0 | 91 | 157 | 0 | 345 | 0 | 120 | 50 | 85 | 70 | 0 | 0 | 55 | 520 | 212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6514 | 3824 | 10338 | 3982 | 895 | 1719 | 361 | 1772 | 770 | 98 | 443 | 374 | 138 | 1 | 886.5551 | 95.95
7:00 | 0 | 0 | 0 | 180 | 300 | 86 | 0 | 407 | 331 |  | 0 | 225 | 0 | 8 | 0 | 30 | 0 | 0 | 93 | 8 | 8 | 16 | 0 | 0 | 0 | 0 | 18 | 55 | 35 | 22 | 25 | 27 | 33 | 32 | 41 | 0 | 35 | 65 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 17 | 33 | 13 | 0 | 15 | 39 | 0 | 0 | 0 | 280 | 280 | 209 | 8 | 30 | 38 | 40 | 0 | 51 | 0 | 39 | 0 | 22 | 10 | 33 | 20 | 124 | 94 | 0 | 21 | 0 | 43 | 0 | 31 | 10 | 0 | 0 | 63 | 10 | 0 | 220 | 0 | 11 | 7 | 280 | 8 | 0 | 50 | 80 | 101 | 94 | 49 | 95 | 35 | 2 | 21 | 200 | 138 | 401 | 49 | 88 | 17 | 1 | 52 | 36 | 55 | 0 | 28 | 20 | 400 | 0 | 10 | 35 | 107 | 0 | 35 | 7 | 74 | 55 | 0 | 0 | 0 |  | 896 | 0 | 175 | 0 | 0 | 228 | 0 | 0 | 0 | 0 | 0 | 60 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 34 | 16 | 8 | 0 | 21 | 0 | 11 | 48 | 0 | 250 | 0 | 0 | 152 | 0 | 0 | 176 | 0 | 91 | 158 | 0 | 346 | 0 | 124 | 50 | 85 | 70 | 0 | 1 | 55 | 500 | 218 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 |  | 6687 | 3829 | 10516 | 3972 | 896 | 1723 | 555 | 1762 | 798 | 100 | 404 | 335 | 124 | 23 | 476.4543 | 95.95
8:00 | 0 | 0 | 0 | 180 | 300 | 86 | 0 | 407 | 332 |  | 0 | 225 | 0 | 7 | 0 | 30 | 0 | 0 | 97 | 8 | 8 | 16 | 0 | 0 | 0 | 0 | 18 | 55 | 35 | 22 | 25 | 27 | 33 | 32 | 41 | 0 | 35 | 65 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 0 | 26 | 17 | 33 | 13 | 0 | 15 | 16 | 0 | 0 | 0 | 280 | 280 | 200 | 8 | 30 | 37 | 53 | 0 | 51 | 0 | 39 | 0 | 19 | 5 | 33 | 20 | 130 | 82 | 0 | 0 | 0 | 43 | 0 | 31 | 10 | 0 | 0 | 63 | 10 | 0 | 220 | 0 | 11 | 7 | 275 | 8 | 0 | 50 | 80 | 52 | 50 | 77 | 50 | 35 | 3 | 21 | 200 | 134 | 401 | 69 | 88 | 17 | 1 | 118 | 36 | 45 | 0 | 29 | 20 | 400 | 3 | 14 | 35 | 107 | 0 | 35 | 12 | 72 | 55 | 0 | 0 | 0 |  | 895 | 0 | 175 | 0 | 0 | 227 | 0 | 0 | 0 | 0 | 0 | 30 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 34 | 16 | 8 | 0 | 21 | 0 | 11 | 68 | 0 | 250 | 0 | 0 | 152 | 0 | 0 | 140 | 0 | 50 | 157 | 0 | 336 | 0 | 80 | 50 | 88 | 70 | 0 | 2 | 55 | 470 | 223 | 0 | 0 | 1 | 10 | 0 | 0 | 0 | 0 |  | 6593 | 3675 | 10268 | 3894 | 895 | 1706 | 332 | 1854 | 788 | 100 | 367 | 299 | 130 | 43 | #REF! | 95.95
9:00 | 0 | 0 | 0 | 180 | 300 | 86 | 0 | 407 | 333 |  | 0 | 225 | 0 | 8 | 0 | 30 | 0 | 0 | 93 | 8 | 8 | 16 | 0 | 0 | 0 | 0 | 18 | 55 | 35 | 0 | 25 | 26 | 33 | 28 | 41 | 0 | 36 | 65 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 9 | 26 | 17 | 33 | 11 | 0 | 15 | 6 | 0 | 0 | 0 | 280 | 280 | 195 | 8 | 30 | 39 | 53 | 0 | 51 | 0 | 37 | 0 | 19 | 10 | 30 | 20 | 128 | 65 | 0 | 20 | 0 | 43 | 0 | 11 | 10 | 0 | 0 | 61 | 10 | 0 | 220 | 0 | 11 | 7 | 280 | 8 | 0 | 52 | 80 | 11 | 91 | 78 | 94 | 35 | 7 | 21 | 200 | 130 | 400 | 69 | 88 | 17 | 2 | 123 | 36 | 35 | 0 | 29 | 20 | 375 | 17 | 37 | 35 | 107 | 0 | 35 | 3 | 61 | 55 | 0 | 0 | 0 |  | 895 | 0 | 170 | 0 | 0 | 229 | 0 | 0 | 0 | 0 | 0 | 55 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 34 | 16 | 8 | 0 | 19 | 0 | 11 | 70 | 0 | 250 | 0 | 0 | 152 | 0 | 0 | 130 | 0 | 20 | 156 | 0 | 333 | 10 | 127 | 50 | 89 | 69 | 0 | 3 | 55 | 460 | 206 | 0 | 0 | 4 | 24 | 0 | 0 | 0 | 0 |  | 6577 | 3702 | 10279 | 3856 | 895 | 1661 | 395 | 1867 | 780 | 101 | 359 | 287 | 128 | 80 | #REF! | 95.95
10:00 | 0 | 0 | 0 | 180 | 300 | 86 | 0 | 405 | 324 |  | 0 | 225 | 0 | 8 | 0 | 30 | 0 | 0 | 95 | 8 | 8 | 16 | 0 | 0 | 0 | 0 | 18 | 55 | 35 | 0 | 25 | 26 | 33 | 28 | 32 | 0 | 35 | 65 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 17 | 33 | 12 | 0 | 15 | 5 | 0 | 0 | 0 | 280 | 260 | 205 | 8 | 30 | 36 | 49 | 0 | 43 | 0 | 40 | 0 | 19 | 10 | 30 | 20 | 122 | 62 | 0 | 20 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 58 | 10 | 0 | 221 | 0 | 11 | 7 | 300 | 8 | 0 | 51 | 80 | 108 | 91 | 78 | 93 | 35 | 2 | 21 | 200 | 134 | 398 | 69 | 70 | 17 | 3 | 124 | 36 | 55 | 0 | 28 | 20 | 395 | 17 | 43 | 35 | 107 | 0 | 31 | 16 | 72 | 55 | 0 | 0 | 0 |  | 895 | 0 | 165 | 0 | 0 | 228 | 0 | 0 | 0 | 0 | 0 | 30 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 34 | 16 | 8 | 0 | 18 | 0 | 11 | 65 | 0 | 250 | 0 | 0 | 152 | 0 | 0 | 130 | 0 | 10 | 152 | 0 | 324 | 17 | 60 | 50 | 71 | 69 | 0 | 5 | 55 | 460 | 220 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 |  | 6658 | 3553 | 10211 | 3812 | 895 | 1640 | 413 | 1864 | 775 | 100 | 358 | 290 | 122 | 72 | #REF! | 95.95
11:00 | 0 | 0 | 0 | 180 | 300 | 83 | 0 | 406 | 342 |  | 0 | 225 | 0 | 7 | 0 | 30 | 0 | 0 | 97 | 8 | 8 | 16 | 0 | 0 | 0 | 0 | 18 | 55 | 35 | 0 | 25 | 26 | 33 | 28 | 32 | 0 | 37 | 65 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 17 | 33 | 12 | 0 | 15 | 3 | 0 | 0 | 0 | 280 | 260 | 201 | 8 | 30 | 36 | 47 | 0 | 43 | 0 | 40 | 0 | 19 | 10 | 30 | 20 | 128 | 62 | 0 | 22 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 55 | 10 | 0 | 221 | 0 | 11 | 7 | 295 | 8 | 0 | 50 | 80 | 100 | 91 | 78 | 25 | 35 | 4 | 21 | 200 | 132 | 370 | 69 | 70 | 17 | 2 | 124 | 36 | 55 | 0 | 29 | 20 | 383 | 17 | 46 | 35 | 96 | 0 | 17 | 9 | 73 | 55 | 0 | 0 | 0 |  | 895 | 0 | 160 | 0 | 26 | 227 | 0 | 0 | 0 | 0 | 0 | 20 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 34 | 24 | 8 | 0 | 10 | 0 | 11 | 70 | 0 | 250 | 0 | 0 | 152 | 0 | 0 | 138 | 0 | 14 | 147 | 0 | 318 | 17 | 60 | 50 | 71 | 68 | 0 | 7 | 55 | 460 | 220 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 |  | 6524 | 3581 | 10105 | 3750 | 895 | 1636 | 340 | 1863 | 780 | 102 | 365 | 306 | 128 | 78 | #REF! | 95.95
12:00 | 0 | 0 | 0 | 180 | 300 | 80 | 0 | 406 | 348 |  | 0 | 225 | 0 | 8 | 0 | 30 | 0 | 0 | 67 | 8 | 8 | 16 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 0 | 25 | 0 | 33 | 28 | 32 | 0 | 37 | 65 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 28 | 17 | 33 | 12 | 0 | 15 | 3 | 0 | 0 | 0 | 300 | 290 | 206 | 8 | 30 | 35 | 48 | 0 | 51 | 0 | 39 | 0 | 19 | 0 | 30 | 18 | 138 | 62 | 0 | 22 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 60 | 10 | 0 | 221 | 0 | 11 | 5 | 290 | 8 | 0 | 70 | 107 | 49 | 25 | 78 | 25 | 60 | 11 | 21 | 200 | 127 | 377 | 68 | 70 | 17 | 6 | 123 | 36 | 55 | 0 | 28 | 20 | 393 | 17 | 45 | 55 | 107 | 0 | 17 | 17 | 73 | 55 | 0 | 0 | 0 |  | 895 | 0 | 160 | 0 | 32 | 231 | 0 | 0 | 0 | 0 | 0 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 34 | 24 | 8 | 0 | 16 | 0 | 11 | 65 | 0 | 250 | 0 | 0 | 152 | 0 | 0 | 195 | 0 | 87 | 145 | 0 | 305 | 17 | 50 | 57 | 71 | 82 | 0 | 7 | 55 | 470 | 184 | 0 | 0 | 3 | 9 | 15 | 0 | 0 | 0 |  | 6562 | 3704 | 10266 | 3756 | 895 | 1600 | 306 | 1998 | 785 | 102 | 426 | 357 | 138 | 98 | #REF! | 95.95
13:00 | 0 | 0 | 0 | 180 | 300 | 80 | 0 | 407 | 311 |  | 0 | 225 | 0 | 8 | 0 | 40 | 0 | 0 | 90 | 8 | 8 | 16 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 17 | 33 | 28 | 32 | 0 | 38 | 65 | 105 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 17 | 33 | 31 | 0 | 15 | 3 | 0 | 0 | 0 | 350 | 270 | 206 | 8 | 62 | 35 | 47 | 0 | 51 | 0 | 45 | 0 | 22 | 0 | 30 | 18 | 138 | 61 | 0 | 20 | 1 | 43 | 0 | 0 | 0 | 0 | 0 | 55 | 10 | 0 | 221 | 0 | 11 | 7 | 290 | 8 | 0 | 60 | 253 | 54 | 50 | 78 | 25 | 137 | 5 | 21 | 200 | 114 | 404 | 68 | 70 | 17 | 3 | 141 | 36 | 55 | 0 | 29 | 20 | 385 | 17 | 48 | 108 | 107 | 0 | 29 | 5 | 59 | 55 | 0 | 0 | 0 |  | 894 | 0 | 155 | 0 | 16 | 229 | 0 | 0 | 0 | 0 | 8 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 5 | 38 | 0 | 34 | 24 | 8 | 0 | 16 | 0 | 11 | 60 | 0 | 250 | 0 | 0 | 152 | 0 | 0 | 150 | 0 | 90 | 144 | 0 | 302 | 17 | 20 | 92 | 70 | 95 | 0 | 5 | 95 | 470 | 186 | 0 | 0 | 2 | 17 | 17 | 0 | 0 | 0 |  | 6984 | 3708 | 10692 | 3891 | 894 | 1563 | 299 | 2388 | 780 | 103 | 379 | 321 | 138 | 86 | 376 | 95.95
14:00 | 0 | 0 | 0 | 180 | 300 | 80 | 0 | 406 | 317 |  | 0 | 225 | 0 | 8 | 0 | 40 | 0 | 0 | 54 | 8 | 8 | 16 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 17 | 33 | 28 | 32 | 0 | 37 | 65 | 105 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 17 | 33 | 31 | 0 | 15 | 2 | 0 | 0 | 0 | 310 | 290 | 202 | 8 | 84 | 35 | 50 | 0 | 51 | 0 | 45 | 0 | 22 | 10 | 33 | 20 | 150 | 61 | 0 | 22 | 1 | 43 | 0 | 0 | 0 | 0 | 0 | 55 | 10 | 0 | 221 | 0 | 11 | 7 | 290 | 8 | 0 | 102 | 132 | 52 | 75 | 78 | 25 | 54 | 14 | 21 | 200 | 117 | 405 | 68 | 88 | 17 | 4 | 142 | 36 | 55 | 0 | 28 | 20 | 390 | 17 | 14 | 108 | 92 | 0 | 35 | 4 | 71 | 39 | 0 | 0 | 0 |  | 895 | 0 | 155 | 0 | 16 | 227 | 0 | 0 | 0 | 0 | 8 | 81 | 11 | 0 | 0 | 0 | 0 | 0 | 6 | 38 | 0 | 34 | 24 | 8 | 33 | 17 | 0 | 0 | 64 | 0 | 249 | 0 | 0 | 152 | 0 | 0 | 160 | 0 | 60 | 142 | 0 | 292 | 17 | 50 | 94 | 70 | 95 | 0 | 7 | 95 | 470 | 184 | 0 | 0 | 0 | 31 | 17 | 0 | 0 | 0 |  | 6831 | 3802 | 10633 | 3923 | 895 | 1555 | 364 | 2194 | 783 | 102 | 387 | 365 | 150 | 75 | 338.218 | 95.95
15:00 | 0 | 0 | 0 | 180 | 300 | 80 | 0 | 406 | 327 |  | 0 | 225 | 0 | 7 | 0 | 30 | 0 | 0 | 92 | 8 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 19 | 25 | 17 | 33 | 28 | 32 | 0 | 36 | 65 | 105 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 17 | 33 | 31 | 0 | 15 | 2 | 0 | 0 | 0 | 328 | 270 | 207 | 8 | 85 | 35 | 49 | 0 | 51 | 0 | 47 | 0 | 19 | 10 | 33 | 20 | 160 | 63 | 0 | 22 | 1 | 43 | 0 | 0 | 0 | 0 | 0 | 55 | 10 | 0 | 220 | 0 | 11 | 7 | 290 | 8 | 0 | 100 | 80 | 112 | 50 | 78 | 25 | 35 | 0 | 21 | 200 | 113 | 379 | 68 | 88 | 17 | 4 | 142 | 36 | 55 | 0 | 28 | 20 | 393 | 17 | 45 | 142 | 107 | 0 | 35 | 8 | 74 | 35 | 0 | 0 | 0 |  | 893 | 0 | 150 | 0 | 16 | 229 | 0 | 0 | 0 | 0 | 8 | 81 | 18 | 0 | 0 | 0 | 0 | 0 | 17 | 38 | 0 | 34 | 24 | 8 | 33 | 16 | 0 | 0 | 69 | 0 | 249 | 0 | 0 | 153 | 0 | 0 | 150 | 0 | 20 | 141 | 0 | 260 | 17 | 20 | 94 | 71 | 95 | 0 | 5 | 95 | 460 | 184 | 0 | 0 | 0 | 1 | 17 | 0 | 0 | 0 |  | 6866 | 3666 | 10532 | 3935 | 893 | 1538 | 327 | 2139 | 778 | 101 | 379 | 368 | 160 | 64 | 339.1396 | 95.95
16:00 | 0 | 0 | 0 | 180 | 300 | 80 | 0 | 407 | 337 |  | 0 | 225 | 0 | 8 | 0 | 30 | 0 | 0 | 57 | 8 | 8 | 30 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 19 | 25 | 17 | 33 | 28 | 32 | 0 | 36 | 65 | 105 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 17 | 33 | 31 | 0 | 15 | 2 | 0 | 0 | 0 | 328 | 270 | 206 | 8 | 85 | 18 | 50 | 0 | 51 | 0 | 47 | 0 | 19 | 10 | 33 | 20 | 158 | 71 | 0 | 22 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 60 | 10 | 0 | 220 | 0 | 11 | 7 | 270 | 8 | 0 | 50 | 80 | 54 | 50 | 78 | 25 | 35 | 0 | 21 | 200 | 118 | 365 | 67 | 88 | 17 | 1 | 142 | 36 | 55 | 0 | 28 | 20 | 350 | 17 | 28 | 162 | 107 | 0 | 35 | 7 | 73 | 55 | 0 | 0 | 0 |  | 892 | 0 | 150 | 0 | 16 | 231 | 0 | 0 | 0 | 0 | 8 | 81 | 19 | 0 | 0 | 0 | 0 | 0 | 27 | 38 | 0 | 34 | 24 | 8 | 33 | 18 | 0 | 11 | 68 | 0 | 240 | 0 | 0 | 152 | 0 | 0 | 150 | 0 | 10 | 143 | 0 | 260 | 17 | 20 | 94 | 71 | 95 | 0 | 6 | 36 | 390 | 160 | 0 | 0 | 1 | 2 | 17 | 0 | 0 | 0 |  | 6687 | 3522 | 10209 | 3851 | 892 | 1508 | 209 | 2124 | 698 | 101 | 381 | 392 | 158 | 45 | 424.8461 | 95.95
17:00 | 0 | 0 | 0 | 180 | 300 | 80 | 0 | 407 | 302 |  | 0 | 225 | 0 | 7 | 0 | 30 | 0 | 0 | 35 | 8 | 8 | 125 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 10 | 25 | 22 | 33 | 28 | 35 | 0 | 36 | 65 | 105 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12 | 26 | 17 | 33 | 30 | 0 | 15 | 12 | 0 | 0 | 0 | 325 | 270 | 206 | 8 | 85 | 18 | 51 | 0 | 51 | 0 | 39 | 0 | 19 | 10 | 33 | 20 | 152 | 71 | 0 | 22 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 58 | 10 | 0 | 221 | 0 | 11 | 7 | 280 | 8 | 0 | 0 | 80 | 302 | 0 | 78 | 0 | 34 | 0 | 21 | 200 | 125 | 352 | 69 | 105 | 36 | 1 | 142 | 36 | 55 | 0 | 28 | 20 | 320 | 17 | 4 | 162 | 107 | 0 | 35 | 3 | 72 | 55 | 0 | 0 | 0 |  | 892 | 0 | 155 | 0 | 16 | 230 | 0 | 0 | 0 | 0 | 8 | 87 | 18 | 0 | 0 | 0 | 0 | 24 | 28 | 38 | 0 | 34 | 24 | 8 | 33 | 18 | 0 | 11 | 73 | 0 | 240 | 0 | 0 | 152 | 0 | 0 | 150 | 0 | 0 | 143 | 0 | 230 | 10 | 0 | 94 | 71 | 96 | 0 | 2 | 36 | 360 | 80 | 0 | 0 | 0 | 5 | 32 | 0 | 0 | 0 |  | 6795 | 3398 | 10193 | 3789 | 892 | 1383 | 302 | 2152 | 673 | 101 | 380 | 504 | 152 | 15 | 367.7084 | 95.95
18:00 | 0 | 0 | 0 | 180 | 300 | 80 | 0 | 409 | 271 |  | 0 | 225 | 0 | 8 | 0 | 30 | 0 | 0 | 37 | 8 | 16 | 129 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 10 | 25 | 22 | 33 | 28 | 41 | 0 | 36 | 65 | 105 | 0 | 2 | 0 | 0 | 0 | 0 |  | 12 | 26 | 17 | 33 | 35 | 0 | 15 | 4 | 0 | 0 | 0 | 310 | 270 | 184 | 8 | 136 | 30 | 52 | 0 | 51 | 0 | 39 | 0 | 19 | 5 | 33 | 18 | 146 | 73 | 0 | 22 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 64 | 10 | 0 | 220 | 0 | 11 | 9 | 290 | 8 | 0 | 0 | 104 | 303 | 0 | 182 | 0 | 38 | 0 | 21 | 200 | 130 | 353 | 78 | 105 | 105 | 0 | 142 | 36 | 55 | 0 | 51 | 20 | 320 | 17 | 2 | 162 | 107 | 0 | 35 | 1 | 62 | 55 | 0 | 0 | 0 |  | 893 | 0 | 160 | 0 | 16 | 230 | 0 | 0 | 20 | 10 | 8 | 86 | 4 | 0 | 0 | 0 | 0 | 24 | 28 | 38 | 0 | 34 | 31 | 8 | 33 | 20 | 0 | 11 | 76 | 0 | 240 | 0 | 0 | 153 | 0 | 0 | 150 | 0 | 0 | 145 | 0 | 230 | 45 | 0 | 94 | 71 | 112 | 0 | 1 | 36 | 350 | 70 | 0 | 0 | 0 | 1 | 36 | 0 | 0 | 0 |  | 7044 | 3464 | 10508 | 3827 | 893 | 1335 | 303 | 2457 | 666 | 101 | 380 | 545 | 146 | 5 | 223.0212 | 95.95
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 508.7094 | 0
19:00 | 0 | 0 | 0 | 180 | 300 | 80 | 0 | 407 | 343 |  | 0 | 225 | 0 | 23 | 0 | 30 | 0 | 0 | 37 | 35 | 50 | 130 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 19 | 25 | 20 | 33 | 28 | 41 | 0 | 36 | 65 | 110 | 0 | 20 | 0 | 0 | 0 | 0 |  | 12 | 26 | 51 | 33 | 84 | 26 | 15 | 18 | 0 | 0 | 0 | 280 | 270 | 209 | 8 | 136 | 31 | 52 | 0 | 51 | 0 | 39 | 0 | 20 | 10 | 33 | 18 | 170 | 88 | 0 | 22 | 0 | 43 | 0 | 6 | 10 | 0 | 0 | 64 | 78 | 0 | 220 | 0 | 13 | 9 | 270 | 8 | 0 | 100 | 265 | 300 | 30 | 185 | 30 | 110 | 0 | 90 | 200 | 128 | 402 | 79 | 105 | 105 | 0 | 208 | 36 | 55 | 0 | 57 | 50 | 384 | 50 | 0 | 162 | 107 | 0 | 35 | 0 | 73 | 55 | 0 | 0 | 0 |  | 893 | 0 | 160 | 0 | 16 | 231 | 0 | 0 | 51 | 45 | 8 | 87 | 17 | 48 | 0 | 0 | 0 | 24 | 28 | 80 | 0 | 42 | 40 | 8 | 33 | 22 | 0 | 11 | 75 | 0 | 240 | 0 | 0 | 153 | 0 | 0 | 130 | 0 | 7 | 146 | 0 | 331 | 53 | 10 | 94 | 71 | 113 | 0 | 0 | 90 | 370 | 59 | 0 | 22 | 0 | 0 | 72 | 0 | 0 | 0 |  | 8168 | 3880 | 12048 | 3969 | 893 | 1592 | 477 | 3253 | 685 | 101 | 361 | 677 | 170 | 0 | 508.7094 | 95.95
19:30 | 0 | 0 | 0 | 180 | 300 | 80 | 0 | 406 | 302 |  | 0 | 225 | 0 | 50 | 0 | 30 | 0 | 0 | 37 | 49 | 50 | 130 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 20 | 33 | 30 | 41 | 0 | 36 | 65 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 51 | 33 | 84 | 36 | 15 | 18 | 0 | 0 | 0 | 280 | 270 | 208 | 8 | 136 | 35 | 52 | 0 | 51 | 0 | 39 | 0 | 20 | 10 | 33 | 20 | 162 | 88 | 0 | 22 | 0 | 43 | 0 | 11 | 10 | 0 | 0 | 62 | 78 | 0 | 220 | 0 | 15 | 9 | 290 | 8 | 0 | 30 | 276 | 304 | 30 | 186 | 30 | 120 | 0 | 90 | 200 | 131 | 402 | 78 | 105 | 105 | 0 | 210 | 36 | 55 | 0 | 57 | 100 | 398 | 53 | 0 | 162 | 107 | 0 | 35 | 0 | 73 | 55 | 0 | 0 | 0 |  | 893 | 0 | 165 | 0 | 16 | 230 | 0 | 0 | 42 | 74 | 8 | 87 | 19 | 48 | 0 | 0 | 0 | 24 | 29 | 80 | 0 | 42 | 40 | 8 | 33 | 22 | 0 | 11 | 75 | 0 | 240 | 0 | 0 | 153 | 0 | 0 | 130 | 0 | 10 | 147 | 0 | 327 | 53 | 30 | 94 | 71 | 112 | 0 | 0 | 95 | 470 | 70 | 0 | 35 | 0 | 0 | 72 | 0 | 0 | 0 |  | 8251 | 4055 | 12306 | 3993 | 893 | 1587 | 434 | 3423 | 785 | 101 | 360 | 698 | 162 | 0 | 363.1005 | 0
20:00 | 0 | 0 | 0 | 180 | 300 | 80 | 0 | 407 | 336 |  | 0 | 225 | 0 | 50 | 0 | 30 | 0 | 0 | 37 | 49 | 50 | 128 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 20 | 33 | 30 | 41 | 0 | 36 | 65 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 51 | 33 | 85 | 42 | 15 | 26 | 0 | 0 | 0 | 325 | 270 | 211 | 8 | 136 | 35 | 52 | 0 | 51 | 0 | 39 | 0 | 21 | 10 | 33 | 21 | 162 | 99 | 0 | 22 | 0 | 43 | 0 | 11 | 10 | 0 | 0 | 64 | 78 | 0 | 220 | 0 | 17 | 9 | 270 | 8 | 0 | 30 | 278 | 303 | 30 | 186 | 70 | 142 | 0 | 90 | 200 | 132 | 402 | 79 | 105 | 105 | 0 | 214 | 36 | 55 | 0 | 57 | 100 | 391 | 53 | 0 | 162 | 107 | 0 | 35 | 0 | 73 | 55 | 0 | 0 | 0 |  | 892 | 0 | 165 | 0 | 16 | 231 | 0 | 0 | 36 | 70 | 8 | 87 | 23 | 48 | 0 | 0 | 0 | 24 | 28 | 80 | 0 | 42 | 40 | 8 | 33 | 22 | 0 | 11 | 83 | 0 | 240 | 0 | 0 | 153 | 0 | 0 | 130 | 0 | 10 | 147 | 0 | 328 | 53 | 30 | 94 | 70 | 112 | 0 | 0 | 95 | 490 | 70 | 0 | 35 | 0 | 0 | 72 | 0 | 0 | 0 |  | 8406 | 4076 | 12482 | 4050 | 892 | 1616 | 473 | 3459 | 813 | 101 | 361 | 685 | 162 | 0 | 246.9821 | 95.95
21:00 | 0 | 0 | 0 | 180 | 300 | 83 | 0 | 406 | 331 |  | 0 | 225 | 0 | 50 | 0 | 30 | 0 | 0 | 87 | 49 | 50 | 110 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 20 | 33 | 30 | 41 | 0 | 36 | 65 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 51 | 33 | 90 | 40 | 15 | 31 | 0 | 0 | 0 | 325 | 305 | 210 | 8 | 136 | 35 | 52 | 0 | 51 | 0 | 39 | 0 | 21 | 10 | 33 | 17 | 164 | 99 | 0 | 22 | 0 | 43 | 0 | 11 | 10 | 0 | 0 | 63 | 78 | 0 | 220 | 0 | 25 | 9 | 275 | 8 | 0 | 0 | 275 | 301 | 0 | 188 | 0 | 136 | 0 | 90 | 200 | 133 | 399 | 79 | 105 | 105 | 0 | 214 | 36 | 51 | 0 | 57 | 100 | 400 | 53 | 0 | 162 | 107 | 0 | 35 | 0 | 59 | 55 | 0 | 0 | 0 |  | 893 | 0 | 170 | 0 | 16 | 219 | 0 | 0 | 41 | 70 | 8 | 87 | 26 | 48 | 0 | 0 | 0 | 32 | 30 | 80 | 0 | 42 | 40 | 8 | 33 | 22 | 0 | 11 | 79 | 0 | 240 | 0 | 0 | 153 | 0 | 0 | 130 | 0 | 0 | 148 | 0 | 328 | 53 | 0 | 94 | 88 | 112 | 0 | 0 | 95 | 570 | 70 | 0 | 35 | 0 | 0 | 72 | 0 | 0 | 0 |  | 8337 | 4143 | 12480 | 4140 | 893 | 1635 | 301 | 3456 | 889 | 101 | 349 | 682 | 164 | 0 | 294.904 | 95.95
22:00 | 0 | 0 | 0 | 180 | 300 | 83 | 0 | 407 | 271 |  | 0 | 225 | 0 | 50 | 0 | 30 | 0 | 0 | 94 | 49 | 50 | 118 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 20 | 33 | 30 | 41 | 0 | 37 | 65 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 51 | 33 | 95 | 6 | 15 | 36 | 0 | 0 | 0 | 325 | 310 | 210 | 8 | 136 | 38 | 53 | 0 | 51 | 0 | 39 | 0 | 21 | 10 | 33 | 17 | 168 | 98 | 0 | 22 | 0 | 43 | 0 | 11 | 10 | 0 | 0 | 60 | 78 | 0 | 220 | 0 | 29 | 9 | 300 | 8 | 0 | 0 | 278 | 306 | 0 | 183 | 0 | 142 | 0 | 90 | 200 | 135 | 403 | 79 | 105 | 105 | 0 | 214 | 36 | 51 | 0 | 57 | 100 | 400 | 53 | 0 | 162 | 107 | 0 | 35 | 0 | 57 | 55 | 0 | 0 | 0 |  | 892 | 0 | 170 | 0 | 16 | 218 | 0 | 0 | 31 | 63 | 8 | 87 | 29 | 48 | 0 | 0 | 0 | 32 | 37 | 80 | 0 | 42 | 40 | 8 | 33 | 22 | 0 | 11 | 81 | 0 | 240 | 0 | 0 | 153 | 0 | 0 | 130 | 0 | 0 | 148 | 0 | 328 | 53 | 0 | 94 | 105 | 113 | 0 | 0 | 95 | 580 | 36 | 0 | 35 | 0 | 0 | 72 | 0 | 0 | 0 |  | 8321 | 4130 | 12451 | 4156 | 892 | 1579 | 306 | 3449 | 901 | 102 | 348 | 680 | 168 | 0 | 229.4722 | 95.95
23:00 | 0 | 0 | 0 | 180 | 300 | 83 | 0 | 411 | 303 |  | 0 | 225 | 0 | 48 | 0 | 30 | 0 | 0 | 97 | 49 | 50 | 128 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 20 | 33 | 30 | 41 | 0 | 37 | 65 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 51 | 33 | 94 | 6 | 15 | 38 | 0 | 0 | 0 | 330 | 310 | 208 | 8 | 137 | 38 | 54 | 0 | 51 | 0 | 39 | 0 | 21 | 10 | 33 | 17 | 170 | 102 | 0 | 22 | 0 | 43 | 20 | 11 | 10 | 0 | 0 | 60 | 78 | 0 | 220 | 0 | 29 | 9 | 290 | 8 | 0 | 0 | 278 | 303 | 0 | 188 | 0 | 86 | 0 | 90 | 200 | 137 | 403 | 79 | 105 | 105 | 0 | 214 | 36 | 53 | 0 | 57 | 100 | 400 | 53 | 0 | 162 | 107 | 0 | 35 | 0 | 57 | 55 | 0 | 0 | 0 |  | 893 | 0 | 165 | 0 | 16 | 218 | 0 | 0 | 20 | 63 | 8 | 102 | 30 | 48 | 0 | 0 | 0 | 32 | 40 | 80 | 0 | 42 | 40 | 8 | 33 | 22 | 0 | 11 | 83 | 0 | 240 | 0 | 0 | 152 | 0 | 0 | 130 | 0 | 0 | 148 | 0 | 329 | 53 | 0 | 94 | 105 | 113 | 0 | 0 | 95 | 590 | 36 | 0 | 35 | 0 | 0 | 72 | 0 | 0 | 0 |  | 8340 | 4146 | 12486 | 4200 | 893 | 1606 | 303 | 3399 | 913 | 102 | 348 | 682 | 170 | 0 | 197.217 | 95.95
24:00 | 0 | 0 | 0 | 180 | 300 | 84 | 0 | 411 | 312 |  | 0 | 225 | 0 | 34 | 0 | 30 | 0 | 0 | 97 | 34 | 24 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 20 | 33 | 30 | 41 | 0 | 38 | 65 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 51 | 33 | 25 | 4 | 15 | 39 | 0 | 0 | 0 | 325 | 310 | 211 | 45 | 136 | 38 | 54 | 0 | 51 | 0 | 40 | 0 | 21 | 10 | 33 | 20 | 168 | 103 | 0 | 22 | 0 | 43 | 20 | 11 | 10 | 0 | 0 | 64 | 78 | 0 | 220 | 0 | 29 | 9 | 300 | 8 | 0 | 25 | 278 | 300 | 92 | 48 | 50 | 72 | 0 | 90 | 200 | 130 | 402 | 49 | 105 | 33 | 0 | 214 | 36 | 55 | 0 | 19 | 100 | 400 | 0 | 0 | 162 | 107 | 0 | 35 | 0 | 58 | 55 | 0 | 0 | 0 |  | 894 | 0 | 170 | 0 | 16 | 219 | 0 | 0 | 21 | 63 | 8 | 136 | 29 | 64 | 0 | 0 | 0 | 32 | 40 | 66 | 0 | 42 | 40 | 8 | 33 | 22 | 0 | 11 | 80 | 0 | 240 | 0 | 0 | 151 | 0 | 0 | 182 | 0 | 10 | 148 | 0 | 322 | 17 | 25 | 94 | 88 | 98 | 0 | 0 | 95 | 610 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 |  | 7996 | 4109 | 12105 | 4242 | 894 | 1620 | 502 | 2817 | 930 | 103 | 401 | 610 | 168 | 0 | 410.1009 | 95.95
KWH | 0 | 0 | 0 | 4378500 | 7201527 | 1972772 | 0 | 9897980 | 7782000 |  | 0 | 5195000 | 0 | 405120 | 0 | 768018 | 0 | 0 | 2015000 | 414470 | 419328 | 1077120 | 0 | 0 | 0 | 0 | 696240 | 1311409 | 884309 | 396468 | 600000 | 511200 | 819100 | 728300 | 908640 | 0 | 860509 | 1556000 | 2500000 | 0 | 566370 | 0 | 0 | 0 | 0 |  | 287520 | 640808 | 706699 | 787440 | 808320 | 150720 | 367872 | 487680 | 0 | 0 | 0 | 7610200 | 6930000 | 4860000 | 217454 | 1788270 | 818640 | 1163040 | 0 | 1187492 | 0 | 967916 | 0 | 477360 | 220140 | 795500 | 494000 | 3574080 | 1924800 | 0 | 469188 | 5950 | 1020000 | 52440 | 336000 | 171720 | 0 | 0 | 1452672 | 821760 | 0 | 5230930 | 0 | 359660 | 192240 | 7154000 | 187824 | 0 | 1173888 | 3394799 | 3085378 | 1356855 | 2236800 | 1188866 | 1482050 | 39825 | 887040 | 4761120 | 3134690 | 9368000 | 1540800 | 2194800 | 986072 | 26760 | 3013418 | 916261 | 1282976 | 0 | 853440 | 965760 | 9207200 | 468480 | 330300 | 2304000 | 2461418 | 0 | 838800 | 84400 | 1661760 | 1303560 | 0 | 0 | 0 |  | 21618909 | 0 | 4063968 | 0 | 318720 | 5493120 | 0 | 0 | 295200 | 650368 | 126000 | 2145353 | 377267 | 356640 | 0 | 0 | 0 | 289840 | 421117 | 1148800 | 0 | 823024 | 544200 | 195082 | 447299 | 439440 | 0 | 220212 | 1204363 | 0 | 6022400 | 0 | 0 | 3875100 | 0 | 0 | 4179118 | 0 | 1140480 | 3806309 | 0 | 7510545 | 449280 | 1908121 | 1815744 | 2019024 | 2100067 | 0 | 51362 | 1602720 | 13034800 | 3896618 | 0 | 224400 | 17340 | 135360 | 507456 | 0 | 0 | 0 |  | 171135231 | 95475166 | 266610397 | 96434053 | 21618909 | 39264688 | 9853588 | 55634105 | 20261563 | 2416509 | 9672238 | 7189367 | 3574080 | 691297 | 0
Fuel Cost | 0 | 0 | 0 | 6523965 | 8065710.24 | 2623786.76 | 0 | 10392879 | 8404560 |  | 0 | 5662550 | 0 | 4529241.6 | 0 | 10176238.5 | 0 | 0 | 3526250 | 6059551.4 | 5899944.96 | 17460115.2 | 0 | 0 | 0 | 0 | 8856172.8 | 17704021.5 | 11858583.69 | 297351 | 450000 | 0 | 0 | 0 | 15455966.4 | 0 | 232337.43 | 420120 | 4725000 | 0 | 9260149.5 | 0 | 0 | 0 | 0 |  | 3752136 | 10688677.44 | 12028016.98 | 10638314.4 | 10249497.6 | 1743830.4 | 467197.44 | 1623974.4 | 0 | 0 | 0 | 8447322 | 7553700 | 5637600 | 280515.66 | 2181689.4 | 925063.2 | 1732929.6 | 0 | 1983111.64 | 0 | 16715909.32 | 0 | 653983.2 | 165105 | 1392125 | 370500 | 25661894.4 | 2098032 | 0 | 638095.68 | 94843 | 1397400 | 69220.8 | 584640 | 297075.6 | 0 | 0 | 2818183.68 | 1873612.8 | 0 | 5283239.3 | 0 | 535893.4 | 380635.2 | 7154000 | 140868 | 0 | 24604692.48 | 46339006.35 | 64669522.88 | 28046192.85 | 30152064 | 24573860.22 | 20526392.5 | 465554.25 | 9154252.8 | 65036899.2 | 41597336.3 | 8618560 | 18736128 | 31736808 | 12473810.8 | 0 | 35377527.32 | 9978082.29 | 13638034.88 | 0 | 11000841.6 | 11376652.8 | 8470624 | 6066816 | 4772835 | 29237760 | 28010936.84 | 0 | 10954728 | 1008580 | 24876547.2 | 17167885.2 | 0 | 0 | 0 |  | 64856727 | 0 | 4551644.16 | 0 | 3317875.2 | 90636480 | 0 | 0 | 5316552 | 11706624 | 1810620 | 2402795.36 | 731897.98 | 3887376 | 0 | 0 | 0 | 4860616.8 | 7365336.33 | 17967232 | 0 | 13629277.44 | 9202422 | 2658967.66 | 7545934.13 | 909640.8 | 0 | 166700.484 | 6997349.03 | 0 | 31858496 | 0 | 0 | 4495116 | 0 | 0 | 72967400.28 | 0 | 23927270.4 | 4415318.44 | 0 | 7435439.55 | 6038323.2 | 40013297.37 | 21480251.52 | 29174896.8 | 26670850.9 | 0 | 567550.1 | 19457020.8 | 117443548 | 3974550.36 | 0 | 1660560 | 196115.4 | 1587772.8 | 7779300.48 | 0 | 0 | 0 |  | 945512259.28 | 681665146.774 | 1627177406.054 | 107341238.384 | 64856727 | 46188813.75 | 205834836.2 | 727187478.83 | 156299393.03 | 652457.43 | 163603880.28 | 120857436.2 | 25661894.4 | 8693250.55 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 300 | 86 | 0 | 407 | 333 |  | 0 | 225 | 0 | 8 | 0 | 30 | 0 | 0 | 93 | 8 | 8 | 16 | 0 | 0 | 0 | 0 | 18 | 55 | 35 | 0 | 25 | 26 | 33 | 28 | 41 | 0 | 36 | 65 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 9 | 26 | 17 | 33 | 11 | 0 | 15 | 6 | 0 | 0 | 0 | 280 | 280 | 195 | 8 | 30 | 39 | 53 | 0 | 51 | 0 | 37 | 0 | 19 | 10 | 30 | 20 | 128 | 65 | 0 | 20 | 0 | 43 | 0 | 11 | 10 | 0 | 0 | 61 | 10 | 0 | 220 | 0 | 11 | 7 | 280 | 8 | 0 | 52 | 80 | 11 | 91 | 78 | 94 | 35 | 7 | 21 | 200 | 130 | 400 | 69 | 88 | 17 | 2 | 123 | 36 | 35 | 0 | 29 | 20 | 375 | 17 | 37 | 35 | 107 | 0 | 35 | 3 | 61 | 55 | 0 | 0 | 0 |  | 895 | 0 | 170 | 0 | 0 | 229 | 0 | 0 | 0 | 0 | 0 | 55 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 34 | 16 | 8 | 0 | 19 | 0 | 11 | 70 | 0 | 250 | 0 | 0 | 152 | 0 | 0 | 130 | 0 | 20 | 156 | 0 | 333 | 10 | 127 | 50 | 89 | 69 | 0 | 3 | 55 | 460 | 206 | 0 | 0 | 4 | 24 | 0 | 0 | 0 | 0 |  | 10279 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 300 | 80 | 0 | 407 | 336 | 0 | 0 | 225 | 0 | 50 | 0 | 30 | 0 | 0 | 37 | 49 | 50 | 128 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 20 | 33 | 30 | 41 | 0 | 36 | 65 | 110 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 12 | 26 | 51 | 33 | 85 | 42 | 15 | 26 | 0 | 0 | 0 | 325 | 270 | 211 | 8 | 136 | 35 | 52 | 0 | 51 | 0 | 39 | 0 | 21 | 10 | 33 | 21 | 162 | 99 | 0 | 22 | 0 | 43 | 0 | 11 | 10 | 0 | 0 | 64 | 78 | 0 | 220 | 0 | 17 | 9 | 270 | 8 | 0 | 30 | 278 | 303 | 30 | 186 | 70 | 142 | 0 | 90 | 200 | 132 | 402 | 79 | 105 | 105 | 0 | 214 | 36 | 55 | 0 | 57 | 100 | 391 | 53 | 0 | 162 | 107 | 0 | 35 | 0 | 73 | 55 | 0 | 0 | 0 |  | 892 | 0 | 165 | 0 | 16 | 231 | 0 | 0 | 36 | 70 | 8 | 87 | 23 | 48 | 0 | 0 | 0 | 24 | 28 | 80 | 0 | 42 | 40 | 8 | 33 | 22 | 0 | 11 | 83 | 0 | 240 | 0 | 0 | 153 | 0 | 0 | 130 | 0 | 10 | 147 | 0 | 328 | 53 | 30 | 94 | 70 | 112 | 0 | 0 | 95 | 490 | 70 | 0 | 35 | 0 | 0 | 72 | 0 | 0 | 0 |  | 12482 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 300 | 80 | 0 | 412 | 330 | 0 | 0 | 225 | 0 | 50 | 0 | 55 | 0 | 0 | 95 | 50 | 50 | 128 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 20 | 33 | 30 | 41 | 0 | 36 | 65 | 110 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 12 | 26 | 51 | 33 | 85 | 42 | 15 | 30 | 0 | 0 | 0 | 325 | 300 | 211 | 8 | 136 | 35 | 55 | 0 | 51 | 0 | 40 | 0 | 22 | 10 | 33 | 21 | 166 | 100 | 0 | 22 | 0 | 43 | 30 | 0 | 10 | 0 | 0 | 64 | 80 | 0 | 220 | 0 | 17 | 9 | 300 | 8 | 0 | 200 | 275 | 300 | 96 | 180 | 100 | 149 | 0 | 90 | 200 | 132 | 400 | 100 | 105 | 105 | 0 | 300 | 36 | 55 | 0 | 57 | 100 | 400 | 50 | 0 | 162 | 107 | 0 | 35 |  | 75 | 55 |  |  |  |  | 912 | 0 | 170 | 0 | 66 | 225 | 0 | 0 | 36 | 70 | 32 | 144 | 23 | 110 | 0 | 0 | 0 | 32 | 40 | 80 | 0 | 42 | 40 | 8 | 33 | 22 | 0 | 11 | 83 | 0 | 250 | 0 | 0 | 160 | 0 | 0 | 220 | 0 | 90 | 150 | 0 | 330 | 52 | 175 | 94 | 105 | 113 | 0 | 0 | 95 | 620 | 0 |  | 110 |  |  | 90
Forecast for Day | 0 | 0 | 0 | 180 | 300 | 80 | 0 | 412 | 330 | 0 | 0 | 225 | 0 | 30 | 0 | 30 | 0 | 0 | 95 | 8 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 19 | 25 | 20 | 33 | 30 | 41 | 0 | 36 | 65 | 110 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 12 | 26 | 17 | 33 | 12 | 19 | 15 | 30 | 0 | 0 | 0 | 300 | 280 | 200 | 8 | 130 | 35 | 55 | 0 | 51 | 0 | 40 | 0 | 22 | 10 | 33 | 20 | 143 | 100 | 0 | 22 | 1.6 | 43 | 30 | 0 | 10 | 0 | 0 | 62 | 25 | 0 | 200 | 0 | 11 | 9 | 300 | 8 | 0 | 100 | 80 | 300 | 60 | 48 | 50 | 43 | 20 | 21 | 200 | 100 | 400 | 78 | 88 | 17 | 5 | 118 | 36 | 55 | 0 | 30 | 20 | 400 | 17 | 50 | 35 | 107 | 0 | 35 | 30 | 74 | 55 |  |  |  |  | 912 | 0 | 170 | 0 | 16 | 225 | 0 | 0 | 0 | 0 | 32 | 144 | 15 | 110 | 0 | 0 | 0 | 32 | 0 | 50 | 0 | 42 | 16 | 8 | 33 | 21 | 0 | 11 | 70 | 0 | 250 | 0 | 0 | 150 | 0 | 0 | 220 | 0 | 90 | 150 | 0 | 330 | 17 | 80 | 50 | 90 | 70 | 0 | 8 | 55 | 620 | 0 |  | 50 | 6 | 100 | 17
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 300 | 91 | 0 | 407 | 292 | 0 | 0 | 225 | 0 | 34 | 0 | 40 | 0 | 0 | 95 | 8 | 8 | 16 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 25 | 20 | 33 | 30 | 41 | 0 | 35 | 65 | 110 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 7 | 26 | 17 | 33 | 12 | 6 | 15 | 42 | 0 | 0 | 0 | 310 | 305 | 212 | 8 | 137 | 26 | 55 | 0 | 51 | 0 | 31 | 0 | 21 | 10 | 33 | 20 | 120 | 104 | 0 | 22 | 0 | 43 | 30 | 0 | 10 | 0 | 0 | 65 | 20 | 0 | 199 | 0 | 11 | 9 | 280 | 8 | 0 | 0 | 45 | 0 | 0 | 76 | 0 | 114 | 10 | 21 | 50 | 80 | 365 | 67 | 105 | 17 | 2 | 135 | 36 | 55 | 0 | 9 | 20 | 360 | 10 | 19 | 54 | 107 | 0 | 35 | 7 | 41 | 55 | 0 | 0 | 0 | 0 | 894 | 0 | 175 | 0 | 66 | 120 | 0 | 0 | 0 | 0 | 32 | 144 | 19 | 32 | 0 | 0 | 0 | 32 | 0 | 44 | 0 | 42 | 24 | 8 | 32 | 20 | 0 | 11 | 81 | 0 | 250 | 0 | 0 | 151 | 0 | 0 | 130 | 0 | 0 | 155 | 0 | 330 | 0 | 0 | 35 | 105 | 70 | 0 | 0 | 35 | 510 | 0 | 0 | 17 | 3 | 18 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 82349298 |  | 0
82349298
| Minimum Generation |  | 10268 | 8:00
| Highest Generation |  | 12486 | 23:00
| Day Peak Generation |  | 10279 | 9:00
| Evening Peak Generation |  | 12482 | 20:00
| HVDC Max Flow |  | 896 | 3:00
| HVDC EvPeak Flow |  | 892 | 20:00
| Load factor L.F |  | 88.97% | [161 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2022-08-15
Till now the maximum generation is : - |  |  | 14782 | 21:00 | Hrs on | 2022-04-16
The Summary of Yesterday's |  | 2022-08-14 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 10279 | MW Hour : | 9:00 | Min. Gen. at | 7:00 | 9926 | MW
Evening Peak Generation : |  | 12482 | MW Hour : | 20:00 | Available Max Generation : |  | 13830 | MW
E.P. Demand (at gen end) : |  | 12750 | MW Hour : | 20:00 | Max Demand (Evening) : |  | 13600 | MW
Maximum Generation : |  | 12486 | MW Hour : | 23:00 | Reserve(Generation end) |  | 230 | MW
Total Gen. (MKWH) : |  | 266.6104 | System Load Factor : | 88.97% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | 182 | MW at | 20:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2022-08-15
Actual : | 95.95 | Ft.(MSL) , | Rule curve : | 93.48 | Ft.( MSL )
Gas Consumed : | Total = | 1014.68 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 153530052.134
: |  | Coal : | 156299393.03 | Oil : | 1217483631.51 | Total : | 1527313076.674
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 60 | 1440:00 | 4355.3635 |  |  | 0 | -1.768%
Chittagong Area | 0 | 0:00 | 1233.2885 |  |  | 0 | 0.5772%
Khulna Area | 0 | 0:00 | 1628.0913 |  |  | 0 | 1.004%
Rajshahi Area | 0 | 0:00 | 1445.1033 |  |  | 0 | 1.604%
Cumilla Area | 0 | 0:00 | 1229.5285 |  |  | 0 | 1.256%
Mymensingh Area | 187 | 4488:00 | 1016.4604 |  |  | 0 | 1.828%
Sylhet Area | 0 | 0:00 | 453.7098 |  |  | 0 | 0.5987%
Barisal Area | 0 | 0:00 | 369.7359 |  |  | 0 | -3.064%
Rangpur Area | 0 | 0:00 | 802.1389 |  |  | 0 | 1.769%
Total | 247 |  | 12533.42 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-2 |  | 10) Payra unit-2
2) Ghorasal-3,4
3) Ashuganj-5
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
7) Sikalbaha 225 MW
8) Shajibazar 330 MW
9) Siddhirganj 335 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Agargaon-Satmosjid 132 kv Ckt-2 was under shut down from 09:33 to 11:50 for D/W.
b) Tongi 132 kV bus-1 was under shut down from 10:48 to 15:46 for D/W.
c) Tongi-Tongi milgate 132 kV Ckt-1 was under shut down from 11:21 to 15:48 for D/W.
d) Chandpur-150 MW CCPP ST was synchronized at 12:30.
e) Munshiganj 132/33 kV T-1 transformer was under shut down from 11:27 to 14:05 for D/W.
f) Bhola-225 MW CCPP ST was synchronized at 13:06.
g) Bhola Nutun Biddut-220 MW CCPP ST tripped at 17:00 due to problem with AVR.
h) Munshiganj 132/33 kV T-2 transformer was under shut down from 14:11 to 15:52 for D/W.
i) Kishorganj 132/33 kV T-3 transformer was under shut down from 14:15 to 15:25 for C/M.
j) Ashuganj 230/132 kV OAT-12 transformer tripped at 14:31 showing O/C relay and was switched on at 15:04.
k) Sherpur(Bogura) 132/33 kV T-1 & T-2 transformer tripped at 15:02 showing O/C relay due to 33 kV Dhunot | [5 empty] | About 25 MW power interruption occurred under
feeder fault and were switched on at 15:22. | [5 empty] | Sherpur S/S area from 15:02 to 15:22.
l) Bogura(O) 132/33 kV T-2 transformer tripped at 14:30 showing O/C relay and was switched on at 15:23.
m) GK 132/33 kV T-2 transformer was under shut down from 14:16 to 16:32 for C/M.
n) Bhola Nutun Biddut-220 MW CCPP GT-2 was shut down at 21:07 due to HRSG leakage and was synchronized
at 22:59 and forced shut down at 07:00(15/8/22).
o) Barishal(N)-Barishal 132 kV Ckt-2 was under shut down from 21:11 to 22:25 for C/M.
p) Amnura S/S-Amnura P/S 132 kV Ckt tripped at 20:47 showing O/C relay.
q) Fenchuganj GT-3 was synchronized at 22:28.
r) Gallamari 132/33 kV TR-2 transformer tripped at 05:16(15/8/22) showing differential relay.
| Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2022-08-14 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4378500
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 300 | 7201527
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 80 | 1972772 | Engine problem
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 407 | 9897980
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 336 | 7782000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 5195000 | Gas shortage & GT-2 S/D.
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 50 | 405120 | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 0 | 0 | Under maint.
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 30 | 768018 | Engine problem
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 396468
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 37 | 2015000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 49 | 414470 | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 50 | 419328 | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 35 | 696240 | Engine problem
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 128 | 1077120 | Engine problem
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 1311409
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 884309 | Engine problem
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 45 | 1111200 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 819100
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 30 | 728300
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 41 | 908640 | #REF!
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 278 | 3394799 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 303 | 3085378 | Fuel shortage
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 30 | 1356855 | Fuel shortage
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 70 | 1188866
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 142 | 1482050 | Engine problem
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 2194800
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 53 | 468480 | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 2304000
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 84400
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 55 | 1303560
| Dhaka area Total |  |  |  | 5847 | 3363 | 65245689
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 110 | 2500000 | Machine problem
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 25 | 566370
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 39825
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 42 | 150720 | Engine problem
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 101 | 2416509 | Low water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | HGPI for 30 days.
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 105 | 986072
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 26 | 640808 | Fuel shortage
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 706699 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 33 | 787440 | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 90 | 887040 | Engine problem
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 15 | 367872 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 26 | 487680
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 85 | 808320 | Engine problem
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 26760
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 214 | 3013418 | Fuel shortage
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 36 | 916261 | Engine problem
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 55 | 1282976 | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 965760 | Engine problem
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 107 | 2461418 | Engine problem
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Chattogram area Total |  |  |  | 2382 | 1221 | 20011948
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 211 | 4860000 | #REF!
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 325 | 7610200 | gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 270 | 6930000 | Gas shortage
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+136*1 | 284 | 0 | 0 | On test.
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 35 | 818640
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 52 | 1163040 | Gas shortage
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 217454 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1187492
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 132 | 3134690 | Engine problem
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 39 | 967916 | Engine problem
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 136 | 1788270 | Machine problem
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 200 | 4761120
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 477360
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 10 | 220140
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 162 | 3574080
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 795500
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 0 | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 21 | 494000
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 30 | 1173888 | low demand.
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Fuel shortage
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 57 | 853440 | Fuel shortage
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 35 | 838800 | 33 kV feeder problem.
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 73 | 1661760 | Fuel shortage
| Cumilla Area Total |  |  |  | 3169 | 1901 | 43527790
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 99 | 1924800 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 469188
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 5950
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 186 | 2236800 | Engine problem
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 79 | 1540800 | Engine problem
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 330300
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 287520 | Engine problem
| Mymensingh Area Total |  |  |  | 614 | 398 | 6795358
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1020000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 52440 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Gas shortage
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 11 | 336000 | Gas shortage
| Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 10 | 171720 | Gas shortage
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 0 | 0 | Engine problem
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 64 | 1452672
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 78 | 821760
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 220 | 5230930
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50MW PP (EPL) |  | NENP | 27*2 | 50 | 17 | 359660 | Gas shortage
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 8 | 187824 | Gas shortage
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 270 | 7154000 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 402 | 9368000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 9 | 192240
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 391 | 9207200
| Sylhet Area Total |  |  |  | 2477 | 1523 | 35554446
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 892 | 21618909
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 16 | 318720 | Fuel shortage
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 36 | 295200 | Engine problem
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 231 | 5493120
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 70 | 650368
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 165 | 4063968 | Gas shortage.
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 8 | 126000 | Fuel shortage
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 10 | 1140480 | low demand.
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 53 | 449280 | Fuel shortage
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 70 | 2019024 | Engine problem
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 135360
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 0 | 0 | 0 | On test.
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 2384 | 1551 | 36310429
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 48 | 356640 | Line O/L
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 23 | 377267 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 87 | 2145353 | ST under S/D
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 490 | 13034800 | Unit-2 S/D
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 70 | 3896618 | ST trip at 17:00
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 35 | 224400 | Line O/L
| Barisal Area Total |  |  |  | 1958 | 753 | 20035078
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 24 | 289840 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 28 | 421117 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contract Expired
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 42 | 823024 | Engine problem
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 40 | 544200 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 153 | 3875100 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 130 | 4179118
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 147 | 3806309 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 328 | 7510545 | Gas shortage
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 33 | 447299 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 439440
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | .
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 220212
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 8 | 195082 | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 80 | 1148800 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 30 | 1908121 | low demand.
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 94 | 1815744 | Engine problem
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 95 | 1602720 | Engine problem
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 17340
| Rajshahi Area Total |  |  |  | 2129 | 1265 | 29244011
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 83 | 1204363
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 240 | 6022400 | Machine problem
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 112 | 2100067 | Engine problem
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 51362
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 72 | 507456 | Fuel shortage
| Rangpur Area Total |  |  |  | 720 | 507 | 9885648
| Total |  |  |  | 21680 | 12482 | 266610397
| Eastern Grid Total |  |  |  | 14489 | 8406 | 171135231
| Western Grid Total |  |  |  | 7191 | 4076 | 95475166
| National Grid Total |  |  |  | 21680 | 12482 | 266610397
*Data collected from respective power station over telephone.
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2022-08-14
(a) ENTIRE EASTERN GRID : |  | 8370.44 | MW | (b) ENTIRE WESTERN GRID : |  | 3713.26 | MW
i) Dhaka area |  | 4287.79 | MW | i) Khulna area |  | 1342.6 | MW
ii) Chittagong area |  | 1328.65 | MW | ii) Rajshahi area |  | 1250 | MW
iii) Comilla area |  | 1223 | MW | iii) Barisal area |  | 267.66 | MW
iv) Mymensingh area |  | 930 | MW | iv) Rangpur area |  | 853 | MW
v) Sylhet area |  | 601 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 12083.7 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
AKS | 21 | 07:00 | Chowmuhani | 196 | 22:00 | Kaptai | 5 | 20:00 | Nawabganj | 38.4 | 00:00 | Sholosohor | N/A | N/A
AKSML | 81 | 13:00 | Chuadanga | 87 | 19:30 | Kazla | 79 | 00:00 | Netrakona | 112 | 08:00 | Shyampur | 162 | 03:00
Aftabnagar | 31 | 13:00 | Coxsbazar | 106 | 19:00 | Keranigonj | 56 | 19:00 | New | 80.4 | 16:00 | Siddhirganj | 114 | 16:00
Agargaon | 84 | 11:00 | Cumilla(N) | 160 | 22:00 | Khagrachori | 28 | 19:30 | Niamatpur | 75 | 22:00 | Sirajganj | 98 | 21:00
Agrabad | 74 | 15:00 | Cumilla(S) | 170 | 19:00 | Khulna | 75 | 00:00 | Noapara | 44 | 19:00 | Sonargaon | 95 | 00:00
Amnura | 54 | 20:00 | Daudkandi | 136 | 22:00 | Khulshi | 169 | 16:00 | PHP | 9 | 20:00 | Sreemongol | 59 | 21:00
Ashuganj | 44 | 23:00 | Dhaka | 38 | 11:00 | Kishoreganj | 112 | 07:00 | Pabna | 106 | 19:00 | Srinagar | 36.6 | 23:00
BSRM | 154 | 18:00 | Dhamrai | 102 | 09:00 | Kodda | 246 | 21:00 | Palashbari | 124 | 22:00 | Sunamganj | 54 | 22:00
Bagerhat | 86 | 20:00 | Dhanmondi | 141 | 14:00 | Kulaura | 46 | 19:30 | Panchagarh | 54 | 19:00 | Sylhet | 158 | 19:00
Bakulia | 123 | 19:00 | Dohazari | 84 | 19:00 | Kurigram | 65 | 19:30 | Patuakhali | 100 | 22:00 | TK | 29.2 | 22:00
Banani | 57 | 13:00 | Faridpur | 123 | 21:00 | Kushtia | 128 | 19:30 | Payra | 0.74 | 18:30 | Tangail | 196 | 21:00
Bangabhaban | 20 | 10:00 | Fatullah | 74 | 15:00 | Lalbag | 82 | 14:00 | Purbachal | 40 | 01:00 | Thakurgaon | 77 | 19:30
Barapukuria | 50 | 22:00 | Fenchuganj | 49 | 20:00 | Lalmonirhat | 50 | 19:30 | Purbasadipur | 15 | 00:00 | Tongi | 120 | 13:00
Barguna | 16 | 00:00 | Feni | 111 | 20:00 | Madanganj | 71 | 14:00 | Rahim | 117 | 21:00 | Ullon | 40 | 00:00
Barishal | 77 | 22:00 | GPH | 92 | 12:00 | Madaripur | 76 | 00:00 | Rajbari | N/A | N/A | Uttara | 86 | 12:00
Barishal-230 | 64 | 01:00 | Ghorashal | 46 | 21:00 | Madartek | 77 | 00:00 | Rajendrapur | 34 | 16:00 | UttaraNew | 19 | 15:00
Baroaulia | 72 | 00:00 | Goalpara | 24 | 12:00 | Madunaghat | 65 | 18:00 | Rajshahi | 55 | 19:30 | Zigatola | 55 | 16:00
Baroirhat | 51 | 19:00 | Gollamari | 46 | 12:00 | Magura | 50 | 19:30 | Rajshahi-230 | 90 | 00:00
Bashundhara | 153 | 13:00 | Gopalganj | 83 | 19:00 | Mahasthangarh | 66 | 21:00 | Ramganj | 130 | 22:00
BashundharaCement | 6 | 00:00 | Gulshan | 112 | 14:00 | Manikganj | 84 | 21:00 | Rampur | 35 | 02:00
Beanibazar | 65 | 20:00 | Halishahar | 91.5 | 15:00 | Maniknagar | 78 | 13:00 | Rangamati | 100 | 21:00
Benapole | 46 | 00:00 | HaripurSBU | 154 | 16:00 | Matarbari | 37 | 19:30 | Rangpur | 21 | 00:00
Bhaluka | 100 | 23:00 | Hasnabad | 82 | 23:00 | Matuail | 69 | 11:00 | Ruppur | 14 | 19:00
Bhandaria | 38 | 22:00 | Hathazari | 95 | 19:00 | Millgate | 58 | 11:00 | SSM | 152 | 20:00
Bhangura | 28 | 20:00 | Ishurdi | 64 | 00:00 | Mirpur | 119 | 19:00 | Saidpur | 4.2 | 10:00
Bheramara(GK) | 59 | 19:30 | Jaldhaka | 63 | 21:00 | Mirsorai | N/A | N/A | Satkhira | 2 | 01:00
Bhulta | 222 | 08:00 | Jamalpur | 124 | 22:00 | Mithapukur | 34 | 19:00 | Satmasjid | 107 | 19:30
Bog-Sherpur | 50 | 23:00 | Jashore | 110 | 19:00 | Modern | 0 | 00:00 | Savar | 96 | 00:00
Bogura | 154 | 20:00 | Jhenaidah | 102 | 20:00 | Mogbazar | 123 | 13:00 | Shahjadpur | 97 | 19:00
Borhanuddin | 24 | 02:00 | Joydebpur | 169 | 09:00 | Mongla | 28 | 00:00 | Shahjibazar | 155 | 09:00
Brahmanbaria | 180 | 21:00 | Joypurhat | 53 | 23:00 | Motijheel | 36 | 13:00 | Shahmirpur | 89 | 20:00
Cantonment | 142 | 13:00 | Juldah | 29 | 10:00 | Munshiganj | 91 | 20:00 | Shariatpur | 144 | 22:00
Chandpur | 60 | 21:00 | KSRM | 33.65 | 08:00 | Mymensingh | 232 | 23:00 | Sherpur | 44 | 14:00
Chandraghona | 30 | 18:30 | Kabirpur | 254 | 18:30 | Naogaon | 116 | 22:00 | Shikalbaha | 64 | 00:00
Chapai | 64 | 06:00 | Kachua | 72 | 22:00 | Narail | 38 | 20:00 | Shikalbaha-230 | 106 | 20:00
Charsaidpur | 39 | 11:00 | Kallyanpur | 93 | 19:00 | Narinda | 75 | 13:00 | Shitalakhya | 28 | 00:00
Chauddagram | 44 | 02:00 | Kalurghat | 7 | 10:00 | Narshingdi | 185 | 22:00 | Sholosohor | N/A | N/A
Chhatak | 33 | 20:00 | Kamrangirchar | 62 | 19:00 | Natore | 124 | 20:00 | Shyampur | 116 | 15:00
Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
(1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2022-08-14 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Bhulta | 391 | 20:00 | 365 | 14:00 | Kaliakoir | 387 | 18:00 | 368 | 14:00
| Bibiana | 404 | 18:00 | 392 | 14:00 | Payra | 422 | 18:00 | 413 | 01:00
| BIPTC | 407 | 11:00 | 397 | 22:00 | Rahanpur_I | N/A | N/A | N/A | N/A
| Gopalganj_I | 418 | 18:30 | 402 | 01:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 226 | 20:00 | 209 | 11:00 | Hasnabad | 228 | 20:00 | 210 | 11:00
| AKSML | 233 | 20:00 | 211 | 11:00 | Hathazari | 234 | 19:00 | 218 | 15:00
| Aminbazar | 228 | 20:00 | 210 | 14:00 | Ishurdi | 237 | 18:00 | 230 | 03:00
| Ashuganj | 238 | 19:30 | 225 | 15:00 | Jhenaidah | 231 | 18:30 | 224 | 07:00
| Baghabari | 234 | 15:00 | 230 | 05:00 | Kaliakoir | 225 | 19:30 | 210 | 14:00
| Barapukuria | 225 | 16:00 | 212 | 04:00 | Keranigonj | 226 | 20:00 | 208 | 11:00
| Barishal | 248 | 12:00 | 240 | 22:00 | Khulna(S) | 241 | 18:00 | 232 | 02:00
| Bheramara | 233 | 18:00 | 226 | 11:00 | Maniknagar | 225 | 20:00 | 211 | 14:00
| Bhulta | 229 | 19:00 | 214 | 14:00 | Meghnaghat | 231 | 20:00 | 215 | 11:00
| Bibiana | 234 | 18:00 | 227 | 11:00 | Mirsorai | N/A | N/A | N/A | N/A
| BIPTC | 236 | 18:00 | 227 | 07:00 | Rajshahi | 236 | 18:00 | 226 | 06:00
| Bogura | 229 | 18:00 | 219 | 07:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 250 | 09:00 | 230 | 01:00 | Rampura | 226 | 20:00 | 213 | 11:00
| BSRM | 230 | 19:00 | 215 | 03:00 | Shikalbaha | 234 | 19:30 | 217 | 04:00
| Cumilla(N) | 228 | 19:00 | 216 | 11:00 | Shyampur | 227 | 20:00 | 209 | 11:00
| Fenchuganj | 238 | 19:00 | 230 | 14:00 | Siddhirganj | 226 | 19:30 | 212 | 14:00
| Ghorashal | N/A | N/A | N/A | N/A | Sirajgonj | 232 | 18:00 | 228 | 03:00
| GPH | 232 | 00:00 | 215 | 15:00 | Tongi | 231 | 19:30 | 210 | 09:00
| Haripur | 225 | 20:00 | 212 | 11:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 138 | 20:00 | 128 | 10:00 | Lalbag | 141 | 20:00 | 129 | 11:00
| Agargaon | 139 | 20:00 | 128 | 11:00 | Lalmonirhat | 131 | 15:00 | 117 | 23:00
| Agrabad | 136 | 19:00 | 125 | 11:00 | Madanganj | 132 | 20:00 | 124 | 11:00
| AKS | 135 | 19:00 | 125 | 00:00 | Madaripur | 141 | 12:00 | 136 | 00:00
| Aminbazar | 136 | 19:00 | 127 | 14:00 | Madartek | 139 | 20:00 | 128 | 10:00
| Amnura | 133 | 19:00 | 126 | 07:00 | Madunaghat | 138 | 19:00 | 128 | 11:00
| Ashuganj | 136 | 18:00 | 134 | 07:00 | Magura | 141 | 18:00 | 135 | 02:00
| Bagerhat | 135 | 17:00 | 129 | 03:00 | Mahasthangarh | 138 | 15:00 | 127 | 07:00
| Bakulia | 137 | 19:00 | 126 | 11:00 | Manikganj | 132 | 06:00 | 125 | 14:00
| Banani | 134 | 20:00 | 121 | 11:00 | Maniknagar | 135 | 20:00 | 125 | 11:00
| Bangabhaban | 134 | 19:00 | 124 | 11:00 | Matarbari | 125 | 19:30 | 114 | 00:00
| Barapukuria | 138 | 16:00 | 128 | 03:00 | Matuail | 132.2 | 20:00 | 124 | 10:00
| Barguna | 140 | 19:00 | 129 | 01:00 | Millgate | 135 | 22:00 | 121 | 11:00
| Barishal | 141 | 12:00 | 128 | 01:00 | Mirpur | 137 | 20:00 | 125 | 11:00
| Barishal-230 | 142 | 09:00 | 136 | 00:00 | Mithapukur | 135 | 16:00 | 122 | 04:00
| Baroaulia | 138 | 19:00 | 128 | 11:00 | Modern | 137 | 19:00 | 126 | 12:00
| Baroirhat | 130 | 18:00 | 124 | 15:00 | Mogbazar | 139 | 20:00 | 129 | 11:00
| Bashundhara | 135 | 20:00 | 120 | 11:00 | Mongla | 135 | 12:00 | 127 | 02:00
| BashundharaCement | 132 | 20:00 | 124 | 11:00 | Motijheel | 134 | 19:00 | 124 | 11:00
| Beanibazar | 129 | 00:00 | 125 | 19:30 | Munshiganj | 132 | 19:00 | 124 | 11:00
| Benapole | 138 | 18:00 | 131 | 02:00 | Mymensingh | 129 | 09:00 | 118 | 07:00
| Bhaluka | 131 | 18:00 | 119 | 07:00 | Naogaon | 136 | 15:00 | 123 | 07:00
| Bhandaria | 144 | 09:00 | 133 | 22:00 | Narail | 139 | 18:00 | 133 | 03:00
| Bhangura | 139 | 18:00 | 135 | 04:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bheramara | 137 | 18:00 | 134 | 01:00 | Narshingdi | 128 | 19:00 | 118 | 14:00
| Bheramara(GK) | 138 | 17:00 | 134 | 03:00 | Natore | 136 | 15:00 | 126 | 07:00
| Bhulta | 124 | 19:00 | 116 | 14:00 | Nawabganj | 140 | 20:00 | 129 | 14:00
| Bog-Sherpur | 138 | 15:00 | 129 | 07:00 | Netrakona | 128 | 09:00 | 118 | 02:00
| Bogura | 140 | 15:00 | 129 | 07:00 | New | 135 | 22:00 | 121 | 11:00
| Bogura-230 | 139 | 18:00 | 130 | 07:00 | Niamatpur | 133 | 12:00 | 118 | 07:00
| Brahmanbaria | 132 | 18:00 | 128 | 10:00 | Noapara | 137 | 13:00 | 133 | 02:00
| Cantonment | 138 | 20:00 | 126 | 11:00 | Pabna | 136 | 18:00 | 132 | 03:00
| Chandpur | 137 | 18:30 | 131 | 23:00 | Palashbari | 134 | 16:00 | 120 | 02:00
| Chandraghona | 136 | 19:30 | 129 | 15:00 | Panchagarh | 130 | 17:00 | 113 | 07:00
| Chapai | 133 | 09:00 | 126 | 23:00 | Patuakhali | 139 | 19:00 | 132 | 01:00
| Charsaidpur | 133 | 19:00 | 124 | 09:00 | Payra | 139 | 18:30 | 135 | 01:00
| Chauddagram | 132 | 19:00 | 124 | 15:00 | PHP | 130 | 18:00 | 123 | 15:00
| Chhatak | 130 | 00:00 | 123 | 20:00 | Postogola | 144 | 20:00 | 132 | 12:00
| Chowmuhani | 130 | 18:00 | 120 | 23:00 | Purbachal | 135 | 22:00 | 120 | 10:00
| Chuadanga | 138 | 18:00 | 130 | 23:00 | Purbasadipur | 132 | 17:00 | 115 | 07:00
| Coxsbazar | 128 | 04:00 | 110 | 00:00 | Rahim | 132 | 18:30 | 125 | 11:00
| Cumilla(N) | 133 | 18:30 | 128 | 11:00 | Rajbari | 138 | 18:30 | 131 | 03:00
| Cumilla(S) | 134 | 19:00 | 126 | 19:00 | Rajendrapur | 139 | 18:30 | 123 | 14:00
| Daudkandi | 134 | 00:00 | 125 | 17:00 | Rajshahi | 134 | 15:00 | 126 | 02:00
| Dhaka | 139 | 20:00 | 128 | 11:00 | Rajshahi-230 | 134 | 16:00 | 128 | 06:00
| Dhamrai | 131 | 20:00 | 121 | 14:00 | Ramganj | 134 | 18:30 | 128 | 00:00
| Dhanmondi | 132 | 20:00 | 123.2 | 15:00 | Rampur | 136 | 20:00 | 125 | 15:00
| Dohazari | 135 | 19:00 | 123 | 06:00 | Rampura | 137 | 19:00 | 128 | 10:00
| Faridpur | 138 | 18:00 | 131 | 03:00 | Rangamati | 135 | 19:00 | 128 | 15:00
| Fatullah | 136 | 20:00 | 127 | 11:00 | Rangpur | 133 | 16:00 | 121 | 23:00
| Fenchuganj | 134 | 07:00 | 130 | 14:00 | Ruppur | 137 | 09:00 | 133 | 01:00
| Feni | 131 | 18:30 | 124 | 23:00 | Saidpur | 133 | 17:00 | 122 | 23:00
| Ghorashal | 138 | 18:30 | 135 | 00:00 | Satkhira | 134 | 16:00 | 128 | 02:00
| Goalpara | 138 | 18:00 | 133 | 01:00 | Satmasjid | 139 | 20:00 | 127 | 11:00
| Gollamari | 136 | 18:00 | 131 | 03:00 | Savar | 138 | 20:00 | 125 | 11:00
| Gopalganj | 140 | 18:00 | 136 | 04:00 | Shahjadpur | 140 | 09:00 | 137 | 07:00
| Gopalganj_I | 142 | 18:00 | 136 | 01:00 | Shahjibazar | 134 | 00:00 | 130 | 23:00
| Gulshan | 139 | 20:00 | 127 | 10:00 | Shahmirpur | 138 | 18:30 | 126 | 09:00
| Halishahar | 137 | 19:00 | 126 | 11:00 | Shariatpur | 141 | 18:00 | 133 | 00:00
| Haripur | 132 | 19:00 | 125 | 11:00 | Sherpur | 134 | 18:00 | 117 | 07:00
| HaripurSBU | 135 | 08:00 | 126 | 12:00 | Shikalbaha | 139 | 19:00 | 127 | 15:00
| Hasnabad | 140 | 05:00 | 132 | 10:00 | Shikalbaha-230 | 138 | 19:30 | 127 | 15:00
| Hathazari | 137 | 19:00 | 129 | 15:00 | Shitalakhya | 143 | 20:00 | 128 | 11:00
| Ishurdi | 138 | 18:00 | 133 | 07:00 | Sholosohor | N/A | N/A | N/A | N/A
| Jaldhaka | 133 | 17:00 | 118 | 07:00 | Shyampur | 135 | 19:00 | 126 | 11:00
| Jamalpur | 137 | 18:00 | 120 | 07:00 | Shyampur-230 | 136 | 20:00 | 126 | 15:00
| Jashore | 137 | 16:00 | 132 | 07:00 | Siddhirganj | 132 | 19:00 | 124 | 11:00
| Jhenaidah | 141 | 18:00 | 136 | 05:00 | Sirajganj | 138 | 15:00 | 132 | 00:00
| Jhenaidah-230 | 141 | 16:00 | 136 | 07:00 | Sonargaon | 131 | 02:00 | 124 | 07:00
| Joydebpur | 142 | 18:30 | 129 | 09:00 | Sreemongol | 135 | 19:00 | 130 | 11:00
| Joypurhat | 134 | 09:00 | 123 | 07:00 | Srinagar | 141 | 20:00 | 128 | 14:00
| Juldah | 139 | 19:00 | 127 | 09:00 | SSM | 140 | 19:00 | 130 | 12:00
| Kabirpur | 135 | 20:00 | 117 | 13:00 | Sunamganj | 128 | 00:00 | 121 | 20:00
| Kachua | 134 | 07:00 | 128 | 23:00 | Sylhet | 131 | 00:00 | 128 | 13:00
| Kaliakoir | 136 | 18:00 | 128 | 14:00 | Tangail | 134 | 09:00 | 128 | 22:00
| Kallyanpur | 137 | 19:30 | 126 | 11:00 | Thakurgaon | 131 | 17:00 | 112 | 07:00
Page 7 of 7

## L-Curve
Date | 2022-08-14
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 360 | 7996 | 4109 | 12105 |  |  |  | QF-LDC-11
0:30 | 519 | 7434.5 | 4110 | 11544.5 | Date: | 2022-08-14
1:00 | 678 | 6873 | 4111 | 10984
1:30 | 676 | 6813.5 | 4111 | 10924.5
2:00 | 674 | 6754 | 4111 | 10865
2:30 | 698 | 6677 | 4107 | 10784 | [5 empty] | Gen. at Eve. Peak | 12482 | 12482 MW (20:00 )
3:00 | 722 | 6600 | 4103 | 10703 | [6 empty] | 20:00
3:30 | 723 | 6630 | 4094 | 10724 | [5 empty] | Gen. at Day Peak | 10279 | 10279 MW (09:00 )
4:00 | 724 | 6660 | 4085 | 10745 | [6 empty] | 9:00
4:30 | 710 | 6634.5 | 4053 | 10687.5 | [5 empty] | Highest Generation | 12486
5:00 | 696 | 6609 | 4021 | 10630 | [6 empty] | 23:00
5:30 | 648 | 6561.5 | 3922.5 | 10484
6:00 | 600 | 6514 | 3824 | 10338
6:30 | 577 | 6600.5 | 3826.5 | 10427
7:00 | 554 | 6687 | 3829 | 10516
7:30 | 555 | 6640 | 3752 | 10392
8:00 | 556 | 6593 | 3675 | 10268
8:30 | 757 | 6585 | 3688.5 | 10273.5
9:00 | 958 | 6577 | 3702 | 10279
9:30 | 938 | 6617.5 | 3627.5 | 10245
10:00 | 918 | 6658 | 3553 | 10211
10:30 | 968 | 6591 | 3567 | 10158
11:00 | 1018 | 6524 | 3581 | 10105
11:30 | 964 | 6543 | 3642.5 | 10185.5
12:00 | 910 | 6562 | 3704 | 10266
12:30 | 890 | 6773 | 3706 | 10479
13:00 | 870 | 6984 | 3708 | 10692
13:30 | 950 | 6907.5 | 3755 | 10662.5
14:00 | 1030 | 6831 | 3802 | 10633
14:30 | 1065 | 6848.5 | 3734 | 10582.5
15:00 | 1100 | 6866 | 3666 | 10532
15:30 | 1028 | 6776.5 | 3594 | 10370.5
16:00 | 956 | 6687 | 3522 | 10209
16:30 | 879 | 6741 | 3460 | 10201
17:00 | 802 | 6795 | 3398 | 10193
17:30 | 708 | 6919.5 | 3431 | 10350.5
18:00 | 614 | 7044 | 3464 | 10508
18:30 | 459 | 7606 | 3672 | 11278
19:00 | 304 | 8168 | 3880 | 12048
19:30 | 226 | 8251 | 4055 | 12306
20:00 | 182 | 8406 | 4076 | 12482 |  |  |  | Executive Engineer
20:30 | 215 | 8371.5 | 4109.5 | 12481 |  |  |  | Network Operation Division
21:00 | 248 | 8337 | 4143 | 12480
21:30 | 219 | 8329 | 4136.5 | 12465.5
22:00 | 190 | 8321 | 4130 | 12451 |  |  |  |  | Page 6 of 7
22:30 | 215 | 8330.5 | 4138 | 12468.5
23:00 | 240 | 8340 | 4146 | 12486
23:30 | 300 | 8168 | 4127.5 | 12295.5
24:00 | 360 | 7996 | 4109 | 12105
12482 MW (20:00 )
10279 MW (09:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2022-08-14 |  | Energy |  | 266610397
[13 empty] | 2022-08-14 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 4242 | 894 | 1620 | 502 | 2817 | 930 | 103 | 401 | 610 | 168 | 0 | 410.1009
0:30 | 4107 | 894.5 | 1709.5 | 528 | 2353.5 | 880 | 103 | 409 | 582.5 | 164 | 0 | 995.7618 | Date: | 2022-08-14
1:00 | 3972 | 895 | 1799 | 554 | 1890 | 830 | 103 | 417 | 555 | 160 | 0 | 1581.4227
1:30 | 3971 | 895 | 1797.5 | 527 | 1857 | 825 | 102 | 430 | 563.5 | 160 | 0 | 1544.0989 | [8 empty] | Total Energy | 266.6104 | Total Energy Gen 266.610 MKWHr Energy Not Served 22.823 MKWHr Energy Requirement 289.433 MKWHr
2:00 | 3970 | 895 | 1796 | 500 | 1824 | 820 | 101 | 443 | 572 | 160 | 0 | 1506.7751 | [8 empty] | Energy not Served | 22.8228
2:30 | 3966.5 | 895.5 | 1767.5 | 479.5 | 1812.5 | 820 | 100.5 | 441 | 557.5 | 159 | 0 | 1443.1865 | [8 empty] | Energy Requirement | 289.4332
3:00 | 3963 | 896 | 1739 | 459 | 1801 | 820 | 100 | 439 | 543 | 158 | 0 | 1379.5978
3:30 | 3975 | 896 | 1750 | 480 | 1802 | 820 | 100.5 | 439 | 519.5 | 156 | 0 | 1268.0872 | [6 empty] | Shortage
4:00 | 3987 | 896 | 1761 | 501 | 1803 | 820 | 101 | 439 | 496 | 154 | 0 | 1156.5766
4:30 | 3978 | 895 | 1751.5 | 500.5 | 1793.5 | 815 | 101 | 441 | 477 | 150 | 0 | 1071.3309
5:00 | 3969 | 894 | 1742 | 500 | 1784 | 810 | 101 | 443 | 458 | 146 | 0 | 986.0853
5:30 | 3975.5 | 894.5 | 1730.5 | 430.5 | 1778 | 790 | 99.5 | 443 | 416 | 142 | 0.5 | 936.3202
6:00 | 3982 | 895 | 1719 | 361 | 1772 | 770 | 98 | 443 | 374 | 138 | 1 | 886.5551
6:30 | 3977 | 895.5 | 1721 | 458 | 1767 | 784 | 99 | 423.5 | 354.5 | 131 | 12 | 681.5047 |  |  |  |  | Coal
7:00 | 3972 | 896 | 1723 | 555 | 1762 | 798 | 100 | 404 | 335 | 124 | 23 | 476.4543
7:30 | 3933 | 895.5 | 1714.5 | 443.5 | 1808 | 793 | 100 | 385.5 | 317 | 127 | 33 | 417.2271 |  |  |  | Oil |  |  |  | ,
8:00 | 3894 | 895 | 1706 | 332 | 1854 | 788 | 100 | 367 | 299 | 130 | 43 | 358
8:30 | 3875 | 895 | 1683.5 | 363.5 | 1860.5 | 784 | 100.5 | 363 | 293 | 129 | 61.5 | 518.5
9:00 | 3856 | 895 | 1661 | 395 | 1867 | 780 | 101 | 359 | 287 | 128 | 80 | 679
9:30 | 3834 | 895 | 1650.5 | 404 | 1865.5 | 777.5 | 100.5 | 358.5 | 288.5 | 125 | 76 | 827.5
10:00 | 3812 | 895 | 1640 | 413 | 1864 | 775 | 100 | 358 | 290 | 122 | 72 | 976
10:30 | 3781 | 895 | 1638 | 376.5 | 1863.5 | 777.5 | 101 | 361.5 | 298 | 125 | 75 | 1172.5
11:00 | 3750 | 895 | 1636 | 340 | 1863 | 780 | 102 | 365 | 306 | 128 | 78 | 1369
11:30 | 3753 | 895 | 1618 | 323 | 1930.5 | 782.5 | 102 | 395.5 | 331.5 | 133 | 88 | 1444
12:00 | 3756 | 895 | 1600 | 306 | 1998 | 785 | 102 | 426 | 357 | 138 | 98 | 1519
12:30 | 3823.5 | 894.5 | 1581.5 | 302.5 | 2193 | 782.5 | 102.5 | 402.5 | 339 | 138 | 92 | 1468.5
13:00 | 3891 | 894 | 1563 | 299 | 2388 | 780 | 103 | 379 | 321 | 138 | 86 | 1418
13:30 | 3891 | 894 | 1563 | 299 | 2388 | 780 | 103 | 379 | 321 | 138 | 86 | 1461
14:00 | 3891 | 894 | 1563 | 299 | 2388 | 780 | 103 | 379 | 321 | 138 | 86 | 1504
14:30 | 3913 | 893.5 | 1550.5 | 313 | 2263.5 | 779 | 102 | 379 | 344.5 | 149 | 75 | 1515
15:00 | 3935 | 893 | 1538 | 327 | 2139 | 778 | 101 | 379 | 368 | 160 | 64 | 1526
15:30 | 3893 | 892.5 | 1523 | 268 | 2131.5 | 738 | 101 | 380 | 380 | 159 | 54.5 | 1490
16:00 | 3851 | 892 | 1508 | 209 | 2124 | 698 | 101 | 381 | 392 | 158 | 45 | 1454
16:30 | 3789 | 892 | 1445.5 | 255.5 | 2138 | 685.5 | 101 | 380.5 | 448 | 155 | 30 | 910.8542
17:00 | 3789 | 892 | 1383 | 302 | 2152 | 673 | 101 | 380 | 504 | 152 | 15 | 367.7084
17:30 | 3808 | 892.5 | 1359 | 302.5 | 2304.5 | 669.5 | 101 | 380 | 524.5 | 149 | 10 | 295.3648
18:00 | 3827 | 893 | 1335 | 303 | 2457 | 666 | 101 | 380 | 545 | 146 | 5 | 223.0212
18:30 | 3898 | 893 | 1463.5 | 390 | 2855 | 675.5 | 101 | 370.5 | 611 | 158 | 2.5 | 365.8653
19:00 | 3969 | 893 | 1592 | 477 | 3253 | 685 | 101 | 361 | 677 | 170 | 0 | 508.7094
19:30 | 3993 | 893 | 1587 | 434 | 3423 | 785 | 101 | 360 | 698 | 162 | 0 | 363.1005
20:00 | 4050 | 892 | 1616 | 473 | 3459 | 813 | 101 | 361 | 685 | 162 | 0 | 246.9821
20:30 | 4095 | 892.5 | 1625.5 | 387 | 3457.5 | 851 | 101 | 355 | 683.5 | 163 | 0 | 270.9431
21:00 | 4140 | 893 | 1635 | 301 | 3456 | 889 | 101 | 349 | 682 | 164 | 0 | 294.904
21:30 | 4148 | 892.5 | 1607 | 303.5 | 3452.5 | 895 | 101.5 | 348.5 | 681 | 166 | 0 | 703.952
22:00 | 4156 | 892 | 1579 | 306 | 3449 | 901 | 102 | 348 | 680 | 168 | 0 | 1113
22:30 | 4178 | 892.5 | 1592.5 | 304.5 | 3424 | 907 | 102 | 348 | 681 | 169 | 0 | 1059.5
23:00 | 4200 | 893 | 1606 | 303 | 3399 | 913 | 102 | 348 | 682 | 170 | 0 | 1006
23:30 | 4221 | 893.5 | 1613 | 402.5 | 3108 | 921.5 | 102.5 | 374.5 | 646 | 169 | 0 | 1127.5 | Max Temp. in Dhaka |  | 24.7° C | 31.8° C
24:00 | 4242 | 894 | 1620 | 502 | 2817 | 930 | 103 | 401 | 610 | 168 | 0 | 1249
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 266.610 MKWHr Energy Not Served 22.823 MKWHr Energy Requirement 289.433 MKWHr
Note on W13: Author:

## Generation
g | 2022-08-14
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 38 | 36 | 35 | 36 | 36 | 33 | 35 | 35 | 36 | 35 | 37 | 37 | 38 | 37 | 36 | 36 | 36 | 36 |  | 36 | 36 | 36 | 36 | 37 | 37 | 38 | 860509
2 | Karnaphuli Hydro PP Unit-4 & 5 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 |  | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 1556000
3 | Chattogram TPP-1 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 100 | 100 | 100 | 105 | 105 | 105 | 105 | 105 | 105 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2500000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 0 | 2 |  | 20 | 25 | 25 | 25 | 25 | 25 | 25 | 566370
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 2 | 3 | 7 | 2 | 4 | 11 | 5 | 14 | 0 | 0 | 0 | 0 | [8 empty] | 39825
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 51 | 51 | 24 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 706699
12 | Hathazari 100 MW peaking PP | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 28 | 26 | 26 | 26 | 26 | 26 | 26 |  | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 640808
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 36 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 33 | 986072
| Daudkandi 200 MW PP (B.Trac) | 100 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 52 | 51 | 50 | 70 | 60 | 102 | 100 | 50 | 0 | 0 |  | 100 | 30 | 30 | 0 |  |  | 25 | 1173888
14 | Titas 50 MW Peaking PP | 40 | 40 | 40 | 40 | 40 | 40 | 39 | 39 | 37 | 40 | 40 | 39 | 45 | 45 | 47 | 47 | 39 | 39 |  | 39 | 39 | 39 | 39 | 39 | 39 | 40 | 967916
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 95 | 94 | 97 | 97 | 97 | 92 | 93 | 97 | 93 | 95 | 97 | 67 | 90 | 54 | 92 | 57 | 35 | 37 |  | 37 | 37 | 37 | 87 | 94 | 97 | 97 | 2015000
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 107 | 253 | 132 | 80 | 80 | 80 | 104 |  | 265 | 276 | 278 | 275 | 278 | 278 | 278 | 3394799
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 45 | 217454
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4378500
24
25 | Ghorasal 365 MW CCPP Unit-7 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 7201527
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 40 | 40 | 38 | 38 | 38 | 38 | 38 | 37 | 39 | 36 | 36 | 35 | 35 | 35 | 35 | 18 | 18 | 30 |  | 31 | 35 | 35 | 35 | 38 | 38 | 38 | 818640
33 | Ashuganj 225 MW CCPP | 187 | 182 | 182 | 188 | 198 | 209 | 209 | 200 | 195 | 205 | 201 | 206 | 206 | 202 | 207 | 206 | 206 | 184 |  | 209 | 208 | 211 | 210 | 210 | 208 | 211 | 4860000
34 | Ashuganj 450 MW CCPP(South) | 290 | 290 | 290 | 290 | 260 | 260 | 280 | 280 | 280 | 260 | 260 | 290 | 270 | 290 | 270 | 270 | 270 | 270 |  | 270 | 270 | 270 | 305 | 310 | 310 | 310 | 6930000
| Ashuganj 450 MW CCPP(North) | 290 | 290 | 290 | 290 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 300 | 350 | 310 | 328 | 328 | 325 | 310 |  | 280 | 280 | 325 | 325 | 325 | 330 | 325 | 7610200
Ashuganj 420 MW CCPP(East)
35 | Ashuganj 55 MW PP (Precision) | 41 | 42 | 42 | 40 | 40 | 40 | 40 | 53 | 53 | 49 | 47 | 48 | 47 | 50 | 49 | 50 | 51 | 52 |  | 52 | 52 | 52 | 52 | 53 | 54 | 54 | 1163040
36 | Chandpur 150 MW CCPP | 49 | 50 | 50 | 50 | 50 | 50 | 30 | 30 | 30 | 30 | 30 | 30 | 62 | 84 | 85 | 85 | 85 | 136 |  | 136 | 136 | 136 | 136 | 136 | 137 | 136 | 1788270
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 404 | 408 | 408 | 407 | 408 | 407 | 407 | 407 | 407 | 405 | 406 | 406 | 407 | 406 | 406 | 407 | 407 | 409 |  | 407 | 406 | 407 | 406 | 407 | 411 | 411 | 9897980
40 | Meghnaghat 450 MW CCPP(MPL) | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 |  | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 5195000
41 | Haripur 360MW CCPP(HPL) | 339 | 338 | 339 | 332 | 334 | 333 | 331 | 332 | 333 | 324 | 342 | 348 | 311 | 317 | 327 | 337 | 302 | 271 |  | 343 | 302 | 336 | 331 | 271 | 303 | 312 | 7782000
42 | RPCL 210MW CCPP | 102 | 102 | 94 | 95 | 101 | 103 | 94 | 82 | 65 | 62 | 62 | 62 | 61 | 61 | 63 | 71 | 71 | 73 |  | 88 | 88 | 99 | 99 | 98 | 102 | 103 | 1924800
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 1 | 10 | 14 | 37 | 43 | 46 | 45 | 48 | 14 | 45 | 28 | 4 | 2 |  | 0 | [6 empty] | 330300
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1020000
45 | Fenchugonj CCPP Phase-2 | [24 empty] | 20 | 20 | 52440
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 64 | 64 | 63 | 64 | 63 | 64 | 63 | 63 | 61 | 58 | 55 | 60 | 55 | 55 | 55 | 60 | 58 | 64 |  | 64 | 62 | 64 | 63 | 60 | 60 | 64 | 1452672
48 | Shahjibazar 86MW PP (Shahjibazar) | 81 | 81 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 821760
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 214 | 214 | 221 | 221 | 221 | 221 | 220 | 220 | 220 | 221 | 221 | 221 | 221 | 221 | 220 | 220 | 221 | 220 |  | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 5230930
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 13 | 15 | 17 | 25 | 29 | 29 | 29 | 359660
53 | Sylhet 10MW PP (Desh) | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 5 | 7 | 7 | 7 | 7 | 7 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 192240
54 | Hobiganj 11MW PP Cofidence-E | [25 empty] | 0 | 0
55 | Fenchugonj 51 MW PP (Barakatullah) | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 11 | [10 empty] | 6 | 11 | 11 | 11 | 11 | 11 | 11 | 336000
56 | Shahjahanulla 25 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 187824
57 | Bibiana-II 341 MW CCPP (Summit) | 300 | 305 | 300 | 320 | 290 | 280 | 280 | 275 | 280 | 300 | 295 | 290 | 290 | 290 | 290 | 270 | 280 | 290 |  | 270 | 290 | 270 | 275 | 300 | 290 | 300 | 7154000
| Bibiyana South 400 MW | 400 | 400 | 393 | 400 | 400 | 400 | 400 | 400 | 375 | 395 | 383 | 393 | 385 | 390 | 393 | 350 | 320 | 320 |  | 384 | 398 | 391 | 400 | 400 | 400 | 400 | 9207200
58 | Nababganj 55 MW PP (Southern power ) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 884309
59 | Tangail Palli Power Gen 22 MW | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 9 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 287520
60 | Barabkunda 22 MW PP (Regent) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 367872
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 0 |  |  | 19 | 19 | 19 | 19 | 10 | 10 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 396468
62 | Tangail 22 MW PP (Doreen) | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 20 | 20 | 22 | 22 | 20 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 469188
63 | Impoprt (Tripura) | 160 | 160 | 158 | 154 | 146 | 138 | 124 | 130 | 128 | 122 | 128 | 138 | 138 | 150 | 160 | 158 | 152 | 146 |  | 170 | 162 | 162 | 164 | 168 | 170 | 168 | 3574080
64 | Malancha, Ctg. EPZ (United) | 30 | 30 | 30 | 30 | 37 | 37 | 39 | 16 | 6 | 5 | 3 | 3 | 3 | 2 | 2 | 2 | 12 | 4 |  | 18 | 18 | 26 | 31 | 36 | 38 | 39 | 487680
65 | Feni 22MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 19 | 19 | 19 | 19 | 22 | 22 | 19 | 19 | 19 | 19 |  | 20 | 20 | 21 | 21 | 21 | 21 | 21 | 477360
66 | Feni 11 MW PP (Doreen) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 5 | 10 | 10 | 10 | 0 |  | 10 | 10 | 10 | 10 | 5 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 220140
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 30 | 30 | 30 | 30 | 30 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 795500
68 | Cumilla 25 MW PP (Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 18 | 18 | 20 | 20 | 20 | 20 | 18 |  | 18 | 20 | 21 | 17 | 17 | 17 | 20 | 494000
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 26 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 26 | 26 | 26 | 0 | 17 | 17 | 17 | 17 | 22 | 22 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 511200
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 819100
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 32 | 32 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 28 | 30 | 30 | 30 | 30 | 30 | 30 | 728300
73 | Ghorashal 108MW PP (Regent) | 87 | 87 | 88 | 88 | 88 | 88 | 86 | 86 | 86 | 86 | 83 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 83 | 83 | 83 | 84 | 1972772
| Feni Lanka Power | [25 empty] | 0 | 0
| Chowmuhani 113 MW | 30 | 29 | 29 | 28 | 28 | 28 | 28 | 29 | 29 | 28 | 29 | 28 | 29 | 28 | 28 | 28 | 28 | 51 |  | 57 | 57 | 57 | 57 | 57 | 57 | 19 | 853440
| Manikgonj 162MW PP(MPGL) | 76 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 55 | 108 | 108 | 142 | 162 | 162 | 162 |  | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 2304000
77 | Siddhirganj 100 PP(Dutch Bangla) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 35 | 49 | 49 | 49 | 49 | 49 | 34 | 414470
78 | Gazipur 52 MW PP | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 35 | 41 |  | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 908640
79 | Kodda 150MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 30 | 125 | 129 |  | 130 | 130 | 128 | 110 | 118 | 128 | 16 | 1077120
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | [26 empty] | 0
| Gazipur 100 MW PP | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 70 | 70 | 70 | 70 | 88 | 88 | 88 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2194800
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 1 | 2 | 3 | 2 | 6 | 3 | 4 | 4 | 1 | 1 | 0 | [8 empty] | 26760
| Jodiac Power | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 |  | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 916261
| Karnaphuli Power Ltd. | 55 | 52 | 50 | 45 | 55 | 55 | 55 | 45 | 35 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 51 | 51 | 53 | 55 | 1282976
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL) | 7 | 8 | 8 | 8 | 8 | 7 | 8 | 7 | 8 | 8 | 7 | 8 | 8 | 8 | 7 | 8 | 7 | 8 |  | 23 | 50 | 50 | 50 | 50 | 48 | 34 | 405120
| Meghnaghat 104 MW PP (OPCL) |  |  |  | 14 |  |  |  | 3 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 50 | 53 | 53 | 53 | 53 | 53 | 0 | 468480
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 787440
92 | Fenchuganj 44MW (Energyprima) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | [10 empty] | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 171720
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 43 | 43 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1187492
94 | Gagnagar 102 MW PP (Digital Power) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 16 |  | 50 | 50 | 50 | 50 | 50 | 50 | 24 | 419328
95 | Patenga 50MW PP (Baraka) | 6 | 6 | 6 | 6 | 6 | 6 | [11 empty] | 0 |  | 26 | 36 | 42 | 40 | 6 | 6 | 4 | 150720
96 | Chattogram 108 MW PP (ECPV) | 12 | 12 | 12 | 13 | 12 | 14 | 13 | 13 | 11 | 12 | 12 | 12 | 31 | 31 | 31 | 31 | 30 | 35 |  | 84 | 84 | 85 | 90 | 95 | 94 | 25 | 808320
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 40 | 40 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 768018
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1311409
101 | Kushiara 163 MW CCPP (KP)
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 0 |  |  |  |  | 1 | 1 | 1 | 0 | 0 | 0 | [8 empty] | 5950
103 | Kamalaghat 54 MW PP(Banco Energy) | 35 | 35 | 35 | 35 | 35 | 35 | 18 | 18 | 18 | 18 | 18 | 35 | 35 | 35 | 17 | 17 | 17 | 17 |  | 17 | 35 | 35 | 35 | 35 | 35 | 54 | 696240
104 | Keranigonj 300 MW PP (APR) | [6 empty] | 101 | 52 | 11 | 108 | 100 | 49 | 54 | 52 | 112 | 54 | 302 | 303 |  | 300 | 304 | 303 | 301 | 306 | 303 | 300 | 3085378
105 | Bramhangoan 100 MW PP (Aggreko) | 90 | 90 | 50 | 92 | 92 | 50 | 94 | 50 | 91 | 91 | 91 | 25 | 50 | 75 | 50 | 50 | 0 |  |  | 30 | 30 | 30 | 0 |  |  | 92 | 1356855
106 | Mymensingh 200 MW PP (United) | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 77 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 182 |  | 185 | 186 | 186 | 188 | 183 | 188 | 48 | 2236800
112 | Aurahati 100MW PP (Aggreko) | 99 | 95 | 95 | 95 | 93 | 50 | 95 | 50 | 94 | 93 | 25 | 25 | 25 | 25 | 25 | 25 | 0 |  |  | 30 | 30 | 70 | 0 |  |  | 50 | 1188866
114 | Kodda 149 MW PP Unit-1 (Summit) | 35 | 35 | 34 | 28 | 32 | 35 | 35 | 35 | 35 | 35 | 35 | 60 | 137 | 54 | 35 | 35 | 34 | 38 |  | 110 | 120 | 142 | 136 | 142 | 86 | 72 | 1482050
115 | Juldah 100 MW PP Unit-3 (Acorn) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 887040
116 | Chandpur 200MW (Desh energy) | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4761120
117 | Ashuganj 150MW PP (Midland) | 137 | 137 | 137 | 137 | 137 | 137 | 138 | 134 | 130 | 134 | 132 | 127 | 114 | 117 | 113 | 118 | 125 | 130 |  | 128 | 131 | 132 | 133 | 135 | 137 | 130 | 3134690
118 | Bibiyana-III 400 MW CCPP | 403 | 401 | 402 | 402 | 402 | 401 | 401 | 401 | 400 | 398 | 370 | 377 | 404 | 405 | 379 | 365 | 352 | 353 |  | 402 | 402 | 402 | 399 | 403 | 403 | 402 | 9368000
| Jamalpur 115 MW PP (United) | 49 | 50 | 50 | 50 | 50 | 49 | 49 | 69 | 69 | 69 | 69 | 68 | 68 | 68 | 68 | 67 | 69 | 78 |  | 79 | 78 | 79 | 79 | 79 | 79 | 49 | 1540800
| Anwara 300 MW PP (United) | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 118 | 123 | 124 | 124 | 123 | 141 | 142 | 142 | 142 | 142 | 142 |  | 208 | 210 | 214 | 214 | 214 | 214 | 214 | 3013418
| Juldah unit-2 (Acorn) | 50 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 50 | 100 | 100 | 100 | 100 | 100 | 100 | 965760
| Anlima Energy Ltd. | 89 | 89 | 89 | 89 | 94 | 95 | 107 | 107 | 107 | 107 | 96 | 107 | 107 | 92 | 107 | 107 | 107 | 107 |  | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 2461418
| Bhairob 54.5 MW | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 31 | 17 | 17 | 29 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 838800
| Spectra Solar Plant Ltd. | [5 empty] | 0 | 7 | 12 | 3 | 16 | 9 | 17 | 5 | 4 | 8 | 7 | 3 | 1 |  | 0 | [6 empty] | 84400
| Chandpur 115(Doreen) | 67 | 74 | 74 | 74 | 74 | 74 | 74 | 72 | 61 | 72 | 73 | 73 | 59 | 71 | 74 | 73 | 72 | 62 |  | 73 | 73 | 73 | 59 | 57 | 57 | 58 | 1661760
| Kanchan Purbachal Power Generation Ltd. | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 39 | 35 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1303560
Mirsharai 150 MW (Oil)
Mirsharai 150 MW (Gas)
120 | Eastern Zone Total | 6873 | 6754 | 6600 | 6660 | 6609 | 6514 | 6687 | 6593 | 6577 | 6658 | 6524 | 6562 | 6984 | 6831 | 6866 | 6687 | 6795 | 7044 | 0 | 8168 | 8251 | 8406 | 8337 | 8321 | 8340 | 7996 | 171135231
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | 16 | 16 | 16 | 16 | 16 | [5 empty] | 26 | 32 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 318720
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 20 | 20 | 20 | 20 | 20 | [11 empty] | 0 | 20 |  | 51 | 42 | 36 | 41 | 31 | 20 | 21 | 295200
| Khulna 225 MW CCPP | 226 | 227 | 224 | 226 | 226 | 228 | 228 | 227 | 229 | 228 | 227 | 231 | 229 | 227 | 229 | 231 | 230 | 230 |  | 231 | 230 | 231 | 219 | 218 | 218 | 219 | 5493120
129 | Rupsha 105 MW PP (Orion rupsha) | [8 empty] | 10 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 10 | 45 |  | 53 | 53 | 53 | 53 | 53 | 53 | 17 | 449280
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 0 | 2 | 10 | 24 | 3 | 10 | 9 | 17 | 31 | 1 | 2 | 5 | 1 |  | 0 | [6 empty] | 135360
131 | Rampal 1320 MW (BIFPCL)
132 | United Payra Power Ltd. | [19 empty] | 22 | 35 | 35 | 35 | 35 | 35 | 35 | 224400
133 | Bhola Nutan Biddut BD LTD (GAS) | 221 | 221 | 220 | 221 | 221 | 212 | 218 | 223 | 206 | 220 | 220 | 184 | 186 | 184 | 184 | 160 | 80 | 70 |  | 59 | 70 | 70 | 70 | 36 | 36 | 0 | 3896618
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 16 | 16 | 16 | 16 | [13 empty] | 0 |  | 48 | 48 | 48 | 48 | 48 | 48 | 64 | 356640
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 30 | 55 | 30 | 20 | 20 | 20 | 81 | 81 | 81 | 87 | 86 |  | 87 | 87 | 87 | 87 | 87 | 102 | 136 | 2145353
140 | Bhola 33 MW PP (Venture) | 23 | 16 | 10 | 11 | 13 | 10 | 9 | 11 | 12 | 10 | 14 | 16 | 16 | 11 | 18 | 19 | 18 | 4 |  | 17 | 19 | 23 | 26 | 29 | 30 | 29 | 377267
141 | Noapara 100 MW PP (Bangla Trac) | 91 | 91 | 90 | 90 | 91 | 91 | 91 | 50 | 20 | 10 | 14 | 87 | 90 | 60 | 20 | 10 | 0 | 0 |  | 7 | 10 | 10 | 0 |  |  | 10 | 1140480
142 | Noapara 40 MW PP (Khanjahan Ali) | 8 | 8 | 8 | 8 | [8 empty] | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 126000
143 | Gopalganj 100 MW Peaking PP | 65 | 65 | 65 | 60 | 22 | [12 empty] | 10 |  | 45 | 74 | 70 | 70 | 63 | 63 | 63 | 650368
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | 105 | 105 | 85 | 85 | 85 | 85 | 85 | 88 | 89 | 71 | 71 | 71 | 70 | 70 | 71 | 71 | 71 | 71 |  | 71 | 71 | 70 | 88 | 105 | 105 | 88 | 2019024
146 | Bheramara HVDC | 895 | 895 | 896 | 896 | 894 | 895 | 896 | 895 | 895 | 895 | 895 | 895 | 894 | 895 | 893 | 892 | 892 | 893 |  | 893 | 893 | 892 | 893 | 892 | 893 | 894 | 21618909
147 | Bheramara 410 MW CCPP | 160 | 160 | 160 | 170 | 175 | 175 | 175 | 175 | 170 | 165 | 160 | 160 | 155 | 155 | 150 | 150 | 155 | 160 |  | 160 | 165 | 165 | 170 | 170 | 165 | 170 | 4063968
148 | Payra 1320 MW | 580 | 570 | 570 | 570 | 560 | 520 | 500 | 470 | 460 | 460 | 460 | 470 | 470 | 470 | 460 | 390 | 360 | 350 |  | 370 | 470 | 490 | 570 | 580 | 590 | 610 | 13034800
149
150 | Barapukuria TPP Unit-1 | [6 empty] | 48 | 68 | 70 | 65 | 70 | 65 | 60 | 64 | 69 | 68 | 73 | 76 |  | 75 | 75 | 83 | 79 | 81 | 83 | 80 | 1204363
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 249 | 249 | 240 | 240 | 240 |  | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 6022400
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 16 | 16 | 16 | 16 | 16 | [10 empty] | 0 | 24 | 24 |  | 24 | 24 | 24 | 32 | 32 | 32 | 32 | 289840
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 0 | 1 | 4 | 0 | 0 | 3 | 2 | 0 | 0 | 1 | 0 | 0 | [8 empty] | 17340
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 152 | 152 | 152 | 152 | 152 | 152 | 152 | 152 | 152 | 152 | 152 | 152 | 152 | 152 | 153 | 152 | 152 | 153 |  | 153 | 153 | 153 | 153 | 153 | 152 | 151 | 3875100
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
| Sirajgonj 225 MW CCPP Unit-2 (Oil) | 191 | 216 | 215 | 213 | 217 | 215 | 176 | 140 | 130 | 130 | 138 | 195 | 150 | 160 | 150 | 150 | 150 | 150 |  | 130 | 130 | 130 | 130 | 130 | 130 | 182 | 4179118
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 150 | 150 | 150 | 150 | 151 | 157 | 158 | 157 | 156 | 152 | 147 | 145 | 144 | 142 | 141 | 143 | 143 | 145 |  | 146 | 147 | 147 | 148 | 148 | 148 | 148 | 3806309
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 313 | 312 | 336 | 345 | 345 | 345 | 346 | 336 | 333 | 324 | 318 | 305 | 302 | 292 | 260 | 260 | 230 | 230 |  | 331 | 327 | 328 | 328 | 328 | 329 | 322 | 7510545
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | 28 | 28 | 28 | 28 | 24 | [7 empty] | 5 | 6 | 17 | 27 | 28 | 28 |  | 28 | 29 | 28 | 30 | 37 | 40 | 40 | 421117
162 | Bogra 22 MW PP (GBB) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 19 | 18 | 10 | 16 | 16 | 17 | 16 | 18 | 18 | 20 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 439440
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 0 | 0 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 220212
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 823024
167 | Katakhali 50 MW Peaking PP | 24 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 31 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 544200
168 | Santahar 50 MW Peaking PP | 33 | 33 | 33 | [10 empty] | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 447299
169 | Natore 52 MW PP (Rajlanka) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 195082
170 | Chapainawabganj 100 MW Peaking PP | 45 | 45 | 44 | 44 | 44 | 44 | 45 | 45 | 45 | 45 | 45 | 38 | 38 | 38 | 38 | 38 | 38 | 38 |  | 80 | 80 | 80 | 80 | 80 | 80 | 66 | 1148800
171 | Baghabari 200 MW PP (Paramount) | 174 | 174 | 174 | 174 | 174 | 120 | 124 | 80 | 127 | 60 | 60 | 50 | 20 | 50 | 20 | 20 | 0 |  |  | 10 | 30 | 30 | 0 |  |  | 25 | 1908121
| Bagura 113 MW PP (Confidence)-2 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 57 | 92 | 94 | 94 | 94 | 94 | 94 |  | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 1815744
172 | Confidence Power Bogura Unit-1 113 MW | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 95 | 95 | 95 | 36 | 36 | 36 |  | 90 | 95 | 95 | 95 | 95 | 95 | 95 | 1602720
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 70 | 70 | 70 | 69 | 70 | 70 | 70 | 70 | 69 | 69 | 68 | 82 | 95 | 95 | 95 | 95 | 96 | 112 |  | 113 | 112 | 112 | 112 | 113 | 113 | 98 | 2100067
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1 | 2 | 3 | 5 | 7 | 7 | 5 | 7 | 5 | 6 | 2 | 1 |  | 0 | [6 empty] | 51362
178 | Energypac Power Venture Thakurgaon Ltd. | [11 empty] | 15 | 17 | 17 | 17 | 17 | 32 | 36 |  | 72 | 72 | 72 | 72 | 72 | 72 | 0 | 507456
178