## Forecast
8 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2022-08-16 | Tuesday
|  |  | Date (day): | 2022-08-16 |  | Tuesday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11733.6 | MW |  |  | (b) At Evening Peak Hour : |  | 13950 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2022-08-15 | 2022-08-16 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 196 | 280 | 300 | 300 |  | 65 | Machine problem
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 86 | 96 | 92 | 92 |  | 16 | Engine problem
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 398 | 395 | 412 | 412
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 331 | 337 | 330 | 330 | 30 |  | Gas shortage
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 240 | 450 | 450 | 225 |  | Gas shortage & GT-2 S/D
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 0 | 50 | 8 | 50 | 50 |  | Fuel shortage
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 0 | 0 | 0 | 0 |  | 102 | Under maint
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 55 | 55 | 30 | 30 |  | 25 | Engine problem
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 19 | 19 | 19 |  | 3 | Engine problem
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 97 | 190 | 100 | 100 | 110 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 0 | 49 | 8 | 50 | 50 |  | Fuel shortage
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 8 | 50 | 8 | 50 | 52 |  | Fuel shortage
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 35 | 54 | 17 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 82 | 125 | 16 | 132 |  | 17 | Fuel shortage
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 55 | 35 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 44 | 44 | 45 | 45 |  | 35 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 31 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 33 | 41 | 41 | 41 |  | 11 | Engine problem
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 50 | 276 | 95 | 285 |  |  | Fuel shortage
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 20 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 0 | 25 | 60 | 96
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 25 | 50 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 50 | 149 | 35 | 149 |  |  | Fuel shortage
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 105 | 105 | 88 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 34 | 55 | 17 | 55 | 49 |  | Fuel shortage
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 145 | 162 | 35 | 162 |  |  | Fuel shortage
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 22 | 0 | 30 | 0
| 40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 55 | 55 | 55 | 55
|  | Dhaka area Total |  |  |  |  | 6263 | 5847 | 2348 | 3253 | 2777 | 3818 | 1287 | 954
| 41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 105 | 110 | 105 | 105 | 75 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 25 | 25 | 25 | 25
| 43 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 19 | 0 | 20 | 0
| 44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 9 | 0 | 6 | 42 |  | 8 | Engine problem
| 45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 103 | 147 | 145 | 145 |  | 85 | Low Water Level
| 46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | S/D due to HGPI
| 47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
| 48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 68 | 105 | 17 | 105 |  |  | Fuel shortage
| 49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 26 | 26 | 26 | 72 |  | Fuel shortage
| 50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 17 | 51 | 51 |  | Fuel shortage
| 51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 33 | 33 | 33 | 33 | 67 |  | Fuel shortage
| 52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 76 | 90 | 21 | 90 |  | 10 | Engine problem
| 53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 15 | 15 | 15 | 15 |  | 7 | Engine problem
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 40 | 42 | 10 | 30
| 54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 85 | 12 | 95 |  | 13 | Fuel shortage
| 55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
| 56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 190 | 300 | 123 | 210 |  |  | Fuel shortage
| 57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 36 | 36 | 36 | 36 |  | 18 | Engine problem
| 58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 68 | 110 | 55 | 110 | 0 |  | Fuel shortage
| 59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 92 | 100 | 20 | 100 |  |  | Fuel shortage
| 60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 107 | 107 | 107 | 107 |  | 9 | Engine problem
|  | Mirsharai 150 MW |  | Gas/HSD | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 990 | 1382 | 798 | 1325 | 445 | 525
| 61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 204 | 211 | 205 | 210
| 63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 290 | 330 | 325 | 330 | 30
| 64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 280 | 300 | 310 | 320 | 40
|  | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+136*1 | 284 | 284 | 0 | 0 | 0 | 0 |  |  | On test.
| 65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 35 | 34 | 35 | 35 |  | 10 | Engine problem
| 66 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 55 | 51 | 56 | 55 | 55
| 67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 80 | 100 | 140 | 143 |  | 7 | Engine problem
| 70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 40 | 40 | 40 |  | 12 | Engine problem
| 71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 136 | 136 | 0 | 0 |  | 163 | Machine problem
| 72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 76 | 200 | 200 | 200
| 73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 22 | 22 | 22
| 74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 10 | 10 | 10 | 10
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 134 | 136 | 143 | 166
| 75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 | 52 |  | Fuel shortage
| 77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 14 | 20 | 20 | 21 |  | 4 | Engine problem
| 78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 200 | 200
| 79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 0 | 0 | 114 |  | Fuel shortage
| 80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 113 | 9 | 57 | 56 |  | Fuel shortage
| 81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 35 | 35 | 35 | 35 |  | 19 | 33 kV feeder fault
| 82 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 35 | 93 | 96 | 100 | 15 |  | Fuel shortage
|  | Cumilla Area Total |  |  |  |  | 3193 | 3169 | 1502 | 1928 | 1937 | 2036 | 628 | 215
| 83 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 100 | 151 | 130 | 100 | 102 |  | Gas shortage
| 84 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 22 | 22 | 22
| 85 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0 |  | 8 | Under maint.
| 86 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 87 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 188 | 191 | 80 | 180 |  | 20 | Engine problem
| 88 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 106 | 87 | 68 | 79 |  | 36 | Engine problem
| 89 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 49 | 0 | 50 | 0
| 90 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 12 | 12 |  | 10 | Engine problem
|  | Mymensingh Area Total |  |  |  |  | 717 | 614 | 477 | 463 | 363.6 | 393 | 102 | 74
| 91 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 30 | 43 | 43 | 43 |  | 27 | Machine problem.
| 92 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 |  | 60 | Machine problem
| 93 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Gas shortage
| 94 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
| 95 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 0 | 5 | 5 | 5 | 46 |  | Gas shortage
| 96 | Fenchuganj 44MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 0 | 5 | 5 | 5 | 45 |  | Gas shortage
| 97 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0
| 98 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 57 | 65 | 62 | 64
| 99 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 10 | 81 | 10 | 80
| 100 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
| 101 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 222 | 221 | 220 | 220
| 102 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Gas shortage
| 103 | Sylhet 50MW PP (EPL) |  | Gas | NENP | 27*2 | 50 | 50 | 0 | 5 | 0 | 0 | 50 |  | Gas shortage
| 104 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 8 | 8 | 0 | 0 | 25 |  | Gas shortage
| 105 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 290 | 300 | 300 |  |  | FGMO
| 106 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 404 | 400 | 400 | 400
| 107 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 9 | 9 | 9 | 9
| 108 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 386 | 400 | 400 | 400
|  | Sylhet Area Total |  |  |  |  | 2522 | 2477 | 1456 | 1562 | 1484 | 1556 | 186 | 680
| 109 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 893 | 884 | 901 | 901
| 110 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 66 | 66 | 16 | 66 | 49 |  | Fuel shortage
| 111 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 40 | 0 | 36 |  | 18 | Engine problem
| 112 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 170 | 150 | 225 | 225
| 113 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 52 | 47 | 70 |  | 39 | Engine problem
| 114 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 205 | 260 | 210 | 180 | 230 |  | Gas shortage
| 115 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 32 | 32 | 32 | 32 | 8 |  | Fuel shortage
| 116 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 90 | 90 |  | 10 | Engine problem
| 117 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 17 | 53 | 17 | 52 | 53 |  | Fuel shortage
| 118 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 61 | 105 | 90 | 105
| 119 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 42 | 0 | 100 | 0
|  | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
|  | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
|  | Khulna Area Total |  |  |  |  | 2388 | 2384 | 1486 | 1642 | 1728 | 1757 | 356 | 67
| 120 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 16 | 48 | 32 | 64 |  |  | Line O/L
| 121 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 20 | 27 | 19 | 27 |  | 13 | Engine problem
| 122 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 152 | 144 | 151 | 151
|  | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
| 123 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 540 | 610 | 620 | 620 |  |  | Line O/L
| 124 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 0 | 57 | 0 | 0 |  | 220 | Machine problem
| 125 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 35 | 50 | 110 |  |  | Line O/L
|  | Barisal Area Total |  |  |  |  | 1958 | 1958 | 728 | 921 | 872 | 972 | 0 | 233
| 126 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 127 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 16 | 32 | 32 |  | 20 | Engine problem
| 128 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 29 | 0 | 40 |  | 31 | Engine problem
| 129 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 130 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 42 | 50 | 42 | 50 |  | 0 | Engine problem
| 131 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 24 | 16 | 40 |  | 10 | Engine problem
| 132 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 153 | 159 | 170 | 150 | 60 |  | Gas shortage
| 133 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 170 | 130 | 220 | 220
| 134 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 169 | 203 | 160 | 150 | 70 |  | Gas shortage
| 135 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 414 | 423 | 400 | 380 | 34 |  | Gas shortage
| 136 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 33 | 33 | 33 |  | 17 | Engine problem
| 137 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 20 | 22 | 21 | 22
| 138 | Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 139 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 140 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 8 | 8 | 8 | 44 |  | Fuel shortage
| 141 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 81 | 50 | 80 |  | 24 | Engine problem
| 142 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 100 | 175 | 25 |  | Engine problem
| 143 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 59 | 94 | 50 | 94 |  | 19 | Engine problem
| 144 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 60 | 95 | 55 | 95 |  | 18 | Engine problem
| 145 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 6 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2129 | 1112 | 1378 | 1374 | 1580 | 404 | 139
| 146 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 80 | 79 | 70 | 83 | 85
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
| 147 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 250 | 250 | 250 | 250 | 24 |  | Machine problem
| 148 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
| 149 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
| 150 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 96 | 103 | 55 | 90 |  |  | Engine problem
| 151 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 7 | 0 | 8 | 0
| 152 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 90 | 90 | 17 | 90 |  | 25 | Fuel shortage
|  | Rangpur Area Total |  |  |  |  | 800 | 720 | 523 | 522 | 400 | 513 | 149 | 110
|  | Total |  |  |  |  | 22482 | 21680 | 10622 | 13051 | 11733.6 | 13950 | 3557 | 2997
| A. |  | 2022-08-15 | (Yesterday) |  |  |  |  | Monday
| 1 | Highest Generation : |  |  | 13081 | MW at | 23:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 9910 | MW at | 9:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 13110 | MW
| 3 | Day peak Generation : |  |  | 10622 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 12585.22 | MW
| 4 | Evening peak Generation : |  |  | 13051 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 54 | MW
| 5 | Total Energy Generation : |  | 271.6676 | MKWHr | By Solar | 1.082 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
|  | By Gas : | 140.2205 | MKWHr |  | By Oil: | 80.4659 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 22.3907 | MKWHr |  | By Hydro: | 2.7663 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 3557 | MW | Dhaka | 4208.5 | 4208.5 |  | 0 |  | 18:00 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2997 | MW | Chittagong | 1276.5 | 1276.5 |  | 0 |  | 19:00 |  | 0
|  |  |  | Total = |  |  | 6554 | MW | Khulna | 1513.6 | 1513.6 |  | 0 |  | 19:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1079.53 | MMCFD |  |  | Rajshahi | 1359.8 | 1359.8 |  | 0 |  | 20:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 161413527.572 | ii) Oil : | Taka | 1114226945.95 | Comilla | 1225 | 1225 |  | 0 |  | 21:00 |  | 54
|  |  | iii) Coal : |  | 173385304.16 | Total | Taka | 1449025777.682 | Mymensingh | 1171 | 1117 |  | 54 |  | 22:00 |  | 67
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0 | MKWHr. | Sylhet | 553 | 553 |  | 0 |  | 23:00 |  | 63.5887
|  | ii) During Peak Demand : |  |  | 76 | MW (E to W) at | 21:00 | hrs | Barisal | 368.82 | 368.82 |  | 0 |  | 24:00 |  | 252.5115
|  | iii) Maximum : |  |  | 46 | MW at | 19:00 | hrs | Rangpur | 909 | 909 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 32.8° C |  |  | Total | 12585.22 | 12531.22 |  | 54
| B. |  | 2022-08-16 | (Today) |  |  |  | Tuesday |  |  | Probable max. temperature in Dhaka |  |  | 31.9° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 14200 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 230 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 13950 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 12000 | MW
| 4 | Reserve(Generation end) |  |  |  | - | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 294.9071 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 10559 | MW at | 7:00 | 0 | 25 | 45 | 48 | 37 | 36 | 11 | 0 | 28
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.528 | MKWHr. | ii) HVDC Flow at Peak Time |  | 884 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.2141 | MKWHr. | iii) Maximum HVDC Flow : |  | 894 | MW at | 4:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 95.95 |  | (b) Today: | 95.95 |  | (c) Rule Curve: |  | 93.8
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2022-08-15
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 300 | 86 | 0 | 413 | 292 |  | 0 | 225 | 0 | 33 | 0 | 55 | 0 | 0 | 97 | 32 | 24 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 20 | 33 | 30 | 41 | 0 | 38 | 65 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 51 | 33 | 12 | 6 | 15 | 39 | 0 | 0 | 0 | 320 | 310 | 210 | 63 | 136 | 35 | 55 | 0 | 51 | 0 | 40 | 0 | 21 | 10 | 33 | 20 | 160 | 102 | 0 | 22 | 0 | 43 | 30 | 0 | 10 | 0 | 0 | 60 | 78 | 0 | 220 | 0 | 11 | 9 | 290 | 8 | 0 | 25 | 165 | 166 | 92 | 48 | 50 | 71 | 0 | 20 | 170 | 135 | 402 | 49 | 105 | 17 | 0 | 280 | 36 | 55 | 0 | 8 | 39 | 400 | 0 | 0 | 162 | 107 | 0 | 35 | 0 | 74 | 55 | 0 | 0 | 0 |  | 893 | 0 | 170 | 0 | 16 | 218 | 0 | 0 | 16 | 63 | 8 | 152 | 28 | 64 | 0 | 0 | 0 | 32 | 40 | 45 | 0 | 34 | 16 | 8 | 33 | 22 | 0 | 11 | 81 | 0 | 240 | 0 | 0 | 151 | 0 | 0 | 219 | 0 | 20 | 152 | 0 | 323 | 0 | 25 | 94 | 105 | 98 | 0 | 0 | 95 | 600 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 |  | 7630 | 4107 | 11737 | 4260 | 893 | 1582 | 378 | 2625 | 921 | 103 | 437 | 597 | 160 | 0 | 380.6105 | 95.95
2:00 | 0 | 0 | 0 | 180 | 300 | 86 | 0 | 418 | 281 |  | 0 | 225 | 0 | 33 | 0 | 55 | 0 | 0 | 97 | 32 | 24 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 20 | 33 | 30 | 41 | 0 | 36 | 65 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 51 | 33 | 12 | 6 | 15 | 38 | 0 | 0 | 0 | 320 | 310 | 212 | 63 | 136 | 35 | 55 | 0 | 51 | 0 | 40 | 0 | 21 | 10 | 33 | 20 | 158 | 98 | 0 | 22 | 0 | 43 | 30 | 0 | 10 | 0 | 0 | 61 | 65 | 0 | 220 | 0 | 11 | 9 | 295 | 8 | 0 | 25 | 143 | 55 | 92 | 47 | 50 | 72 | 0 | 21 | 170 | 137 | 402 | 49 | 105 | 17 | 0 | 268 | 36 | 55 | 0 | 9 | 20 | 400 | 0 | 0 | 162 | 107 | 0 | 35 | 0 | 74 | 55 | 0 | 0 | 0 |  | 893 | 0 | 170 | 0 | 16 | 210 | 0 | 0 | 16 | 63 | 0 | 152 | 28 | 64 | 0 | 0 | 0 | 32 | 40 | 45 | 0 | 34 | 16 | 8 | 33 | 22 | 0 | 11 | 79 | 0 | 240 | 0 | 0 | 151 | 0 | 0 | 205 | 0 | 20 | 152 | 0 | 333 | 0 | 25 | 94 | 105 | 98 | 0 | 0 | 95 | 600 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 |  | 7450 | 4085 | 11535 | 4264 | 893 | 1572 | 267 | 2568 | 919 | 101 | 415 | 583 | 158 | 0 | 336.3749 | 95.95
3:00 | 0 | 0 | 0 | 180 | 300 | 86 | 0 | 418 | 272 |  | 0 | 225 | 0 | 34 | 0 | 55 | 0 | 0 | 97 | 32 | 24 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 20 | 33 | 30 | 41 | 0 | 35 | 65 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 51 | 33 | 12 | 6 | 15 | 39 | 0 | 0 | 0 | 320 | 310 | 210 | 8 | 136 | 35 | 55 | 0 | 51 | 0 | 40 | 0 | 21 | 10 | 33 | 20 | 154 | 98 | 0 | 22 | 0 | 43 | 30 | 0 | 10 | 0 | 0 | 61 | 50 | 0 | 220 | 0 | 11 | 9 | 275 | 8 | 0 | 25 | 145 | 28 | 50 | 48 | 25 | 71 | 0 | 21 | 170 | 135 | 402 | 49 | 105 | 17 | 0 | 268 | 36 | 47 | 0 | 9 | 20 | 400 | 0 | 0 | 162 | 107 | 0 | 35 | 0 | 74 | 55 | 0 | 0 | 0 |  | 893 | 0 | 170 | 0 | 16 | 200 | 0 | 0 | 16 | 63 | 0 | 152 | 27 | 32 | 0 | 0 | 0 | 32 | 40 | 45 | 0 | 42 | 16 | 8 | 33 | 22 | 0 | 11 | 80 | 0 | 240 | 0 | 0 | 151 | 0 | 0 | 130 | 0 | 20 | 152 | 0 | 334 | 0 | 0 | 94 | 105 | 98 | 0 | 0 | 95 | 600 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 |  | 7244 | 3952 | 11196 | 4262 | 893 | 1474 | 148 | 2537 | 920 | 100 | 330 | 508 | 154 | 0 | 326.2376 | 95.95
4:00 | 0 | 0 | 0 | 180 | 300 | 86 | 0 | 418 | 277 |  | 0 | 225 | 0 | 34 | 0 | 55 | 0 | 0 | 97 | 32 | 24 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 8 | 0 | 30 | 41 | 0 | 35 | 65 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 17 | 17 | 33 | 12 | 6 | 15 | 39 | 0 | 0 | 0 | 320 | 310 | 209 | 8 | 136 | 35 | 54 | 0 | 51 | 0 | 40 | 0 | 21 | 10 | 33 | 20 | 152 | 98 | 0 | 22 | 0 | 43 | 30 | 0 | 10 | 0 | 0 | 61 | 25 | 0 | 220 | 0 | 11 | 9 | 280 | 8 | 0 | 0 | 95 | 0 | 0 | 48 | 0 | 72 | 0 | 21 | 170 | 135 | 401 | 49 | 105 | 17 | 0 | 251 | 36 | 55 | 0 | 9 | 20 | 399 | 15 | 0 | 162 | 107 | 0 | 35 | 0 | 74 | 55 | 0 | 0 | 0 |  | 894 | 0 | 170 | 0 | 16 | 200 | 0 | 0 | 16 | 58 | 0 | 152 | 22 | 32 | 0 | 0 | 0 | 32 | 40 | 45 | 0 | 34 | 16 | 8 | 33 | 22 | 0 | 11 | 81 | 0 | 240 | 0 | 0 | 150 | 0 | 0 | 130 | 0 | 10 | 153 | 0 | 335 | 0 | 0 | 94 | 105 | 98 | 0 | 0 | 95 | 580 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6964 | 3889 | 10853 | 4214 | 894 | 1454 | 10 | 2468 | 901 | 100 | 330 | 460 | 152 | 0 | 319.7865 | 95.95
5:00 | 0 | 0 | 0 | 180 | 300 | 86 | 0 | 418 | 293 |  | 0 | 225 | 0 | 33 | 0 | 55 | 0 | 0 | 96 | 14 | 8 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 20 | 0 | 33 | 41 | 0 | 35 | 65 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 17 | 33 | 12 | 6 | 15 | 41 | 0 | 0 | 0 | 320 | 310 | 202 | 8 | 136 | 35 | 54 | 0 | 51 | 0 | 40 | 0 | 21 | 10 | 33 | 20 | 146 | 98 | 0 | 22 | 0 | 43 | 30 | 0 | 10 | 0 | 0 | 61 | 20 | 0 | 220 | 0 | 11 | 9 | 290 | 8 | 0 | 0 | 80 | 0 | 0 | 48 | 0 | 71 | 0 | 21 | 170 | 128 | 402 | 49 | 105 | 17 | 0 | 251 | 36 | 55 | 0 | 9 | 20 | 400 | 0 | 0 | 162 | 107 | 0 | 35 | 0 | 65 | 55 | 0 | 0 | 0 |  | 893 | 0 | 175 | 0 | 16 | 200 | 0 | 0 | 16 | 20 | 0 | 152 | 22 | 32 | 0 | 0 | 0 | 32 | 40 | 45 | 0 | 34 | 16 | 8 | 33 | 22 | 0 | 11 | 80 | 0 | 240 | 0 | 0 | 151 | 0 | 0 | 130 | 0 | 0 | 155 | 0 | 338 | 0 | 0 | 94 | 105 | 99 | 0 | 0 | 70 | 580 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6917 | 3826 | 10743 | 4231 | 893 | 1480 | 0 | 2362 | 900 | 100 | 330 | 431 | 146 | 0 | 282.9235 | 95.95
6:00 | 0 | 0 | 0 | 180 | 300 | 89 | 0 | 418 | 293 |  | 0 | 225 | 0 | 33 | 0 | 55 | 0 | 0 | 97 | 8 | 8 | 16 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 25 | 20 | 0 | 33 | 32 | 0 | 35 | 65 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 17 | 33 | 11 | 6 | 15 | 42 | 0 | 0 | 0 | 315 | 310 | 206 | 8 | 137 | 35 | 54 | 0 | 51 | 0 | 32 | 0 | 21 | 10 | 33 | 20 | 128 | 98 | 0 | 22 | 0 | 43 | 30 | 0 | 10 | 0 | 0 | 61 | 20 | 0 | 212 | 0 | 11 | 9 | 260 | 8 | 0 | 0 | 45 | 0 | 0 | 48 | 0 | 86 | 1 | 21 | 149 | 128 | 363 | 49 | 105 | 17 | 0 | 170 | 36 | 55 | 0 | 9 | 20 | 360 | 0 | 1 | 108 | 107 | 0 | 35 | 0 | 43 | 55 | 0 | 0 | 0 |  | 893 | 0 | 175 | 0 | 16 | 170 | 0 | 0 | 0 | 0 | 8 | 152 | 22 | 32 | 0 | 0 | 0 | 32 | 0 | 45 | 0 | 34 | 16 | 8 | 33 | 22 | 0 | 11 | 80 | 0 | 240 | 0 | 0 | 151 | 0 | 0 | 130 | 0 | 0 | 156 | 0 | 335 | 0 | 0 | 50 | 105 | 99 | 0 | 0 | 35 | 540 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6548 | 3607 | 10155 | 4146 | 893 | 1451 | 0 | 2058 | 860 | 100 | 300 | 347 | 128 | 2 | 271.8646 | 95.95
7:00 | 0 | 0 | 0 | 180 | 300 | 90 | 0 | 408 | 291 |  | 0 | 225 | 0 | 34 | 0 | 40 | 0 | 0 | 95 | 8 | 8 | 16 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 25 | 20 | 28 | 33 | 41 | 0 | 35 | 65 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 17 | 33 | 12 | 6 | 15 | 42 | 0 | 0 | 0 | 310 | 305 | 209 | 8 | 136 | 35 | 55 | 0 | 51 | 0 | 32 | 0 | 21 | 10 | 33 | 20 | 124 | 96 | 0 | 22 | 0 | 43 | 30 | 0 | 10 | 0 | 0 | 61 | 20 | 0 | 199 | 0 | 11 | 9 | 270 | 8 | 0 | 0 | 45 | 0 | 0 | 48 | 0 | 147 | 6 | 21 | 73 | 80 | 365 | 49 | 105 | 17 | 1 | 135 | 36 | 55 | 0 | 9 | 20 | 360 | 0 | 8 | 54 | 107 | 0 | 35 | 2 | 35 | 55 | 0 | 0 | 0 |  | 893 | 0 | 175 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 8 | 152 | 21 | 32 | 0 | 0 | 0 | 32 | 0 | 44 | 0 | 34 | 16 | 8 | 33 | 22 | 0 | 11 | 80 | 0 | 240 | 0 | 0 | 150 | 0 | 0 | 130 | 0 | 0 | 156 | 0 | 340 | 0 | 0 | 35 | 105 | 99 | 0 | 1 | 35 | 510 | 0 | 0 | 17 | 1 | 10 | 0 | 0 | 0 | 0 |  | 6400 | 3526 | 9926 | 4140 | 893 | 1465 | 0 | 1879 | 830 | 100 | 250 | 346 | 124 | 29 | 188.0013 | 95.95
8:00 | 0 | 0 | 0 | 180 | 300 | 91 | 0 | 407 | 292 |  | 0 | 225 | 0 | 34 | 0 | 40 | 0 | 0 | 95 | 8 | 8 | 16 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 25 | 20 | 33 | 30 | 41 | 0 | 35 | 65 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 7 | 26 | 17 | 33 | 12 | 6 | 15 | 42 | 0 | 0 | 0 | 310 | 305 | 212 | 8 | 137 | 26 | 55 | 0 | 51 | 0 | 31 | 0 | 21 | 10 | 33 | 20 | 120 | 104 | 0 | 22 | 0 | 43 | 30 | 0 | 10 | 0 | 0 | 65 | 20 | 0 | 199 | 0 | 11 | 9 | 280 | 8 | 0 | 0 | 45 | 0 | 0 | 76 | 0 | 114 | 10 | 21 | 50 | 80 | 365 | 67 | 105 | 17 | 2 | 135 | 36 | 55 | 0 | 9 | 20 | 360 | 10 | 19 | 54 | 107 | 0 | 35 | 7 | 41 | 55 | 0 | 0 | 0 |  | 894 | 0 | 175 | 0 | 66 | 120 | 0 | 0 | 0 | 0 | 32 | 144 | 19 | 32 | 0 | 0 | 0 | 32 | 0 | 44 | 0 | 42 | 24 | 8 | 32 | 20 | 0 | 11 | 81 | 0 | 250 | 0 | 0 | 151 | 0 | 0 | 130 | 0 | 0 | 155 | 0 | 330 | 0 | 0 | 35 | 105 | 70 | 0 | 0 | 35 | 510 | 0 | 0 | 17 | 3 | 18 | 0 | 0 | 0 | 0 |  | 6437 | 3585 | 10022 | 4140 | 894 | 1463 | 0 | 1933 | 841 | 100 | 250 | 352 | 120 | 59 | #REF! | 95.95
9:00 | 0 | 0 | 0 | 180 | 300 | 88 | 0 | 407 | 291 |  | 0 | 225 | 0 | 32 | 0 | 40 | 0 | 0 | 96 | 0 | 8 | 27 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 25 | 12 | 33 | 31 | 41 | 0 | 36 | 65 | 108 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 0 | 0 | 33 | 7 | 6 | 15 | 40 | 0 | 0 | 0 | 310 | 305 | 210 | 8 | 137 | 26 | 56 | 0 | 51 | 0 | 31 | 0 | 21 | 10 | 28 | 20 | 122 | 102 | 0 | 22 | 1 | 43 | 30 | 0 | 0 | 0 | 0 | 61 | 10 | 0 | 200 | 0 | 0 | 9 | 270 | 8 | 0 | 0 | 45 | 0 | 0 | 76 | 0 | 70 | 12 | 10 | 51 | 80 | 365 | 68 | 105 | 27 | 4 | 135 | 36 | 58 | 0 | 9 | 70 | 370 | 32 | 33 | 54 | 107 | 0 | 35 | 14 | 39 | 55 | 0 | 0 | 0 |  | 894 | 0 | 175 | 0 | 66 | 120 | 0 | 0 | 0 | 0 | 32 | 151 | 19 | 16 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 42 | 24 | 8 | 33 | 19 | 0 | 11 | 80 | 0 | 250 | 0 | 0 | 152 | 0 | 0 | 130 | 0 | 0 | 155 | 0 | 368 | 2 | 0 | 35 | 70 | 49 | 0 | 2 | 35 | 510 | 0 | 0 | 0 | 3 | 29 | 0 | 0 | 0 | 0 |  | 6398 | 3512 | 9910 | 4138 | 894 | 1454 | 0 | 1866 | 840 | 101 | 250 | 277 | 122 | 98 | #REF! | 95.95
10:00 | 0 | 0 | 0 | 180 | 300 | 83 | 0 | 405 | 292 |  | 0 | 225 | 0 | 0 | 0 | 40 | 0 | 0 | 97 | 0 | 8 | 48 | 0 | 0 | 0 | 0 | 35 | 17 | 17 | 19 | 25 | 16 | 33 | 31 | 33 | 0 | 37 | 65 | 108 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 0 | 0 | 33 | 0 | 6 | 15 | 37 | 0 | 0 | 0 | 310 | 305 | 207 | 8 | 136 | 19 | 54 | 0 | 51 | 0 | 31 | 0 | 21 | 10 | 23 | 20 | 126 | 98 | 0 | 22 | 1 | 43 | 30 | 0 | 0 | 0 | 0 | 61 | 10 | 0 | 201 | 0 | 0 | 9 | 280 | 8 | 0 | 0 | 30 | 0 | 0 | 180 | 0 | 62 | 20 | 10 | 51 | 80 | 365 | 85 | 105 | 105 | 5 | 135 | 36 | 85 | 0 | 9 | 100 | 370 | 34 | 54 | 54 | 107 | 0 | 35 | 9 | 39 | 48 | 0 | 0 | 0 |  | 893 | 0 | 185 | 0 | 66 | 120 | 0 | 0 | 0 | 0 | 32 | 152 | 19 | 16 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 42 | 24 | 8 | 33 | 19 | 0 | 11 | 78 | 0 | 250 | 0 | 0 | 152 | 0 | 0 | 130 | 0 | 0 | 158 | 0 | 400 | 17 | 0 | 35 | 67 | 60 | 0 | 5 | 35 | 510 | 0 | 0 | 0 | 3 | 34 | 40 | 0 | 0 | 0 |  | 6539 | 3626 | 10165 | 4136 | 893 | 1487 | 0 | 2034 | 838 | 102 | 250 | 298 | 126 | 131 | #REF! | 95.95
11:00 | 0 | 0 | 0 | 180 | 300 | 85 | 0 | 398 | 332 |  | 0 | 225 | 0 | 0 | 0 | 40 | 0 | 0 | 95 | 0 | 8 | 48 | 0 | 0 | 0 | 0 | 35 | 17 | 17 | 19 | 25 | 19 | 33 | 31 | 33 | 0 | 38 | 65 | 105 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 0 | 0 | 33 | 0 | 6 | 15 | 40 | 0 | 0 | 0 | 345 | 330 | 202 | 8 | 136 | 26 | 53 | 0 | 51 | 0 | 0 | 0 | 21 | 10 | 25 | 20 | 128 | 100 | 0 | 22 | 2 | 30 | 30 | 0 | 0 | 0 | 0 | 57 | 10 | 0 | 222 | 0 | 0 | 7 | 300 | 8 | 0 | 0 | 30 | 0 | 0 | 180 | 0 | 50 | 7 | 14 | 51 | 80 | 400 | 106 | 105 | 68 | 5 | 135 | 36 | 68 | 0 | 9 | 100 | 376 | 34 | 44 | 60 | 107 | 0 | 35 | 35 | 39 | 48 | 0 | 0 | 0 |  | 893 | 0 | 200 | 0 | 66 | 120 | 0 | 0 | 0 | 0 | 32 | 150 | 19 | 16 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 42 | 0 | 8 | 0 | 19 | 0 | 11 | 79 | 0 | 250 | 0 | 0 | 152 | 0 | 0 | 130 | 0 | 0 | 164 | 0 | 414 | 17 | 0 | 35 | 67 | 70 | 0 | 6 | 35 | 510 | 0 | 0 | 0 | 3 | 35 | 90 | 0 | 0 | 0 |  | 6644 | 3649 | 10293 | 4257 | 893 | 1563 | 0 | 2059 | 839 | 103 | 250 | 194 | 128 | 137 | #REF! | 95.95
12:00 | 0 | 0 | 0 | 180 | 196 | 86 | 0 | 398 | 331 |  | 0 | 225 | 0 | 0 | 0 | 55 | 0 | 0 | 97 | 0 | 8 | 82 | 0 | 0 | 0 | 0 | 35 | 17 | 17 | 19 | 25 | 19 | 33 | 31 | 33 | 0 | 38 | 65 | 105 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 0 | 0 | 33 | 0 | 9 | 15 | 40 | 0 | 0 | 0 | 290 | 280 | 204 | 8 | 136 | 35 | 51 | 0 | 51 | 0 | 0 | 0 | 21 | 10 | 33 | 14 | 134 | 100 | 0 | 20 | 2 | 30 | 30 | 0 | 0 | 0 | 0 | 57 | 10 | 0 | 222 | 0 | 0 | 9 | 300 | 8 | 0 | 0 | 50 | 0 | 0 | 188 | 0 | 50 | 19 | 76 | 76 | 80 | 404 | 106 | 105 | 68 | 4 | 190 | 36 | 68 | 0 | 9 | 92 | 386 | 34 | 49 | 145 | 107 | 0 | 35 | 22 | 35 | 55 | 0 | 0 | 0 |  | 893 | 0 | 205 | 0 | 66 | 170 | 0 | 0 | 0 | 0 | 32 | 152 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 8 | 0 | 20 | 0 | 11 | 80 | 0 | 250 | 0 | 0 | 153 | 0 | 0 | 170 | 0 | 0 | 169 | 0 | 414 | 17 | 0 | 59 | 61 | 96 | 0 | 7 | 60 | 540 | 0 | 0 | 0 | 6 | 42 | 90 | 0 | 0 | 0 |  | 6773 | 3849 | 10622 | 4088 | 893 | 1565 | 0 | 2396 | 870 | 103 | 340 | 252 | 134 | 151 | #REF! | 95.95
13:00 | 0 | 0 | 0 | 180 | 196 | 89 | 0 | 397 | 322 |  | 0 | 225 | 0 | 0 | 0 | 55 | 0 | 0 | 188 | 0 | 16 | 110 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 19 | 25 | 19 | 33 | 31 | 33 | 0 | 38 | 65 | 105 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 0 | 0 | 33 | 0 | 32 | 15 | 40 | 0 | 0 | 0 | 280 | 270 | 207 | 8 | 136 | 38 | 51 | 0 | 51 | 0 | 0 | 0 | 21 | 10 | 33 | 20 | 146 | 100 | 0 | 20 | 3 | 10 | 30 | 0 | 0 | 0 | 0 | 58 | 10 | 0 | 222 | 0 | 0 | 9 | 300 | 8 | 0 | 0 | 105 | 0 | 0 | 187 | 0 | 50 | 20 | 76 | 132 | 92 | 403 | 106 | 105 | 68 | 5 | 230 | 36 | 68 | 0 | 9 | 90 | 392 | 35 | 8 | 162 | 107 | 0 | 35 | 35 | 37 | 55 | 0 | 0 | 0 |  | 893 | 0 | 205 | 0 | 65 | 155 | 0 | 0 | 0 | 0 | 32 | 150 | 23 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 8 | 0 | 20 | 0 | 11 | 80 | 0 | 250 | 0 | 0 | 152 | 0 | 0 | 130 | 0 | 0 | 176 | 0 | 414 | 35 | 0 | 70 | 67 | 97 | 0 | 8 | 70 | 540 | 0 | 0 | 16 | 4 | 18 | 90 | 0 | 0 | 0 |  | 7097 | 3845 | 10942 | 4160 | 893 | 1562 | 0 | 2712 | 870 | 103 | 285 | 240 | 146 | 101 | 0 | 95.95
14:00 | 0 | 0 | 0 | 180 | 195 | 89 | 0 | 397 | 330 |  | 0 | 225 | 0 | 0 | 0 | 55 | 0 | 0 | 152 | 0 | 16 | 124 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 19 | 25 | 8 | 33 | 31 | 33 | 0 | 38 | 65 | 105 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 0 | 0 | 33 | 0 | 41 | 15 | 40 | 0 | 0 | 0 | 280 | 270 | 207 | 8 | 136 | 37 | 52 | 0 | 51 | 0 | 0 | 0 | 21 | 10 | 25 | 20 | 136 | 101 | 0 | 22 | 1 | 8 | 30 | 0 | 0 | 0 | 0 | 59 | 10 | 0 | 221 | 0 | 0 | 9 | 280 | 8 | 0 | 0 | 148 | 0 | 0 | 189 | 0 | 50 | 18 | 90 | 200 | 100 | 404 | 106 | 105 | 68 | 5 | 230 | 36 | 68 | 0 | 9 | 90 | 391 | 35 | 56 | 162 | 107 | 0 | 35 | 18 | 51 | 55 | 0 | 0 | 0 |  | 893 | 0 | 210 | 0 | 65 | 120 | 0 | 0 | 0 | 0 | 32 | 152 | 21 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 8 | 0 | 20 | 0 | 11 | 80 | 0 | 250 | 0 | 0 | 152 | 0 | 0 | 130 | 0 | 0 | 176 | 0 | 380 | 35 | 0 | 70 | 67 | 96 | 0 | 7 | 70 | 550 | 0 | 0 | 17 | 2 | 50 | 90 | 0 | 0 | 0 |  | 7219 | 3820 | 11039 | 4111 | 893 | 1515 | 0 | 2870 | 880 | 103 | 250 | 254 | 136 | 157 | 0 | 95.95
15:00 | 0 | 0 | 0 | 180 | 200 | 89 | 0 | 397 | 333 |  | 0 | 225 | 0 | 0 | 0 | 55 | 0 | 0 | 121 | 0 | 16 | 124 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 19 | 25 | 20 | 22 | 31 | 33 | 0 | 38 | 65 | 105 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 0 | 0 | 33 | 0 | 44 | 15 | 40 | 0 | 0 | 0 | 290 | 275 | 204 | 8 | 136 | 36 | 51 | 0 | 51 | 0 | 0 | 0 | 21 | 10 | 25 | 20 | 120 | 100 | 0 | 22 | 1 | 30 | 30 | 0 | 0 | 0 | 0 | 60 | 10 | 0 | 222 | 0 | 0 | 10 | 280 | 8 | 0 | 0 | 145 | 0 | 0 | 190 | 0 | 50 | 15 | 60 | 200 | 100 | 405 | 85 | 105 | 34 | 2 | 230 | 36 | 68 | 0 | 9 | 90 | 390 | 35 | 4 | 162 | 107 | 0 | 35 | 26 | 51 | 35 | 0 | 0 | 0 |  | 893 | 0 | 210 | 0 | 65 | 120 | 0 | 0 | 0 | 0 | 32 | 148 | 26 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 8 | 0 | 21 | 0 | 11 | 79 | 0 | 250 | 0 | 0 | 153 | 0 | 0 | 130 | 0 | 0 | 169 | 0 | 380 | 35 | 0 | 70 | 71 | 96 | 0 | 5 | 70 | 560 | 0 | 0 | 17 | 5 | 40 | 89 | 0 | 0 | 0 |  | 7061 | 3819 | 10880 | 4110 | 893 | 1524 | 0 | 2769 | 889 | 103 | 250 | 254 | 120 | 98 | 0 | 95.95
16:00 | 0 | 0 | 0 | 180 | 20 | 96 | 0 | 399 | 322 |  | 0 | 225 | 0 | 0 | 0 | 55 | 0 | 0 | 150 | 0 | 16 | 124 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 19 | 25 | 26 | 33 | 31 | 33 | 0 | 36 | 65 | 105 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 0 | 0 | 33 | 0 | 44 | 15 | 40 | 0 | 0 | 0 | 280 | 305 | 205 | 8 | 137 | 36 | 50 | 0 | 51 | 0 | 0 | 0 | 21 | 10 | 33 | 20 | 124 | 102 | 0 | 22 | 1 | 30 | 30 | 0 | 0 | 0 | 0 | 61 | 10 | 0 | 221 | 0 | 0 | 10 | 310 | 8 | 0 | 0 | 145 | 0 | 0 | 191 | 0 | 50 | 10 | 60 | 155 | 100 | 402 | 65 | 105 | 34 | 1 | 230 | 36 | 68 | 0 | 9 | 90 | 401 | 35 | 5 | 162 | 107 | 0 | 35 | 9 | 51 | 35 | 0 | 0 | 0 |  | 893 | 0 | 220 | 0 | 65 | 120 | 0 | 0 | 0 | 0 | 32 | 152 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 8 | 0 | 20 | 0 | 11 | 80 | 0 | 250 | 0 | 0 | 153 | 0 | 0 | 130 | 0 | 0 | 163 | 0 | 380 | 53 | 0 | 70 | 67 | 96 | 0 | 4 | 70 | 560 | 0 | 0 | 17 | 3 | 34 | 89 | 0 | 0 | 0 |  | 6910 | 3822 | 10732 | 4026 | 893 | 1546 | 0 | 2711 | 890 | 101 | 250 | 254 | 124 | 67 | 0 | 95.95
17:00 | 0 | 0 | 0 | 180 | 20 | 97 | 0 | 397 | 322 |  | 0 | 225 | 0 | 0 | 0 | 55 | 0 | 0 | 120 | 0 | 16 | 124 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 19 | 25 | 26 | 33 | 31 | 41 | 0 | 65 | 65 | 105 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 0 | 0 | 33 | 0 | 44 | 15 | 40 | 0 | 0 | 0 | 280 | 300 | 207 | 8 | 136 | 38 | 51 | 0 | 51 | 0 | 0 | 0 | 21 | 10 | 33 | 18 | 124 | 102 | 0 | 22 | 0 | 5 | 30 | 5 | 5 | 0 | 0 | 60 | 10 | 0 | 221 | 0 | 0 | 10 | 280 | 8 | 0 | 0 | 145 | 0 | 0 | 193 | 0 | 50 | 4 | 60 | 155 | 100 | 400 | 48 | 105 | 17 | 0 | 230 | 36 | 51 | 0 | 9 | 90 | 400 | 37 | 3 | 108 | 107 | 0 | 35 | 10 | 51 | 55 | 0 | 0 | 0 |  | 886 | 0 | 230 | 0 | 65 | 120 | 0 | 0 | 0 | 0 | 8 | 150 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 8 | 0 | 20 | 0 | 11 | 80 | 0 | 250 | 0 | 0 | 153 | 0 | 0 | 130 | 0 | 0 | 183 | 0 | 380 | 17 | 0 | 35 | 67 | 104 | 0 | 3 | 35 | 530 | 0 | 0 | 17 | 1 | 15 | 89 | 0 | 0 | 0 |  | 6774 | 3631 | 10405 | 3989 | 886 | 1524 | 0 | 2482 | 860 | 130 | 250 | 254 | 124 | 36 | 0 | 95.95
18:00 | 0 | 0 | 0 | 180 | 20 | 52 | 0 | 396 | 322 |  | 0 | 225 | 0 | 1 | 0 | 55 | 0 | 0 | 121 | 2 | 16 | 124 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 0 | 25 | 19 | 33 | 33 | 41 | 0 | 81 | 65 | 105 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 2 | 0 | 33 | 3 | 35 | 15 | 40 | 0 | 0 | 0 | 280 | 305 | 207 | 8 | 136 | 38 | 50 | 0 | 51 | 0 | 0 | 0 | 21 | 10 | 0 | 20 | 124 | 112 | 0 | 22 | 0 | 20 | 30 | 5 | 5 | 0 | 0 | 64 | 10 | 0 | 221 | 0 | 5 | 10 | 275 | 8 | 0 | 0 | 145 | 0 | 0 | 200 | 0 | 50 | 1 | 30 | 100 | 100 | 352 | 48 | 105 | 17 | 0 | 190 | 36 | 43 | 0 | 9 | 60 | 360 | 53 | 1 | 108 | 107 | 0 | 35 | 2 | 51 | 17 | 0 | 0 | 0 |  | 886 | 0 | 235 | 0 | 65 | 120 | 0 | 0 | 9 | 30 | 8 | 149 | 21 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 8 | 0 | 21 | 0 | 11 | 78 | 0 | 250 | 0 | 0 | 153 | 0 | 0 | 130 | 0 | 0 | 189 | 0 | 340 | 17 | 0 | 35 | 67 | 104 | 0 | 2 | 35 | 490 | 57 | 0 | 17 | 0 | 1 | 90 | 0 | 0 | 8 |  | 6443 | 3650 | 10093 | 3890 | 886 | 1497 | 0 | 2302 | 826 | 146 | 250 | 295 | 124 | 7 | 0 | 95.95
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 20 | 96 | 0 | 396 | 337 |  | 0 | 240 | 0 | 22 | 0 | 55 | 0 | 0 | 195 | 18 | 50 | 125 | 0 | 0 | 0 | 0 | 54 | 35 | 50 | 19 | 25 | 19 | 33 | 33 | 41 | 0 | 81 | 65 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 25 | 51 | 33 | 17 | 0 | 15 | 31 | 0 | 0 | 0 | 280 | 300 | 207 | 8 | 136 | 38 | 50 | 0 | 51 | 0 | 3 | 0 | 21 | 10 | 20 | 20 | 136 | 130 | 0 | 22 | 0 | 43 | 30 | 5 | 5 | 0 | 0 | 64 | 81 | 0 | 221 | 0 | 5 | 9 | 295 | 8 | 0 | 70 | 215 | 156 | 90 | 200 | 100 | 68 | 0 | 90 | 140 | 100 | 400 | 87 | 105 | 42 | 0 | 282 | 36 | 58 | 0 | 50 | 68 | 400 | 55 | 0 | 150 | 107 | 0 | 35 | 0 | 56 | 0 | 0 | 0 | 0 |  | 885 | 0 | 240 | 0 | 66 | 130 | 0 | 0 | 40 | 55 | 32 | 150 | 26 | 32 | 0 | 0 | 0 | 8 | 5 | 82 | 0 | 50 | 16 | 8 | 34 | 22 | 0 | 11 | 79 | 0 | 251 | 0 | 0 | 153 | 0 | 0 | 135 | 0 | 0 | 195 | 0 | 414 | 20 | 0 | 38 | 82 | 104 | 0 | 0 | 80 | 500 | 57 | 0 | 17 | 0 | 0 | 90 | 0 | 0 | 0 |  | 7866 | 4107 | 11973 | 4144 | 885 | 1732 | 416 | 2975 | 830 | 146 | 265 | 579 | 136 | 0 | 0 | 95.95
19:30 | 0 | 0 | 0 | 180 | 90 | 96 | 0 | 395 | 337 |  | 0 | 240 | 0 | 50 | 0 | 55 | 0 | 0 | 191 | 50 | 50 | 125 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 19 | 33 | 33 | 41 | 0 | 81 | 65 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 51 | 33 | 20 | 0 | 15 | 42 | 0 | 0 | 0 | 280 | 305 | 210 | 8 | 136 | 34 | 53 | 0 | 51 | 0 | 28 | 0 | 21 | 10 | 33 | 20 | 136 | 150 | 0 | 22 | 0 | 43 | 30 | 5 | 5 | 0 | 0 | 65 | 81 | 0 | 221 | 0 | 5 | 9 | 275 | 8 | 0 | 70 | 245 | 137 | 97 | 200 | 96 | 149 | 0 | 90 | 200 | 100 | 401 | 88 | 105 | 105 | 0 | 285 | 36 | 110 | 0 | 112 | 100 | 400 | 55 | 0 | 162 | 107 | 0 | 35 | 0 | 100 | 55 | 0 | 0 | 0 |  | 885 | 0 | 245 | 0 | 65 | 150 | 0 | 0 | 50 | 65 | 32 | 150 | 26 | 48 | 0 | 0 | 0 | 8 | 5 | 82 | 0 | 50 | 16 | 8 | 34 | 22 | 0 | 11 | 79 | 0 | 250 | 0 | 0 | 152 | 0 | 0 | 170 | 0 | 20 | 201 | 0 | 414 | 53 | 0 | 70 | 105 | 104 | 0 | 0 | 95 | 580 | 57 | 0 | 35 | 0 | 0 | 91 | 0 | 0 | 0 |  | 8557 | 4428 | 12985 | 4258 | 885 | 1726 | 420 | 3695 | 909 | 146 | 320 | 660 | 136 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 180 | 150 | 96 | 0 | 395 | 337 |  | 0 | 240 | 0 | 50 | 0 | 55 | 0 | 0 | 191 | 50 | 50 | 125 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 19 | 33 | 33 | 41 | 0 | 82 | 65 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 51 | 33 | 48 | 0 | 15 | 42 | 0 | 0 | 0 | 330 | 300 | 210 | 8 | 136 | 33 | 53 | 0 | 51 | 0 | 40 | 0 | 21 | 10 | 33 | 20 | 134 | 150 | 0 | 22 | 0 | 43 | 30 | 5 | 5 | 0 | 0 | 64 | 81 | 0 | 221 | 0 | 5 | 9 | 280 | 8 | 0 | 10 | 275 | 24 | 60 | 200 | 60 | 149 | 0 | 90 | 200 | 100 | 401 | 87 | 105 | 105 | 0 | 300 | 36 | 103 | 0 | 112 | 100 | 400 | 55 | 0 | 162 | 107 | 0 | 35 | 0 | 84 | 46 | 0 | 0 | 0 |  | 883 | 0 | 250 | 0 | 66 | 150 | 0 | 0 | 44 | 70 | 32 | 152 | 27 | 48 | 0 | 0 | 0 | 8 | 17 | 82 | 0 | 50 | 16 | 8 | 34 | 22 | 0 | 11 | 80 | 0 | 250 | 0 | 0 | 152 | 0 | 0 | 130 | 0 | 20 | 200 | 0 | 420 | 53 | 0 | 80 | 105 | 105 | 0 | 0 | 95 | 600 | 57 | 0 | 35 | 0 | 0 | 90 | 0 | 0 | 0 |  | 8470 | 4442 | 12912 | 4367 | 883 | 1738 | 174 | 3746 | 930 | 147 | 280 | 643 | 134 | 0 | 0 | 95.95
21:00 | 0 | 0 | 0 | 180 | 280 | 96 | 0 | 395 | 337 |  | 0 | 240 | 0 | 50 | 0 | 55 | 0 | 0 | 190 | 49 | 50 | 125 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 19 | 33 | 33 | 41 | 0 | 82 | 65 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 51 | 33 | 85 | 0 | 15 | 42 | 0 | 0 | 0 | 330 | 300 | 211 | 8 | 136 | 34 | 56 | 0 | 51 | 0 | 40 | 0 | 22 | 10 | 33 | 20 | 136 | 151 | 0 | 22 | 0 | 43 | 30 | 5 | 5 | 0 | 0 | 65 | 81 | 0 | 221 | 0 | 5 | 9 | 290 | 8 | 0 | 0 | 276 | 20 | 25 | 191 | 25 | 149 | 0 | 90 | 200 | 100 | 400 | 87 | 105 | 105 | 0 | 300 | 36 | 110 | 0 | 113 | 100 | 400 | 55 | 0 | 162 | 107 | 0 | 35 | 0 | 93 | 55 | 0 | 0 | 0 |  | 884 | 0 | 260 | 0 | 66 | 150 | 0 | 0 | 40 | 52 | 32 | 144 | 27 | 48 | 0 | 0 | 0 | 16 | 29 | 81 | 0 | 50 | 24 | 8 | 33 | 22 | 0 | 11 | 79 | 0 | 250 | 0 | 0 | 159 | 0 | 0 | 130 | 0 | 0 | 203 | 0 | 423 | 53 | 0 | 94 | 105 | 103 | 0 | 0 | 95 | 610 | 57 | 0 | 35 | 0 | 0 | 90 | 0 | 0 | 0 |  | 8588 | 4463 | 13051 | 4512 | 884 | 1754 | 70 | 3812 | 939 | 147 | 280 | 647 | 136 | 0 | 54 | 95.95
22:00 | 0 | 0 | 0 | 180 | 300 | 96 | 0 | 398 | 337 |  | 0 | 225 | 0 | 50 | 0 | 55 | 0 | 0 | 152 | 49 | 24 | 125 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 19 | 33 | 33 | 41 | 0 | 82 | 65 | 105 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 51 | 33 | 61 | 0 | 15 | 42 | 0 | 0 | 0 | 350 | 320 | 208 | 8 | 137 | 34 | 56 | 0 | 51 | 0 | 40 | 0 | 22 | 10 | 33 | 20 | 136 | 151 | 0 | 22 | 0 | 43 | 30 | 5 | 5 | 0 | 0 | 64 | 81 | 0 | 221 | 0 | 5 | 9 | 295 | 8 | 0 | 0 | 275 | 0 | 0 | 192 | 0 | 149 | 0 | 90 | 200 | 100 | 402 | 88 | 105 | 105 | 0 | 300 | 36 | 110 | 0 | 113 | 100 | 400 | 55 | 0 | 162 | 107 | 0 | 35 | 0 | 97 | 55 | 0 | 0 | 0 |  | 883 | 0 | 265 | 0 | 66 | 120 | 0 | 0 | 38 | 47 | 32 | 152 | 28 | 48 | 0 | 0 | 0 | 16 | 29 | 81 | 0 | 50 | 24 | 8 | 33 | 22 | 0 | 11 | 80 | 0 | 250 | 0 | 0 | 188 | 0 | 0 | 130 | 0 | 0 | 206 | 0 | 380 | 53 | 0 | 94 | 105 | 106 | 0 | 0 | 95 | 622 | 57 | 0 | 35 | 0 | 0 | 91 | 0 | 0 | 0 |  | 8482 | 4445 | 12927 | 4576 | 883 | 1702 | 0 | 3771 | 952 | 147 | 250 | 640 | 136 | 0 | 67 | 95.95
23:00 | 0 | 0 | 0 | 180 | 300 | 96 | 0 | 408 | 332 |  | 0 | 225 | 0 | 50 | 0 | 55 | 0 | 0 | 153 | 49 | 32 | 125 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 19 | 33 | 33 | 41 | 0 | 84 | 65 | 105 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 51 | 33 | 52 | 6 | 15 | 42 | 0 | 0 | 0 | 365 | 330 | 208 | 8 | 136 | 34 | 56 | 0 | 51 | 0 | 37 | 0 | 22 | 10 | 33 | 20 | 136 | 155 | 0 | 22 | 0 | 43 | 30 | 5 | 5 | 0 | 0 | 59 | 81 | 0 | 220 | 0 | 5 | 9 | 320 | 8 | 0 | 60 | 283 | 150 | 96 | 173 | 80 | 149 | 0 | 90 | 200 | 100 | 403 | 70 | 105 | 105 | 0 | 52 | 36 | 110 | 0 | 52 | 100 | 397 | 55 | 0 | 162 | 107 | 0 | 35 | 0 | 96 | 55 | 0 | 0 | 0 |  | 884 | 0 | 270 | 0 | 16 | 170 | 0 | 0 | 39 | 47 | 8 | 152 | 30 | 48 | 0 | 0 | 0 | 24 | 40 | 81 | 0 | 50 | 24 | 8 | 33 | 22 | 0 | 11 | 74 | 0 | 250 | 0 | 0 | 188 | 0 | 0 | 164 | 0 | 0 | 205 | 0 | 414 | 53 | 0 | 94 | 105 | 105 | 0 | 0 | 95 | 622 | 45 | 0 | 35 | 0 | 0 | 91 | 0 | 0 | 0 |  | 8584 | 4497 | 13081 | 4611 | 884 | 1746 | 386 | 3362 | 946 | 149 | 334 | 691 | 136 | 0 | 63.5887 | 95.95
24:00 | 0 | 0 | 0 | 180 | 300 | 93 | 0 | 408 | 332 |  | 0 | 225 | 0 | 11 | 0 | 55 | 0 | 0 | 195 | 14 | 50 | 48 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 19 | 33 | 33 | 41 | 0 | 84 | 65 | 105 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 51 | 33 | 17 | 6 | 15 | 42 | 0 | 0 | 0 | 335 | 310 | 209 | 8 | 136 | 34 | 55 | 0 | 51 | 0 | 39 | 0 | 22 | 10 | 33 | 20 | 134 | 156 | 0 | 22 | 0 | 43 | 30 | 5 | 5 | 0 | 0 | 61 | 81 | 0 | 220 | 0 | 5 | 9 | 295 | 8 | 0 | 100 | 281 | 180 | 98 | 48 | 96 | 54 | 0 | 21 | 200 | 113 | 402 | 49 | 105 | 29 | 0 | 52 | 36 | 55 | 0 | 31 | 62 | 400 | 17 | 0 | 162 | 107 | 0 | 35 | 0 | 78 | 55 | 0 | 0 | 0 |  | 883 | 0 | 270 | 0 | 16 | 227 | 0 | 0 | 28 | 47 | 8 | 152 | 29 | 48 | 0 | 0 | 0 | 24 | 38 | 81 | 0 | 50 | 16 | 8 | 33 | 22 | 0 | 11 | 68 | 0 | 250 | 0 | 0 | 183 | 0 | 0 | 216 | 0 | 10 | 204 | 0 | 420 | 17 | 60 | 94 | 105 | 56 | 0 | 0 | 95 | 622 | 0 | 0 | 35 | 0 | 0 | 72 | 0 | 0 | 0 |  | 7928 | 4498 | 12426 | 4603 | 883 | 1677 | 544 | 2622 | 940 | 149 | 443 | 647 | 134 | 0 | 252.5115 | 95.95
KWH | 0 | 0 | 0 | 4347000 | 5534455 | 2070000 | 0 | 9867260 | 7524000 |  | 0 | 5259000 | 0 | 547200 | 0 | 1265389 | 0 | 0 | 3287000 | 402240 | 494496 | 1720320 | 0 | 0 | 0 | 0 | 1068840 | 1098613 | 1115495 | 418284 | 600000 | 405180 | 685800 | 760000 | 931680 | 0 | 1194333 | 1572000 | 2600000 | 0 | 603495 | 0 | 0 | 0 | 0 |  | 293280 | 345288 | 547734 | 785640 | 392640 | 336480 | 364080 | 1025280 | 0 | 0 | 0 | 7742800 | 7401000 | 5033000 | 334545 | 3251940 | 797184 | 1282560 | 0 | 1224719 | 0 | 551728 | 0 | 508356 | 226080 | 696700 | 482250 | 3214080 | 2597760 | 0 | 475704 | 13350 | 844000 | 674840 | 45600 | 141336 | 0 | 0 | 1474464 | 947520 | 0 | 5207310 | 0 | 169800 | 211140 | 7025500 | 188112 | 0 | 285888 | 3472580 | 777968 | 578276 | 3122400 | 406977 | 1994256 | 138645 | 1123200 | 3501120 | 2636218 | 9423000 | 1699200 | 2541600 | 1205199 | 34080 | 5211382 | 915241 | 1702829 | 0 | 641760 | 1577280 | 9305100 | 697920 | 278450 | 3299040 | 2581855 | 0 | 885960 | 189859 | 1454400 | 1195560 | 0 | 0 | 0 |  | 21528000 | 0 | 5090688 | 0 | 1107840 | 3772800 | 0 | 0 | 303840 | 578560 | 448500 | 3623671 | 567602 | 776064 | 0 | 0 | 0 | 431120 | 323153 | 795080 | 0 | 904432 | 285448 | 190560 | 515531 | 491280 | 0 | 262746 | 1886836 | 0 | 5989600 | 0 | 0 | 3984591 | 0 | 0 | 3750918 | 0 | 132480 | 4396245 | 0 | 9010981 | 503520 | 111194 | 1715328 | 2161728 | 2215065 | 0 | 53252 | 1663488 | 14510300 | 333082 | 0 | 513600 | 36660 | 337680 | 1257024 | 0 | 0 | 3990 |  | 175103123 | 96564477 | 271667600 | 102556600 | 21528000 | 37663945 | 2292783 | 64251637 | 22390726 | 2766333 | 7523718 | 6397802 | 3214080 | 1081976 | 0
Fuel Cost | 0 | 0 | 0 | 6477030 | 6198589.6 | 2753100 | 0 | 10360623 | 8125920 |  | 0 | 5732310 | 0 | 6117696 | 0 | 16766404.25 | 0 | 0 | 5752250 | 5880748.8 | 6957558.72 | 27886387.2 | 0 | 0 | 0 | 0 | 13595644.8 | 14831275.5 | 14958787.95 | 313713 | 450000 | 0 | 0 | 0 | 15847876.8 | 0 | 322469.91 | 424440 | 4914000 | 0 | 9867143.25 | 0 | 0 | 0 | 0 |  | 3827304 | 5759403.84 | 9322432.68 | 10613996.4 | 4978675.2 | 3893073.6 | 462381.6 | 3414182.4 | 0 | 0 | 0 | 8594508 | 8067090 | 5838280 | 431563.05 | 3967366.8 | 900817.92 | 1911014.4 | 0 | 2045280.73 | 0 | 9528342.56 | 0 | 696447.72 | 169560 | 1219225 | 361687.5 | 23077094.4 | 2831558.4 | 0 | 646957.44 | 212799 | 1156280 | 890788.8 | 79344 | 244511.28 | 0 | 0 | 2860460.16 | 2160345.6 | 0 | 5259383.1 | 0 | 253002 | 418057.2 | 7025500 | 141084 | 0 | 5992212.48 | 47400717 | 16306209.28 | 11952964.92 | 42089952 | 8412214.59 | 27620445.6 | 1620760.05 | 11591424 | 47825299.2 | 34982612.86 | 8669160 | 20662272 | 36751536 | 15245767.35 | 0 | 61181624.68 | 9966974.49 | 18101072.27 | 0 | 8272286.4 | 18580358.4 | 8560692 | 9038064 | 4023602.5 | 41864817.6 | 29381509.9 | 0 | 11570637.6 | 2268815.05 | 21772368 | 15745525.2 | 0 | 0 | 0 |  | 64584000 | 0 | 5701570.56 | 0 | 11532614.4 | 62251200 | 0 | 0 | 5472158.4 | 10414080 | 6444945 | 4058511.52 | 1101147.88 | 8459097.6 | 0 | 0 | 0 | 7229882.4 | 5651945.97 | 12435051.2 | 0 | 14977393.92 | 4826925.68 | 2597332.8 | 8697007.97 | 1016949.6 | 0 | 198898.722 | 10962517.16 | 0 | 31684984 | 0 | 0 | 4622125.56 | 0 | 0 | 65491028.28 | 0 | 2779430.4 | 5099644.2 | 0 | 8920871.19 | 6767308.8 | 2331738.18 | 20292330.24 | 31236969.6 | 28131325.5 | 0 | 588434.6 | 20194744.32 | 130737803 | 339743.64 | 0 | 3800640 | 414624.6 | 3960986.4 | 19270177.92 | 0 | 0 | 0 |  | 915245662.98 | 635278141.212 | 1550523804.192 | 115440684.602 | 64584000 | 45972842.97 | 47774769.85 | 831486329.92 | 173385304.16 | 746909.91 | 127742228.28 | 107223617.9 | 23077094.4 | 13090022.2 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 196 | 86 | 0 | 398 | 331 |  | 0 | 225 | 0 | 0 | 0 | 55 | 0 | 0 | 97 | 0 | 8 | 82 | 0 | 0 | 0 | 0 | 35 | 17 | 17 | 19 | 25 | 19 | 33 | 31 | 33 | 0 | 38 | 65 | 105 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 0 | 0 | 33 | 0 | 9 | 15 | 40 | 0 | 0 | 0 | 290 | 280 | 204 | 8 | 136 | 35 | 51 | 0 | 51 | 0 | 0 | 0 | 21 | 10 | 33 | 14 | 134 | 100 | 0 | 20 | 2 | 30 | 30 | 0 | 0 | 0 | 0 | 57 | 10 | 0 | 222 | 0 | 0 | 9 | 300 | 8 | 0 | 0 | 50 | 0 | 0 | 188 | 0 | 50 | 19 | 76 | 76 | 80 | 404 | 106 | 105 | 68 | 4 | 190 | 36 | 68 | 0 | 9 | 92 | 386 | 34 | 49 | 145 | 107 | 0 | 35 | 22 | 35 | 55 | 0 | 0 | 0 |  | 893 | 0 | 205 | 0 | 66 | 170 | 0 | 0 | 0 | 0 | 32 | 152 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 8 | 0 | 20 | 0 | 11 | 80 | 0 | 250 | 0 | 0 | 153 | 0 | 0 | 170 | 0 | 0 | 169 | 0 | 414 | 17 | 0 | 59 | 61 | 96 | 0 | 7 | 60 | 540 | 0 | 0 | 0 | 6 | 42 | 90 | 0 | 0 | 0 |  | 10622 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 280 | 96 | 0 | 395 | 337 | 0 | 0 | 240 | 0 | 50 | 0 | 55 | 0 | 0 | 190 | 49 | 50 | 125 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 19 | 33 | 33 | 41 | 0 | 82 | 65 | 110 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 12 | 26 | 51 | 33 | 85 | 0 | 15 | 42 | 0 | 0 | 0 | 330 | 300 | 211 | 8 | 136 | 34 | 56 | 0 | 51 | 0 | 40 | 0 | 22 | 10 | 33 | 20 | 136 | 151 | 0 | 22 | 0 | 43 | 30 | 5 | 5 | 0 | 0 | 65 | 81 | 0 | 221 | 0 | 5 | 9 | 290 | 8 | 0 | 0 | 276 | 20 | 25 | 191 | 25 | 149 | 0 | 90 | 200 | 100 | 400 | 87 | 105 | 105 | 0 | 300 | 36 | 110 | 0 | 113 | 100 | 400 | 55 | 0 | 162 | 107 | 0 | 35 | 0 | 93 | 55 | 0 | 0 | 0 |  | 884 | 0 | 260 | 0 | 66 | 150 | 0 | 0 | 40 | 52 | 32 | 144 | 27 | 48 | 0 | 0 | 0 | 16 | 29 | 81 | 0 | 50 | 24 | 8 | 33 | 22 | 0 | 11 | 79 | 0 | 250 | 0 | 0 | 159 | 0 | 0 | 130 | 0 | 0 | 203 | 0 | 423 | 53 | 0 | 94 | 105 | 103 | 0 | 0 | 95 | 610 | 57 | 0 | 35 | 0 | 0 | 90 | 0 | 0 | 0 |  | 13051 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 300 | 92 | 0 | 412 | 330 | 0 | 0 | 450 | 0 | 50 | 0 | 30 | 0 | 0 | 100 | 50 | 50 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 20 | 33 | 33 | 41 | 0 | 80 | 65 | 105 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 12 | 26 | 51 | 33 | 95 | 42 | 15 | 30 | 0 | 0 | 0 | 330 | 320 | 210 | 8 | 0 | 35 | 55 | 0 | 51 | 0 | 40 | 0 | 22 | 10 | 33 | 21 | 166 | 100 | 0 | 22 | 0 | 43 | 30 | 5 | 5 | 0 | 0 | 64 | 80 | 0 | 220 | 0 | 0 | 9 | 300 | 0 | 0 | 200 | 285 | 300 | 96 | 180 | 100 | 149 | 0 | 90 | 200 | 143 | 400 | 79 | 105 | 105 | 0 | 210 | 36 | 110 | 0 | 57 | 100 | 400 | 55 | 0 | 162 | 107 | 0 | 35 |  | 100 | 55 |  |  |  |  | 901 | 0 | 180 | 0 | 66 | 225 | 0 | 0 | 36 | 70 | 32 | 151 | 27 | 64 | 0 | 0 | 0 | 32 | 40 | 80 | 0 | 50 | 40 | 8 | 33 | 22 | 0 | 11 | 83 | 0 | 250 | 0 | 0 | 150 | 0 | 0 | 220 | 0 | 90 | 150 | 0 | 380 | 52 | 175 | 94 | 105 | 90 | 0 | 0 | 95 | 620 | 0 |  | 110 |  |  | 90
Forecast for Day | 0 | 0 | 0 | 180 | 300 | 92 | 0 | 412 | 330 | 0 | 0 | 450 | 0 | 8 | 0 | 30 | 0 | 0 | 100 | 8 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 19 | 25 | 20 | 33 | 33 | 41 | 0 | 80 | 65 | 105 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 12 | 26 | 17 | 33 | 12 | 6 | 15 | 10 | 0 | 0 | 0 | 325 | 310 | 205 | 8 | 0 | 35 | 55 | 0 | 51 | 0 | 40 | 0 | 22 | 10 | 33 | 20 | 143 | 130 | 0 | 22 | 1.6 | 43 | 30 | 5 | 5 | 0 | 0 | 62 | 10 | 0 | 220 | 0 | 0 | 9 | 300 | 0 | 0 | 200 | 95 | 100 | 60 | 80 | 50 | 35 | 20 | 21 | 200 | 140 | 400 | 68 | 88 | 17 | 5 | 123 | 36 | 55 | 0 | 9 | 20 | 400 | 17 | 50 | 35 | 107 | 0 | 35 | 30 | 96 | 55 |  |  |  |  | 901 | 0 | 210 | 0 | 16 | 225 | 0 | 0 | 0 | 47 | 32 | 151 | 19 | 32 | 0 | 0 | 0 | 32 | 0 | 50 | 0 | 42 | 16 | 8 | 33 | 21 | 0 | 11 | 70 | 0 | 250 | 0 | 0 | 170 | 0 | 0 | 220 | 0 | 90 | 160 | 0 | 400 | 17 | 100 | 50 | 90 | 55 | 0 | 8 | 55 | 620 | 0 |  | 50 | 6 | 100 | 17
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 300 | 92 | 0 | 408 | 328 | 0 | 0 | 420 | 0 | 8 | 0 | 30 | 0 | 0 | 156 | 8 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 16 | 25 | 19 | 33 | 33 | 41 | 0 | 80 | 65 | 105 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 12 | 26 | 17 | 33 | 12 | 6 | 15 | 18 | 0 | 0 | 0 | 345 | 320 | 208 | 8 | 0 | 37 | 55 | 0 | 51 | 0 | 40 | 0 | 22 | 8 | 0 | 20 | 132 | 156 | 0 | 22 | 0 | 43 | 30 | 5 | 5 | 0 | 0 | 61 | 10 | 0 | 220 | 0 | 6 | 9 | 300 | 8 | 0 | 0 | 95 | 0 | 0 | 76 | 0 | 35 | 2 | 21 | 155 | 58 | 402 | 69 | 88 | 17 | 2 | 120 | 36 | 55 | 0 | 9 | 20 | 400 | 17 | 20 | 35 | 107 | 0 | 35 | 8 | 96 | 55 | 0 | 0 | 0 | 0 | 884 | 0 | 255 | 0 | 16 | 221 | 0 | 0 | 0 | 36 | 0 | 151 | 19 | 16 | 0 | 0 | 0 | 24 | 0 | 39 | 0 | 8 | 0 | 8 | 33 | 22 | 0 | 11 | 71 | 0 | 250 | 0 | 0 | 184 | 0 | 0 | 168 | 0 | 0 | 193 | 0 | 414 | 0 | 0 | 50 | 89 | 55 | 0 | 2 | 55 | 622 | 0 | 0 | 0 | 3 | 48 | 34 | 0 | 0 | 0 | 0 |  |  |  |  | 80465940 |  | 0
80465940
| Minimum Generation |  | 9910 | 9:00
| Highest Generation |  | 13081 | 23:00
| Day Peak Generation |  | 10622 | 12:00
| Evening Peak Generation |  | 13051 | 21:00
| HVDC Max Flow |  | 894 | 4:00
| HVDC EvPeak Flow |  | 884 | 21:00
| Load factor L.F |  | 86.53% | [161 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2022-08-16
Till now the maximum generation is : - |  |  | 14782 | 21:00 | Hrs on | 2022-04-16
The Summary of Yesterday's |  | 2022-08-15 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 10622 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 10559 | MW
Evening Peak Generation : |  | 13051 | MW Hour : | 21:00 | Available Max Generation : |  | 13950 | MW
E.P. Demand (at gen end) : |  | 13110 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 14200 | MW
Maximum Generation : |  | 13081 | MW Hour : | 23:00 | Reserve(Generation end) |  | - | MW
Total Gen. (MKWH) : |  | 271.6676 | System Load Factor : | 86.53% | Load Shed : |  | 230 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | 46 | MW at | 19:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2022-08-16
Actual : | 95.95 | Ft.(MSL) , | Rule curve : | 93.8 | Ft.( MSL )
Gas Consumed : | Total = | 1079.53 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 161413527.572
: |  | Coal : | 173385304.16 | Oil : | 1114226945.95 | Total : | 1449025777.682
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4547.5118 |  |  | 0 | 2.532%
Chittagong Area | 0 | 0:00 | 1287.6983 |  |  | 25 | 4.778%
Khulna Area | 0 | 0:00 | 1699.9188 |  |  | 45 | 5.187%
Rajshahi Area | 0 | 0:00 | 1508.8579 |  |  | 48 | 5.762%
Cumilla Area | 0 | 0:00 | 1283.7724 |  |  | 37 | 5.428%
Mymensingh Area | 54 | 1296:00 | 1061.3042 |  |  | 36 | 5.976%
Sylhet Area | 0 | 0:00 | 473.7264 |  |  | 11 | 4.799%
Barisal Area | 0 | 0:00 | 386.0478 |  |  | 0 | 1.291%
Rangpur Area | 0 | 0:00 | 837.5274 |  |  | 28 | 5.92%
Total | 54 |  | 13086.365 |  |  | 230
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-2 |  | 10) Payra unit-2
2) Ghorasal-3,4
3) Ashuganj-5
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
7) Sikalbaha 225 MW
8) Shajibazar 330 MW
9) Siddhirganj 335 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Munshiganj 132/33 kV T-2 transformer was under shut down from 11:40 to 13:40 for R/H maintenance at 33 kV CB terminal.
b) Ghorashal unit-7 tripped at 11:48 and GT was synchronized at 19:43 and ST was synchronized at 19:43.
c) Siddhirganj Peaking GT-2 synchronized at 12:17.
d) Rampal 400/230 kV transformer was charged at 16:04 from 230 kV side.
e) Rampal 400/230 kV transformer was given power to 400 kV Bus at 16:07.
f) Rampal unit-1 synchronized on test at 17:58 and tripped at 18:02.
g) Bhola Nutan Biddut GT-1 was synchronized at 17:10.
h) Rohonpur-Adani Power 400 kV Ckt-2 was charged from Rohanpur at 17:50.
i) Adani Power-Rohanpur 400 kV Ckt-2 was switched on at 18:33.
j) Meghnaghat 450 MW GT-1 was synchronized at 18:55 and was shut down at 21:20 due to valve gland leakage
at boiler and again synchronized at 03:04(16/8/2022)
k) Amnura S/S-Amnura P/S 132 kV Ckt was switched on at 16:21.
l) Comilla(S)-Chowddagram 132 kV Ckt 1 & 2 tripped at 01:04(16/8/2022) from Comilla(S) end showing O/C relay | [5 empty] | About 516 MW power interruption occurred under
and was switched on at 01:16. | [5 empty] | Chowddogram,Feni,PHP,Baroierhat,Chowmuhoni,Ramganj
m) Kachua-Chandpur 132 kV Ckt 1 & 2 tripped at 01:04(16/8/2022) from Kachua end showing O/C relay and was | [5 empty] | & Chandpur S/S areas from 01:04(16/8/2022) to 01:30.
switched on at 01:30.
n) Hathazari-Baroierhat 132 kV Ckt 1 & 2 tripped at 01:04(16/8/2022) from Hathazari end showing O/C,E/F relay and
was switched on at 01:35.
o) Chandpur DESH-Ramganj 132 kV Ckt 1 & 2 tripped at 01:04(16/8/2022) showing O/C relay and were switched
on at 01:38.
p) Chandpur DESH P/S-Chandpur S/S 132 kV Ckt 1 & 2 tripped at 01:04(16/8/2022) showing O/C relay and were
switched on at 01:30.
q) Comilla(N) 132/33 kV T-3 & T-4 transformers tripped at 04:28(16/8/2022) showing O/C relay due to 33 kV Ekbaria | [5 empty] | About 55 MW power interruption occurred under
PBS feeder fault and were switched on at 04:44 & 04:42 respectively. | [5 empty] | Comilla(N) S/S area from 04:28(16/8/2022) to 04:44.
r) Kabirpur-Kodda 132 kV Ckt-2 was shut down at 05:49(16/8/2022) for C/M.
s) Khulna(S)-Rampal 230 kV Ckt-1 was shut down at 07:20(16/8/2022) for C/M.
t) Khulna(S) 230 kV Bus-1 was shut down at 07:20(16/8/2022) for C/M.
| Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2022-08-15 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4347000
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 280 | 5534455
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 96 | 2070000 | Engine problem
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 395 | 9867260
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 337 | 7524000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 240 | 5259000 | Gas shortage & GT-2 S/D.
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 50 | 547200 | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 0 | 0 | Under maint.
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 55 | 1265389
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 418284
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 190 | 3287000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 49 | 402240 | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 50 | 494496 | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1068840
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 125 | 1720320 | Engine problem
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 1098613
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 1115495
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 44 | 1005180 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 685800
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 760000
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 41 | 931680 | #REF!
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 276 | 3472580 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 20 | 777968 | Low demand.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 25 | 578276 | Low demand.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 25 | 406977 | Low demand.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 1994256
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 2541600
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 55 | 697920 | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 3299040
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 189859
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 55 | 1195560
| Dhaka area Total |  |  |  | 5847 | 3253 | 64556288
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 110 | 2600000 | Machine problem
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 25 | 603495
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 138645
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 336480 | Engine problem
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 147 | 2766333 | Low water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | HGPI for 30 days.
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 105 | 1205199
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 26 | 345288 | Fuel shortage
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 547734 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 33 | 785640 | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 90 | 1123200 | Engine problem
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 15 | 364080 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 42 | 1025280
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 85 | 392640 | Engine problem
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 34080
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 300 | 5211382
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 36 | 915241 | Engine problem
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 110 | 1702829
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 1577280 | Engine problem
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 107 | 2581855 | Engine problem
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Chattogram area Total |  |  |  | 2382 | 1382 | 24256681
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 211 | 5033000 | #REF!
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 330 | 7742800
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 300 | 7401000 | FGMO
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+136*1 | 284 | 0 | 0 | On test.
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 34 | 797184
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 56 | 1282560
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 334545 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1224719
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 100 | 2636218 | Engine problem
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 40 | 551728 | Engine problem
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 136 | 3251940 | Machine problem
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 200 | 3501120
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 508356
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 10 | 226080
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 136 | 3214080
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 696700
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 0 | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 20 | 482250
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 285888 | Reserve.
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Fuel shortage
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 113 | 641760
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 35 | 885960 | 33 kV feeder problem.
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 93 | 1454400 | Engine problem
| Cumilla Area Total |  |  |  | 3169 | 1928 | 42152288
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 151 | 2597760 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 475704
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 13350
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 191 | 3122400 | Engine problem
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 87 | 1699200 | Engine problem
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 278450
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 293280 | Engine problem
| Mymensingh Area Total |  |  |  | 614 | 463 | 8480144
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 844000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 674840 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Gas shortage
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 5 | 45600 | Gas shortage
| Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 5 | 141336 | Gas shortage
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 0 | 0 | Engine problem
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 65 | 1474464
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 947520
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 221 | 5207310
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50MW PP (EPL) |  | NENP | 27*2 | 50 | 5 | 169800 | Gas shortage
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 8 | 188112 | Gas shortage
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 7025500 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 400 | 9423000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 9 | 211140
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 400 | 9305100
| Sylhet Area Total |  |  |  | 2477 | 1562 | 35657722
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 884 | 21528000
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 66 | 1107840 | Fuel shortage
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 40 | 303840 | Engine problem
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 150 | 3772800
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 52 | 578560 | Engine problem
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 260 | 5090688 | Gas shortage.
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 32 | 448500 | Engine problem
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 132480 | Reserve.
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 53 | 503520 | Fuel shortage
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 105 | 2161728
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 337680
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 0 | 0 | 0 | On test.
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 0 | 0 | 0 | 3990
| Khulna Area Total |  |  |  | 2384 | 1642 | 35969626
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 48 | 776064 | Line O/L
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 27 | 567602 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 144 | 3623671 | ST under S/D
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 610 | 14510300 | Unit-2 S/D
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 57 | 333082 | ST Under maint.
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 35 | 513600 | Line O/L
| Barisal Area Total |  |  |  | 1958 | 921 | 20324319
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 16 | 431120 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 29 | 323153 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contract Expired
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 50 | 904432
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 24 | 285448 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 159 | 3984591 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 130 | 3750918
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 203 | 4396245 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 423 | 9010981
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 33 | 515531 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 491280
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | .
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 262746
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 8 | 190560 | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 81 | 795080 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 111194 | Reserve.
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 94 | 1715328 | Engine problem
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 95 | 1663488 | Engine problem
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 36660
| Rajshahi Area Total |  |  |  | 2129 | 1378 | 28868755
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 79 | 1886836
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 250 | 5989600 | Machine problem
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 103 | 2215065 | Engine problem
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 53252
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 90 | 1257024 | Fuel shortage
| Rangpur Area Total |  |  |  | 720 | 522 | 11401777
| Total |  |  |  | 21680 | 13051 | 271667600
| Eastern Grid Total |  |  |  | 14489 | 8588 | 175103123
| Western Grid Total |  |  |  | 7191 | 4463 | 96564477
| National Grid Total |  |  |  | 21680 | 13051 | 271667600
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2022-08-15
(a) ENTIRE EASTERN GRID : |  | 8380 | MW | (b) ENTIRE WESTERN GRID : |  | 4151.22 | MW
i) Dhaka area |  | 4208.5 | MW | i) Khulna area |  | 1513.6 | MW
ii) Chittagong area |  | 1276.5 | MW | ii) Rajshahi area |  | 1359.8 | MW
iii) Comilla area |  | 1225 | MW | iii) Barisal area |  | 368.82 | MW
iv) Mymensingh area |  | 1117 | MW | iv) Rangpur area |  | 909 | MW
v) Sylhet area |  | 553 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 12531.22 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
AKS | 0 | 00:00 | Chowmuhani | 202 | 20:00 | Kaptai | 4.5 | 20:00 | Nawabganj | 36.9 | 19:00 | Siddhirganj | 108 | 22:00
AKSML | 66 | 23:00 | Chuadanga | 97 | 19:30 | Kazla | 81 | 14:00 | Netrakona | 96 | 19:00 | Sirajganj | 88 | 07:00
Aftabnagar | 30 | 19:00 | Coxsbazar | 118 | 19:00 | Keranigonj | 52 | 21:00 | New | 81 | 09:00 | Sonargaon | 80 | 12:00
Agargaon | 74 | 19:00 | Cumilla(N) | 170 | 22:00 | Khagrachori | 28 | 19:00 | Niamatpur | 64 | 06:00 | Sreemongol | 44 | 12:00
Agrabad | 66 | 19:30 | Cumilla(S) | 168 | 00:00 | Khulna | 92 | 19:30 | Noapara | 47 | 01:00 | Srinagar | 46.28 | 21:00
Amnura | 58 | 21:00 | Daudkandi | 140 | 23:00 | Khulshi | 162 | 23:00 | PHP | 11 | 10:00 | Sunamganj | 38 | 22:00
Ashuganj | 47 | 23:00 | Dhaka | 18 | 11:00 | Kishoreganj | 150 | 21:00 | Pabna | 89 | 00:00 | Sylhet | 136 | 00:00
BSRM | 161 | 01:00 | Dhamrai | 92 | 00:00 | Kodda | 245 | 00:00 | Palashbari | 108 | 23:00 | TK | 28.5 | 19:00
Bagerhat | 98 | 19:30 | Dhanmondi | 98 | 19:00 | Kulaura | 44 | 00:00 | Panchagarh | 46 | 08:00 | Tangail | 195 | 22:00
Bakulia | 111 | 21:00 | Dohazari | 88 | 19:00 | Kurigram | 68 | 20:00 | Patuakhali | 133 | 22:00 | Thakurgaon | 66 | 22:00
Banani | 41 | 19:00 | Faridpur | 148 | 21:00 | Kushtia | 118 | 01:00 | Payra | 1.02 | 16:00 | Tongi | 116 | 19:30
Bangabhaban | 6 | 11:00 | Fatullah | 66 | 00:00 | Lalbag | 62 | 01:00 | Purbachal | 20 | 21:00 | Ullon | 40 | 21:00
Barapukuria | 52 | 23:00 | Fenchuganj | 48 | 19:00 | Lalmonirhat | 52 | 19:30 | Purbasadipur | 96 | 05:00 | Uttara | 93 | 21:00
Barguna | 18 | 22:00 | Feni | 110 | 19:30 | Madanganj | 90 | 21:00 | Rahim | 26 | 08:00 | UttaraNew | 18 | 00:00
Barishal | 105 | 23:00 | GPH | 91 | 20:00 | Madaripur | 98 | 21:00 | Rajbari | 60 | 19:30 | Zigatola | 57 | 19:00
Barishal-230 | 62 | 21:00 | Ghorashal | 71 | 22:00 | Madartek | 82 | 23:00 | Rajendrapur | 92 | 05:00
Baroaulia | 59 | 23:00 | Goalpara | 25 | 13:00 | Madunaghat | 58 | 19:30 | Rajshahi | 132 | 22:00
Baroirhat | 54 | 21:00 | Gollamari | 62 | 13:00 | Magura | 60 | 19:30 | Rajshahi-230 | 26 | 02:00
Bashundhara | 140 | 14:00 | Gopalganj | 96 | 19:30 | Mahasthangarh | 72 | 23:00 | Ramganj | 88 | 19:00
BashundharaCement | 7 | 14:00 | Gulshan | 92 | 19:00 | Manikganj | 89 | 21:00 | Rampur | 16 | 00:00
Beanibazar | 67 | 20:00 | Halishahar | 80 | 09:00 | Maniknagar | 57 | 13:00 | Rangamati | 14 | 19:00
Benapole | 48 | 19:30 | HaripurSBU | 149 | 00:00 | Matarbari | 43 | 21:00 | Rangpur | 105 | 08:00
Bhaluka | 108 | 20:00 | Hasnabad | 90 | 22:00 | Matuail | 58 | 00:00 | Ruppur | 5 | 09:00
Bhandaria | 46 | 22:00 | Hathazari | 94 | 21:00 | Millgate | 43 | 00:00 | SSM | 3 | 05:00
Bhangura | 30 | 19:30 | Ishurdi | 60 | 19:30 | Mirpur | 112 | 19:00 | Saidpur | 93 | 08:00
Bheramara(GK) | 55 | 21:00 | Jaldhaka | 72 | 19:00 | Mirsorai | N/A | N/A | Satkhira | 95 | 06:00
Bhulta | 221 | 01:00 | Jamalpur | 157 | 20:00 | Mithapukur | 32 | 19:00 | Satmasjid | 101 | 19:00
Bog-Sherpur | 56 | 19:30 | Jashore | 120 | 20:00 | Modern | 0 | 00:00 | Savar | 156 | 09:00
Bogura | 163 | 19:30 | Jhenaidah | 110 | 19:00 | Mogbazar | 98 | 13:00 | Shahjadpur | 85 | 22:00
Borhanuddin | 40 | 22:00 | Joydebpur | 144 | 04:00 | Mongla | 26 | 01:00 | Shahjibazar | 95 | 00:00
Brahmanbaria | 170 | 21:00 | Joypurhat | 57 | 22:00 | Motijheel | 26 | 19:00 | Shahmirpur | 46.5 | 18:30
Cantonment | 136 | 19:30 | Juldah | 26 | 18:30 | Munshiganj | 104 | 23:00 | Shariatpur | 78 | 22:00
Chandpur | 65 | 23:00 | KSRM | 29.56 | 01:00 | Mymensingh | 238 | 19:00 | Sherpur | 100 | 19:00
Chandraghona | 30 | 19:00 | Kabirpur | 203 | 01:00 | Naogaon | 118 | 19:30 | Shikalbaha | 28 | 19:00
Chapai | 67 | 21:00 | Kachua | 73 | 21:00 | Narail | 43 | 20:00 | Shikalbaha-230 | N/A | N/A
Charsaidpur | 35 | 01:00 | Kallyanpur | 96 | 23:00 | Narinda | 51 | 13:00 | Shitalakhya | 114 | 12:00
Chauddagram | 43 | 00:00 | Kalurghat | 4 | 00:00 | Narshingdi | 181 | 23:00 | Sholosohor | N/A | N/A
Chhatak | 33 | 19:00 | Kamrangirchar | 52 | 13:00 | Natore | 124 | 20:00 | Shyampur | 144 | 01:00
Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
(1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2022-08-15 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Bhulta | 387 | 20:00 | 373 | 11:00 | Kaliakoir | 387 | 06:00 | 379 | 11:00
| Bibiana | 405 | 08:00 | 396 | 01:00 | Payra | 420 | 08:00 | 408 | 12:00
| BIPTC | 403 | 05:00 | 397 | 20:00 | Rahanpur_I | 372 | 18:00 | 363 | 22:00
| Gopalganj_I | 414 | 18:30 | 403 | 22:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 223 | 19:30 | 214 | 11:00 | Hasnabad | 222 | 05:00 | 214 | 22:00
| AKSML | 235 | 20:00 | 217 | 00:00 | Hathazari | 236 | 21:00 | 220 | 22:00
| Aminbazar | 224 | 00:00 | 217 | 11:00 | Ishurdi | 235 | 18:30 | 228 | 22:00
| Ashuganj | 237 | 00:00 | 230 | 10:00 | Jhenaidah | 229 | 18:00 | 220 | 23:00
| Baghabari | 233 | 04:00 | 228 | 20:00 | Kaliakoir | 224 | 19:00 | 218 | 10:00
| Barapukuria | 223 | 17:00 | 213 | 00:00 | Keranigonj | 222 | 00:00 | 213 | 11:00
| Barishal | 246 | 08:00 | 234 | 23:00 | Khulna(S) | 238 | 05:00 | 229 | 23:00
| Bheramara | 232 | 18:30 | 225 | 22:00 | Maniknagar | 224 | 19:30 | 217 | 11:00
| Bhulta | 227 | 20:00 | 220 | 11:00 | Meghnaghat | 230 | 00:00 | 222 | 07:00
| Bibiana | 235 | 08:00 | 228 | 11:00 | Mirsorai | N/A | N/A | N/A | N/A
| BIPTC | 234 | 18:30 | 225 | 21:00 | Rajshahi | 234 | 18:30 | 224 | 11:00
| Bogura | 228 | 18:30 | 219 | 21:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 247 | 07:00 | 240 | 23:00 | Rampura | 225 | 04:00 | 218 | 10:00
| BSRM | 231 | 19:00 | 222 | 01:00 | Shikalbaha | 236 | 21:00 | 228 | 03:00
| Cumilla(N) | 226 | 05:00 | 220 | 11:00 | Shyampur | 223 | 00:00 | 214 | 11:00
| Fenchuganj | 236 | 07:00 | 230 | 18:30 | Siddhirganj | 225 | 00:00 | 219 | 11:00
| Ghorashal | N/A | N/A | N/A | N/A | Sirajgonj | 232 | 18:30 | 228 | 11:00
| GPH | 234 | 21:00 | 225 | 00:00 | Tongi | 230 | 19:00 | 220 | 10:00
| Haripur | 223 | 19:00 | 216 | 11:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 137 | 03:00 | 130 | 11:00 | Lalbag | 139 | 01:00 | 132 | 11:00
| Agargaon | 138 | 00:00 | 132 | 11:00 | Lalmonirhat | 130 | 18:00 | 116 | 00:00
| Agrabad | 137 | 14:00 | 127 | 23:00 | Madanganj | 132 | 19:00 | 126 | 11:00
| AKS | 136 | 14:00 | 126 | 23:00 | Madaripur | 140 | 08:00 | 133 | 23:00
| Aminbazar | 135 | 00:00 | 130 | 09:00 | Madartek | 137 | 00:00 | 131 | 11:00
| Amnura | 133 | 18:30 | 123 | 12:00 | Madunaghat | 138 | 14:00 | 130 | 23:00
| Ashuganj | 136 | 06:00 | 134 | 22:00 | Magura | 139 | 08:00 | 131 | 22:00
| Bagerhat | 136 | 16:00 | 126 | 23:00 | Mahasthangarh | 135 | 18:00 | 126 | 00:00
| Bakulia | 138 | 14:00 | 131 | 01:00 | Manikganj | 133 | 07:00 | 127 | 00:00
| Banani | 136 | 19:30 | 130 | 11:00 | Maniknagar | 134 | 06:00 | 129 | 11:00
| Bangabhaban | 134 | 07:00 | 129 | 11:00 | Matarbari | 127 | 09:00 | 115 | 23:00
| Barapukuria | 137 | 18:00 | 127 | 00:00 | Matuail | 131.5 | 19:00 | 126.6 | 12:00
| Barguna | 139 | 00:00 | 130 | 18:30 | Millgate | 137 | 19:00 | 130 | 11:00
| Barishal | 140 | 00:00 | 130 | 11:00 | Mirpur | 134 | 00:00 | 128 | 11:00
| Barishal-230 | 140 | 06:00 | 133 | 23:00 | Mithapukur | 134 | 18:00 | 122 | 00:00
| Baroaulia | 140 | 21:00 | 130 | 23:00 | Modern | 138 | 18:30 | 130 | 23:00
| Baroirhat | 130 | 14:00 | 124 | 00:00 | Mogbazar | 138 | 04:00 | 132 | 13:00
| Bashundhara | 136 | 19:30 | 129 | 11:00 | Mongla | 135 | 13:00 | 128 | 22:00
| BashundharaCement | 132 | 19:00 | 126 | 11:00 | Motijheel | 134 | 07:00 | 129 | 11:00
| Beanibazar | 129 | 06:00 | 124 | 22:00 | Munshiganj | 132 | 19:30 | 127 | 15:00
| Benapole | 136 | 18:00 | 128 | 23:00 | Mymensingh | 129 | 18:00 | 114 | 22:00
| Bhaluka | 129 | 18:00 | 113 | 22:00 | Naogaon | 133 | 18:00 | 123 | 22:00
| Bhandaria | 140 | 07:00 | 128 | 23:00 | Narail | 137 | 05:00 | 129 | 22:00
| Bhangura | 138 | 06:00 | 133 | 21:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bheramara | 137 | 18:30 | 133 | 22:00 | Narshingdi | 127 | 19:00 | 121 | 15:00
| Bheramara(GK) | 138 | 17:00 | 135 | 00:00 | Natore | 135 | 18:30 | 129 | 01:00
| Bhulta | 123 | 00:00 | 119 | 10:00 | Nawabganj | 139 | 00:00 | 131 | 11:00
| Bog-Sherpur | 135 | 18:00 | 128 | 22:00 | Netrakona | 128 | 17:00 | 112 | 22:00
| Bogura | 136 | 18:00 | 129 | 21:00 | New | 137 | 19:30 | 129 | 11:00
| Bogura-230 | 137 | 18:00 | 130 | 22:00 | Niamatpur | 133 | 18:00 | 118 | 22:00
| Brahmanbaria | 132 | 18:00 | 128 | 22:00 | Noapara | 136 | 08:00 | 130 | 23:00
| Cantonment | 137 | 00:00 | 131 | 11:00 | Pabna | 135 | 06:00 | 130 | 22:00
| Chandpur | 136 | 19:30 | 131 | 00:00 | Palashbari | 129 | 14:00 | 121 | 00:00
| Chandraghona | 138 | 14:00 | 132 | 01:00 | Panchagarh | 131 | 18:00 | 109 | 00:00
| Chapai | 134 | 18:30 | 124 | 12:00 | Patuakhali | 138 | 07:00 | 132 | 19:00
| Charsaidpur | 134 | 19:30 | 127 | 11:00 | Payra | 138 | 02:00 | 136 | 11:00
| Chauddagram | 131 | 20:00 | 125 | 00:00 | PHP | 130 | 14:00 | 123 | 01:00
| Chhatak | 130 | 07:00 | 123 | 22:00 | Postogola | 142 | 19:30 | 134 | 11:00
| Chowmuhani | 129 | 20:00 | 120 | 00:00 | Purbachal | 136 | 19:30 | 129 | 11:00
| Chuadanga | 136 | 18:00 | 127 | 22:00 | Purbasadipur | 134 | 17:00 | 113 | 00:00
| Coxsbazar | 127 | 08:00 | 114 | 23:00 | Rahim | 132 | 19:00 | 127 | 12:00
| Cumilla(N) | 132 | 19:00 | 128 | 11:00 | Rajbari | 136 | 08:00 | 131 | 22:00
| Cumilla(S) | 132 | 18:30 | 127 | 11:00 | Rajendrapur | 140 | 18:30 | 126 | 01:00
| Daudkandi | 132 | 19:30 | 124 | 11:00 | Rajshahi | 133 | 18:30 | 128 | 00:00
| Dhaka | 137 | 00:00 | 131 | 12:00 | Rajshahi-230 | 133 | 18:30 | 124 | 10:00
| Dhamrai | 131 | 18:30 | 126 | 11:00 | Ramganj | 131 | 14:00 | 124 | 23:00
| Dhanmondi | 132 | 19:30 | 126 | 11:00 | Rampur | 137 | 20:00 | 128 | 23:00
| Dohazari | 135 | 08:00 | 127 | 00:00 | Rampura | 137 | 03:00 | 131 | 10:00
| Faridpur | 136 | 18:30 | 131 | 22:00 | Rangamati | 137 | 14:00 | 131 | 01:00
| Fatullah | 135 | 00:00 | 128 | 11:00 | Rangpur | 131 | 18:30 | 116 | 01:00
| Fenchuganj | 134 | 06:00 | 130 | 15:00 | Ruppur | 136 | 05:00 | 133 | 23:00
| Feni | 130 | 08:00 | 125 | 00:00 | Saidpur | 134 | 17:00 | 125 | 03:00
| Ghorashal | 138 | 01:00 | 136 | 10:00 | Satkhira | 134 | 17:00 | 126 | 22:00
| Goalpara | 137 | 08:00 | 132 | 23:00 | Satmasjid | 137 | 00:00 | 132 | 11:00
| Gollamari | 136 | 18:00 | 130 | 23:00 | Savar | 135 | 00:00 | 128 | 10:00
| Gopalganj | 140 | 08:00 | 135 | 23:00 | Shahjadpur | 140 | 18:00 | 135 | 21:00
| Gopalganj_I | 141 | 05:00 | 135 | 22:00 | Shahjibazar | 134 | 18:30 | 130 | 05:00
| Gulshan | 137 | 06:00 | 130 | 11:00 | Shahmirpur | 139 | 19:30 | 129 | 23:00
| Halishahar | 138 | 20:00 | 131 | 01:00 | Shariatpur | 139 | 08:00 | 130 | 23:00
| Haripur | 132 | 19:00 | 127 | 12:00 | Sherpur | 131 | 18:30 | 114 | 08:00
| HaripurSBU | 133 | 19:30 | 127 | 10:00 | Shikalbaha | 140 | 21:00 | 130 | 00:00
| Hasnabad | 141 | 19:00 | 136 | 09:00 | Shikalbaha-230 | 139 | 19:30 | 132 | 01:00
| Hathazari | 137 | 09:00 | 130 | 22:00 | Shitalakhya | 141 | 19:30 | 132 | 11:00
| Ishurdi | 137 | 18:00 | 133 | 00:00 | Sholosohor | N/A | N/A | N/A | N/A
| Jaldhaka | 131 | 18:00 | 117 | 00:00 | Shyampur | 135 | 20:00 | 126 | 11:00
| Jamalpur | 134 | 18:30 | 119 | 09:00 | Shyampur-230 | 135 | 19:30 | 128 | 11:00
| Jashore | 136 | 18:00 | 129 | 22:00 | Siddhirganj | 132 | 19:00 | 127 | 10:00
| Jhenaidah | 140 | 18:00 | 133 | 22:00 | Sirajganj | 136 | 18:00 | 133 | 23:00
| Jhenaidah-230 | 140 | 18:00 | 134 | 22:00 | Sonargaon | 131 | 00:00 | 124 | 13:00
| Joydebpur | 142 | 14:00 | 138 | 01:00 | Sreemongol | 135 | 01:00 | 130 | 12:00
| Joypurhat | 135 | 18:00 | 121 | 22:00 | Srinagar | 138 | 19:00 | 132 | 11:00
| Juldah | 139 | 20:00 | 130 | 00:00 | SSM | 141 | 21:00 | 134 | 18:30
| Kabirpur | 135 | 06:00 | 129 | 00:00 | Sunamganj | 127 | 18:00 | 120 | 22:00
| Kachua | 133 | 19:00 | 127 | 23:00 | Sylhet | 131 | 17:00 | 127 | 11:00
| Kaliakoir | 135 | 06:00 | 128 | 11:00 | Tangail | 132 | 17:00 | 123 | 22:00
| Kallyanpur | 136 | 00:00 | 129 | 11:00 | Thakurgaon | 132 | 17:00 | 107 | 00:00
| Kamrangirchar | 139 | 00:00 | 131 | 11:00 | Tongi | 136 | 19:30 | 133 | 00:00
| Kaptai | 135 | 00:00 | 135 | 00:00 | Ullon | 137 | 04:00 | 131 | 11:00
| Kazla | 133 | 03:00 | 129 | 11:00 | Uttara | 134 | 19:00 | 129 | 10:00
| Keranigonj | 138 | 00:00 | 131 | 11:00 | UttaraNew | 135 | 00:00 | 128 | 11:00
| Khagrachori | 137 | 21:00 | 131 | 00:00 | Zigatola | 139 | 20:00 | 132 | 11:00
| Khulna | 136 | 08:00 | 132 | 22:00
| Khulna(S) | 136 | 18:00 | 131 | 23:00
| Khulshi | 136 | 14:00 | 130 | 00:00
| Kishoreganj | 131 | 06:00 | 120 | 22:00
| Kodda | 142 | 19:00 | 128 | 00:00
| KSRM | 138 | 19:30 | 130 | 23:00
| Kulaura | 132 | 07:00 | 130 | 01:00
| Kurigram | 129 | 17:00 | 117 | 21:00
| Kushtia | 137 | 06:00 | 132 | 22:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2022-08-15
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 354 | 7928 | 4498 | 12426 |  |  |  | QF-LDC-11
0:30 | 390 | 7779 | 4302.5 | 12081.5 | Date: | 2022-08-15
1:00 | 426 | 7630 | 4107 | 11737
1:30 | 442 | 7540 | 4096 | 11636
2:00 | 458 | 7450 | 4085 | 11535
2:30 | 447 | 7347 | 4018.5 | 11365.5 | [5 empty] | Gen. at Eve. Peak | 13051 | 13051 MW (21:00 )
3:00 | 436 | 7244 | 3952 | 11196 | [6 empty] | 21:00
3:30 | 454 | 7104 | 3920.5 | 11024.5 | [5 empty] | Gen. at Day Peak | 10622 | 10622 MW (12:00 )
4:00 | 472 | 6964 | 3889 | 10853 | [6 empty] | 12:00
4:30 | 476 | 6940.5 | 3857.5 | 10798 | [5 empty] | Highest Generation | 13081
5:00 | 480 | 6917 | 3826 | 10743 | [6 empty] | 23:00
5:30 | 478 | 6732.5 | 3716.5 | 10449
6:00 | 476 | 6548 | 3607 | 10155
6:30 | 442 | 6474 | 3566.5 | 10040.5
7:00 | 408 | 6400 | 3526 | 9926
7:30 | 408 | 6418.5 | 3555.5 | 9974
8:00 | 408 | 6437 | 3585 | 10022
8:30 | 414 | 6417.5 | 3548.5 | 9966
9:00 | 420 | 6398 | 3512 | 9910
9:30 | 498 | 6468.5 | 3569 | 10037.5
10:00 | 576 | 6539 | 3626 | 10165
10:30 | 546 | 6591.5 | 3637.5 | 10229
11:00 | 516 | 6644 | 3649 | 10293
11:30 | 543 | 6708.5 | 3749 | 10457.5
12:00 | 570 | 6773 | 3849 | 10622
12:30 | 521 | 6935 | 3847 | 10782
13:00 | 472 | 7097 | 3845 | 10942
13:30 | 488 | 7158 | 3832.5 | 10990.5
14:00 | 504 | 7219 | 3820 | 11039
14:30 | 505 | 7140 | 3819.5 | 10959.5
15:00 | 506 | 7061 | 3819 | 10880
15:30 | 548 | 6985.5 | 3820.5 | 10806
16:00 | 590 | 6910 | 3822 | 10732
16:30 | 582 | 6842 | 3726.5 | 10568.5
17:00 | 574 | 6774 | 3631 | 10405
17:30 | 588 | 6608.5 | 3640.5 | 10249
18:00 | 602 | 6443 | 3650 | 10093
18:30 | 324 | 7154.5 | 3878.5 | 11033
19:00 | 46 | 7866 | 4107 | 11973
19:30 | 78 | 8557 | 4428 | 12985
20:00 | 100 | 8470 | 4442 | 12912 |  |  |  | Executive Engineer
20:30 | 88 | 8529 | 4452.5 | 12981.5 |  |  |  | Network Operation Division
21:00 | 76 | 8588 | 4463 | 13051
21:30 | 83 | 8535 | 4454 | 12989
22:00 | 90 | 8482 | 4445 | 12927 |  |  |  |  | Page 6 of 7
22:30 | 148 | 8533 | 4471 | 13004
23:00 | 206 | 8584 | 4497 | 13081
23:30 | 280 | 8256 | 4497.5 | 12753.5
24:00 | 354 | 7928 | 4498 | 12426
13051 MW (21:00 )
10622 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2022-08-15 |  | Energy |  | 271667600
[13 empty] | 2022-08-15 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 4603 | 883 | 1677 | 544 | 2622 | 940 | 149 | 443 | 647 | 134 | 0 | 252.5115
0:30 | 4431.5 | 888 | 1629.5 | 461 | 2623.5 | 930.5 | 126 | 440 | 622 | 147 | 0 | 316.561 | Date: | 2022-08-15
1:00 | 4260 | 893 | 1582 | 378 | 2625 | 921 | 103 | 437 | 597 | 160 | 0 | 380.6105
1:30 | 4262 | 893 | 1577 | 322.5 | 2596.5 | 920 | 102 | 426 | 590 | 159 | 0 | 358.4927 | [8 empty] | Total Energy | 271.6676 | Total Energy Gen 271.668 MKWHr Energy Not Served 15.560 MKWHr Energy Requirement 287.227 MKWHr
2:00 | 4264 | 893 | 1572 | 267 | 2568 | 919 | 101 | 415 | 583 | 158 | 0 | 336.3749 | [8 empty] | Energy not Served | 15.5596
2:30 | 4263 | 893 | 1523 | 207.5 | 2552.5 | 919.5 | 100.5 | 372.5 | 545.5 | 156 | 0 | 331.3062 | [8 empty] | Energy Requirement | 287.2272
3:00 | 4262 | 893 | 1474 | 148 | 2537 | 920 | 100 | 330 | 508 | 154 | 0 | 326.2376
3:30 | 4238 | 893.5 | 1464 | 79 | 2502.5 | 910.5 | 100 | 330 | 484 | 153 | 0 | 323.012 | [6 empty] | Shortage
4:00 | 4214 | 894 | 1454 | 10 | 2468 | 901 | 100 | 330 | 460 | 152 | 0 | 319.7865
4:30 | 4222.5 | 893.5 | 1467 | 5 | 2415 | 900.5 | 100 | 330 | 445.5 | 149 | 0 | 301.355
5:00 | 4231 | 893 | 1480 | 0 | 2362 | 900 | 100 | 330 | 431 | 146 | 0 | 282.9235
5:30 | 4188.5 | 893 | 1465.5 | 0 | 2210 | 880 | 100 | 315 | 389 | 137 | 1 | 277.3941
6:00 | 4146 | 893 | 1451 | 0 | 2058 | 860 | 100 | 300 | 347 | 128 | 2 | 271.8646
6:30 | 4143 | 893 | 1458 | 0 | 1968.5 | 845 | 100 | 275 | 346.5 | 126 | 15.5 | 229.933 |  |  |  |  | Coal
7:00 | 4140 | 893 | 1465 | 0 | 1879 | 830 | 100 | 250 | 346 | 124 | 29 | 188.0013
7:30 | 4140 | 893.5 | 1464 | 0 | 1906 | 835.5 | 100 | 250 | 349 | 122 | 44 | 273.0007 |  |  |  | Oil |  |  |  | ,
8:00 | 4140 | 894 | 1463 | 0 | 1933 | 841 | 100 | 250 | 352 | 120 | 59 | 358
8:30 | 4139 | 894 | 1458.5 | 0 | 1899.5 | 840.5 | 100.5 | 250 | 314.5 | 121 | 78.5 | 518.5
9:00 | 4138 | 894 | 1454 | 0 | 1866 | 840 | 101 | 250 | 277 | 122 | 98 | 679
9:30 | 4137 | 893.5 | 1470.5 | 0 | 1950 | 839 | 101.5 | 250 | 287.5 | 124 | 114.5 | 827.5
10:00 | 4136 | 893 | 1487 | 0 | 2034 | 838 | 102 | 250 | 298 | 126 | 131 | 976
10:30 | 4196.5 | 893 | 1525 | 0 | 2046.5 | 838.5 | 102.5 | 250 | 246 | 127 | 134 | 1172.5
11:00 | 4257 | 893 | 1563 | 0 | 2059 | 839 | 103 | 250 | 194 | 128 | 137 | 1369
11:30 | 4172.5 | 893 | 1564 | 0 | 2227.5 | 854.5 | 103 | 295 | 223 | 131 | 144 | 1444
12:00 | 4088 | 893 | 1565 | 0 | 2396 | 870 | 103 | 340 | 252 | 134 | 151 | 1519
12:30 | 4124 | 893 | 1563.5 | 0 | 2554 | 870 | 103 | 312.5 | 246 | 140 | 126 | 1468.5
13:00 | 4160 | 893 | 1562 | 0 | 2712 | 870 | 103 | 285 | 240 | 146 | 101 | 1418
13:30 | 4160 | 893 | 1562 | 0 | 2712 | 870 | 103 | 285 | 240 | 146 | 101 | 1461
14:00 | 4160 | 893 | 1562 | 0 | 2712 | 870 | 103 | 285 | 240 | 146 | 101 | 1504
14:30 | 4135 | 893 | 1543 | 0 | 2740.5 | 879.5 | 103 | 267.5 | 247 | 133 | 99.5 | 1515
15:00 | 4110 | 893 | 1524 | 0 | 2769 | 889 | 103 | 250 | 254 | 120 | 98 | 1526
15:30 | 4068 | 893 | 1535 | 0 | 2740 | 889.5 | 102 | 250 | 254 | 122 | 82.5 | 1490
16:00 | 4026 | 893 | 1546 | 0 | 2711 | 890 | 101 | 250 | 254 | 124 | 67 | 1454
16:30 | 3989 | 889.5 | 1535 | 0 | 2596.5 | 875 | 115.5 | 250 | 254 | 124 | 51.5 | 727
17:00 | 3989 | 886 | 1524 | 0 | 2482 | 860 | 130 | 250 | 254 | 124 | 36 | 0
17:30 | 3939.5 | 886 | 1510.5 | 0 | 2392 | 843 | 138 | 250 | 274.5 | 124 | 21.5 | 0
18:00 | 3890 | 886 | 1497 | 0 | 2302 | 826 | 146 | 250 | 295 | 124 | 7 | 0
18:30 | 4017 | 885.5 | 1614.5 | 208 | 2638.5 | 828 | 146 | 257.5 | 437 | 130 | 3.5 | 0
19:00 | 4144 | 885 | 1732 | 416 | 2975 | 830 | 146 | 265 | 579 | 136 | 0 | 0
19:30 | 4258 | 885 | 1726 | 420 | 3695 | 909 | 146 | 320 | 660 | 136 | 0 | 0
20:00 | 4367 | 883 | 1738 | 174 | 3746 | 930 | 147 | 280 | 643 | 134 | 0 | 0
20:30 | 4439.5 | 883.5 | 1746 | 122 | 3779 | 934.5 | 147 | 280 | 645 | 135 | 0 | 27
21:00 | 4512 | 884 | 1754 | 70 | 3812 | 939 | 147 | 280 | 647 | 136 | 0 | 54
21:30 | 4544 | 883.5 | 1728 | 35 | 3791.5 | 945.5 | 147 | 265 | 643.5 | 136 | 0 | 583.5
22:00 | 4576 | 883 | 1702 | 0 | 3771 | 952 | 147 | 250 | 640 | 136 | 0 | 1113
22:30 | 4593.5 | 883.5 | 1724 | 193 | 3566.5 | 949 | 148 | 292 | 665.5 | 136 | 0 | 1059.5
23:00 | 4611 | 884 | 1746 | 386 | 3362 | 946 | 149 | 334 | 691 | 136 | 0 | 1006
23:30 | 4607 | 883.5 | 1711.5 | 465 | 2992 | 943 | 149 | 388.5 | 669 | 135 | 0 | 1127.5 | Max Temp. in Dhaka |  | 24.7° C | 32.8° C
24:00 | 4603 | 883 | 1677 | 544 | 2622 | 940 | 149 | 443 | 647 | 134 | 0 | 1249
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 271.668 MKWHr Energy Not Served 15.560 MKWHr Energy Requirement 287.227 MKWHr
Note on W13: Author:

## Generation
g | 2022-08-15
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 38 | 36 | 35 | 35 | 35 | 35 | 35 | 35 | 36 | 37 | 38 | 38 | 38 | 38 | 38 | 36 | 65 | 81 |  | 81 | 81 | 82 | 82 | 82 | 84 | 84 | 1194333
2 | Karnaphuli Hydro PP Unit-4 & 5 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 |  | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 1572000
3 | Chattogram TPP-1 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 108 | 108 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 |  | 110 | 110 | 110 | 110 | 105 | 105 | 105 | 2600000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 603495
| Teknaf 20MW PP (Solartech) | [5 empty] | 1 | 6 | 10 | 12 | 20 | 7 | 19 | 20 | 18 | 15 | 10 | 4 | 1 |  | 0 | [6 empty] | 138645
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 51 | 51 | 51 | 17 | 17 | 17 | 17 | 17 | [9 empty] | 0 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 547734
12 | Hathazari 100 MW peaking PP | 26 | 26 | 26 | 17 | 26 | 26 | 26 | 26 | [9 empty] | 2 |  | 25 | 26 | 26 | 26 | 26 | 26 | 26 | 345288
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 27 | 105 | 68 | 68 | 68 | 68 | 34 | 34 | 17 | 17 |  | 42 | 105 | 105 | 105 | 105 | 105 | 29 | 1205199
| Daudkandi 200 MW PP (B.Trac) | 25 | 25 | 25 | [16 empty] | 70 | 70 | 10 | 0 |  | 60 | 100 | 285888
14 | Titas 50 MW Peaking PP | 40 | 40 | 40 | 40 | 40 | 32 | 32 | 31 | 31 | 31 | [9 empty] | 3 | 28 | 40 | 40 | 40 | 37 | 39 | 551728
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 97 | 97 | 97 | 97 | 96 | 97 | 95 | 95 | 96 | 97 | 95 | 97 | 188 | 152 | 121 | 150 | 120 | 121 |  | 195 | 191 | 191 | 190 | 152 | 153 | 195 | 3287000
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 165 | 143 | 145 | 95 | 80 | 45 | 45 | 45 | 45 | 30 | 30 | 50 | 105 | 148 | 145 | 145 | 145 | 145 |  | 215 | 245 | 275 | 276 | 275 | 283 | 281 | 3472580
19 | Ashuganj 195MW PP (APSCL-United) | 63 | 63 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 334545
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4347000
24
25 | Ghorasal 365 MW CCPP Unit-7 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 196 | 196 | 195 | 200 | 20 | 20 | 20 |  | 20 | 90 | 150 | 280 | 300 | 300 | 300 | 5534455
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 26 | 26 | 19 | 26 | 35 | 38 | 37 | 36 | 36 | 38 | 38 |  | 38 | 34 | 33 | 34 | 34 | 34 | 34 | 797184
33 | Ashuganj 225 MW CCPP | 210 | 212 | 210 | 209 | 202 | 206 | 209 | 212 | 210 | 207 | 202 | 204 | 207 | 207 | 204 | 205 | 207 | 207 |  | 207 | 210 | 210 | 211 | 208 | 208 | 209 | 5033000
34 | Ashuganj 450 MW CCPP(South) | 310 | 310 | 310 | 310 | 310 | 310 | 305 | 305 | 305 | 305 | 330 | 280 | 270 | 270 | 275 | 305 | 300 | 305 |  | 300 | 305 | 300 | 300 | 320 | 330 | 310 | 7401000
| Ashuganj 450 MW CCPP(North) | 320 | 320 | 320 | 320 | 320 | 315 | 310 | 310 | 310 | 310 | 345 | 290 | 280 | 280 | 290 | 280 | 280 | 280 |  | 280 | 280 | 330 | 330 | 350 | 365 | 335 | 7742800
Ashuganj 420 MW CCPP(East)
35 | Ashuganj 55 MW PP (Precision) | 55 | 55 | 55 | 54 | 54 | 54 | 55 | 55 | 56 | 54 | 53 | 51 | 51 | 52 | 51 | 50 | 51 | 50 |  | 50 | 53 | 53 | 56 | 56 | 56 | 55 | 1282560
36 | Chandpur 150 MW CCPP | 136 | 136 | 136 | 136 | 136 | 137 | 136 | 137 | 137 | 136 | 136 | 136 | 136 | 136 | 136 | 137 | 136 | 136 |  | 136 | 136 | 136 | 136 | 137 | 136 | 136 | 3251940
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 413 | 418 | 418 | 418 | 418 | 418 | 408 | 407 | 407 | 405 | 398 | 398 | 397 | 397 | 397 | 399 | 397 | 396 |  | 396 | 395 | 395 | 395 | 398 | 408 | 408 | 9867260
40 | Meghnaghat 450 MW CCPP(MPL) | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 |  | 240 | 240 | 240 | 240 | 225 | 225 | 225 | 5259000
41 | Haripur 360MW CCPP(HPL) | 292 | 281 | 272 | 277 | 293 | 293 | 291 | 292 | 291 | 292 | 332 | 331 | 322 | 330 | 333 | 322 | 322 | 322 |  | 337 | 337 | 337 | 337 | 337 | 332 | 332 | 7524000
42 | RPCL 210MW CCPP | 102 | 98 | 98 | 98 | 98 | 98 | 96 | 104 | 102 | 98 | 100 | 100 | 100 | 101 | 100 | 102 | 102 | 112 |  | 130 | 150 | 150 | 151 | 151 | 155 | 156 | 2597760
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 1 | 8 | 19 | 33 | 54 | 44 | 49 | 8 | 56 | 4 | 5 | 3 | 1 |  | 0 | [6 empty] | 278450
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 30 | 30 | 10 | 8 | 30 | 30 | 5 | 20 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 844000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 674840
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 60 | 61 | 61 | 61 | 61 | 61 | 61 | 65 | 61 | 61 | 57 | 57 | 58 | 59 | 60 | 61 | 60 | 64 |  | 64 | 65 | 64 | 65 | 64 | 59 | 61 | 1474464
48 | Shahjibazar 86MW PP (Shahjibazar) | 78 | 65 | 50 | 25 | 20 | 20 | 20 | 20 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 947520
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 220 | 220 | 220 | 220 | 220 | 212 | 199 | 199 | 200 | 201 | 222 | 222 | 222 | 221 | 222 | 221 | 221 | 221 |  | 221 | 221 | 221 | 221 | 221 | 220 | 220 | 5207310
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 0 | [8 empty] | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 169800
53 | Sylhet 10MW PP (Desh) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 7 | 9 | 9 | 9 | 10 | 10 | 10 | 10 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 211140
54 | Hobiganj 11MW PP Cofidence-E | [26 empty] | 0
55 | Fenchugonj 51 MW PP (Barakatullah) | [16 empty] | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 45600
56 | Shahjahanulla 25 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 188112
57 | Bibiana-II 341 MW CCPP (Summit) | 290 | 295 | 275 | 280 | 290 | 260 | 270 | 280 | 270 | 280 | 300 | 300 | 300 | 280 | 280 | 310 | 280 | 275 |  | 295 | 275 | 280 | 290 | 295 | 320 | 295 | 7025500
| Bibiyana South 400 MW | 400 | 400 | 400 | 399 | 400 | 360 | 360 | 360 | 370 | 370 | 376 | 386 | 392 | 391 | 390 | 401 | 400 | 360 |  | 400 | 400 | 400 | 400 | 400 | 397 | 400 | 9305100
58 | Nababganj 55 MW PP (Southern power ) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 17 | 17 | 17 | 35 | 35 | 35 | 35 | 35 | 35 |  | 50 | 55 | 55 | 55 | 55 | 55 | 55 | 1115495
59 | Tangail Palli Power Gen 22 MW | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 7 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 293280
60 | Barabkunda 22 MW PP (Regent) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 364080
61 | Narshingdi 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 0 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 418284
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 20 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 475704
63 | Impoprt (Tripura) | 160 | 158 | 154 | 152 | 146 | 128 | 124 | 120 | 122 | 126 | 128 | 134 | 146 | 136 | 120 | 124 | 124 | 124 |  | 136 | 136 | 134 | 136 | 136 | 136 | 134 | 3214080
64 | Malancha, Ctg. EPZ (United) | 39 | 38 | 39 | 39 | 41 | 42 | 42 | 42 | 40 | 37 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 31 | 42 | 42 | 42 | 42 | 42 | 42 | 1025280
65 | Feni 22MW PP (Doreen) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 22 | 22 | 22 | 22 | 508356
66 | Feni 11 MW PP (Doreen) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 226080
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 28 | 23 | 25 | 33 | 33 | 25 | 25 | 33 | 33 | 0 |  | 20 | 33 | 33 | 33 | 33 | 33 | 33 | 696700
68 | Cumilla 25 MW PP (Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 14 | 20 | 20 | 20 | 20 | 18 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 482250
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 20 | 20 | 20 | 8 | 20 | 20 | 20 | 20 | 12 | 16 | 19 | 19 | 19 | 8 | 20 | 26 | 26 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 405180
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 |  |  |  | 28 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 22 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 685800
72 | Rupganj 33 MW PP(Summit) | 30 | 30 | 30 | 30 | 33 | 33 | 33 | 30 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 760000
73 | Ghorashal 108MW PP (Regent) | 86 | 86 | 86 | 86 | 86 | 89 | 90 | 91 | 88 | 83 | 85 | 86 | 89 | 89 | 89 | 96 | 97 | 52 |  | 96 | 96 | 96 | 96 | 96 | 96 | 93 | 2070000
| Feni Lanka Power | [26 empty] | 0
| Chowmuhani 113 MW | 8 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  | 50 | 112 | 112 | 113 | 113 | 52 | 31 | 641760
| Manikgonj 162MW PP(MPGL) | 162 | 162 | 162 | 162 | 162 | 108 | 54 | 54 | 54 | 54 | 60 | 145 | 162 | 162 | 162 | 162 | 108 | 108 |  | 150 | 162 | 162 | 162 | 162 | 162 | 162 | 3299040
77 | Siddhirganj 100 PP(Dutch Bangla) | 32 | 32 | 32 | 32 | 14 | 8 | 8 | 8 | [9 empty] | 2 |  | 18 | 50 | 50 | 49 | 49 | 49 | 14 | 402240
78 | Gazipur 52 MW PP | 41 | 41 | 41 | 41 | 41 | 32 | 41 | 41 | 41 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 41 | 41 |  | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 931680
79 | Kodda 150MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 27 | 48 | 48 | 82 | 110 | 124 | 124 | 124 | 124 | 124 |  | 125 | 125 | 125 | 125 | 125 | 125 | 48 | 1720320
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | [26 empty] | 0
| Gazipur 100 MW PP | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2541600
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 2 | 4 | 5 | 5 | 4 | 5 | 5 | 2 | 1 | 0 | [9 empty] | 34080
| Jodiac Power | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 |  | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 915241
| Karnaphuli Power Ltd. | 55 | 55 | 47 | 55 | 55 | 55 | 55 | 55 | 58 | 85 | 68 | 68 | 68 | 68 | 68 | 68 | 51 | 43 |  | 58 | 110 | 103 | 110 | 110 | 110 | 55 | 1702829
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL) | 33 | 33 | 34 | 34 | 33 | 33 | 34 | 34 | 32 | [7 empty] | 0 | 1 |  | 22 | 50 | 50 | 50 | 50 | 50 | 11 | 547200
| Meghnaghat 104 MW PP (OPCL) |  |  |  | 15 |  |  |  | 10 | 32 | 34 | 34 | 34 | 35 | 35 | 35 | 35 | 37 | 53 |  | 55 | 55 | 55 | 55 | 55 | 55 | 17 | 697920
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 785640
92 | Fenchuganj 44MW (Energyprima) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | [8 empty] | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 141336
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1224719
94 | Gagnagar 102 MW PP (Digital Power) | 24 | 24 | 24 | 24 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 16 | 16 | 16 | 16 | 16 | 16 |  | 50 | 50 | 50 | 50 | 24 | 32 | 50 | 494496
95 | Patenga 50MW PP (Baraka) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 9 | 32 | 41 | 44 | 44 | 44 | 35 |  | 0 |  | 0 |  | 0 | 6 | 6 | 336480
96 | Chattogram 108 MW PP (ECPV) | 12 | 12 | 12 | 12 | 12 | 11 | 12 | 12 | 7 | [8 empty] | 3 |  | 17 | 20 | 48 | 85 | 61 | 52 | 17 | 392640
97 | katpotti 52 MW
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 55 | 55 | 55 | 55 | 55 | 55 | 40 | 40 | 40 | 40 | 40 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1265389
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 17 | 17 | 17 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 55 | 55 | 55 | 55 | 55 | 55 | 1098613
101 | Kushiara 163 MW CCPP (KP)
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 0 | 1 | 1 | 2 | 2 | 3 | 1 | 1 | 1 | 0 | 0 | [8 empty] | 13350
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 54 | 54 | 54 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1068840
104 | Keranigonj 300 MW PP (APR) | 166 | 55 | 28 | [16 empty] | 156 | 137 | 24 | 20 | 0 | 150 | 180 | 777968
105 | Bramhangoan 100 MW PP (Aggreko) | 92 | 92 | 50 | [16 empty] | 90 | 97 | 60 | 25 | 0 | 96 | 98 | 578276
106 | Mymensingh 200 MW PP (United) | 48 | 47 | 48 | 48 | 48 | 48 | 48 | 76 | 76 | 180 | 180 | 188 | 187 | 189 | 190 | 191 | 193 | 200 |  | 200 | 200 | 200 | 191 | 192 | 173 | 48 | 3122400
112 | Aurahati 100MW PP (Aggreko) | 50 | 50 | 25 | [16 empty] | 100 | 96 | 60 | 25 | 0 | 80 | 96 | 406977
114 | Kodda 149 MW PP Unit-1 (Summit) | 71 | 72 | 71 | 72 | 71 | 86 | 147 | 114 | 70 | 62 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 68 | 149 | 149 | 149 | 149 | 149 | 54 | 1994256
115 | Juldah 100 MW PP Unit-3 (Acorn) | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 10 | 10 | 14 | 76 | 76 | 90 | 60 | 60 | 60 | 30 |  | 90 | 90 | 90 | 90 | 90 | 90 | 21 | 1123200
116 | Chandpur 200MW (Desh energy) | 170 | 170 | 170 | 170 | 170 | 149 | 73 | 50 | 51 | 51 | 51 | 76 | 132 | 200 | 200 | 155 | 155 | 100 |  | 140 | 200 | 200 | 200 | 200 | 200 | 200 | 3501120
117 | Ashuganj 150MW PP (Midland) | 135 | 137 | 135 | 135 | 128 | 128 | 80 | 80 | 80 | 80 | 80 | 80 | 92 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 113 | 2636218
118 | Bibiyana-III 400 MW CCPP | 402 | 402 | 402 | 401 | 402 | 363 | 365 | 365 | 365 | 365 | 400 | 404 | 403 | 404 | 405 | 402 | 400 | 352 |  | 400 | 401 | 401 | 400 | 402 | 403 | 402 | 9423000
| Jamalpur 115 MW PP (United) | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 67 | 68 | 85 | 106 | 106 | 106 | 106 | 85 | 65 | 48 | 48 |  | 87 | 88 | 87 | 87 | 88 | 70 | 49 | 1699200
| Anwara 300 MW PP (United) | 280 | 268 | 268 | 251 | 251 | 170 | 135 | 135 | 135 | 135 | 135 | 190 | 230 | 230 | 230 | 230 | 230 | 190 |  | 282 | 285 | 300 | 300 | 300 | 52 | 52 | 5211382
| Juldah unit-2 (Acorn) | 39 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 70 | 100 | 100 | 92 | 90 | 90 | 90 | 90 | 90 | 60 |  | 68 | 100 | 100 | 100 | 100 | 100 | 62 | 1577280
| Anlima Energy Ltd. | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 |  | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 2581855
| Bhairob 54.5 MW | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 885960
| Spectra Solar Plant Ltd. | [5 empty] | 0 | 2 | 7 | 14 | 9 | 35 | 22 | 35 | 18 | 26 | 9 | 10 | 2 |  | 0 | [6 empty] | 189859
| Chandpur 115(Doreen) | 74 | 74 | 74 | 74 | 65 | 43 | 35 | 41 | 39 | 39 | 39 | 35 | 37 | 51 | 51 | 51 | 51 | 51 |  | 56 | 100 | 84 | 93 | 97 | 96 | 78 | 1454400
| Kanchan Purbachal Power Generation Ltd. | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 48 | 48 | 55 | 55 | 55 | 35 | 35 | 55 | 17 |  | 0 | 55 | 46 | 55 | 55 | 55 | 55 | 1195560
Mirsharai 150 MW (Oil)
Mirsharai 150 MW (Gas)
120 | Eastern Zone Total | 7630 | 7450 | 7244 | 6964 | 6917 | 6548 | 6400 | 6437 | 6398 | 6539 | 6644 | 6773 | 7097 | 7219 | 7061 | 6910 | 6774 | 6443 |  | 7866 | 8557 | 8470 | 8588 | 8482 | 8584 | 7928 | 175103123
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 66 | 66 | 66 | 66 | 66 | 65 | 65 | 65 | 65 | 65 | 65 |  | 66 | 65 | 66 | 66 | 66 | 16 | 16 | 1107840
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 16 | 16 | 16 | 16 | 16 | [12 empty] | 9 |  | 40 | 50 | 44 | 40 | 38 | 39 | 28 | 303840
| Khulna 225 MW CCPP | 218 | 210 | 200 | 200 | 200 | 170 | 120 | 120 | 120 | 120 | 120 | 170 | 155 | 120 | 120 | 120 | 120 | 120 |  | 130 | 150 | 150 | 150 | 120 | 170 | 227 | 3772800
129 | Rupsha 105 MW PP (Orion rupsha) | [8 empty] | 2 | 17 | 17 | 17 | 35 | 35 | 35 | 53 | 17 | 17 |  | 20 | 53 | 53 | 53 | 53 | 53 | 17 | 503520
130 | Mongla Orion 100 MW Solar PP | [6 empty] | 10 | 18 | 29 | 34 | 35 | 42 | 18 | 50 | 40 | 34 | 15 | 1 |  | 0 | [6 empty] | 337680
131 | Rampal 1320 MW (BIFPCL) | [17 empty] | 8 |  | 0 | [6 empty] | 3990
132 | United Payra Power Ltd. | 35 | 35 | 35 | 17 | 17 | 17 | 17 | 17 |  |  |  |  | 16 | 17 | 17 | 17 | 17 | 17 |  | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 513600
133 | Bhola Nutan Biddut BD LTD (GAS) | [17 empty] | 57 |  | 57 | 57 | 57 | 57 | 57 | 45 | 0 | 333082
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 64 | 64 | 32 | 32 | 32 | 32 | 32 | 32 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 32 | 48 | 48 | 48 | 48 | 48 | 48 | 776064
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 152 | 152 | 152 | 152 | 152 | 152 | 152 | 144 | 151 | 152 | 150 | 152 | 150 | 152 | 148 | 152 | 150 | 149 |  | 150 | 150 | 152 | 144 | 152 | 152 | 152 | 3623671
140 | Bhola 33 MW PP (Venture) | 28 | 28 | 27 | 22 | 22 | 22 | 21 | 19 | 19 | 19 | 19 | 20 | 23 | 21 | 26 | 24 | 20 | 21 |  | 26 | 26 | 27 | 27 | 28 | 30 | 29 | 567602
141 | Noapara 100 MW PP (Bangla Trac) | 20 | 20 | 20 | 10 | [16 empty] | 20 | 20 | 0 |  | 0 | 10 | 132480
142 | Noapara 40 MW PP (Khanjahan Ali) | 8 |  |  |  |  | 8 | 8 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 8 | 8 |  | 32 | 32 | 32 | 32 | 32 | 8 | 8 | 448500
143 | Gopalganj 100 MW Peaking PP | 63 | 63 | 63 | 58 | 20 | [12 empty] | 30 |  | 55 | 65 | 70 | 52 | 47 | 47 | 47 | 578560
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 70 | 67 | 67 | 61 | 67 | 67 | 71 | 67 | 67 | 67 |  | 82 | 105 | 105 | 105 | 105 | 105 | 105 | 2161728
146 | Bheramara HVDC | 893 | 893 | 893 | 894 | 893 | 893 | 893 | 894 | 894 | 893 | 893 | 893 | 893 | 893 | 893 | 893 | 886 | 886 |  | 885 | 885 | 883 | 884 | 883 | 884 | 883 | 21528000
147 | Bheramara 410 MW CCPP | 170 | 170 | 170 | 170 | 175 | 175 | 175 | 175 | 175 | 185 | 200 | 205 | 205 | 210 | 210 | 220 | 230 | 235 |  | 240 | 245 | 250 | 260 | 265 | 270 | 270 | 5090688
148 | Payra 1320 MW | 600 | 600 | 600 | 580 | 580 | 540 | 510 | 510 | 510 | 510 | 510 | 540 | 540 | 550 | 560 | 560 | 530 | 490 |  | 500 | 580 | 600 | 610 | 622 | 622 | 622 | 14510300
149
150 | Barapukuria TPP Unit-1 | 81 | 79 | 80 | 81 | 80 | 80 | 80 | 81 | 80 | 78 | 79 | 80 | 80 | 80 | 79 | 80 | 80 | 78 |  | 79 | 79 | 80 | 79 | 80 | 74 | 68 | 1886836
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 |  | 251 | 250 | 250 | 250 | 250 | 250 | 250 | 5989600
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 16 | [6 empty] | 0 |  | 8 | 8 | 8 | 16 | 16 | 24 | 24 | 431120
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 1 | 3 | 3 | 3 | 3 | 6 | 4 | 2 | 5 | 3 | 1 | 0 | [8 empty] | 36660
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 151 | 151 | 151 | 150 | 151 | 151 | 150 | 151 | 152 | 152 | 152 | 153 | 152 | 152 | 153 | 153 | 153 | 153 |  | 153 | 152 | 152 | 159 | 188 | 188 | 183 | 3984591
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
| Sirajgonj 225 MW CCPP Unit-2 (Oil) | 219 | 205 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 170 | 130 | 130 | 130 | 130 | 130 | 130 |  | 135 | 170 | 130 | 130 | 130 | 164 | 216 | 3750918
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 152 | 152 | 152 | 153 | 155 | 156 | 156 | 155 | 155 | 158 | 164 | 169 | 176 | 176 | 169 | 163 | 183 | 189 |  | 195 | 201 | 200 | 203 | 206 | 205 | 204 | 4396245
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 323 | 333 | 334 | 335 | 338 | 335 | 340 | 330 | 368 | 400 | 414 | 414 | 414 | 380 | 380 | 380 | 380 | 340 |  | 414 | 414 | 420 | 423 | 380 | 414 | 420 | 9010981
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | 40 | 40 | 40 | 40 | 40 | [14 empty] | 5 | 5 | 17 | 29 | 29 | 40 | 38 | 323153
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 19 | 19 | 19 | 20 | 20 | 20 | 21 | 20 | 20 | 21 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 491280
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 262746
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | 34 | 34 | 42 | 34 | 34 | 34 | 34 | 42 | 42 | 42 | 42 | 42 | 50 | 50 | 50 | 42 | 8 | 8 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 904432
167 | Katakhali 50 MW Peaking PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 24 | 24 | 24 | [9 empty] | 16 | 16 | 16 | 24 | 24 | 24 | 16 | 285448
168 | Santahar 50 MW Peaking PP | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 32 | 33 | 33 | [9 empty] | 34 | 34 | 34 | 33 | 33 | 33 | 33 | 515531
169 | Natore 52 MW PP (Rajlanka) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 190560
170 | Chapainawabganj 100 MW Peaking PP | 45 | 45 | 45 | 45 | 45 | 45 | 44 | 44 | [11 empty] | 82 | 82 | 82 | 81 | 81 | 81 | 81 | 795080
171 | Baghabari 200 MW PP (Paramount) | 25 | 25 | [22 empty] | 0 | 60 | 111194
| Bagura 113 MW PP (Confidence)-2 | 94 | 94 | 94 | 94 | 94 | 50 | 35 | 35 | 35 | 35 | 35 | 59 | 70 | 70 | 70 | 70 | 35 | 35 |  | 38 | 70 | 80 | 94 | 94 | 94 | 94 | 1715328
172 | Confidence Power Bogura Unit-1 113 MW | 95 | 95 | 95 | 95 | 70 | 35 | 35 | 35 | 35 | 35 | 35 | 60 | 70 | 70 | 70 | 70 | 35 | 35 |  | 80 | 95 | 95 | 95 | 95 | 95 | 95 | 1663488
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 98 | 98 | 98 | 98 | 99 | 99 | 99 | 70 | 49 | 60 | 70 | 96 | 97 | 96 | 96 | 96 | 104 | 104 |  | 104 | 104 | 105 | 103 | 106 | 105 | 56 | 2215065
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1 |  | 2 | 5 | 6 | 7 | 8 | 7 | 5 | 4 | 3 | 2 |  | 0 | [6 empty] | 53252
178 | Energypac Power Venture Thakurgaon Ltd. | [9 empty] | 40 | 90 | 90 | 90 | 90 | 89 | 89 | 89 | 90 |  | 90 | 91 | 90 | 90 | 91 | 91 | 72 | 1257024
178