## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on forecasted generation & Demand of national grid on | [6 empty] | 2019-05-31 | Friday
|  | Date (day): | 2019-05-31 |  | Friday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13326 | MW |  |  | (b) At Evening Peak Hour : |  | 14995 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2019-05-30 | 2019-05-31 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | Gas | PDB | 2*55 | 110 | 85 | 35 | 35 | 35 | 35 |  | 50 | ST-1 under maint.
| Ghorasal GT: Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 94 | 94 | 94 | 94 |  |  | On test.
| Ghorasal GT: Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 98 | 100 | 100 | 100 | 80 |  | Gas shortage
| Ghorasal ST: Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 115 | 115 | 115 | 115 | 75 |  | Gas shoetage
2 | Ghorasal ST: Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 300 | 240 | 300 | 380
3 | Ghorashal 78MW (MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 20 | 0 | 20 |  |  | Gas Shortage
4 | Ghorashal (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 6 | 22 | 0 | 20 |  |  | Gas Shortage
5 | Haripur GT: Unit-1, 2 |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 | 40 |  | Gas shortage
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 346 | 329 | 412 | 412 |  |  | FGMO
7 | Haripur NEPC 110MW |  | HFO | IPP | 8*15 | 110 | 110 | 26 | 110 | 110 | 110
8 | Haripur Power CCPP 360MW |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 336 | 320 | 360 | 360
9 | Meghnaghat CCPP 450MW |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 400 | 340 | 450 | 450
10 | Meghnaghat (IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 7 | 100 | 100 | 100
11 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 295 | 275 | 335 | 335 |  |  | FGMO
12 | Madanganj 102MW |  | HFO | QRPP | 6*17 | 102 | 100 | 30 | 80 | 100 | 100
13 | Madanganj-55 MW |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55
14 | Keraniganj (Powerpac) 100MW |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 88 | 100 | 100
15 | Narshingdi (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 16 | 19 | 22 | 22
16 | Siddhirgonj ST 210MW |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 115 |  | Gas shortage
17 | Siddhirgonj GT Unit-1& 2 |  | Gas | EGCB | 2*105 | 210 | 210 | 90 | 87 | 100 | 100 | 110 |  | Gas shortage
| Siddhirganj Desh |  | HSD | QRPP | 96*1.2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
18 | Siddhirganj (Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 85 | 100 | 100 | 100
19 | Siddhirganj CCPP-335 MW |  | Gas | EGCB | 1*217 | 217 | 217 | 0 | 0 | 0 | 0 | 37 |  | Gas shortage
0 | Pagla (DPA ) |  | HSD | QRPP | 100*0.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
20 | Gagnagar (Orion) |  | HFO | IPP | 12*8.924 | 102 | 102 | 100 | 100 | 102 | 102
21 | Katpotti 51 MW |  | HFO | IPP | 7*7.9 | 51 | 51 | 6 | 49 | 49 | 49
22 | Banco Energy 54MW |  | HFO | IPP | 3*18 | 54 | 54 | 35 | 35 | 35 | 35 |  | 19 | Engine problem
23 | Kodda 149MW |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 15 | 140 | 149 | 149
24 | Northern 55 MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 56 | 56 | 55 | 55
25 | Southern 55MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
26 | Bosila 108MW |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 63 | 63 | 65 | 65 |  | 43 | Engine problem
27 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 56 | 57 | 58 | 58 |  | 22 | Engine problem
28 | Summit Maona |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
29 | Summit Rupganj |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 33 | 33
30 | Gazipur (RPCL) |  | HFO | IPP | 6*8.9 | 52 | 52 | 40 | 48 | 48 | 48 |  | 4
31 | Tongi GT |  | Gas | PDB | 1* 105 | 105 | 105 | 40 | 40 | 40 | 40 | 65 |  | Gas shortage
32 | Summit Gazipur -2 |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 300 | 100 | 300
33 | APR Energy , Keranigonj |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 107 | 100 | 300
34 | Bramhangoan 100 MW (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 51 | 0 | 100 |  |  | Low demand
35 | Aggreko Aurahati 100MW |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 53 | 0 | 100 |  |  | Low demand
36 | Summit Gazipur-1 150MW |  | HFO | IPP | 149 | 149 | 149 | 46 | 149 | 149 | 149
| Gazipur 100 MW |  | HFO | RPCL | 100 MW | 0 | 0 | 109 | 108 | 100 | 100
| Dhaka area Total |  |  |  |  | 5934 | 5698 | 3013 | 3998 | 4059 | 4779 | 522 | 138
37 | Chattogram ST-1 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 100 | 100 | 100 | 80 |  | Gas shortage
| Chittgong ST-2 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
38 | Raozan 25 MW (RPCL) |  | HFO | IPP | 3*8.9 | 25 | 25 | 24 | 16 | 25 | 25
39 | Teknaf Solartech 20MW |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 19.6 | 0 | 20 | 0
40 | Patenga 50MW |  | HFO | IPP | 8*6.98 | 50 | 50 | 46 | 47 | 45 | 45
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 34 | 36 | 35 | 35 |  | 195 | Low water lavel
42 | Sikalbaha ST 60MW |  | Gas | PDB | 1*60 | 60 | 40 | 0 | 0 | 0 | 0 |  | 40 | Under S/D
43 | Sikalbaha 225MW |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 125 | 230 | 225 | 225
44 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 142 | 130 | 140 | 140
45 | Sikalbaha (Energis) |  | HFO | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 51 | 16 | 24 | 24 | 24 |  | 27 | Engine problem
| Baraka Sikalbaha PL |  | HFO | IPP | 105 MW | 0 | 0 | 105 | 105 | 105 | 105
46 | Hathazari peaking |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 83 | 74 | 74
47 | Dohazari Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 17 | 85 | 85 | 85
48 | Juldah (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 10 | 86 | 100 | 100
49 | Juldah 100 MW Unit-3 |  | HFO | IPP | 0 | 100 | 100 | 100 | 100 | 100 | 100
50 | Barabkunda (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 19 | 19 | 19 |  | 3
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 26 | 10 | 40
51 | Chattogram ECPV 108 MW |  | HFO | IPP | 16*7 | 108 | 108 | 83 | 90 | 100 | 100
| Kaptai Solar |  | Solar | PDB | 7.4 MW | 0 | 0 | 5.4 | 0 | 3 | 0
| Anwara United |  | HFO | United Group | 300 MW | 0 | 0 | 135 | 132 | 84 | 150
| Chattogram area Total |  |  |  |  | 1761 | 1681 | 982 | 1309 | 1294 | 1367 | 260 | 265
52 | Ashuganj ST: Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
| Ashuganj ST: Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
| Ashuganj ST: Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 80 | 0 | 120 | 120 | 54 |  | Gas shortage
53 | Ashuganj CCPP 225 MW |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 206 | 0 | 221 | 221
54 | Ashuganj CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 320 | 220 | 360 | 360
55 | Ashuganj CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 320 | 220 | 360 | 360
56 | Ashuganj Engines TSK |  | Gas | APSCL | 14*3.968 | 53 | 45 | 33 | 0 | 0 | 0 |  | 45 | Gas Line problem.
57 | Ashuganj (Precision) 55MW |  | Gas | RPP | 15*4 | 55 | 55 | 52 | 0 | 55 | 55 | 0
58 | Ashuganj (United) 53MW |  | Gas | QRPP | 14*4 | 53 | 53 | 5 | 0 | 5 | 5 | 48 |  | Gas Shortage
59 | Ashuganj 195MW Modular |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
60 | Ashuganj (Midland) 51MW |  | Gas | IPP | 6*9.34 | 51 | 51 | 10 | 0 | 7 | 7 |  | 44 | Engine problem
61 | Midland 150MW |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 0 | 0 | 133 |  |  | Low demand.
62 | B.Baria (Aggreko) 85MW |  | Gas | QRPP | 86*1.10 | 85 | 85 | 0 | 0 | 0 | 0 |  |  | Contract expired
63 | Daudkandi Peaking 52MW |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 50 | 0 | 50
64 | Chandpur CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 100 | 100 | 100 | 100
65 | Chandpur Desh 200MW |  | HFO | IPP | 0 | 200 | 200 | 146 | 200 | 200 | 200
66 | Feni (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 22 | 0 | 22
67 | Feni, Mohipal (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 0 | 11
** | Tripura |  |  | Imported power | 0 | 160 | 160 | 138 | 190 | 149 | 188
68 | Jangalia (Summit) 33MW |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 25 | 25 | 33 | 33
69 | Lakdhanvi 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 52 | 52 | 52 | 52
70 | Summit Cumilla 25MW |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 20 | 20
71 | Daudkandi bangla trak |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 150 | 0 | 200
| Cumilla Area Total |  |  |  |  | 2951 | 2891 | 1546 | 1268 | 1690 | 2145 | 553 | 89
72 | Mymensingh RPCL 210MW |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 145 | 147 | 150 | 150 | 52 |  | Gas shortage
73 | Tangail (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 20 | 20
74 | Jamalpur 95MW |  | HFO | IPP | 12*8.924 | 95 | 95 | 8 | 94 | 70 | 95
75 | Sarishabari (Solar) |  | Solar | IPP | 1*3 | 3 | 3 | 0.8 | 0 | 2 | 0
76 | United Mymensingh PPL |  | HFO | IPP | 200 | 200 | 200 | 7 | 122 | 100 | 200
77 | United Jamalpur PPL |  | HFO | IPP | 115 MW | 115 | 115 | 96 | 95 | 100 | 100 |  | 15 | Engine problem
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 276.8 | 478 | 442 | 565 | 52 | 0
78 | Fenchugonj CCPP-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 55 | 55 | 57 | 57
79 | Fenchugonj CCPP-2 |  | Gas | PDB | !F71 | 104 | 90 | 58 | 40 | 58 | 58
80 | Kushiara 163 MW CCPP GT |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 100 | 163 | 163 | 163
81 | Shajibazar 330 MW |  | Gas | PDB | 3*110 | 330 | 330 | 248 | 250 | 330 | 330 |  |  | FGMO
82 | Fenchugonj (Barakatullah) 51MW |  | Gas | RPP | 19*2.90 | 51 | 51 | 34 | 50 | 50 | 50
83 | Fenchuganj (EPL) 44MW |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 44 | 50 | 44 | 44
84 | Hobiganj 11MW |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
85 | Shahjibazar GT: Unit- 8, 9 |  | Gas | PDB | 2*35 | 70 | 66 | 59 | 61 | 66 | 66 |  |  | FGMO
86 | Shahjibazar 86MW |  | Gas | RPP | 32*2.90 | 86 | 86 | 75 | 77 | 86 | 86
87 | Shahjibazar (EPL) 50MW |  | Gas | RPP | 27*2.0 | 50 | 50 | 43 | 45 | 46 | 46
88 | Sylhet GT 150 MW |  | Gas | PDB | 1*142 | 142 | 142 | 122 | 112 | 130 | 130
89 | Sylhet GT 20 MW |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18
90 | Sylhet (EPL) 50MW |  | Gas | RPP | 27*2 | 50 | 50 | 43 | 46 | 50 | 50
91 | Shahjahanulla 25 MW |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 23 | 23 | 25 | 25
92 | Summit Bibiana- 2 |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 280 | 260 | 341 | 341 |  |  | FGMO
| Bibiyana-3 285 MW |  | Gas | PDB | 285 MW | 0 | 0 | 283 | 250 | 269 | 269 |  |  | On test
93 | Sylhet (Desh) 10MW |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1594 | 1549 | 1506 | 1521 | 1754 | 1754 | 0 | 0
94 | Bheramara GT-1,2,3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 48 | 0 | 48
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 936 | 939 | 945 | 945
| Khulna (KPCL-1 & 3) |  | HFO | IPP | 19*6.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
95 | Khulna (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 16 | 115 | 115 | 115
96 | Faridpur Peaking |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 32 | 33 | 33
97 | Khulna CCPP 225MW |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 120 | 233 | 225 | 225
98 | Gopalganj Peaking |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 52 | 50 | 80
99 | Bheramara 360 MW |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 |  | 410 | Under maint. |  | 15/06/2019
100 | Noapara (KZA) 40MW |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 40 | 40 | 40
0 | Khulna (Aggreeco) 55MW |  | HSD | QRPP | 71*0.85 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
101 | Bangla Trak Noapara |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 97 | 0 | 100
102 | Labon Chora 105 MW |  | HFO | IPP | 6*18.445 | 105 | 105 | 35 | 90 | 105 | 105
103 | Madhumati Power Plant |  | HFO | IPP | 100 MW | 105 | 105 | 53 | 107 | 102 | 102
| Khulna Area Total |  |  |  |  | 2328 | 2314 | 1160 | 1753 | 1615 | 1793 | 0 | 410
104 | Summit Barisal 110 MW |  | HFO | IPP | 7*17.076 | 110 | 110 | 16 | 110 | 110 | 110
105 | Barisal GT: Unit-1, 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 12 | 0 | 20
106 | Bhola (Venture) 33MW |  | Gas | RPP | 1*34.50 | 33 | 33 | 22 | 40 | 39 | 39
107 | Bhola CCPP 194MW |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 174 | 173 | 173 | 173
108 | Bhola Aggreko 95MW |  | Gas | QRPP | 96*1.10 | 95 | 95 | 92 | 97 | 90 | 90
| Barisal Area Total |  |  |  |  | 472 | 462 | 304 | 432 | 412 | 432 | 0 | 0
109 | Baghabari GT 71MW |  | Gas | PDB | 1*71 | 71 | 71 | 55 | 55 | 60 | 60
| Baghabari GT 100MW |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
110 | Baghabari Peaking 50MW |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 0 | 50
111 | Bera Peaking |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 33 | 35 | 35
112 | Amnura 50MW |  | HFO | QRPP | 7*7.79 | 50 | 50 | 12 | 0 | 50 | 50
113 | Katakhali (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 50 | 50 | 50
114 | Katakhali Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 44 | 47 | 47
115 | Sirajgonj Unit-1 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 196 | 184 | 200 | 200 |  |  | FGMO
116 | Sirajgonj Unit-2 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 160 | 174 | 200 | 200 |  |  | FGMO
117 | Sirajgonj Unit-3 225MW |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 175 | 192 | 220 | 220 |  |  | FGMO
118 | Sirajgonj Unit-4 414 MW(Gas) |  | Gas | SNWPGCL | 1*282+1*132 | 414 | 414 | 350 | 350 | 414 | 414
119 | Santahar Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 34 | 35 | 35
120 | Bogra (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 21 | 22 | 22 | 22
121 | Bogra (EPL) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 13 | 16 | 16 | 16
122 | Ullapara (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
123 | Rajlanka 52 MW |  | HFO | IPP | 52 | 52 | 52 | 8 | 50 | 52 | 52
124 | Chapainawabganj-100 MW |  | HFO | PDB | 104 | 104 | 104 | 0 | 95 | 95 | 95
125 | Paramount Baghabari |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
126 | Confidence Bogura-2 (CPBL) |  | HFO | IPP | 113 MW | 113 | 113 | 53 | 108 | 50 | 100
| Rajshahi Area Total |  |  |  |  | 2080 | 2070 | 1051 | 1468 | 1757 | 1857 | 0 | 100
127 | Barapukuria Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under overhauling
| Barapukuria Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 67 | 68 | 70 | 70
128 | Barapukuria Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 200 | 200 | 199 | 199 | 75
129 | Rangpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 17 | 16 | 16
130 | Saidpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 17 | 18 | 18
| Confidence Rangpur |  | HFO | IPP | 113 MW | 0 | 0 | 4 | 0 | 0 | 0
| Rangpur Area Total |  |  |  |  | 564 | 484 | 271 | 302 | 303 | 303 | 75 | 85
| Total |  |  |  |  | 18329 | 17786 | 10109.8 | 12529 | 13326 | 14995 | 1462 | 1087
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 9648.2464 | 11957 | 12717.6137 | 14310.417
A. |  | 2019-05-30 | (Yesterday) |  |  |  |  | Thursday
1 | Highest Generation : |  |  | 12581 | MW at | 22:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 8599.5 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 12529 | MW
3 | Day peak Generation : |  |  | 10109.8 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 11957 | MW
4 | Evening peak Generation : |  |  | 12529 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 258.7691 | MKWHr | By Solar | 0.18454 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas: | 153.1889 | MKWHr |  | By Oil: | 71.8394 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal: | 6.452 | MKWHr |  | By Hydro: | 0.78696 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1462 | MW | Dhaka | 4437 | 4437 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1087 | MW | Chittagong | 1227 | 1227 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 2549 | MW | Khulna | 1564 | 1564 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1328.33 | MMCFD |  |  | Rajshahi | 1184 | 1184 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 104635861.15 | ii) Oil : | Taka | 520980306.98 | Comilla | 1164 | 1164 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 28387071.63 | Total | Taka | 654003239.76 | Mymensingh | 853 | 853 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0.1515 | MKWHr. | Sylhet | 529 | 529 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -160 | MW (E to W) at | 21:00 | hrs | Barisal | 350 | 350 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -180 | MW at | 1:00 | hrs | Rangpur | 649 | 649 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 36.2° C |  |  | Total | 11957 | 11957 |  | 0
B. |  | 2019-05-31 | (Today) |  |  |  | Friday |  |  | Probable max. temperature in Dhaka |  |  | 35.1° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 12000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 14995 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 9800 | MW
4 | Reserve(Generation end) |  |  |  | 2995 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 246.8189 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 7327.2 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 22.4735 | MKWHr. | ii) HVDC Flow at Peak Time |  | 939 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.8438 | MKWHr. | iii) Maximum HVDC Flow : |  | 940 | MW at | 24:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 73.9 |  | (b) Today: | 73.92 |  | (c) Rule Curve: |  | 76.2
.
** Wapda control unable to give gas reading.

## YesterdayGen
2019-05-30
Plant Name | Ghorasal ST: Unit-1,2 | Ghorasal GT: Unit-3 | Ghorasal GT: Unit-4 | Ghorasal ST: Unit-5 | Ghorasal ST: Unit-7 | Ghorashal (Regent) | Ghorashal 78MW (MAX) | Haripur 412 MW CCPP | Haripur Power CCPP 360MW | Haripur NEPC 110MW | Haripur GT: Unit-1, 2 | Meghnaghat CCPP 450MW | Meghnaghat CCPP(Summit) | Meghnaghat (IEL) | Madanganj 102MW | Madanganj-55 MW | Siddhirganj CCPP-335 MW | Siddhirgonj ST 210MW | Siddhirgonj GT Unit-1& 2 | Siddhirganj Desh | Siddhirganj (Dutch Bangla) | Gagnagar (Orion) | Kodda 149MW | Keraniganj (Powerpac) 100MW | Bosila 108MW | Pagla (DPA ) | Katpotti 51 MW | Banco Energy 54MW | Northern 55 MW | Southern 55MW | Narshingdi (Doreen) | Summit Ashulia | Summit Madhabdi | Summit Maona | Summit Rupganj | Gazipur (RPCL) | Tongi GT | Kaptai Unit-1, 2 & 3 | Kaptai Unit-4 & 5 | Chattogram ST-1 (Raozan) | Chittgong ST-2 (Raozan) | Raozan 25 MW (RPCL) | Sikalbaha 225MW (Gas) | Sikalbaha 225MW (Oil) | Sikalbaha GT 150MW (Gas) | Sikalbaha GT 150MW (Oil) | Sikalbaha ST 60MW | Sikalbaha (Energis) | Hathazari peaking | Dohazari Peaking | Juldah (Acorn) | Chattogram ECPV 108 MW | Patenga 50MW | Barabkunda (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj ST: Unit- 3 | Ashuganj ST: Unit- 4 | Ashuganj ST: Unit- 5 | Ashuganj CCPP(North) | Ashuganj CCPP(South) | Ashuganj CCPP 225 MW | Ashuganj 195MW Modular | Chandpur CCPP | Ashuganj Engines TSK | Ashuganj (Precision) 55MW | Ashuganj (United) 53MW | Ashuganj (Midland) 51MW | B.Baria (Aggreko) 85MW | Daudkandi Peaking 52MW | Lakdhanvi 52 MW | Feni (Doreen) 22MW | Feni, Mohipal (Doreen) | Jangalia (Summit) 33MW | Summit Cumilla 25MW | Tripura | Mymensingh RPCL 210MW | Jamalpur 95MW | Tangail (Doreen) 22MW | Sarishabari (Solar) | Fenchugonj CCPP-1 | Fenchugonj CCPP-2 | Fenchugonj (Barakatullah) 51MW | Fenchuganj (EPL) 44MW | Kushiara 163 MW CCPP GT | Shajibazar 330 MW | Shahjibazar GT: Unit- 8, 9 | Shahjibazar 86MW | Shahjibazar (EPL) 50MW | Sylhet GT 150 MW | Sylhet GT 20 MW | Sylhet (EPL) 50MW | Sylhet (Desh) 10MW | Summit Bibiana- 2 | Shahjahanulla 25 MW | Hobiganj 11MW | Daudkandi bangla trak | Summit Gazipur -2 | APR Energy , Keranigonj | Bramhangoan 100 MW (Aggreko) | United Mymensingh PPL | Aggreko Aurahati 100MW | Summit Gazipur-1 150MW | Teknaf Solartech 20MW | Juldah 100 MW Unit-3 | Chandpur Desh 200MW | Midland 150MW | Bibiyana-3 285 MW | United Jamalpur PPL | Gazipur 100 MW | Baraka Sikalbaha PL | Kaptai Solar | Anwara United | EasternBlank | Bheramara (HVDC ) | Bheramara GT-1,2,3 | Bheramara 360 MW | Khulna (KPCL-1 & 3) | Khulna (KPCL-2) | Khulna CCPP 225MW | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur Peaking | Gopalganj Peaking | Noapara (KZA) 40MW | Bhola CCPP 194MW | Bhola (Venture) 33MW | Summit Barisal 110 MW | Barisal GT: Unit-1, 2 | Baghabari GT 100MW | Baghabari GT 71MW | Baghabari Peaking 50MW | Bera Peaking | Chapainawabganj-100 MW | Amnura 50MW | Katakhali (Northern) | Katakhali Peaking | Rajlanka 52 MW | Santahar Peaking | Bogra (GBB) | Bogra (EPL) | Ullapara (Summit) | Barapukuria Unit-1 | Barapukuria Unit-2 | Barapukuria Unit-3 | Rangpur GT | Saidpur GT | Sirajgonj Unit-1 225MW (Gas) | Sirajgonj Unit-1 225MW (Oil) | Sirajgonj Unit-2 225MW (Gas) | Sirajgonj Unit-2 225MW (Oil) | Bhola Aggreko 95MW | Bangla Trak Noapara | Sirajgonj Unit-3 225 MW(Gas) | Sirajgonj Unit-3 225 MW(Oil) | Sirajgonj Unit-4 414 MW(Gas) | Labon Chora 105 MW | Paramount Baghabari | Confidence Bogura-2 (CPBL) | Madhumati Power Plant | Confidence Rangpur | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 35 | 94 | 100 | 115 | 300 | 6 | 0 | 331 | 335 | 27 | 0 | 400 | 280 | 65 | 48 | 15 | 0 | 0 | 87 | 0 | 0 | 68 | 145 | 0 | 65 | 0 | 13 | 35 | 56 | 55 | 19 | 25 | 31 | 33 | 25 | 40 | 40 | 35 | 0 | 100 | 0 | 25 | 218 | 0 | 140 | 0 | 0 | 16 | 83 | 85 | 89 | 90 | 47 | 15 | 36 | 0 | 0 | 125 | 360 | 320 | 215 | 8 | 100 | 36 | 55 | 5 | 35 | 0 | 0 | 52 | 22 | 11 | 25 | 20 | 170 | 146 | 61 | 20 | 0 | 58 | 58 | 50 | 50 | 130 | 250 | 62 | 77 | 44 | 105 | 18 | 44 | 10 | 250 | 22 | 11 | 0 | 0 | 0 | 0 | 150 | 0 | 149 | 0 | 100 | 198 | 150 | 250 | 95 | 109 | 105 | 0 | 104 |  | 935 | 32 | 0 | 0 | 99 | 236 | 0 | 0 | 36 | 50 | 40 | 173 | 34 | 110 | 0 | 0 | 55 | 50 | 33 | 85 | 50 | 16 | 0 | 41 | 35 | 22 | 16 | 11 | 0 | 65 | 199 | 17 | 17 | 159 | 0 | 151 | 0 | 96 | 94 | 175 | 0 | 350 | 105 | 0 | 107 | 107 | 0 |  | 8302 | 3801 | 12103 | 4666 | 935 | 2053 | 3076 | 264 | 35 | 904 | 170 | 0 | 0 | 73.9
2:00 | 35 | 95 | 100 | 115 | 300 | 6 | 0 | 327 | 335 | 0 | 0 | 400 | 240 | 25 | 48 | 0 | 0 | 0 | 82 | 0 | 0 | 7 | 140 | 0 | 66 | 0 | 14 | 35 | 56 | 55 | 19 | 25 | 31 | 33 | 25 | 43 | 40 | 35 | 0 | 100 | 0 | 25 | 210 | 0 | 90 | 0 | 0 | 16 | 83 | 85 | 88 | 87 | 43 | 15 | 37 | 0 | 0 | 125 | 320 | 300 | 182 | 8 | 100 | 36 | 56 | 5 | 35 | 0 | 0 | 52 | 22 | 11 | 25 | 20 | 168 | 150 | 60 | 20 | 0 | 58 | 58 | 50 | 50 | 130 | 254 | 45 | 77 | 44 | 105 | 18 | 44 | 10 | 240 | 22 | 11 | 0 | 0 | 0 | 0 | 150 | 0 | 133 | 0 | 100 | 199 | 120 | 250 | 95 | 109 | 105 | 0 | 117 |  | 935 | 0 | 0 | 0 | 99 | 170 | 0 | 0 | 36 | 50 | 40 | 173 | 31 | 110 | 0 | 0 | 55 | 50 | 24 | 55 | 34 | 16 | 0 | 34 | 10 | 22 | 16 | 11 | 0 | 65 | 200 | 0 | 0 | 155 | 0 | 146 | 0 | 96 | 0 | 171 | 0 | 350 | 105 | 0 | 75 | 108 | 0 |  | 7900 | 3442 | 11342 | 4485 | 935 | 2042 | 2709 | 265 | 35 | 703 | 168 | 0 | 0 | 73.9
3:00 | 35 | 95 | 100 | 115 | 300 | 6 | 0 | 335 | 308 | 0 | 0 | 370 | 300 | 7 | 48 | 0 | 0 | 0 | 87 | 0 | 0 | 7 | 55 | 0 | 24 | 0 | 13 | 35 | 18 | 17 | 19 | 25 | 31 | 33 | 25 | 32 | 40 | 35 | 0 | 100 | 0 | 25 | 218 | 0 | 96 | 0 | 0 | 16 | 83 | 85 | 88 | 90 | 43 | 15 | 34 | 0 | 0 | 80 | 300 | 270 | 203 | 8 | 100 | 36 | 55 | 5 | 35 | 0 | 0 | 25 | 22 | 11 | 25 | 20 | 168 | 146 | 60 | 20 | 0 | 58 | 58 | 50 | 50 | 130 | 254 | 61 | 74 | 44 | 115 | 18 | 44 | 10 | 245 | 22 | 11 | 0 | 0 | 0 | 0 | 150 | 0 | 79 | 0 | 100 | 167 | 0 | 250 | 95 | 109 | 105 | 0 | 117 |  | 936 | 0 | 0 | 0 | 66 | 120 | 0 | 0 | 36 | 50 | 40 | 173 | 33 | 110 | 0 | 0 | 55 | 50 | 0 | 55 | 12 | 0 | 0 | 8 | 0 | 11 | 16 | 11 | 0 | 66 | 200 | 0 | 0 | 162 | 0 | 153 | 0 | 96 | 0 | 169 | 0 | 350 | 70 | 0 | 17 | 108 | 0 |  | 7413 | 3173 | 10586 | 4472 | 936 | 1974 | 2201 | 266 | 35 | 534 | 168 | 0 | 0 | 73.9
4:00 | 35 | 95 | 100 | 115 | 300 | 6 | 0 | 365 | 308 | 0 | 0 | 370 | 300 | 7 | 30 | 0 | 0 | 0 | 85 | 0 | 0 | 7 | 48 | 0 | 24 | 0 | 13 | 35 | 18 | 17 | 19 | 25 | 31 | 33 | 25 | 32 | 40 | 35 | 0 | 100 | 0 | 25 | 218 | 0 | 99 | 0 | 0 | 16 | 83 | 85 | 10 | 90 | 46 | 18 | 34 | 0 | 0 | 80 | 300 | 270 | 204 | 8 | 100 | 36 | 56 | 5 | 35 | 0 | 0 | 25 | 22 | 11 | 25 | 20 | 160 | 146 | 32 | 20 | 0 | 58 | 58 | 50 | 47 | 130 | 250 | 62 | 74 | 44 | 110 | 18 | 44 | 10 | 240 | 22 | 11 | 0 | 0 | 0 | 0 | 100 | 0 | 102 | 0 | 100 | 128 | 0 | 249 | 97 | 108 | 105 | 0 | 117 |  | 936 | 0 | 0 | 0 | 66 | 120 | 0 | 0 | 36 | 50 | 40 | 173 | 32 | 80 | 0 | 0 | 55 | 0 | 0 | 55 | 12 | 0 | 0 | 8 | 0 | 18 | 16 | 11 | 0 | 66 | 199 | 0 | 0 | 173 | 0 | 165 | 0 | 95 | 0 | 175 | 0 | 350 | 70 | 0 | 17 | 107 | 0 |  | 7231 | 3125 | 10356 | 4527 | 936 | 1972 | 1984 | 265 | 35 | 477 | 160 | 0 | 0 | 73.9
5:00 | 35 | 95 | 100 | 115 | 300 | 6 | 0 | 335 | 308 | 0 | 0 | 370 | 240 | 7 | 0 | 0 | 0 | 0 | 82 | 0 | 0 | 7 | 40 | 0 | 24 | 0 | 13 | 35 | 18 | 17 | 19 | 25 | 31 | 33 | 25 | 32 | 40 | 35 | 0 | 100 | 0 | 25 | 217 | 0 | 90 | 0 | 0 | 16 | 42 | 63 | 10 | 90 | 47 | 18 | 0 | 0 | 0 | 80 | 300 | 270 | 182 | 8 | 100 | 36 | 55 | 5 | 35 | 0 | 0 | 25 | 22 | 11 | 25 | 20 | 150 | 155 | 32 | 20 | 0 | 58 | 58 | 50 | 47 | 130 | 248 | 64 | 74 | 45 | 110 | 18 | 44 | 10 | 240 | 22 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 51 | 0 | 100 | 129 | 0 | 249 | 97 | 108 | 105 | 0 | 117 |  | 936 | 0 | 0 | 0 | 32 | 120 | 0 | 0 | 6 | 0 | 40 | 173 | 33 | 32 | 0 | 0 | 60 | 0 | 0 | 32 | 12 | 0 | 0 | 8 | 0 | 16 | 16 | 11 | 0 | 67 | 199 | 0 | 0 | 162 | 0 | 152 | 0 | 95 | 0 | 174 | 0 | 350 | 70 | 0 | 17 | 108 | 0 |  | 6828 | 2921 | 9749 | 4451 | 936 | 1937 | 1671 | 266 | 35 | 303 | 150 | 0 | 0 | 73.9
6:00 | 35 | 95 | 100 | 115 | 250 | 6 | 0 | 330 | 309 | 0 | 0 | 370 | 280 | 7 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 7 | 15 | 0 | 24 | 0 | 14 | 35 | 18 | 17 | 19 | 25 | 31 | 33 | 25 | 16 | 40 | 36 | 0 | 100 | 0 | 8 | 218 | 0 | 90 | 0 | 0 | 16 | 0 | 34 | 10 | 71 | 47 | 18 | 20 | 0 | 0 | 80 | 300 | 270 | 182 | 8 | 100 | 36 | 55 | 5 | 10 | 0 | 0 | 25 | 22 | 11 | 25 | 20 | 138 | 155 | 8 | 20 | 0 | 58 | 58 | 11 | 10 | 130 | 250 | 63 | 10 | 45 | 108 | 18 | 10 | 10 | 230 | 22 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 15 | 1.5 | 100 | 124 | 0 | 199 | 97 | 108 | 105 | 0 | 110 |  | 936 | 0 | 0 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 16 | 173 | 27 | 16 | 0 | 0 | 60 | 0 | 0 | 16 | 12 | 0 | 0 | 8 | 0 | 5 | 12 | 8 | 0 | 67 | 199 | 0 | 0 | 157 | 0 | 145 | 0 | 97 | 0 | 165 | 0 | 350 | 35 | 0 | 17 | 53 | 0 |  | 6296.5 | 2710 | 9006.5 | 4272 | 936 | 1730 | 1442 | 266 | 36 | 185 | 138 | 1.5 | 0 | 73.9
7:00 | 35 | 95 | 100 | 115 | 250 | 6 | 0 | 335 | 278 | 0 | 0 | 350 | 290 | 7 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 7 | 15 | 0 | 24 | 0 | 13 | 35 | 18 | 17 | 19 | 25 | 31 | 33 | 25 | 16 | 40 | 36 | 0 | 100 | 0 | 8 | 195 | 0 | 90 | 0 | 0 | 16 | 0 | 17 | 10 | 18 | 47 | 18 | 6 | 0 | 0 | 80 | 270 | 270 | 202 | 8 | 100 | 36 | 20 | 5 | 10 | 0 | 0 | 25 | 22 | 11 | 25 | 20 | 132 | 151 | 8 | 20 | 0 | 50 | 58 | 11 | 10 | 100 | 252 | 62 | 10 | 10 | 121 | 18 | 0 | 10 | 240 | 22 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 15 | 3.9 | 100 | 90 | 0 | 201 | 42 | 72 | 70 | 1.6 | 116 |  | 936 | 0 | 0 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 16 | 176 | 23 | 16 | 0 | 0 | 60 | 0 | 0 | 16 | 12 | 0 | 0 | 8 | 0 | 5 | 3 | 8 | 0 | 67 | 199 | 0 | 0 | 160 | 0 | 145 | 0 | 97 | 0 | 167 | 0 | 350 | 35 | 0 | 17 | 54 | 0 |  | 5893.5 | 2706 | 8599.5 | 4259 | 936 | 1552 | 1245 | 266 | 36 | 168 | 132 | 5.5 | 0 | 73.91
8:00 | 35 | 95 | 100 | 115 | 250 | 6 | 0 | 349 | 278 | 0 | 0 | 350 | 285 | 7 | 2 | 0 | 0 | 0 | 60 | 0 | 0 | 7 | 15 | 0 | 24 | 0 | 13 | 35 | 36 | 17 | 19 | 25 | 31 | 0 | 25 | 24 | 40 | 36 | 0 | 100 | 0 | 8 | 0 | 229 | 90 | 0 | 0 | 16 | 0 | 17 | 10 | 20 | 47 | 18 | 6 | 0 | 0 | 80 | 270 | 270 | 190 | 8 | 100 | 30 | 20 | 5 | 10 | 0 | 0 | 25 | 22 | 11 | 25 | 20 | 136 | 151 | 8 | 20 | 0 | 59 | 58 | 11 | 10 | 100 | 250 | 63 | 10 | 45 | 113 | 19 | 43 | 10 | 250 | 16 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 15 | 10.5 | 100 | 88 | 0 | 200 | 45 | 80 | 70 | 2.8 | 116 |  | 937 | 0 | 0 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 16 | 173 | 20 | 16 | 0 | 0 | 60 | 0 | 0 | 16 | 12 | 0 | 0 | 8 | 0 | 5 | 3 | 8 | 0 | 66 | 199 | 0 | 0 | 171 | 0 | 161 | 0 | 95 | 0 | 175 | 0 | 350 | 35 | 0 | 17 | 53 | 0 |  | 6043.3 | 2732 | 8775.3 | 4078 | 937 | 1635 | 1278 | 265 | 36 | 397 | 136 | 13.3 | 0 | 73.85
9:00 | 35 | 96 | 100 | 115 | 260 | 6 | 0 | 342 | 330 | 0 | 0 | 400 | 305 | 7 | 15 | 0 | 0 | 0 | 60 | 0 | 0 | 7 | 15 | 0 | 24 | 0 | 13 | 35 | 37 | 17 | 16 | 25 | 31 | 25 | 25 | 32 | 40 | 36 | 0 | 100 | 0 | 8 | 0 | 229 | 140 | 0 | 0 | 16 | 0 | 17 | 10 | 50 | 40 | 18 | 3 | 0 | 0 | 80 | 270 | 270 | 206 | 8 | 100 | 27 | 49 | 5 | 10 | 0 | 0 | 25 | 22 | 11 | 25 | 20 | 134 | 145 | 8 | 20 | 1.6 | 55 | 58 | 11 | 10 | 100 | 253 | 63 | 10 | 44 | 123 | 19 | 43 | 10 | 260 | 16 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 44 | 11.7 | 100 | 88 | 0 | 200 | 45 | 109 | 109 | 4 | 116 |  | 936 | 0 | 0 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 16 | 173 | 18 | 16 | 0 | 0 | 55 | 0 | 0 | 16 | 12 | 0 | 0 | 8 | 0 | 18 | 3 | 5 | 0 | 67 | 199 | 0 | 0 | 167 | 0 | 158 | 0 | 95 | 0 | 175 | 0 | 350 | 35 | 0 | 17 | 53 | 0 |  | 6436.3 | 2728 | 9164.3 | 4155 | 936 | 1783 | 1440 | 266 | 36 | 397 | 134 | 17.3 | 0 | 73.85
10:00 | 35 | 94 | 100 | 115 | 300 | 6 | 0 | 354 | 329 | 26 | 0 | 400 | 260 | 7 | 15 | 0 | 0 | 0 | 95 | 0 | 8 | 15 | 15 | 0 | 57 | 0 | 8 | 35 | 56 | 20 | 16 | 25 | 31 | 0 | 25 | 34 | 40 | 35 | 0 | 100 | 0 | 8 | 0 | 229 | 130 | 0 | 0 | 16 | 0 | 17 | 10 | 63 | 28 | 18 | 2 | 0 | 0 | 80 | 320 | 320 | 183 | 8 | 100 | 27 | 51 | 5 | 10 | 0 | 0 | 36 | 22 | 11 | 25 | 20 | 136 | 147 | 8 | 20 | 2 | 55 | 58 | 11 | 36 | 100 | 253 | 59 | 50 | 43 | 108 | 19 | 43 | 10 | 265 | 16 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 46 | 9.3 | 100 | 108 | 0 | 295 | 85 | 109 | 105 | 4.8 | 133 |  | 937 | 0 | 0 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 16 | 173 | 17 | 16 | 0 | 0 | 55 | 0 | 0 | 16 | 12 | 0 | 0 | 8 | 0 | 18 | 10 | 5 | 0 | 67 | 199 | 0 | 0 | 197 | 0 | 161 | 0 | 92 | 0 | 175 | 0 | 350 | 35 | 0 | 26 | 54 | 0 |  | 6847.1 | 2775 | 9622.1 | 4393 | 937 | 1856 | 1586 | 266 | 35 | 397 | 136 | 16.1 | 0 | 73.86
11:00 | 35 | 94 | 102 | 115 | 300 | 6 | 0 | 328 | 329 | 26 | 0 | 400 | 270 | 7 | 30 | 44 | 0 | 0 | 94 | 0 | 50 | 65 | 15 | 0 | 62 | 0 | 6 | 35 | 56 | 55 | 16 | 25 | 32 | 33 | 25 | 40 | 40 | 35 | 0 | 100 | 0 | 21 | 0 | 224 | 130 | 0 | 0 | 16 | 0 | 17 | 10 | 83 | 41 | 18 | 2 | 0 | 0 | 80 | 320 | 320 | 184 | 8 | 100 | 29 | 53 | 5 | 10 | 0 | 0 | 52 | 21 | 11 | 25 | 20 | 150 | 147 | 8 | 20 | 2.2 | 56 | 58 | 11 | 44 | 100 | 253 | 61 | 50 | 43 | 108 | 18 | 43 | 10 | 250 | 16 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 46 | 19.4 | 100 | 140 | 0 | 291 | 85 | 109 | 105 | 5.3 | 118 |  | 936 | 0 | 0 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 16 | 173 | 19 | 16 | 0 | 0 | 55 | 0 | 0 | 0 | 12 | 0 | 0 | 8 | 0 | 18 | 14 | 8 | 0 | 67 | 199 | 0 | 0 | 201 | 0 | 146 | 0 | 92 | 0 | 174 | 0 | 350 | 35 | 0 | 53 | 53 | 0 |  | 7154.9 | 2781 | 9935.9 | 4393 | 936 | 1857 | 1896 | 266 | 35 | 376 | 150 | 26.9 | 0 | 73.86
12:00 | 35 | 94 | 98 | 115 | 300 | 6 | 0 | 346 | 336 | 26 | 0 | 400 | 295 | 7 | 30 | 55 | 0 | 0 | 90 | 0 | 85 | 100 | 15 | 0 | 63 | 0 | 6 | 35 | 56 | 55 | 16 | 25 | 31 | 33 | 25 | 40 | 40 | 34 | 0 | 100 | 0 | 24 | 125 | 0 | 142 | 0 | 0 | 16 | 0 | 17 | 10 | 83 | 46 | 18 | 2 | 0 | 0 | 80 | 320 | 320 | 206 | 8 | 100 | 33 | 52 | 5 | 10 | 0 | 0 | 52 | 20 | 11 | 25 | 20 | 138 | 145 | 8 | 20 | 0.8 | 55 | 58 | 34 | 44 | 100 | 248 | 59 | 75 | 43 | 122 | 18 | 43 | 10 | 280 | 23 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 46 | 19.6 | 100 | 146 | 0 | 283 | 96 | 109 | 105 | 5.4 | 135 |  | 936 | 0 | 0 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 0 | 174 | 22 | 16 | 0 | 0 | 55 | 0 | 0 | 0 | 12 | 0 | 0 | 8 | 0 | 21 | 13 | 8 | 0 | 67 | 200 | 0 | 0 | 196 | 0 | 160 | 0 | 92 | 0 | 175 | 0 | 350 | 35 | 0 | 53 | 53 | 4 |  | 7323.8 | 2786 | 10109.8 | 4578 | 936 | 1946 | 2033 | 267 | 34 | 152 | 138 | 25.8 | 0 | 73.86
13:00 | 35 | 94 | 100 | 115 | 300 | 6 | 0 | 338 | 337 | 26 | 0 | 400 | 270 | 7 | 30 | 55 | 0 | 0 | 92 | 0 | 89 | 100 | 62 | 0 | 63 | 0 | 6 | 35 | 56 | 55 | 16 | 25 | 31 | 33 | 25 | 40 | 40 | 33 | 0 | 100 | 0 | 24 | 126 | 0 | 130 | 0 | 0 | 24 | 0 | 17 | 10 | 83 | 46 | 18 | 7 | 0 | 0 | 80 | 360 | 300 | 147 | 8 | 95 | 0 | 53 | 5 | 35 | 0 | 0 | 52 | 20 | 11 | 25 | 20 | 142 | 144 | 48 | 20 | 2.2 | 55 | 0 | 47 | 41 | 100 | 246 | 60 | 71 | 43 | 109 | 18 | 44 | 10 | 275 | 23 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 46 | 18.8 | 100 | 170 | 63 | 287 | 95 | 109 | 105 | 4.7 | 125 |  | 936 | 0 | 0 | 0 | 32 | 120 | 0 | 0 | 0 | 0 | 16 | 174 | 17 | 16 | 0 | 0 | 55 | 0 | 0 | 0 | 12 | 0 | 0 | 24 | 0 | 21 | 13 | 8 | 0 | 65 | 200 | 0 | 0 | 189 | 0 | 198 | 0 | 92 | 0 | 190 | 0 | 411 | 105 | 0 | 75 | 107 | 0 |  | 7349.7 | 3076 | 10425.7 | 4463 | 936 | 2036 | 2326 | 265 | 33 | 199 | 142 | 25.7 | 0 | 73.87
14:00 | 35 | 94 | 100 | 115 | 300 | 102 | 0 | 348 | 336 | 26 | 0 | 420 | 200 | 7 | 30 | 55 | 0 | 0 | 52 | 0 | 95 | 99 | 62 | 0 | 62 | 0 | 6 | 35 | 56 | 55 | 19 | 25 | 30 | 33 | 25 | 39 | 40 | 33 | 0 | 100 | 0 | 24 | 227 | 0 | 131 | 0 | 0 | 24 | 0 | 17 | 50 | 83 | 46 | 18 | 2 | 0 | 0 | 80 | 360 | 345 | 182 | 8 | 95 | 0 | 53 | 5 | 35 | 0 | 0 | 52 | 19 | 11 | 25 | 20 | 172 | 147 | 60 | 20 | 1.9 | 53 | 0 | 50 | 47 | 130 | 251 | 61 | 74 | 44 | 108 | 18 | 44 | 10 | 260 | 16 | 8 | 0 | 0 | 0 | 0 | 14 | 0 | 46 | 16.2 | 100 | 200 | 125 | 290 | 95 | 109 | 105 | 0 | 130 |  | 936 | 0 | 0 | 0 | 40 | 120 | 0 | 0 | 0 | 0 | 24 | 173 | 26 | 16 | 0 | 0 | 55 | 0 | 0 | 0 | 35 | 0 | 0 | 37 | 0 | 21 | 16 | 5 | 0 | 64 | 200 | 0 | 0 | 193 | 0 | 192 | 0 | 92 | 0 | 207 | 0 | 412 | 105 | 0 | 90 | 107 | 0 |  | 7751.1 | 3166 | 10917.1 | 4626 | 936 | 2187 | 2482 | 264 | 33 | 199 | 172 | 18.1 | 0 | 73.87
15:00 | 35 | 94 | 100 | 115 | 280 | 102 | 20 | 328 | 338 | 26 | 0 | 420 | 295 | 7 | 30 | 55 | 0 | 0 | 57 | 0 | 98 | 99 | 62 | 0 | 60 | 0 | 6 | 35 | 0 | 55 | 19 | 25 | 30 | 33 | 25 | 39 | 40 | 34 | 0 | 100 | 0 | 24 | 226 | 0 | 131 | 0 | 0 | 24 | 0 | 16 | 78 | 88 | 46 | 18 | 2 | 0 | 0 | 80 | 320 | 320 | 182 | 8 | 96 | 0 | 52 | 5 | 35 | 0 | 0 | 52 | 19 | 11 | 25 | 20 | 170 | 144 | 80 | 20 | 1.1 | 53 | 0 | 50 | 46 | 163 | 250 | 61 | 74 | 44 | 110 | 18 | 43 | 10 | 250 | 23 | 8 | 0 | 0 | 0 | 0 | 40 | 0 | 83 | 12.8 | 100 | 200 | 130 | 287 | 93 | 108 | 105 | 0 | 132 |  | 936 | 0 | 0 | 0 | 66 | 120 | 0 | 0 | 0 | 0 | 40 | 173 | 28 | 16 | 0 | 0 | 55 | 0 | 0 | 0 | 50 | 16 | 0 | 48 | 0 | 21 | 16 | 5 | 0 | 65 | 199 | 0 | 0 | 182 | 0 | 179 | 0 | 93 | 0 | 206 | 0 | 370 | 105 | 0 | 90 | 107 | 14 |  | 7848.9 | 3200 | 11048.9 | 4503 | 936 | 2190 | 2740 | 264 | 34 | 198 | 170 | 13.9 | 0 | 73.87
16:00 | 35 | 94 | 100 | 115 | 280 | 108 | 40 | 329 | 336 | 26 | 0 | 420 | 280 | 7 | 30 | 30 | 0 | 0 | 57 | 0 | 85 | 65 | 60 | 0 | 60 | 0 | 6 | 35 | 56 | 55 | 19 | 25 | 31 | 33 | 25 | 39 | 40 | 34 | 0 | 100 | 0 | 24 | 225 | 0 | 132 | 0 | 0 | 24 | 0 | 16 | 50 | 83 | 46 | 18 | 8 | 0 | 0 | 80 | 320 | 320 | 183 | 8 | 100 | 0 | 52 | 5 | 35 | 0 | 0 | 50 | 20 | 11 | 24 | 20 | 164 | 144 | 92 | 20 | 0.4 | 53 | 0 | 52 | 49 | 163 | 248 | 58 | 76 | 44 | 108 | 18 | 44 | 10 | 270 | 23 | 8 | 0 | 0 | 0 | 0 | 48 | 0 | 93 | 8.4 | 100 | 200 | 135 | 288 | 93 | 108 | 105 | 2.3 | 135 |  | 936 | 0 | 0 | 0 | 32 | 120 | 0 | 0 | 0 | 13 | 40 | 173 | 28 | 16 | 0 | 0 | 55 | 0 | 0 | 0 | 50 | 16 | 0 | 48 | 0 | 22 | 16 | 5 | 0 | 66 | 199 | 0 | 0 | 185 | 0 | 182 | 0 | 93 | 0 | 204 | 0 | 370 | 105 | 0 | 90 | 107 | 14 |  | 7869.1 | 3185 | 11054.1 | 4508 | 936 | 2249 | 2678 | 265 | 34 | 209 | 164 | 11.1 | 0 | 73.88
17:00 | 35 | 94 | 100 | 115 | 280 | 105 | 50 | 328 | 337 | 26 | 0 | 420 | 260 | 7 | 30 | 15 | 0 | 0 | 55 | 0 | 60 | 32 | 30 | 0 | 60 | 0 | 8 | 35 | 56 | 55 | 19 | 25 | 31 | 33 | 25 | 42 | 40 | 34 | 0 | 100 | 0 | 24 | 228 | 0 | 130 | 0 | 0 | 24 | 0 | 16 | 50 | 90 | 45 | 18 | 3 | 0 | 0 | 80 | 320 | 320 | 182 | 8 | 96 | 0 | 52 | 5 | 35 | 0 | 0 | 52 | 20 | 11 | 24 | 20 | 154 | 145 | 50 | 20 | 0.3 | 53 | 0 | 49 | 49 | 163 | 247 | 61 | 77 | 44 | 108 | 18 | 44 | 10 | 260 | 23 | 8 | 0 | 0 | 0 | 0 | 27 | 0 | 70 | 3.4 | 100 | 200 | 80 | 251 | 93 | 108 | 105 | 0.9 | 135 |  | 936 | 0 | 0 | 0 | 32 | 120 | 0 | 0 | 0 | 40 | 40 | 173 | 28 | 16 | 0 | 0 | 55 | 0 | 0 | 0 | 50 | 16 | 0 | 24 | 0 | 22 | 16 | 8 | 0 | 65 | 199 | 0 | 0 | 182 | 0 | 179 | 0 | 95 | 0 | 200 | 0 | 370 | 105 | 0 | 90 | 107 | 6 |  | 7551.6 | 3174 | 10725.6 | 4460 | 936 | 2242 | 2425 | 264 | 34 | 206 | 154 | 4.6 | 0 | 73.88
18:00 | 35 | 94 | 100 | 115 | 280 | 62 | 50 | 328 | 318 | 26 | 0 | 370 | 255 | 7 | 30 | 15 | 0 | 0 | 50 | 0 | 50 | 32 | 30 | 0 | 60 | 0 | 8 | 35 | 56 | 55 | 19 | 25 | 31 | 33 | 25 | 47 | 40 | 35 | 0 | 100 | 0 | 24 | 229 | 0 | 130 | 0 | 0 | 24 | 0 | 16 | 50 | 90 | 46 | 18 | 3 | 0 | 0 | 80 | 290 | 280 | 182 | 8 | 96 | 0 | 53 | 5 | 35 | 0 | 0 | 52 | 20 | 11 | 24 | 20 | 154 | 147 | 50 | 20 | 0 | 55 | 0 | 25 | 20 | 130 | 252 | 61 | 40 | 20 | 109 | 18 | 22 | 10 | 250 | 23 | 11 | 0 | 0 | 0 | 0 | 27 | 0 | 67 | 0 | 100 | 200 | 80 | 200 | 94 | 108 | 105 | 0 | 122 |  | 936 | 0 | 0 | 0 | 32 | 120 | 0 | 0 | 36 | 43 | 16 | 173 | 27 | 16 | 0 | 0 | 55 | 0 | 0 | 0 | 50 | 16 | 0 | 24 | 0 | 22 | 16 | 8 | 0 | 65 | 199 | 0 | 0 | 181 | 0 | 179 | 0 | 54 | 0 | 199 | 0 | 300 | 65 | 0 | 101 | 107 | 52 |  | 7122 | 3092 | 10214 | 4346 | 936 | 1840 | 2394 | 264 | 35 | 245 | 154 | 0 | 0 | 73.88
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 35 | 95 | 100 | 115 | 260 | 62 | 50 | 335 | 289 | 55 | 0 | 350 | 265 | 20 | 30 | 22 | 0 | 0 | 57 | 0 | 55 | 50 | 100 | 16 | 60 | 0 | 14 | 35 | 56 | 55 | 0 | 25 | 18 | 33 | 25 | 48 | 40 | 35 | 0 | 100 | 0 | 24 | 224 | 0 | 130 | 0 | 0 | 24 | 43 | 85 | 78 | 90 | 46 | 18 | 28 | 0 | 0 | 0 | 250 | 240 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 27 | 52 | 21 | 11 | 25 | 20 | 182 | 147 | 72 | 20 | 0 | 55 | 0 | 50 | 41 | 130 | 251 | 61 | 70 | 20 | 109 | 18 | 45 | 10 | 250 | 23 | 11 | 10 | 65 | 107 | 10 | 58 | 11 | 72 | 0 | 100 | 200 | 0 | 201 | 95 | 108 | 105 | 0 | 132 |  | 939 | 16 | 0 | 0 | 115 | 150 | 0 | 0 | 34 | 72 | 40 | 173 | 38 | 64 | 0 | 0 | 55 | 42 | 5 | 70 | 50 | 16 | 44 | 50 | 31 | 22 | 16 | 11 | 0 | 67 | 199 | 17 | 18 | 185 | 0 | 194 | 0 | 94 | 13 | 203 | 0 | 272 | 105 | 0 | 108 | 108 | 51 |  | 7280 | 3687 | 10967 | 3994 | 939 | 1837 | 2960 | 266 | 35 | 754 | 182 | 0 | 0 | 73.89
19:30 | 35 | 94 | 100 | 115 | 260 | 62 | 50 | 350 | 290 | 86 | 0 | 380 | 210 | 50 | 42 | 55 | 0 | 0 | 90 | 0 | 70 | 100 | 140 | 70 | 61 | 0 | 14 | 35 | 56 | 55 | 0 | 25 | 18 | 33 | 25 | 48 | 40 | 35 | 0 | 100 | 0 | 25 | 224 | 0 | 129 | 0 | 0 | 24 | 74 | 85 | 78 | 90 | 46 | 19 | 24 | 0 | 0 | 0 | 250 | 240 | 0 | 0 | 95 | 0 | 0 | 0 | 0 | 0 | 50 | 52 | 21 | 11 | 25 | 20 | 184 | 145 | 93 | 20 | 0 | 55 | 0 | 50 | 50 | 163 | 249 | 63 | 77 | 45 | 108 | 18 | 46 | 10 | 240 | 23 | 11 | 150 | 150 | 213 | 51 | 100 | 103 | 149 | 0 | 100 | 200 | 0 | 249 | 95 | 108 | 105 | 0 | 137 |  | 939 | 16 | 0 | 0 | 115 | 180 | 0 | 0 | 34 | 64 | 40 | 173 | 39 | 105 | 10 | 0 | 60 | 50 | 12 | 95 | 50 | 34 | 45 | 50 | 35 | 22 | 16 | 11 | 0 | 67 | 199 | 17 | 18 | 189 | 0 | 194 | 0 | 95 | 80 | 200 | 0 | 320 | 95 | 0 | 108 | 108 | 0 |  | 8336 | 3885 | 12221 | 4087 | 939 | 1979 | 3806 | 266 | 35 | 925 | 184 | 0 | 0 | 73.89
20:00 | 35 | 94 | 100 | 115 | 250 | 22 | 20 | 333 | 288 | 110 | 0 | 380 | 235 | 75 | 55 | 55 | 0 | 0 | 27 | 0 | 94 | 99 | 140 | 73 | 63 | 0 | 17 | 35 | 56 | 55 | 0 | 25 | 27 | 33 | 25 | 48 | 40 | 36 | 0 | 100 | 0 | 25 | 231 | 0 | 130 | 0 | 0 | 24 | 76 | 85 | 78 | 90 | 46 | 19 | 26 | 0 | 0 | 0 | 250 | 220 | 0 | 0 | 95 | 0 | 0 | 0 | 0 | 0 | 50 | 52 | 22 | 11 | 25 | 20 | 180 | 149 | 93 | 20 | 0 | 55 | 0 | 50 | 50 | 163 | 249 | 63 | 77 | 45 | 134 | 18 | 46 | 10 | 240 | 23 | 11 | 150 | 213 | 175 | 51 | 110 | 104 | 149 | 0 | 100 | 200 | 0 | 249 | 95 | 108 | 105 | 0 | 135 |  | 939 | 16 | 0 | 0 | 115 | 220 | 0 | 0 | 32 | 50 | 40 | 173 | 39 | 110 | 12 | 0 | 55 | 50 | 33 | 95 | 50 | 50 | 47 | 50 | 36 | 22 | 16 | 11 | 0 | 68 | 199 | 17 | 17 | 185 | 0 | 190 | 0 | 97 | 82 | 200 | 0 | 291 | 90 | 0 | 108 | 107 | 0 |  | 8355 | 3912 | 12267 | 4012 | 939 | 1882 | 3975 | 267 | 36 | 976 | 180 | 0 | 0 | 73.89
21:00 | 35 | 94 | 100 | 115 | 240 | 22 | 20 | 329 | 320 | 110 | 0 | 340 | 275 | 100 | 80 | 55 | 0 | 0 | 87 | 0 | 100 | 100 | 140 | 88 | 63 | 0 | 49 | 35 | 56 | 55 | 19 | 25 | 32 | 33 | 25 | 48 | 40 | 36 | 0 | 100 | 0 | 16 | 230 | 0 | 130 | 0 | 0 | 24 | 83 | 85 | 86 | 90 | 47 | 19 | 26 | 0 | 0 | 0 | 220 | 220 | 0 | 8 | 100 | 0 | 0 | 0 | 0 | 0 | 50 | 52 | 22 | 11 | 25 | 20 | 190 | 147 | 94 | 20 | 0 | 55 | 40 | 50 | 50 | 163 | 250 | 61 | 77 | 45 | 112 | 18 | 46 | 10 | 260 | 23 | 11 | 150 | 300 | 107 | 51 | 122 | 53 | 149 | 0 | 100 | 200 | 0 | 250 | 95 | 108 | 105 | 0 | 132 |  | 939 | 48 | 0 | 0 | 115 | 233 | 0 | 0 | 32 | 52 | 40 | 173 | 40 | 110 | 12 | 0 | 55 | 50 | 33 | 95 | 0 | 50 | 44 | 50 | 34 | 22 | 16 | 11 | 0 | 68 | 200 | 17 | 17 | 184 | 0 | 174 | 0 | 97 | 97 | 192 | 0 | 350 | 90 | 0 | 108 | 107 | 0 |  | 8574 | 3955 | 12529 | 4047 | 939 | 1962 | 4062 | 268 | 36 | 1025 | 190 | 0 | 0 | 73.89
22:00 | 35 | 94 | 100 | 115 | 250 | 22 | 20 | 328 | 300 | 110 | 0 | 340 | 246 | 100 | 81 | 55 | 0 | 0 | 82 | 0 | 100 | 100 | 140 | 88 | 63 | 0 | 49 | 35 | 56 | 55 | 19 | 25 | 31 | 33 | 25 | 48 | 40 | 36 | 0 | 100 | 0 | 25 | 231 | 0 | 130 | 0 | 0 | 24 | 83 | 71 | 90 | 90 | 46 | 19 | 30 | 0 | 0 | 0 | 220 | 220 | 0 | 8 | 95 | 0 | 25 | 5 | 12 | 0 | 50 | 52 | 22 | 11 | 25 | 20 | 186 | 147 | 94 | 20 | 0 | 55 | 40 | 50 | 50 | 163 | 247 | 63 | 77 | 45 | 108 | 18 | 46 | 10 | 265 | 23 | 11 | 150 | 301 | 106 | 51 | 163 | 52 | 149 | 0 | 100 | 198 | 15 | 250 | 95 | 108 | 105 | 0 | 132 |  | 939 | 48 | 0 | 0 | 115 | 235 | 0 | 0 | 32 | 52 | 40 | 173 | 38 | 110 | 24 | 0 | 55 | 50 | 33 | 90 | 18 | 24 | 44 | 50 | 35 | 22 | 16 | 11 | 0 | 68 | 199 | 17 | 17 | 183 | 0 | 181 | 0 | 97 | 96 | 196 | 0 | 350 | 90 | 0 | 108 | 107 | 0 |  | 8618 | 3963 | 12581 | 4051 | 939 | 1991 | 4090 | 267 | 36 | 1021 | 186 | 0 | 0 | 73.92
23:00 | 35 | 94 | 100 | 115 | 250 | 21 | 20 | 327 | 300 | 55 | 0 | 340 | 265 | 85 | 30 | 55 | 0 | 0 | 83 | 0 | 100 | 100 | 144 | 50 | 64 | 0 | 49 | 35 | 56 | 55 | 22 | 25 | 30 | 33 | 25 | 48 | 40 | 36 | 0 | 100 | 0 | 25 | 231 | 0 | 130 | 0 | 0 | 24 | 83 | 80 | 82 | 90 | 46 | 19 | 37 | 0 | 0 | 0 | 220 | 220 | 110 | 8 | 100 | 0 | 44 | 5 | 7 | 0 | 50 | 52 | 22 | 11 | 25 | 20 | 180 | 148 | 94 | 20 | 0 | 55 | 40 | 50 | 50 | 130 | 250 | 58 | 78 | 45 | 109 | 18 | 47 | 10 | 250 | 24 | 11 | 120 | 200 | 0 | 0 | 170 | 0 | 149 | 0 | 100 | 196 | 60 | 248 | 95 | 106 | 105 | 0 | 150 |  | 939 | 32 | 0 | 0 | 115 | 200 | 0 | 0 | 32 | 52 | 40 | 173 | 38 | 110 | 12 | 0 | 60 | 50 | 33 | 30 | 0 | 8 | 0 | 8 | 35 | 22 | 17 | 11 | 0 | 68 | 199 | 17 | 17 | 179 | 0 | 178 | 0 | 97 | 96 | 198 | 0 | 300 | 90 | 0 | 108 | 107 | 0 |  | 8294 | 3671 | 11965 | 4167 | 939 | 1916 | 3593 | 267 | 36 | 867 | 180 | 0 | 0 | 73.92
24:00 | 35 | 94 | 100 | 115 | 250 | 22 | 20 | 328 | 300 | 13 | 0 | 340 | 285 | 40 | 30 | 55 | 0 | 0 | 87 | 0 | 40 | 100 | 144 | 10 | 64 | 0 | 49 | 35 | 56 | 55 | 22 | 25 | 30 | 33 | 16 | 48 | 40 | 34 | 0 | 100 | 0 | 25 | 232 | 0 | 90 | 0 | 0 | 16 | 0 | 80 | 84 | 90 | 46 | 19 | 38 | 0 | 0 | 0 | 220 | 220 | 100 | 8 | 100 | 0 | 48 | 5 | 7 | 0 | 50 | 52 | 22 | 11 | 25 | 20 | 174 | 148 | 94 | 20 | 0 | 58 | 40 | 50 | 50 | 130 | 250 | 58 | 78 | 45 | 112 | 18 | 47 | 10 | 250 | 24 | 11 | 120 | 95 | 0 | 0 | 180 | 0 | 149 | 0 | 100 | 196 | 6 | 249 | 95 | 106 | 105 | 0 | 150 |  | 940 | 32 | 0 | 0 | 115 | 125 | 0 | 0 | 32 | 52 | 40 | 173 | 37 | 110 | 12 | 0 | 55 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 22 | 17 | 0 | 0 | 67 | 199 | 17 | 17 | 181 | 0 | 179 | 0 | 97 | 30 | 198 | 0 | 300 | 90 | 0 | 107 | 107 | 0 |  | 7841 | 3436 | 11277 | 4108 | 940 | 1921 | 3188 | 266 | 34 | 646 | 174 | 0 | 0 | 73.92
KWH | 680000 | 2411200 | 2404000 | 2772000 | 6670063 | 682681 | 373184 | 8163330 | 7544000 | 773700 | 0 | 8963000 | 6595229 | 696960 | 879096 | 708414 | 0 | 0 | 1828000 | 0 | 1186560 | 1361952 | 1603680 | 359598 | 1204800 | 0 | 425414 | 867240 | 1025760 | 1041566 | 388440 | 600000 | 690480 | 647000 | 592300 | 915240 | 985874 | 786960 | 0 | 2300000 | 0 | 494908 | 5014360 | 0 | 2865060 | 0 | 0 | 501600 | 773128 | 1109745 | 1106760 | 1896960 | 1076160 | 417168 | 402720 | 0 | 0 | 1602880 | 7483500 | 6925500 | 3658000 | 184000 | 2317710 | 404640 | 1027680 | 105000 | 535160 | 0 | 249256 | 1070712 | 501048 | 257220 | 619900 | 512370 | 3843840 | 3458760 | 1254720 | 450684 | 11000 | 1329000 | 889040 | 925800 | 1000800 | 3296381 | 5634000 | 1445088 | 1429440 | 945000 | 2782340 | 438000 | 978340 | 239400 | 6245250 | 510456 | 252624 | 675840 | 1319781 | 436195 | 162719 | 1716000 | 223242 | 2005920 | 136890 | 2449920 | 3983520 | 1115709 | 6019000 | 2074800 | 2528232 | 2443843 | 36648 | 3008400 |  | 22473454 | 227300 | 0 | 0 | 1355520 | 3662400 | 0 | 0 | 372000 | 593920 | 696750 | 4216060 | 693636 | 1299840 | 66665 | 0 | 1350000 | 418376 | 210254 | 799616 | 618660 | 241180 | 158895 | 567840 | 256995 | 425760 | 317592 | 217100 | 0 | 1575709 | 4876300 | 119000 | 129000 | 4554682 | 0 | 4242536 | 0 | 2241723 | 591360 | 4683636 | 0 | 8447270 | 1800000 | 0 | 1677792 | 2223648 | 429120 |  | 179937488 | 78831589 | 258769077 | 106185049 | 22473454 | 47003817 | 61089180 | 6452009 | 786960 | 10750230 | 3843840 | 184538 | 0
Fuel Cost | 584800 | 2073632 | 2067440 | 2383920 | 4268840.32 | 552971.61 | 350792.96 | 4979631.3 | 4601840 | 7435257 | 0 | 6005210 | 100181528.51 | 4376908.8 | 5872361.28 | 4328409.54 | 0 | 0 | 2029080 | 0 | 7416000 | 8975263.68 | 15507585.6 | 2290639.26 | 7216752 | 0 | 2837511.38 | 6183421.2 | 6411000 | 6530618.82 | 291330 | 450000 | 0 | 0 | 0 | 8658170.4 | 1133755.1 | 0 | 0 | 2530000 | 0 | 4686778.76 | 3309477.6 | 0 | 3294819 | 0 | 0 | 4409064 | 8326588.56 | 10797818.85 | 6850844.4 | 12254361.6 | 7038086.4 | 354592.8 | 0 | 0 | 0 | 1458620.8 | 4639770 | 4778595 | 2560600 | 126960 | 2225001.6 | 271108.8 | 883804.8 | 96600 | 438831.2 | 0 | 2701935.04 | 7944683.04 | 385806.96 | 192915 | 477323 | 384277.5 | 26291865.6 | 2594070 | 11530876.8 | 347026.68 | 0 | 1382160 | 924601.6 | 888768 | 900720 | 2571177.18 | 3943800 | 1647400.32 | 1529500.8 | 1039500 | 3171867.6 | 560640 | 909856.2 | 222642 | 3996960 | 382842 | 191994.24 | 11712307.2 | 9581610.06 | 7559259.35 | 2774358.95 | 12269400 | 3806276.1 | 0 | 0 | 0 | 37206076.8 | 10420722.06 | 5236530 | 0 | 0 | 0 | 0 | 0 |  | 114614615.4 | 6625795 | 0 | 0 | 11237260.8 | 58891392 | 0 | 0 | 4188720 | 6996377.6 | 5490390 | 2909081.4 | 686699.64 | 9618816 | 2245277.2 | 0 | 1417500 | 4790405.2 | 2253922.88 | 7164559.36 | 5351409 | 2146502 | 1692231.75 | 5632972.8 | 3024831.15 | 468336 | 298536.48 | 164344.7 | 0 | 9564553.63 | 18822518 | 3835370 | 3453330 | 3097183.76 | 0 | 2969775.2 | 0 | 0 | 10248268.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 485008745.01 | 309900975.75 | 794909720.76 | 78066154.28 | 114614615.4 | 26569706.87 | 378484166.79 | 28387071.63 | 0 | 142496140.19 | 26291865.6 | 0 | 0
Yesterday Day Peak | 35 | 94 | 98 | 115 | 300 | 6 | 0 | 346 | 336 | 26 | 0 | 400 | 295 | 7 | 30 | 55 | 0 | 0 | 90 | 0 | 85 | 100 | 15 | 0 | 63 | 0 | 6 | 35 | 56 | 55 | 16 | 25 | 31 | 33 | 25 | 40 | 40 | 34 | 0 | 100 | 0 | 24 | 125 | 0 | 142 | 0 | 0 | 16 | 0 | 17 | 10 | 83 | 46 | 18 | 2 | 0 | 0 | 80 | 320 | 320 | 206 | 8 | 100 | 33 | 52 | 5 | 10 | 0 | 0 | 52 | 20 | 11 | 25 | 20 | 138 | 145 | 8 | 20 | 0.8 | 55 | 58 | 34 | 44 | 100 | 248 | 59 | 75 | 43 | 122 | 18 | 43 | 10 | 280 | 23 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 46 | 19.6 | 100 | 146 | 0 | 283 | 96 | 109 | 105 | 5.4 | 135 |  | 936 | 0 | 0 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 0 | 174 | 22 | 16 | 0 | 0 | 55 | 0 | 0 | 0 | 12 | 0 | 0 | 8 | 0 | 21 | 13 | 8 | 0 | 67 | 200 | 0 | 0 | 196 | 0 | 160 | 0 | 92 | 0 | 175 | 0 | 350 | 35 | 0 | 53 | 53 | 4 |  | 10109.8 | DayPeak
Yesterday Evening Peak | 35 | 94 | 100 | 115 | 240 | 22 | 20 | 329 | 320 | 110 | 0 | 340 | 275 | 100 | 80 | 55 | 0 | 0 | 87 | 0 | 100 | 100 | 140 | 88 | 63 | 0 | 49 | 35 | 56 | 55 | 19 | 25 | 32 | 33 | 25 | 48 | 40 | 36 | 0 | 100 | 0 | 16 | 230 | 0 | 130 | 0 | 0 | 24 | 83 | 85 | 86 | 90 | 47 | 19 | 26 | 0 | 0 | 0 | 220 | 220 | 0 | 8 | 100 | 0 | 0 | 0 | 0 | 0 | 50 | 52 | 22 | 11 | 25 | 20 | 190 | 147 | 94 | 20 | 0 | 55 | 40 | 50 | 50 | 163 | 250 | 61 | 77 | 45 | 112 | 18 | 46 | 10 | 260 | 23 | 11 | 150 | 300 | 107 | 51 | 122 | 53 | 149 | 0 | 100 | 200 | 0 | 250 | 95 | 108 | 105 | 0 | 132 |  | 939 | 48 | 0 | 0 | 115 | 233 | 0 | 0 | 32 | 52 | 40 | 173 | 40 | 110 | 12 | 0 | 55 | 50 | 33 | 95 | 0 | 50 | 44 | 50 | 34 | 22 | 16 | 11 | 0 | 68 | 200 | 17 | 17 | 184 | 0 | 174 | 0 | 97 | 97 | 192 | 0 | 350 | 90 | 0 | 108 | 107 | 0 |  | 12529 | EvPeak
Forecast for Evening | 35 | 94 | 100 | 115 | 380 | 20 | 20 | 412 | 360 | 110 | 0 | 450 | 335 | 100 | 100 | 55 | 0 | 0 | 100 | 0 | 100 | 102 | 149 | 100 | 65 | 0 | 49 | 35 | 55 | 55 | 22 | 25 | 33 | 33 | 33 | 48 | 40 | 35 | 0 | 100 | 0 | 25 | 225 |  | 140 | 0 | 0 | 24 | 74 | 85 | 100 | 100 | 45 | 19 | 40 | 0 | 0 | 120 | 360 | 360 | 221 | 8 | 100 | 0 | 55 | 5 | 7 | 0 | 50 | 52 | 22 | 11 | 33 | 20 | 188 | 150 | 95 | 20 | 0 | 57 | 58 | 50 | 44 | 163 | 330 | 66 | 86 | 46 | 130 | 18 | 50 | 10 | 341 | 25 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 133 | 269 | 100 | 100 | 105 |  | 150 |  | 945 | 48 | 0 | 0 | 115 | 225 | 0 | 0 | 33 | 80 | 40 | 173 | 39 | 110 | 20 | 0 | 60 | 50 | 35 | 95 | 50 | 50 | 47 | 52 | 35 | 22 | 16 | 11 | 0 | 70 | 199 | 16 | 18 | 200 | 0 | 200 | 0 | 90 | 100 | 220 | 0 | 414 | 105 | 200 | 100 | 102 | 0
Forecast for Day | 35 | 94 | 100 | 115 | 300 | 0 | 0 | 412 | 360 | 110 | 0 | 450 | 335 | 100 | 100 | 55 | 0 | 0 | 100 | 0 | 100 | 102 | 149 | 100 | 65 | 0 | 49 | 35 | 55 | 55 | 22 | 25 | 33 | 33 | 33 | 48 | 40 | 35 | 0 | 100 | 0 | 25 | 225 | 0 | 140 | 0 | 0 | 24 | 74 | 85 | 100 | 100 | 45 | 19 | 10 | 0 | 0 | 120 | 360 | 360 | 221 | 8 | 100 | 0 | 55 | 5 | 7 | 0 | 0 | 52 | 0 | 0 | 33 | 20 | 149 | 150 | 70 | 20 | 2 | 57 | 58 | 50 | 44 | 163 | 330 | 66 | 86 | 46 | 130 | 18 | 50 | 10 | 341 | 25 | 11 | 0 | 100 | 100 | 0 | 100 | 0 | 149 | 20 | 100 | 200 | 0 | 269 | 100 | 100 | 105 | 3 | 84 |  | 945 | 0 | 0 | 0 | 115 | 225 | 0 | 0 | 33 | 50 | 40 | 173 | 39 | 110 | 0 | 0 | 60 | 0 | 35 | 95 | 50 | 50 | 47 | 52 | 35 | 22 | 16 | 11 | 0 | 70 | 199 | 16 | 18 | 200 | 0 | 200 | 0 | 90 | 0 | 220 | 0 | 414 | 105 | 0 | 50 | 102 | 0
Generation at 08:00(Today) | 35 | 94 | 100 | 115 | 200 | 0 | 0 | 341 | 250 | 0 | 0 | 320 | 287 | 0 | 0 | 0 | 0 | 0 | 97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 18 | 17 | 22 | 25 | 10 | 33 | 25 | 0 | 40 | 32 | 0 | 100 | 0 | 0 | 233 | 0 | 100 | 0 | 0 | 16 | 0 | 0 | 10 | 12 | 0 | 19 | 0 | 0 | 0 | 80 | 220 | 220 | 89 | 8 | 100 | 0 | 50 | 5 | 7 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 100 | 152 | 0 | 0 | 0.2 | 30 | 40 | 5 | 5 | 130 | 238 | 40 | 10 | 45 | 112 | 0 | 12 | 0 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.73 | 50 | 17 | 0 | 200 | 8 | 54 | 36 | 2.71 | 150 | 0 | 934 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 173 | 19 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 5 | 0 | 68 | 150 | 0 | 0 | 174 | 0 | 158 | 0 | 11 | 0 | 175 | 0 | 210 | 0 | 0 | 0 | 17 | 0 | 0
199
| Minimum Generation |  | 8599.5 | 7:00
| Highest Generation |  | 12581 | 22:00
| Day Peak Generation |  | 10109.8 | 12:00
| Evening Peak Generation |  | 12529 | 21:00
| HVDC Max Flow |  | 940 | 24:00
| HVDC EvPeak Flow |  | 939 | 21:00
| Load factor L.F |  | 85.7%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2019-05-31
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2019-05-30 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 10109.8 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 7327.2 | MW
Evening Peak Generation : |  | 12529 | MW Hour : | 21:00 | Available Max Generation : |  | 14995 | MW
E.P. Demand (at gen end) : |  | 12529 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 12000 | MW
Maximum Generation : |  | 12581 | MW Hour : | 22:00 | Reserve(Generation end) |  | 2995 | MW
Total Gen. (MKWH) : |  | 258.7691 | System Load Factor : | 85.7% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -180 | MW at | 1:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2019-05-31
Actual : | 73.92 | Ft.(MSL) , | Rule curve : | 76.2 | Ft.( MSL )
Gas Consumed : | Total = | 1328.33 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 104635861.15
|  | Coal : | 28387071.63 | Oil : | 520980306.98 | Total : | 654003239.76
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4259.8636 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1450.8508 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1300.3172 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1175.0894 |  |  | 0 | 0%
Comilla Area | 0 | 0:00 | 1061.8324 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 856.8668 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 476.2077 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 220.5432 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 660.8722 |  |  | 0 | 0%
Total | 0 |  | 11462.4432 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1 | 7) Baghabari 100 MW
|  |  |  | 2) Khulna ST 110 MW | 8) Ghorasal Unit-1 ST
|  |  |  | 3) Sikalbaha ST 60 MW | 9) Haripur GT-1 & 2
4) Bheramara 410 MW.
5) Siddhirganj ST
6) Ashuganj #3,4
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Natore 132/33 kV T2 transformer was under shut down from 11:02 to 11:24 due to red hot maint at 33 kV bus isolator.
b) Saidpur 132/33 kV T4 transformer was under shut down from 11:24 to 12:38 due to red hot maint at 33 kV |  |  |  |  | About 5 MW Power interruption occurred under Saidpur S/S area
bus isolator. |  |  |  |  | from 11:24 to 12:38.
c) Faridpur-Madaripur 132 kV Ckt-1 tripped at 13:04 from both end showing Dist 3 phase Z1 and was switched on at
at 13:12.
d) Bheramara HVDC CB 10C01A & B was under shut down since at 10:47 for C/M.
e) Mirpur 132/33 kV T1 transformer was under shut down from 09:23 to 15:17 due to oil leakage.
f) After maintenance Ashuganj 230/132 kV OAT11 was switched on at 14:02.
g) Ashuganj CT of OAT11(new transformer) blast and fire spread around the transformer, at the same time Ashuganj
132 kV bus-1 tripped with associate lines bushing of transformer also damaged.
h) Ashuganj 132 kV bus-1 normalized and allied lines were switched on at 19:35.
i) Rajshahi-Chapainawabganj 132 kV Ckt-1 tripped at 20:59 from both end showing directional E/F relay at Rajshahi
S/S end & Chapainawabganj S/S no relay.
j) Amnura-Chapainawabganj 132 kV Ckt-1 tripped at 20:59 from both end showing dist 3 phase Z2 at Amnura S/S |  |  |  |  | About 40 MW Power interruption occurred under Chapainawabganj S/S area
end & directional E/F relay Chapainawabganj S/S and was switched on at 22:50. |  |  |  |  | from 20:59 to 22:50.
k) Ashuganj 230 kV bus-1,2 normalized and allied lines were switched on at 20:14.
l) Tangail-RPCL 132 kV Ckt-1 tripped at 00:41 from both end showing dist Z1 3 phase at RPCL end & dist Z1 Tangail end.
m) Dohazari 132/33 kV T-1 transformer was under shut down from 23:12 to 00:17 due to red hot maint at 33 kV potia |  |  |  |  | About 30 MW Power interruption occurred under Dohazari S/S area
feeder |  |  |  |  | from 23:12 to 00:17.
n) Mymensing-Bhaluka 132 kV Ckt-1 tripped at 01:24 from Bhaluka end showing dist B phase and was switched on at
02:12(31/05/2019).
o) Narsingdi 132/33 kV T-2 transformer tripped at 2:35 fro both side due to O/L(Norsingdi 22 MW tripped ) and was |  |  |  |  | About 62 MW Power interruption occurred under Narsingdi S/S area
switched on at 02:45(31/5/20190. |  |  |  |  | from 2:35 to 2:45.
p) Sylhet-Chattok 132 kV Ckt-1 tripped at 04:01 from Chattak end showing dist relay and was switched on at 04:33(31/5/2019).
q) Halishahar 132 kV bus was under shut down from 06:08 to 08:18(31/05/2019) for C/M. |  |  |  |  | About 90 MW Power interruption occurred under Halishahar S/S area
from 06:08 to 08:18.
r) Mymensing-132/33 kV T-1 transformer along with 33 kV bus-1 is under shut down since 05:55 for C/M. |  |  |  |  | About 15 MW Power interruption occurred under Mymensing S/S area
since at 05:55 .
s) Bagerhat-Bhandaria 132 kV Ckt tripped at 05:00 from both end showing dist Z1,ABC phase and was switched on at 05:04.
t) Feni 132/33 kV T-1 transformer was under shut down from 07:16 to 09:39(31/05/2019) for C/M

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2019-05-30 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | PDB | 2*55 | 85 | 35 | 680000 | #1 Under maint.
| Ghorasal GT: Unit-3 |  | PDB | 1*210 | 170 | 94 | 2411200 | Gas shortage
| Ghorasal GT: Unit-4 |  | PDB | 1*210 | 180 | 100 | 2404000 | Gas shortage
| Ghorasal ST: Unit-5 |  | PDB | 1*210 | 190 | 115 | 2772000 | Gas shortage
2 | Ghorasal ST: Unit-7 |  | PDB | 1*243+1*122 | 365 | 240 | 6670063 | Gas shortage
3 | Ghorashal 78MW (MAX) |  | QRPP | 2*40 | 78 | 20 | 373184 | Gas shortage
4 | Ghorashal (Regent) |  | IPP | 34*3.35 | 108 | 22 | 682681 | Gas shortage
5 | Haripur GT: Unit-1, 2 |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Gas shortage
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 329 | 8163330 | FGMO
7 | Haripur NEPC 110MW |  | IPP | 8*15 | 110 | 110 | 773700
8 | Haripur Power CCPP 360MW |  | IPP | 1*235+1*125 | 360 | 320 | 7544000 | Frequency control
9 | Meghnaghat CCPP 450MW |  | IPP | 2*150+1*150 | 450 | 340 | 8963000 | Frequency control
10 | Meghnaghat (IEL) |  | QRPP | 12*8.9 | 100 | 100 | 696960
11 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 275 | 6595229 | FGMO
12 | Madanganj 102MW |  | QRPP | 6*17 | 100 | 80 | 879096 | Engine problem
13 | Madanganj-55 MW |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 708414
14 | Keraniganj (Powerpac) 100MW |  | QRPP | 8*13.45 | 100 | 88 | 359598 | Engine problem
15 | Narshingdi (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 388440
16 | Siddhirgonj ST 210MW |  | PDB | 1*210 | 115 | 0 | 0 | Gas shortage
17 | Siddhirgonj GT Unit-1& 2 |  | EGCB | 2*105 | 210 | 87 | 1828000 | Gas shortage
| Siddhirganj Desh |  | QRPP | 96*1.2 | 0 | 0 | 0 | Contract Expired
18 | Siddhirganj (Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 100 | 1186560
19 | Siddhirganj CCPP-335 MW |  | EGCB | 1*217 | 217 | 0 | 0 | Gas shortage
0 | Pagla (DPA ) |  | QRPP | 100*0.5 | 0 | 0 | 0 | Contract Expired
20 | Gagnagar (Orion) |  | IPP | 12*8.924 | 102 | 100 | 1361952
21 | Katpotti 51 MW |  | IPP | 7*7.9 | 51 | 49 | 425414
22 | Banco Energy 54MW |  | IPP | 3*18 | 54 | 35 | 867240 | Engine problem
23 | Kodda 149MW |  | BPDB-RPCL | 9*17.06 | 149 | 140 | 1603680
24 | Northern 55 MW |  | IPP | 3*19.3 | 55 | 56 | 1025760
25 | Southern 55MW |  | IPP | 3*19.3 | 55 | 55 | 1041566
26 | Bosila 108MW |  | IPP | 12*8.775+1*3.5 | 108 | 63 | 1204800 | Engine problem
27 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 57 | 1290480 | Engine problem
28 | Summit Maona |  | SIPP,REB | 4*8.73 | 33 | 33 | 647000
29 | Summit Rupganj |  | SIPP,REB | 4*8.73 | 33 | 25 | 592300 | Engine problem
30 | Gazipur (RPCL) |  | IPP | 6*8.9 | 52 | 48 | 915240
31 | Tongi GT |  | PDB | 1* 105 | 105 | 40 | 985874 | Gas shortage
32 | Summit Gazipur -2 |  | IPP | 18*17.076 | 300 | 300 | 1319781
33 | APR Energy , Keranigonj |  | IPP | 256*1.4 | 300 | 107 | 436195 | Low demand
34 | Bramhangoan 100 MW (Aggreko) |  | IPP | 100 | 100 | 51 | 162719 | Low demand
35 | Aggreko Aurahati 100MW |  | IPP | 0.85*23+0.95*91 | 100 | 53 | 223242 | Low demand
36 | Summit Gazipur-1 150MW |  | IPP | 149 | 149 | 149 | 2005920
| Gazipur 100 MW |  | RPCL | 100 MW | 0 | 108 | 2528232 | on test
| Dhaka area Total |  |  |  | 5698 | 3998 | 72716850
37 | Chattogram ST-1 (Raozan) |  | PDB | 1*210 | 180 | 100 | 2300000
| Chittgong ST-2 (Raozan) |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
38 | Raozan 25 MW (RPCL) |  | IPP | 3*8.9 | 25 | 16 | 494908
39 | Teknaf Solartech 20MW |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 136890
40 | Patenga 50MW |  | IPP | 8*6.98 | 50 | 47 | 1076160
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 36 | 786960 | Low water level
42 | Sikalbaha ST 60MW |  | PDB | 1*60 | 40 | 0 | 0 | Under maint.
43 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 230 | 5014360 | FGMO
44 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 130 | 2865060 | FGMO
45 | Sikalbaha (Energis) |  | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 24 | 501600 | Low demand
| Baraka Sikalbaha PL |  | IPP | 105 MW | 0 | 105 | 2443843
46 | Hathazari peaking |  | PDB | 11*8.9 | 98 | 83 | 773128
47 | Dohazari Peaking |  | PDB | 6*17 | 102 | 85 | 1109745
48 | Juldah (Acorn) |  | QRPP | 8*13.45 | 100 | 86 | 1106760
49 | Juldah 100 MW Unit-3 |  | IPP | 0 | 100 | 100 | 2449920
50 | Barabkunda (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 417168 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 26 | 402720
51 | Chattogram ECPV 108 MW |  | IPP | 16*7 | 108 | 90 | 1896960 | Engine problem
| Kaptai Solar |  | PDB | 7.4 MW | 0 | 0 | 36648 | on test
| Anwara United |  | United Group | 300 MW | 0 | 132 | 3008400 | on test
| Chattogram area Total |  |  |  | 1681 | 1309 | 26821230
52 | Ashuganj ST: Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage
| Ashuganj ST: Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj ST: Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 1602880 | Machine tripped at 18:42
53 | Ashuganj CCPP 225 MW |  | APSCL | 1*142+1*75 | 221 | 0 | 3658000 | Machine tripped
54 | Ashuganj CCPP(North) |  | APSCL | 1*360 | 360 | 220 | 7483500 | Frequency control
55 | Ashuganj CCPP(South) |  | APSCL | 1*360 | 360 | 220 | 6925500 | Frequency control
56 | Ashuganj Engines TSK |  | APSCL | 14*3.968 | 45 | 0 | 404640 | Machine problem
57 | Ashuganj (Precision) 55MW |  | RPP | 15*4 | 55 | 0 | 1027680 | Machine tripped
58 | Ashuganj (United) 53MW |  | QRPP | 14*4 | 53 | 0 | 105000 | Gas shortage
59 | Ashuganj 195MW Modular |  | IPP | 20*9.73+1*16 | 195 | 8 | 184000 | Gas shortage
60 | Ashuganj (Midland) 51MW |  | IPP | 6*9.34 | 51 | 0 | 535160 | Engine problem
61 | Midland 150MW |  | IPP | 23*7.015 | 150 | 0 | 1115709 | Under shut down
62 | B.Baria (Aggreko) 85MW |  | QRPP | 86*1.10 | 85 | 0 | 0 | Contract Expired
63 | Daudkandi Peaking 52MW |  | PDB | 6*8.92 | 52 | 50 | 249256
64 | Chandpur CCPP |  | PDB | 1*106+1*57 | 163 | 100 | 2317710
65 | Chandpur Desh 200MW |  | IPP | 0 | 200 | 200 | 3983520
66 | Feni (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 22 | 501048
67 | Feni, Mohipal (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 257220
** | Tripura |  | Imported power | 0 | 160 | 190 | 3843840
68 | Jangalia (Summit) 33MW |  | SIPP, PDB | 4*8.73 | 33 | 25 | 619900
69 | Lakdhanvi 52 MW |  | IPP | 6*8.92 | 52 | 52 | 1070712
70 | Summit Cumilla 25MW |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 20 | 512370 | Engine problem
71 | Daudkandi bangla trak |  | IPP | 154*1.4 | 200 | 150 | 675840 | Low demand
| Cumilla Area Total |  |  |  | 2891 | 1268 | 37073485
72 | Mymensingh RPCL 210MW |  | IPP | 4*35+1*70 | 202 | 147 | 3458760 | GT-1 Under maint
73 | Tangail (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 20 | 450684
74 | Jamalpur 95MW |  | IPP | 12*8.924 | 95 | 94 | 1254720
75 | Sarishabari (Solar) |  | IPP | 1*3 | 3 | 0 | 11000
76 | United Mymensingh PPL |  | IPP | 200 | 200 | 122 | 1716000 | High Voltage
77 | United Jamalpur PPL |  | IPP | 115 MW | 115 | 95 | 2074800 | Engine problem
| Mymensingh Area Total |  |  |  | 637 | 478 | 8965964
78 | Fenchugonj CCPP-1 |  | PDB | 2*32+1*33 | 70 | 55 | 1329000
79 | Fenchugonj CCPP-2 |  | PDB | 2*35+1*35 | 90 | 40 | 889040
80 | Kushiara 163 MW CCPP GT |  | IPP | 1*109+1*54 | 163 | 163 | 3296381
81 | Shajibazar 330 MW |  | PDB | 3*110 | 330 | 250 | 5634000 | Machine problem
82 | Fenchugonj (Barakatullah) 51MW |  | RPP | 19*2.90 | 51 | 50 | 925800
83 | Fenchuganj (EPL) 44MW |  | RPP | 12*3.3+5*2 | 44 | 50 | 1000800
84 | Hobiganj 11MW |  | SIPP, REB | 4*2.90 | 11 | 11 | 252624
85 | Shahjibazar GT: Unit- 8, 9 |  | PDB | 2*35 | 66 | 61 | 1445088 | FGMO
86 | Shahjibazar 86MW |  | RPP | 32*2.90 | 86 | 77 | 1429440
87 | Shahjibazar (EPL) 50MW |  | RPP | 27*2.0 | 50 | 45 | 945000
88 | Sylhet GT 150 MW |  | PDB | 1*142 | 142 | 112 | 2782340 | Frequency control
89 | Sylhet GT 20 MW |  | PDB | 1*20 | 20 | 18 | 438000
90 | Sylhet (EPL) 50MW |  | RPP | 27*2 | 50 | 46 | 978340
91 | Shahjahanulla 25 MW |  | SIPP, REB | 3*9.34 | 25 | 23 | 510456
92 | Summit Bibiana- 2 |  | IPP | 1*222+1*119 | 341 | 260 | 6245250 | FGMO
| Bibiyana-3 285 MW |  | PDB | 285 MW | 0 | 250 | 6019000 | On test
93 | Sylhet (Desh) 10MW |  | RPP | 6*1.95 | 10 | 10 | 239400
| Sylhet Area Total |  |  |  | 1549 | 1521 | 34359959
94 | Bheramara GT-1,2,3 |  | PDB | 3*20 | 46 | 48 | 227300
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 939 | 22473454
| Khulna (KPCL-1 & 3) |  | IPP | 19*6.5 | 0 | 0 | 0 | Contract Expired
95 | Khulna (KPCL-2) |  | QRPP | 7*17 | 115 | 115 | 1355520
96 | Faridpur Peaking |  | PDB | 8*6.89 | 54 | 32 | 372000
97 | Khulna CCPP 225MW |  | NWPGCL | 1*150+1*75 | 230 | 233 | 3662400
98 | Gopalganj Peaking |  | PDB | 16*6.98 | 109 | 52 | 593920
99 | Bheramara 360 MW |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Under maint.
100 | Noapara (KZA) 40MW |  | QRPP | 5*8.5 | 40 | 40 | 696750
0 | Khulna (Aggreeco) 55MW |  | QRPP | 71*0.85 | 0 | 0 | 0 | Contract Expired
101 | Bangla Trak Noapara |  | IPP | 70*1.4 | 100 | 97 | 591360
102 | Labon Chora 105 MW |  | IPP | 6*18.445 | 105 | 90 | 1800000
103 | Madhumati Power Plant |  | IPP | 100 MW | 105 | 107 | 2223648
| Khulna Area Total |  |  |  | 2314 | 1753 | 33996352
104 | Summit Barisal 110 MW |  | IPP | 7*17.076 | 110 | 110 | 1299840
105 | Barisal GT: Unit-1, 2 |  | PDB | 2*20 | 30 | 12 | 66665
106 | Bhola (Venture) 33MW |  | RPP | 1*34.50 | 33 | 40 | 693636
107 | Bhola CCPP 194MW |  | PDB | 2*63+1*68 | 194 | 173 | 4216060 | FGMO
108 | Bhola Aggreko 95MW |  | QRPP | 96*1.10 | 95 | 97 | 2241723
| Barisal Area Total |  |  |  | 462 | 432 | 8517924
109 | Baghabari GT 71MW |  | PDB | 1*71 | 71 | 55 | 1350000
| Baghabari GT 100MW |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
110 | Baghabari Peaking 50MW |  | PDB | 6*8.9 | 52 | 50 | 418376
111 | Bera Peaking |  | PDB | 9*8.29 | 71 | 33 | 210254
112 | Amnura 50MW |  | QRPP | 7*7.79 | 50 | 0 | 618660 | Machine tripped at 20:57
113 | Katakhali (Northern) |  | QRPP | 6*8.9 | 50 | 50 | 241180
114 | Katakhali Peaking |  | PDB | 6*8.7 | 50 | 44 | 158895
115 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 184 | 4554682 | FGMO
116 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 174 | 4242536 | FGMO
117 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 192 | 4683636 | FGMO
118 | Sirajgonj Unit-4 414 MW(Gas) |  | SNWPGCL | 1*282+1*132 | 414 | 350 | 8447270 | Frequency control
119 | Santahar Peaking |  | PDB | 6*8.7 | 50 | 34 | 256995
120 | Bogra (GBB) |  | RPP | 6*4 | 22 | 22 | 425760
121 | Bogra (EPL) |  | RPP | 5*3.3+5*2 | 10 | 16 | 317592
122 | Ullapara (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 217100
123 | Rajlanka 52 MW |  | IPP | 6*8.92 | 52 | 50 | 567840
124 | Chapainawabganj-100 MW |  | PDB | 12*8.924 | 104 | 95 | 799616
125 | Paramount Baghabari |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
126 | Confidence Bogura-2 (CPBL) |  | IPP | 113 MW | 113 | 108 | 1677792
| Rajshahi Area Total |  |  |  | 2070 | 1468 | 29188184
107 | Barapukuria Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under overhauling
| Barapukuria Unit-2 |  | PDB | 1*125 | 85 | 68 | 1575709
108 | Barapukuria Unit-3 |  | PDB | 1*275 | 274 | 200 | 4876300
129 | Rangpur GT |  | PDB | 1*20 | 20 | 17 | 119000
130 | Saidpur GT |  | PDB | 1*20 | 20 | 17 | 129000
| Confidence Rangpur |  | IPP | 113 MW | 0 | 0 | 429120
| Rangpur Area Total |  |  |  | 484 | 302 | 7129129
| Total |  |  |  | 17786 | 12529 | 258769077
| Eastern Grid Total |  |  |  | 12456 | 8574 | 179937488
| Western Grid Total |  |  |  | 5330 | 3955 | 78831589
| National Grid Total |  |  |  | 17786 | 12529 | 258769077
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date: | 2019-05-30
| (a) ENTIRE EASTERN GRID : |  | 8210 | MW | (b) ENTIRE WESTERN GRID : |  | 3747 | MW
| i) Dhaka area |  | 4437 | MW | i) Khulna area |  | 1564 | MW
| ii) Chittagong area |  | 1227 | MW | ii) Rajshahi area |  | 1184 | MW
| iii) Comilla area |  | 1164 | MW | iii) Barisal area |  | 350 | MW
| iv) Mymensingh area |  | 853 | MW | iv) Rangpur area |  | 649 | MW
| v) Sylhet area |  | 529 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 11957 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
SL NO | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
1 | Siddhirganj | 132 | 1500 | Jamalpur | 126 | 100 | Jessore | 120 | 2300
2 | Munsiganj | 135 | 2100 | Sherpur | 90 | 2300 | Jhenida | 124 | 2300
3 | Sonargaon | 72 | 100 | Srimongal | 42 | 2100 | Bottail | 140 | 2100
4 | Shyampur | 200 | 100 | Shahjibazar | 125 | 2200 | G.K Project | 62 | 2200
5 | Bhulta | 200 | 1000 | Fenchuganj | 50 | 2000 | Faridpur | 186 | 2200
6 | Madanganj | 63 | 900 | Kulawara | 50 | 2100 | Madaripur | 128 | 2100
7 | Shitalakhya | 122 | 1200 | Sylhet | 147 | 2100 | Gopalganj | 101 | 2200
8 | Rahim steel | 16 | 1100 | Chatak | 34 | 2200 | Bagerhat | 85 | 2100
9 | Matuail | 101 | 1200 | Sunamganj | 39 | 2200 | Mongla | 40 | 1400
10 | Ghorasal | 84 | 100 | Biani Bazar | 48 | 1900 | Satkhira | 111 | 2300
11 | Narsingdi | 133 | 300 | Comilla (S) | 190 | 2100 | Gallamari | 56 | 2300
12 | Haripur (SBU) | 103 | 1200 | Comilla(N) | 129 | 2100 | Magura | 61 | 1930
13 | Ullon | 101 | 1700 | Chandpur | 108 | 2200 | Chuadanga | 90 | 2200
14 | Hasnabad | 238 | 2000 | Feni | 165 | 2200 | Barisal | 116 | 1930
15 | Magbazar | 145 | 1400 | Chowmuhani | 186 | 2100 | Patuakhali | 109 | 2200
16 | Maniknagar | 110 | 1200 | Ashuganj | 52 | 2300 | Bhandaria | 60 | 2200
17 | Bangabhaban | 38 | 1400 | Daudkandi | 162 | 2200 | Barisal (N) | 48 | 2000
18 | Narinda | 102 | 1300 | B.Baria | 131 | 2300 | Sariatpur | 39 | 2200
19 | Dhanmondi | 181 | 1300 | Ramganj | 104 | 2200 | Benapol | 47 | 2200
20 | Lalbag | 83 | 1400 | Madunaghat | 70 | 2100 | Borhan Uddin | 37 | 2100
21 | Madartek | 63 | 2100 | Hathazari | 105 | 2100 | Ishurdi | 71 | 2000
22 | Mirpur | 121 | 2000 | Khulshi | 204 | 1930 | Ruppur Paromanobik | 2 | 800
23 | Kalyanpur | 129 | 2000 | Halishahar | 161 | 1500 | Natore | 136 | 2000
24 | Gulshan | 172 | 1400 | Baraulia | 178 | 1700 | Bogra | 246 | 100
25 | Uttara | 72 | 1900 | Sikalbaha | 42 | 2000 | Noagaon | 127 | 2100
26 | Uttara New | 18 | 1200 | Dohazari | 112 | 2100 | Rajshahi | 167 | 2000
27 | Kamrangirchar | 80 | 1930 | Cox'sbazar | 95 | 100 | C.Nawabganj | 75 | 2000
28 | Savar | 145 | 1200 | Chandraghona | 30 | 1930 | Amnura | 35 | 1930
29 | Bhasantec | 179 | 1930 | Kaptai | 4 | 1900 | Pabna | 125 | 2000
30 | Agargaon | 64 | 1200 | A. Khaer Stl. | 0 | 1200 | Shahjadpur | 97 | 1930
31 | Satmosjid | 119 | 1930 | Bakulia | 115 | 2000 | Serajganj | 109 | 2000
32 | Tongi | 157 | 2100 | Julda | 22 | 2100 | Niyamatpur | 59 | 2000
33 | Kabirpur | 244 | 1500 | TK chemical | 4.8 | 8+ | Joypurhat | 51 | 100
34 | Basundhara | 146 | 1930 | Modern Steel | 15 | 1400 | Mohastangor | 16 | 1930
35 | Manikganj | 107 | 2100 | Shahmirpur | 32 | 100 | Rangpur | 138 | 100
36 | Joydevpur | 224 | 1930 | Khagrachhari | 20 | 1900 | Lalmonirhat | 85 | 1930
37 | New Tongi | 107 | 1500 | Matarbari | 31.5 | 2100 | Saidpur | 100 | 2000
38 | Korda | 260 | 1500 | Baroiar Hat | 32 | 1930 | Purbasadipur | 97 | 100
39 | Dhamrai | 58 | 2100 | Rangamati | 12 | 1900 | Thakurgaon | 70 | 2000
40 | Valuka | 100 | 2000 | Abul Khair 230 | 122 | 800 | Palashbari | 104 | 100
41 | Tangail | 200 | 2100 | BSRM | 80 | 1800 | Barapukuria | 47 | 2000
42 | Mymensing | 224 | 2200 | Goalpara | 29 | 2300 | Panchagar | 40 | 1900
43 | Kishorganj | 121 | 2100 | Central (S) | 102 | 2100 | Joldhaka | 15 | 1930
44 | Netrokona | 85 | 100 | Noapara | 109 | 2200
| Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  | (24) Director,System Planning,PDB.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2019-05-30
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min
|  |  |  | Voltage |  |  | Voltage |  | Voltage
SL NO | 400 KV | KV |  | KV |  |  | KV |  | 126
1 | Bibiyana | 382 | 2:00 | 373 | 15:00 | Kaliakoir | 360 | 5:00 | 348
2 | Bheramara | 393 | 7:00 | 383 | 15:00 | Bhulta | 380 | 20:00 | 366
3 | Ashuganj(N) | 385 | 1:00 | 373 | 8:00
SL NO | 230 KV | KV |  | KV |  | 230 KV | KV |  | 9:00
1 | Ghorasal | 228 | 19:30 | 220 | 7:00 | Hathazari | 218 | 1:00 | 213
2 | Ishurdi | 237 | 6:00 | 226 | 12:00 | Megnaghat | 220 | 19:30 | 212
3 | Ashuganj | 235 | 1:00 | 226 | 21:00 | Fenchuganj | 231 | 2:00 | 228
4 | Serajganj | 235 | 2:00 | 228 | 21:00 | Siddhirganj | 219 | 22:00 | 210
5 | Baghabari | 232 | 8:00 | 225 | 21:00 | Maniknagar | 217 | 22:00 | 208
6 | Barapukuria | 240 | 3:00 | 222 | 21:00 | Old Airport | 216 | 20:00 | 207
7 | Bogra | 235 | 2:00 | 218 | 21:00 | Barisal | 235 | 8:00 | 225
8 | Khulna South | 232 | 23:00 | 220 | 12:00 | AKSML | 216 | 18:00 | 209
9 | Rampura | 219 | 1:00 | 210 | 12:00 | BSRM | 218 | 20:00 | 212
10 | Haripur | 219 | 20:00 | 210 | 10:00 | Bibiyana | 229 | 6:00 | 224
11 | Hasnabad | 220 | 20:00 | 209 | 9:00 | Bhulta | 221 | 20:00 | 211
12 | Aminbazar | 217 | 18:30 | 207 | 10:00 | Ashuganj (S) | 232 | 1:00 | 226
13 | Tongi | 218 | 20:00 | 208 | 12:00 | Kaliakoir | 220 | 19:30 | 211
14 | Comilla (N) | 224 | 1:00 | 220 | 4:00
SL NO | 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
1 | Siddhirganj | 133 | 2100 | 125 | 1000 | Hathazari | 130 | 200 | 126
2 | Munsiganj | 135 | 2000 | 124 | 1000 | Khulshi | 127 | 100 | 124
3 | Megnaghat | 132 | 2100 | 126 | 1300 | Halishahar | 132 | 300 | 127
4 | Shyampur | 133 | 2100 | 126 | 1200 | Baraulia | 128 | 200 | 125
5 | Bhulta | 126 | 2100 | 120 | 1200 | Sikalbaha | 132 | 200 | 128
6 | Madanganj | 135 | 2100 | 122 | 900 | Dohazari | 130 | 500 | 125
7 | Shitalakhya | 139 | 2000 | 123 | 1000 | Cox'sbazar | 123 | 1000 | 116
8 | Rahim steal | 133 | 2100 | 126 | 1200 | Chandraghona | 130 | 2000 | 126
9 | Matuail | 132 | 2100 | 123 | 900 | Kaptai | 130 | 1930 | 126
10 | Ghorasal | 135 | 100 | 130 | 1300 | A. Khaer Stl. | 128 | 1900 | 125
11 | Narsinghdi | 125 | 700 | 114 | 2100 | Bakulia | 130 | 1800 | 126
12 | Haripur (SBU) | 132 | 2100 | 126 | 1200 | Julda | 131 | 300 | 128
13 | Ullon | 129 | 700 | 122 | 1400 | TK Chemical | 134 | 1800 | 125
14 | Hasnabad | 136 | 2000 | 125 | 1000 | Modern Steel | 131 | 2000 | 127
15 | Magbazar | 130 | 600 | 121 | 1500 | Shahmirpur | 130 | 1800 | 126
16 | Maniknagar | 131 | 600 | 125 | 1200 | Khagrachhari | 129 | 500 | 124
17 | Bangabhaban | 131 | 600 | 125 | 1200 | Matarbari | 124 | 1000 | 120
18 | Narinda | 130 | 600 | 121 | 1200 | Baroiar Hat | 125 | 1800 | 120
19 | Dhanmondi | 129 | 700 | 122 | 1400 | Rangamati | 128 | 100 | 125
20 | Lalbag | 135 | 2000 | 121 | 1000 | Goalpara | 138 | 100 | 132
21 | Madartek | 130 | 600 | 121 | 1200 | Central s/s | 137 | 2300 | 131
22 | Mirpur | 127 | 2100 | 122 | 1200 | Noapara | 134 | 2300 | 125
23 | Kalyanpur | 130 | 2100 | 125 | 1200 | Jessore | 128 | 800 | 118
24 | Gulshan | 129 | 100 | 121 | 1200 | Jhenida | 128 | 800 | 116
25 | Uttara | 130 | 200 | 120 | 900 | Bottail | 135 | 2300 | 121
26 | Uttara New | 131 | 2000 | 123 | 1200 | G.K.Project | 141 | 600 | 131
27 | Kamrangirchar | 134 | 2100 | 122 | 1700 | Faridpur | 133 | 800 | 119
28 | Savar | 127 | 300 | 120 | 1500 | Madaripur | 135 | 800 | 123
29 | Bhasantec | 131 | 600 | 123 | 1500 | Gopalganj | 146 | 1830 | 133
30 | Agargaon | 131 | 200 | 125 | 1200 | Bagerhat | 130 | 700 | 121
31 | Satmosjid | 131 | 500 | 124 | 1200 | Mongla | 132 | 1700 | 125
32 | Tongi | 133 | 2100 | 126 | 1300 | Satkhira | 134 | 800 | 126
33 | Kabirpur | 127 | 800 | 121 | 1500 | Gallamari | 137 | 800 | 130
34 | Basundhara | 129 | 1930 | 118 | 1200 | Magura | 130 | 2300 | 109
35 | Manikganj | 135 | 1930 | 128 | 1300 | Chuadanga | 123 | 800 | 100
36 | Joydevpur | 136 | 100 | 127 | 1200 | Barisal | 136 | 800 | 130
37 | New Tongi | 132 | 1900 | 124 | 1300 | Patuakhali | 137 | 800 | 125
38 | Kodda | 135 | 1900 | 120 | 700 | Bhandaria | 134 | 800 | 125
39 | Dhamrai | 130 | 600 | 123 | 1500 | Barisal (N) | 139 | 800 | 130
40 | Valuka | 125 | 600 | 115 | 100 | Sariatpur | 135 | 800 | 120
41 | Tangail | 130 | 500 | 120 | 2100 | Benapol | 129 | 800 | 117
42 | Mymensing | 126 | 600 | 116 | 1930 | Ishurdi | 141 | 600 | 130
43 | Kishorganj | 125 | 600 | 116 | 2100 | Ruppur Paromanobik | 140 | 600 | 130
44 | Netrokona | 133 | 500 | 117 | 1930 | Natore | 136 | 600 | 126
45 | Jamalpur | 136 | 500 | 125 | 1300 | Bogra | 139 | 300 | 126
46 | Sherpur | 135 | 400 | 124 | 1200 | Noagaon | 138 | 300 | 120
47 | Srimongal | 134 | 900 | 125 | 1830 | Rajshahi | 133 | 200 | 121
48 | Shahjibazar | 132 | 500 | 121 | 1830 | C.Nawabganj | 132 | 100 | 118
49 | Fenchuganj | 133 | 600 | 128 | 1830 | Amnura | 138 | 200 | 118
50 | Khulawara | 133 | 800 | 128 | 2000 | Pabna | 137 | 600 | 127
51 | Sylhet | 135 | 800 | 129 | 1930 | Shahjadpur | 140 | 400 | 134
52 | Chatak | 134 | 600 | 127 | 2100 | Serajganj | 136 | 300 | 127
53 | Sunamganj | 134 | 600 | 125 | 2100 | Niyamatpur | 139 | 300 | 113
54 | Biani Bazar | 134 | 700 | 126 | 1830 | Joypurhat | 140 | 500 | 120
55 | Comilla(s) | 122 | 1700 | 118 | 1100 | Mohastangor | 139 | 300 | 123
56 | Comilla(n) | 132 | 1800 | 130 | 700 | Rangpur | 138 | 200 | 116
57 | Chandpur | 130 | 1000 | 127 | 700 | Lalmonirhat | 142 | 300 | 110
58 | Feni | 125 | 1000 | 120 | 1900 | Saidpur | 136 | 300 | 115
59 | Chowmuhani | 121 | 1000 | 115 | 2100 | Purbasadipur | 132 | 500 | 114
60 | Ashuganj | 134 | 600 | 122 | 2100 | Thakurgaon | 136 | 300 | 103
61 | Daudkandi | 134 | 2100 | 122 | 1600 | Palashbari | 138 | 300 | 118
62 | B.Baria | 128 | 700 | 119 | 2300 | Barapukuria | 140 | 300 | 122

## L-Curve
Date | 2019-05-30
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 620 | 7841 | 3436 | 11277 |  |  |  | QF-LDC-12
0:30 | 400 | 8071.5 | 3618.5 | 11690 | Date: | 2019-05-30
1:00 | 180 | 8302 | 3801 | 12103
1:30 | 90 | 8101 | 3621.5 | 11722.5
2:00 | 0 | 7900 | 3442 | 11342
2:30 | 245 | 7656.5 | 3307.5 | 10964 | [5 empty] | Gen. at Eve. Peak | 12529 | 12529 MW (21:00 )
3:00 | 490 | 7413 | 3173 | 10586 | [6 empty] | 21:00
3:30 | 420 | 7322 | 3149 | 10471 | [5 empty] | Gen. at Day Peak | 10109.8 | 10109.8 MW (12:00 )
4:00 | 350 | 7231 | 3125 | 10356 | [6 empty] | 12:00
4:30 | 360 | 7029.5 | 3023 | 10052.5 | [5 empty] | Highest Generation | 12581
5:00 | 370 | 6828 | 2921 | 9749 | [6 empty] | 22:00
5:30 | 420 | 6562.25 | 2815.5 | 9377.75
6:00 | 470 | 6296.5 | 2710 | 9006.5
6:30 | 505 | 6095 | 2708 | 8803
7:00 | 540 | 5893.5 | 2706 | 8599.5
7:30 | 535 | 5968.4 | 2719 | 8687.4
8:00 | 530 | 6043.3 | 2732 | 8775.3
8:30 | 515 | 6239.8 | 2730 | 8969.8
9:00 | 500 | 6436.3 | 2728 | 9164.3
9:30 | 400 | 6641.7 | 2751.5 | 9393.2
10:00 | 300 | 6847.1 | 2775 | 9622.1
10:30 | 260 | 7001 | 2778 | 9779
11:00 | 220 | 7154.9 | 2781 | 9935.9
11:30 | 215 | 7239.35 | 2783.5 | 10022.85
12:00 | 210 | 7323.8 | 2786 | 10109.8
12:30 | 235 | 7336.75 | 2931 | 10267.75
13:00 | 260 | 7349.7 | 3076 | 10425.7
13:30 | 220 | 7550.4 | 3121 | 10671.4
14:00 | 180 | 7751.1 | 3166 | 10917.1
14:30 | 230 | 7800 | 3183 | 10983
15:00 | 280 | 7848.9 | 3200 | 11048.9
15:30 | 240 | 7859 | 3192.5 | 11051.5
16:00 | 200 | 7869.1 | 3185 | 11054.1
16:30 | 250 | 7710.35 | 3179.5 | 10889.85
17:00 | 300 | 7551.6 | 3174 | 10725.6
17:30 | 265 | 7336.8 | 3133 | 10469.8
18:00 | 230 | 7122 | 3092 | 10214
18:30 | 150 | 7201 | 3389.5 | 10590.5
19:00 | 70 | 7280 | 3687 | 10967
19:30 | 170 | 8336 | 3885 | 12221
20:00 | 160 | 8355 | 3912 | 12267 |  |  |  | Executive Engineer
20:30 | 160 | 8464.5 | 3933.5 | 12398 |  |  |  | Network Operation Division
21:00 | 160 | 8574 | 3955 | 12529
21:30 | 120 | 8596 | 3959 | 12555
22:00 | 80 | 8618 | 3963 | 12581 |  |  |  |  | Page 6 of 7
22:30 | 240 | 8456 | 3817 | 12273
23:00 | 400 | 8294 | 3671 | 11965
23:30 | 510 | 8067.5 | 3553.5 | 11621
24:00 | 620 | 7841 | 3436 | 11277
12529 MW (21:00 )
10109.8 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2019-05-30 |  | Energy | 258769077
[10 empty] | 2019-05-30 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 4108 | 940 | 1921 | 3188 | 266 | 34 | 646 | 0 | 174
0:30 | 4387 | 937.5 | 1987 | 3132 | 265 | 34.5 | 775 | 0 | 172 | Date: | 2019-05-30
1:00 | 4666 | 935 | 2053 | 3076 | 264 | 35 | 904 | 0 | 170
1:30 | 4575.5 | 935 | 2047.5 | 2892.5 | 264.5 | 35 | 803.5 | 0 | 169 | [7 empty] | Total Energy | 258.7691 | Total Energy Gen 258.769 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 258.769 MKWHr
2:00 | 4485 | 935 | 2042 | 2709 | 265 | 35 | 703 | 0 | 168 | [7 empty] | Energy not Served | 0
2:30 | 4478.5 | 935.5 | 2008 | 2455 | 265.5 | 35 | 618.5 | 0 | 168 | [7 empty] | Energy Requirement | 258.7691
3:00 | 4472 | 936 | 1974 | 2201 | 266 | 35 | 534 | 0 | 168
3:30 | 4499.5 | 936 | 1973 | 2092.5 | 265.5 | 35 | 505.5 | 0 | 164 | [6 empty] | Shortage
4:00 | 4527 | 936 | 1972 | 1984 | 265 | 35 | 477 | 0 | 160
4:30 | 4489 | 936 | 1954.5 | 1827.5 | 265.5 | 35 | 390 | 0 | 155
5:00 | 4451 | 936 | 1937 | 1671 | 266 | 35 | 303 | 0 | 150
5:30 | 4361.5 | 936 | 1833.5 | 1556.5 | 266 | 35.5 | 244 | 0 | 144
6:00 | 4272 | 936 | 1730 | 1442 | 266 | 36 | 185 | 0 | 138
6:30 | 4265.5 | 936 | 1641 | 1343.5 | 266 | 36 | 176.5 | 0 | 135 |  |  |  |  | Coal
7:00 | 4259 | 936 | 1552 | 1245 | 266 | 36 | 168 | 0 | 132
7:30 | 4168.5 | 936.5 | 1593.5 | 1261.5 | 265.5 | 36 | 282.5 | 0 | 134 |  |  |  | Oil |  |  |  | ,
8:00 | 4078 | 937 | 1635 | 1278 | 265 | 36 | 397 | 0 | 136
8:30 | 4116.5 | 936.5 | 1709 | 1359 | 265.5 | 36 | 397 | 0 | 135
9:00 | 4155 | 936 | 1783 | 1440 | 266 | 36 | 397 | 0 | 134
9:30 | 4274 | 936.5 | 1819.5 | 1513 | 266 | 35.5 | 397 | 0 | 135
10:00 | 4393 | 937 | 1856 | 1586 | 266 | 35 | 397 | 0 | 136
10:30 | 4393 | 936.5 | 1856.5 | 1741 | 266 | 35 | 386.5 | 0 | 143
11:00 | 4393 | 936 | 1857 | 1896 | 266 | 35 | 376 | 0 | 150
11:30 | 4485.5 | 936 | 1901.5 | 1964.5 | 266.5 | 34.5 | 264 | 0 | 144
12:00 | 4578 | 936 | 1946 | 2033 | 267 | 34 | 152 | 0 | 138
12:30 | 4520.5 | 936 | 1991 | 2179.5 | 266 | 33.5 | 175.5 | 0 | 140
13:00 | 4463 | 936 | 2036 | 2326 | 265 | 33 | 199 | 0 | 142
13:30 | 4463 | 936 | 2036 | 2326 | 265 | 33 | 199 | 0 | 142
14:00 | 4463 | 936 | 2036 | 2326 | 265 | 33 | 199 | 0 | 142
14:30 | 4483 | 936 | 2113 | 2533 | 264.5 | 33.5 | 198.5 | 0 | 156
15:00 | 4503 | 936 | 2190 | 2740 | 264 | 34 | 198 | 0 | 170
15:30 | 4505.5 | 936 | 2219.5 | 2709 | 264.5 | 34 | 203.5 | 0 | 167
16:00 | 4508 | 936 | 2249 | 2678 | 265 | 34 | 209 | 0 | 164
16:30 | 4484 | 936 | 2245.5 | 2551.5 | 264.5 | 34 | 207.5 | 0 | 159
17:00 | 4460 | 936 | 2242 | 2425 | 264 | 34 | 206 | 0 | 154
17:30 | 4403 | 936 | 2041 | 2409.5 | 264 | 34.5 | 225.5 | 0 | 154
18:00 | 4346 | 936 | 1840 | 2394 | 264 | 35 | 245 | 0 | 154
18:30 | 4170 | 937.5 | 1838.5 | 2677 | 265 | 35 | 499.5 | 0 | 168
19:00 | 3994 | 939 | 1837 | 2960 | 266 | 35 | 754 | 0 | 182
19:30 | 4087 | 939 | 1979 | 3806 | 266 | 35 | 925 | 0 | 184
20:00 | 4012 | 939 | 1882 | 3975 | 267 | 36 | 976 | 0 | 180
20:30 | 4029.5 | 939 | 1922 | 4018.5 | 267.5 | 36 | 1000.5 | 0 | 185
21:00 | 4047 | 939 | 1962 | 4062 | 268 | 36 | 1025 | 0 | 190
21:30 | 4049 | 939 | 1976.5 | 4076 | 267.5 | 36 | 1023 | 0 | 188
22:00 | 4051 | 939 | 1991 | 4090 | 267 | 36 | 1021 | 0 | 186
22:30 | 4109 | 939 | 1953.5 | 3841.5 | 267 | 36 | 944 | 0 | 183
23:00 | 4167 | 939 | 1916 | 3593 | 267 | 36 | 867 | 0 | 180
23:30 | 4137.5 | 939.5 | 1918.5 | 3390.5 | 266.5 | 35 | 756.5 | 0 | 177 | Max Temp. in Dhaka |  | 36.2° C
24:00 | 4108 | 940 | 1921 | 3188 | 266 | 34 | 646 | 0 | 174
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 258.769 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 258.769 MKWHr
Note on W13: Author:

## Generation
2019-05-30
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Kaptai Unit-1, 2 & 3 | 35 | 35 | 35 | 35 | 35 | 36 | 36 | 36 | 36 | 35 | 35 | 34 | 33 | 33 | 34 | 34 | 34 | 35 |  | 35 | 35 | 36 | 36 | 36 | 36 | 34 | 786960
2 | Kaptai Unit-4 & 5
3 | Chattogram ST-1 (Raozan) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2300000
4 | Chittgong ST-2 (Raozan)
5 | Raozan 25 MW (RPCL) | 25 | 25 | 25 | 25 | 25 | 8 | 8 | 8 | 8 | 8 | 21 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 25 | 25 | 16 | 25 | 25 | 25 | 494908
| Teknaf Solartech 20MW |  |  |  |  | 0 | 1.5 | 3.9 | 10.5 | 11.7 | 9.3 | 19.4 | 19.6 | 18.8 | 16.2 | 12.8 | 8.4 | 3.4 | 0 | [8 empty] | 136890
6 | Sikalbaha 225MW (Gas) | 218 | 210 | 218 | 218 | 217 | 218 | 195 | 0 |  |  |  | 125 | 126 | 227 | 226 | 225 | 228 | 229 |  | 224 | 224 | 231 | 230 | 231 | 231 | 232 | 5014360
7 | Sikalbaha 225MW (Oil) | [6 empty] | 0 | 229 | 229 | 229 | 224 | 0 | 0 | 0 | 0
8 | Sikalbaha ST 60MW
9 | Sikalbaha GT 150MW (Gas) | 140 | 90 | 96 | 99 | 90 | 90 | 90 | 90 | 140 | 130 | 130 | 142 | 130 | 131 | 131 | 132 | 130 | 130 |  | 130 | 129 | 130 | 130 | 130 | 130 | 90 | 2865060
10 | Sikalbaha GT 150MW (Oil)
| Dohazari Peaking | 85 | 85 | 85 | 85 | 63 | 34 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 16 | 16 | 16 | 16 |  | 85 | 85 | 85 | 85 | 71 | 80 | 80 | 1109745
12 | Hathazari peaking | 83 | 83 | 83 | 83 | 42 | 0 | [13 empty] | 43 | 74 | 76 | 83 | 83 | 83 | 0 | 773128
| Baraka Sikalbaha PL | 105 | 105 | 105 | 105 | 105 | 105 | 70 | 70 | 109 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2443843
| Daudkandi bangla trak | [19 empty] | 10 | 150 | 150 | 150 | 150 | 120 | 120 | 675840
14 | Daudkandi Peaking 52MW | [19 empty] | 27 | 50 | 50 | 50 | 50 | 50 | 50 | 249256
15 | Siddhirgonj ST 210MW
16 | Siddhirgonj GT Unit-1& 2 | 87 | 82 | 87 | 85 | 82 | 32 | 35 | 60 | 60 | 95 | 94 | 90 | 92 | 52 | 57 | 57 | 55 | 50 |  | 57 | 90 | 27 | 87 | 82 | 83 | 87 | 1828000
17 | Siddhirganj CCPP-335 MW
18 | Summit Gazipur -2 | [17 empty] | 0 |  | 65 | 150 | 213 | 300 | 301 | 200 | 95 | 1319781
19 | Ashuganj 195MW Modular | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 0 | 0 | 0 | 8 | 8 | 8 | 8 | 184000
20 | Ghorasal ST: Unit-1,2 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 680000
21 | Ghorasal GT: Unit-3 | 94 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 96 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 |  | 95 | 94 | 94 | 94 | 94 | 94 | 94 | 2411200
22 | Ghorasal GT: Unit-4 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 102 | 98 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2404000
23 | Ghorasal ST: Unit-5 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2772000
24
25 | Ghorasal ST: Unit-7 | 300 | 300 | 300 | 300 | 300 | 250 | 250 | 250 | 260 | 300 | 300 | 300 | 300 | 300 | 280 | 280 | 280 | 280 |  | 260 | 260 | 250 | 240 | 250 | 250 | 250 | 6670063
26
28 | Ashuganj ST: Unit- 3
29 | Ashuganj ST: Unit- 4
30 | Ashuganj ST: Unit- 5 | 125 | 125 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 0 | 0 | [5 empty] | 1602880
32 | Ashuganj Engines TSK | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 30 | 27 | 27 | 29 | 33 | 0 | 0 | [12 empty] | 404640
33 | Ashuganj CCPP 225 MW | 215 | 182 | 203 | 204 | 182 | 182 | 202 | 190 | 206 | 183 | 184 | 206 | 147 | 182 | 182 | 183 | 182 | 182 |  | 0 | 0 |  |  | 0 | 110 | 100 | 3658000
34 | Ashuganj CCPP(South) | 320 | 300 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 320 | 320 | 320 | 300 | 345 | 320 | 320 | 320 | 280 |  | 240 | 240 | 220 | 220 | 220 | 220 | 220 | 6925500
| Ashuganj CCPP(North) | 360 | 320 | 300 | 300 | 300 | 300 | 270 | 270 | 270 | 320 | 320 | 320 | 360 | 360 | 320 | 320 | 320 | 290 |  | 250 | 250 | 250 | 220 | 220 | 220 | 220 | 7483500
35 | Ashuganj (Precision) 55MW | 55 | 56 | 55 | 56 | 55 | 55 | 20 | 20 | 49 | 51 | 53 | 52 | 53 | 53 | 52 | 52 | 52 | 53 |  | 0 | 0 |  |  | 25 | 44 | 48 | 1027680
36 | Chandpur CCPP | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 95 | 95 | 96 | 100 | 96 | 96 |  | 100 | 95 | 95 | 100 | 95 | 100 | 100 | 2317710
37 | Tongi GT | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 985874
38 | Haripur GT: Unit-1, 2
39 | Haripur 412 MW CCPP | 331 | 327 | 335 | 365 | 335 | 330 | 335 | 349 | 342 | 354 | 328 | 346 | 338 | 348 | 328 | 329 | 328 | 328 |  | 335 | 350 | 333 | 329 | 328 | 327 | 328 | 8163330
40 | Meghnaghat CCPP 450MW | 400 | 400 | 370 | 370 | 370 | 370 | 350 | 350 | 400 | 400 | 400 | 400 | 400 | 420 | 420 | 420 | 420 | 370 |  | 350 | 380 | 380 | 340 | 340 | 340 | 340 | 8963000
41 | Haripur Power CCPP 360MW | 335 | 335 | 308 | 308 | 308 | 309 | 278 | 278 | 330 | 329 | 329 | 336 | 337 | 336 | 338 | 336 | 337 | 318 |  | 289 | 290 | 288 | 320 | 300 | 300 | 300 | 7544000
42 | Mymensingh RPCL 210MW | 146 | 150 | 146 | 146 | 155 | 155 | 151 | 151 | 145 | 147 | 147 | 145 | 144 | 147 | 144 | 144 | 145 | 147 |  | 147 | 145 | 149 | 147 | 147 | 148 | 148 | 3458760
43 | Haripur NEPC 110MW | 27 | 0 | [7 empty] | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 |  | 55 | 86 | 110 | 110 | 110 | 55 | 13 | 773700
44 | Fenchugonj CCPP-1 | 58 | 58 | 58 | 58 | 58 | 58 | 50 | 59 | 55 | 55 | 56 | 55 | 55 | 53 | 53 | 53 | 53 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 58 | 1329000
45 | Fenchugonj CCPP-2 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 0 | 0 |  |  |  | 0 |  |  |  |  | 40 | 40 | 40 | 40 | 889040
46 | Shajibazar 330 MW | 250 | 254 | 254 | 250 | 248 | 250 | 252 | 250 | 253 | 253 | 253 | 248 | 246 | 251 | 250 | 248 | 247 | 252 |  | 251 | 249 | 249 | 250 | 247 | 250 | 250 | 5634000
47 | Shahjibazar GT: Unit- 8, 9 | 62 | 45 | 61 | 62 | 64 | 63 | 62 | 63 | 63 | 59 | 61 | 59 | 60 | 61 | 61 | 58 | 61 | 61 |  | 61 | 63 | 63 | 61 | 63 | 58 | 58 | 1445088
48 | Shahjibazar 86MW | 77 | 77 | 74 | 74 | 74 | 10 | 10 | 10 | 10 | 50 | 50 | 75 | 71 | 74 | 74 | 76 | 77 | 40 |  | 70 | 77 | 77 | 77 | 77 | 78 | 78 | 1429440
49 | Shahjibazar (EPL) 50MW | 44 | 44 | 44 | 44 | 45 | 45 | 10 | 45 | 44 | 43 | 43 | 43 | 43 | 44 | 44 | 44 | 44 | 20 |  | 20 | 45 | 45 | 45 | 45 | 45 | 45 | 945000
50 | Sylhet GT 150 MW | 105 | 105 | 115 | 110 | 110 | 108 | 121 | 113 | 123 | 108 | 108 | 122 | 109 | 108 | 110 | 108 | 108 | 109 |  | 109 | 108 | 134 | 112 | 108 | 109 | 112 | 2782340
51 | Sylhet GT 20 MW | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 19 | 19 | 19 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 438000
52 | Sylhet (EPL) 50MW | 44 | 44 | 44 | 44 | 44 | 10 | 0 | 43 | 43 | 43 | 43 | 43 | 44 | 44 | 43 | 44 | 44 | 22 |  | 45 | 46 | 46 | 46 | 46 | 47 | 47 | 978340
53 | Sylhet (Desh) 10MW | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 239400
54 | Hobiganj 11MW | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 252624
55 | Fenchugonj (Barakatullah) 51MW | 50 | 50 | 50 | 50 | 50 | 11 | 11 | 11 | 11 | 11 | 11 | 34 | 47 | 50 | 50 | 52 | 49 | 25 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 925800
56 | Shahjahanulla 25 MW | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 16 | 16 | 16 | 16 | 23 | 23 | 16 | 23 | 23 | 23 | 23 |  | 23 | 23 | 23 | 23 | 23 | 24 | 24 | 510456
57 | Summit Bibiana- 2 | 250 | 240 | 245 | 240 | 240 | 230 | 240 | 250 | 260 | 265 | 250 | 280 | 275 | 260 | 250 | 270 | 260 | 250 |  | 250 | 240 | 240 | 260 | 265 | 250 | 250 | 6245250
58 | Southern 55MW | 55 | 55 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 20 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1041566
59 | Sikalbaha (Energis) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 16 | 501600
60 | Barabkunda (Regent) | 15 | 15 | 15 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 19 | 19 | 19 | 19 | 19 | 19 | 417168
61 | Narshingdi (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 16 | 16 | 16 | 16 | 16 | 19 | 19 | 19 | 19 | 19 |  | 0 | 0 | 0 | 19 | 19 | 22 | 22 | 388440
62 | Tangail (Doreen) 22MW | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 450684
63 | Tripura | 170 | 168 | 168 | 160 | 150 | 138 | 132 | 136 | 134 | 136 | 150 | 138 | 142 | 172 | 170 | 164 | 154 | 154 |  | 182 | 184 | 180 | 190 | 186 | 180 | 174 | 3843840
64 | Malancha, Ctg. EPZ (United) | 36 | 37 | 34 | 34 |  | 20 | 6 | 6 | 3 | 2 | 2 | 2 | 7 | 2 | 2 | 8 | 3 | 3 |  | 28 | 24 | 26 | 26 | 30 | 37 | 38 | 402720
65 | Feni (Doreen) 22MW | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 20 | 20 | 19 | 19 | 20 | 20 | 20 |  | 21 | 21 | 22 | 22 | 22 | 22 | 22 | 501048
66 | Feni, Mohipal (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 257220
67 | Jangalia (Summit) 33MW | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 24 | 24 | 24 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 619900
68 | Summit Cumilla 25MW | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 512370
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 32 | 31 | 31 | 30 | 30 | 31 | 31 | 31 |  | 18 | 18 | 27 | 32 | 31 | 30 | 30 | 690480
71 | Summit Maona | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 0 | 25 | 0 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 647000
72 | Summit Rupganj | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 16 | 592300
73 | Ghorashal (Regent) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 102 | 102 | 108 | 105 | 62 |  | 62 | 62 | 22 | 22 | 22 | 21 | 22 | 682681
76 | Siddhirganj Desh
77 | Siddhirganj (Dutch Bangla) | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 8 | 50 | 85 | 89 | 95 | 98 | 85 | 60 | 50 |  | 55 | 70 | 94 | 100 | 100 | 100 | 40 | 1186560
78 | Gazipur (RPCL) | 40 | 43 | 32 | 32 | 32 | 16 | 16 | 24 | 32 | 34 | 40 | 40 | 40 | 39 | 39 | 39 | 42 | 47 |  | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 915240
79 | Kodda 149MW | 145 | 140 | 55 | 48 | 40 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 62 | 62 | 62 | 60 | 30 | 30 |  | 100 | 140 | 140 | 140 | 140 | 144 | 144 | 1603680
80 | Jamalpur 95MW | 61 | 60 | 60 | 32 | 32 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 48 | 60 | 80 | 92 | 50 | 50 |  | 72 | 93 | 93 | 94 | 94 | 94 | 94 | 1254720
81 | Lakdhanvi 52 MW | 52 | 52 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 36 | 52 | 52 | 52 | 52 | 52 | 50 | 52 | 52 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 1070712
| Gazipur 100 MW | 109 | 109 | 109 | 108 | 108 | 108 | 72 | 80 | 109 | 109 | 109 | 109 | 109 | 109 | 108 | 108 | 108 | 108 |  | 108 | 108 | 108 | 108 | 108 | 106 | 106 | 2528232
| Kaptai Solar | [5 empty] | 0 | 1.6 | 2.8 | 4 | 4.8 | 5.3 | 5.4 | 4.7 | 0 | 0 | 2.3 | 0.9 | 0 | [8 empty] | 36648
82 | Madanganj 102MW | 48 | 48 | 48 | 30 | 0 |  |  | 2 | 15 | 15 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 42 | 55 | 80 | 81 | 30 | 30 | 879096
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj (Powerpac) 100MW | 0 | [18 empty] | 16 | 70 | 73 | 88 | 88 | 50 | 10 | 359598
86 | Meghnaghat CCPP(Summit) | 280 | 240 | 300 | 300 | 240 | 280 | 290 | 285 | 305 | 260 | 270 | 295 | 270 | 200 | 295 | 280 | 260 | 255 |  | 265 | 210 | 235 | 275 | 246 | 265 | 285 | 6595229
87 | Meghnaghat (IEL) | 65 | 25 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 |  | 20 | 50 | 75 | 100 | 100 | 85 | 40 | 696960
88 | Ghorashal 78MW (MAX) | [14 empty] | 20 | 40 | 50 | 50 |  | 50 | 50 | 20 | 20 | 20 | 20 | 20 | 373184
90 | Ashuganj (United) 53MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 0 | 0 | 0 | 0 | 5 | 5 | 5 | 105000
91 | Juldah (Acorn) | 89 | 88 | 88 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 50 | 78 | 50 | 50 | 50 |  | 78 | 78 | 78 | 86 | 90 | 82 | 84 | 1106760
92 | Fenchuganj (EPL) 44MW | 50 | 50 | 50 | 47 | 47 | 10 | 10 | 10 | 10 | 36 | 44 | 44 | 41 | 47 | 46 | 49 | 49 | 20 |  | 41 | 50 | 50 | 50 | 50 | 50 | 50 | 1000800
93 | Ashuganj (Midland) 51MW | 35 | 35 | 35 | 35 | 35 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 35 | 35 | 35 | 35 | 35 | 35 |  | 0 | 0 |  |  | 12 | 7 | 7 | 535160
94 | Gagnagar (Orion) | 68 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 15 | 65 | 100 | 100 | 99 | 99 | 65 | 32 | 32 |  | 50 | 100 | 99 | 100 | 100 | 100 | 100 | 1361952
95 | Patenga 50MW | 47 | 43 | 43 | 46 | 47 | 47 | 47 | 47 | 40 | 28 | 41 | 46 | 46 | 46 | 46 | 46 | 45 | 46 |  | 46 | 46 | 46 | 47 | 46 | 46 | 46 | 1076160
96 | Chattogram ECPV 108 MW | 90 | 87 | 90 | 90 | 90 | 71 | 18 | 20 | 50 | 63 | 83 | 83 | 83 | 83 | 88 | 83 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 1896960
97 | Katpotti 51 MW | 13 | 14 | 13 | 13 | 13 | 14 | 13 | 13 | 13 | 8 | 6 | 6 | 6 | 6 | 6 | 6 | 8 | 8 |  | 14 | 14 | 17 | 49 | 49 | 49 | 49 | 425414
98 | Bosila 108MW | 65 | 66 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 57 | 62 | 63 | 63 | 62 | 60 | 60 | 60 | 60 |  | 60 | 61 | 63 | 63 | 63 | 64 | 64 | 1204800
99 | Madanganj-55 MW | 15 | 0 | [7 empty] | 0 | 44 | 55 | 55 | 55 | 55 | 30 | 15 | 15 |  | 22 | 55 | 55 | 55 | 55 | 55 | 55 | 708414
100 | Northern 55 MW | 56 | 56 | 18 | 18 | 18 | 18 | 18 | 36 | 37 | 56 | 56 | 56 | 56 | 56 | 0 | 56 | 56 | 56 |  | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 1025760
101 | Kushiara 163 MW CCPP GT | 130 | 130 | 130 | 130 | 130 | 130 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 130 | 163 | 163 | 163 | 130 |  | 130 | 163 | 163 | 163 | 163 | 130 | 130 | 3296381
102 | Sarishabari (Solar) | [8 empty] | 1.6 | 2 | 2.2 | 0.8 | 2.2 | 1.9 | 1.1 | 0.4 | 0.3 | 0 | [8 empty] | 11000
103 | Banco Energy 54MW | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 867240
104 | APR Energy , Keranigonj | [19 empty] | 107 | 213 | 175 | 107 | 106 | 0 |  | 436195
105 | Bramhangoan 100 MW (Aggreko) | [19 empty] | 10 | 51 | 51 | 51 | 51 | 0 |  | 162719
106 | United Mymensingh PPL | 150 | 150 | 150 | 100 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 14 | 40 | 48 | 27 | 27 |  | 58 | 100 | 110 | 122 | 163 | 170 | 180 | 1716000
112 | Aggreko Aurahati 100MW | [19 empty] | 11 | 103 | 104 | 53 | 52 | 0 |  | 223242
114 | Summit Gazipur-1 150MW | 149 | 133 | 79 | 102 | 51 | 15 | 15 | 15 | 44 | 46 | 46 | 46 | 46 | 46 | 83 | 93 | 70 | 67 |  | 72 | 149 | 149 | 149 | 149 | 149 | 149 | 2005920
115 | Juldah 100 MW Unit-3 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2449920
116 | Chandpur Desh 200MW | 198 | 199 | 167 | 128 | 129 | 124 | 90 | 88 | 88 | 108 | 140 | 146 | 170 | 200 | 200 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 198 | 196 | 196 | 3983520
117 | Midland 150MW | 150 | 120 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 63 | 125 | 130 | 135 | 80 | 80 |  | 0 | 0 | 0 | 0 | 15 | 60 | 6 | 1115709
118 | Bibiyana-3 285 MW | 250 | 250 | 250 | 249 | 249 | 199 | 201 | 200 | 200 | 295 | 291 | 283 | 287 | 290 | 287 | 288 | 251 | 200 |  | 201 | 249 | 249 | 250 | 250 | 248 | 249 | 6019000
| United Jamalpur PPL | 95 | 95 | 95 | 97 | 97 | 97 | 42 | 45 | 45 | 85 | 85 | 96 | 95 | 95 | 93 | 93 | 93 | 94 |  | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 2074800
| Anwara United | 104 | 117 | 117 | 117 | 117 | 110 | 116 | 116 | 116 | 133 | 118 | 135 | 125 | 130 | 132 | 135 | 135 | 122 |  | 132 | 137 | 135 | 132 | 132 | 150 | 150 | 3008400
120 | Eastern Zone Total | 8302 | 7900 | 7413 | 7231 | 6828 | 6296.5 | 5893.5 | 6043.3 | 6436.3 | 6847.1 | 7154.9 | 7323.8 | 7349.7 | 7751.1 | 7848.9 | 7869.1 | 7551.6 | 7122 |  | 7280 | 8336 | 8355 | 8574 | 8618 | 8294 | 7841 | 179937488
121
122
123 | Khulna 60MW
124 | Khulna (KPCL-1 & 3)
125 | Khulna (KPCL-2) | 99 | 99 | 66 | 66 | 32 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 32 | 40 | 66 | 32 | 32 | 32 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 1355520
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur Peaking | 36 | 36 | 36 | 36 | 6 | 0 | [11 empty] | 36 |  | 34 | 34 | 32 | 32 | 32 | 32 | 32 | 372000
| Khulna CCPP 225MW | 236 | 170 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 150 | 180 | 220 | 233 | 235 | 200 | 125 | 3662400
129 | Labon Chora 105 MW | 105 | 105 | 70 | 70 | 70 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 105 | 105 | 105 | 105 | 105 | 65 |  | 105 | 95 | 90 | 90 | 90 | 90 | 90 | 1800000
130
131
132
133
| Summit Barisal 110 MW | 110 | 110 | 110 | 80 | 32 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 64 | 105 | 110 | 110 | 110 | 110 | 110 | 1299840
136 | Barisal GT: Unit-1, 2 | [20 empty] | 10 | 12 | 12 | 24 | 12 | 12 | 66665
137 | Bhola Aggreko 95MW | 96 | 96 | 96 | 95 | 95 | 97 | 97 | 95 | 95 | 92 | 92 | 92 | 92 | 92 | 93 | 93 | 95 | 54 |  | 94 | 95 | 97 | 97 | 97 | 97 | 97 | 2241723
| Bhola CCPP 194MW | 173 | 173 | 173 | 173 | 173 | 173 | 176 | 173 | 173 | 173 | 173 | 174 | 174 | 173 | 173 | 173 | 173 | 173 |  | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 4216060
140 | Bhola (Venture) 33MW | 34 | 31 | 33 | 32 | 33 | 27 | 23 | 20 | 18 | 17 | 19 | 22 | 17 | 26 | 28 | 28 | 28 | 27 |  | 38 | 39 | 39 | 40 | 38 | 38 | 37 | 693636
141 | Bangla Trak Noapara | 94 | 0 | [17 empty] | 13 | 80 | 82 | 97 | 96 | 96 | 30 | 591360
142 | Noapara (KZA) 40MW | 40 | 40 | 40 | 40 | 40 | 16 | 16 | 16 | 16 | 16 | 16 | 0 | 16 | 24 | 40 | 40 | 40 | 16 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 696750
143 | Gopalganj Peaking | 50 | 50 | 50 | 50 | 0 | [10 empty] | 13 | 40 | 43 |  | 72 | 64 | 50 | 52 | 52 | 52 | 52 | 593920
144 | Bheramara GT-1,2,3 | 32 | 0 | [17 empty] | 16 | 16 | 16 | 48 | 48 | 32 | 32 | 227300
145 | Madhumati Power Plant | 107 | 108 | 108 | 107 | 108 | 53 | 54 | 53 | 53 | 54 | 53 | 53 | 107 | 107 | 107 | 107 | 107 | 107 |  | 108 | 108 | 107 | 107 | 107 | 107 | 107 | 2223648
146 | Bheramara HVDC | 935 | 935 | 936 | 936 | 936 | 936 | 936 | 937 | 936 | 937 | 936 | 936 | 936 | 936 | 936 | 936 | 936 | 936 |  | 939 | 939 | 939 | 939 | 939 | 939 | 940 | 22473454
147 | Bheramara 360 MW
148
149
150 | Barapukuria Unit-1
151 | Barapukuria Unit-2 | 65 | 65 | 66 | 66 | 67 | 67 | 67 | 66 | 67 | 67 | 67 | 67 | 65 | 64 | 65 | 66 | 65 | 65 |  | 67 | 67 | 68 | 68 | 68 | 68 | 67 | 1575709
152 | Barapukuria Unit-3 | 199 | 200 | 200 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 200 | 200 | 200 | 199 | 199 | 199 | 199 |  | 199 | 199 | 199 | 200 | 199 | 199 | 199 | 4876300
153 | Baghabari GT 71MW | 55 | 55 | 55 | 55 | 60 | 60 | 60 | 60 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 60 | 55 | 55 | 55 | 60 | 55 | 1350000
156 | Baghabari GT 100MW
| Baghabari Peaking 50MW | 50 | 50 | 50 | [16 empty] | 42 | 50 | 50 | 50 | 50 | 50 | 50 | 418376
157 | Sirajgonj Unit-1 225MW (Gas) | 159 | 155 | 162 | 173 | 162 | 157 | 160 | 171 | 167 | 197 | 201 | 196 | 189 | 193 | 182 | 185 | 182 | 181 |  | 185 | 189 | 185 | 184 | 183 | 179 | 181 | 4554682
158 | Sirajgonj Unit-1 225MW (Oil)
| Sirajgonj Unit-2 225MW (Gas) | 151 | 146 | 153 | 165 | 152 | 145 | 145 | 161 | 158 | 161 | 146 | 160 | 198 | 192 | 179 | 182 | 179 | 179 |  | 194 | 194 | 190 | 174 | 181 | 178 | 179 | 4242536
Sirajgonj Unit-2 225MW (Oil)
159 | Sirajgonj Unit-3 225 MW(Gas) | 175 | 171 | 169 | 175 | 174 | 165 | 167 | 175 | 175 | 175 | 174 | 175 | 190 | 207 | 206 | 204 | 200 | 199 |  | 203 | 200 | 200 | 192 | 196 | 198 | 198 | 4683636
Sirajgonj Unit-3 225 MW(Oil)
160 | Sirajgonj Unit-4 414 MW(Gas) | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 411 | 412 | 370 | 370 | 370 | 300 |  | 272 | 320 | 291 | 350 | 350 | 300 | 300 | 8447270
161 | Bera Peaking | 33 | 24 | [17 empty] | 5 | 12 | 33 | 33 | 33 | 33 | 0 | 210254
162 | Bogra (GBB) | 22 | 22 | 11 | 18 | 16 | 5 | 5 | 5 | 18 | 18 | 18 | 21 | 21 | 21 | 21 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 425760
163 | Bogra (EPL) | 16 | 16 | 16 | 16 | 16 | 12 | 3 | 3 | 3 | 10 | 14 | 13 | 13 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 17 | 17 | 317592
164 | Ullapara (Summit) | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 5 | 5 | 8 | 8 | 8 | 5 | 5 | 5 | 8 | 8 |  | 11 | 11 | 11 | 11 | 11 | 11 | 0 | 217100
165 | Amnura 50MW | 50 | 34 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 35 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 0 | 18 | 0 |  | 618660
166 | Katakhali (Northern) | 16 | 16 | [12 empty] | 16 | 16 | 16 | 16 |  | 16 | 34 | 50 | 50 | 24 | 8 | 0 | 241180
167 | Katakhali Peaking | 0 | [18 empty] | 44 | 45 | 47 | 44 | 44 | 0 |  | 158895
168 | Santahar Peaking | 35 | 10 | [17 empty] | 31 | 35 | 36 | 34 | 35 | 35 | 35 | 256995
169 | Rajlanka 52 MW | 41 | 34 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 24 | 37 | 48 | 48 | 24 | 24 |  | 50 | 50 | 50 | 50 | 50 | 8 | 0 | 567840
170 | Chapainawabganj-100 MW | 85 | 55 | 55 | 55 | 32 | 16 | 16 | 16 | 16 | 16 | 0 | 0 | [7 empty] | 70 | 95 | 95 | 95 | 90 | 30 | 0 | 799616
171 | Paramount Baghabari
172 | Confidence Bogura-2 (CPBL) | 107 | 75 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 26 | 53 | 53 | 75 | 90 | 90 | 90 | 90 | 101 |  | 108 | 108 | 108 | 108 | 108 | 108 | 107 | 1677792
173 | Rangpur GT | 17 | [18 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 119000
175 | Saidpur GT | 17 | [18 empty] | 18 | 18 | 17 | 17 | 17 | 17 | 17 | 129000
176 | Confidence Rangpur | 0 | [9 empty] | 0 | 4 | 0 |  | 14 | 14 | 6 | 52 |  | 51 | 0 | 0 |  |  |  |  | 429120
177
178
178 | Western Zone Total | 3801 | 3442 | 3173 | 3125 | 2921 | 2710 | 2706 | 2732 | 2728 | 2775 | 2781 | 2786 | 3076 | 3166 | 3200 | 3185 | 3174 | 3092 | 0 | 3687 | 3885 | 3912 | 3955 | 3963 | 3671 | 3436 | 78831589