## Forecast
8 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2022-08-17 | Wednesday
|  |  | Date (day): | 2022-08-17 |  | Wednesday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11904.6 | MW |  |  | (b) At Evening Peak Hour : |  | 13880 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2022-08-16 | 2022-08-17 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 300 | 300 | 300 | 300 |  | 65 | Machine problem
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 89 | 81 | 92 | 92 |  | 16 | Engine problem
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 408 | 398 | 412 | 412
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 330 | 321 | 330 | 330 | 30 |  | Gas shortage
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 8 | 47 | 8 | 50 | 50 |  | Fuel shortage
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 0 | 0 | 0 | 0 |  | 102 | Under maint
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 30 | 30 | 30 | 30 |  | 25 | Engine problem
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 16 | 22 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 193 | 95 | 100 | 100 | 110 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 8 | 32 | 8 | 32 | 68 |  | Fuel shortage
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 8 | 32 | 8 | 32 | 70 |  | Fuel shortage
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 54 | 17 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 16 | 125 | 16 | 132 |  | 17 | Engine problem
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 35 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 44 | 50 | 50 | 50 |  | 30 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 24 | 25 | 24
| 29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 41 | 41 | 41 | 41 |  | 11 | Engine problem
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 95 | 296 | 95 | 285 |  | 15 | Engine problem
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 103 | 301 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 92 | 81 | 60 | 96
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 94 | 86 | 86 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 35 | 149 | 35 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 88 | 105 | 88 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 17 | 34 | 17 | 34 | 70 |  | Fuel shortage
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 35 | 162 | 35 | 162 |  |  | Fuel shortage
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 31 | 0 | 30 | 0
| 40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 47 | 55 | 55 | 55
|  | Dhaka area Total |  |  |  |  | 6263 | 5847 | 2923 | 3694 | 2813 | 3760 | 1119 | 961
| 41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 105 | 105 | 105 | 105 | 75 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 16 | 25 | 25 | 25
| 43 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 17 | 0 | 20 | 0
| 44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 6 | 42 | 6 | 42 |  | 8 | Engine problem
| 45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 147 | 150 | 145 | 145 |  | 85 | Low Water Level
| 46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | S/D due to HGPI
| 47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
| 48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 17 | 51 | 17 | 105 |  |  | Fuel shortage
| 49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 26 | 26 | 26 | 26 | 72 |  | Fuel shortage
| 50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 17 | 51 | 17 | 51 | 51 |  | Fuel shortage
| 51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 33 | 33 | 33 | 33 | 67 |  | Fuel shortage
| 52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 21 | 21 | 21 | 21 |  | 79 | Engine problem
| 53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 10 | 14 | 15 | 15 |  | 7 | Engine problem
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 5 | 29 | 7 | 30
| 54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 12 | 91 | 12 | 95 |  |  | Fuel shortage
| 55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 3 | 0 | 5 | 0
| 56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 123 | 213 | 123 | 210 | 90 |  | Fuel shortage
| 57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 36 | 36 | 36 | 36 |  | 18 | Engine problem
| 58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 55 | 55 | 0 | 0 |  | 110 | Under maint
| 59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 20 | 20 | 20 | 100 |  |  | Fuel shortage
| 60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 107 | 107 | 107 | 107 |  | 9 | Engine problem
|  | Mirsharai 150 MW |  | Gas/HSD | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 776 | 1069 | 740 | 1146 | 535 | 691
| 61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 205 | 206 | 205 | 210 |  |  | Gas shortage
| 63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 335 | 330 | 330 | 330 | 30 |  | Gas shortage
| 64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 325 | 310 | 310 | 320 | 40 |  | Gas shortage
|  | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+136*1 | 284 | 284 | 0 | 0 | 0 | 0 |  |  | On test.
| 65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 40 | 40 | 35 | 35 |  | 10 | Engine problem
| 66 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 55 | 52 | 55 | 55 | 55
| 67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 26 | 8 | 8 | 187 |  | Gas shortage
| 68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 51 | 51 | 51
| 69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 124 | 133 | 125 | 133 |  | 17 | Engine problem
| 70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 40 | 37 | 40 | 40 |  | 12 | Engine problem
| 71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 142 | 140 | 142 |  | 21 | Machine problem
| 72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 200 | 200 | 200 | 200
| 73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 22 | 22 | 22
| 74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 10 | 10 | 10 | 10
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 134 | 168 | 143 | 166
| 75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 | 52 |  | Fuel shortage
| 77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 17 | 20 | 21 |  | 4 | Engine problem
| 78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 150 | 200 | 200 | 200
| 79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 0 | 0 | 114 |  | Fuel shortage
| 80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 58 | 9 | 57 | 56 |  | Fuel shortage
| 81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 35 | 35 | 35 | 35 |  | 19 | 33 kV feeder fault
| 82 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 96 | 95 | 96 | 100 | 15 |  | Fuel shortage
|  | Cumilla Area Total |  |  |  |  | 3193 | 3169 | 1928 | 2168 | 2067 | 2168 | 628 | 83
| 83 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 131 | 101 | 130 | 100 | 102 |  | Gas shortage
| 84 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 85 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0 |  | 8 | Under maint.
| 86 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 87 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 77 | 180 | 80 | 180 |  | 20 | Engine problem
| 88 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 68 | 79 | 68 | 79 |  | 36 | Engine problem
| 89 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 54 | 0 | 50 | 0
| 90 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 12 | 12 |  | 10 | Engine problem
|  | Mymensingh Area Total |  |  |  |  | 717 | 614 | 366 | 394 | 363.6 | 393 | 102 | 74
| 91 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 43 | 43 | 43 |  | 27 | Machine problem.
| 92 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 |  | 60 | Machine problem
| 93 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 | 163 |  | Gas shortage
| 94 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
| 95 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 5 | 5 | 5 | 5 | 46 |  | Gas shortage
| 96 | Fenchuganj 44MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 5 | 5 | 5 | 5 | 45 |  | Gas shortage
| 97 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0
| 98 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 60 | 63 | 62 | 64
| 99 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 10 | 81 | 10 | 80
| 100 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
| 101 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 193 | 221 | 220 | 220
| 102 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Gas shortage
| 103 | Sylhet 50MW PP (EPL) |  | Gas | NENP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Gas shortage
| 104 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 0 | 0 | 0 | 0 | 25 |  | Gas shortage
| 105 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 280 | 300 | 300 |  |  | FGMO
| 106 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 405 | 402 | 400 | 400
| 107 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 9 | 10 | 10 | 10
| 108 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 400 | 400 | 400 | 400
|  | Sylhet Area Total |  |  |  |  | 2522 | 2477 | 1460 | 1540 | 1485 | 1557 | 349 | 517
| 109 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 884 | 884 | 924 | 924
| 110 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 16 | 16 | 16 | 66 | 49 |  | Fuel shortage
| 111 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 37 | 0 | 36 |  | 18 | Engine problem
| 112 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 222 | 223 | 225 | 225
| 113 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 31 | 65 | 35 | 65 |  | 44 | Engine problem
| 114 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 220 | 160 | 200 | 180 | 230 |  | Gas shortage
| 115 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 0 | 0 | 0 | 40 |  | Fuel shortage
| 116 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 10 | 93 | 90 | 90 |  | 10 | Engine problem
| 117 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 17 | 53 | 17 | 52 | 53 |  | Fuel shortage
| 118 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 89 | 105 | 90 | 105
| 119 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 91 | 0 | 100 | 0
|  | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
|  | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
|  | Khulna Area Total |  |  |  |  | 2388 | 2384 | 1580 | 1636 | 1697 | 1743 | 388 | 72
| 120 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 16 | 110 | 32 | 110 |  |  | Line O/L
| 121 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 18 | 30 | 19 | 30 |  | 10 | Engine problem
| 122 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 150 | 149 | 151 | 151
|  | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
| 123 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 622 | 610 | 620 | 620 |  |  | Line O/L
| 124 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 0 | 0 | 0 | 0 |  | 220 | Machine problem
| 125 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 15 | 150 | 150 | 150 |  |  | Line O/L
|  | Barisal Area Total |  |  |  |  | 1958 | 1958 | 821 | 1049 | 972 | 1061 | 0 | 230
| 126 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 127 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 24 | 30 | 32 | 32 |  | 20 | Engine problem
| 128 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 40 | 0 | 40 |  | 31 | Engine problem
| 129 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 130 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 42 | 50 | 42 | 50
| 131 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 32 | 16 | 40 |  | 10 | Engine problem
| 132 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 175 | 160 | 170 | 150 | 60 |  | Gas shortage
| 133 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 209 | 215 | 220 | 220
| 134 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 165 | 150 | 160 | 150 | 70 |  | Gas shortage
| 135 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 414 | 321 | 400 | 380 | 34 |  | Gas shortage
| 136 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 33 | 32 | 33 | 33 |  | 17 | Engine problem
| 137 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 21 | 22 | 21 | 22
| 138 | Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 139 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 8 | 11 | 11
| 140 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 8 | 8 | 8 | 44 |  | Fuel shortage
| 141 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 39 | 78 | 50 | 80 |  | 24 | Engine problem
| 142 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 52 | 168 | 100 | 175 |  | 25 | Fuel shortage
| 143 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 50 | 94 | 50 | 94 |  | 19 | Engine problem
| 144 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 55 | 95 | 55 | 95 |  | 18 | Engine problem
| 145 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2129 | 1303 | 1503 | 1374 | 1580 | 379 | 164
| 146 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 80 | 80 | 80 | 80
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
| 147 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 250 | 250 | 250 | 250 | 24 |  | Machine problem
| 148 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
| 149 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
| 150 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 55 | 91 | 55 | 90 |  |  | Engine problem
| 151 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5 | 0 | 8 | 0
| 152 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 17 | 52 | 0 | 52 |  | 63 | Fuel shortage
|  | Rangpur Area Total |  |  |  |  | 800 | 720 | 407 | 473 | 393 | 472 | 64 | 148
|  | Total |  |  |  |  | 22482 | 21680 | 11564 | 13526 | 11904.6 | 13880 | 3564 | 2940
| A. |  | 2022-08-16 | (Yesterday) |  |  |  |  | Tuesday
| 1 | Highest Generation : |  |  | 13526 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 10559 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 14100 | MW
| 3 | Day peak Generation : |  |  | 11564 | MW at | 10:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 13384.95 | MW
| 4 | Evening peak Generation : |  |  | 13526 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 529 | MW
| 5 | Total Energy Generation : |  | 283.5601 | MKWHr | By Solar | 1.5714 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
|  | By Gas : | 143.9084 | MKWHr |  | By Oil: | 86.3274 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 23.6141 | MKWHr |  | By Hydro: | 3.5417 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 3564 | MW | Dhaka | 4846.8 | 4846.8 |  | 0 |  | 18:00 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2940 | MW | Chittagong | 1307.4 | 1307.4 |  | 0 |  | 19:00 |  | 569.5334
|  |  |  | Total = |  |  | 6504 | MW | Khulna | 1613.4 | 1443.4 |  | 170 |  | 19:30 |  | 557.5529
| 7 | Total Gas Supplied : |  |  | 1055.89 | MMCFD |  |  | Rajshahi | 1385.6 | 1306.6 |  | 79 |  | 20:00 |  | 561.2392
| 8 | Fuel Cost : | i) Gas : | Taka | 163972917.032 | ii) Oil : | Taka | 1293586325.53 | Comilla | 1317 | 1267 |  | 50 |  | 21:00 |  | 528.984
|  |  | iii) Coal : |  | 184180148.71 | Total | Taka | 1641739391.272 | Mymensingh | 1087 | 907 |  | 180 |  | 22:00 |  | 608.2395
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.0165 | MKWHr. | Sylhet | 559 | 559 |  | 0 |  | 23:00 |  | 1010.9678
|  | ii) During Peak Demand : |  |  | 412 | MW (E to W) at | 21:00 | hrs | Barisal | 397.75 | 397.75 |  | 0 |  | 24:00 |  | 1655.1487
|  | iii) Maximum : |  |  | 272 | MW at | 19:00 | hrs | Rangpur | 871 | 821 |  | 50
| 10 | Maximum Temperature in Dhaka was |  |  |  | 35° C |  |  | Total | 13384.95 | 12855.95 |  | 529
| B. |  | 2022-08-17 | (Today) |  |  |  | Wednesday |  |  | Probable max. temperature in Dhaka |  |  | 34.5° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 14300 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 433 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 13880 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 12200 | MW
| 4 | Reserve(Generation end) |  |  |  | - | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 299.7863 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 11212 | MW at | 6:00 | 0 | 42 | 89 | 86 | 73 | 105 | 0 | 0 | 38
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.7171 | MKWHr. | ii) HVDC Flow at Peak Time |  | 884 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.88 | MKWHr. | iii) Maximum HVDC Flow : |  | 897 | MW at | 23:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 95.95 |  | (b) Today: | 95.9 |  | (c) Rule Curve: |  | 94.12
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2022-08-16
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 300 | 93 | 0 | 407 | 337 |  | 0 | 225 | 0 | 8 | 0 | 30 | 0 | 0 | 195 | 8 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 55 | 0 | 19 | 25 | 19 | 33 | 33 | 41 | 0 | 81 | 65 | 105 | 0 | 25 | 0 | 0 | 0 | 0 |  | 10 | 26 | 51 | 33 | 12 | 6 | 15 | 42 | 0 | 0 | 0 | 335 | 310 | 210 | 8 | 136 | 37 | 56 | 0 | 51 | 0 | 40 | 0 | 22 | 6 | 33 | 20 | 132 | 158 | 0 | 22 | 0 | 43 | 30 | 5 | 5 | 0 | 0 | 62 | 81 | 0 | 220 | 0 | 5 | 9 | 300 | 8 | 0 | 175 | 130 | 187 | 96 | 48 | 96 | 52 | 0 | 21 | 200 | 125 | 402 | 49 | 105 | 17 | 0 | 52 | 36 | 55 | 0 | 28 | 20 | 400 | 0 | 0 | 108 | 107 | 0 | 35 | 0 | 89 | 55 | 0 | 0 | 0 |  | 884 | 0 | 265 | 0 | 16 | 229 | 0 | 0 | 16 | 47 | 8 | 152 | 29 | 48 | 0 | 0 | 0 | 24 | 39 | 60 | 0 | 42 | 0 | 8 | 31 | 22 | 0 | 11 | 71 | 0 | 250 | 0 | 0 | 183 | 0 | 0 | 215 | 0 | 52 | 203 | 0 | 414 | 0 | 174 | 50 | 105 | 56 | 0 | 0 | 55 | 620 | 0 | 0 | 35 | 0 | 0 | 52 | 0 | 0 | 0 |  | 7552 | 4466 | 12018 | 4599 | 884 | 1682 | 780 | 2060 | 941 | 146 | 444 | 565 | 132 | 0 | 259.8842 | 95.95
2:00 | 0 | 0 | 0 | 180 | 300 | 93 | 0 | 406 | 336 |  | 0 | 225 | 0 | 7 | 0 | 30 | 0 | 0 | 194 | 8 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 55 | 0 | 19 | 25 | 19 | 33 | 33 | 41 | 0 | 81 | 65 | 105 | 0 | 25 | 0 | 0 | 0 | 0 |  | 10 | 26 | 51 | 33 | 12 | 6 | 15 | 42 | 0 | 0 | 0 | 335 | 310 | 211 | 8 | 0 | 37 | 56 | 0 | 51 | 0 | 40 | 0 | 0 | 0 | 33 | 20 | 130 | 158 | 0 | 22 | 0 | 43 | 30 | 5 | 5 | 0 | 0 | 56 | 10 | 0 | 220 | 0 | 5 | 9 | 275 | 8 | 0 | 196 | 85 | 159 | 97 | 48 | 96 | 36 | 0 | 21 | 0 | 130 | 401 | 49 | 105 | 1 | 0 | 52 | 10 | 51 | 0 | 4 | 20 | 400 | 0 | 0 | 108 | 107 | 0 | 35 | 0 | 0 | 55 | 0 | 0 | 0 |  | 884 | 0 | 265 | 0 | 16 | 230 | 0 | 0 | 16 | 42 | 0 | 152 | 28 | 48 | 0 | 0 | 0 | 24 | 33 | 46 | 0 | 42 | 0 | 8 | 31 | 22 | 0 | 11 | 75 | 0 | 250 | 0 | 0 | 183 | 0 | 0 | 218 | 0 | 50 | 194 | 0 | 414 | 0 | 100 | 50 | 105 | 55 | 0 | 0 | 55 | 620 | 0 | 0 | 35 | 0 | 0 | 34 | 0 | 0 | 0 |  | 6859 | 4336 | 11195 | 4418 | 884 | 1584 | 698 | 1617 | 945 | 146 | 448 | 543 | 130 | 0 | 297.6687 | 95.95
3:00 | 0 | 0 | 0 | 180 | 300 | 92 | 0 | 406 | 340 |  | 0 | 225 | 0 | 8 | 0 | 30 | 0 | 0 | 197 | 8 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 55 | 0 | 16 | 25 | 19 | 33 | 33 | 41 | 0 | 81 | 65 | 105 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 51 | 33 | 12 | 5 | 15 | 42 | 0 | 0 | 0 | 330 | 310 | 211 | 8 | 0 | 37 | 56 | 0 | 51 | 0 | 40 | 0 | 22 | 0 | 33 | 20 | 130 | 158 | 0 | 22 | 0 | 43 | 30 | 5 | 5 | 0 | 0 | 56 | 10 | 0 | 220 | 0 | 5 | 9 | 285 | 8 | 0 | 150 | 90 | 104 | 97 | 48 | 96 | 35 | 0 | 21 | 68 | 133 | 402 | 49 | 105 | 15 | 0 | 52 | 36 | 51 | 0 | 9 | 20 | 400 | 0 | 0 | 90 | 107 | 0 | 35 | 0 | 60 | 55 | 0 | 0 | 0 |  | 884 | 0 | 270 | 0 | 16 | 229 | 0 | 0 | 16 | 42 | 0 | 152 | 27 | 48 | 0 | 0 | 0 | 24 | 33 | 45 | 0 | 42 | 0 | 8 | 31 | 22 | 0 | 11 | 74 | 0 | 250 | 0 | 0 | 184 | 0 | 0 | 218 | 0 | 0 | 200 | 0 | 414 | 0 | 0 | 50 | 105 | 55 | 0 | 0 | 55 | 620 | 0 | 0 | 35 | 0 | 0 | 34 | 0 | 0 | 0 |  | 6953 | 4194 | 11147 | 4448 | 884 | 1596 | 447 | 1781 | 944 | 146 | 447 | 542 | 130 | 0 | 233.1585 | 95.95
4:00 | 0 | 0 | 0 | 180 | 300 | 92 | 0 | 407 | 336 |  | 0 | 280 | 0 | 8 | 0 | 30 | 0 | 0 | 191 | 8 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 55 | 0 | 16 | 25 | 19 | 33 | 33 | 41 | 0 | 81 | 65 | 105 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 17 | 33 | 12 | 6 | 15 | 42 | 0 | 0 | 0 | 330 | 305 | 212 | 8 | 0 | 37 | 55 | 0 | 51 | 0 | 40 | 0 | 22 | 8 | 33 | 20 | 110 | 158 | 0 | 22 | 0 | 43 | 30 | 5 | 5 | 0 | 0 | 56 | 10 | 0 | 220 | 0 | 5 | 9 | 290 | 8 | 0 | 0 | 85 | 22 | 97 | 48 | 58 | 35 | 0 | 21 | 182 | 137 | 401 | 49 | 105 | 17 | 0 | 52 | 36 | 55 | 0 | 9 | 20 | 400 | 17 | 0 | 35 | 107 | 0 | 35 | 0 | 94 | 55 | 0 | 0 | 0 |  | 884 | 0 | 275 | 0 | 16 | 230 | 0 | 0 | 16 | 42 | 0 | 151 | 25 | 48 | 0 | 0 | 0 | 24 | 33 | 45 | 0 | 42 | 0 | 8 | 31 | 22 | 0 | 11 | 74 | 0 | 250 | 0 | 0 | 187 | 0 | 0 | 218 | 0 | 0 | 201 | 0 | 414 | 0 | 0 | 50 | 105 | 55 | 0 | 0 | 55 | 620 | 0 | 0 | 35 | 0 | 0 | 34 | 0 | 0 | 0 |  | 6798 | 4201 | 10999 | 4454 | 884 | 1649 | 177 | 1897 | 944 | 146 | 448 | 508 | 110 | 0 | 231.3153 | 95.95
5:00 | 0 | 0 | 0 | 180 | 300 | 92 | 0 | 407 | 336 |  | 0 | 400 | 0 | 8 | 0 | 30 | 0 | 0 | 154 | 8 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 55 | 0 | 16 | 25 | 19 | 33 | 33 | 41 | 0 | 81 | 65 | 105 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 17 | 33 | 12 | 6 | 15 | 42 | 0 | 0 | 0 | 335 | 310 | 209 | 8 | 0 | 37 | 55 | 0 | 51 | 0 | 40 | 0 | 22 | 8 | 0 | 20 | 132 | 160 | 0 | 22 | 0 | 43 | 30 | 5 | 5 | 0 | 0 | 56 | 10 | 0 | 220 | 0 | 5 | 9 | 270 | 8 | 0 | 0 | 92 | 0 | 0 | 47 | 0 | 35 | 0 | 21 | 155 | 100 | 401 | 49 | 105 | 17 | 0 | 52 | 36 | 55 | 0 | 9 | 20 | 400 | 17 | 0 | 35 | 107 | 0 | 35 | 0 | 96 | 55 | 0 | 0 | 0 |  | 884 | 0 | 285 | 0 | 16 | 229 | 0 | 0 | 16 | 42 | 0 | 152 | 25 | 48 | 0 | 0 | 0 | 24 | 23 | 45 | 0 | 42 | 0 | 8 | 31 | 22 | 0 | 11 | 74 | 0 | 250 | 0 | 0 | 189 | 0 | 0 | 219 | 0 | 0 | 201 | 0 | 400 | 0 | 0 | 50 | 105 | 56 | 0 | 0 | 55 | 620 | 0 | 0 | 35 | 0 | 0 | 34 | 0 | 0 | 0 |  | 6626 | 4191 | 10817 | 4406 | 884 | 1735 | 0 | 1842 | 944 | 146 | 448 | 499 | 132 | 0 | 352.9632 | 95.95
6:00 | 0 | 0 | 0 | 180 | 300 | 92 | 0 | 406 | 338 |  | 0 | 400 | 0 | 7 | 0 | 30 | 0 | 0 | 115 | 8 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 55 | 0 | 16 | 25 | 19 | 33 | 33 | 41 | 0 | 81 | 65 | 105 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 17 | 33 | 12 | 6 | 15 | 41 | 0 | 0 | 0 | 335 | 310 | 213 | 8 | 0 | 37 | 55 | 0 | 51 | 0 | 40 | 0 | 22 | 8 | 33 | 20 | 124 | 160 | 0 | 22 | 0 | 43 | 30 | 5 | 5 | 0 | 0 | 57 | 10 | 0 | 220 | 0 | 5 | 9 | 270 | 8 | 0 | 0 | 90 | 0 | 0 | 48 | 0 | 35 | 1 | 21 | 155 | 70 | 352 | 49 | 105 | 17 | 0 | 52 | 36 | 55 | 0 | 9 | 20 | 350 | 0 | 1 | 35 | 107 | 0 | 35 | 0 | 96 | 55 | 0 | 0 | 0 |  | 883 | 0 | 290 | 0 | 16 | 230 | 0 | 0 | 0 | 42 | 0 | 149 | 21 | 48 | 0 | 0 | 0 | 24 | 0 | 45 | 0 | 42 | 0 | 8 | 34 | 22 | 0 | 11 | 71 | 0 | 250 | 0 | 0 | 191 | 0 | 0 | 219 | 0 | 0 | 201 | 0 | 360 | 0 | 0 | 50 | 88 | 55 | 0 | 0 | 55 | 620 | 0 | 0 | 35 | 0 | 2 | 34 | 0 | 0 | 0 |  | 6471 | 4096 | 10567 | 4309 | 883 | 1692 | 0 | 1775 | 941 | 146 | 449 | 463 | 124 | 4 | 122.5695 | 95.95
7:00 | 0 | 0 | 0 | 180 | 300 | 93 | 0 | 407 | 337 |  | 0 | 420 | 0 | 8 | 0 | 30 | 0 | 0 | 121 | 8 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 55 | 17 | 16 | 25 | 19 | 33 | 33 | 41 | 0 | 80 | 65 | 105 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 17 | 33 | 12 | 6 | 15 | 40 | 0 | 0 | 0 | 360 | 325 | 209 | 8 | 0 | 37 | 55 | 0 | 51 | 0 | 40 | 0 | 22 | 8 | 33 | 20 | 126 | 157 | 0 | 22 | 0 | 43 | 30 | 5 | 5 | 0 | 0 | 59 | 10 | 0 | 220 | 0 | 6 | 9 | 280 | 8 | 0 | 0 | 85 | 0 | 0 | 48 | 0 | 35 | 3 | 21 | 155 | 50 | 398 | 58 | 105 | 17 | 0 | 52 | 36 | 55 | 0 | 9 | 20 | 380 | 0 | 12 | 35 | 107 | 0 | 35 | 3 | 95 | 55 | 0 | 0 | 0 |  | 884 | 0 | 285 | 0 | 16 | 170 | 0 | 0 | 0 | 36 | 0 | 152 | 20 | 16 | 0 | 0 | 0 | 24 | 0 | 45 | 0 | 8 | 0 | 8 | 33 | 22 | 0 | 11 | 71 | 0 | 250 | 0 | 0 | 199 | 0 | 0 | 130 | 0 | 0 | 201 | 0 | 414 | 0 | 0 | 50 | 89 | 55 | 0 | 1 | 55 | 620 | 0 | 0 | 0 | 1 | 22 | 34 | 0 | 0 | 0 |  | 6637 | 3922 | 10559 | 4433 | 884 | 1775 | 0 | 1676 | 941 | 145 | 300 | 367 | 126 | 42 | 111.5106 | 95.95
8:00 | 0 | 0 | 0 | 180 | 300 | 92 | 0 | 408 | 328 |  | 0 | 420 | 0 | 8 | 0 | 30 | 0 | 0 | 156 | 8 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 16 | 25 | 19 | 33 | 33 | 41 | 0 | 80 | 65 | 105 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 17 | 33 | 12 | 6 | 15 | 18 | 0 | 0 | 0 | 345 | 320 | 208 | 8 | 0 | 37 | 55 | 0 | 51 | 0 | 40 | 0 | 22 | 8 | 0 | 20 | 132 | 156 | 0 | 22 | 0 | 43 | 30 | 5 | 5 | 0 | 0 | 61 | 10 | 0 | 220 | 0 | 6 | 9 | 300 | 8 | 0 | 0 | 95 | 0 | 0 | 76 | 0 | 35 | 2 | 21 | 155 | 58 | 402 | 69 | 88 | 17 | 2 | 120 | 36 | 55 | 0 | 9 | 20 | 400 | 17 | 20 | 35 | 107 | 0 | 35 | 8 | 96 | 55 | 0 | 0 | 0 |  | 884 | 0 | 255 | 0 | 16 | 221 | 0 | 0 | 0 | 36 | 0 | 151 | 19 | 16 | 0 | 0 | 0 | 24 | 0 | 39 | 0 | 8 | 0 | 8 | 33 | 22 | 0 | 11 | 71 | 0 | 250 | 0 | 0 | 184 | 0 | 0 | 168 | 0 | 0 | 193 | 0 | 414 | 0 | 0 | 50 | 89 | 55 | 0 | 2 | 55 | 622 | 0 | 0 | 0 | 3 | 48 | 34 | 0 | 0 | 0 |  | 6796 | 3981 | 10777 | 4386 | 884 | 1762 | 0 | 1820 | 943 | 145 | 389 | 399 | 132 | 85 | #REF! | 95.94
9:00 | 0 | 0 | 0 | 180 | 300 | 89 | 0 | 407 | 330 |  | 0 | 450 | 0 | 7 | 0 | 30 | 0 | 0 | 193 | 8 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 16 | 25 | 19 | 33 | 25 | 41 | 0 | 81 | 65 | 105 | 0 | 16 | 0 | 0 | 0 | 0 |  | 12 | 26 | 17 | 33 | 12 | 6 | 15 | 13 | 0 | 0 | 0 | 320 | 310 | 209 | 8 | 0 | 40 | 55 | 0 | 51 | 0 | 40 | 0 | 22 | 8 | 33 | 20 | 142 | 148 | 0 | 22 | 2 | 43 | 30 | 5 | 5 | 0 | 0 | 62 | 10 | 0 | 221 | 0 | 6 | 9 | 310 | 8 | 0 | 20 | 95 | 104 | 50 | 77 | 50 | 35 | 8 | 21 | 169 | 85 | 402 | 68 | 88 | 17 | 4 | 122 | 36 | 55 | 0 | 9 | 20 | 400 | 17 | 42 | 35 | 107 | 0 | 35 | 23 | 96 | 55 | 0 | 0 | 0 |  | 884 | 0 | 240 | 0 | 16 | 224 | 0 | 0 | 0 | 31 | 0 | 150 | 21 | 16 | 0 | 0 | 0 | 24 | 0 | 39 | 0 | 42 | 0 | 8 | 33 | 22 | 0 | 11 | 74 | 0 | 250 | 0 | 0 | 170 | 0 | 0 | 171 | 0 | 6 | 179 | 0 | 414 | 17 | 8 | 50 | 89 | 55 | 0 | 2 | 55 | 622 | 0 | 0 | 0 | 1 | 76 | 34 | 0 | 0 | 0 |  | 7169 | 4034 | 11203 | 4366 | 884 | 1798 | 238 | 1904 | 946 | 146 | 395 | 397 | 142 | 158 | #REF! | 95.94
10:00 | 0 | 0 | 0 | 180 | 300 | 89 | 0 | 408 | 330 |  | 0 | 450 | 0 | 8 | 0 | 30 | 0 | 0 | 193 | 8 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 16 | 25 | 19 | 33 | 25 | 41 | 0 | 82 | 65 | 105 | 0 | 16 | 0 | 0 | 0 | 0 |  | 12 | 26 | 17 | 33 | 12 | 6 | 10 | 5 | 0 | 0 | 0 | 335 | 325 | 205 | 8 | 50 | 40 | 52 | 0 | 43 | 0 | 40 | 0 | 19 | 10 | 33 | 20 | 134 | 131 | 0 | 22 | 2 | 43 | 30 | 5 | 5 | 0 | 0 | 60 | 10 | 0 | 193 | 0 | 0 | 9 | 300 | 0 | 0 | 150 | 95 | 103 | 92 | 77 | 94 | 35 | 17 | 21 | 200 | 124 | 405 | 68 | 88 | 17 | 3 | 123 | 36 | 55 | 0 | 9 | 20 | 400 | 17 | 54 | 35 | 107 | 0 | 35 | 31 | 96 | 47 | 0 | 0 | 0 |  | 884 | 0 | 220 | 0 | 16 | 222 | 0 | 0 | 0 | 31 | 0 | 150 | 18 | 16 | 0 | 0 | 0 | 24 | 0 | 39 | 0 | 42 | 0 | 8 | 33 | 21 | 0 | 11 | 80 | 0 | 250 | 0 | 0 | 175 | 0 | 0 | 209 | 0 | 10 | 165 | 0 | 414 | 17 | 52 | 50 | 89 | 55 | 0 | 5 | 55 | 622 | 0 | 0 | 15 | 5 | 91 | 17 | 0 | 0 | 0 |  | 7453 | 4111 | 11564 | 4356 | 884 | 1759 | 501 | 1966 | 952 | 147 | 431 | 435 | 134 | 208 | #REF! | 95.94
11:00 | 0 | 0 | 0 | 180 | 300 | 92 | 0 | 403 | 330 |  | 0 | 450 | 0 | 8 | 0 | 30 | 0 | 0 | 95 | 8 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 19 | 25 | 22 | 33 | 25 | 41 | 0 | 82 | 65 | 105 | 0 | 16 | 0 | 0 | 0 | 0 |  | 12 | 26 | 17 | 33 | 11 | 6 | 10 | 3 | 0 | 0 | 0 | 320 | 310 | 207 | 8 | 50 | 37 | 51 | 0 | 43 | 0 | 40 | 0 | 19 | 10 | 25 | 20 | 146 | 117 | 0 | 22 | 2 | 43 | 30 | 5 | 5 | 0 | 0 | 61 | 10 | 0 | 194 | 0 | 0 | 9 | 290 | 0 | 0 | 200 | 80 | 103 | 70 | 78 | 70 | 35 | 20 | 21 | 192 | 135 | 403 | 68 | 88 | 17 | 3 | 123 | 36 | 55 | 0 | 9 | 20 | 395 | 16 | 51 | 35 | 107 | 0 | 35 | 30 | 91 | 36 | 0 | 0 | 0 |  | 884 | 0 | 200 | 0 | 16 | 222 | 0 | 0 | 0 | 20 | 0 | 147 | 22 | 16 | 0 | 0 | 0 | 24 | 0 | 39 | 0 | 42 | 0 | 8 | 33 | 20 | 0 | 11 | 79 | 0 | 250 | 0 | 0 | 184 | 0 | 0 | 212 | 0 | 48 | 149 | 0 | 401 | 17 | 114 | 50 | 71 | 55 | 0 | 3 | 55 | 622 | 0 | 0 | 35 | 6 | 97 | 17 | 0 | 0 | 0 |  | 7274 | 4169 | 11443 | 4171 | 884 | 1739 | 605 | 1939 | 951 | 147 | 434 | 427 | 146 | 212 | #REF! | 95.94
12:00 | 0 | 0 | 0 | 180 | 300 | 92 | 0 | 403 | 322 |  | 0 | 450 | 0 | 7 | 0 | 30 | 0 | 0 | 93 | 8 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 19 | 25 | 22 | 33 | 25 | 41 | 0 | 83 | 65 | 105 | 0 | 16 | 0 | 0 | 0 | 0 |  | 12 | 26 | 17 | 33 | 11 | 6 | 11 | 2 | 0 | 0 | 0 | 320 | 305 | 207 | 8 | 30 | 35 | 50 | 0 | 43 | 0 | 40 | 0 | 21 | 5 | 25 | 20 | 154 | 102 | 0 | 22 | 1 | 43 | 30 | 5 | 5 | 0 | 0 | 59 | 10 | 0 | 213 | 0 | 0 | 9 | 280 | 0 | 0 | 200 | 80 | 104 | 70 | 78 | 70 | 35 | 0 | 21 | 180 | 125 | 402 | 68 | 70 | 17 | 4 | 123 | 36 | 55 | 0 | 9 | 20 | 400 | 17 | 42 | 44 | 107 | 0 | 35 | 35 | 94 | 36 | 0 | 0 | 0 |  | 885 | 0 | 190 | 0 | 16 | 222 | 0 | 0 | 0 | 20 | 0 | 147 | 23 | 32 | 0 | 0 | 0 | 24 | 0 | 38 | 0 | 42 | 0 | 8 | 33 | 18 | 0 | 11 | 79 | 0 | 250 | 0 | 0 | 179 | 0 | 0 | 215 | 0 | 72 | 147 | 0 | 368 | 17 | 170 | 50 | 70 | 55 | 0 | 4 | 55 | 622 | 0 | 0 | 35 | 4 | 105 | 17 | 0 | 0 | 0 |  | 7187 | 4223 | 11410 | 4129 | 885 | 1685 | 686 | 1926 | 951 | 148 | 437 | 429 | 154 | 195 | #REF! | 95.94
13:00 | 0 | 0 | 0 | 180 | 300 | 92 | 0 | 399 | 326 |  | 0 | 450 | 0 | 8 | 0 | 30 | 0 | 0 | 93 | 8 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 22 | 25 | 16 | 33 | 16 | 41 | 0 | 83 | 65 | 105 | 0 | 16 | 0 | 0 | 0 | 0 |  | 12 | 26 | 17 | 33 | 11 | 6 | 14 | 3 | 0 | 0 | 0 | 320 | 305 | 204 | 16 | 31 | 35 | 50 | 0 | 43 | 0 | 40 | 0 | 21 | 10 | 29 | 20 | 92 | 95 | 0 | 22 | 1 | 43 | 30 | 5 | 5 | 0 | 0 | 60 | 10 | 0 | 220 | 0 | 0 | 10 | 290 | 0 | 0 | 200 | 80 | 104 | 70 | 78 | 70 | 34 | 19 | 21 | 180 | 125 | 402 | 68 | 70 | 17 | 3 | 123 | 36 | 50 | 0 | 9 | 20 | 393 | 17 | 40 | 108 | 107 | 0 | 35 | 30 | 95 | 35 | 0 | 0 | 0 |  | 885 | 0 | 175 | 0 | 0 | 221 | 0 | 0 | 0 | 20 | 0 | 146 | 22 | 32 | 0 | 0 | 0 | 32 | 0 | 37 | 0 | 42 | 0 | 8 | 33 | 17 | 0 | 11 | 80 | 0 | 250 | 0 | 0 | 177 | 0 | 0 | 177 | 0 | 90 | 148 | 0 | 335 | 17 | 169 | 50 | 71 | 54 | 0 | 4 | 75 | 622 | 0 | 0 | 35 | 5 | 105 | 17 | 0 | 0 | 0 |  | 7207 | 4162 | 11369 | 4100 | 885 | 1674 | 703 | 1989 | 952 | 148 | 398 | 398 | 92 | 207 | 489 | 95.94
14:00 | 0 | 0 | 0 | 180 | 300 | 86 | 0 | 399 | 326 |  | 0 | 450 | 0 | 8 | 0 | 30 | 0 | 0 | 92 | 8 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 22 | 25 | 16 | 33 | 16 | 41 | 0 | 83 | 65 | 105 | 0 | 16 | 0 | 0 | 0 | 0 |  | 12 | 26 | 17 | 33 | 11 | 6 | 13 | 3 | 0 | 0 | 0 | 325 | 310 | 202 | 26 | 31 | 34 | 49 | 0 | 43 | 0 | 31 | 0 | 22 | 10 | 33 | 20 | 126 | 70 | 0 | 22 | 2 | 43 | 30 | 5 | 5 | 0 | 0 | 60 | 10 | 0 | 221 | 0 | 0 | 10 | 310 | 0 | 0 | 196 | 85 | 103 | 70 | 77 | 70 | 35 | 19 | 21 | 180 | 124 | 404 | 68 | 88 | 17 | 3 | 123 | 36 | 55 | 0 | 9 | 20 | 386 | 17 | 49 | 108 | 107 | 0 | 35 | 31 | 94 | 45 | 0 | 0 | 0 |  | 885 | 0 | 165 | 0 | 0 | 219 | 0 | 0 | 0 | 16 | 0 | 146 | 24 | 32 | 0 | 0 | 0 | 32 | 5 | 37 | 0 | 42 | 0 | 8 | 32 | 16 | 0 | 8 | 80 | 0 | 250 | 0 | 0 | 171 | 0 | 0 | 135 | 0 | 90 | 147 | 0 | 315 | 17 | 168 | 50 | 71 | 54 | 0 | 3 | 75 | 622 | 0 | 0 | 72 | 4 | 91 | 17 | 0 | 0 | 0 |  | 7278 | 4099 | 11377 | 4061 | 885 | 1678 | 697 | 2062 | 952 | 148 | 354 | 347 | 126 | 202 | 666 | 95.94
15:00 | 0 | 0 | 0 | 180 | 300 | 85 | 0 | 394 | 317 |  | 0 | 450 | 0 | 8 | 0 | 30 | 0 | 0 | 94 | 8 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 22 | 25 | 16 | 33 | 20 | 41 | 0 | 84 | 70 | 105 | 0 | 16 | 0 | 0 | 0 | 0 |  | 12 | 26 | 17 | 33 | 11 | 6 | 13 | 2 | 0 | 0 | 0 | 325 | 305 | 203 | 26 | 30 | 34 | 48 | 0 | 43 | 0 | 37 | 0 | 22 | 10 | 33 | 20 | 166 | 71 | 0 | 22 | 2 | 43 | 30 | 5 | 5 | 0 | 0 | 57 | 10 | 0 | 221 | 0 | 0 | 10 | 310 | 0 | 0 | 200 | 85 | 101 | 70 | 77 | 70 | 35 | 15 | 21 | 200 | 122 | 403 | 68 | 88 | 17 | 3 | 123 | 36 | 46 | 0 | 16 | 20 | 391 | 17 | 16 | 108 | 107 | 0 | 35 | 25 | 96 | 45 | 0 | 0 | 0 |  | 885 | 0 | 150 | 0 | 0 | 217 | 0 | 0 | 0 | 14 | 0 | 143 | 29 | 32 | 0 | 0 | 0 | 32 | 5 | 37 | 0 | 42 | 0 | 8 | 32 | 16 | 0 | 8 | 81 | 0 | 250 | 0 | 0 | 167 | 0 | 0 | 149 | 0 | 90 | 144 | 0 | 290 | 17 | 168 | 50 | 71 | 54 | 0 | 6 | 75 | 622 | 0 | 0 | 72 | 4 | 77 | 17 | 0 | 0 | 0 |  | 7293 | 4054 | 11347 | 4034 | 885 | 1646 | 699 | 2080 | 953 | 154 | 366 | 365 | 166 | 148 | 786 | 95.94
16:00 | 0 | 0 | 0 | 180 | 300 | 84 | 0 | 397 | 317 |  | 0 | 450 | 0 | 8 | 0 | 30 | 0 | 0 | 93 | 8 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 22 | 25 | 23 | 33 | 22 | 41 | 0 | 82 | 70 | 105 | 0 | 16 | 0 | 0 | 0 | 0 |  | 12 | 26 | 17 | 33 | 12 | 6 | 14 | 5 | 0 | 0 | 0 | 325 | 305 | 204 | 26 | 31 | 34 | 48 | 0 | 43 | 0 | 37 | 0 | 22 | 7 | 25 | 20 | 164 | 82 | 0 | 22 | 1 | 44 | 30 | 5 | 5 | 0 | 0 | 59 | 10 | 0 | 221 | 0 | 0 | 10 | 300 | 0 | 0 | 200 | 80 | 60 | 70 | 77 | 70 | 35 | 6 | 21 | 180 | 123 | 404 | 68 | 88 | 17 | 2 | 123 | 36 | 53 | 0 | 28 | 20 | 392 | 17 | 32 | 162 | 107 | 0 | 35 | 19 | 91 | 55 | 0 | 0 | 0 |  | 885 | 0 | 150 | 0 | 0 | 220 | 0 | 0 | 0 | 13 | 0 | 147 | 27 | 48 | 0 | 0 | 0 | 32 | 34 | 37 | 0 | 42 | 0 | 8 | 32 | 17 | 0 | 8 | 83 | 0 | 250 | 0 | 0 | 163 | 0 | 0 | 194 | 0 | 93 | 144 | 0 | 290 | 17 | 168 | 56 | 71 | 56 | 0 | 5 | 75 | 570 | 0 | 0 | 90 | 2 | 53 | 17 | 0 | 0 | 0 |  | 7313 | 4097 | 11410 | 4053 | 885 | 1637 | 661 | 2177 | 903 | 152 | 414 | 438 | 164 | 120 | 682 | 95.93
17:00 | 0 | 0 | 0 | 180 | 300 | 81 | 0 | 400 | 343 |  | 0 | 450 | 0 | 11 | 0 | 30 | 0 | 0 | 95 | 8 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 55 | 55 | 22 | 25 | 22 | 33 | 22 | 41 | 0 | 80 | 70 | 105 | 0 | 19 | 0 | 0 | 0 | 0 |  | 10 | 30 | 17 | 33 | 13 | 6 | 14 | 5 | 0 | 0 | 0 | 330 | 320 | 204 | 26 | 84 | 37 | 49 | 0 | 43 | 0 | 37 | 0 | 22 | 0 | 33 | 20 | 164 | 82 | 0 | 22 | 1 | 43 | 30 | 5 | 5 | 0 | 0 | 58 | 10 | 0 | 221 | 0 | 0 | 9 | 295 | 0 | 0 | 200 | 80 | 60 | 70 | 77 | 70 | 65 | 5 | 21 | 180 | 123 | 405 | 68 | 88 | 17 | 1 | 123 | 36 | 55 | 0 | 50 | 20 | 391 | 17 | 8 | 162 | 107 | 0 | 35 | 7 | 95 | 55 | 0 | 0 | 0 |  | 884 | 0 | 150 | 0 | 0 | 218 | 0 | 0 | 0 | 14 | 0 | 147 | 25 | 48 | 0 | 0 | 0 | 32 | 37 | 37 | 0 | 42 | 0 | 8 | 32 | 19 | 0 | 8 | 84 | 0 | 250 | 0 | 0 | 161 | 0 | 0 | 140 | 0 | 93 | 145 | 0 | 288 | 17 | 120 | 88 | 80 | 77 | 0 | 3 | 95 | 570 | 0 | 0 | 127 | 1 | 30 | 47 | 0 | 0 | 0 |  | 7457 | 4117 | 11574 | 4131 | 884 | 1653 | 613 | 2409 | 904 | 150 | 358 | 392 | 164 | 56 | 300 | 95.93
18:00 | 0 | 0 | 0 | 180 | 300 | 78 | 0 | 401 | 350 |  | 0 | 450 | 0 | 48 | 0 | 30 | 0 | 0 | 95 | 11 | 8 | 126 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 26 | 33 | 22 | 41 | 0 | 77 | 70 | 105 | 0 | 25 | 0 | 0 | 0 | 0 |  | 8 | 26 | 17 | 33 | 30 | 6 | 14 | 3 | 0 | 0 | 0 | 340 | 310 | 207 | 26 | 83 | 37 | 48 | 0 | 43 | 0 | 37 | 0 | 22 | 10 | 33 | 20 | 154 | 82 | 0 | 22 | 0 | 43 | 30 | 5 | 5 | 0 | 0 | 58 | 10 | 0 | 221 | 0 | 0 | 9 | 290 | 0 | 0 | 100 | 224 | 30 | 50 | 170 | 50 | 148 | 0 | 21 | 200 | 130 | 402 | 78 | 105 | 44 | 0 | 123 | 36 | 55 | 0 | 58 | 20 | 400 | 22 | 3 | 162 | 107 | 0 | 35 | 2 | 72 | 55 | 0 | 0 | 0 |  | 885 | 0 | 155 | 0 | 0 | 221 | 0 | 0 | 17 | 12 | 0 | 142 | 18 | 48 | 0 | 0 | 0 | 32 | 37 | 37 | 0 | 42 | 0 | 8 | 32 | 19 | 0 | 8 | 85 | 0 | 250 | 0 | 0 | 161 | 0 | 0 | 130 | 0 | 60 | 145 | 0 | 294 | 53 | 120 | 94 | 105 | 84 | 0 | 2 | 95 | 540 | 0 | 0 | 127 | 0 | 7 | 54 | 0 | 0 | 0 |  | 7849 | 4119 | 11968 | 4132 | 885 | 1648 | 410 | 2979 | 875 | 147 | 351 | 503 | 154 | 14 | 0 | 95.93
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 300 | 80 | 0 | 398 | 350 |  | 0 | 450 | 0 | 49 | 0 | 30 | 0 | 0 | 94 | 32 | 32 | 125 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 21 | 33 | 22 | 41 | 0 | 77 | 70 | 105 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 51 | 33 | 77 | 16 | 14 | 20 | 0 | 0 | 0 | 325 | 305 | 208 | 26 | 142 | 37 | 50 | 0 | 51 | 0 | 37 | 0 | 22 | 10 | 33 | 20 | 174 | 105 | 0 | 22 | 0 | 43 | 30 | 5 | 5 | 0 | 0 | 63 | 81 | 0 | 221 | 0 | 0 | 10 | 285 | 0 | 0 | 185 | 291 | 240 | 81 | 170 | 92 | 149 | 0 | 21 | 200 | 130 | 398 | 77 | 105 | 105 | 0 | 207 | 36 | 55 | 0 | 58 | 20 | 387 | 34 | 0 | 162 | 107 | 0 | 35 | 0 | 94 | 55 | 0 | 0 | 0 |  | 885 | 0 | 155 | 0 | 16 | 223 | 0 | 0 | 40 | 27 | 0 | 131 | 24 | 48 | 0 | 0 | 0 | 30 | 40 | 68 | 0 | 50 | 18 | 8 | 32 | 21 | 0 | 8 | 80 | 0 | 250 | 0 | 0 | 161 | 0 | 0 | 136 | 0 | 65 | 146 | 0 | 287 | 53 | 111 | 94 | 105 | 90 | 0 | 0 | 95 | 550 | 0 | 0 | 127 | 0 | 0 | 52 | 0 | 0 | 0 |  | 8756 | 4226 | 12982 | 4164 | 885 | 1745 | 774 | 3360 | 880 | 147 | 359 | 630 | 174 | 0 | 569.5334 | 95.93
19:30 | 0 | 0 | 0 | 180 | 300 | 80 | 0 | 398 | 322 |  | 0 | 450 | 0 | 50 | 0 | 30 | 0 | 0 | 92 | 32 | 32 | 125 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 0 | 25 | 25 | 33 | 22 | 41 | 0 | 78 | 70 | 105 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 51 | 33 | 91 | 39 | 14 | 24 | 0 | 0 | 0 | 325 | 310 | 207 | 26 | 142 | 37 | 50 | 0 | 51 | 0 | 37 | 0 | 22 | 10 | 33 | 17 | 174 | 101 | 0 | 22 | 0 | 43 | 30 | 5 | 5 | 0 | 0 | 63 | 81 | 0 | 221 | 0 | 0 | 10 | 270 | 0 | 0 | 150 | 296 | 202 | 80 | 170 | 70 | 149 | 0 | 21 | 200 | 132 | 403 | 79 | 105 | 105 | 0 | 210 | 36 | 55 | 0 | 58 | 20 | 400 | 34 | 0 | 162 | 107 | 0 | 35 | 0 | 96 | 55 | 0 | 0 | 0 |  | 886 | 0 | 160 | 0 | 16 | 223 | 0 | 0 | 50 | 35 | 0 | 148 | 24 | 48 | 0 | 0 | 0 | 30 | 40 | 78 | 0 | 50 | 32 | 8 | 32 | 21 | 0 | 8 | 79 | 0 | 250 | 0 | 0 | 161 | 0 | 0 | 172 | 0 | 93 | 148 | 0 | 312 | 53 | 154 | 94 | 105 | 90 | 0 | 0 | 95 | 600 | 0 | 0 | 127 | 0 | 0 | 52 | 0 | 0 | 0 |  | 8671 | 4474 | 13145 | 4205 | 886 | 1731 | 749 | 3392 | 929 | 148 | 395 | 708 | 174 | 0 | 557.5529 | 0
20:00 | 0 | 0 | 0 | 180 | 300 | 80 | 0 | 398 | 322 |  | 0 | 450 | 0 | 49 | 0 | 30 | 0 | 0 | 95 | 32 | 32 | 125 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 25 | 33 | 22 | 41 | 0 | 80 | 70 | 105 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 51 | 33 | 91 | 40 | 14 | 25 | 0 | 0 | 0 | 330 | 310 | 206 | 26 | 142 | 37 | 53 | 0 | 51 | 0 | 37 | 0 | 22 | 10 | 33 | 17 | 158 | 103 | 0 | 22 | 0 | 43 | 30 | 5 | 5 | 0 | 0 | 62 | 81 | 0 | 221 | 0 | 0 | 10 | 280 | 0 | 0 | 150 | 296 | 250 | 80 | 180 | 93 | 149 | 0 | 21 | 200 | 132 | 402 | 79 | 105 | 105 | 0 | 211 | 36 | 55 | 0 | 58 | 20 | 400 | 34 | 0 | 162 | 107 | 0 | 35 | 0 | 96 | 55 | 0 | 0 | 0 |  | 884 | 0 | 160 | 0 | 16 | 222 | 0 | 0 | 37 | 42 | 0 | 149 | 30 | 55 | 0 | 0 | 0 | 30 | 40 | 78 | 0 | 50 | 32 | 8 | 32 | 22 | 0 | 8 | 80 | 0 | 250 | 0 | 0 | 161 | 0 | 0 | 192 | 0 | 93 | 149 | 0 | 317 | 53 | 162 | 94 | 105 | 91 | 0 | 0 | 95 | 600 | 0 | 0 | 150 | 0 | 0 | 52 | 0 | 0 | 0 |  | 8802 | 4539 | 13341 | 4236 | 884 | 1757 | 828 | 3454 | 930 | 150 | 414 | 722 | 158 | 0 | 561.2392 | 95.93
21:00 | 0 | 0 | 0 | 180 | 300 | 81 | 0 | 398 | 321 |  | 0 | 450 | 0 | 47 | 0 | 30 | 0 | 0 | 95 | 32 | 32 | 125 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 25 | 33 | 24 | 41 | 0 | 80 | 70 | 105 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 51 | 33 | 91 | 42 | 14 | 29 | 0 | 0 | 0 | 330 | 310 | 206 | 26 | 142 | 40 | 55 | 0 | 51 | 0 | 37 | 0 | 22 | 10 | 33 | 17 | 168 | 101 | 0 | 22 | 0 | 43 | 30 | 5 | 5 | 0 | 0 | 63 | 81 | 0 | 221 | 0 | 0 | 10 | 280 | 0 | 0 | 200 | 296 | 301 | 81 | 180 | 86 | 149 | 0 | 21 | 200 | 133 | 402 | 79 | 105 | 51 | 0 | 213 | 36 | 55 | 0 | 58 | 20 | 400 | 34 | 0 | 162 | 107 | 0 | 35 | 0 | 95 | 55 | 0 | 0 | 0 |  | 884 | 0 | 160 | 0 | 16 | 223 | 0 | 0 | 37 | 65 | 0 | 149 | 30 | 110 | 0 | 0 | 0 | 30 | 40 | 78 | 0 | 50 | 32 | 8 | 32 | 22 | 0 | 8 | 80 | 0 | 250 | 0 | 0 | 160 | 0 | 0 | 215 | 0 | 93 | 150 | 0 | 321 | 53 | 168 | 94 | 105 | 91 | 0 | 0 | 95 | 610 | 0 | 0 | 150 | 0 | 0 | 52 | 0 | 0 | 0 |  | 8865 | 4661 | 13526 | 4240 | 884 | 1767 | 929 | 3457 | 940 | 150 | 438 | 768 | 168 | 0 | 528.984 | 95.93
22:00 | 0 | 0 | 0 | 180 | 300 | 81 | 0 | 398 | 326 |  | 0 | 450 | 0 | 41 | 0 | 30 | 0 | 0 | 96 | 32 | 32 | 126 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 25 | 33 | 24 | 41 | 0 | 81 | 70 | 105 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 51 | 33 | 92 | 12 | 14 | 37 | 0 | 0 | 0 | 335 | 320 | 205 | 26 | 140 | 30 | 55 | 0 | 51 | 0 | 37 | 0 | 22 | 10 | 0 | 20 | 162 | 101 | 0 | 22 | 0 | 43 | 30 | 5 | 5 | 0 | 0 | 62 | 81 | 0 | 221 | 0 | 0 | 10 | 300 | 0 | 0 | 200 | 296 | 301 | 81 | 179 | 86 | 149 | 0 | 21 | 200 | 138 | 403 | 79 | 105 | 51 | 0 | 213 | 36 | 55 | 0 | 58 | 20 | 395 | 34 | 0 | 162 | 107 | 0 | 35 | 0 | 96 | 55 | 0 | 0 | 0 |  | 886 | 0 | 160 | 0 | 16 | 223 | 0 | 0 | 37 | 60 | 0 | 147 | 29 | 80 | 0 | 0 | 0 | 30 | 37 | 78 | 0 | 42 | 32 | 8 | 32 | 22 | 0 | 8 | 80 | 0 | 250 | 0 | 0 | 160 | 0 | 0 | 214 | 0 | 93 | 150 | 0 | 322 | 53 | 168 | 94 | 105 | 91 | 0 | 0 | 95 | 622 | 0 | 0 | 150 | 0 | 0 | 34 | 0 | 0 | 0 |  | 8832 | 4608 | 13440 | 4206 | 886 | 1800 | 929 | 3371 | 952 | 151 | 437 | 760 | 162 | 0 | 608.2395 | 95.92
23:00 | 0 | 0 | 0 | 180 | 300 | 80 | 0 | 398 | 329 |  | 0 | 450 | 0 | 49 | 0 | 30 | 0 | 0 | 95 | 32 | 32 | 126 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 25 | 33 | 24 | 41 | 0 | 84 | 70 | 105 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 25 | 51 | 33 | 58 | 6 | 14 | 38 | 0 | 0 | 0 | 275 | 265 | 209 | 26 | 142 | 30 | 55 | 0 | 51 | 0 | 37 | 0 | 22 | 10 | 33 | 20 | 162 | 102 | 0 | 22 | 0 | 43 | 30 | 5 | 5 | 0 | 0 | 64 | 78 | 0 | 221 | 0 | 0 | 10 | 290 | 0 | 0 | 150 | 293 | 155 | 50 | 179 | 86 | 149 | 0 | 21 | 200 | 133 | 402 | 79 | 105 | 51 | 0 | 52 | 36 | 55 | 0 | 58 | 20 | 400 | 34 | 0 | 162 | 107 | 0 | 35 | 0 | 96 | 55 | 0 | 0 | 0 |  | 897 | 0 | 160 | 0 | 16 | 226 | 0 | 0 | 37 | 58 | 0 | 152 | 33 | 80 | 0 | 0 | 0 | 30 | 37 | 78 | 0 | 42 | 24 | 8 | 32 | 22 | 0 | 8 | 80 | 0 | 250 | 0 | 0 | 160 | 0 | 0 | 215 | 0 | 50 | 150 | 0 | 320 | 53 | 168 | 94 | 105 | 91 | 0 | 0 | 95 | 622 | 0 | 0 | 150 | 0 | 0 | 34 | 0 | 0 | 0 |  | 8326 | 4577 | 12903 | 4141 | 897 | 1792 | 659 | 3170 | 952 | 154 | 441 | 750 | 162 | 0 | 1010.9678 | 95.92
24:00 | 0 | 0 | 0 | 180 | 300 | 80 | 0 | 397 | 312 |  | 0 | 450 | 0 | 10 | 0 | 30 | 0 | 0 | 96 | 9 | 8 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 25 | 33 | 24 | 41 | 0 | 0 | 70 | 105 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 51 | 33 | 11 | 6 | 14 | 38 | 0 | 0 | 0 | 305 | 295 | 208 | 26 | 141 | 30 | 56 | 0 | 51 | 0 | 39 | 0 | 22 | 10 | 33 | 20 | 164 | 102 | 0 | 20 | 0 | 43 | 30 | 5 | 5 | 0 | 0 | 62 | 78 | 0 | 220 | 0 | 0 | 10 | 310 | 0 | 0 | 200 | 140 | 207 | 50 | 47 | 86 | 53 | 0 | 21 | 180 | 132 | 404 | 49 | 105 | 27 | 0 | 52 | 36 | 55 | 0 | 16 | 20 | 396 | 19 | 0 | 72 | 107 | 0 | 35 | 0 | 80 | 55 | 0 | 0 | 0 |  | 897 | 0 | 160 | 0 | 0 | 226 | 0 | 0 | 26 | 53 | 0 | 152 | 33 | 80 | 0 | 0 | 0 | 30 | 37 | 78 | 0 | 42 | 24 | 8 | 32 | 22 | 0 | 11 | 80 | 0 | 251 | 0 | 0 | 160 | 0 | 0 | 213 | 0 | 82 | 151 | 0 | 320 | 0 | 168 | 50 | 105 | 56 | 0 | 0 | 55 | 610 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 |  | 7542 | 4362 | 11904 | 4196 | 897 | 1796 | 793 | 2196 | 941 | 70 | 439 | 625 | 164 | 0 | 1655.1487 | 0
KWH | 0 | 0 | 0 | 4284000 | 7139018 | 2064772 | 0 | 9775110 | 7904000 |  | 0 | 8905250 | 0 | 439680 | 0 | 740685 | 0 | 0 | 3309000 | 321600 | 302688 | 1052160 | 0 | 0 | 0 | 0 | 662400 | 1325689 | 773708 | 402120 | 600000 | 464040 | 788760 | 623400 | 980640 | 0 | 1929731 | 1612000 | 2500000 | 0 | 532513 | 0 | 0 | 0 | 0 |  | 287280 | 602360 | 706931 | 790320 | 666240 | 237600 | 324192 | 579360 | 0 | 0 | 0 | 8247900 | 7649000 | 5007000 | 418181 | 1300970 | 852624 | 1266240 | 0 | 1128102 | 0 | 932664 | 0 | 475344 | 193320 | 670900 | 459620 | 2880000 | 2787840 | 0 | 502848 | 13950 | 1022000 | 686936 | 129600 | 143640 | 0 | 0 | 1424736 | 777600 | 0 | 5215200 | 0 | 61340 | 224100 | 7228000 | 74160 | 0 | 3173952 | 3362181 | 2919141 | 1508028 | 2181600 | 1572319 | 1621584 | 108540 | 519360 | 4163520 | 2898836 | 9544000 | 1537200 | 2316000 | 725963 | 28080 | 2606945 | 884462 | 1313922 | 0 | 611520 | 493440 | 9451500 | 404160 | 323550 | 2328480 | 2570564 | 0 | 887040 | 238890 | 2125440 | 1251000 | 0 | 0 | 0 |  | 21717090 | 0 | 5153472 | 0 | 270720 | 5351040 | 0 | 0 | 292800 | 791680 | 0 | 3570435 | 596135 | 1102368 | 0 | 0 | 0 | 617312 | 469985 | 1179216 | 0 | 895568 | 135126 | 194770 | 762000 | 468240 | 0 | 226386 | 1846691 | 0 | 6095000 | 0 | 0 | 4400582 | 0 | 0 | 4805473 | 0 | 1372800 | 4251164 | 0 | 8636290 | 477600 | 2621519 | 1666272 | 2237040 | 1569456 | 0 | 38680 | 1706112 | 15672400 | 0 | 0 | 1653600 | 33420 | 786240 | 823104 | 0 | 0 | 0 |  | 179072279 | 104487786 | 283560065 | 103377577 | 21717090 | 40530850 | 13167759 | 55460870 | 23614091 | 3541731 | 10156513 | 7542234 | 2880000 | 1571350 | 0
Fuel Cost | 0 | 0 | 0 | 6383160 | 7995700.16 | 2746146.76 | 0 | 10263865.5 | 8536320 |  | 0 | 9706722.5 | 0 | 4915622.4 | 0 | 9814076.25 | 0 | 0 | 5790750 | 4701792 | 4258820.16 | 17055513.6 | 0 | 0 | 0 | 0 | 8425728 | 17896801.5 | 10375424.28 | 301590 | 450000 | 0 | 0 | 0 | 16680686.4 | 0 | 521027.37 | 435240 | 4725000 | 0 | 8706587.55 | 0 | 0 | 0 | 0 |  | 3749004 | 10047364.8 | 12031965.62 | 10677223.2 | 8447923.2 | 2749032 | 411723.84 | 1929268.8 | 0 | 0 | 0 | 9155169 | 8337410 | 5808120 | 539453.49 | 1587183.4 | 963465.12 | 1886697.6 | 0 | 1883930.34 | 0 | 16107107.28 | 0 | 651221.28 | 144990 | 1174075 | 344715 | 20678400 | 3038745.6 | 0 | 683873.28 | 222363 | 1400140 | 906755.52 | 225504 | 248497.2 | 0 | 0 | 2763987.84 | 1772928 | 0 | 5267352 | 0 | 91396.6 | 443718 | 7228000 | 55620 | 0 | 66526033.92 | 45893770.65 | 61185195.36 | 31170938.76 | 29407968 | 32499833.73 | 22458938.4 | 1268832.6 | 5359795.2 | 56873683.2 | 38467553.72 | 8780480 | 18692352 | 33489360 | 9183431.95 | 0 | 30605534.3 | 9631791.18 | 13966990.86 | 0 | 7882492.8 | 5812723.2 | 8695380 | 5233872 | 4675297.5 | 29548411.2 | 29253018.32 | 0 | 11584742.4 | 2854735.5 | 31817836.8 | 16475670 | 0 | 0 | 0 |  | 65151270 | 0 | 5771888.64 | 0 | 2818195.2 | 88292160 | 0 | 0 | 5273328 | 14250240 | 0 | 3998887.2 | 1156501.9 | 12015811.2 | 0 | 0 | 0 | 10352322.24 | 8220037.65 | 18442938.24 | 0 | 14830606.08 | 2284980.66 | 2654715.1 | 12854940 | 969256.8 | 0 | 171374.202 | 10729274.71 | 0 | 32242550 | 0 | 0 | 5104675.12 | 0 | 0 | 83903558.58 | 0 | 28801344 | 4931350.24 | 0 | 8549927.1 | 6418944 | 54973253.43 | 19711997.76 | 32325228 | 19932091.2 | 0 | 427414 | 20712199.68 | 141208324 | 0 | 0 | 12236640 | 377980.2 | 9222595.2 | 12618184.32 | 0 | 0 | 0 |  | 973637561.99 | 773936984.652 | 1747574546.642 | 116058647.942 | 65151270 | 47914269.09 | 275156599.2 | 719313269.66 | 184180148.71 | 956267.37 | 172195718.58 | 126920738.09 | 20678400 | 19049218 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 300 | 89 | 0 | 408 | 330 |  | 0 | 450 | 0 | 8 | 0 | 30 | 0 | 0 | 193 | 8 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 16 | 25 | 19 | 33 | 25 | 41 | 0 | 82 | 65 | 105 | 0 | 16 | 0 | 0 | 0 | 0 |  | 12 | 26 | 17 | 33 | 12 | 6 | 10 | 5 | 0 | 0 | 0 | 335 | 325 | 205 | 8 | 50 | 40 | 52 | 0 | 43 | 0 | 40 | 0 | 19 | 10 | 33 | 20 | 134 | 131 | 0 | 22 | 2 | 43 | 30 | 5 | 5 | 0 | 0 | 60 | 10 | 0 | 193 | 0 | 0 | 9 | 300 | 0 | 0 | 150 | 95 | 103 | 92 | 77 | 94 | 35 | 17 | 21 | 200 | 124 | 405 | 68 | 88 | 17 | 3 | 123 | 36 | 55 | 0 | 9 | 20 | 400 | 17 | 54 | 35 | 107 | 0 | 35 | 31 | 96 | 47 | 0 | 0 | 0 |  | 884 | 0 | 220 | 0 | 16 | 222 | 0 | 0 | 0 | 31 | 0 | 150 | 18 | 16 | 0 | 0 | 0 | 24 | 0 | 39 | 0 | 42 | 0 | 8 | 33 | 21 | 0 | 11 | 80 | 0 | 250 | 0 | 0 | 175 | 0 | 0 | 209 | 0 | 10 | 165 | 0 | 414 | 17 | 52 | 50 | 89 | 55 | 0 | 5 | 55 | 622 | 0 | 0 | 15 | 5 | 91 | 17 | 0 | 0 | 0 |  | 11564 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 300 | 81 | 0 | 398 | 321 | 0 | 0 | 450 | 0 | 47 | 0 | 30 | 0 | 0 | 95 | 32 | 32 | 125 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 25 | 33 | 24 | 41 | 0 | 80 | 70 | 105 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 12 | 26 | 51 | 33 | 91 | 42 | 14 | 29 | 0 | 0 | 0 | 330 | 310 | 206 | 26 | 142 | 40 | 55 | 0 | 51 | 0 | 37 | 0 | 22 | 10 | 33 | 17 | 168 | 101 | 0 | 22 | 0 | 43 | 30 | 5 | 5 | 0 | 0 | 63 | 81 | 0 | 221 | 0 | 0 | 10 | 280 | 0 | 0 | 200 | 296 | 301 | 81 | 180 | 86 | 149 | 0 | 21 | 200 | 133 | 402 | 79 | 105 | 51 | 0 | 213 | 36 | 55 | 0 | 58 | 20 | 400 | 34 | 0 | 162 | 107 | 0 | 35 | 0 | 95 | 55 | 0 | 0 | 0 |  | 884 | 0 | 160 | 0 | 16 | 223 | 0 | 0 | 37 | 65 | 0 | 149 | 30 | 110 | 0 | 0 | 0 | 30 | 40 | 78 | 0 | 50 | 32 | 8 | 32 | 22 | 0 | 8 | 80 | 0 | 250 | 0 | 0 | 160 | 0 | 0 | 215 | 0 | 93 | 150 | 0 | 321 | 53 | 168 | 94 | 105 | 91 | 0 | 0 | 95 | 610 | 0 | 0 | 150 | 0 | 0 | 52 | 0 | 0 | 0 |  | 13526 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 300 | 92 | 0 | 412 | 330 | 0 | 0 | 450 | 0 | 50 | 0 | 30 | 0 | 0 | 100 | 32 | 32 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 25 | 33 | 24 | 41 | 0 | 80 | 65 | 105 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 12 | 26 | 51 | 33 | 95 | 42 | 15 | 30 | 0 | 0 | 0 | 330 | 320 | 210 | 8 | 142 | 35 | 55 | 0 | 51 | 0 | 40 | 0 | 22 | 10 | 33 | 21 | 166 | 100 | 0 | 22 | 0 | 43 | 30 | 5 | 5 | 0 | 0 | 64 | 80 | 0 | 220 | 0 | 0 | 10 | 300 | 0 | 0 | 200 | 285 | 300 | 96 | 180 | 100 | 149 | 0 | 21 | 200 | 133 | 400 | 79 | 105 | 105 | 0 | 210 | 36 | 0 | 0 | 57 | 100 | 400 | 34 | 0 | 162 | 107 | 0 | 35 |  | 100 | 55 |  |  |  |  | 924 | 0 | 180 | 0 | 66 | 225 | 0 | 0 | 36 | 65 | 0 | 151 | 30 | 110 | 0 | 0 | 0 | 32 | 40 | 80 | 0 | 50 | 40 | 8 | 33 | 22 | 0 | 11 | 80 | 0 | 250 | 0 | 0 | 150 | 0 | 0 | 220 | 0 | 90 | 150 | 0 | 380 | 52 | 175 | 94 | 105 | 90 | 0 | 0 | 95 | 620 | 0 |  | 150 |  |  | 52
Forecast for Day | 0 | 0 | 0 | 180 | 300 | 92 | 0 | 412 | 330 | 0 | 0 | 450 | 0 | 8 | 0 | 30 | 0 | 0 | 100 | 8 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 22 | 25 | 25 | 33 | 25 | 41 | 0 | 80 | 65 | 105 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 12 | 26 | 17 | 33 | 12 | 6 | 15 | 7 | 0 | 0 | 0 | 330 | 310 | 205 | 8 | 140 | 35 | 55 | 0 | 51 | 0 | 40 | 0 | 22 | 10 | 33 | 20 | 143 | 130 | 0 | 22 | 1.6 | 43 | 30 | 5 | 5 | 0 | 0 | 62 | 10 | 0 | 220 | 0 | 0 | 10 | 300 | 0 | 0 | 200 | 95 | 100 | 60 | 80 | 86 | 35 | 20 | 21 | 200 | 125 | 400 | 68 | 88 | 17 | 5 | 123 | 36 | 0 | 0 | 9 | 20 | 400 | 17 | 50 | 35 | 107 | 0 | 35 | 30 | 96 | 55 |  |  |  |  | 924 | 0 | 200 | 0 | 16 | 225 | 0 | 0 | 0 | 35 | 0 | 151 | 19 | 32 | 0 | 0 | 0 | 32 | 0 | 50 | 0 | 42 | 16 | 8 | 33 | 21 | 0 | 11 | 80 | 0 | 250 | 0 | 0 | 170 | 0 | 0 | 220 | 0 | 90 | 160 | 0 | 400 | 17 | 100 | 50 | 90 | 55 | 0 | 8 | 55 | 620 | 0 |  | 150 | 6 | 100 | 0
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 300 | 77 | 0 | 401 | 332 | 0 | 0 | 450 | 0 | 8 | 0 | 30 | 0 | 0 | 92 | 7 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 35 | 19 | 25 | 25 | 33 | 24 | 41 | 0 | 80 | 70 | 105 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 12 | 26 | 51 | 33 | 12 | 6 | 14 | 14 | 0 | 0 | 0 | 330 | 295 | 208 | 8 | 143 | 31 | 56 | 0 | 51 | 0 | 31 | 0 | 22 | 10 | 33 | 20 | 152 | 62 | 0 | 22 | 0 | 43 | 30 | 8 | 5 | 0 | 0 | 59 | 10 | 0 | 220 | 0 | 0 | 10 | 290 | 0 | 0 | 196 | 80 | 12 | 50 | 75 | 70 | 33 | 3 | 21 | 155 | 115 | 400 | 68 | 105 | 17 | 2 | 120 | 36 | 0 | 0 | 9 | 20 | 400 | 17 | 7 | 35 | 107 | 0 | 35 | 11 | 73 | 55 | 0 | 0 | 0 | 0 | 905 | 0 | 170 | 0 | 0 | 226 | 0 | 0 | 16 | 40 | 0 | 149 | 20 | 48 | 0 | 0 | 0 | 30 | 0 | 44 | 0 | 0 | 0 | 8 | 26 | 20 | 0 | 8 | 79 | 0 | 250 | 0 | 0 | 167 | 0 | 0 | 215 | 0 | 93 | 152 | 0 | 328 | 17 | 166 | 50 | 105 | 55 | 0 | 2 | 55 | 550 | 0 | 0 | 150 | 0 | 38 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 86327376 |  | 0
86327376
| Minimum Generation |  | 10559 | 7:00
| Highest Generation |  | 13526 | 21:00
| Day Peak Generation |  | 11564 | 10:00
| Evening Peak Generation |  | 13526 | 21:00
| HVDC Max Flow |  | 897 | 23:00
| HVDC EvPeak Flow |  | 884 | 21:00
| Load factor L.F |  | 87.35% | [161 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2022-08-17
Till now the maximum generation is : - |  |  | 14782 | 21:00 | Hrs on | 2022-04-16
The Summary of Yesterday's |  | 2022-08-16 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 11564 | MW Hour : | 10:00 | Min. Gen. at | 6:00 | 11212 | MW
Evening Peak Generation : |  | 13526 | MW Hour : | 21:00 | Available Max Generation : |  | 13880 | MW
E.P. Demand (at gen end) : |  | 14100 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 14300 | MW
Maximum Generation : |  | 13526 | MW Hour : | 21:00 | Reserve(Generation end) |  | - | MW
Total Gen. (MKWH) : |  | 283.5601 | System Load Factor : | 87.35% | Load Shed : |  | 433 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | 272 | MW at | 19:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2022-08-17
Actual : | 95.9 | Ft.(MSL) , | Rule curve : | 94.12 | Ft.( MSL )
Gas Consumed : | Total = | 1055.89 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 163972917.032
: |  | Coal : | 184180148.71 | Oil : | 1293586325.53 | Total : | 1641739391.272
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4579.5366 |  |  | 0 | 1.188%
Chittagong Area | 0 | 0:00 | 1296.7666 |  |  | 42 | 3.418%
Khulna Area | 170 | 4080:00 | 1711.8901 |  |  | 89 | 3.823%
Rajshahi Area | 79 | 1896:00 | 1519.4836 |  |  | 86 | 4.395%
Cumilla Area | 50 | 1200:00 | 1292.8131 |  |  | 73 | 4.063%
Mymensingh Area | 180 | 4320:00 | 1068.7782 |  |  | 105 | 4.608%
Sylhet Area | 0 | 0:00 | 477.0625 |  |  | 0 | 3.437%
Barisal Area | 0 | 0:00 | 388.7664 |  |  | 0 | -0.1191%
Rangpur Area | 50 | 1200:00 | 843.4254 |  |  | 38 | 4.551%
Total | 529 |  | 13178.5225 |  |  | 433
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-2 |  | 10) Payra unit-2
2) Ghorasal-3,4
3) Ashuganj-5
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
7) Sikalbaha 225 MW
8) Shajibazar 330 MW
9) Siddhirganj 335 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Sikalbaha-Juldah 132 kV Ckt was under shut down from 08:28 to 16:25 for D/W.
b) Sirajganj-Sherpur(Bogura) 132 kV Ckt-1 tripped at 08:38 from both ends showing Dist. Z1, C-φ at Sirajganj end
& Dist. Z1, B-φ at Sherpur end and was switched on at 09:36.
c) Mymensingh-Kishoreganj 132 kV Ckt-2 was under shut down from 09:52 to 17:23 for C/M.
d) Mohasthangar-Bogura 132 kV Ckt-2 was under shut down from 10:24 to 13:50 for C/M.
e) Tongi-Tongi Millgate 132 kV Ckt was under shut down from 12:30 to 17:11 for C/M.
f) Barishal(N) 132/33 kV T-4 & T-5 transformers were under shut down from 10:43 to 12:43 for C/M.
g) Tongi 132 kV Bus-2 was under shutdown from 12:38 to 17:05 for C/M.
h) Khulna(S)-Rampal 230 kV Ckt-2 was under shut down from 12:14 to 17:44 for C/M.
i) Rajshahi(New)-Rajshahi(Old) 132 kV Ckt tripped at 13:20 from both ends showing Dist. Z1, ARC at Rajshahi(New) end
& Dist. Z1, A-φ at Rajshahi(Old) end and was switched on at 14:35.
j) Cumilla(S) 132/33 kV T-1 & T-2 transformers were shutdown at 12:35 due to fire 33 kV feeder and T-1 was | [5 empty] | About 80 MW power interruption occurred under
switched on at 12:51 & T-2 at 14:52. | [5 empty] | Comilla(S) S/S area from 12:35 to 12:51.
k) Chandpur 150 MW CCPP ST was synchronized at 16:38.
l) 33 kV side of Kulaura 132/33 kV T-1 & T-1 transformers tripped at 01:20(17/08/2022) due to Jumper broke down | [5 empty] | About 36 MW power interruption occurred under
at auxiliary transformer and were switched on at 02:02(17/08/2022)(T-2) & 02:37(17/08/2022)(T-1). | [5 empty] | Kulaura S/S area from 01:20(17/08/2022) to 02:02.
m) Kabirpur-Kodda 132 kV Ckt-2 was shut down at 06:19(17/08/2022) for C/M.
n) Bogura(Old) 132/33 kV T-4 transformer was shutdown at 07:09(17/08/2022) for C/M.
| Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2022-08-16 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4284000
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 300 | 7139018 | Machine problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 81 | 2064772 | Engine problem
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 398 | 9775110 | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 321 | 7904000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 8905250
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 47 | 439680 | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 0 | 0 | Under maint.
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 30 | 740685 | Engine problem
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 402120
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 95 | 3309000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 32 | 321600 | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 32 | 302688 | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 662400
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 125 | 1052160 | Engine problem
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 1325689
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 773708
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 50 | 1064040 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 788760
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 24 | 623400 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 41 | 980640 | #REF!
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 296 | 3362181
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 301 | 2919141
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 81 | 1508028 | Engine problem
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 86 | 1572319 | Engine problem
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 1621584
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 2316000
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 34 | 404160 | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 2328480
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 238890
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 55 | 1251000
| Dhaka area Total |  |  |  | 5847 | 3694 | 70380503
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 105 | 2500000 | Machine problem
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 25 | 532513
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 108540
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 42 | 237600 | Engine problem
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 150 | 3541731 | Low water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | HGPI for 30 days.
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 51 | 725963 | Engine problem
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 26 | 602360 | Fuel shortage
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 706931 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 33 | 790320 | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 21 | 519360 | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 14 | 324192 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 29 | 579360
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 91 | 666240 | Engine problem
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 28080
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 213 | 2606945 | Engine problem
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 36 | 884462 | Engine problem
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 55 | 1313922
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 20 | 493440 | Engine problem
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 107 | 2570564 | Engine problem
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Chattogram area Total |  |  |  | 2382 | 1069 | 19732523
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 206 | 5007000 | #REF!
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 330 | 8247900 | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 310 | 7649000 | FGMO
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+136*1 | 284 | 0 | 0 | On test.
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 40 | 852624
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 55 | 1266240
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 26 | 418181 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1128102
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 133 | 2898836 | Engine problem
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 37 | 932664 | Engine problem
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 142 | 1300970 | Machine problem
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 200 | 4163520
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 475344
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 10 | 193320
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 168 | 2880000
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 670900
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 0 | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 17 | 459620 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 200 | 3173952
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Fuel shortage
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 58 | 611520 | Fuel shortage
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 35 | 887040 | 33 kV feeder problem.
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 95 | 2125440 | Engine problem
| Cumilla Area Total |  |  |  | 3169 | 2168 | 45342173
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 101 | 2787840 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 502848
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 13950
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 180 | 2181600 | Engine problem
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 79 | 1537200 | Engine problem
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 323550
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 287280 | Engine problem
| Mymensingh Area Total |  |  |  | 614 | 394 | 7634268
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1022000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 686936 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Gas shortage
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 5 | 129600 | Gas shortage
| Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 5 | 143640 | Gas shortage
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 0 | 0 | Engine problem
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 63 | 1424736
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 777600
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 221 | 5215200
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50MW PP (EPL) |  | NENP | 27*2 | 50 | 0 | 61340 | Gas shortage
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 0 | 74160 | Gas shortage
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 280 | 7228000 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 402 | 9544000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 224100
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 400 | 9451500
| Sylhet Area Total |  |  |  | 2477 | 1540 | 35982812
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 884 | 21717090
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 16 | 270720 | Fuel shortage
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 37 | 292800 | Engine problem
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 223 | 5351040
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 65 | 791680 | Engine problem
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 160 | 5153472 | Gas shortage.
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 0 | 0 | Fuel shortage
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 93 | 1372800 | Engine problem
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 53 | 477600 | Fuel shortage
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 105 | 2237040
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 786240
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 0 | 0 | 0 | On test.
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 2384 | 1636 | 38450482
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 110 | 1102368 | Line O/L
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 30 | 596135 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 149 | 3570435 | ST under S/D
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 610 | 15672400 | Unit-2 S/D
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 0 | 0 | Under maint.
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 150 | 1653600 | Line O/L
| Barisal Area Total |  |  |  | 1958 | 1049 | 22594938
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 30 | 617312 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 40 | 469985 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contract Expired
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 50 | 895568
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 135126 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 160 | 4400582 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 215 | 4805473
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 150 | 4251164 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 321 | 8636290 | Gas shortage
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 762000 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 468240
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | .
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 226386 | Engine problem
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 8 | 194770 | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 78 | 1179216 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 168 | 2621519 | Engine problem
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 94 | 1666272 | Engine problem
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 95 | 1706112 | Engine problem
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 33420
| Rajshahi Area Total |  |  |  | 2129 | 1503 | 33069435
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 80 | 1846691
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 250 | 6095000 | Machine problem
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 91 | 1569456 | Engine problem
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 38680
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 52 | 823104 | Fuel shortage
| Rangpur Area Total |  |  |  | 720 | 473 | 10372931
| Total |  |  |  | 21680 | 13526 | 283560065
| Eastern Grid Total |  |  |  | 14489 | 8865 | 179072279
| Western Grid Total |  |  |  | 7191 | 4661 | 104487786
| National Grid Total |  |  |  | 21680 | 13526 | 283560065
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2022-08-16
(a) ENTIRE EASTERN GRID : |  | 8887.2 | MW | (b) ENTIRE WESTERN GRID : |  | 3968.75 | MW
i) Dhaka area |  | 4846.8 | MW | i) Khulna area |  | 1443.4 | MW
ii) Chittagong area |  | 1307.4 | MW | ii) Rajshahi area |  | 1306.6 | MW
iii) Comilla area |  | 1267 | MW | iii) Barisal area |  | 397.75 | MW
iv) Mymensingh area |  | 907 | MW | iv) Rangpur area |  | 821 | MW
v) Sylhet area |  | 559 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 12855.95 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
AKS | 0 | 00:00 | Chowmuhani | 182 | 19:30 | Kaptai | 4 | 18:00 | Nawabganj | 36.9 | 19:00 | Siddhirganj | 108 | 22:00
AKSML | 146 | 05:00 | Chuadanga | 86 | 00:00 | Kazla | 95 | 18:30 | Netrakona | 96 | 19:00 | Sirajganj | 88 | 07:00
Aftabnagar | 34 | 16:00 | Coxsbazar | 119 | 19:00 | Keranigonj | 54 | 13:00 | New | 81 | 09:00 | Sonargaon | 80 | 12:00
Agargaon | 95 | 16:00 | Cumilla(N) | 162 | 21:00 | Khagrachori | 28 | 19:00 | Niamatpur | 64 | 06:00 | Sreemongol | 44 | 12:00
Agrabad | 76 | 18:00 | Cumilla(S) | 174 | 19:00 | Khulna | 85 | 21:00 | Noapara | 47 | 01:00 | Srinagar | 46.28 | 21:00
Amnura | 61 | 19:00 | Daudkandi | 155 | 21:00 | Khulshi | 183 | 20:00 | PHP | 11 | 10:00 | Sunamganj | 38 | 22:00
Ashuganj | 47 | 00:00 | Dhaka | 40 | 12:00 | Kishoreganj | 114 | 21:00 | Pabna | 89 | 00:00 | Sylhet | 136 | 00:00
BSRM | 157 | 23:00 | Dhamrai | 116 | 20:00 | Kodda | 299 | 21:00 | Palashbari | 108 | 23:00 | TK | 28.5 | 19:00
Bagerhat | 89 | 00:00 | Dhanmondi | 130 | 14:00 | Kulaura | 50 | 19:30 | Panchagarh | 46 | 08:00 | Tangail | 195 | 22:00
Bakulia | 126 | 19:30 | Dohazari | 92 | 19:00 | Kurigram | 61 | 01:00 | Patuakhali | 133 | 22:00 | Thakurgaon | 66 | 22:00
Banani | 60 | 14:00 | Faridpur | 133 | 00:00 | Kushtia | 120 | 18:00 | Payra | 1.02 | 16:00 | Tongi | 116 | 19:30
Bangabhaban | 22 | 11:00 | Fatullah | 72 | 10:00 | Lalbag | 78 | 19:00 | Purbachal | 20 | 21:00 | Ullon | 40 | 21:00
Barapukuria | 57 | 23:00 | Fenchuganj | 48 | 21:00 | Lalmonirhat | 48 | 01:00 | Purbasadipur | 96 | 05:00 | Uttara | 93 | 21:00
Barguna | 20 | 23:00 | Feni | 118 | 21:00 | Madanganj | 82 | 00:00 | Rahim | 26 | 08:00 | UttaraNew | 18 | 00:00
Barishal | 118 | 19:30 | GPH | 20 | 00:00 | Madaripur | 108 | 22:00 | Rajbari | 60 | 19:30 | Zigatola | 57 | 19:00
Barishal-230 | 66 | 23:00 | Ghorashal | 69 | 00:00 | Madartek | 92 | 23:00 | Rajendrapur | 92 | 05:00
Baroaulia | 69 | 23:00 | Goalpara | 25 | 19:00 | Madunaghat | 60 | 19:00 | Rajshahi | 132 | 22:00
Baroirhat | 56 | 19:30 | Gollamari | 56 | 19:00 | Magura | 50 | 00:00 | Rajshahi-230 | 26 | 02:00
Bashundhara | 158 | 19:00 | Gopalganj | 88.6 | 23:00 | Mahasthangarh | 70 | 00:00 | Ramganj | 88 | 19:00
BashundharaCement | 12 | 11:00 | Gulshan | 138 | 17:00 | Manikganj | 100 | 20:00 | Rampur | 16 | 00:00
Beanibazar | 65 | 00:00 | Halishahar | 89 | 20:00 | Maniknagar | 80 | 16:00 | Rangamati | 14 | 19:00
Benapole | 52 | 07:00 | HaripurSBU | 148 | 21:00 | Matarbari | 40 | 21:00 | Rangpur | 105 | 08:00
Bhaluka | 96 | 19:30 | Hasnabad | 109 | 21:00 | Matuail | 64 | 10:00 | Ruppur | 5 | 09:00
Bhandaria | 48 | 23:00 | Hathazari | 97 | 19:00 | Millgate | 58 | 15:00 | SSM | 3 | 05:00
Bhangura | 30 | 22:00 | Ishurdi | 73 | 19:30 | Mirpur | 133 | 19:00 | Saidpur | 93 | 08:00
Bheramara(GK) | 51 | 00:00 | Jaldhaka | 60 | 00:00 | Mirsorai | N/A | N/A | Satkhira | 95 | 06:00
Bhulta | 252 | 21:00 | Jamalpur | 124 | 19:00 | Mithapukur | 34 | 19:30 | Satmasjid | 101 | 19:00
Bog-Sherpur | 50 | 22:00 | Jashore | 122 | 19:00 | Modern | 0 | 00:00 | Savar | 156 | 09:00
Bogura | 158 | 19:30 | Jhenaidah | 99 | 20:00 | Mogbazar | 132 | 17:00 | Shahjadpur | 85 | 22:00
Borhanuddin | 41 | 23:00 | Joydebpur | 196 | 19:30 | Mongla | 32 | 09:00 | Shahjibazar | 95 | 00:00
Brahmanbaria | 160 | 00:00 | Joypurhat | 62 | 22:00 | Motijheel | 38 | 11:00 | Shahmirpur | 46.5 | 18:30
Cantonment | 167 | 19:00 | Juldah | 27 | 09:00 | Munshiganj | 110 | 22:00 | Shariatpur | 78 | 22:00
Chandpur | 70 | 22:00 | KSRM | 29 | 09:00 | Mymensingh | 210 | 19:00 | Sherpur | 100 | 19:00
Chandraghona | 34 | 19:30 | Kabirpur | 273 | 12:00 | Naogaon | 116 | 00:00 | Shikalbaha | 28 | 19:00
Chapai | 64 | 00:00 | Kachua | 81 | 21:00 | Narail | 48 | 21:00 | Shikalbaha-230 | N/A | N/A
Charsaidpur | 22 | 07:00 | Kallyanpur | 102 | 19:00 | Narinda | 73 | 17:00 | Shitalakhya | 114 | 12:00
Chauddagram | 47 | 21:00 | Kalurghat | 6 | 13:00 | Narshingdi | 194 | 22:00 | Sholosohor | N/A | N/A
Chhatak | 32 | 00:00 | Kamrangirchar | 63 | 19:00 | Natore | 149 | 22:00 | Shyampur | 144 | 01:00
Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
(1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2022-08-16 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Bhulta | 382 | 19:00 | 366 | 10:00 | Kaliakoir | 384 | 18:30 | 371 | 12:00
| Bibiana | 404 | 19:00 | 394 | 10:00 | Payra | 417 | 04:00 | 409 | 21:00
| BIPTC | 401 | 06:00 | 393 | 20:00 | Rahanpur_I | 413 | 19:00 | 364 | 00:00
| Gopalganj_I | 409 | 19:00 | 394 | 21:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 220 | 00:00 | 210 | 02:00 | Hasnabad | 221 | 00:00 | 210 | 10:00
| AKSML | 224 | 19:00 | 211 | 05:00 | Hathazari | 224 | 19:30 | 215 | 09:00
| Aminbazar | 221 | 00:00 | 211 | 09:00 | Ishurdi | 234 | 19:00 | 228 | 10:00
| Ashuganj | 236 | 23:00 | 227 | 10:00 | Jhenaidah | 227 | 19:00 | 220 | 00:00
| Baghabari | 232 | 18:30 | 228 | 09:00 | Kaliakoir | 220 | 02:00 | 211 | 10:00
| Barapukuria | 221 | 17:00 | 211 | 00:00 | Keranigonj | 219 | 00:00 | 209 | 10:00
| Barishal | 245 | 12:00 | 232 | 22:00 | Khulna(S) | 236 | 19:30 | 229 | 00:00
| Bheramara | 232 | 19:00 | 225 | 00:00 | Maniknagar | 221 | 00:00 | 212 | 10:00
| Bhulta | 225 | 19:00 | 215 | 10:00 | Meghnaghat | 223 | 00:00 | 216 | 09:00
| Bibiana | 232 | 04:00 | 228 | 09:00 | Mirsorai | N/A | N/A | N/A | N/A
| BIPTC | 233 | 19:00 | 226 | 00:00 | Rajshahi | 232 | 19:30 | 225 | 00:00
| Bogura | 227 | 18:30 | 217 | 01:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 247 | 11:00 | 236 | 22:00 | Rampura | 222 | 23:00 | 211 | 10:00
| BSRM | 224 | 19:00 | 214 | 09:00 | Shikalbaha | 225 | 19:30 | 214 | 10:00
| Cumilla(N) | 224 | 19:00 | 217 | 10:00 | Shyampur | 219 | 00:00 | 210 | 10:00
| Fenchuganj | 240 | 14:00 | 230 | 10:00 | Siddhirganj | 223 | 03:00 | 214 | 10:00
| Ghorashal | N/A | N/A | N/A | N/A | Sirajgonj | 233 | 18:30 | 230 | 23:00
| GPH | 223 | 19:30 | 213 | 09:00 | Tongi | 228 | 00:00 | 212 | 10:00
| Haripur | 222 | 23:00 | 212 | 17:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 135 | 21:00 | 126 | 17:00 | Lalbag | 137 | 00:00 | 129 | 17:00
| Agargaon | 136 | 02:00 | 128 | 10:00 | Lalmonirhat | 128 | 17:00 | 116 | 01:00
| Agrabad | 130 | 11:00 | 124 | 09:00 | Madanganj | 130 | 19:00 | 123 | 10:00
| AKS | 130 | 00:00 | 123 | 09:00 | Madaripur | 137 | 07:00 | 128 | 22:00
| Aminbazar | 133 | 21:00 | 124 | 09:00 | Madartek | 135 | 23:00 | 126 | 17:00
| Amnura | 134 | 19:00 | 128 | 08:00 | Madunaghat | 131 | 19:00 | 127 | 12:00
| Ashuganj | 136 | 18:00 | 133 | 13:00 | Magura | 137 | 06:00 | 132 | 00:00
| Bagerhat | 133 | 19:00 | 125 | 00:00 | Mahasthangarh | 133 | 17:00 | 124 | 01:00
| Bakulia | 130 | 16:00 | 127 | 08:00 | Manikganj | 134 | 19:00 | 122 | 14:00
| Banani | 134 | 00:00 | 123 | 11:00 | Maniknagar | 132 | 03:00 | 124 | 17:00
| Bangabhaban | 131 | 00:00 | 124 | 10:00 | Matarbari | 121 | 11:00 | 110 | 18:30
| Barapukuria | 135 | 17:00 | 126 | 00:00 | Matuail | 129 | 19:00 | 123 | 11:00
| Barguna | 140 | 06:00 | 129 | 09:00 | Millgate | 134 | 00:00 | 120 | 18:00
| Barishal | 140 | 05:00 | 127 | 09:00 | Mirpur | 132 | 01:00 | 123 | 10:00
| Barishal-230 | 139 | 06:00 | 130 | 22:00 | Mithapukur | 131 | 17:00 | 120 | 00:00
| Baroaulia | 132 | 20:00 | 126 | 14:00 | Modern | 130 | 05:00 | 125 | 09:00
| Baroirhat | 127 | 19:30 | 122 | 01:00 | Mogbazar | 135 | 03:00 | 129 | 17:00
| Bashundhara | 134 | 00:00 | 123 | 17:00 | Mongla | 132 | 19:30 | 126 | 00:00
| BashundharaCement | 130 | 19:00 | 123 | 10:00 | Motijheel | 131 | 00:00 | 124 | 10:00
| Beanibazar | 128 | 07:00 | 124 | 00:00 | Munshiganj | 131 | 06:00 | 124 | 15:00
| Benapole | 134 | 06:00 | 129 | 00:00 | Mymensingh | 133 | 10:00 | 117 | 06:00
| Bhaluka | 130 | 18:00 | 117 | 02:00 | Naogaon | 133 | 18:30 | 122 | 01:00
| Bhandaria | 138 | 09:00 | 125 | 22:00 | Narail | 136 | 06:00 | 130 | 00:00
| Bhangura | 137 | 18:00 | 134 | 00:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bheramara | 136 | 19:00 | 133 | 00:00 | Narshingdi | 124 | 19:00 | 115 | 10:00
| Bheramara(GK) | 139 | 05:00 | 134 | 17:00 | Natore | 134 | 19:00 | 129 | 00:00
| Bhulta | 122 | 18:30 | 115 | 10:00 | Nawabganj | 138 | 03:00 | 129 | 11:00
| Bog-Sherpur | 135 | 17:00 | 128 | 01:00 | Netrakona | 129 | 10:00 | 115 | 04:00
| Bogura | 136 | 18:00 | 127 | 01:00 | New | 133 | 02:00 | 123 | 17:00
| Bogura-230 | 137 | 18:30 | 128 | 01:00 | Niamatpur | 131 | 18:00 | 119 | 00:00
| Brahmanbaria | 131 | 07:00 | 128 | 12:00 | Noapara | 135 | 12:00 | 130 | 00:00
| Cantonment | 135 | 02:00 | 126 | 10:00 | Pabna | 134 | 06:00 | 131 | 00:00
| Chandpur | 139 | 01:00 | 123 | 02:00 | Palashbari | 130 | 18:30 | 120 | 00:00
| Chandraghona | 132 | 06:00 | 127 | 23:00 | Panchagarh | 126 | 17:00 | 109 | 01:00
| Chapai | 135 | 19:00 | 129 | 01:00 | Patuakhali | 138 | 14:00 | 131 | 09:00
| Charsaidpur | 131 | 23:00 | 124 | 10:00 | Payra | 138 | 04:00 | 135 | 07:00
| Chauddagram | 129 | 11:00 | 123 | 00:00 | PHP | 127 | 11:00 | 121 | 03:00
| Chhatak | 129 | 07:00 | 123 | 21:00 | Postogola | 139 | 23:00 | 132 | 10:00
| Chowmuhani | 126 | 11:00 | 117 | 03:00 | Purbachal | 133 | 01:00 | 123 | 17:00
| Chuadanga | 133 | 06:00 | 127 | 00:00 | Purbasadipur | 128 | 17:00 | 115 | 00:00
| Coxsbazar | 121 | 16:00 | 107 | 23:00 | Rahim | 130 | 00:00 | 125 | 10:00
| Cumilla(N) | 131 | 19:00 | 127 | 02:00 | Rajbari | 135 | 19:00 | 130 | 22:00
| Cumilla(S) | 133 | 04:00 | 125 | 15:00 | Rajendrapur | 138 | 23:00 | 123 | 09:00
| Daudkandi | 132 | 11:00 | 124 | 08:00 | Rajshahi | 132 | 06:00 | 128 | 22:00
| Dhaka | 135 | 21:00 | 127 | 17:00 | Rajshahi-230 | 133 | 19:00 | 129 | 00:00
| Dhamrai | 130 | 23:00 | 121 | 10:00 | Ramganj | 129 | 16:00 | 118 | 03:00
| Dhanmondi | 129 | 00:00 | 123 | 10:00 | Rampur | 129 | 07:00 | 124 | 10:00
| Dohazari | 130 | 11:00 | 123 | 09:00 | Rampura | 135 | 23:00 | 126 | 10:00
| Faridpur | 135 | 19:00 | 130 | 21:00 | Rangamati | 131 | 03:00 | 126 | 10:00
| Fatullah | 133 | 00:00 | 126 | 11:00 | Rangpur | 129 | 17:00 | 116 | 00:00
| Fenchuganj | 133 | 18:00 | 130 | 01:00 | Ruppur | 137 | 19:00 | 133 | 00:00
| Feni | 129 | 11:00 | 123 | 18:30 | Saidpur | 130 | 16:00 | 119 | 00:00
| Ghorashal | 137 | 00:00 | 132 | 10:00 | Satkhira | 131 | 06:00 | 124 | 22:00
| Goalpara | 135 | 06:00 | 132 | 00:00 | Satmasjid | 138 | 15:00 | 127 | 10:00
| Gollamari | 134 | 19:00 | 131 | 00:00 | Savar | 134 | 02:00 | 123 | 11:00
| Gopalganj | 139 | 02:00 | 134 | 22:00 | Shahjadpur | 140 | 05:00 | 136 | 00:00
| Gopalganj_I | 139 | 19:00 | 132 | 22:00 | Shahjibazar | 134 | 16:00 | 130 | 01:00
| Gulshan | 134 | 19:00 | 126 | 17:00 | Shahmirpur | 131 | 19:00 | 125 | 10:00
| Halishahar | 130 | 11:00 | 124 | 12:00 | Shariatpur | 137 | 09:00 | 127 | 22:00
| Haripur | 130 | 00:00 | 125 | 10:00 | Sherpur | 134 | 23:00 | 114 | 04:00
| HaripurSBU | 130 | 00:00 | 125 | 17:00 | Shikalbaha | 132 | 19:30 | 126 | 09:00
| Hasnabad | 140 | 00:00 | 131 | 17:00 | Shikalbaha-230 | 131 | 05:00 | 126 | 10:00
| Hathazari | 132 | 19:30 | 127 | 09:00 | Shitalakhya | 139 | 00:00 | 129 | 10:00
| Ishurdi | 136 | 06:00 | 133 | 00:00 | Sholosohor | N/A | N/A | N/A | N/A
| Jaldhaka | 130 | 18:30 | 115 | 00:00 | Shyampur | 133 | 00:00 | 126 | 10:00
| Jamalpur | 137 | 18:00 | 117 | 06:00 | Shyampur-230 | 132 | 00:00 | 126 | 10:00
| Jashore | 134 | 19:00 | 129 | 00:00 | Siddhirganj | 130 | 19:00 | 124 | 10:00
| Jhenaidah | 138 | 19:00 | 134 | 00:00 | Sirajganj | 134 | 18:00 | 129 | 10:00
| Jhenaidah-230 | 138 | 06:00 | 134 | 00:00 | Sonargaon | 130 | 22:00 | 125 | 01:00
| Joydebpur | 140 | 19:00 | 127 | 12:00 | Sreemongol | 135 | 23:00 | 131 | 10:00
| Joypurhat | 133 | 18:00 | 121 | 00:00 | Srinagar | 137 | 02:00 | 130 | 10:00
| Juldah | 130 | 04:00 | 125 | 09:00 | SSM | 133 | 12:00 | 130 | 01:00
| Kabirpur | 135 | 18:30 | 123 | 10:00 | Sunamganj | 128 | 12:00 | 119 | 21:00
| Kachua | 132 | 11:00 | 121 | 02:00 | Sylhet | 131 | 06:00 | 128 | 00:00
| Kaliakoir | 135 | 18:00 | 126 | 08:00 | Tangail | 135 | 19:00 | 124 | 14:00
| Kallyanpur | 133 | 00:00 | 125 | 10:00 | Thakurgaon | 128 | 17:00 | 110 | 01:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2022-08-16
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 636 | 7542 | 4362 | 11904 |  |  |  | QF-LDC-11
0:30 | 555 | 7547 | 4414 | 11961 | Date: | 2022-08-16
1:00 | 474 | 7552 | 4466 | 12018
1:30 | 482 | 7205.5 | 4401 | 11606.5
2:00 | 490 | 6859 | 4336 | 11195
2:30 | 489 | 6906 | 4265 | 11171 | [5 empty] | Gen. at Eve. Peak | 13526 | 13526 MW (21:00 )
3:00 | 488 | 6953 | 4194 | 11147 | [6 empty] | 21:00
3:30 | 510 | 6875.5 | 4197.5 | 11073 | [5 empty] | Gen. at Day Peak | 11564 | 11564 MW (10:00 )
4:00 | 532 | 6798 | 4201 | 10999 | [6 empty] | 10:00
4:30 | 574 | 6712 | 4196 | 10908 | [5 empty] | Highest Generation | 13526
5:00 | 616 | 6626 | 4191 | 10817 | [6 empty] | 21:00
5:30 | 683 | 6548.5 | 4143.5 | 10692
6:00 | 750 | 6471 | 4096 | 10567
6:30 | 628 | 6554 | 4009 | 10563
7:00 | 506 | 6637 | 3922 | 10559
7:30 | 612 | 6716.5 | 3951.5 | 10668
8:00 | 718 | 6796 | 3981 | 10777
8:30 | 789 | 6982.5 | 4007.5 | 10990
9:00 | 860 | 7169 | 4034 | 11203
9:30 | 850 | 7311 | 4072.5 | 11383.5
10:00 | 840 | 7453 | 4111 | 11564
10:30 | 834 | 7363.5 | 4140 | 11503.5
11:00 | 828 | 7274 | 4169 | 11443
11:30 | 841 | 7230.5 | 4196 | 11426.5
12:00 | 854 | 7187 | 4223 | 11410
12:30 | 794 | 7197 | 4192.5 | 11389.5
13:00 | 734 | 7207 | 4162 | 11369
13:30 | 735 | 7242.5 | 4130.5 | 11373
14:00 | 736 | 7278 | 4099 | 11377
14:30 | 745 | 7285.5 | 4076.5 | 11362
15:00 | 754 | 7293 | 4054 | 11347
15:30 | 755 | 7303 | 4075.5 | 11378.5
16:00 | 756 | 7313 | 4097 | 11410
16:30 | 744 | 7385 | 4107 | 11492
17:00 | 732 | 7457 | 4117 | 11574
17:30 | 670 | 7653 | 4118 | 11771
18:00 | 608 | 7849 | 4119 | 11968
18:30 | 440 | 8302.5 | 4172.5 | 12475
19:00 | 272 | 8756 | 4226 | 12982
19:30 | 424 | 8671 | 4474 | 13145
20:00 | 512 | 8802 | 4539 | 13341 |  |  |  | Executive Engineer
20:30 | 462 | 8833.5 | 4600 | 13433.5 |  |  |  | Network Operation Division
21:00 | 412 | 8865 | 4661 | 13526
21:30 | 367 | 8848.5 | 4634.5 | 13483
22:00 | 322 | 8832 | 4608 | 13440 |  |  |  |  | Page 6 of 7
22:30 | 403 | 8579 | 4592.5 | 13171.5
23:00 | 484 | 8326 | 4577 | 12903
23:30 | 560 | 7934 | 4469.5 | 12403.5
24:00 | 636 | 7542 | 4362 | 11904
13526 MW (21:00 )
11564 MW (10:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2022-08-16 |  | Energy |  | 283560065
[13 empty] | 2022-08-16 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 4196 | 897 | 1796 | 793 | 2196 | 941 | 70 | 439 | 625 | 164 | 0 | 1655.1487
0:30 | 4397.5 | 890.5 | 1739 | 786.5 | 2128 | 941 | 108 | 441.5 | 595 | 148 | 0 | 957.5164 | Date: | 2022-08-16
1:00 | 4599 | 884 | 1682 | 780 | 2060 | 941 | 146 | 444 | 565 | 132 | 0 | 259.8842
1:30 | 4508.5 | 884 | 1633 | 739 | 1838.5 | 943 | 146 | 446 | 554 | 131 | 0 | 278.7764 | [8 empty] | Total Energy | 283.5601 | Total Energy Gen 283.560 MKWHr Energy Not Served 17.918 MKWHr Energy Requirement 301.478 MKWHr
2:00 | 4418 | 884 | 1584 | 698 | 1617 | 945 | 146 | 448 | 543 | 130 | 0 | 297.6687 | [8 empty] | Energy not Served | 17.9184
2:30 | 4433 | 884 | 1590 | 572.5 | 1699 | 944.5 | 146 | 447.5 | 542.5 | 130 | 0 | 265.4136 | [8 empty] | Energy Requirement | 301.4785
3:00 | 4448 | 884 | 1596 | 447 | 1781 | 944 | 146 | 447 | 542 | 130 | 0 | 233.1585
3:30 | 4451 | 884 | 1622.5 | 312 | 1839 | 944 | 146 | 447.5 | 525 | 120 | 0 | 232.2369 | [6 empty] | Shortage
4:00 | 4454 | 884 | 1649 | 177 | 1897 | 944 | 146 | 448 | 508 | 110 | 0 | 231.3153
4:30 | 4430 | 884 | 1692 | 88.5 | 1869.5 | 944 | 146 | 448 | 503.5 | 121 | 0 | 292.1393
5:00 | 4406 | 884 | 1735 | 0 | 1842 | 944 | 146 | 448 | 499 | 132 | 0 | 352.9632
5:30 | 4357.5 | 883.5 | 1713.5 | 0 | 1808.5 | 942.5 | 146 | 448.5 | 481 | 128 | 2 | 237.7664
6:00 | 4309 | 883 | 1692 | 0 | 1775 | 941 | 146 | 449 | 463 | 124 | 4 | 122.5695
6:30 | 4371 | 883.5 | 1733.5 | 0 | 1725.5 | 941 | 145.5 | 374.5 | 415 | 125 | 23 | 117.04 |  |  |  |  | Coal
7:00 | 4433 | 884 | 1775 | 0 | 1676 | 941 | 145 | 300 | 367 | 126 | 42 | 111.5106
7:30 | 4409.5 | 884 | 1768.5 | 0 | 1748 | 942 | 145 | 344.5 | 383 | 129 | 63.5 | 234.7553 |  |  |  | Oil |  |  |  | ,
8:00 | 4386 | 884 | 1762 | 0 | 1820 | 943 | 145 | 389 | 399 | 132 | 85 | 358
8:30 | 4376 | 884 | 1780 | 119 | 1862 | 944.5 | 145.5 | 392 | 398 | 137 | 121.5 | 518.5
9:00 | 4366 | 884 | 1798 | 238 | 1904 | 946 | 146 | 395 | 397 | 142 | 158 | 679
9:30 | 4361 | 884 | 1778.5 | 369.5 | 1935 | 949 | 146.5 | 413 | 416 | 138 | 183 | 827.5
10:00 | 4356 | 884 | 1759 | 501 | 1966 | 952 | 147 | 431 | 435 | 134 | 208 | 976
10:30 | 4263.5 | 884 | 1749 | 553 | 1952.5 | 951.5 | 147 | 432.5 | 431 | 140 | 210 | 1172.5
11:00 | 4171 | 884 | 1739 | 605 | 1939 | 951 | 147 | 434 | 427 | 146 | 212 | 1369
11:30 | 4150 | 884.5 | 1712 | 645.5 | 1932.5 | 951 | 147.5 | 435.5 | 428 | 150 | 203.5 | 1444
12:00 | 4129 | 885 | 1685 | 686 | 1926 | 951 | 148 | 437 | 429 | 154 | 195 | 1519
12:30 | 4114.5 | 885 | 1679.5 | 694.5 | 1957.5 | 951.5 | 148 | 417.5 | 413.5 | 123 | 201 | 1468.5
13:00 | 4100 | 885 | 1674 | 703 | 1989 | 952 | 148 | 398 | 398 | 92 | 207 | 1418
13:30 | 4100 | 885 | 1674 | 703 | 1989 | 952 | 148 | 398 | 398 | 92 | 207 | 1461
14:00 | 4100 | 885 | 1674 | 703 | 1989 | 952 | 148 | 398 | 398 | 92 | 207 | 1504
14:30 | 4067 | 885 | 1660 | 701 | 2034.5 | 952.5 | 151 | 382 | 381.5 | 129 | 177.5 | 1515
15:00 | 4034 | 885 | 1646 | 699 | 2080 | 953 | 154 | 366 | 365 | 166 | 148 | 1526
15:30 | 4043.5 | 885 | 1641.5 | 680 | 2128.5 | 928 | 153 | 390 | 401.5 | 165 | 134 | 1490
16:00 | 4053 | 885 | 1637 | 661 | 2177 | 903 | 152 | 414 | 438 | 164 | 120 | 1454
16:30 | 4131 | 884.5 | 1645 | 637 | 2293 | 903.5 | 151 | 386 | 415 | 164 | 88 | 877
17:00 | 4131 | 884 | 1653 | 613 | 2409 | 904 | 150 | 358 | 392 | 164 | 56 | 300
17:30 | 4131.5 | 884.5 | 1650.5 | 511.5 | 2694 | 889.5 | 148.5 | 354.5 | 447.5 | 159 | 35 | 150
18:00 | 4132 | 885 | 1648 | 410 | 2979 | 875 | 147 | 351 | 503 | 154 | 14 | 0
18:30 | 4148 | 885 | 1696.5 | 592 | 3169.5 | 877.5 | 147 | 355 | 566.5 | 164 | 7 | 284.7667
19:00 | 4164 | 885 | 1745 | 774 | 3360 | 880 | 147 | 359 | 630 | 174 | 0 | 569.5334
19:30 | 4205 | 886 | 1731 | 749 | 3392 | 929 | 148 | 395 | 708 | 174 | 0 | 557.5529
20:00 | 4236 | 884 | 1757 | 828 | 3454 | 930 | 150 | 414 | 722 | 158 | 0 | 561.2392
20:30 | 4238 | 884 | 1762 | 878.5 | 3455.5 | 935 | 150 | 426 | 745 | 163 | 0 | 545.1116
21:00 | 4240 | 884 | 1767 | 929 | 3457 | 940 | 150 | 438 | 768 | 168 | 0 | 528.984
21:30 | 4223 | 885 | 1783.5 | 929 | 3414 | 946 | 150.5 | 437.5 | 764 | 165 | 0 | 820.992
22:00 | 4206 | 886 | 1800 | 929 | 3371 | 952 | 151 | 437 | 760 | 162 | 0 | 1113
22:30 | 4173.5 | 891.5 | 1796 | 794 | 3270.5 | 952 | 152.5 | 439 | 755 | 162 | 0 | 1059.5
23:00 | 4141 | 897 | 1792 | 659 | 3170 | 952 | 154 | 441 | 750 | 162 | 0 | 1006
23:30 | 4168.5 | 897 | 1794 | 726 | 2683 | 946.5 | 112 | 440 | 687.5 | 163 | 0 | 1127.5 | Max Temp. in Dhaka |  | 24.7° C | 35° C
24:00 | 4196 | 897 | 1796 | 793 | 2196 | 941 | 70 | 439 | 625 | 164 | 0 | 1249
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 283.560 MKWHr Energy Not Served 17.918 MKWHr Energy Requirement 301.478 MKWHr
Note on W13: Author:

## Generation
g | 2022-08-16
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 81 | 81 | 81 | 81 | 81 | 81 | 80 | 80 | 81 | 82 | 82 | 83 | 83 | 83 | 84 | 82 | 80 | 77 |  | 77 | 78 | 80 | 80 | 81 | 84 | 0 | 1929731
2 | Karnaphuli Hydro PP Unit-4 & 5 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1612000
3 | Chattogram TPP-1 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2500000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 19 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 532513
| Teknaf 20MW PP (Solartech) |  |  |  |  | 0 | 1 | 3 | 2 | 8 | 17 | 20 |  | 19 | 19 | 15 | 6 | 5 | 0 | [8 empty] | 108540
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 51 | 51 | 51 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 706931
12 | Hathazari 100 MW peaking PP | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 30 | 26 |  | 26 | 26 | 26 | 26 | 26 | 25 | 26 | 602360
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 17 | 1 | 15 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 44 |  | 105 | 105 | 105 | 51 | 51 | 51 | 27 | 725963
| Daudkandi 200 MW PP (B.Trac) | 175 | 196 | 150 | 0 |  |  |  |  | 20 | 150 | 200 | 200 | 200 | 196 | 200 | 200 | 200 | 100 |  | 185 | 150 | 150 | 200 | 200 | 150 | 200 | 3173952
14 | Titas 50 MW Peaking PP | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 31 | 37 | 37 | 37 | 37 |  | 37 | 37 | 37 | 37 | 37 | 37 | 39 | 932664
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 195 | 194 | 197 | 191 | 154 | 115 | 121 | 156 | 193 | 193 | 95 | 93 | 93 | 92 | 94 | 93 | 95 | 95 |  | 94 | 92 | 95 | 95 | 96 | 95 | 96 | 3309000
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 130 | 85 | 90 | 85 | 92 | 90 | 85 | 95 | 95 | 95 | 80 | 80 | 80 | 85 | 85 | 80 | 80 | 224 |  | 291 | 296 | 296 | 296 | 296 | 293 | 140 | 3362181
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 16 | 26 | 26 | 26 | 26 | 26 |  | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 418181
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4284000
24
25 | Ghorasal 365 MW CCPP Unit-7 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 7139018
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 40 | 40 | 37 | 35 | 35 | 34 | 34 | 34 | 37 | 37 |  | 37 | 37 | 37 | 40 | 30 | 30 | 30 | 852624
33 | Ashuganj 225 MW CCPP | 210 | 211 | 211 | 212 | 209 | 213 | 209 | 208 | 209 | 205 | 207 | 207 | 204 | 202 | 203 | 204 | 204 | 207 |  | 208 | 207 | 206 | 206 | 205 | 209 | 208 | 5007000
34 | Ashuganj 450 MW CCPP(South) | 310 | 310 | 310 | 305 | 310 | 310 | 325 | 320 | 310 | 325 | 310 | 305 | 305 | 310 | 305 | 305 | 320 | 310 |  | 305 | 310 | 310 | 310 | 320 | 265 | 295 | 7649000
| Ashuganj 450 MW CCPP(North) | 335 | 335 | 330 | 330 | 335 | 335 | 360 | 345 | 320 | 335 | 320 | 320 | 320 | 325 | 325 | 325 | 330 | 340 |  | 325 | 325 | 330 | 330 | 335 | 275 | 305 | 8247900
Ashuganj 420 MW CCPP(East)
35 | Ashuganj 55 MW PP (Precision) | 56 | 56 | 56 | 55 | 55 | 55 | 55 | 55 | 55 | 52 | 51 | 50 | 50 | 49 | 48 | 48 | 49 | 48 |  | 50 | 50 | 53 | 55 | 55 | 55 | 56 | 1266240
36 | Chandpur 150 MW CCPP | 136 | 0 | [7 empty] | 50 | 50 | 30 | 31 | 31 | 30 | 31 | 84 | 83 |  | 142 | 142 | 142 | 142 | 140 | 142 | 141 | 1300970
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 407 | 406 | 406 | 407 | 407 | 406 | 407 | 408 | 407 | 408 | 403 | 403 | 399 | 399 | 394 | 397 | 400 | 401 |  | 398 | 398 | 398 | 398 | 398 | 398 | 397 | 9775110
40 | Meghnaghat 450 MW CCPP(MPL) | 225 | 225 | 225 | 280 | 400 | 400 | 420 | 420 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 |  | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 8905250
41 | Haripur 360MW CCPP(HPL) | 337 | 336 | 340 | 336 | 336 | 338 | 337 | 328 | 330 | 330 | 330 | 322 | 326 | 326 | 317 | 317 | 343 | 350 |  | 350 | 322 | 322 | 321 | 326 | 329 | 312 | 7904000
42 | RPCL 210MW CCPP | 158 | 158 | 158 | 158 | 160 | 160 | 157 | 156 | 148 | 131 | 117 | 102 | 95 | 70 | 71 | 82 | 82 | 82 |  | 105 | 101 | 103 | 101 | 101 | 102 | 102 | 2787840
43 | Sutiakhali 50 MW Solar PP |  |  |  |  | 0 | 1 | 12 | 20 | 42 | 54 | 51 | 42 | 40 | 49 | 16 | 32 | 8 | 3 | [8 empty] | 323550
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 44 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1022000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 686936
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 62 | 56 | 56 | 56 | 56 | 57 | 59 | 61 | 62 | 60 | 61 | 59 | 60 | 60 | 57 | 59 | 58 | 58 |  | 63 | 63 | 62 | 63 | 62 | 64 | 62 | 1424736
48 | Shahjibazar 86MW PP (Shahjibazar) | 81 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 81 | 81 | 81 | 81 | 81 | 78 | 78 | 777600
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 221 | 193 | 194 | 213 | 220 | 221 | 221 | 221 | 221 | 221 |  | 221 | 221 | 221 | 221 | 221 | 221 | 220 | 5215200
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL) | 5 | 5 | 5 | 5 | 5 | 5 | 6 | 6 | 6 | [16 empty] | 0 | 61340
53 | Sylhet 10MW PP (Desh) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 10 | 10 | 10 | 10 | 9 | 9 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 224100
54 | Hobiganj 11MW PP Cofidence-E | [26 empty] | 0
55 | Fenchugonj 51 MW PP (Barakatullah) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 129600
56 | Shahjahanulla 25 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | [16 empty] | 0 | 74160
57 | Bibiana-II 341 MW CCPP (Summit) | 300 | 275 | 285 | 290 | 270 | 270 | 280 | 300 | 310 | 300 | 290 | 280 | 290 | 310 | 310 | 300 | 295 | 290 |  | 285 | 270 | 280 | 280 | 300 | 290 | 310 | 7228000
| Bibiyana South 400 MW | 400 | 400 | 400 | 400 | 400 | 350 | 380 | 400 | 400 | 400 | 395 | 400 | 393 | 386 | 391 | 392 | 391 | 400 |  | 387 | 400 | 400 | 400 | 395 | 400 | 396 | 9451500
58 | Nababganj 55 MW PP (Southern power ) | [6 empty] | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 55 | 55 |  | 55 | 35 | 55 | 55 | 55 | 55 | 55 | 773708
59 | Tangail Palli Power Gen 22 MW | 10 | 10 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 10 | 8 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 287280
60 | Barabkunda 22 MW PP (Regent) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 10 | 10 | 11 | 14 | 13 | 13 | 14 | 14 | 14 |  | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 324192
61 | Narshingdi 22 MW PP (Doreen) | 19 | 19 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 19 | 19 | 22 | 22 | 22 | 22 | 22 |  |  |  |  | 22 | 22 | 22 | 22 | 22 | 402120
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 502848
63 | Impoprt (Tripura) | 132 | 130 | 130 | 110 | 132 | 124 | 126 | 132 | 142 | 134 | 146 | 154 | 92 | 126 | 166 | 164 | 164 | 154 |  | 174 | 174 | 158 | 168 | 162 | 162 | 164 | 2880000
64 | Malancha, Ctg. EPZ (United) | 42 | 42 | 42 | 42 | 42 | 41 | 40 | 18 | 13 | 5 | 3 | 2 | 3 | 3 | 2 | 5 | 5 | 3 |  | 20 | 24 | 25 | 29 | 37 | 38 | 38 | 579360
65 | Feni 22MW PP (Doreen) | 22 | 0 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 19 | 21 | 21 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 475344
66 | Feni 11 MW PP (Doreen) | 6 | 0 | 0 | 8 | 8 | 8 | 8 | 8 | 8 | 10 | 10 | 5 | 10 | 10 | 10 | 7 |  | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 193320
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 0 | 33 | 33 |  | 33 | 33 | 25 | 25 | 29 | 33 | 33 | 25 | 33 | 33 |  | 33 | 33 | 33 | 33 | 0 | 33 | 33 | 670900
68 | Cumilla 25 MW PP (Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 17 | 17 | 17 | 20 | 20 | 20 | 459620
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 22 | 22 | 16 | 16 | 16 | 23 | 22 | 26 |  | 21 | 25 | 25 | 25 | 25 | 25 | 25 | 464040
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 788760
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 25 | 25 | 16 | 16 | 20 | 22 | 22 | 22 |  | 22 | 22 | 22 | 24 | 24 | 24 | 24 | 623400
73 | Ghorashal 108MW PP (Regent) | 93 | 93 | 92 | 92 | 92 | 92 | 93 | 92 | 89 | 89 | 92 | 92 | 92 | 86 | 85 | 84 | 81 | 78 |  | 80 | 80 | 80 | 81 | 81 | 80 | 80 | 2064772
| Feni Lanka Power | [25 empty] | 0 | 0
| Chowmuhani 113 MW | 28 | 4 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 16 | 28 | 50 | 58 |  | 58 | 58 | 58 | 58 | 58 | 58 | 16 | 611520
| Manikgonj 162MW PP(MPGL) | 108 | 108 | 90 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 44 | 108 | 108 | 108 | 162 | 162 | 162 |  | 162 | 162 | 162 | 162 | 162 | 162 | 72 | 2328480
77 | Siddhirganj 100 PP(Dutch Bangla) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 |  | 32 | 32 | 32 | 32 | 32 | 32 | 9 | 321600
78 | Gazipur 52 MW PP | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 |  | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 980640
79 | Kodda 150MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 126 |  | 125 | 125 | 125 | 125 | 126 | 126 | 16 | 1052160
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | [26 empty] | 0
| Gazipur 100 MW PP | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 88 | 88 | 88 | 88 | 70 | 70 | 88 | 88 | 88 | 88 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2316000
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 0 | 2 | 4 | 3 | 3 | 4 | 3 | 3 | 3 | 2 | 1 | [9 empty] | 28080
| Jodiac Power | 36 | 10 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 |  | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 884462
| Karnaphuli Power Ltd. | 55 | 51 | 51 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 50 | 55 | 46 | 53 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1313922
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL) | 8 | 7 | 8 | 8 | 8 | 7 | 8 | 8 | 7 | 8 | 8 | 7 | 8 | 8 | 8 | 8 | 11 | 48 |  | 49 | 50 | 49 | 47 | 41 | 49 | 10 | 439680
| Meghnaghat 104 MW PP (OPCL) |  |  | 0 | 17 | 17 | 0 |  | 17 | 17 | 17 | 16 | 17 | 17 | 17 | 17 | 17 | 17 | 22 |  | 34 | 34 | 34 | 34 | 34 | 34 | 19 | 404160
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 790320
92 | Fenchuganj 44MW (Energyprima) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 143640
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1128102
94 | Gagnagar 102 MW PP (Digital Power) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 32 | 32 | 32 | 32 | 32 | 32 | 8 | 302688
95 | Patenga 50MW PP (Baraka) | 6 | 6 | 5 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 |  | 16 | 39 | 40 | 42 | 12 | 6 | 6 | 237600
96 | Chattogram 108 MW PP (ECPV) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 11 | 11 | 11 | 11 | 11 | 12 | 13 | 30 |  | 77 | 91 | 91 | 91 | 92 | 58 | 11 | 666240
97 | katpotti 52 MW
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 740685
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1325689
101 | Kushiara 163 MW CCPP (KP)
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 0 | 2 | 2 | 2 | 1 | 1 | 2 | 2 | 1 | 1 | [9 empty] | 13950
103 | Kamalaghat 54 MW PP(Banco Energy) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 662400
104 | Keranigonj 300 MW PP (APR) | 187 | 159 | 104 | 22 | 0 |  |  |  | 104 | 103 | 103 | 104 | 104 | 103 | 101 | 60 | 60 | 30 |  | 240 | 202 | 250 | 301 | 301 | 155 | 207 | 2919141
105 | Bramhangoan 100 MW PP (Aggreko) | 96 | 97 | 97 | 97 | 0 |  |  |  | 50 | 92 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 50 |  | 81 | 80 | 80 | 81 | 81 | 50 | 50 | 1508028
106 | Mymensingh 200 MW PP (United) | 48 | 48 | 48 | 48 | 47 | 48 | 48 | 76 | 77 | 77 | 78 | 78 | 78 | 77 | 77 | 77 | 77 | 170 |  | 170 | 170 | 180 | 180 | 179 | 179 | 47 | 2181600
112 | Aurahati 100MW PP (Aggreko) | 96 | 96 | 96 | 58 | 0 |  |  |  | 50 | 94 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 50 |  | 92 | 70 | 93 | 86 | 86 | 86 | 86 | 1572319
114 | Kodda 149 MW PP Unit-1 (Summit) | 52 | 36 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 34 | 35 | 35 | 35 | 65 | 148 |  | 149 | 149 | 149 | 149 | 149 | 149 | 53 | 1621584
115 | Juldah 100 MW PP Unit-3 (Acorn) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 519360
116 | Chandpur 200MW (Desh energy) | 200 | 0 | 68 | 182 | 155 | 155 | 155 | 155 | 169 | 200 | 192 | 180 | 180 | 180 | 200 | 180 | 180 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 180 | 4163520
117 | Ashuganj 150MW PP (Midland) | 125 | 130 | 133 | 137 | 100 | 70 | 50 | 58 | 85 | 124 | 135 | 125 | 125 | 124 | 122 | 123 | 123 | 130 |  | 130 | 132 | 132 | 133 | 138 | 133 | 132 | 2898836
118 | Bibiyana-III 400 MW CCPP | 402 | 401 | 402 | 401 | 401 | 352 | 398 | 402 | 402 | 405 | 403 | 402 | 402 | 404 | 403 | 404 | 405 | 402 |  | 398 | 403 | 402 | 402 | 403 | 402 | 404 | 9544000
| Jamalpur 115 MW PP (United) | 49 | 49 | 49 | 49 | 49 | 49 | 58 | 69 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 78 |  | 77 | 79 | 79 | 79 | 79 | 79 | 49 | 1537200
| Anwara 300 MW PP (United) | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 120 | 122 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 |  | 207 | 210 | 211 | 213 | 213 | 52 | 52 | 2606945
| Juldah unit-2 (Acorn) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 493440
| Anlima Energy Ltd. | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 |  | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 2570564
| Bhairob 54.5 MW | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 887040
| Spectra Solar Plant Ltd. | [5 empty] | 0 | 3 | 8 | 23 | 31 | 30 | 35 | 30 | 31 | 25 | 19 | 7 | 2 | [8 empty] | 238890
| Chandpur 115(Doreen) | 89 | 0 | 60 | 94 | 96 | 96 | 95 | 96 | 96 | 96 | 91 | 94 | 95 | 94 | 96 | 91 | 95 | 72 |  | 94 | 96 | 96 | 95 | 96 | 96 | 80 | 2125440
| Kanchan Purbachal Power Generation Ltd. | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 47 | 36 | 36 | 35 | 45 | 45 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1251000
Mirsharai 150 MW (Oil)
Mirsharai 150 MW (Gas)
120 | Eastern Zone Total | 7552 | 6859 | 6953 | 6798 | 6626 | 6471 | 6637 | 6796 | 7169 | 7453 | 7274 | 7187 | 7207 | 7278 | 7293 | 7313 | 7457 | 7849 |  | 8756 | 8671 | 8802 | 8865 | 8832 | 8326 | 7542 | 179072279
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | [7 empty] | 16 | 16 | 16 | 16 | 16 | 16 | 0 | 270720
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 16 | 16 | 16 | 16 | 16 | 0 | [11 empty] | 17 |  | 40 | 50 | 37 | 37 | 37 | 37 | 26 | 292800
| Khulna 225 MW CCPP | 229 | 230 | 229 | 230 | 229 | 230 | 170 | 221 | 224 | 222 | 222 | 222 | 221 | 219 | 217 | 220 | 218 | 221 |  | 223 | 223 | 222 | 223 | 223 | 226 | 226 | 5351040
129 | Rupsha 105 MW PP (Orion rupsha) | [8 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 53 |  | 53 | 53 | 53 | 53 | 53 | 53 | 0 | 477600
130 | Mongla Orion 100 MW Solar PP |  |  |  |  | 0 | 2 | 22 | 48 | 76 | 91 | 97 | 105 | 105 | 91 | 77 | 53 | 30 | 7 | [8 empty] | 786240
131 | Rampal 1320 MW (BIFPCL)
132 | United Payra Power Ltd. | 35 | 35 | 35 | 35 | 35 | 35 | 0 |  |  | 15 | 35 | 35 | 35 | 72 | 72 | 90 | 127 | 127 |  | 127 | 127 | 150 | 150 | 150 | 150 | 150 | 1653600
133 | Bhola Nutan Biddut BD LTD (GAS)
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 48 | 48 | 48 | 48 | 48 | 48 | 16 | 16 | 16 | 16 | 16 | 32 | 32 | 32 | 32 | 48 | 48 | 48 |  | 48 | 48 | 55 | 110 | 80 | 80 | 80 | 1102368
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 152 | 152 | 152 | 151 | 152 | 149 | 152 | 151 | 150 | 150 | 147 | 147 | 146 | 146 | 143 | 147 | 147 | 142 |  | 131 | 148 | 149 | 149 | 147 | 152 | 152 | 3570435
140 | Bhola 33 MW PP (Venture) | 29 | 28 | 27 | 25 | 25 | 21 | 20 | 19 | 21 | 18 | 22 | 23 | 22 | 24 | 29 | 27 | 25 | 18 |  | 24 | 24 | 30 | 30 | 29 | 33 | 33 | 596135
141 | Noapara 100 MW PP (Bangla Trac) | 52 | 50 | 0 | [5 empty] | 6 | 10 | 48 | 72 | 90 | 90 | 90 | 93 | 93 | 60 |  | 65 | 93 | 93 | 93 | 93 | 50 | 82 | 1372800
142 | Noapara 40 MW PP (Khanjahan Ali) | 8 | 0
143 | Gopalganj 100 MW Peaking PP | 47 | 42 | 42 | 42 | 42 | 42 | 36 | 36 | 31 | 31 | 20 | 20 | 20 | 16 | 14 | 13 | 14 | 12 |  | 27 | 35 | 42 | 65 | 60 | 58 | 53 | 791680
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | 105 | 105 | 105 | 105 | 105 | 88 | 89 | 89 | 89 | 89 | 71 | 70 | 71 | 71 | 71 | 71 | 80 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2237040
146 | Bheramara HVDC | 884 | 884 | 884 | 884 | 884 | 883 | 884 | 884 | 884 | 884 | 884 | 885 | 885 | 885 | 885 | 885 | 884 | 885 |  | 885 | 886 | 884 | 884 | 886 | 897 | 897 | 21717090
147 | Bheramara 410 MW CCPP | 265 | 265 | 270 | 275 | 285 | 290 | 285 | 255 | 240 | 220 | 200 | 190 | 175 | 165 | 150 | 150 | 150 | 155 |  | 155 | 160 | 160 | 160 | 160 | 160 | 160 | 5153472
148 | Payra 1320 MW | 620 | 620 | 620 | 620 | 620 | 620 | 620 | 622 | 622 | 622 | 622 | 622 | 622 | 622 | 622 | 570 | 570 | 540 |  | 550 | 600 | 600 | 610 | 622 | 622 | 610 | 15672400
149
150 | Barapukuria TPP Unit-1 | 71 | 75 | 74 | 74 | 74 | 71 | 71 | 71 | 74 | 80 | 79 | 79 | 80 | 80 | 81 | 83 | 84 | 85 |  | 80 | 79 | 80 | 80 | 80 | 80 | 80 | 1846691
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 |  | 250 | 250 | 250 | 250 | 250 | 250 | 251 | 6095000
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 32 | 32 | 32 | 32 | 32 | 32 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 617312
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 1 | 3 | 1 | 5 | 6 | 4 | 5 | 4 | 4 | 2 | 1 | 0 | [8 empty] | 33420
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 183 | 183 | 184 | 187 | 189 | 191 | 199 | 184 | 170 | 175 | 184 | 179 | 177 | 171 | 167 | 163 | 161 | 161 |  | 161 | 161 | 161 | 160 | 160 | 160 | 160 | 4400582
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
| Sirajgonj 225 MW CCPP Unit-2 (Oil) | 215 | 218 | 218 | 218 | 219 | 219 | 130 | 168 | 171 | 209 | 212 | 215 | 177 | 135 | 149 | 194 | 140 | 130 |  | 136 | 172 | 192 | 215 | 214 | 215 | 213 | 4805473
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 203 | 194 | 200 | 201 | 201 | 201 | 201 | 193 | 179 | 165 | 149 | 147 | 148 | 147 | 144 | 144 | 145 | 145 |  | 146 | 148 | 149 | 150 | 150 | 150 | 151 | 4251164
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 414 | 414 | 414 | 414 | 400 | 360 | 414 | 414 | 414 | 414 | 401 | 368 | 335 | 315 | 290 | 290 | 288 | 294 |  | 287 | 312 | 317 | 321 | 322 | 320 | 320 | 8636290
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | 39 | 33 | 33 | 33 | 23 | 0 | [7 empty] | 5 | 5 | 34 | 37 | 37 |  | 40 | 40 | 40 | 40 | 37 | 37 | 37 | 469985
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 20 | 18 | 17 | 16 | 16 | 17 | 19 | 19 |  | 21 | 21 | 22 | 22 | 22 | 22 | 22 | 468240
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 226386
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | 42 | 42 | 42 | 42 | 42 | 42 | 8 | 8 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 |  | 50 | 50 | 50 | 50 | 42 | 42 | 42 | 895568
167 | Katakhali 50 MW Peaking PP | [19 empty] | 18 | 32 | 32 | 32 | 32 | 24 | 24 | 135126
168 | Santahar 50 MW Peaking PP | 31 | 31 | 31 | 31 | 31 | 34 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 32 | 32 | 32 | 32 | 32 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 762000
169 | Natore 52 MW PP (Rajlanka) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 194770
170 | Chapainawabganj 100 MW Peaking PP | 60 | 46 | 45 | 45 | 45 | 45 | 45 | 39 | 39 | 39 | 39 | 38 | 37 | 37 | 37 | 37 | 37 | 37 |  | 68 | 78 | 78 | 78 | 78 | 78 | 78 | 1179216
171 | Baghabari 200 MW PP (Paramount) | 174 | 100 | 0 | [5 empty] | 8 | 52 | 114 | 170 | 169 | 168 | 168 | 168 | 120 | 120 |  | 111 | 154 | 162 | 168 | 168 | 168 | 168 | 2621519
| Bagura 113 MW PP (Confidence)-2 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 56 | 88 | 94 |  | 94 | 94 | 94 | 94 | 94 | 94 | 50 | 1666272
172 | Confidence Power Bogura Unit-1 113 MW | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 75 | 75 | 75 | 75 | 95 | 95 |  | 95 | 95 | 95 | 95 | 95 | 95 | 55 | 1706112
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 56 | 55 | 55 | 55 | 56 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 54 | 54 | 54 | 56 | 77 | 84 |  | 90 | 90 | 91 | 91 | 91 | 91 | 56 | 1569456
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1 | 2 | 2 | 5 | 3 | 4 | 4 | 3 | 6 | 5 | 3 | 2 | [8 empty] | 38680
178 | Energypac Power Venture Thakurgaon Ltd. | 52 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 47 | 54 |  | 52 | 52 | 52 | 52 | 34 | 34 | 0 | 823104
178