## Forecast
8 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2022-08-20 | Saturday
|  |  | Date (day): | 2022-08-20 |  | Saturday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11322.6 | MW |  |  | (b) At Evening Peak Hour : |  | 13826 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2022-08-19 | 2022-08-20 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 200 | 200 | 200 | 200 |  | 165
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 86 | 91 | 86 | 86 |  | 22 | Engine problem
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 407 | 410 | 412 | 412
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 283 | 282 | 260 | 260 | 100 |  | Gas shortage
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 400 | 450 | 250 | 400 |  |  | Gas shortage
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 7 | 7 | 7 | 7 | 93 |  | Fuel shortage
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 0 | 0 | 0 | 0 |  | 102 | Under maint
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 30 | 30 | 30 | 30 |  | 25 | Engine problem
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 18 | 22 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 8 | 16 | 8 | 16 | 84 |  | Fuel shortage
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 74 | 180 | 180 | 180 | 155 |  | Gas shortage
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 8 | 16 | 8 | 16 | 86 |  | Fuel shortage
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 54 | 17 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 16 | 115 | 16 | 126 |  | 23 | Engine problem
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 55 | 0 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 35 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 51 | 52 | 52 | 52 |  | 28 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 31 | 32 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 24 | 40 | 24 | 40 |  | 12 | Engine problem
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 112 | 260 | 110 | 285 |  | 15 | Engine problem
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 157 | 0 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 60 | 0 | 70 | 93 |  |  | Engine problem
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 80 | 0 | 0 | 70 |  |  | Fuel shortage
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 16 | 132 | 35 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 88 | 52 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 0 | 17 | 17 | 17 | 87 |  | Fuel shortage
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 45 | 162 | 35 | 162
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 24 | 0 | 30 | 0
| 40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 55 | 55 | 55
|  | Dhaka area Total |  |  |  |  | 6263 | 5847 | 2454 | 3034 | 2357 | 3493 | 1201 | 1072
| 41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 110 | 110 | 110 | 70 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 22 | 25 | 16 | 25
| 43 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 6 | 0 | 20 | 0
| 44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 6 | 38 | 6 | 37 |  | 13 | Engine problem
| 45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 152 | 144 | 145 | 145 |  | 85 | Low Water Level
| 46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | S/D due to HGPI
| 47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
| 48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 17 | 87 | 17 | 105
| 49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 26 | 26 | 25 | 25 | 73 |  | Fuel shortage
| 50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 17 | 51 | 17 | 51 | 51 |  | Fuel shortage
| 51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 10 | 10 | 10 | 10 | 90 |  | Fuel shortage
| 52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 10 | 10 | 10 | 10 |  | 90 | Fuel shortage
| 53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 13 | 13 | 13 | 13 |  | 9 | Engine problem
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 32 | 42 | 10 | 25
| 54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 12 | 94 | 12 | 93 |  |  | Fuel shortage
| 55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 3 | 0 | 5 | 0
| 56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 124 | 213 | 123 | 215 | 85 |  | Fuel shortage
| 57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 54 | 54 | 36 | 54 |  | 0 | Engine problem
| 58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 55 | 55 | 55 | 55 |  | 55 | Fuel shortage
| 59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 10 | 10 | 10 | 10 |  |  | Fuel shortage
| 60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 90 | 90 | 90 | 90 |  | 26 | Engine problem
|  | Mirsharai 150 MW |  | Gas/HSD | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 759 | 1072 | 730 | 1073 | 549 | 653
| 61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 207 | 207 | 210 | 210 |  |  | Gas shortage
| 63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 315 | 325 | 320 | 320 | 40 |  | Gas shortage
| 64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 305 | 320 | 305 | 305 | 55 |  | Gas shortage
|  | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+136*1 | 284 | 284 | 0 | 0 | 0 | 0 |  |  | On test.
| 65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 38 | 34 | 35 | 35 |  | 10 | Engine problem
| 66 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 55 | 56 | 55 | 55 | 55
| 67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 16 | 55 | 55 | 55 | 140 |  | Gas shortage
| 68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 127 | 100 | 132 | 140 |  | 10 | Engine problem
| 70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 38 | 44 | 44 | 45 |  | 7 | Engine problem
| 71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 144 | 143 | 145 | 145 |  | 18 | Machine problem
| 72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 185 | 200 | 200 | 200
| 73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 21 | 21 | 21
| 74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 8 | 8 | 8
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 98 | 164 | 143 | 165
| 75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 30 | 33 | 33 | 33
| 76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 | 52 |  | Fuel shortage
| 77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 14 | 12 | 12 | 12 |  | 13 | Engine problem
| 78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 100 | 0 | 100 | 200
| 79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 88 | 17 | 114 | 114
| 80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 28 | 9 | 26 | 87 |  | Fuel shortage
| 81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 35 | 35 | 35 | 35 |  | 19 | 33 kV feeder fault
| 82 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 38 | 97 | 96 | 96 | 19 |  | Fuel shortage
|  | Cumilla Area Total |  |  |  |  | 3193 | 3169 | 1850 | 2020 | 2026 | 2271 | 641 | 77
| 83 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 140 | 150 | 140 | 140 | 62 |  | Gas shortage
| 84 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 22 | 22 | 22
| 85 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0 |  | 8 | Under maint.
| 86 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1 | 0 | 1.6 | 0
| 87 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 76 | 180 | 80 | 180 |  | 20 | Engine problem
| 88 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 69 | 78 | 68 | 79 |  | 36 | Engine problem
| 89 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 56 | 0 | 50 | 0
| 90 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 12 | 12 |  | 10 | Engine problem
|  | Mymensingh Area Total |  |  |  |  | 717 | 614 | 374 | 442 | 373.6 | 433 | 62 | 74
| 91 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 43 | 43 | 43 |  | 27 | Machine problem.
| 92 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 |  | 60 | Machine problem
| 93 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 | 163 |  | Gas shortage
| 94 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
| 95 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 0 | 5 | 5 | 5 | 46 |  | Gas shortage
| 96 | Fenchuganj 44MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 0 | 5 | 5 | 5 | 45 |  | Gas shortage
| 97 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0
| 98 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 59 | 58 | 62 | 62
| 99 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 50 | 81 | 10 | 80
| 100 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
| 101 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 208 | 208 | 210 | 210 |  |  | Gas shortage
| 102 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Gas shortage
| 103 | Sylhet 50MW PP (EPL) |  | Gas | NENP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Gas shortage
| 104 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 0 | 8 | 8 | 8 | 17 |  | Gas shortage
| 105 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 290 | 290 | 300 |  |  | FGMO
| 106 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 402 | 403 | 400 | 400
| 107 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| 108 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 386 | 400 | 400 | 400
|  | Sylhet Area Total |  |  |  |  | 2522 | 2477 | 1488 | 1541 | 1473 | 1553 | 341 | 517
| 109 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 906 | 907 | 924 | 924
| 110 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 16 | 16 | 16 | 16 | 99 |  | Fuel shortage
| 111 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 44 | 20 | 43 |  | 11 | Engine problem
| 112 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 120 | 210 | 225 | 225
| 113 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 30 | 68 | 40 | 50 |  | 59 | Engine problem
| 114 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 155 | 175 | 175 | 175 | 235 |  | Gas shortage
| 115 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 0 | 0 | 0 | 40 |  | Fuel shortage
| 116 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 50 | 95 |  | 5 | Engine problem
| 117 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 17 | 35 | 17 | 35 | 70 |  | Fuel shortage
| 118 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 32 | 15 | 100 |  |  | Fuel shortage
| 119 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 54 | 0 | 100 | 0
|  | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
|  | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
|  | Khulna Area Total |  |  |  |  | 2388 | 2384 | 1298 | 1487 | 1582 | 1663 | 460 | 75
| 120 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 16 | 16 | 35 |  |  | Line O/L
| 121 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 12 | 24 | 15 | 25 |  | 15 | Engine problem
| 122 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 152 | 150 | 151 | 151 |  |  | Machine problem
|  | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
| 123 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 890 | 1060 | 1110 | 1110
| 124 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 0 | 0 | 0 | 0 |  | 220 | Machine problem
| 125 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 0 | 17 |  |  | Line O/L
|  | Barisal Area Total |  |  |  |  | 1958 | 1958 | 1054 | 1250 | 1292 | 1338 | 0 | 235
| 126 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 127 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 32 | 32 | 0 | 32 |  | 20 | Engine problem
| 128 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 40 | 0 | 40 |  | 31 | Engine problem
| 129 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 130 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Fuel shortage
| 131 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 32 | 0 | 32 |  | 18 | Engine problem
| 132 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 170 | 186 | 180 | 180 | 30 |  | Gas shortage
| 133 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 181 | 159 | 130 | 220
| 134 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 146 | 158 | 150 | 150 | 70 |  | Gas shortage
| 135 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 298 | 358 | 350 | 350 | 64 |  | Gas shortage
| 136 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 31 | 0 | 32 |  | 18 | Engine problem
| 137 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 19 | 20 | 21 | 21
| 138 | Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 139 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 140 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 8 | 8 | 8 | 44 |  | Fuel shortage
| 141 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 80 | 35 | 80 |  | 24 | Engine problem
| 142 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 20 | 0 | 100 | 170 |  | 30 | Fuel shortage
| 143 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 50 | 94 | 50 | 94 |  | 19 | Engine problem
| 144 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 55 | 95 | 55 | 95 |  | 18 | Engine problem
| 145 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 3 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2129 | 985 | 1304 | 1096 | 1515 | 379 | 178
| 146 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 82 | 80 | 80 | 80
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
| 147 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 250 | 251 | 250 | 250 | 24
| 148 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
| 149 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
| 150 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 56 | 91 | 55 | 90 |  |  | Engine problem
| 151 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 8 | 0 | 8 | 0
| 152 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 0 | 72 | 0 | 67 |  | 48 | Fuel shortage
|  | Rangpur Area Total |  |  |  |  | 800 | 720 | 396 | 494 | 393 | 487 | 64 | 133
|  | Total |  |  |  |  | 22482 | 21680 | 10658 | 12644 | 11322.6 | 13826 | 3697 | 3014
| A. |  | 2022-08-19 | (Yesterday) |  |  |  |  | Friday
| 1 | Highest Generation : |  |  | 12948 | MW at | 23:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 10433 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 12759 | MW
| 3 | Day peak Generation : |  |  | 10658 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 12208.96 | MW
| 4 | Evening peak Generation : |  |  | 12644 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 106 | MW
| 5 | Total Energy Generation : |  | 272.6296 | MKWHr | By Solar | 0.88036 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
|  | By Gas : | 138.5147 | MKWHr |  | By Oil: | 71.6492 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 33.2293 | MKWHr |  | By Hydro: | 3.4402 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 3697 | MW | Dhaka | 4318.97 | 4318.97 |  | 0 |  | 18:00 |  | 338.218
|  |  |  | For Plants S/D or M/C prob = |  |  | 3014 | MW | Chittagong | 1247.9 | 1247.9 |  | 0 |  | 19:00 |  | 176.0208
|  |  |  | Total = |  |  | 6711 | MW | Khulna | 1291.2 | 1291.2 |  | 0 |  | 19:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1081.82 | MMCFD |  |  | Rajshahi | 1358.1 | 1358.1 |  | 0 |  | 20:00 |  | 49.765
| 8 | Fuel Cost : | i) Gas : | Taka | 157359522.73 | ii) Oil : | Taka | 1059252133.63 | Comilla | 1188 | 1188 |  | 0 |  | 21:00 |  | 105.9811
|  |  | iii) Coal : |  | 271063617.29 | Total | Taka | 1487675273.65 | Mymensingh | 1147 | 1041 |  | 106 |  | 22:00 |  | 148
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0 | MKWHr. | Sylhet | 486 | 486 |  | 0 |  | 23:00 |  | 241
|  | ii) During Peak Demand : |  |  | 530 | MW (E to W) at | 21:00 | hrs | Barisal | 254.79 | 254.79 |  | 0 |  | 24:00 |  | 773
|  | iii) Maximum : |  |  | 410 | MW at | 19:00 | hrs | Rangpur | 917 | 917 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 34.0° C |  |  | Total | 12208.96 | 12102.96 |  | 106
| B. |  | 2022-08-20 | (Today) |  |  |  | Saturday |  |  | Probable max. temperature in Dhaka |  |  | 35.0° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 14000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 160 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 13826 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 11800 | MW
| 4 | Reserve(Generation end) |  |  |  | - | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 294.7803 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 10502 | MW at | 8:00 | 0 | 40 | 0 | 0 | 40 | 80 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.936 | MKWHr. | ii) HVDC Flow at Peak Time |  | 907 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.9798 | MKWHr. | iii) Maximum HVDC Flow : |  | 908 | MW at | 3:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 95.69 |  | (b) Today: | 95.55 |  | (c) Rule Curve: |  | 95.08
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2022-08-19
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 300 | 87 | 0 | 405 | 253 |  | 0 | 380 | 0 | 8 | 0 | 30 | 76 | 0 | 37 | 8 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 9 | 33 | 33 | 24 | 0 | 81 | 70 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 17 | 10 | 12 | 6 | 12 | 35 | 0 | 0 | 0 | 325 | 320 | 207 | 16 | 143 | 39 | 56 | 0 | 51 | 0 | 46 | 0 | 22 | 10 | 33 | 14 | 122 | 106 | 0 | 22 | 0 | 43 | 30 | 5 | 5 | 0 | 0 | 62 | 81 | 0 | 207 | 0 | 0 | 10 | 300 | 8 | 0 | 194 | 110 | 252 | 70 | 48 | 70 | 17 | 0 | 10 | 155 | 145 | 402 | 49 | 50 | 17 | 0 | 52 | 36 | 55 | 17 | 9 | 10 | 398 | 0 | 0 | 54 | 107 | 0 | 35 | 0 | 85 | 55 | 0 | 0 | 0 |  | 907 | 0 | 175 | 0 | 0 | 225 | 0 | 0 | 20 | 65 | 0 | 145 | 25 | 32 | 0 | 0 | 0 | 30 | 35 | 51 | 0 | 0 | 0 | 0 | 30 | 22 | 0 | 11 | 80 | 0 | 235 | 0 | 0 | 169 | 0 | 0 | 218 | 0 | 93 | 155 | 0 | 343 | 0 | 164 | 50 | 15 | 56 | 0 | 0 | 55 | 1150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 7120 | 4556 | 11676 | 4256 | 907 | 1669 | 843 | 1484 | 1465 | 151 | 443 | 554 | 122 | 0 | 1035.8503 | 95.71
2:00 | 0 | 0 | 0 | 180 | 300 | 87 | 0 | 405 | 253 |  | 0 | 380 | 0 | 7 | 0 | 30 | 76 | 0 | 37 | 8 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 28 | 33 | 33 | 24 | 0 | 81 | 70 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 17 | 10 | 12 | 6 | 12 | 35 | 0 | 0 | 0 | 335 | 330 | 207 | 16 | 143 | 39 | 55 | 0 | 51 | 0 | 38 | 0 | 22 | 10 | 33 | 14 | 118 | 106 | 0 | 22 | 0 | 43 | 30 | 5 | 5 | 0 | 0 | 62 | 81 | 0 | 207 | 0 | 0 | 10 | 310 | 8 | 0 | 195 | 111 | 304 | 70 | 48 | 70 | 17 | 0 | 10 | 159 | 145 | 402 | 49 | 50 | 17 | 0 | 52 | 36 | 55 | 17 | 9 | 10 | 396 | 0 | 0 | 54 | 107 | 0 | 35 | 0 | 55 | 55 | 0 | 0 | 0 |  | 907 | 0 | 175 | 0 | 0 | 225 | 0 | 0 | 20 | 65 | 0 | 147 | 24 | 32 | 0 | 0 | 0 | 30 | 36 | 44 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 79 | 0 | 235 | 0 | 0 | 170 | 0 | 0 | 217 | 0 | 93 | 155 | 0 | 349 | 0 | 164 | 50 | 0 | 55 | 0 | 0 | 55 | 1150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 7203 | 4510 | 11713 | 4318 | 907 | 1683 | 896 | 1442 | 1464 | 151 | 442 | 509 | 118 | 0 | 817.437 | 95.71
3:00 | 0 | 0 | 0 | 180 | 300 | 87 | 0 | 405 | 253 |  | 0 | 380 | 0 | 8 | 0 | 30 | 75 | 0 | 37 | 8 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 28 | 33 | 33 | 24 | 0 | 81 | 70 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 17 | 10 | 12 | 6 | 0 | 36 | 0 | 0 | 0 | 310 | 305 | 207 | 16 | 143 | 39 | 56 | 0 | 51 | 0 | 44 | 0 | 22 | 10 | 33 | 14 | 116 | 105 | 0 | 22 | 0 | 43 | 30 | 5 | 5 | 0 | 0 | 64 | 81 | 0 | 207 | 0 | 0 | 10 | 310 | 8 | 0 | 195 | 111 | 300 | 70 | 48 | 70 | 17 | 0 | 10 | 170 | 145 | 402 | 49 | 50 | 17 | 0 | 52 | 36 | 55 | 17 | 9 | 10 | 395 | 0 | 0 | 54 | 107 | 0 | 35 | 0 | 56 | 55 | 0 | 0 | 0 |  | 908 | 0 | 175 | 0 | 0 | 225 | 0 | 0 | 20 | 65 | 0 | 149 | 22 | 32 | 0 | 0 | 0 | 30 | 36 | 44 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 79 | 0 | 235 | 0 | 0 | 170 | 0 | 0 | 217 | 0 | 93 | 155 | 0 | 349 | 0 | 164 | 50 | 0 | 55 | 0 | 0 | 55 | 1130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 7155 | 4491 | 11646 | 4257 | 908 | 1683 | 892 | 1455 | 1444 | 151 | 442 | 515 | 116 | 0 | 694.8675 | 95.7
4:00 | 0 | 0 | 0 | 180 | 300 | 87 | 0 | 404 | 249 |  | 0 | 380 | 0 | 8 | 0 | 30 | 75 | 0 | 36 | 8 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 28 | 33 | 33 | 24 | 0 | 81 | 70 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 17 | 10 | 12 | 6 | 9 | 36 | 0 | 0 | 0 | 310 | 305 | 208 | 16 | 143 | 37 | 56 | 0 | 51 | 0 | 44 | 0 | 22 | 10 | 33 | 14 | 116 | 107 | 0 | 22 | 0 | 43 | 30 | 5 | 5 | 0 | 0 | 64 | 81 | 0 | 207 | 0 | 0 | 10 | 300 | 8 | 0 | 195 | 110 | 302 | 70 | 48 | 70 | 17 | 0 | 10 | 170 | 145 | 402 | 49 | 50 | 17 | 0 | 52 | 36 | 55 | 17 | 9 | 10 | 400 | 15 | 0 | 54 | 107 | 0 | 35 | 0 | 57 | 55 | 0 | 0 | 0 |  | 907 | 0 | 180 | 0 | 0 | 226 | 0 | 0 | 20 | 65 | 0 | 150 | 22 | 32 | 0 | 0 | 0 | 30 | 36 | 44 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 79 | 0 | 235 | 0 | 0 | 171 | 0 | 0 | 217 | 0 | 93 | 156 | 0 | 355 | 0 | 170 | 50 | 0 | 55 | 0 | 0 | 55 | 1130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 7171 | 4511 | 11682 | 4278 | 907 | 1675 | 900 | 1470 | 1444 | 151 | 443 | 515 | 116 | 0 | 477.3759 | 95.7
5:00 | 0 | 0 | 0 | 180 | 300 | 87 | 0 | 403 | 253 |  | 0 | 380 | 0 | 8 | 0 | 30 | 75 | 0 | 37 | 8 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 28 | 33 | 33 | 24 | 0 | 81 | 70 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 17 | 10 | 12 | 6 | 9 | 36 | 0 | 0 | 0 | 310 | 305 | 207 | 16 | 143 | 37 | 56 | 0 | 51 | 0 | 44 | 0 | 22 | 10 | 33 | 14 | 114 | 106 | 0 | 22 | 0 | 43 | 30 | 5 | 5 | 0 | 0 | 64 | 81 | 0 | 207 | 0 | 0 | 10 | 290 | 8 | 0 | 195 | 110 | 240 | 70 | 48 | 70 | 17 | 0 | 10 | 136 | 138 | 402 | 49 | 50 | 17 | 0 | 52 | 36 | 55 | 17 | 9 | 10 | 400 | 17 | 0 | 54 | 107 | 0 | 35 | 0 | 56 | 45 | 0 | 0 | 0 |  | 908 | 0 | 180 | 0 | 0 | 225 | 0 | 0 | 19 | 55 | 0 | 150 | 14 | 16 | 0 | 0 | 0 | 30 | 36 | 44 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 80 | 0 | 234 | 0 | 0 | 171 | 0 | 0 | 218 | 0 | 93 | 157 | 0 | 354 | 0 | 176 | 50 | 0 | 55 | 0 | 0 | 55 | 1090 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 7049 | 4443 | 11492 | 4277 | 908 | 1660 | 844 | 1404 | 1404 | 151 | 443 | 505 | 114 | 0 | 376.0026 | 95.69
6:00 | 0 | 0 | 0 | 180 | 300 | 87 | 0 | 403 | 253 |  | 0 | 380 | 0 | 8 | 0 | 30 | 76 | 0 | 37 | 8 | 24 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 24 | 33 | 33 | 24 | 0 | 80 | 70 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 17 | 10 | 12 | 6 | 9 | 38 | 0 | 0 | 0 | 310 | 305 | 209 | 16 | 143 | 37 | 55 | 0 | 51 | 0 | 44 | 0 | 22 | 10 | 33 | 14 | 102 | 107 | 0 | 22 | 0 | 43 | 30 | 5 | 5 | 0 | 0 | 64 | 81 | 0 | 207 | 0 | 0 | 10 | 270 | 8 | 0 | 152 | 110 | 53 | 70 | 48 | 70 | 17 | 1 | 10 | 136 | 140 | 402 | 49 | 50 | 17 | 0 | 52 | 36 | 55 | 17 | 9 | 10 | 400 | 0 | 2 | 54 | 107 | 0 | 35 | 1 | 56 | 55 | 0 | 0 | 0 |  | 908 | 0 | 180 | 0 | 0 | 228 | 0 | 0 | 19 | 55 | 0 | 151 | 15 | 16 | 0 | 0 | 0 | 30 | 0 | 44 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 80 | 0 | 235 | 0 | 0 | 171 | 0 | 0 | 190 | 0 | 10 | 158 | 0 | 354 | 0 | 50 | 50 | 0 | 55 | 0 | 0 | 55 | 1040 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 |  | 6802 | 4129 | 10931 | 4279 | 908 | 1642 | 405 | 1415 | 1355 | 150 | 418 | 441 | 102 | 6 | 340.0612 | 95.69
7:00 | 0 | 0 | 0 | 180 | 300 | 87 | 0 | 403 | 253 |  | 0 | 380 | 0 | 7 | 0 | 55 | 76 | 0 | 37 | 8 | 24 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 17 | 22 | 25 | 24 | 33 | 33 | 24 | 0 | 81 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 17 | 10 | 12 | 6 | 9 | 40 | 0 | 0 | 0 | 310 | 305 | 209 | 16 | 143 | 37 | 55 | 0 | 51 | 0 | 38 | 0 | 22 | 10 | 33 | 11 | 98 | 117 | 0 | 22 | 0 | 43 | 30 | 5 | 5 | 0 | 0 | 64 | 81 | 0 | 207 | 0 | 0 | 10 | 270 | 8 | 0 | 152 | 110 | 10 | 25 | 48 | 25 | 17 | 4 | 10 | 136 | 137 | 402 | 49 | 50 | 17 | 0 | 52 | 36 | 55 | 17 | 9 | 10 | 400 | 0 | 6 | 35 | 107 | 0 | 35 | 3 | 56 | 55 | 0 | 0 | 0 |  | 907 | 0 | 175 | 0 | 0 | 225 | 0 | 0 | 19 | 54 | 0 | 146 | 13 | 0 | 0 | 0 | 0 | 30 | 0 | 44 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 79 | 0 | 235 | 0 | 0 | 170 | 0 | 0 | 170 | 0 | 10 | 157 | 0 | 354 | 0 | 10 | 50 | 0 | 55 | 0 | 0 | 55 | 970 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 |  | 6662 | 3972 | 10634 | 4274 | 907 | 1642 | 232 | 1418 | 1284 | 116 | 395 | 414 | 98 | 24 | 171.4129 | 95.69
8:00 | 0 | 0 | 0 | 180 | 300 | 86 | 0 | 403 | 268 |  | 0 | 380 | 0 | 7 | 0 | 55 | 72 | 0 | 0 | 8 | 24 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 35 | 22 | 25 | 26 | 33 | 33 | 24 | 0 | 81 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 17 | 10 | 11 | 6 | 9 | 25 | 0 | 0 | 0 | 315 | 305 | 211 | 16 | 145 | 37 | 56 | 0 | 51 | 0 | 38 | 0 | 22 | 10 | 33 | 11 | 90 | 156 | 0 | 22 | 1 | 43 | 30 | 5 | 5 | 0 | 0 | 62 | 10 | 0 | 207 | 0 | 0 | 10 | 270 | 0 | 0 | 10 | 110 | 10 | 25 | 75 | 25 | 16 | 6 | 10 | 136 | 132 | 403 | 69 | 52 | 17 | 1 | 120 | 36 | 55 | 17 | 9 | 10 | 394 | 17 | 31 | 35 | 107 | 0 | 35 | 6 | 53 | 55 | 0 | 0 | 0 |  | 907 | 0 | 175 | 0 | 0 | 185 | 0 | 0 | 19 | 54 | 0 | 152 | 10 | 0 | 0 | 0 | 0 | 30 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 81 | 0 | 250 | 0 | 0 | 170 | 0 | 0 | 130 | 0 | 10 | 156 | 0 | 341 | 0 | 10 | 50 | 0 | 56 | 0 | 1 | 55 | 900 | 0 | 0 | 0 | 2 | 11 | 0 | 0 | 0 | 0 |  | 6609 | 3824 | 10433 | 4273 | 907 | 1554 | 90 | 1561 | 1231 | 116 | 315 | 367 | 90 | 59 | #REF! | 0
9:00 | 0 | 0 | 0 | 180 | 300 | 86 | 0 | 405 | 274 |  | 0 | 390 | 0 | 8 | 0 | 55 | 77 | 0 | 0 | 8 | 24 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 35 | 18 | 25 | 26 | 33 | 31 | 24 | 0 | 81 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 17 | 10 | 11 | 6 | 13 | 40 | 0 | 0 | 0 | 315 | 305 | 206 | 16 | 144 | 37 | 56 | 0 | 51 | 0 | 38 | 0 | 22 | 5 | 32 | 11 | 90 | 155 | 0 | 20 | 1 | 43 | 30 | 5 | 5 | 0 | 0 | 60 | 10 | 0 | 207 | 0 | 0 | 10 | 290 | 0 | 0 | 10 | 112 | 10 | 25 | 77 | 25 | 16 | 4 | 10 | 136 | 128 | 404 | 69 | 52 | 17 | 3 | 122 | 36 | 44 | 17 | 9 | 10 | 400 | 17 | 43 | 35 | 107 | 0 | 35 | 20 | 56 | 55 | 0 | 0 | 0 |  | 907 | 0 | 170 | 0 | 0 | 180 | 0 | 0 | 13 | 57 | 0 | 152 | 9 | 0 | 0 | 0 | 0 | 30 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 81 | 0 | 250 | 0 | 0 | 170 | 0 | 0 | 130 | 0 | 0 | 153 | 0 | 328 | 17 | 0 | 50 | 0 | 56 | 0 | 1 | 55 | 860 | 0 | 0 | 0 | 3 | 35 | 0 | 0 | 0 | 0 |  | 6676 | 3776 | 10452 | 4260 | 907 | 1591 | 70 | 1573 | 1191 | 116 | 310 | 364 | 90 | 110 | #REF! | 0
10:00 | 0 | 0 | 0 | 180 | 300 | 86 | 0 | 408 | 273 |  | 0 | 400 | 0 | 8 | 0 | 30 | 77 | 0 | 0 | 8 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 35 | 0 | 25 | 27 | 33 | 31 | 24 | 0 | 82 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 17 | 10 | 11 | 6 | 13 | 32 | 0 | 0 | 0 | 325 | 320 | 204 | 16 | 143 | 30 | 54 | 0 | 51 | 0 | 38 | 0 | 22 | 5 | 30 | 11 | 84 | 152 | 0 | 20 | 1 | 43 | 30 | 5 | 5 | 0 | 0 | 59 | 10 | 0 | 209 | 0 | 0 | 10 | 300 | 0 | 0 | 10 | 112 | 12 | 25 | 77 | 25 | 16 | 0 | 10 | 136 | 123 | 405 | 69 | 52 | 17 | 3 | 123 | 36 | 51 | 17 | 9 | 10 | 388 | 0 | 54 | 35 | 105 | 0 | 35 | 14 | 56 | 55 | 0 | 0 | 0 |  | 907 | 0 | 160 | 0 | 0 | 180 | 0 | 0 | 0 | 30 | 0 | 152 | 11 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 80 | 0 | 250 | 0 | 0 | 170 | 0 | 0 | 130 | 0 | 0 | 150 | 0 | 317 | 17 | 0 | 50 | 0 | 56 | 0 | 7 | 55 | 800 | 0 | 0 | 0 | 2 | 91 | 0 | 0 | 0 | 0 |  | 6612 | 3677 | 10289 | 4233 | 907 | 1591 | 72 | 1516 | 1130 | 117 | 310 | 287 | 84 | 172 | #REF! | 0
11:00 | 0 | 0 | 0 | 180 | 196 | 86 | 0 | 407 | 274 |  | 0 | 400 | 0 | 9 | 0 | 30 | 76 | 0 | 0 | 8 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 35 | 0 | 25 | 20 | 33 | 31 | 24 | 0 | 82 | 35 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 17 | 10 | 12 | 6 | 13 | 8 | 0 | 0 | 0 | 335 | 330 | 205 | 16 | 143 | 36 | 54 | 0 | 51 | 0 | 38 | 0 | 22 | 5 | 30 | 11 | 94 | 153 | 0 | 20 | 1 | 43 | 30 | 5 | 5 | 0 | 0 | 57 | 10 | 0 | 208 | 0 | 0 | 10 | 300 | 0 | 0 | 40 | 110 | 110 | 60 | 77 | 80 | 16 | 9 | 10 | 140 | 120 | 402 | 69 | 52 | 17 | 2 | 124 | 40 | 55 | 17 | 9 | 10 | 380 | 0 | 6 | 35 | 90 | 0 | 35 | 25 | 48 | 35 | 0 | 0 | 0 |  | 907 | 0 | 155 | 0 | 0 | 155 | 0 | 0 | 0 | 30 | 0 | 145 | 13 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 11 | 82 | 0 | 250 | 0 | 0 | 170 | 0 | 0 | 130 | 0 | 0 | 148 | 0 | 312 | 17 | 2 | 50 | 0 | 56 | 0 | 6 | 55 | 800 | 0 | 0 | 0 | 5 | 30 | 0 | 0 | 0 | 0 |  | 6656 | 3580 | 10236 | 4120 | 907 | 1563 | 292 | 1483 | 1132 | 117 | 285 | 289 | 94 | 84 | #REF! | 0
12:00 | 0 | 0 | 0 | 180 | 200 | 86 | 0 | 407 | 283 |  | 0 | 400 | 0 | 7 | 0 | 30 | 74 | 0 | 0 | 8 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 35 | 18 | 25 | 26 | 33 | 31 | 24 | 0 | 82 | 70 | 100 | 0 | 22 | 0 | 0 | 0 | 0 |  | 12 | 26 | 17 | 10 | 12 | 6 | 13 | 32 | 0 | 0 | 0 | 315 | 305 | 207 | 16 | 144 | 38 | 56 | 0 | 51 | 0 | 38 | 0 | 22 | 5 | 30 | 14 | 98 | 140 | 0 | 20 | 1 | 43 | 30 | 0 | 0 | 0 | 0 | 59 | 50 | 0 | 208 | 0 | 0 | 10 | 300 | 0 | 0 | 100 | 112 | 157 | 60 | 76 | 80 | 16 | 6 | 10 | 185 | 127 | 402 | 69 | 52 | 17 | 3 | 124 | 54 | 55 | 17 | 9 | 10 | 386 | 0 | 56 | 45 | 90 | 0 | 35 | 24 | 38 | 0 | 0 | 0 | 0 |  | 906 | 0 | 155 | 0 | 16 | 120 | 0 | 0 | 0 | 30 | 0 | 152 | 12 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 11 | 82 | 0 | 250 | 0 | 0 | 170 | 0 | 0 | 181 | 0 | 0 | 146 | 0 | 298 | 17 | 20 | 50 | 0 | 56 | 0 | 8 | 55 | 890 | 0 | 0 | 0 | 3 | 54 | 0 | 0 | 0 | 0 |  | 6925 | 3733 | 10658 | 4109 | 906 | 1613 | 417 | 1526 | 1222 | 152 | 301 | 340 | 98 | 155 | #REF! | 0
13:00 | 0 | 0 | 0 | 180 | 200 | 90 | 0 | 403 | 283 |  | 0 | 400 | 0 | 7 | 0 | 30 | 75 | 0 | 0 | 8 | 8 | 29 | 0 | 0 | 0 | 0 | 17 | 0 | 35 | 18 | 25 | 18 | 33 | 31 | 24 | 0 | 82 | 70 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 17 | 10 | 11 | 1 | 13 | 42 | 0 | 0 | 0 | 315 | 305 | 209 | 16 | 143 | 35 | 55 | 0 | 51 | 0 | 37 | 0 | 22 | 5 | 30 | 14 | 144 | 122 | 0 | 20 | 2 | 43 | 30 | 0 | 0 | 0 | 0 | 61 | 50 | 0 | 208 | 0 | 0 | 10 | 290 | 0 | 0 | 160 | 112 | 293 | 45 | 76 | 80 | 16 | 2 | 10 | 185 | 127 | 404 | 69 | 52 | 17 | 2 | 124 | 54 | 49 | 17 | 9 | 10 | 360 | 0 | 54 | 102 | 90 | 0 | 35 | 36 | 56 | 0 | 0 | 0 | 0 |  | 908 | 0 | 150 | 0 | 16 | 120 | 0 | 0 | 0 | 25 | 0 | 132 | 11 | 16 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 11 | 79 | 0 | 250 | 0 | 0 | 171 | 0 | 0 | 210 | 0 | 0 | 145 | 0 | 297 | 17 | 36 | 50 | 0 | 55 | 0 | 8 | 55 | 910 | 0 | 0 | 0 | 2 | 4 | 0 | 0 | 0 | 0 |  | 7186 | 3728 | 10914 | 4031 | 908 | 1614 | 614 | 1607 | 1239 | 152 | 330 | 375 | 144 | 110 | 211.9623 | 0
14:00 | 0 | 0 | 0 | 180 | 200 | 87 | 0 | 411 | 283 |  | 0 | 400 | 0 | 8 | 0 | 30 | 76 | 0 | 0 | 8 | 8 | 29 | 0 | 0 | 0 | 0 | 17 | 0 | 35 | 18 | 25 | 18 | 33 | 31 | 24 | 0 | 84 | 70 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 17 | 10 | 12 | 6 | 13 | 40 | 0 | 0 | 0 | 305 | 305 | 201 | 16 | 143 | 34 | 54 | 0 | 51 | 0 | 37 | 0 | 22 | 5 | 33 | 14 | 126 | 132 | 0 | 22 | 1 | 43 | 30 | 0 | 0 | 0 | 0 | 59 | 10 | 0 | 208 | 0 | 0 | 10 | 260 | 0 | 0 | 10 | 112 | 23 | 0 | 77 | 25 | 17 | 4 | 10 | 200 | 127 | 401 | 69 | 52 | 17 | 3 | 124 | 54 | 55 | 17 | 9 | 10 | 378 | 17 | 43 | 108 | 90 | 0 | 35 | 25 | 66 | 0 | 0 | 0 | 0 |  | 908 | 0 | 145 | 0 | 16 | 120 | 0 | 0 | 0 | 28 | 0 | 148 | 9 | 16 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 11 | 79 | 0 | 250 | 0 | 0 | 170 | 0 | 0 | 150 | 0 | 0 | 144 | 0 | 296 | 17 | 10 | 50 | 0 | 55 | 0 | 6 | 55 | 910 | 0 | 0 | 0 | 6 | 13 | 0 | 0 | 0 | 0 |  | 6635 | 3661 | 10296 | 4058 | 908 | 1534 | 68 | 1670 | 1239 | 154 | 270 | 318 | 126 | 101 | 372.3163 | 95.65
15:00 | 0 | 0 | 0 | 180 | 200 | 87 | 0 | 400 | 292 |  | 0 | 410 | 0 | 8 | 0 | 30 | 76 | 0 | 0 | 8 | 8 | 29 | 0 | 0 | 0 | 0 | 17 | 0 | 35 | 18 | 25 | 18 | 33 | 28 | 24 | 0 | 77 | 70 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 17 | 10 | 12 | 6 | 13 | 34 | 0 | 0 | 0 | 310 | 305 | 205 | 16 | 143 | 31 | 51 | 0 | 51 | 0 | 36 | 0 | 21 | 5 | 33 | 14 | 142 | 151 | 0 | 22 | 2 | 43 | 30 | 0 | 0 | 0 | 0 | 58 | 10 | 0 | 208 | 0 | 0 | 8 | 300 | 0 | 0 | 100 | 115 | 250 | 0 | 77 | 50 | 16 | 3 | 10 | 175 | 127 | 390 | 69 | 52 | 17 | 1 | 124 | 54 | 55 | 17 | 9 | 10 | 378 | 17 | 44 | 108 | 90 | 0 | 35 | 29 | 56 | 0 | 0 | 0 | 0 |  | 908 | 0 | 150 | 0 | 16 | 120 | 0 | 0 | 0 | 28 | 0 | 150 | 9 | 16 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 11 | 78 | 0 | 251 | 0 | 0 | 170 | 0 | 0 | 130 | 0 | 0 | 145 | 0 | 293 | 17 | 25 | 50 | 0 | 55 | 0 | 6 | 55 | 930 | 0 | 0 | 0 | 4 | 1 | 0 | 0 | 0 | 0 |  | 7001 | 3666 | 10667 | 4064 | 908 | 1579 | 425 | 1637 | 1259 | 147 | 250 | 296 | 142 | 90 | 214.727 | 95.64
16:00 | 0 | 0 | 0 | 180 | 200 | 87 | 0 | 404 | 307 |  | 0 | 410 | 0 | 8 | 0 | 30 | 75 | 0 | 0 | 8 | 8 | 30 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 18 | 25 | 18 | 33 | 21 | 24 | 0 | 76 | 65 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 17 | 10 | 12 | 6 | 13 | 37 | 0 | 0 | 0 | 310 | 305 | 204 | 16 | 145 | 31 | 50 | 0 | 51 | 0 | 42 | 0 | 21 | 5 | 33 | 14 | 120 | 150 | 0 | 22 | 1 | 42 | 30 | 0 | 0 | 0 | 0 | 60 | 10 | 0 | 208 | 0 | 0 | 9 | 280 | 0 | 0 | 0 | 112 | 10 | 0 | 76 | 50 | 16 | 1 | 10 | 175 | 122 | 400 | 69 | 52 | 17 | 1 | 124 | 54 | 55 | 17 | 8 | 10 | 386 | 17 | 30 | 136 | 90 | 0 | 35 | 21 | 56 | 0 | 0 | 0 | 0 |  | 907 | 0 | 150 | 0 | 16 | 120 | 0 | 0 | 0 | 28 | 0 | 152 | 7 | 16 | 0 | 0 | 0 | 30 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 11 | 81 | 0 | 250 | 0 | 0 | 170 | 0 | 0 | 130 | 0 | 0 | 145 | 0 | 302 | 17 | 2 | 50 | 0 | 52 | 0 | 4 | 55 | 880 | 0 | 0 | 0 | 3 | 14 | 0 | 0 | 0 | 0 |  | 6681 | 3617 | 10298 | 4081 | 907 | 1586 | 62 | 1687 | 1211 | 141 | 250 | 308 | 120 | 75 | 278.3157 | 95.64
17:00 | 0 | 0 | 0 | 180 | 200 | 87 | 0 | 407 | 314 |  | 0 | 430 | 0 | 7 | 0 | 30 | 40 | 0 | 0 | 8 | 8 | 45 | 0 | 0 | 0 | 0 | 17 | 47 | 55 | 18 | 25 | 18 | 33 | 22 | 24 | 0 | 77 | 65 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 17 | 10 | 11 | 6 | 13 | 42 | 0 | 0 | 0 | 280 | 270 | 204 | 16 | 146 | 34 | 51 | 0 | 51 | 0 | 44 | 0 | 21 | 8 | 33 | 14 | 128 | 152 | 0 | 22 | 0 | 42 | 30 | 0 | 0 | 0 | 0 | 61 | 10 | 0 | 208 | 0 | 0 | 8 | 280 | 0 | 0 | 0 | 130 | 0 | 0 | 76 | 0 | 38 | 1 | 10 | 175 | 100 | 328 | 75 | 72 | 17 | 0 | 124 | 54 | 55 | 17 | 9 | 10 | 320 | 0 | 15 | 162 | 90 | 0 | 35 | 4 | 48 | 0 | 0 | 0 | 0 |  | 907 | 0 | 155 | 0 | 16 | 120 | 0 | 0 | 0 | 28 | 0 | 152 | 7 | 16 | 0 | 0 | 0 | 32 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 11 | 82 | 0 | 250 | 0 | 0 | 170 | 0 | 0 | 130 | 0 | 0 | 147 | 0 | 309 | 17 | 0 | 50 | 0 | 87 | 0 | 3 | 50 | 800 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 |  | 6507 | 3565 | 10072 | 3874 | 907 | 1625 | 0 | 1793 | 1132 | 142 | 250 | 327 | 128 | 24 | 202.7465 | 95.63
18:00 | 0 | 0 | 0 | 180 | 200 | 52 | 0 | 396 | 253 |  | 0 | 350 | 0 | 8 | 0 | 30 | 40 | 0 | 0 | 9 | 8 | 50 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 18 | 33 | 22 | 24 | 0 | 75 | 65 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 17 | 10 | 22 | 6 | 13 | 42 | 0 | 0 | 0 | 280 | 270 | 205 | 16 | 142 | 35 | 52 | 0 | 51 | 0 | 44 | 0 | 21 | 8 | 33 | 14 | 126 | 153 | 0 | 22 | 0 | 43 | 30 | 0 | 0 | 0 | 0 | 61 | 10 | 0 | 208 | 0 | 0 | 10 | 265 | 8 | 0 | 0 | 150 | 0 | 0 | 170 | 0 | 147 | 0 | 10 | 175 | 100 | 328 | 78 | 72 | 17 | 0 | 124 | 54 | 55 | 17 | 14 | 10 | 290 | 0 | 5 | 162 | 90 | 0 | 35 | 2 | 17 | 0 | 0 | 0 | 0 |  | 908 | 0 | 160 | 0 | 16 | 120 | 0 | 0 | 9 | 37 | 0 | 151 | 10 | 16 | 0 | 0 | 0 | 32 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 11 | 82 | 0 | 251 | 0 | 0 | 140 | 0 | 0 | 130 | 0 | 0 | 130 | 0 | 235 | 35 | 0 | 50 | 15 | 85 | 0 | 2 | 50 | 770 | 0 | 0 | 0 | 0 | 1 | 72 | 0 | 0 | 0 |  | 6533 | 3550 | 10083 | 3799 | 908 | 1366 | 0 | 2154 | 1103 | 140 | 250 | 357 | 126 | 10 | 338.218 | 95.63
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 200 | 90 | 0 | 397 | 322 |  | 0 | 450 | 0 | 8 | 0 | 30 | 78 | 0 | 0 | 16 | 16 | 122 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 18 | 33 | 31 | 34 | 0 | 80 | 65 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 51 | 10 | 79 | 17 | 13 | 42 | 0 | 0 | 0 | 280 | 265 | 209 | 16 | 143 | 35 | 52 | 0 | 51 | 0 | 44 | 0 | 21 | 8 | 33 | 14 | 156 | 155 | 0 | 22 | 0 | 43 | 30 | 5 | 0 | 0 | 0 | 64 | 81 | 0 | 208 | 0 | 0 | 10 | 270 | 8 | 0 | 30 | 215 | 44 | 91 | 180 | 92 | 149 | 0 | 10 | 175 | 117 | 402 | 78 | 88 | 44 | 0 | 210 | 54 | 55 | 56 | 27 | 10 | 360 | 17 | 0 | 162 | 90 | 0 | 35 | 0 | 63 | 0 | 0 | 0 | 0 |  | 907 | 0 | 170 | 0 | 16 | 160 | 0 | 0 | 43 | 57 | 0 | 141 | 18 | 16 | 0 | 0 | 0 | 32 | 37 | 68 | 0 | 0 | 20 | 8 | 31 | 20 | 0 | 11 | 80 | 0 | 251 | 0 | 0 | 149 | 0 | 0 | 144 | 0 | 4 | 144 | 0 | 358 | 35 | 9 | 75 | 32 | 91 | 0 | 0 | 80 | 790 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 0 |  | 7840 | 4069 | 11909 | 4019 | 907 | 1785 | 270 | 2671 | 1121 | 145 | 304 | 675 | 156 | 0 | 176.0208 | 95.61
19:30 | 0 | 0 | 0 | 180 | 200 | 90 | 0 | 404 | 322 |  | 0 | 450 | 0 | 8 | 0 | 30 | 130 | 0 | 0 | 16 | 16 | 122 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 27 | 33 | 31 | 40 | 0 | 80 | 65 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 51 | 10 | 87 | 37 | 13 | 42 | 0 | 0 | 0 | 295 | 275 | 206 | 16 | 142 | 31 | 52 | 0 | 51 | 0 | 44 | 0 | 21 | 8 | 33 | 14 | 156 | 154 | 0 | 22 | 0 | 43 | 30 | 5 | 5 | 0 | 0 | 62 | 81 | 0 | 208 | 0 | 0 | 10 | 310 | 8 | 0 | 20 | 255 | 20 | 25 | 180 | 25 | 149 | 0 | 10 | 175 | 134 | 403 | 78 | 88 | 89 | 0 | 210 | 54 | 55 | 88 | 29 | 10 | 398 | 17 | 0 | 162 | 90 | 0 | 35 | 0 | 97 | 10 | 0 | 0 | 0 |  | 908 | 0 | 175 | 0 | 16 | 194 | 0 | 0 | 51 | 63 | 0 | 150 | 19 | 16 | 0 | 0 | 0 | 32 | 37 | 80 | 0 | 0 | 32 | 8 | 31 | 20 | 0 | 11 | 79 | 0 | 251 | 0 | 0 | 170 | 0 | 0 | 212 | 0 | 10 | 158 | 0 | 351 | 35 | 20 | 94 | 32 | 91 | 0 | 0 | 95 | 870 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 0 |  | 8053 | 4383 | 12436 | 4189 | 908 | 1824 | 120 | 2919 | 1200 | 145 | 406 | 781 | 156 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 180 | 200 | 91 | 0 | 410 | 311 |  | 0 | 450 | 0 | 8 | 0 | 30 | 201 | 0 | 0 | 16 | 16 | 105 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 27 | 33 | 32 | 40 | 0 | 80 | 65 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 51 | 10 | 93 | 36 | 13 | 42 | 0 | 0 | 0 | 310 | 305 | 210 | 16 | 143 | 32 | 54 | 0 | 51 | 0 | 44 | 0 | 22 | 8 | 33 | 12 | 162 | 158 | 0 | 22 | 0 | 43 | 30 | 5 | 5 | 0 | 0 | 61 | 81 | 0 | 208 | 0 | 0 | 10 | 260 | 8 | 0 | 0 | 258 | 0 | 0 | 180 | 0 | 149 | 0 | 10 | 175 | 100 | 402 | 78 | 88 | 87 | 0 | 213 | 54 | 55 | 88 | 28 | 10 | 400 | 17 | 0 | 162 | 90 | 0 | 35 | 0 | 96 | 25 | 0 | 0 | 0 |  | 908 | 0 | 175 | 0 | 16 | 227 | 0 | 0 | 41 | 75 | 0 | 144 | 19 | 16 | 0 | 0 | 0 | 32 | 40 | 80 | 0 | 0 | 32 | 8 | 31 | 20 | 0 | 11 | 80 | 0 | 250 | 0 | 0 | 174 | 0 | 0 | 213 | 0 | 0 | 158 | 0 | 355 | 35 | 0 | 94 | 32 | 91 | 0 | 0 | 95 | 910 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 0 |  | 8014 | 4434 | 12448 | 4319 | 908 | 1770 | 0 | 2907 | 1240 | 145 | 440 | 770 | 162 | 0 | 49.765 | 95.62
21:00 | 0 | 0 | 0 | 180 | 200 | 91 | 0 | 410 | 282 |  | 0 | 450 | 0 | 7 | 0 | 30 | 180 | 0 | 0 | 16 | 16 | 115 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 27 | 33 | 32 | 40 | 0 | 79 | 65 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 51 | 10 | 94 | 38 | 13 | 42 | 0 | 0 | 0 | 325 | 320 | 207 | 55 | 143 | 34 | 55 | 0 | 51 | 0 | 44 | 0 | 21 | 8 | 33 | 12 | 164 | 150 | 0 | 22 | 0 | 43 | 30 | 5 | 5 | 0 | 0 | 58 | 81 | 0 | 208 | 0 | 0 | 10 | 290 | 8 | 0 | 0 | 260 | 0 | 0 | 180 | 0 | 132 | 0 | 10 | 200 | 100 | 403 | 78 | 88 | 87 | 0 | 213 | 54 | 55 | 88 | 28 | 10 | 400 | 17 | 0 | 162 | 90 | 0 | 35 | 0 | 97 | 55 | 0 | 0 | 0 |  | 907 | 0 | 175 | 0 | 16 | 210 | 0 | 0 | 44 | 68 | 0 | 150 | 24 | 16 | 0 | 0 | 0 | 32 | 40 | 80 | 0 | 0 | 32 | 8 | 31 | 20 | 0 | 11 | 80 | 0 | 251 | 0 | 0 | 186 | 0 | 0 | 159 | 0 | 0 | 158 | 0 | 358 | 35 | 0 | 94 | 32 | 91 | 0 | 0 | 95 | 1060 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 0 |  | 8109 | 4535 | 12644 | 4337 | 907 | 1819 | 0 | 2950 | 1391 | 144 | 369 | 722 | 164 | 0 | 105.9811 | 95.61
22:00 | 0 | 0 | 0 | 180 | 200 | 91 | 0 | 410 | 297 |  | 0 | 450 | 0 | 8 | 0 | 30 | 181 | 0 | 0 | 16 | 16 | 121 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 27 | 33 | 33 | 41 | 0 | 80 | 65 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 51 | 10 | 94 | 12 | 13 | 42 | 0 | 0 | 0 | 350 | 340 | 206 | 55 | 143 | 37 | 56 | 0 | 51 | 0 | 45 | 0 | 21 | 8 | 33 | 12 | 168 | 156 | 0 | 22 | 0 | 43 | 30 | 5 | 5 | 0 | 0 | 60 | 81 | 0 | 208 | 0 | 0 | 10 | 300 | 8 | 0 | 0 | 258 | 0 | 0 | 180 | 0 | 132 | 0 | 10 | 175 | 100 | 403 | 78 | 88 | 105 | 0 | 214 | 54 | 55 | 88 | 29 | 10 | 394 | 17 | 0 | 162 | 90 | 0 | 35 | 0 | 98 | 55 | 0 | 0 | 0 |  | 907 | 0 | 180 | 0 | 16 | 225 | 0 | 0 | 44 | 68 | 0 | 147 | 25 | 16 | 0 | 0 | 0 | 32 | 37 | 80 | 0 | 0 | 32 | 8 | 32 | 20 | 0 | 11 | 80 | 0 | 250 | 0 | 0 | 183 | 0 | 0 | 213 | 0 | 0 | 158 | 0 | 363 | 35 | 0 | 94 | 32 | 92 | 0 | 0 | 95 | 1100 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 0 |  | 8168 | 4647 | 12815 | 4387 | 907 | 1851 | 0 | 2921 | 1430 | 145 | 438 | 781 | 168 | 0 | 148 | 95.61
23:00 | 0 | 0 | 0 | 180 | 200 | 91 | 0 | 408 | 310 |  | 0 | 450 | 0 | 7 | 0 | 30 | 179 | 0 | 0 | 16 | 16 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 27 | 33 | 33 | 41 | 0 | 80 | 65 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 51 | 10 | 61 | 6 | 13 | 42 | 0 | 0 | 0 | 345 | 340 | 206 | 55 | 144 | 37 | 56 | 0 | 51 | 0 | 45 | 0 | 21 | 8 | 33 | 12 | 172 | 156 | 0 | 22 | 0 | 43 | 30 | 5 | 5 | 0 | 0 | 60 | 81 | 0 | 208 | 0 | 0 | 10 | 320 | 8 | 0 | 80 | 258 | 207 | 70 | 180 | 92 | 132 | 0 | 10 | 136 | 100 | 402 | 78 | 88 | 78 | 0 | 52 | 54 | 55 | 88 | 29 | 10 | 395 | 17 | 0 | 162 | 90 | 0 | 35 | 0 | 96 | 55 | 0 | 0 | 0 |  | 908 | 0 | 185 | 0 | 16 | 225 | 0 | 0 | 44 | 68 | 0 | 147 | 28 | 16 | 0 | 0 | 0 | 32 | 37 | 80 | 0 | 0 | 32 | 8 | 32 | 21 | 0 | 11 | 80 | 0 | 250 | 0 | 0 | 183 | 0 | 0 | 213 | 0 | 0 | 157 | 0 | 362 | 35 | 22 | 94 | 32 | 92 | 0 | 0 | 95 | 1100 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 0 |  | 8271 | 4677 | 12948 | 4383 | 908 | 1887 | 471 | 2651 | 1430 | 145 | 438 | 676 | 172 | 0 | 241 | 95.6
24:00 | 0 | 0 | 0 | 180 | 200 | 88 | 0 | 408 | 311 |  | 0 | 450 | 0 | 8 | 0 | 30 | 178 | 0 | 0 | 8 | 8 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 0 | 33 | 33 | 24 | 0 | 80 | 65 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 51 | 10 | 12 | 6 | 13 | 42 | 0 | 0 | 0 | 310 | 310 | 208 | 55 | 143 | 37 | 55 | 0 | 51 | 0 | 45 | 0 | 21 | 8 | 25 | 14 | 168 | 159 | 0 | 22 | 0 | 43 | 30 | 5 | 5 | 0 | 0 | 64 | 81 | 0 | 208 | 0 | 0 | 10 | 300 | 8 | 0 | 150 | 150 | 303 | 70 | 48 | 70 | 41 | 0 | 20 | 136 | 100 | 402 | 49 | 52 | 17 | 0 | 52 | 40 | 55 | 17 | 29 | 10 | 397 | 0 | 0 | 162 | 90 | 0 | 35 | 0 | 97 | 48 | 0 | 0 | 0 |  | 908 | 0 | 180 | 0 | 16 | 226 | 0 | 0 | 33 | 68 | 0 | 152 | 28 | 16 | 0 | 0 | 0 | 31 | 37 | 80 | 0 | 0 | 32 | 0 | 26 | 21 | 0 | 11 | 80 | 0 | 250 | 0 | 0 | 183 | 0 | 0 | 214 | 0 | 36 | 157 | 0 | 362 | 17 | 60 | 50 | 15 | 56 | 0 | 0 | 55 | 1120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 7641 | 4520 | 12161 | 4272 | 908 | 1864 | 689 | 1780 | 1450 | 145 | 440 | 659 | 168 | 0 | 773 | 95.6
KWH | 0 | 0 | 0 | 4347000 | 5888118 | 2025045 | 0 | 9828350 | 6634000 |  | 0 | 8575750 | 0 | 198720 | 0 | 818813 | 2284110 | 0 | 316000 | 236160 | 287280 | 873120 | 0 | 0 | 0 | 0 | 661320 | 457246 | 780678 | 392112 | 600000 | 521100 | 803300 | 740600 | 657120 | 0 | 1960233 | 1480000 | 2400000 | 0 | 588949 | 0 | 0 | 0 | 0 |  | 298080 | 605328 | 610523 | 259200 | 657600 | 2275200 | 265056 | 912480 | 0 | 0 | 0 | 7970900 | 7557000 | 4992000 | 568727 | 1534080 | 846072 | 1307520 | 0 | 1210040 | 0 | 1006280 | 0 | 507636 | 167220 | 784100 | 329540 | 2979840 | 3180480 | 0 | 492588 | 14300 | 1019000 | 682872 | 91200 | 104112 | 0 | 0 | 1466496 | 1270080 | 0 | 4823580 | 0 | 0 | 237600 | 7129000 | 108552 | 0 | 1958400 | 3495162 | 2794706 | 856142 | 2200800 | 1067694 | 1211184 | 41040 | 256320 | 4008960 | 3046036 | 9476000 | 1548000 | 1491600 | 738508 | 22439 | 2604436 | 1139512 | 1316431 | 784320 | 344400 | 263040 | 9142200 | 202560 | 340130 | 2340000 | 2317145 | 0 | 889200 | 176873 | 1534080 | 856440 | 0 | 0 | 0 |  | 21936000 | 0 | 4168512 | 0 | 192960 | 4472177 | 0 | 0 | 406080 | 1201024 | 0 | 3560890 | 385906 | 381696 | 0 | 0 | 0 | 752080 | 403875 | 794552 | 0 | 0 | 146328 | 36000 | 199846 | 471600 | 0 | 256320 | 1906909 | 0 | 5975900 | 0 | 0 | 4341436 | 0 | 0 | 4457755 | 0 | 612480 | 3897291 | 0 | 7901127 | 389280 | 1309933 | 1589184 | 218160 | 1560940 | 0 | 47859 | 1575744 | 25346500 | 0 | 0 | 0 | 31080 | 206640 | 412416 | 0 | 0 | 0 |  | 171083164 | 101546480 | 272629644 | 99690511 | 21936000 | 38824187 | 8599355 | 47120880 | 33229309 | 3440233 | 8929932 | 6999036 | 2979840 | 880361 | 0
Fuel Cost | 0 | 0 | 0 | 6477030 | 6594692.16 | 2693309.85 | 0 | 10319767.5 | 7164720 |  | 0 | 9347567.5 | 0 | 2221689.6 | 0 | 10849272.25 | 2558203.2 | 0 | 553000 | 3452659.2 | 4042029.6 | 14153275.2 | 0 | 0 | 0 | 0 | 8411990.4 | 6172821 | 10468891.98 | 294084 | 450000 | 0 | 0 | 0 | 11177611.2 | 0 | 529262.91 | 399600 | 4536000 | 0 | 9629316.15 | 0 | 0 | 0 | 0 |  | 3889944 | 10096871.04 | 10391101.46 | 3501792 | 8338368 | 26324064 | 336621.12 | 3038558.4 | 0 | 0 | 0 | 8847699 | 8237130 | 5790720 | 733657.83 | 1871577.6 | 956061.36 | 1948204.8 | 0 | 2020766.8 | 0 | 17378455.6 | 0 | 695461.32 | 125415 | 1372175 | 247155 | 21395251.2 | 3466723.2 | 0 | 669919.68 | 227942 | 1396030 | 901391.04 | 158688 | 180113.76 | 0 | 0 | 2845002.24 | 2895782.4 | 0 | 4871815.8 | 0 | 0 | 470448 | 7129000 | 81414 | 0 | 41048064 | 47708961.3 | 58577037.76 | 17696455.14 | 29666784 | 22069234.98 | 16774898.4 | 479757.6 | 2645222.4 | 54762393.6 | 40420897.72 | 8717920 | 18823680 | 21568536 | 9342126.2 | 0 | 30576078.64 | 12409285.68 | 13993661.53 | 10643222.4 | 4439316 | 3098611.2 | 8410824 | 2623152 | 4914878.5 | 29694600 | 26369110.1 | 0 | 11612952 | 2113632.35 | 22965177.6 | 11279314.8 | 0 | 0 | 0 |  | 65808000 | 0 | 4668733.44 | 0 | 2008713.6 | 73790920.5 | 0 | 0 | 7313500.8 | 21618432 | 0 | 3988196.8 | 748657.64 | 4160486.4 | 0 | 0 | 0 | 12612381.6 | 7063773.75 | 12426793.28 | 0 | 0 | 2474406.48 | 490680 | 3371402.02 | 976212 | 0 | 194034.24 | 11079141.29 | 0 | 31612511 | 0 | 0 | 5036065.76 | 0 | 0 | 77832402.3 | 0 | 12849830.4 | 4520857.56 | 0 | 7822115.73 | 5231923.2 | 27469295.01 | 18800046.72 | 3152412 | 19823938 | 0 | 528841.95 | 19129532.16 | 228371965 | 0 | 0 | 0 | 351514.8 | 2423887.2 | 6322337.28 | 0 | 0 | 0 |  | 880773900.25 | 706073941.91 | 1586847842.16 | 110031720.02 | 65808000 | 47327802.71 | 179709917.29 | 609018500.31 | 271063617.29 | 928862.91 | 151623322.8 | 118900393.23 | 21395251.2 | 11040454.4 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 200 | 86 | 0 | 407 | 283 |  | 0 | 400 | 0 | 7 | 0 | 30 | 74 | 0 | 0 | 8 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 35 | 18 | 25 | 26 | 33 | 31 | 24 | 0 | 82 | 70 | 100 | 0 | 22 | 0 | 0 | 0 | 0 |  | 12 | 26 | 17 | 10 | 12 | 6 | 13 | 32 | 0 | 0 | 0 | 315 | 305 | 207 | 16 | 144 | 38 | 56 | 0 | 51 | 0 | 38 | 0 | 22 | 5 | 30 | 14 | 98 | 140 | 0 | 20 | 1 | 43 | 30 | 0 | 0 | 0 | 0 | 59 | 50 | 0 | 208 | 0 | 0 | 10 | 300 | 0 | 0 | 100 | 112 | 157 | 60 | 76 | 80 | 16 | 6 | 10 | 185 | 127 | 402 | 69 | 52 | 17 | 3 | 124 | 54 | 55 | 17 | 9 | 10 | 386 | 0 | 56 | 45 | 90 | 0 | 35 | 24 | 38 | 0 | 0 | 0 | 0 |  | 906 | 0 | 155 | 0 | 16 | 120 | 0 | 0 | 0 | 30 | 0 | 152 | 12 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 11 | 82 | 0 | 250 | 0 | 0 | 170 | 0 | 0 | 181 | 0 | 0 | 146 | 0 | 298 | 17 | 20 | 50 | 0 | 56 | 0 | 8 | 55 | 890 | 0 | 0 | 0 | 3 | 54 | 0 | 0 | 0 | 0 |  | 10658 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 200 | 91 | 0 | 410 | 282 | 0 | 0 | 450 | 0 | 7 | 0 | 30 | 180 | 0 | 0 | 16 | 16 | 115 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 27 | 33 | 32 | 40 | 0 | 79 | 65 | 110 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 12 | 26 | 51 | 10 | 94 | 38 | 13 | 42 | 0 | 0 | 0 | 325 | 320 | 207 | 55 | 143 | 34 | 55 | 0 | 51 | 0 | 44 | 0 | 21 | 8 | 33 | 12 | 164 | 150 | 0 | 22 | 0 | 43 | 30 | 5 | 5 | 0 | 0 | 58 | 81 | 0 | 208 | 0 | 0 | 10 | 290 | 8 | 0 | 0 | 260 | 0 | 0 | 180 | 0 | 132 | 0 | 10 | 200 | 100 | 403 | 78 | 88 | 87 | 0 | 213 | 54 | 55 | 88 | 28 | 10 | 400 | 17 | 0 | 162 | 90 | 0 | 35 | 0 | 97 | 55 | 0 | 0 | 0 |  | 907 | 0 | 175 | 0 | 16 | 210 | 0 | 0 | 44 | 68 | 0 | 150 | 24 | 16 | 0 | 0 | 0 | 32 | 40 | 80 | 0 | 0 | 32 | 8 | 31 | 20 | 0 | 11 | 80 | 0 | 251 | 0 | 0 | 186 | 0 | 0 | 159 | 0 | 0 | 158 | 0 | 358 | 35 | 0 | 94 | 32 | 91 | 0 | 0 | 95 | 1060 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 0 |  | 12644 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 200 | 86 | 0 | 412 | 260 | 0 | 0 | 400 | 0 | 7 | 0 | 30 | 180 | 0 | 0 | 16 | 16 | 126 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 27 | 33 | 33 | 40 | 0 | 80 | 65 | 110 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 12 | 25 | 51 | 10 | 93 | 37 | 13 | 25 | 0 | 0 | 0 | 320 | 305 | 210 | 55 | 145 | 35 | 55 | 0 | 51 | 0 | 45 | 0 | 21 | 8 | 33 | 12 | 165 | 140 | 0 | 22 | 0 | 43 | 30 | 5 | 5 | 0 | 0 | 62 | 80 | 0 | 210 | 0 | 0 | 10 | 300 | 8 | 0 | 200 | 285 | 300 | 93 | 180 | 70 | 149 | 0 | 10 | 200 | 140 | 400 | 79 | 105 | 105 | 0 | 215 | 54 | 55 | 114 | 26 | 10 | 400 | 17 | 0 | 162 | 90 | 0 | 35 |  | 96 | 55 |  |  |  |  | 924 | 0 | 175 | 0 | 16 | 225 | 0 | 0 | 43 | 50 | 0 | 151 | 25 | 35 | 0 | 0 | 0 | 32 | 40 | 80 | 0 | 0 | 32 | 8 | 32 | 21 | 0 | 11 | 80 | 0 | 250 | 0 | 0 | 180 | 0 | 0 | 220 | 0 | 95 | 150 | 0 | 350 | 35 | 170 | 94 | 100 | 90 | 0 | 0 | 95 | 1110 | 0 |  | 17 |  |  | 67
Forecast for Day | 0 | 0 | 0 | 180 | 200 | 86 | 0 | 412 | 260 | 0 | 0 | 250 | 0 | 7 | 0 | 30 | 180 | 0 | 0 | 8 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 35 | 22 | 25 | 27 | 33 | 33 | 24 | 0 | 80 | 65 | 110 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 12 | 25 | 17 | 10 | 12 | 6 | 13 | 10 | 0 | 0 | 0 | 320 | 305 | 210 | 55 | 145 | 35 | 55 | 0 | 51 | 0 | 44 | 0 | 21 | 8 | 33 | 12 | 143 | 140 | 0 | 22 | 1.6 | 43 | 30 | 5 | 5 | 0 | 0 | 62 | 10 | 0 | 210 | 0 | 0 | 10 | 290 | 8 | 0 | 100 | 110 | 100 | 70 | 80 | 0 | 35 | 20 | 10 | 200 | 132 | 400 | 68 | 52 | 17 | 5 | 123 | 36 | 55 | 17 | 9 | 10 | 400 | 17 | 50 | 35 | 90 | 0 | 35 | 30 | 96 | 55 |  |  |  |  | 924 | 0 | 175 | 0 | 16 | 225 | 0 | 0 | 20 | 40 | 0 | 151 | 15 | 16 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 8 | 0 | 21 | 0 | 11 | 80 | 0 | 250 | 0 | 0 | 180 | 0 | 0 | 130 | 0 | 50 | 150 | 0 | 350 | 17 | 100 | 50 | 15 | 55 | 0 | 8 | 55 | 1110 | 0 |  | 0 | 6 | 100 | 0
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 200 | 91 | 0 | 414 | 331 | 0 | 0 | 180 | 0 | 7 | 0 | 30 | 181 | 0 | 0 | 8 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 26 | 22 | 25 | 27 | 33 | 33 | 24 | 0 | 83 | 65 | 110 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 12 | 26 | 17 | 10 | 12 | 6 | 13 | 10 | 0 | 0 | 0 | 320 | 315 | 207 | 55 | 146 | 33 | 55 | 0 | 51 | 0 | 45 | 0 | 21 | 8 | 33 | 12 | 130 | 157 | 0 | 22 | 1 | 43 | 30 | 5 | 5 | 0 | 0 | 61 | 20 | 0 | 207 | 0 | 0 | 10 | 290 | 0 | 0 | 0 | 112 | 85 | 25 | 76 | 0 | 17 | 7 | 10 | 120 | 100 | 403 | 68 | 52 | 17 | 1 | 120 | 36 | 55 | 17 | 9 | 10 | 394 | 17 | 12 | 35 | 90 | 0 | 17 | 13 | 78 | 55 | 0 | 0 | 0 | 0 | 907 | 0 | 170 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 150 | 18 | 16 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 80 | 0 | 250 | 0 | 0 | 183 | 0 | 0 | 130 | 0 | 0 | 156 | 0 | 342 | 0 | 0 | 50 | 15 | 56 | 0 | 0 | 55 | 1030 | 0 | 0 | 0 | 2 | 58 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 71649203 |  | 0
71649203
| Minimum Generation |  | 10433 | 8:00
| Highest Generation |  | 12948 | 23:00
| Day Peak Generation |  | 10658 | 12:00
| Evening Peak Generation |  | 12644 | 21:00
| HVDC Max Flow |  | 908 | 3:00
| HVDC EvPeak Flow |  | 907 | 21:00
| Load factor L.F |  | 87.73% | [161 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2022-08-20
Till now the maximum generation is : - |  |  | 14782 | 21:00 | Hrs on | 2022-04-16
The Summary of Yesterday's |  | 2022-08-19 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 10658 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 10502 | MW
Evening Peak Generation : |  | 12644 | MW Hour : | 21:00 | Available Max Generation : |  | 13826 | MW
E.P. Demand (at gen end) : |  | 12759 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 14000 | MW
Maximum Generation : |  | 12948 | MW Hour : | 23:00 | Reserve(Generation end) |  | - | MW
Total Gen. (MKWH) : |  | 272.6296 | System Load Factor : | 87.73% | Load Shed : |  | 160 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | 410 | MW at | 19:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2022-08-20
Actual : | 95.55 | Ft.(MSL) , | Rule curve : | 95.08 | Ft.( MSL )
Gas Consumed : | Total = | 1081.82 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 157359522.73
: |  | Coal : | 271063617.29 | Oil : | 1059252133.63 | Total : | 1487675273.65
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4483.4624 |  |  | 0 | -0.6443%
Chittagong Area | 0 | 0:00 | 1269.5617 |  |  | 40 | 1.682%
Khulna Area | 0 | 0:00 | 1675.9763 |  |  | 0 | 2.105%
Rajshahi Area | 0 | 0:00 | 1487.6064 |  |  | 0 | 2.7%
Cumilla Area | 0 | 0:00 | 1265.6911 |  |  | 40 | 2.355%
Mymensingh Area | 106 | 2544:00 | 1046.3563 |  |  | 80 | 2.922%
Sylhet Area | 0 | 0:00 | 467.0542 |  |  | 0 | 1.703%
Barisal Area | 0 | 0:00 | 380.6105 |  |  | 0 | -0.1191%
Rangpur Area | 0 | 0:00 | 825.7312 |  |  | 0 | 2.864%
Total | 106 |  | 12902.05 |  |  | 160
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-2 |  | 10) Ghorasal-7 ST
2) Ghorasal-3,4
3) Ashuganj-5
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
7) Sikalbaha 225 MW
8) Shajibazar 330 MW
9) Siddhirganj 335 MW ST
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Barisal-Bhandaria 132 kV Ckt-1 tripped at 08:43 from Barisal end showing Dist.C-phase relay and was | [5 empty] | About 4 MW power interruption occurred under
switched on at 11:00. | [5 empty] | Barisal S/S area from 08:43 to 11:00.
b) Cox'sbazar 132/33 kV T-1 & T2 transformers tripped at 08:00showing E/F relays & 33 kV Kolatoli feeder | [5 empty] | About 12 MW power interruption occurred under
fault and were switched on at 08:14. | [5 empty] | Cox'sbazar S/S area from 08:00 to 08:14.
c) Madanganj-Sitalakha 132 kV Ckt was under shut down from 08:44 for C/M
d) Rangpur-Rangpur Confidence-1 P/P 132 kV Ckt was under shut down from 08:47 to 18:23 for D/W.
e) Rangpur-Rangpur Confidence-1 P/P 132 kV Ckt was under shut down from 08:48 to 18:24 for D/W.
f) GK 132/33 kV T-3 transformer was under shut down from 09:30 to 12:25 due to R/H maintenance at 33 kV | [5 empty] | About 18 MW power interruption occurred under
Bus coupler CT Y-phase. | [5 empty] | GK S/S area from 09:30 to 12:25.
g) Joydevpur 132/33 kV T-2 transformer tripped at 10:10 due to 33 kV Sreepur-2,3 & Rajendrapur feeder fault | [5 empty] | About 30 MW power interruption occurred under
and was switched on at 10:13. | [5 empty] | Rajendrapur S/S area from 10:10 to 10:13.
h) Lalbag-Kamrangirchar 132 kV Ckt was switched on at 10:09.
i) Ghorasal-Ashuganj 132 kV Ckt-1 tripped at 13:20 from both end showing Dist. Z1, C-phase relays and was
switched on at 13:39.
j) Noapara-Khulna© 132 kV Ckt-1 mid breaker was open at 11:42.
k) Ghorasal-7 CCPP DT was tripped at 10:58. showing relay protection alarm.
l) Bogura(N)-Sherpur 132 kV Ckt-1 tripped at 15:01 from Bogura end showing O/C, Dist. Z1 A-phase relays and
was switched on at 15:20.
m) Bagerhat 132/33 kV T-2 transformer was under shut down from 21:11 to 21:50 for C/M. | [5 empty] | About 10 MW power interruption occurred under
Bagerhat S/S area from 21:11 to 21:50.
n) Niamatpur 132/33 kV T-1 transformer was under shut down from 23:12 to 00:27(20-08-22) for C/M. | [5 empty] | About 36 MW power interruption occurred under
Niamatpur S/S area from 23:12 to 00:27(20-8-22)
o) Dhamrai 132/33 kV T1 & T2 transformers tripped at 05:38(20-08-2022) from 33 kV end showing O/C relay and | [5 empty] | About 76 MW power interruption occurred under
was switched on at 05:51(20-08-2022). | [5 empty] | Dhamrai S/S area from 05:38(20-8-22) to 05:51.
p) Maniknagar-Narinda 132 kV Ckt-1 was shut down at 07:06(20-08-2022) for C/M.
q) Rohanpur-Adani 400 kV Ckt-2 tripped at 06:10 showing Dist, Z1, SOTF, L2,L3 carrier at Rohanpur end.
r) Gallamari 132/33 kV T-2 transformer was shut down at 07:04(20-08-22) for C/M.
s) Natore 132/33 kV T-3 transformer was shut down at 07:52(20-08-22) for C/M. | [5 empty] | About 13 MW power interruption occurred under
Natore S/S area from 07:52(20-08-22) to till.
| Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2022-08-19 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4347000
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 200 | 5888118 | Machine problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 91 | 2025045 | Engine problem
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 410 | 9828350
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 282 | 6634000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 8575750
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 7 | 198720 | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 0 | 0 | Under maint.
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 30 | 818813 | Engine problem
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 392112
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 316000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 16 | 236160 | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 180 | 2284110 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 16 | 287280 | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 661320
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 115 | 873120 | Engine problem
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 457246
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 780678
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 52 | 1121100 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 803300
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 32 | 740600
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 40 | 657120 | #REF!
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 260 | 3495162 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 2794706 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 0 | 856142 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 1067694 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 132 | 1211184 | Engine problem
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 88 | 1491600 | Engine problem
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 17 | 202560 | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 2340000
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 176873
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 55 | 856440
| Dhaka area Total |  |  |  | 5847 | 3034 | 62418303
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 110 | 2400000 | Machine problem
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 25 | 588949
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 41040
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 38 | 2275200 | Engine problem
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 144 | 3440233 | Low water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | HGPI for 30 days.
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 87 | 738508 | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 26 | 605328 | Fuel shortage
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 610523 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 10 | 259200 | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 10 | 256320 | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 13 | 265056 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 42 | 912480
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 94 | 657600 | Engine problem
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 22439
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 213 | 2604436 | Fuel shortage
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1139512
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 55 | 1316431 | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 10 | 263040 | Engine problem
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 90 | 2317145 | Engine problem
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Chattogram area Total |  |  |  | 2382 | 1072 | 20713440
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 207 | 4992000 | #REF!
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 325 | 7970900 | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 320 | 7557000 | FGMO
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+136*1 | 284 | 0 | 0 | On test.
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 34 | 846072 | Engine problem
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 55 | 1307520
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 55 | 568727 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1210040
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 100 | 3046036 | Engine problem
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 44 | 1006280 | Engine problem
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 143 | 1534080 | Machine problem
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 200 | 4008960
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 507636
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 167220
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 164 | 2979840
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 784100
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 0 | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 12 | 329540 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 1958400 | Reserve.
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 88 | 784320 | Fuel shortage
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 28 | 344400 | Fuel shortage
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 35 | 889200 | 33 kV feeder problem.
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 97 | 1534080 | Engine problem
| Cumilla Area Total |  |  |  | 3169 | 2020 | 44326351
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 150 | 3180480 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 492588
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 14300
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 180 | 2200800 | Engine problem
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 78 | 1548000 | Engine problem
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 340130
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 298080 | Engine problem
| Mymensingh Area Total |  |  |  | 614 | 442 | 8074378
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1019000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 682872 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Gas shortage
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 5 | 91200 | Gas shortage
| Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 5 | 104112 | Gas shortage
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 0 | 0 | Engine problem
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 58 | 1466496
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1270080
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 208 | 4823580
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50MW PP (EPL) |  | NENP | 27*2 | 50 | 0 | 0 | Gas shortage
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 8 | 108552 | Gas shortage
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 7129000 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 403 | 9476000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 237600
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 400 | 9142200
| Sylhet Area Total |  |  |  | 2477 | 1541 | 35550692
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 907 | 21936000
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 16 | 192960 | Fuel shortage
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 44 | 406080 | Engine problem
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 210 | 4472177
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 68 | 1201024 | Engine problem
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 175 | 4168512 | Gas shortage.
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 0 | 0 | Fuel shortage
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 612480 | Reserve.
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 35 | 389280 | Fuel shortage
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 32 | 218160 | Fuel shortage
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 206640
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 0 | 0 | 0 | On test.
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 2384 | 1487 | 33803313
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 16 | 381696 | Line O/L
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 24 | 385906 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 150 | 3560890 | Gas shortage
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1060 | 25346500 | Line O/L
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 0 | 0 | Under maint.
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Line O/L
| Barisal Area Total |  |  |  | 1958 | 1250 | 29674992
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 32 | 752080 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 40 | 403875 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contract Expired
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Fuel shortage
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 146328 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 186 | 4341436 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 159 | 4457755
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 158 | 3897291 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 358 | 7901127 | Gas shortage
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 31 | 199846 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 20 | 471600
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | .
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 256320
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 8 | 36000 | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 80 | 794552 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 1309933 | Reserve.
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 94 | 1589184 | Engine problem
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 95 | 1575744 | Engine problem
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 31080
| Rajshahi Area Total |  |  |  | 2129 | 1304 | 28164151
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 80 | 1906909
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 251 | 5975900 | Machine problem
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 91 | 1560940 | Engine problem
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 47859
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 72 | 412416 | Fuel shortage
| Rangpur Area Total |  |  |  | 720 | 494 | 9904024
| Total |  |  |  | 21680 | 12644 | 272629644
| Eastern Grid Total |  |  |  | 14489 | 8109 | 171083164
| Western Grid Total |  |  |  | 7191 | 4535 | 101546480
| National Grid Total |  |  |  | 21680 | 12644 | 272629644
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2022-08-19
(a) ENTIRE EASTERN GRID : |  | 8281.87 | MW | (b) ENTIRE WESTERN GRID : |  | 3821.09 | MW
i) Dhaka area |  | 4318.97 | MW | i) Khulna area |  | 1291.2 | MW
ii) Chittagong area |  | 1247.9 | MW | ii) Rajshahi area |  | 1358.1 | MW
iii) Comilla area |  | 1188 | MW | iii) Barisal area |  | 254.79 | MW
iv) Mymensingh area |  | 1041 | MW | iv) Rangpur area |  | 917 | MW
v) Sylhet area |  | 486 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 12102.96 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
AKS | 0 | 00:00 | Chowmuhani | 198 | 22:00 | Kaptai | 5 | 19:00 | Nawabganj | 36.9 | 19:00 | Siddhirganj | 108 | 22:00
AKSML | 150 | 11:00 | Chuadanga | 96 | 19:00 | Kazla | 88 | 00:00 | Netrakona | 96 | 19:00 | Sirajganj | 88 | 07:00
Aftabnagar | 30 | 00:00 | Coxsbazar | 113 | 21:00 | Keranigonj | 48 | 00:00 | New | 81 | 09:00 | Sonargaon | 80 | 12:00
Agargaon | 80 | 00:00 | Cumilla(N) | 181 | 00:00 | Khagrachori | 30 | 19:30 | Niamatpur | 64 | 06:00 | Sreemongol | 44 | 12:00
Agrabad | 64 | 19:00 | Cumilla(S) | 172 | 23:00 | Khulna | 75 | 23:00 | Noapara | 47 | 01:00 | Srinagar | 46.28 | 21:00
Amnura | 54 | 21:00 | Daudkandi | 141 | 21:00 | Khulshi | 155 | 01:00 | PHP | 11 | 10:00 | Sunamganj | 38 | 22:00
Ashuganj | 39 | 23:00 | Dhaka | 20 | 00:00 | Kishoreganj | 154 | 19:30 | Pabna | 89 | 00:00 | Sylhet | 136 | 00:00
BSRM | 166 | 04:00 | Dhamrai | 96 | 00:00 | Kodda | 281 | 14:00 | Palashbari | 108 | 23:00 | TK | 28.5 | 19:00
Bagerhat | 85 | 22:00 | Dhanmondi | 113 | 19:00 | Kulaura | 38 | 05:00 | Panchagarh | 46 | 08:00 | Tangail | 195 | 22:00
Bakulia | 88 | 19:30 | Dohazari | 88 | 19:00 | Kurigram | 69 | 20:00 | Patuakhali | 133 | 22:00 | Thakurgaon | 66 | 22:00
Banani | 45 | 19:00 | Faridpur | 129 | 21:00 | Kushtia | 130 | 19:30 | Payra | 1.02 | 16:00 | Tongi | 116 | 19:30
Bangabhaban | 6 | 00:00 | Fatullah | 69 | 01:00 | Lalbag | 69 | 07:00 | Purbachal | 20 | 21:00 | Ullon | 40 | 21:00
Barapukuria | 56 | 23:00 | Fenchuganj | 44 | 05:00 | Lalmonirhat | 52 | 22:00 | Purbasadipur | 96 | 05:00 | Uttara | 93 | 21:00
Barguna | 16 | 01:00 | Feni | 105 | 23:00 | Madanganj | 81 | 09:00 | Rahim | 26 | 08:00 | UttaraNew | 18 | 00:00
Barishal | 105 | 00:00 | GPH | 89 | 04:00 | Madaripur | 95 | 23:00 | Rajbari | 60 | 19:30 | Zigatola | 57 | 19:00
Barishal-230 | 56 | 01:00 | Ghorashal | 64 | 22:00 | Madartek | 86 | 01:00 | Rajendrapur | 92 | 05:00
Baroaulia | 65 | 22:00 | Goalpara | 23 | 04:00 | Madunaghat | 55 | 19:00 | Rajshahi | 132 | 22:00
Baroirhat | 55 | 19:30 | Gollamari | 48 | 03:00 | Magura | 54 | 19:00 | Rajshahi-230 | 26 | 02:00
Bashundhara | 150 | 19:00 | Gopalganj | 85.6 | 23:00 | Mahasthangarh | 78 | 00:00 | Ramganj | 88 | 19:00
BashundharaCement | 12 | 00:00 | Gulshan | 132 | 08:00 | Manikganj | 96 | 01:00 | Rampur | 16 | 00:00
Beanibazar | 63 | 23:00 | Halishahar | 72 | 21:00 | Maniknagar | 64 | 00:00 | Rangamati | 14 | 19:00
Benapole | 46 | 07:00 | HaripurSBU | 146 | 00:00 | Matarbari | 35 | 07:00 | Rangpur | 105 | 08:00
Bhaluka | 140 | 20:00 | Hasnabad | 96 | 01:00 | Matuail | 62 | 00:00 | Ruppur | 5 | 09:00
Bhandaria | 38 | 01:00 | Hathazari | 84 | 22:00 | Millgate | 52 | 09:00 | SSM | 3 | 05:00
Bhangura | 30 | 19:30 | Ishurdi | 70 | 22:00 | Mirpur | 119 | 19:00 | Saidpur | 93 | 08:00
Bheramara(GK) | 61 | 20:00 | Jaldhaka | 70 | 19:30 | Mirsorai | N/A | N/A | Satkhira | 95 | 06:00
Bhulta | 228 | 04:00 | Jamalpur | 150 | 18:00 | Mithapukur | 34 | 00:00 | Satmasjid | 101 | 19:00
Bog-Sherpur | 64 | 19:00 | Jashore | 114 | 00:00 | Modern | 0 | 00:00 | Savar | 156 | 09:00
Bogura | 176 | 22:00 | Jhenaidah | 108 | 20:00 | Mogbazar | 113 | 15:00 | Shahjadpur | 85 | 22:00
Borhanuddin | 238 | 01:00 | Joydebpur | 161 | 22:00 | Mongla | 22 | 01:00 | Shahjibazar | 95 | 00:00
Brahmanbaria | 170 | 19:30 | Joypurhat | 68 | 00:00 | Motijheel | 28 | 01:00 | Shahmirpur | 46.5 | 18:30
Cantonment | 140 | 19:00 | Juldah | 28 | 12:00 | Munshiganj | 102 | 23:00 | Shariatpur | 78 | 22:00
Chandpur | 68 | 00:00 | KSRM | 29.2 | 13:00 | Mymensingh | 245 | 19:30 | Sherpur | 100 | 19:00
Chandraghona | 32 | 19:00 | Kabirpur | 243 | 00:00 | Naogaon | 128 | 03:00 | Shikalbaha | 28 | 19:00
Chapai | 68 | 21:00 | Kachua | 77 | 00:00 | Narail | 38 | 19:00 | Shikalbaha-230 | N/A | N/A
Charsaidpur | 37 | 04:00 | Kallyanpur | 96 | 00:00 | Narinda | 53 | 00:00 | Shitalakhya | 114 | 12:00
Chauddagram | 44 | 23:00 | Kalurghat | 23 | 00:00 | Narshingdi | 178 | 22:00 | Sholosohor | N/A | N/A
Chhatak | 35 | 20:00 | Kamrangirchar | 55 | 00:00 | Natore | 138 | 22:00 | Shyampur | 144 | 01:00
Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
(1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2022-08-19 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Bhulta | 386 | 13:00 | 375 | 10:00 | Kaliakoir | 388 | 17:00 | 337 | 11:00
| Bibiana | 406 | 19:00 | 393 | 12:00 | Payra | 420 | 18:30 | 409 | 01:00
| BIPTC | 400 | 17:00 | 392 | 00:00 | Rahanpur_I | 399 | 17:00 | 372 | 22:00
| Gopalganj_I | 413 | 18:00 | 391 | 02:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 223 | 19:00 | 213 | 10:00 | Hasnabad | 223 | 13:00 | 214 | 10:00
| AKSML | 228 | 19:30 | 223 | 13:00 | Hathazari | 230 | 19:30 | 215 | 23:00
| Aminbazar | 223 | 13:00 | 214 | 10:00 | Ishurdi | 236 | 17:00 | 226 | 22:00
| Ashuganj | 237 | 19:00 | 230 | 00:00 | Jhenaidah | 232 | 17:00 | 221 | 22:00
| Baghabari | 233 | 18:00 | 227 | 22:00 | Kaliakoir | 226 | 17:00 | 221 | 20:00
| Barapukuria | 222 | 18:30 | 209 | 22:00 | Keranigonj | 223 | 19:00 | 212 | 10:00
| Barishal | 248 | 09:00 | 236 | 00:00 | Khulna(S) | 242 | 18:30 | 232 | 22:00
| Bheramara | 232 | 13:00 | 222 | 22:00 | Maniknagar | 224 | 19:00 | 216 | 10:00
| Bhulta | 227 | 19:00 | 220 | 10:00 | Meghnaghat | 227 | 13:00 | 221 | 00:00
| Bibiana | 236 | 17:00 | 230 | 09:00 | Mirsorai | N/A | N/A | N/A | N/A
| BIPTC | 236 | 17:00 | 223 | 22:00 | Rajshahi | 234 | 18:30 | 221 | 23:00
| Bogura | 228 | 18:30 | 214 | 22:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 251 | 09:00 | 238 | 02:00 | Rampura | 225 | 19:00 | 219 | 00:00
| BSRM | 229 | 19:00 | 215 | 04:00 | Shikalbaha | 232 | 19:30 | 215 | 04:00
| Cumilla(N) | 226 | 13:00 | 219 | 09:00 | Shyampur | 226 | 19:30 | 214 | 10:00
| Fenchuganj | 240 | 19:00 | 232 | 10:00 | Siddhirganj | 225 | 13:00 | 218 | 10:00
| Ghorashal | N/A | N/A | N/A | N/A | Sirajgonj | 257 | 21:00 | 226 | 22:00
| GPH | 231 | 18:00 | 214 | 04:00 | Tongi | 226 | 18:00 | 215 | 09:00
| Haripur | 223 | 13:00 | 217 | 00:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 137 | 06:00 | 133 | 10:00 | Lalbag | 137 | 04:00 | 132 | 10:00
| Agargaon | 137 | 13:00 | 132 | 22:00 | Lalmonirhat | 126 | 18:30 | 114 | 22:00
| Agrabad | 137 | 19:00 | 124 | 23:00 | Madanganj | 131 | 19:00 | 126 | 00:00
| AKS | 136 | 19:00 | 124 | 23:00 | Madaripur | 141 | 16:00 | 133 | 00:00
| Aminbazar | 134 | 13:00 | 126 | 09:00 | Madartek | 137 | 13:00 | 133 | 01:00
| Amnura | 134 | 01:00 | 125 | 22:00 | Madunaghat | 139 | 19:00 | 125 | 23:00
| Ashuganj | 137 | 13:00 | 134 | 20:00 | Magura | 140 | 11:00 | 132 | 21:00
| Bagerhat | 137 | 08:00 | 129 | 01:00 | Mahasthangarh | 136 | 17:00 | 124 | 03:00
| Bakulia | 138 | 19:00 | 128 | 00:00 | Manikganj | 133 | 19:00 | 124 | 10:00
| Banani | 131 | 18:30 | 125 | 10:00 | Maniknagar | 133 | 19:00 | 127 | 09:00
| Bangabhaban | 133 | 13:00 | 126 | 10:00 | Matarbari | 127 | 19:00 | 109 | 23:00
| Barapukuria | 136 | 18:30 | 125 | 21:00 | Matuail | 130 | 13:00 | 126 | 22:00
| Barguna | 140 | 16:00 | 130 | 23:00 | Millgate | 132 | 19:00 | 125 | 10:00
| Barishal | 142 | 09:00 | 128 | 23:00 | Mirpur | 134 | 19:00 | 124 | 11:00
| Barishal-230 | 142 | 13:00 | 133 | 00:00 | Mithapukur | 138 | 17:00 | 119 | 22:00
| Baroaulia | 137 | 19:00 | 126 | 03:00 | Modern | 138 | 23:00 | 127 | 03:00
| Baroirhat | 130 | 19:30 | 121 | 23:00 | Mogbazar | 137 | 04:00 | 134 | 11:00
| Bashundhara | 131 | 18:30 | 125 | 10:00 | Mongla | 136 | 09:00 | 129 | 22:00
| BashundharaCement | 131 | 19:00 | 126 | 00:00 | Motijheel | 159 | 01:00 | 126 | 10:00
| Beanibazar | 134 | 19:00 | 124 | 23:00 | Munshiganj | 131 | 18:00 | 126 | 01:00
| Benapole | 137 | 18:00 | 128 | 22:00 | Mymensingh | 130 | 15:00 | 113 | 20:00
| Bhaluka | 130 | 13:00 | 111 | 18:00 | Naogaon | 132 | 18:30 | 118 | 22:00
| Bhandaria | 144 | 17:00 | 129 | 01:00 | Narail | 139 | 17:00 | 130 | 22:00
| Bhangura | 139 | 18:00 | 133 | 21:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bheramara | 137 | 18:00 | 131 | 22:00 | Narshingdi | 125 | 06:00 | 118 | 00:00
| Bheramara(GK) | 139 | 16:00 | 135 | 01:00 | Natore | 135 | 18:00 | 126 | 22:00
| Bhulta | 123 | 13:00 | 120 | 00:00 | Nawabganj | 139 | 13:00 | 131 | 10:00
| Bog-Sherpur | 136 | 18:00 | 126 | 22:00 | Netrakona | 127 | 18:30 | 113 | 18:00
| Bogura | 137 | 18:00 | 127 | 21:00 | New | 132 | 13:00 | 126 | 09:00
| Bogura-230 | 138 | 18:30 | 128 | 22:00 | Niamatpur | 131 | 18:00 | 113 | 22:00
| Brahmanbaria | 133 | 13:00 | 128 | 19:30 | Noapara | 137 | 10:00 | 131 | 22:00
| Cantonment | 136 | 19:00 | 130 | 10:00 | Pabna | 136 | 17:00 | 129 | 21:00
| Chandpur | 134 | 18:00 | 128 | 01:00 | Palashbari | 134 | 17:00 | 120 | 01:00
| Chandraghona | 137 | 19:00 | 128 | 04:00 | Panchagarh | 129 | 18:00 | 107 | 02:00
| Chapai | 135 | 18:00 | 126 | 21:00 | Patuakhali | 138 | 15:00 | 131 | 23:00
| Charsaidpur | 132 | 19:00 | 127 | 00:00 | Payra | 139 | 17:00 | 135 | 02:00
| Chauddagram | 132 | 19:00 | 124 | 03:00 | PHP | 130 | 19:00 | 121 | 03:00
| Chhatak | 130 | 18:30 | 123 | 22:00 | Postogola | 142 | 19:00 | 135 | 09:00
| Chowmuhani | 130 | 19:00 | 118 | 05:00 | Purbachal | 133 | 18:30 | 125 | 10:00
| Chuadanga | 137 | 09:00 | 127 | 19:00 | Purbasadipur | 131 | 18:00 | 111 | 10:00
| Coxsbazar | 127 | 19:00 | 112 | 23:00 | Rahim | 131 | 13:00 | 127 | 00:00
| Cumilla(N) | 131 | 13:00 | 126 | 23:00 | Rajbari | 137 | 18:00 | 128 | 22:00
| Cumilla(S) | 133 | 19:00 | 125 | 04:00 | Rajendrapur | 133 | 18:00 | 120 | 13:00
| Daudkandi | 133 | 13:00 | 124 | 21:00 | Rajshahi | 133 | 17:00 | 125 | 22:00
| Dhaka | 138 | 06:00 | 133 | 11:00 | Rajshahi-230 | 136 | 18:00 | 124 | 22:00
| Dhamrai | 131 | 19:00 | 124 | 10:00 | Ramganj | 130 | 19:00 | 121 | 23:00
| Dhanmondi | 130.5 | 19:00 | 126 | 11:00 | Rampur | 135 | 20:00 | 127 | 05:00
| Dohazari | 136 | 19:00 | 125 | 08:00 | Rampura | 137 | 13:00 | 133 | 00:00
| Faridpur | 136 | 18:00 | 130 | 01:00 | Rangamati | 134 | 19:00 | 127 | 04:00
| Fatullah | 134 | 13:00 | 128 | 10:00 | Rangpur | 126 | 07:00 | 116 | 12:00
| Fenchuganj | 136 | 18:30 | 131 | 05:00 | Ruppur | 138 | 13:00 | 131 | 22:00
| Feni | 132 | 19:00 | 125 | 01:00 | Saidpur | 134 | 18:30 | 116 | 12:00
| Ghorashal | 138 | 18:30 | 133 | 08:00 | Satkhira | 136 | 18:00 | 127 | 01:00
| Goalpara | 138 | 18:00 | 133 | 03:00 | Satmasjid | 137 | 19:00 | 131 | 10:00
| Gollamari | 137 | 18:00 | 131 | 01:00 | Savar | 135 | 19:00 | 123 | 11:00
| Gopalganj | 140 | 18:00 | 134 | 01:00 | Shahjadpur | 138 | 00:00 | 134 | 22:00
| Gopalganj_I | 142 | 17:00 | 134 | 01:00 | Shahjibazar | 134 | 00:00 | 131 | 10:00
| Gulshan | 136 | 07:00 | 132 | 11:00 | Shahmirpur | 137 | 19:00 | 125 | 23:00
| Halishahar | 136 | 19:00 | 124 | 23:00 | Shariatpur | 141 | 18:30 | 130 | 01:00
| Haripur | 131 | 13:00 | 127 | 00:00 | Sherpur | 130 | 18:30 | 110 | 06:00
| HaripurSBU | 132 | 13:00 | 128 | 00:00 | Shikalbaha | 138 | 19:00 | 124 | 23:00
| Hasnabad | 142 | 19:00 | 135 | 09:00 | Shikalbaha-230 | 136 | 19:30 | 127 | 04:00
| Hathazari | 135 | 19:30 | 127 | 23:00 | Shitalakhya | 141 | 19:00 | 129 | 08:00
| Ishurdi | 138 | 18:30 | 131 | 22:00 | Sholosohor | N/A | N/A | N/A | N/A
| Jaldhaka | 130 | 18:00 | 113 | 22:00 | Shyampur | 134 | 13:00 | 129 | 10:00
| Jamalpur | 133 | 17:00 | 114 | 06:00 | Shyampur-230 | 135 | 19:00 | 128 | 10:00
| Jashore | 137 | 17:00 | 129 | 22:00 | Siddhirganj | 131 | 13:00 | 127 | 01:00
| Jhenaidah | 141 | 17:00 | 132 | 22:00 | Sirajganj | 136 | 18:00 | 127 | 22:00
| Jhenaidah-230 | 142 | 18:00 | 134 | 21:00 | Sonargaon | 129 | 02:00 | 124 | 10:00
| Joydebpur | 141 | 19:00 | 128 | 03:00 | Sreemongol | 135 | 19:00 | 132 | 10:00
| Joypurhat | 132 | 18:00 | 117 | 22:00 | Srinagar | 138 | 13:00 | 131 | 10:00
| Juldah | 138 | 19:00 | 124 | 23:00 | SSM | 140 | 19:00 | 129 | 03:00
| Kabirpur | 136 | 19:00 | 123 | 10:00 | Sunamganj | 128 | 18:00 | 120 | 22:00
| Kachua | 132 | 19:00 | 125 | 23:00 | Sylhet | 132 | 19:00 | 129 | 09:00
| Kaliakoir | 135 | 17:00 | 129 | 20:00 | Tangail | 135 | 18:00 | 124 | 20:00
| Kallyanpur | 132 | 06:00 | 124 | 10:00 | Thakurgaon | 132 | 18:00 | 107 | 02:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2022-08-19
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 865 | 7641 | 4520 | 12161 |  |  |  | QF-LDC-11
0:30 | 957.5 | 7380.5 | 4538 | 11918.5 | Date: | 2022-08-19
1:00 | 1050 | 7120 | 4556 | 11676
1:30 | 1050 | 7161.5 | 4533 | 11694.5
2:00 | 1050 | 7203 | 4510 | 11713
2:30 | 1050 | 7179 | 4500.5 | 11679.5 | [5 empty] | Gen. at Eve. Peak | 12644 | 12644 MW (21:00 )
3:00 | 1050 | 7155 | 4491 | 11646 | [6 empty] | 21:00
3:30 | 1040 | 7163 | 4501 | 11664 | [5 empty] | Gen. at Day Peak | 10658 | 10658 MW (12:00 )
4:00 | 1030 | 7171 | 4511 | 11682 | [6 empty] | 12:00
4:30 | 1010 | 7110 | 4477 | 11587 | [5 empty] | Highest Generation | 12948
5:00 | 990 | 7049 | 4443 | 11492 | [6 empty] | 23:00
5:30 | 952.5 | 6925.5 | 4286 | 11211.5
6:00 | 915 | 6802 | 4129 | 10931
6:30 | 877.5 | 6732 | 4050.5 | 10782.5
7:00 | 840 | 6662 | 3972 | 10634
7:30 | 877.5 | 6635.5 | 3898 | 10533.5
8:00 | 915 | 6609 | 3824 | 10433
8:30 | 925 | 6642.5 | 3800 | 10442.5
9:00 | 935 | 6676 | 3776 | 10452
9:30 | 925 | 6644 | 3726.5 | 10370.5
10:00 | 915 | 6612 | 3677 | 10289
10:30 | 867.5 | 6634 | 3628.5 | 10262.5
11:00 | 820 | 6656 | 3580 | 10236
11:30 | 835 | 6790.5 | 3656.5 | 10447
12:00 | 850 | 6925 | 3733 | 10658
12:30 | 780 | 7055.5 | 3730.5 | 10786
13:00 | 710 | 7186 | 3728 | 10914
13:30 | 730 | 6910.5 | 3694.5 | 10605
14:00 | 750 | 6635 | 3661 | 10296
14:30 | 800 | 6818 | 3663.5 | 10481.5
15:00 | 850 | 7001 | 3666 | 10667
15:30 | 902.5 | 6841 | 3641.5 | 10482.5
16:00 | 955 | 6681 | 3617 | 10298
16:30 | 917.5 | 6594 | 3591 | 10185
17:00 | 880 | 6507 | 3565 | 10072
17:30 | 890 | 6520 | 3557.5 | 10077.5
18:00 | 900 | 6533 | 3550 | 10083
18:30 | 655 | 7186.5 | 3809.5 | 10996
19:00 | 410 | 7840 | 4069 | 11909
19:30 | 470 | 8053 | 4383 | 12436
20:00 | 500 | 8014 | 4434 | 12448 |  |  |  | Executive Engineer
20:30 | 515 | 8061.5 | 4484.5 | 12546 |  |  |  | Network Operation Division
21:00 | 530 | 8109 | 4535 | 12644
21:30 | 520 | 8138.5 | 4591 | 12729.5
22:00 | 510 | 8168 | 4647 | 12815 |  |  |  |  | Page 6 of 7
22:30 | 610 | 8219.5 | 4662 | 12881.5
23:00 | 710 | 8271 | 4677 | 12948
23:30 | 787.5 | 7956 | 4598.5 | 12554.5
24:00 | 865 | 7641 | 4520 | 12161
12644 MW (21:00 )
10658 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2022-08-19 |  | Energy |  | 272629644
[13 empty] | 2022-08-19 |  |  |  |  | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 4272 | 908 | 1864 | 689 | 1780 | 1450 | 145 | 440 | 659 | 168 | 0 | 773
0:30 | 4264 | 907.5 | 1766.5 | 766 | 1632 | 1457.5 | 148 | 441.5 | 606.5 | 145 | 0 | 904.4252 | Date: | 2022-08-19
1:00 | 4256 | 907 | 1669 | 843 | 1484 | 1465 | 151 | 443 | 554 | 122 | 0 | 1035.8503
1:30 | 4287 | 907 | 1676 | 869.5 | 1463 | 1464.5 | 151 | 442.5 | 531.5 | 120 | 0 | 926.6437 | [7 empty] | Total Energy | 272.6296 | Total Energy Gen 272.630 MKWHr Energy Not Served 18.401 MKWHr Energy Requirement 291.031 MKWHr
2:00 | 4318 | 907 | 1683 | 896 | 1442 | 1464 | 151 | 442 | 509 | 118 | 0 | 817.437 | [7 empty] | Energy not Served | 18.4011
2:30 | 4287.5 | 907.5 | 1683 | 894 | 1448.5 | 1454 | 151 | 442 | 512 | 117 | 0 | 756.1523 | [7 empty] | Energy Requirement | 291.0307
3:00 | 4257 | 908 | 1683 | 892 | 1455 | 1444 | 151 | 442 | 515 | 116 | 0 | 694.8675
3:30 | 4267.5 | 907.5 | 1679 | 896 | 1462.5 | 1444 | 151 | 442.5 | 515 | 116 | 0 | 586.1217 | [5 empty] | Shortage
4:00 | 4278 | 907 | 1675 | 900 | 1470 | 1444 | 151 | 443 | 515 | 116 | 0 | 477.3759
4:30 | 4277.5 | 907.5 | 1667.5 | 872 | 1437 | 1424 | 151 | 443 | 510 | 115 | 0 | 426.6892
5:00 | 4277 | 908 | 1660 | 844 | 1404 | 1404 | 151 | 443 | 505 | 114 | 0 | 376.0026
5:30 | 4278 | 908 | 1651 | 624.5 | 1409.5 | 1379.5 | 150.5 | 430.5 | 473 | 108 | 3 | 358.0319
6:00 | 4279 | 908 | 1642 | 405 | 1415 | 1355 | 150 | 418 | 441 | 102 | 6 | 340.0612
6:30 | 4276.5 | 907.5 | 1642 | 318.5 | 1416.5 | 1319.5 | 133 | 406.5 | 427.5 | 100 | 15 | 255.7371 |  |  |  | Coal
7:00 | 4274 | 907 | 1642 | 232 | 1418 | 1284 | 116 | 395 | 414 | 98 | 24 | 171.4129
7:30 | 4273.5 | 907 | 1598 | 161 | 1489.5 | 1257.5 | 116 | 355 | 390.5 | 94 | 41.5 | 264.7065 |  |  | Oil |  |  |  | ,
8:00 | 4273 | 907 | 1554 | 90 | 1561 | 1231 | 116 | 315 | 367 | 90 | 59 | 358
8:30 | 4266.5 | 907 | 1572.5 | 80 | 1567 | 1211 | 116 | 312.5 | 365.5 | 90 | 84.5 | 518.5
9:00 | 4260 | 907 | 1591 | 70 | 1573 | 1191 | 116 | 310 | 364 | 90 | 110 | 679
9:30 | 4246.5 | 907 | 1591 | 71 | 1544.5 | 1160.5 | 116.5 | 310 | 325.5 | 87 | 141 | 827.5
10:00 | 4233 | 907 | 1591 | 72 | 1516 | 1130 | 117 | 310 | 287 | 84 | 172 | 976
10:30 | 4176.5 | 907 | 1577 | 182 | 1499.5 | 1131 | 117 | 297.5 | 288 | 89 | 128 | 1172.5
11:00 | 4120 | 907 | 1563 | 292 | 1483 | 1132 | 117 | 285 | 289 | 94 | 84 | 1369
11:30 | 4114.5 | 906.5 | 1588 | 354.5 | 1504.5 | 1177 | 134.5 | 293 | 314.5 | 96 | 119.5 | 1444
12:00 | 4109 | 906 | 1613 | 417 | 1526 | 1222 | 152 | 301 | 340 | 98 | 155 | 1519
12:30 | 4070 | 907 | 1613.5 | 515.5 | 1566.5 | 1230.5 | 152 | 315.5 | 357.5 | 121 | 132.5 | 1468.5
13:00 | 4031 | 908 | 1614 | 614 | 1607 | 1239 | 152 | 330 | 375 | 144 | 110 | 1418
13:30 | 4031 | 908 | 1614 | 614 | 1607 | 1239 | 152 | 330 | 375 | 144 | 110 | 1461
14:00 | 4031 | 908 | 1614 | 614 | 1607 | 1239 | 152 | 330 | 375 | 144 | 110 | 1504
14:30 | 4047.5 | 908 | 1596.5 | 519.5 | 1622 | 1249 | 149.5 | 290 | 335.5 | 143 | 100 | 1515
15:00 | 4064 | 908 | 1579 | 425 | 1637 | 1259 | 147 | 250 | 296 | 142 | 90 | 1526
15:30 | 4072.5 | 907.5 | 1582.5 | 243.5 | 1662 | 1235 | 144 | 250 | 302 | 131 | 82.5 | 1490
16:00 | 4081 | 907 | 1586 | 62 | 1687 | 1211 | 141 | 250 | 308 | 120 | 75 | 1454
16:30 | 3874 | 907 | 1605.5 | 31 | 1740 | 1171.5 | 141.5 | 250 | 317.5 | 124 | 49.5 | 828.3733
17:00 | 3874 | 907 | 1625 | 0 | 1793 | 1132 | 142 | 250 | 327 | 128 | 24 | 202.7465
17:30 | 3836.5 | 907.5 | 1495.5 | 0 | 1973.5 | 1117.5 | 141 | 250 | 342 | 127 | 17 | 270.4823
18:00 | 3799 | 908 | 1366 | 0 | 2154 | 1103 | 140 | 250 | 357 | 126 | 10 | 338.218
18:30 | 3909 | 907.5 | 1575.5 | 135 | 2412.5 | 1112 | 142.5 | 277 | 516 | 141 | 5 | 257.1194
19:00 | 4019 | 907 | 1785 | 270 | 2671 | 1121 | 145 | 304 | 675 | 156 | 0 | 176.0208
19:30 | 4189 | 908 | 1824 | 120 | 2919 | 1200 | 145 | 406 | 781 | 156 | 0 | 0
20:00 | 4319 | 908 | 1770 | 0 | 2907 | 1240 | 145 | 440 | 770 | 162 | 0 | 49.765
20:30 | 4328 | 907.5 | 1794.5 | 0 | 2928.5 | 1315.5 | 144.5 | 404.5 | 746 | 163 | 0 | 77.8731
21:00 | 4337 | 907 | 1819 | 0 | 2950 | 1391 | 144 | 369 | 722 | 164 | 0 | 105.9811
21:30 | 4362 | 907 | 1835 | 0 | 2935.5 | 1410.5 | 144.5 | 403.5 | 751.5 | 166 | 0 | 609.4906
22:00 | 4387 | 907 | 1851 | 0 | 2921 | 1430 | 145 | 438 | 781 | 168 | 0 | 1113
22:30 | 4385 | 907.5 | 1869 | 235.5 | 2786 | 1430 | 145 | 438 | 728.5 | 170 | 0 | 1059.5
23:00 | 4383 | 908 | 1887 | 471 | 2651 | 1430 | 145 | 438 | 676 | 172 | 0 | 1006
23:30 | 4327.5 | 908 | 1875.5 | 580 | 2215.5 | 1440 | 145 | 439 | 667.5 | 170 | 0 | 1127.5 | Max Temp. in Dhaka |  | 34.0° C
24:00 | 4272 | 908 | 1864 | 689 | 1780 | 1450 | 145 | 440 | 659 | 168 | 0 | 1249
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 272.630 MKWHr Energy Not Served 18.401 MKWHr Energy Requirement 291.031 MKWHr
Shortage
Note on W13: Author:

## Generation
g | 2022-08-19
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 81 | 81 | 81 | 81 | 81 | 80 | 81 | 81 | 81 | 82 | 82 | 82 | 82 | 84 | 77 | 76 | 77 | 75 |  | 80 | 80 | 80 | 79 | 80 | 80 | 80 | 1960233
2 | Karnaphuli Hydro PP Unit-4 & 5 | 70 | 70 | 70 | 70 | 70 | 70 | 35 | 35 | 35 | 35 | 35 | 70 | 70 | 70 | 70 | 65 | 65 | 65 |  | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 1480000
3 | Chattogram TPP-1 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2400000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 22 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 588949
| Teknaf 20MW PP (Solartech) | [5 empty] | 1 | 4 | 6 | 4 |  | 9 | 6 | 2 | 4 | 3 | 1 | 1 | 0 | [8 empty] | 41040
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 610523
12 | Hathazari 100 MW peaking PP | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 |  | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 605328
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 44 | 89 | 87 | 87 | 105 | 78 | 17 | 738508
| Daudkandi 200 MW PP (B.Trac) | 194 | 195 | 195 | 195 | 195 | 152 | 152 | 10 | 10 | 10 | 40 | 100 | 160 | 10 | 100 | 0 |  |  |  | 30 | 20 | 0 |  |  | 80 | 150 | 1958400
14 | Titas 50 MW Peaking PP | 46 | 38 | 44 | 44 | 44 | 44 | 38 | 38 | 38 | 38 | 38 | 38 | 37 | 37 | 36 | 42 | 44 | 44 |  | 44 | 44 | 44 | 44 | 45 | 45 | 45 | 1006280
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 37 | 37 | 37 | 36 | 37 | 37 | 37 | [18 empty] | 0 | 316000
17 | Siddhirganj 335 MW CCPP | 76 | 76 | 75 | 75 | 75 | 76 | 76 | 72 | 77 | 77 | 76 | 74 | 75 | 76 | 76 | 75 | 40 | 40 |  | 78 | 130 | 201 | 180 | 181 | 179 | 178 | 2284110
18 | Kodda 300 MW PP Unit-2 (Summit) | 110 | 111 | 111 | 110 | 110 | 110 | 110 | 110 | 112 | 112 | 110 | 112 | 112 | 112 | 115 | 112 | 130 | 150 |  | 215 | 255 | 258 | 260 | 258 | 258 | 150 | 3495162
19 | Ashuganj 195MW PP (APSCL-United) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 55 | 55 | 55 | 55 | 568727
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4347000
24
25 | Ghorasal 365 MW CCPP Unit-7 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 196 | 200 | 200 | 200 | 200 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 5888118
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 39 | 39 | 39 | 37 | 37 | 37 | 37 | 37 | 37 | 30 | 36 | 38 | 35 | 34 | 31 | 31 | 34 | 35 |  | 35 | 31 | 32 | 34 | 37 | 37 | 37 | 846072
33 | Ashuganj 225 MW CCPP | 207 | 207 | 207 | 208 | 207 | 209 | 209 | 211 | 206 | 204 | 205 | 207 | 209 | 201 | 205 | 204 | 204 | 205 |  | 209 | 206 | 210 | 207 | 206 | 206 | 208 | 4992000
34 | Ashuganj 450 MW CCPP(South) | 320 | 330 | 305 | 305 | 305 | 305 | 305 | 305 | 305 | 320 | 330 | 305 | 305 | 305 | 305 | 305 | 270 | 270 |  | 265 | 275 | 305 | 320 | 340 | 340 | 310 | 7557000
| Ashuganj 450 MW CCPP(North) | 325 | 335 | 310 | 310 | 310 | 310 | 310 | 315 | 315 | 325 | 335 | 315 | 315 | 305 | 310 | 310 | 280 | 280 |  | 280 | 295 | 310 | 325 | 350 | 345 | 310 | 7970900
Ashuganj 420 MW CCPP(East)
35 | Ashuganj 55 MW PP (Precision) | 56 | 55 | 56 | 56 | 56 | 55 | 55 | 56 | 56 | 54 | 54 | 56 | 55 | 54 | 51 | 50 | 51 | 52 |  | 52 | 52 | 54 | 55 | 56 | 56 | 55 | 1307520
36 | Chandpur 150 MW CCPP | 143 | 143 | 143 | 143 | 143 | 143 | 143 | 145 | 144 | 143 | 143 | 144 | 143 | 143 | 143 | 145 | 146 | 142 |  | 143 | 142 | 143 | 143 | 143 | 144 | 143 | 1534080
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 405 | 405 | 405 | 404 | 403 | 403 | 403 | 403 | 405 | 408 | 407 | 407 | 403 | 411 | 400 | 404 | 407 | 396 |  | 397 | 404 | 410 | 410 | 410 | 408 | 408 | 9828350
40 | Meghnaghat 450 MW CCPP(MPL) | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 390 | 400 | 400 | 400 | 400 | 400 | 410 | 410 | 430 | 350 |  | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 8575750
41 | Haripur 360MW CCPP(HPL) | 253 | 253 | 253 | 249 | 253 | 253 | 253 | 268 | 274 | 273 | 274 | 283 | 283 | 283 | 292 | 307 | 314 | 253 |  | 322 | 322 | 311 | 282 | 297 | 310 | 311 | 6634000
42 | RPCL 210MW CCPP | 106 | 106 | 105 | 107 | 106 | 107 | 117 | 156 | 155 | 152 | 153 | 140 | 122 | 132 | 151 | 150 | 152 | 153 |  | 155 | 154 | 158 | 150 | 156 | 156 | 159 | 3180480
43 | Sutiakhali 50 MW Solar PP |  |  |  |  | 0 | 2 | 6 | 31 | 43 | 54 | 6 | 56 | 54 | 43 | 44 | 30 | 15 | 5 |  | 0 | [6 empty] | 340130
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 42 | 42 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1019000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 682872
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 62 | 62 | 64 | 64 | 64 | 64 | 64 | 62 | 60 | 59 | 57 | 59 | 61 | 59 | 58 | 60 | 61 | 61 |  | 64 | 62 | 61 | 58 | 60 | 60 | 64 | 1466496
48 | Shahjibazar 86MW PP (Shahjibazar) | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 10 | 10 | 10 | 10 | 50 | 50 | 10 | 10 | 10 | 10 | 10 |  | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 1270080
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 207 | 207 | 207 | 207 | 207 | 207 | 207 | 207 | 207 | 209 | 208 | 208 | 208 | 208 | 208 | 208 | 208 | 208 |  | 208 | 208 | 208 | 208 | 208 | 208 | 208 | 4823580
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 8 | 9 | 8 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 237600
54 | Hobiganj 11MW PP Cofidence-E
55 | Fenchugonj 51 MW PP (Barakatullah) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | [6 empty] | 0 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 91200
56 | Shahjahanulla 25 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | [9 empty] | 0 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 108552
57 | Bibiana-II 341 MW CCPP (Summit) | 300 | 310 | 310 | 300 | 290 | 270 | 270 | 270 | 290 | 300 | 300 | 300 | 290 | 260 | 300 | 280 | 280 | 265 |  | 270 | 310 | 260 | 290 | 300 | 320 | 300 | 7129000
| Bibiyana South 400 MW | 398 | 396 | 395 | 400 | 400 | 400 | 400 | 394 | 400 | 388 | 380 | 386 | 360 | 378 | 378 | 386 | 320 | 290 |  | 360 | 398 | 400 | 400 | 394 | 395 | 397 | 9142200
58 | Nababganj 55 MW PP (Southern power ) | [6 empty] | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 780678
59 | Tangail Palli Power Gen 22 MW | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 298080
60 | Barabkunda 22 MW PP (Regent) | 12 | 12 | 0 | 9 | 9 | 9 | 9 | 9 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 |  | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 265056
61 | Narshingdi 22 MW PP (Doreen) | 0 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 18 |  |  | 18 | 18 | 18 | 18 | 18 | 18 | 19 |  | 19 | 19 | 19 | 22 | 22 | 22 | 0 | 392112
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 20 | 20 | 20 | 20 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 492588
63 | Impoprt (Tripura) | 122 | 118 | 116 | 116 | 114 | 102 | 98 | 90 | 90 | 84 | 94 | 98 | 144 | 126 | 142 | 120 | 128 | 126 |  | 156 | 156 | 162 | 164 | 168 | 172 | 168 | 2979840
64 | Malancha, Ctg. EPZ (United) | 35 | 35 | 36 | 36 | 36 | 38 | 40 | 25 | 40 | 32 | 8 | 32 | 42 | 40 | 34 | 37 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 912480
65 | Feni 22MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 21 | 21 | 21 |  | 21 | 21 | 22 | 21 | 21 | 21 | 21 | 507636
66 | Feni 11 MW PP (Doreen) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 167220
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 32 | 30 | 30 | 30 | 30 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 784100
68 | Cumilla 25 MW PP (Summit) | 14 | 14 | 14 | 14 | 14 | 14 | 11 | 11 | 11 | 11 | 11 | 14 | 14 | 14 | 14 | 14 | 14 | 14 |  | 14 | 14 | 12 | 12 | 12 | 12 | 14 | 329540
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 9 | 28 | 28 | 28 | 28 | 24 | 24 | 26 | 26 | 27 | 20 | 26 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 27 | 27 | 27 | 27 | 27 | 0 | 521100
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 803300
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 31 | 31 | 31 | 31 | 31 | 31 | 28 | 21 | 22 | 22 |  | 31 | 31 | 32 | 32 | 33 | 33 | 33 | 740600
73 | Ghorashal 108MW PP (Regent) | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 86 | 86 | 86 | 86 | 86 | 90 | 87 | 87 | 87 | 87 | 52 |  | 90 | 90 | 91 | 91 | 91 | 91 | 88 | 2025045
| Feni Lanka Power | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 56 | 88 | 88 | 88 | 88 | 88 | 17 | 784320
| Chowmuhani 113 MW | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 8 | 9 | 14 |  | 27 | 29 | 28 | 28 | 29 | 29 | 29 | 344400
| Manikgonj 162MW PP(MPGL) | 54 | 54 | 54 | 54 | 54 | 54 | 35 | 35 | 35 | 35 | 35 | 45 | 102 | 108 | 108 | 136 | 162 | 162 |  | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 2340000
77 | Siddhirganj 100 PP(Dutch Bangla) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 9 |  | 16 | 16 | 16 | 16 | 16 | 16 | 8 | 236160
78 | Gazipur 52 MW PP | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 34 | 40 | 40 | 40 | 41 | 41 | 24 | 657120
79 | Kodda 150MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 29 | 29 | 29 | 30 | 45 | 50 |  | 122 | 122 | 105 | 115 | 121 | 16 | 16 | 873120
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | [26 empty] | 0
| Gazipur 100 MW PP | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 72 | 72 |  | 88 | 88 | 88 | 88 | 88 | 88 | 52 | 1491600
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 0 | 1 | 3 | 3 | 2 | 3 | 2 | 3 | 1 | 1 | 0 | [9 empty] | 22439
| Jodiac Power | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 40 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 40 | 1139512
| Karnaphuli Power Ltd. | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 44 | 51 | 55 | 55 | 49 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1316431
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL) | 8 | 7 | 8 | 8 | 8 | 8 | 7 | 7 | 8 | 8 | 9 | 7 | 7 | 8 | 8 | 8 | 7 | 8 |  | 8 | 8 | 8 | 7 | 8 | 7 | 8 | 198720
| Meghnaghat 104 MW PP (OPCL) |  |  | 0 | 15 | 17 | 0 |  | 17 | 17 |  |  |  |  | 17 | 17 | 17 | 0 |  |  | 17 | 17 | 17 | 17 | 17 | 17 | 0 | 202560
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 259200
92 | Fenchuganj 44MW (Energyprima) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | [8 empty] | 0 | 5 | 5 | 5 | 5 | 5 | 5 | 104112
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1210040
94 | Gagnagar 102 MW PP (Digital Power) | 8 | 8 | 8 | 8 | 8 | 24 | 24 | 24 | 24 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 16 | 16 | 16 | 16 | 16 | 16 | 8 | 287280
95 | Patenga 50MW PP (Baraka) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 1 | 6 | 6 | 6 | 6 | 6 |  | 17 | 37 | 36 | 38 | 12 | 6 | 6 | 2275200
96 | Chattogram 108 MW PP (ECPV) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 11 | 11 | 11 | 12 | 12 | 11 | 12 | 12 | 12 | 11 | 22 |  | 79 | 87 | 93 | 94 | 94 | 61 | 12 | 657600
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 30 | 30 | 30 | 30 | 30 | 30 | 55 | 55 | 55 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 818813
100 | Manikganj 55 MW PP (Northern) | [14 empty] | 0 | 35 | 47 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 457246
101 | Kushiara 163 MW CCPP (KP)
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 2 | 1 |  | 0 | [8 empty] | 14300
103 | Kamalaghat 54 MW PP(Banco Energy) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 661320
104 | Keranigonj 300 MW PP (APR) | 252 | 304 | 300 | 302 | 240 | 53 | 10 | 10 | 10 | 12 | 110 | 157 | 293 | 23 | 250 | 10 | 0 | 0 |  | 44 | 20 | 0 |  |  | 207 | 303 | 2794706
105 | Bramhangoan 100 MW PP (Aggreko) | 70 | 70 | 70 | 70 | 70 | 70 | 25 | 25 | 25 | 25 | 60 | 60 | 45 | 0 |  |  |  | 0 |  | 91 | 25 | 0 |  |  | 70 | 70 | 856142
106 | Mymensingh 200 MW PP (United) | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 75 | 77 | 77 | 77 | 76 | 76 | 77 | 77 | 76 | 76 | 170 |  | 180 | 180 | 180 | 180 | 180 | 180 | 48 | 2200800
112 | Aurahati 100MW PP (Aggreko) | 70 | 70 | 70 | 70 | 70 | 70 | 25 | 25 | 25 | 25 | 80 | 80 | 80 | 25 | 50 | 50 | 0 | 0 |  | 92 | 25 | 0 |  |  | 92 | 70 | 1067694
114 | Kodda 149 MW PP Unit-1 (Summit) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 16 | 16 | 16 | 16 | 16 | 16 | 17 | 16 | 16 | 38 | 147 |  | 149 | 149 | 149 | 132 | 132 | 132 | 41 | 1211184
115 | Juldah 100 MW PP Unit-3 (Acorn) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 20 | 256320
116 | Chandpur 200MW (Desh energy) | 155 | 159 | 170 | 170 | 136 | 136 | 136 | 136 | 136 | 136 | 140 | 185 | 185 | 200 | 175 | 175 | 175 | 175 |  | 175 | 175 | 175 | 200 | 175 | 136 | 136 | 4008960
117 | Ashuganj 150MW PP (Midland) | 145 | 145 | 145 | 145 | 138 | 140 | 137 | 132 | 128 | 123 | 120 | 127 | 127 | 127 | 127 | 122 | 100 | 100 |  | 117 | 134 | 100 | 100 | 100 | 100 | 100 | 3046036
118 | Bibiyana-III 400 MW CCPP | 402 | 402 | 402 | 402 | 402 | 402 | 402 | 403 | 404 | 405 | 402 | 402 | 404 | 401 | 390 | 400 | 328 | 328 |  | 402 | 403 | 402 | 403 | 403 | 402 | 402 | 9476000
| Jamalpur 115 MW PP (United) | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 75 | 78 |  | 78 | 78 | 78 | 78 | 78 | 78 | 49 | 1548000
| Anwara 300 MW PP (United) | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 120 | 122 | 123 | 124 | 124 | 124 | 124 | 124 | 124 | 124 | 124 |  | 210 | 210 | 213 | 213 | 214 | 52 | 52 | 2604436
| Juldah unit-2 (Acorn) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 263040
| Anlima Energy Ltd. | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 105 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 2317145
| Bhairob 54.5 MW | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 889200
| Spectra Solar Plant Ltd. | [5 empty] | 1 | 3 | 6 | 20 | 14 | 25 | 24 | 36 | 25 | 29 | 21 | 4 | 2 |  | 0 | [6 empty] | 176873
| Chandpur 115(Doreen) | 85 | 55 | 56 | 57 | 56 | 56 | 56 | 53 | 56 | 56 | 48 | 38 | 56 | 66 | 56 | 56 | 48 | 17 |  | 63 | 97 | 96 | 97 | 98 | 96 | 97 | 1534080
| Kanchan Purbachal Power Generation Ltd. | 55 | 55 | 55 | 55 | 45 | 55 | 55 | 55 | 55 | 55 | 35 | [8 empty] | 0 | 10 | 25 | 55 | 55 | 55 | 48 | 856440
Mirsharai 150 MW (Oil)
Mirsharai 150 MW (Gas)
120 | Eastern Zone Total | 7120 | 7203 | 7155 | 7171 | 7049 | 6802 | 6662 | 6609 | 6676 | 6612 | 6656 | 6925 | 7186 | 6635 | 7001 | 6681 | 6507 | 6533 |  | 7840 | 8053 | 8014 | 8109 | 8168 | 8271 | 7641 | 171083164
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | [11 empty] | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 192960
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 20 | 20 | 20 | 20 | 19 | 19 | 19 | 19 | 13 | [7 empty] | 0 | 9 |  | 43 | 51 | 41 | 44 | 44 | 44 | 33 | 406080
| Khulna 225 MW CCPP | 225 | 225 | 225 | 226 | 225 | 228 | 225 | 185 | 180 | 180 | 155 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 160 | 194 | 227 | 210 | 225 | 225 | 226 | 4472177
129 | Rupsha 105 MW PP (Orion rupsha) | [8 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 17 | 389280
130 | Mongla Orion 100 MW Solar PP |  |  |  |  | 0 | 2 | 11 | 11 | 35 | 91 | 30 | 54 | 4 | 13 | 1 | 14 | 0 | 1 |  | 0 | [5 empty] | 0 | 206640
131 | Rampal 1320 MW (BIFPCL)
132 | United Payra Power Ltd. | [25 empty] | 0 | 0
133 | Bhola Nutan Biddut BD LTD (GAS)
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 32 | 32 | 32 | 32 | 16 | 16 | 0 | [5 empty] | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 381696
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 145 | 147 | 149 | 150 | 150 | 151 | 146 | 152 | 152 | 152 | 145 | 152 | 132 | 148 | 150 | 152 | 152 | 151 |  | 141 | 150 | 144 | 150 | 147 | 147 | 152 | 3560890
140 | Bhola 33 MW PP (Venture) | 25 | 24 | 22 | 22 | 14 | 15 | 13 | 10 | 9 | 11 | 13 | 12 | 11 | 9 | 9 | 7 | 7 | 10 |  | 18 | 19 | 19 | 24 | 25 | 28 | 28 | 385906
141 | Noapara 100 MW PP (Bangla Trac) | 93 | 93 | 93 | 93 | 93 | 10 | 10 | 10 | [9 empty] | 0 |  | 4 | 10 | 0 |  |  |  | 36 | 612480
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP | 65 | 65 | 65 | 65 | 55 | 55 | 54 | 54 | 57 | 30 | 30 | 30 | 25 | 28 | 28 | 28 | 28 | 37 |  | 57 | 63 | 75 | 68 | 68 | 68 | 68 | 1201024
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | 15 | [15 empty] | 0 | 15 |  | 32 | 32 | 32 | 32 | 32 | 32 | 15 | 218160
146 | Bheramara HVDC | 907 | 907 | 908 | 907 | 908 | 908 | 907 | 907 | 907 | 907 | 907 | 906 | 908 | 908 | 908 | 907 | 907 | 908 |  | 907 | 908 | 908 | 907 | 907 | 908 | 908 | 21936000
147 | Bheramara 410 MW CCPP | 175 | 175 | 175 | 180 | 180 | 180 | 175 | 175 | 170 | 160 | 155 | 155 | 150 | 145 | 150 | 150 | 155 | 160 |  | 170 | 175 | 175 | 175 | 180 | 185 | 180 | 4168512
148 | Payra 1320 MW | 1150 | 1150 | 1130 | 1130 | 1090 | 1040 | 970 | 900 | 860 | 800 | 800 | 890 | 910 | 910 | 930 | 880 | 800 | 770 |  | 790 | 870 | 910 | 1060 | 1100 | 1100 | 1120 | 25346500
149
150 | Barapukuria TPP Unit-1 | 80 | 79 | 79 | 79 | 80 | 80 | 79 | 81 | 81 | 80 | 82 | 82 | 79 | 79 | 78 | 81 | 82 | 82 |  | 80 | 79 | 80 | 80 | 80 | 80 | 80 | 1906909
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 235 | 235 | 235 | 235 | 234 | 235 | 235 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 251 | 250 | 250 | 251 |  | 251 | 251 | 250 | 251 | 250 | 250 | 250 | 5975900
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 32 | 32 | 31 | 31 | 30 | 30 | 32 | 32 |  | 32 | 32 | 32 | 32 | 32 | 32 | 31 | 752080
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 0 | 2 | 3 | 2 | 5 | 3 | 2 | 6 | 4 | 3 | 1 | 0 | [8 empty] | 31080
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 169 | 170 | 170 | 171 | 171 | 171 | 170 | 170 | 170 | 170 | 170 | 170 | 171 | 170 | 170 | 170 | 170 | 140 |  | 149 | 170 | 174 | 186 | 183 | 183 | 183 | 4341436
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
| Sirajgonj 225 MW CCPP Unit-2 (Oil) | 218 | 217 | 217 | 217 | 218 | 190 | 170 | 130 | 130 | 130 | 130 | 181 | 210 | 150 | 130 | 130 | 130 | 130 |  | 144 | 212 | 213 | 159 | 213 | 213 | 214 | 4457755
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 155 | 155 | 155 | 156 | 157 | 158 | 157 | 156 | 153 | 150 | 148 | 146 | 145 | 144 | 145 | 145 | 147 | 130 |  | 144 | 158 | 158 | 158 | 158 | 157 | 157 | 3897291
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 343 | 349 | 349 | 355 | 354 | 354 | 354 | 341 | 328 | 317 | 312 | 298 | 297 | 296 | 293 | 302 | 309 | 235 |  | 358 | 351 | 355 | 358 | 363 | 362 | 362 | 7901127
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | 35 | 36 | 36 | 36 | 36 | 0 | [8 empty] | 0 | 5 | 5 | 12 |  | 37 | 37 | 40 | 40 | 37 | 37 | 37 | 403875
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 21 | 21 | 19 | 19 | 19 | 18 | 18 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 21 | 21 | 471600
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 256320
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP | [17 empty] | 0 |  | 20 | 32 | 32 | 32 | 32 | 32 | 32 | 146328
168 | Santahar 50 MW Peaking PP | 30 | 0 | [15 empty] | 0 |  | 31 | 31 | 31 | 31 | 32 | 32 | 26 | 199846
169 | Natore 52 MW PP (Rajlanka) | [17 empty] | 0 |  | 8 | 8 | 8 | 8 | 8 | 8 | 0 | 36000
170 | Chapainawabganj 100 MW Peaking PP | 51 | 44 | 44 | 44 | 44 | 44 | 44 | 37 | 37 | [8 empty] | 0 |  | 68 | 80 | 80 | 80 | 80 | 80 | 80 | 794552
171 | Baghabari 200 MW PP (Paramount) | 164 | 164 | 164 | 170 | 176 | 50 | 10 | 10 |  |  | 2 | 20 | 36 | 10 | 25 | 2 | 0 | 0 |  | 9 | 20 | 0 |  |  | 22 | 60 | 1309933
| Bagura 113 MW PP (Confidence)-2 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 75 | 94 | 94 | 94 | 94 | 94 | 50 | 1589184
172 | Confidence Power Bogura Unit-1 113 MW | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 50 | 50 |  | 80 | 95 | 95 | 95 | 95 | 95 | 55 | 1575744
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | 56 | 55 | 55 | 55 | 55 | 55 | 55 | 56 | 56 | 56 | 56 | 56 | 55 | 55 | 55 | 52 | 87 | 85 |  | 91 | 91 | 91 | 91 | 92 | 92 | 56 | 1560940
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 0 | 1 | 1 | 7 | 6 | 8 | 8 | 6 | 6 | 4 | 3 | 2 | [8 empty] | 47859
178 | Energypac Power Venture Thakurgaon Ltd. | [16 empty] | 0 | 72 |  | 72 | 72 | 72 | 72 | 72 | 72 | 0 | 412416
178