## Forecast
8 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2022-08-21 | Sunday
|  |  | Date (day): | 2022-08-21 |  | Sunday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11692.6 | MW |  |  | (b) At Evening Peak Hour : |  | 13638 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2022-08-20 | 2022-08-21 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 200 | 300 | 300 | 300 |  | 65
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 86 | 93 | 87 | 87 |  | 21 | Engine problem
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 406 | 409 | 412 | 412
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 328 | 257 | 275 | 275 | 85 |  | Gas shortage
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 260 | 260 | 240 | 240 |  |  | Machine problem
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 8 | 8 | 8 | 8 | 92 |  | Fuel shortage
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 0 | 0 | 0 | 0 |  | 102 | Under maint
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 30 | 30 | 30 | 30 |  | 25 | Engine problem
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 22 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 35 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 8 | 7 | 8 | 8 | 92 |  | Fuel shortage
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 185 | 93 | 200 | 200 | 135 |  | ST shut down
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 8 | 8 | 8 | 8 | 94 |  | Fuel shortage
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 54 | 17 | 54 |  |  | Fuel shortage
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 45 | 119 | 16 | 120 |  | 29 | Fuel shortage
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 55 | 0 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 35 | 35 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 52 | 52 | 52 | 52 |  | 28 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 32 | 32 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 24 | 40 | 24 | 40 |  | 12 | Engine problem
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 188 | 243 | 110 | 285 |  | 15 | Engine problem
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 300 | 300 | 230 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 70 | 91 | 0 | 0 | 100 |  | Fuel shortage
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 91 | 70 | 90
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 17 | 149 | 16 | 149 |  |  | Fuel shortage
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 105 | 52 | 105 |  |  | Fuel shortage
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 0 | 17 | 17 | 17 | 87 |  | Fuel shortage
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 50 | 162 | 35 | 162 |  |  | Fuel shortage
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 16 | 0 | 30 | 0
| 40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 55 | 55 | 55 | 55
|  | Dhaka area Total |  |  |  |  | 6263 | 5847 | 2685 | 3335 | 2595 | 3375 | 1281 | 977
| 41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 108 | 110 | 110 | 110 | 70 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 16 | 25 | 25 | 25
| 43 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 13 | 0 | 20 | 0
| 44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 6 | 38 | 25 | 37 |  | 13 | Engine problem
| 45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 156 | 156 | 150 | 150 |  | 80 | Low Water Level
| 46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | S/D due to HGPI
| 47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
| 48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 34 | 87 | 69 | 85 |  |  | Engine problem
| 49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 9 | 43 | 40 | 40 | 58 |  | Fuel shortage
| 50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 17 | 51 | 17 | 51 | 51 |  | Fuel shortage
| 51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 10 | 10 | 10 | 10 | 90 |  | Fuel shortage
| 52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 10 | 10 | 10 | 10 |  | 90 | Fuel shortage
| 53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 11 | 11 | 11 | 11 |  | 11 | Engine problem
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 25 | 10 | 25
| 54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 12 | 94 | 12 | 93 |  |  | Fuel shortage
| 55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5 | 0 | 5 | 0
| 56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 124 | 181 | 85 | 178 | 122 |  | Fuel shortage
| 57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 36 | 54 | 36 | 54
| 58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 55 | 110 | 110 | 110
| 59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 10 | 10 | 10 | 10 |  |  | Fuel shortage
| 60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 90 | 108 | 108 | 108 |  | 8 | Engine problem
|  | Mirsharai 150 MW |  | Gas/HSD | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 724 | 1123 | 863 | 1107 | 571 | 577
| 61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 204 | 206 | 210 | 210 | 11
| 63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 290 | 310 | 300 | 320
| 64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 330 | 305 | 300 | 310
|  | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+136*1 | 284 | 284 | 0 | 0 | 0 | 0 |  |  | On test.
| 65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 35 | 40 | 35 | 35 |  | 10 | Engine problem
| 66 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 55 | 49 | 54 | 55 | 55
| 67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 55 | 73 | 36 | 36 | 159 |  | Gas shortage
| 68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 51 | 43 | 51
| 69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 105 | 138 | 140 | 140 |  | 10 | Engine problem
| 70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 44 | 47 | 37 | 45 |  | 7 | Engine problem
| 71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 143 | 144 | 145 | 145 |  | 18 | Machine problem
| 72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 200 | 200 | 100 | 200
| 73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 22 | 21 | 21
| 74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 10 | 10 | 10
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 152 | 156 | 143 | 165
| 75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 22 | 33 | 33 | 33
| 76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 8 | 8 | 8 | 44 |  | Fuel shortage
| 77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 12 | 18 | 18 | 18 |  | 7 | Engine problem
| 78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 150 | 195 | 200 | 200
| 79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 34 | 17 | 114 |  |  | Fuel shortage
| 80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 29 | 9 | 26 | 87 |  | Fuel shortage
| 81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 19 | 35 | 35 | 35 |  | 19 | 33 kV feeder fault
| 82 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 96 | 96 | 96 | 96 | 19 |  | Fuel shortage
|  | Cumilla Area Total |  |  |  |  | 3193 | 3169 | 2004 | 2204 | 1991 | 2273 | 454 | 71
| 83 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 113 | 127 | 85 | 100 | 102 |  | Gas shortage
| 84 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 85 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0 |  | 8 | Under maint.
| 86 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 87 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 77 | 106 | 80 | 180 |  | 20 | Engine problem
| 88 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 68 | 68 | 48 | 68 |  | 47 | Engine problem
| 89 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 56 | 0 | 50 | 0
| 90 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 12 | 12 |  | 10 | Engine problem
|  | Mymensingh Area Total |  |  |  |  | 717 | 614 | 350 | 335 | 298.6 | 382 | 102 | 85
| 91 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 43 | 43 | 43 |  | 27 | Machine problem.
| 92 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 20 | 30 | 30 |  | 60 | Machine problem
| 93 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 | 163 |  | Gas shortage
| 94 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
| 95 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 0 | 5 | 0 | 5 | 46 |  | Gas shortage
| 96 | Fenchuganj 44MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 0 | 5 | 0 | 5 | 45 |  | Gas shortage
| 97 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0
| 98 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 59 | 62 | 62 | 62
| 99 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 10 | 81 | 10 | 80
| 100 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
| 101 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 207 | 193 | 193 | 193 |  |  | Machine problem
| 102 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Gas shortage
| 103 | Sylhet 50MW PP (EPL) |  | Gas | NENP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Gas shortage
| 104 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 0 | 8 | 0 | 0 | 25 |  | Gas shortage
| 105 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 295 | 300 | 310 |  |  | FGMO
| 106 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 402 | 405 | 400 | 400
| 107 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 9 | 10 | 10 | 10
| 108 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 378 | 391 | 400 | 400
|  | Sylhet Area Total |  |  |  |  | 2522 | 2477 | 1438 | 1518 | 1448 | 1538 | 349 | 517
| 109 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 907 | 905 | 904 | 904
| 110 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 0 | 16 | 16 | 16 | 99 |  | Fuel shortage
| 111 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 40 | 20 | 43 |  | 11 | Engine problem
| 112 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 150 | 225 | 225 | 225
| 113 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 64 | 40 | 50 |  | 59 | Engine problem
| 114 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 150 | 155 | 155 | 155 | 255 |  | Gas shortage
| 115 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 0 | 0 | 0 | 40 |  | Fuel shortage
| 116 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 92 | 50 | 95
| 117 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 17 | 35 | 17 | 35 | 70 |  | Fuel shortage
| 118 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 32 | 67 | 15 | 67 |  |  | Fuel shortage
| 119 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 10 | 0 | 100 | 0
|  | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
|  | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
|  | Khulna Area Total |  |  |  |  | 2388 | 2384 | 1266 | 1599 | 1542 | 1590 | 480 | 70
| 120 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 32 | 32 | 48 |  |  | Line O/L
| 121 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 19 | 28 | 16 | 25 |  | 15 | Engine problem
| 122 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 148 | 150 | 151 | 151 |  |  | Machine problem
|  | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
| 123 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 960 | 1160 | 1170 | 1170
| 124 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 0 | 0 | 0 | 0 |  | 220 | Machine problem
| 125 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 0 | 17 |  |  | Line O/L
|  | Barisal Area Total |  |  |  |  | 1958 | 1958 | 1127 | 1370 | 1369 | 1411 | 0 | 235
| 126 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 127 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 32 | 32 | 32 |  | 20 | Engine problem
| 128 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 40 | 0 | 40 |  | 31 | Engine problem
| 129 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 130 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Fuel shortage
| 131 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 32 | 0 | 32 |  | 18 | Engine problem
| 132 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 174 | 174 | 180 | 180 | 30 |  | Gas shortage
| 133 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 130 | 196 | 220 | 220
| 134 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 148 | 148 | 150 | 150 | 70 |  | Gas shortage
| 135 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 291 | 316 | 305 | 305 | 109 |  | Gas shortage
| 136 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 32 | 0 | 32 |  | 18 | Engine problem
| 137 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 18 | 21 | 21 | 21
| 138 | Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 139 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 140 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 8 | 8 | 8 | 44 |  | Fuel shortage
| 141 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 38 | 82 | 35 | 80 |  | 24 | Engine problem
| 142 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 18 | 172 | 120 | 170 |  | 30 | Engine problem
| 143 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 50 | 94 | 50 | 94 |  | 19 | Engine problem
| 144 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 55 | 95 | 55 | 95 |  | 18 | Engine problem
| 145 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 2 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2129 | 935 | 1453 | 1193 | 1470 | 424 | 178
| 146 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 82 | 81 | 80 | 80
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
| 147 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 251 | 251 | 250 | 250 | 24
| 148 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
| 149 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
| 150 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 56 | 91 | 55 | 90 |  |  | Engine problem
| 151 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 6 | 0 | 8 | 0
| 152 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 0 | 72 | 0 | 72 |  | 43 | Fuel shortage
|  | Rangpur Area Total |  |  |  |  | 800 | 720 | 395 | 495 | 393 | 492 | 64 | 128
|  | Total |  |  |  |  | 22482 | 21680 | 10924 | 13432 | 11692.6 | 13638 | 3725 | 2838
| A. |  | 2022-08-20 | (Yesterday) |  |  |  |  | Saturday
| 1 | Highest Generation : |  |  | 13478 | MW at | 22:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 20:00 | hrs.
| 2 | Minimum Generation : |  |  | 10502 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 13950 | MW
| 3 | Day peak Generation : |  |  | 10924 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 13236.12 | MW
| 4 | Evening peak Generation : |  |  | 13432 | MW at | 20:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 431 | MW
| 5 | Total Energy Generation : |  | 272.9502 | MKWHr | By Solar | 1.1631 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
|  | By Gas : | 130.9561 | MKWHr |  | By Oil: | 75.7144 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 35.968 | MKWHr |  | By Hydro: | 3.6155 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 3725 | MW | Dhaka | 4795.32 | 4735.32 |  | 60 |  | 18:00 |  | 110
|  |  |  | For Plants S/D or M/C prob = |  |  | 2838 | MW | Chittagong | 1233.76 | 1233.76 |  | 0 |  | 19:00 |  | 388
|  |  |  | Total = |  |  | 6563 | MW | Khulna | 1522 | 1522 |  | 0 |  | 19:30 |  | 301
| 7 | Total Gas Supplied : |  |  | 1063.5 | MMCFD |  |  | Rajshahi | 1349.2 | 1349.2 |  | 0 |  | 20:00 |  | 431
| 8 | Fuel Cost : | i) Gas : | Taka | 149368898.92 | ii) Oil : | Taka | 1148424829.19 | Comilla | 1255 | 1184 |  | 71 |  | 21:00 |  | 480
|  |  | iii) Coal : |  | 295592113.16 | Total | Taka | 1593385841.27 | Mymensingh | 1174 | 874 |  | 300 |  | 22:00 |  | 388.9047
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0 | MKWHr. | Sylhet | 613 | 613 |  | 0 |  | 23:00 |  | 577.8275
|  | ii) During Peak Demand : |  |  | 615 | MW (E to W) at | 20:00 | hrs | Barisal | 367.84 | 367.84 |  | 0 |  | 24:00 |  | 927.1045
|  | iii) Maximum : |  |  | 515 | MW at | 21:00 | hrs | Rangpur | 926 | 926 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 34.3° C |  |  | Total | 13236.12 | 12805.12 |  | 431
| B. |  | 2022-08-21 | (Today) |  |  |  | Sunday |  |  | Probable max. temperature in Dhaka |  |  | 35.6° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 14200 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 518 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 13638 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 12200 | MW
| 4 | Reserve(Generation end) |  |  |  | - | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 287.5718 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 10977 | MW at | 8:00 | 100 | 58 | 83 | 82 | 66 | 60 | 22 | 0 | 47
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.9302 | MKWHr. | ii) HVDC Flow at Peak Time |  | 905 | MW at | 20:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.6029 | MKWHr. | iii) Maximum HVDC Flow : |  | 908 | MW at | 1:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 95.55 |  | (b) Today: | 95.3 |  | (c) Rule Curve: |  | 95.4
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2022-08-20
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 200 | 91 | 0 | 405 | 312 |  | 0 | 450 | 0 | 7 | 0 | 30 | 175 | 0 | 0 | 8 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 0 | 33 | 33 | 24 | 0 | 81 | 65 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 51 | 10 | 12 | 6 | 13 | 42 | 0 | 0 | 0 | 310 | 310 | 208 | 55 | 143 | 37 | 56 | 0 | 51 | 0 | 45 | 0 | 21 | 8 | 25 | 14 | 144 | 158 | 0 | 22 | 0 | 43 | 30 | 5 | 5 | 0 | 0 | 63 | 81 | 0 | 207 | 0 | 0 | 10 | 320 | 0 | 0 | 192 | 115 | 302 | 70 | 48 | 70 | 17 | 0 | 10 | 136 | 100 | 402 | 48 | 52 | 17 | 0 | 52 | 36 | 55 | 17 | 15 | 10 | 398 | 0 | 0 | 54 | 90 | 0 | 35 | 0 | 96 | 55 | 0 | 0 | 0 |  | 908 | 0 | 175 | 0 | 0 | 226 | 0 | 0 | 21 | 60 | 0 | 151 | 28 | 16 | 0 | 0 | 0 | 30 | 37 | 73 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 81 | 0 | 240 | 0 | 0 | 183 | 0 | 0 | 213 | 0 | 48 | 155 | 0 | 360 | 0 | 76 | 50 | 15 | 56 | 0 | 0 | 55 | 1140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 7330 | 4429 | 11759 | 4248 | 908 | 1887 | 758 | 1409 | 1461 | 146 | 439 | 572 | 144 | 0 | 867.2021 | 95.59
2:00 | 0 | 0 | 0 | 180 | 200 | 91 | 0 | 411 | 318 |  | 0 | 450 | 0 | 8 | 0 | 30 | 180 | 0 | 0 | 8 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 0 | 33 | 33 | 24 | 0 | 82 | 65 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 34 | 10 | 12 | 6 | 13 | 42 | 0 | 0 | 0 | 310 | 310 | 210 | 55 | 142 | 37 | 56 | 0 | 51 | 0 | 37 | 0 | 21 | 8 | 25 | 14 | 152 | 158 | 0 | 22 | 0 | 43 | 30 | 5 | 5 | 0 | 0 | 64 | 70 | 0 | 207 | 0 | 0 | 10 | 300 | 0 | 0 | 190 | 112 | 303 | 70 | 48 | 70 | 17 | 0 | 10 | 135 | 100 | 402 | 48 | 52 | 17 | 0 | 52 | 36 | 55 | 17 | 13 | 10 | 400 | 0 | 0 | 54 | 90 | 0 | 30 | 0 | 96 | 55 | 0 | 0 | 0 |  | 907 | 0 | 180 | 0 | 0 | 227 | 0 | 0 | 21 | 60 | 0 | 152 | 26 | 16 | 0 | 0 | 0 | 31 | 37 | 52 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 80 | 0 | 240 | 0 | 0 | 183 | 0 | 0 | 217 | 0 | 70 | 156 | 0 | 366 | 0 | 100 | 50 | 15 | 56 | 0 | 0 | 55 | 1140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 7315 | 4470 | 11785 | 4292 | 907 | 1867 | 803 | 1399 | 1460 | 147 | 444 | 531 | 152 | 0 | 474.6111 | 95.59
3:00 | 0 | 0 | 0 | 180 | 200 | 91 | 0 | 410 | 318 |  | 0 | 450 | 0 | 7 | 0 | 30 | 182 | 0 | 0 | 8 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 27 | 33 | 33 | 24 | 0 | 83 | 65 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 34 | 10 | 12 | 6 | 13 | 42 | 0 | 0 | 0 | 310 | 310 | 208 | 55 | 143 | 37 | 56 | 0 | 51 | 0 | 35 | 0 | 21 | 8 | 25 | 14 | 148 | 157 | 0 | 22 | 0 | 43 | 30 | 5 | 5 | 0 | 0 | 63 | 40 | 0 | 207 | 0 | 0 | 10 | 290 | 0 | 0 | 190 | 112 | 301 | 70 | 48 | 70 | 17 | 0 | 10 | 136 | 100 | 403 | 49 | 52 | 17 | 0 | 52 | 36 | 55 | 17 | 9 | 10 | 400 | 0 | 0 | 54 | 90 | 0 | 17 | 0 | 97 | 55 | 0 | 0 | 0 |  | 908 | 0 | 180 | 0 | 0 | 226 | 0 | 0 | 10 | 58 | 0 | 151 | 25 | 16 | 0 | 0 | 0 | 31 | 37 | 45 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 80 | 0 | 240 | 0 | 0 | 182 | 0 | 0 | 216 | 0 | 0 | 157 | 0 | 361 | 0 | 10 | 50 | 15 | 56 | 0 | 0 | 55 | 1140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 7279 | 4282 | 11561 | 4317 | 908 | 1821 | 641 | 1384 | 1460 | 148 | 442 | 508 | 148 | 0 | 404.5714 | 95.58
4:00 | 0 | 0 | 0 | 180 | 200 | 91 | 0 | 409 | 330 |  | 0 | 450 | 0 | 8 | 0 | 30 | 182 | 0 | 0 | 8 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 27 | 33 | 33 | 24 | 0 | 83 | 65 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 34 | 10 | 12 | 6 | 13 | 42 | 0 | 0 | 0 | 310 | 310 | 209 | 55 | 143 | 37 | 56 | 0 | 51 | 0 | 43 | 0 | 21 | 8 | 33 | 14 | 146 | 157 | 0 | 22 | 0 | 43 | 30 | 5 | 5 | 0 | 0 | 64 | 30 | 0 | 207 | 0 | 0 | 10 | 280 | 0 | 0 | 40 | 112 | 225 | 70 | 48 | 70 | 17 | 0 | 10 | 136 | 100 | 403 | 49 | 52 | 17 | 0 | 52 | 36 | 55 | 17 | 9 | 10 | 400 | 0 | 0 | 54 | 90 | 0 | 17 | 0 | 96 | 55 | 0 | 0 | 0 |  | 907 | 0 | 180 | 0 | 0 | 227 | 0 | 0 | 10 | 60 | 0 | 150 | 23 | 16 | 0 | 0 | 0 | 31 | 35 | 45 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 80 | 0 | 240 | 0 | 0 | 183 | 0 | 0 | 216 | 0 | 0 | 157 | 0 | 360 | 0 | 0 | 50 | 15 | 56 | 0 | 0 | 55 | 1080 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 7060 | 4209 | 11269 | 4326 | 907 | 1810 | 405 | 1384 | 1400 | 148 | 443 | 516 | 146 | 0 | 305.0413 | 95.57
5:00 | 0 | 0 | 0 | 180 | 200 | 91 | 0 | 413 | 337 |  | 0 | 450 | 0 | 8 | 0 | 30 | 182 | 0 | 0 | 8 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 27 | 33 | 33 | 24 | 0 | 83 | 65 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 34 | 10 | 12 | 6 | 13 | 42 | 0 | 0 | 0 | 345 | 340 | 206 | 55 | 143 | 37 | 56 | 0 | 51 | 0 | 44 | 0 | 21 | 8 | 33 | 14 | 142 | 154 | 0 | 22 | 0 | 43 | 30 | 5 | 5 | 0 | 0 | 64 | 20 | 0 | 207 | 0 | 0 | 10 | 310 | 0 | 0 | 20 | 112 | 201 | 70 | 48 | 0 | 17 | 0 | 10 | 136 | 100 | 403 | 49 | 52 | 17 | 0 | 52 | 36 | 55 | 17 | 9 | 10 | 394 | 0 | 0 | 54 | 90 | 0 | 17 | 0 | 80 | 55 | 0 | 0 | 0 |  | 906 | 0 | 180 | 0 | 0 | 218 | 0 | 0 | 10 | 60 | 0 | 149 | 23 | 16 | 0 | 0 | 0 | 31 | 35 | 45 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 80 | 0 | 240 | 0 | 0 | 183 | 0 | 0 | 180 | 0 | 0 | 157 | 0 | 365 | 0 | 0 | 50 | 15 | 56 | 0 | 0 | 55 | 1080 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 7011 | 4167 | 11178 | 4382 | 906 | 1842 | 291 | 1368 | 1400 | 148 | 398 | 481 | 142 | 0 | 204.5896 | 95.56
6:00 | 0 | 0 | 0 | 180 | 200 | 91 | 0 | 414 | 338 |  | 0 | 450 | 0 | 7 | 0 | 30 | 182 | 0 | 0 | 8 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 27 | 33 | 33 | 24 | 0 | 83 | 65 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 8 | 26 | 34 | 10 | 12 | 6 | 13 | 38 | 0 | 0 | 0 | 310 | 310 | 211 | 55 | 144 | 36 | 56 | 0 | 51 | 0 | 43 | 0 | 21 | 8 | 33 | 14 | 126 | 159 | 0 | 22 | 0 | 43 | 30 | 5 | 5 | 0 | 0 | 64 | 20 | 0 | 207 | 0 | 0 | 10 | 300 | 0 | 0 | 0 | 112 | 165 | 50 | 48 | 0 | 18 | 1 | 10 | 120 | 100 | 402 | 49 | 52 | 17 | 0 | 52 | 36 | 45 | 17 | 9 | 10 | 400 | 0 | 2 | 54 | 90 | 0 | 17 | 1 | 80 | 55 | 0 | 0 | 0 |  | 907 | 0 | 180 | 0 | 0 | 190 | 0 | 0 | 0 | 60 | 0 | 147 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 80 | 0 | 240 | 0 | 0 | 183 | 0 | 0 | 150 | 0 | 0 | 157 | 0 | 361 | 0 | 0 | 50 | 15 | 56 | 0 | 0 | 55 | 1070 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 |  | 6830 | 4017 | 10847 | 4331 | 907 | 1822 | 215 | 1338 | 1390 | 148 | 340 | 374 | 126 | 6 | 141.001 | 95.55
7:00 | 0 | 0 | 0 | 180 | 200 | 91 | 0 | 413 | 338 |  | 0 | 200 | 0 | 8 | 0 | 30 | 182 | 0 | 0 | 8 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 27 | 33 | 33 | 24 | 0 | 82 | 65 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 11 | 26 | 17 | 10 | 12 | 6 | 13 | 36 | 0 | 0 | 0 | 315 | 310 | 209 | 55 | 145 | 33 | 56 | 0 | 51 | 0 | 45 | 0 | 21 | 8 | 33 | 12 | 124 | 157 | 0 | 22 | 0 | 43 | 30 | 5 | 5 | 0 | 0 | 62 | 20 | 0 | 207 | 0 | 0 | 10 | 300 | 0 | 0 | 0 | 112 | 166 | 50 | 48 | 0 | 17 | 3 | 10 | 120 | 100 | 403 | 49 | 52 | 17 | 1 | 52 | 36 | 55 | 17 | 9 | 10 | 394 | 17 | 13 | 35 | 90 | 0 | 17 | 3 | 79 | 55 | 0 | 0 | 0 |  | 908 | 0 | 180 | 0 | 0 | 190 | 0 | 0 | 0 | 60 | 0 | 149 | 19 | 16 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 79 | 0 | 250 | 0 | 0 | 182 | 0 | 0 | 130 | 0 | 0 | 157 | 0 | 363 | 0 | 0 | 50 | 15 | 56 | 0 | 1 | 55 | 1030 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 |  | 6576 | 3984 | 10560 | 4321 | 908 | 1571 | 216 | 1348 | 1359 | 147 | 320 | 339 | 124 | 37 | 129.0205 | 95.55
8:00 | 0 | 0 | 0 | 180 | 200 | 91 | 0 | 414 | 331 |  | 0 | 180 | 0 | 7 | 0 | 30 | 181 | 0 | 0 | 8 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 26 | 22 | 25 | 27 | 33 | 33 | 24 | 0 | 83 | 65 | 110 | 0 | 16 | 0 | 0 | 0 | 0 |  | 12 | 26 | 17 | 10 | 12 | 6 | 13 | 10 | 0 | 0 | 0 | 320 | 315 | 207 | 55 | 146 | 33 | 55 | 0 | 51 | 0 | 45 | 0 | 21 | 8 | 33 | 12 | 130 | 157 | 0 | 22 | 1 | 43 | 30 | 5 | 5 | 0 | 0 | 61 | 20 | 0 | 207 | 0 | 0 | 10 | 290 | 0 | 0 | 0 | 112 | 85 | 25 | 76 | 0 | 17 | 7 | 10 | 120 | 100 | 403 | 68 | 52 | 17 | 1 | 120 | 36 | 55 | 17 | 9 | 10 | 394 | 17 | 12 | 35 | 90 | 0 | 17 | 13 | 78 | 55 | 0 | 0 | 0 |  | 907 | 0 | 170 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 150 | 18 | 16 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 80 | 0 | 250 | 0 | 0 | 183 | 0 | 0 | 130 | 0 | 0 | 156 | 0 | 342 | 0 | 0 | 50 | 15 | 56 | 0 | 0 | 55 | 1030 | 0 | 0 | 0 | 2 | 58 | 0 | 0 | 0 | 0 |  | 6566 | 3936 | 10502 | 4320 | 907 | 1485 | 110 | 1479 | 1360 | 148 | 320 | 279 | 130 | 94 | #REF! | 95.54
9:00 | 0 | 0 | 0 | 180 | 200 | 88 | 0 | 410 | 327 |  | 0 | 210 | 0 | 8 | 0 | 30 | 181 | 0 | 0 | 8 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 35 | 22 | 25 | 24 | 33 | 33 | 24 | 0 | 83 | 65 | 110 | 0 | 16 | 0 | 0 | 0 | 0 |  | 12 | 26 | 17 | 10 | 12 | 6 | 13 | 2 | 0 | 0 | 0 | 325 | 310 | 207 | 55 | 145 | 36 | 55 | 0 | 51 | 0 | 44 | 0 | 21 | 0 | 28 | 12 | 136 | 155 | 0 | 22 | 2 | 43 | 30 | 5 | 5 | 0 | 0 | 60 | 20 | 0 | 207 | 0 | 0 | 10 | 300 | 0 | 0 | 30 | 112 | 120 | 25 | 77 | 0 | 18 | 15 | 10 | 127 | 100 | 404 | 68 | 52 | 17 | 4 | 121 | 36 | 55 | 17 | 9 | 10 | 392 | 17 | 27 | 35 | 90 | 0 | 17 | 10 | 83 | 55 | 0 | 0 | 0 |  | 907 | 0 | 165 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 150 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 81 | 0 | 251 | 0 | 0 | 182 | 0 | 0 | 130 | 0 | 0 | 152 | 0 | 322 | 17 | 0 | 50 | 15 | 56 | 0 | 0 | 55 | 1010 | 0 | 0 | 0 | 2 | 52 | 0 | 0 | 0 | 0 |  | 6688 | 3897 | 10585 | 4288 | 907 | 1488 | 175 | 1521 | 1342 | 148 | 320 | 278 | 136 | 112 | #REF! | 95.53
10:00 | 0 | 0 | 0 | 180 | 200 | 88 | 0 | 407 | 327 |  | 0 | 260 | 0 | 11 | 0 | 30 | 180 | 0 | 0 | 8 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 35 | 22 | 25 | 24 | 33 | 33 | 24 | 0 | 80 | 65 | 108 | 0 | 16 | 0 | 0 | 0 | 0 |  | 12 | 26 | 17 | 10 | 12 | 6 | 13 | 6 | 0 | 0 | 0 | 310 | 335 | 204 | 55 | 143 | 33 | 53 | 0 | 43 | 0 | 44 | 0 | 21 | 8 | 25 | 12 | 136 | 127 | 0 | 22 | 1 | 42 | 30 | 5 | 5 | 0 | 0 | 60 | 20 | 0 | 207 | 0 | 0 | 10 | 310 | 0 | 0 | 30 | 112 | 204 | 70 | 77 | 0 | 17 | 7 | 10 | 138 | 100 | 402 | 68 | 52 | 17 | 4 | 124 | 36 | 55 | 17 | 9 | 10 | 385 | 0 | 46 | 35 | 90 | 0 | 17 | 32 | 96 | 55 | 0 | 0 | 0 |  | 908 | 0 | 150 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 150 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 11 | 80 | 0 | 251 | 0 | 0 | 177 | 0 | 0 | 130 | 0 | 0 | 149 | 0 | 312 | 17 | 0 | 50 | 15 | 56 | 0 | 3 | 55 | 1010 | 0 | 0 | 0 | 3 | 21 | 0 | 0 | 0 | 0 |  | 6875 | 3814 | 10689 | 4228 | 908 | 1529 | 304 | 1533 | 1341 | 145 | 300 | 278 | 136 | 117 | #REF! | 95.52
11:00 | 0 | 0 | 0 | 180 | 200 | 84 | 0 | 409 | 328 |  | 0 | 260 | 0 | 9 | 0 | 30 | 180 | 0 | 0 | 8 | 8 | 45 | 0 | 0 | 0 | 0 | 17 | 0 | 35 | 0 | 25 | 27 | 33 | 32 | 24 | 0 | 80 | 65 | 108 | 0 | 16 | 0 | 0 | 0 | 0 |  | 12 | 20 | 17 | 10 | 12 | 3 | 11 | 2 | 0 | 0 | 0 | 310 | 320 | 204 | 55 | 141 | 35 | 51 | 0 | 43 | 0 | 44 | 0 | 21 | 8 | 22 | 12 | 142 | 128 | 0 | 22 | 3 | 42 | 30 | 5 | 5 | 0 | 0 | 60 | 20 | 0 | 207 | 0 | 0 | 10 | 280 | 0 | 0 | 50 | 112 | 250 | 70 | 77 | 0 | 17 | 13 | 10 | 158 | 102 | 395 | 68 | 52 | 17 | 5 | 124 | 36 | 55 | 17 | 9 | 10 | 380 | 0 | 36 | 40 | 90 | 0 | 17 | 31 | 96 | 55 | 0 | 0 | 0 |  | 907 | 0 | 155 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 149 | 18 | 16 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 11 | 80 | 0 | 251 | 0 | 0 | 177 | 0 | 0 | 130 | 0 | 0 | 148 | 0 | 315 | 17 | 0 | 50 | 15 | 52 | 0 | 7 | 55 | 980 | 0 | 0 | 0 | 4 | 30 | 0 | 0 | 0 | 0 |  | 6902 | 3743 | 10645 | 4182 | 907 | 1494 | 370 | 1551 | 1311 | 145 | 250 | 294 | 142 | 129 | #REF! | 95.52
12:00 | 0 | 0 | 0 | 180 | 200 | 86 | 0 | 406 | 328 |  | 0 | 260 | 0 | 8 | 0 | 30 | 185 | 0 | 0 | 8 | 8 | 45 | 0 | 0 | 0 | 0 | 17 | 0 | 35 | 0 | 25 | 27 | 33 | 32 | 24 | 0 | 86 | 70 | 108 | 0 | 16 | 0 | 0 | 0 | 0 |  | 12 | 9 | 17 | 10 | 12 | 6 | 11 | 2 | 0 | 0 | 0 | 290 | 330 | 204 | 55 | 143 | 35 | 49 | 0 | 43 | 0 | 44 | 0 | 21 | 8 | 22 | 12 | 152 | 113 | 0 | 22 | 2 | 43 | 30 | 0 | 0 | 0 | 0 | 59 | 10 | 0 | 207 | 0 | 0 | 9 | 300 | 0 | 0 | 150 | 188 | 300 | 70 | 77 | 0 | 17 | 13 | 10 | 200 | 105 | 402 | 68 | 52 | 34 | 5 | 124 | 36 | 55 | 17 | 9 | 10 | 378 | 0 | 56 | 50 | 90 | 0 | 19 | 16 | 96 | 55 | 0 | 0 | 0 |  | 907 | 0 | 150 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 148 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 11 | 82 | 0 | 251 | 0 | 0 | 174 | 0 | 0 | 130 | 0 | 0 | 148 | 0 | 291 | 17 | 18 | 50 | 32 | 56 | 0 | 6 | 55 | 960 | 0 | 0 | 0 | 2 | 10 | 0 | 0 | 0 | 0 |  | 7201 | 3723 | 10924 | 4157 | 907 | 1470 | 538 | 1708 | 1293 | 156 | 280 | 283 | 152 | 110 | #REF! | 95.51
13:00 | 0 | 0 | 0 | 180 | 200 | 86 | 0 | 406 | 323 |  | 0 | 260 | 0 | 8 | 0 | 30 | 180 | 0 | 0 | 8 | 8 | 45 | 0 | 0 | 0 | 0 | 17 | 0 | 35 | 22 | 25 | 27 | 33 | 32 | 24 | 0 | 86 | 70 | 108 | 0 | 16 | 0 | 0 | 0 | 0 |  | 12 | 25 | 17 | 10 | 12 | 6 | 11 | 2 | 0 | 0 | 0 | 315 | 305 | 205 | 55 | 142 | 35 | 51 | 0 | 43 | 0 | 40 | 0 | 21 | 8 | 22 | 12 | 160 | 113 | 0 | 22 | 1 | 43 | 30 | 0 | 0 | 0 | 0 | 60 | 10 | 0 | 208 | 0 | 0 | 10 | 300 | 0 | 0 | 170 | 194 | 300 | 70 | 77 | 0 | 17 | 14 | 10 | 200 | 113 | 404 | 68 | 52 | 87 | 5 | 124 | 36 | 81 | 17 | 9 | 10 | 385 | 0 | 28 | 108 | 90 | 0 | 35 | 29 | 96 | 55 | 0 | 0 | 0 |  | 907 | 0 | 150 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 147 | 21 | 0 | 0 | 0 | 0 | 0 | 4 | 38 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 11 | 82 | 0 | 250 | 0 | 0 | 174 | 0 | 0 | 170 | 0 | 0 | 145 | 0 | 290 | 17 | 20 | 50 | 32 | 56 | 0 | 7 | 55 | 1030 | 0 | 0 | 0 | 4 | 44 | 0 | 0 | 0 | 0 |  | 7419 | 3872 | 11291 | 4181 | 907 | 1469 | 560 | 1875 | 1362 | 156 | 320 | 339 | 160 | 132 | 377 | 95.5
14:00 | 0 | 0 | 0 | 180 | 0 | 89 | 0 | 400 | 322 |  | 0 | 260 | 0 | 8 | 0 | 30 | 183 | 0 | 0 | 7 | 8 | 45 | 0 | 0 | 0 | 0 | 17 | 0 | 35 | 22 | 25 | 27 | 33 | 32 | 24 | 0 | 86 | 70 | 108 | 0 | 17 | 0 | 0 | 0 | 0 |  | 12 | 36 | 17 | 10 | 12 | 25 | 11 | 2 | 0 | 0 | 0 | 325 | 310 | 189 | 55 | 145 | 35 | 51 | 0 | 43 | 0 | 43 | 0 | 21 | 8 | 25 | 12 | 150 | 102 | 0 | 22 | 2 | 43 | 30 | 0 | 0 | 0 | 0 | 58 | 10 | 0 | 207 | 0 | 0 | 8 | 315 | 0 | 0 | 170 | 130 | 300 | 70 | 80 | 0 | 17 | 8 | 10 | 200 | 120 | 375 | 68 | 52 | 87 | 1 | 158 | 36 | 109 | 17 | 9 | 10 | 366 | 4 | 16 | 108 | 90 | 0 | 35 | 14 | 96 | 55 | 0 | 0 | 0 |  | 908 | 0 | 145 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 137 | 21 | 0 | 0 | 0 | 0 | 32 | 5 | 38 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 11 | 81 | 0 | 250 | 0 | 0 | 173 | 0 | 0 | 160 | 0 | 0 | 142 | 0 | 275 | 17 | 63 | 50 | 32 | 56 | 0 | 7 | 55 | 1090 | 0 | 0 | 0 | 5 | 5 | 0 | 0 | 0 | 0 |  | 7173 | 3926 | 11099 | 3902 | 908 | 1469 | 603 | 1906 | 1421 | 156 | 310 | 376 | 150 | 58 | 646 | 95.48
15:00 | 0 | 0 | 0 | 180 | 20 | 89 | 0 | 397 | 316 |  | 0 | 260 | 0 | 7 | 0 | 30 | 184 | 0 | 0 | 7 | 8 | 45 | 0 | 0 | 0 | 0 | 17 | 17 | 35 | 22 | 25 | 27 | 33 | 32 | 24 | 0 | 86 | 70 | 108 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 43 | 17 | 10 | 12 | 25 | 11 | 10 | 0 | 0 | 0 | 335 | 325 | 201 | 55 | 145 | 31 | 50 | 0 | 43 | 0 | 43 | 0 | 21 | 8 | 33 | 12 | 148 | 101 | 0 | 22 | 2 | 43 | 30 | 0 | 0 | 0 | 0 | 59 | 10 | 0 | 207 | 0 | 0 | 10 | 300 | 0 | 0 | 170 | 112 | 300 | 70 | 78 | 0 | 17 | 15 | 10 | 200 | 122 | 382 | 68 | 52 | 87 | 4 | 160 | 36 | 110 | 17 | 8 | 10 | 377 | 0 | 40 | 108 | 90 | 0 | 35 | 6 | 96 | 55 | 0 | 0 | 0 |  | 907 | 0 | 135 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 146 | 23 | 0 | 0 | 0 | 0 | 32 | 5 | 38 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 11 | 80 | 0 | 250 | 0 | 0 | 170 | 0 | 0 | 170 | 0 | 17 | 140 | 0 | 283 | 17 | 141 | 50 | 32 | 50 | 0 | 6 | 55 | 1100 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 |  | 7273 | 4083 | 11356 | 3973 | 907 | 1467 | 698 | 1904 | 1430 | 156 | 350 | 393 | 148 | 100 | 317 | 95.47
16:00 | 0 | 0 | 0 | 180 | 70 | 89 | 0 | 403 | 287 |  | 0 | 260 | 0 | 8 | 0 | 30 | 165 | 0 | 27 | 7 | 8 | 45 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 25 | 27 | 33 | 32 | 24 | 0 | 88 | 70 | 108 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 40 | 17 | 10 | 11 | 25 | 11 | 4 | 0 | 0 | 0 | 310 | 305 | 206 | 55 | 143 | 31 | 51 | 0 | 43 | 0 | 36 | 0 | 21 | 8 | 33 | 13 | 154 | 117 | 0 | 22 | 0 | 42 | 30 | 0 | 0 | 0 | 0 | 61 | 10 | 0 | 207 | 0 | 0 | 10 | 295 | 0 | 0 | 140 | 112 | 249 | 70 | 82 | 0 | 17 | 10 | 10 | 200 | 123 | 400 | 68 | 52 | 87 | 2 | 158 | 43 | 110 | 17 | 9 | 10 | 390 | 0 | 6 | 115 | 90 | 0 | 35 | 4 | 96 | 55 | 0 | 0 | 0 |  | 908 | 0 | 140 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 147 | 21 | 16 | 0 | 0 | 0 | 32 | 12 | 38 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 11 | 81 | 0 | 250 | 0 | 0 | 169 | 0 | 0 | 150 | 0 | 20 | 141 | 0 | 282 | 17 | 100 | 50 | 32 | 56 | 0 | 4 | 55 | 1080 | 0 | 0 | 0 | 2 | 59 | 0 | 0 | 0 | 0 |  | 7213 | 4051 | 11264 | 4050 | 908 | 1425 | 579 | 1962 | 1411 | 158 | 310 | 370 | 154 | 87 | 310 | 95.46
17:00 | 0 | 0 | 0 | 180 | 120 | 92 | 0 | 406 | 277 |  | 0 | 260 | 0 | 7 | 0 | 30 | 90 | 0 | 34 | 7 | 8 | 45 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 22 | 25 | 27 | 33 | 32 | 24 | 0 | 88 | 70 | 108 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 43 | 17 | 10 | 11 | 27 | 11 | 6 | 0 | 0 | 0 | 310 | 305 | 206 | 55 | 144 | 28 | 51 | 0 | 43 | 0 | 42 | 0 | 21 | 8 | 33 | 17 | 152 | 115 | 0 | 22 | 0 | 42 | 30 | 0 | 0 | 0 | 0 | 60 | 10 | 0 | 207 | 0 | 0 | 10 | 290 | 0 | 0 | 106 | 115 | 180 | 70 | 83 | 0 | 24 | 2 | 10 | 200 | 117 | 404 | 68 | 52 | 87 | 1 | 158 | 54 | 110 | 34 | 9 | 10 | 386 | 0 | 17 | 162 | 90 | 0 | 35 | 5 | 85 | 55 | 0 | 0 | 0 |  | 907 | 0 | 140 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 148 | 20 | 16 | 0 | 0 | 0 | 32 | 36 | 38 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 11 | 81 | 0 | 250 | 0 | 0 | 169 | 0 | 0 | 130 | 0 | 10 | 143 | 0 | 280 | 17 | 80 | 94 | 32 | 80 | 0 | 2 | 95 | 1080 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 |  | 7184 | 4073 | 11257 | 4037 | 907 | 1412 | 446 | 2160 | 1411 | 158 | 290 | 383 | 152 | 31 | 224 | 95.45
18:00 | 0 | 0 | 0 | 180 | 250 | 92 | 0 | 412 | 267 |  | 0 | 260 | 0 | 8 | 0 | 30 | 94 | 0 | 34 | 7 | 8 | 110 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 27 | 33 | 32 | 26 | 0 | 88 | 70 | 108 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 43 | 34 | 10 | 24 | 38 | 11 | 9 | 0 | 0 | 0 | 310 | 305 | 206 | 55 | 143 | 34 | 51 | 0 | 43 | 0 | 43 | 0 | 21 | 9 | 33 | 17 | 148 | 129 | 0 | 22 | 0 | 42 | 30 | 0 | 0 | 0 | 0 | 60 | 10 | 0 | 207 | 0 | 0 | 10 | 270 | 0 | 0 | 10 | 188 | 12 | 25 | 107 | 0 | 142 | 0 | 10 | 155 | 123 | 370 | 68 | 105 | 87 | 0 | 158 | 54 | 110 | 34 | 21 | 10 | 393 | 0 | 1 | 162 | 105 | 0 | 35 | 1 | 55 | 55 | 0 | 0 | 0 |  | 906 | 0 | 145 | 0 | 0 | 160 | 0 | 0 | 0 | 11 | 0 | 150 | 17 | 16 | 0 | 0 | 0 | 32 | 37 | 38 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 11 | 79 | 0 | 250 | 0 | 0 | 170 | 0 | 0 | 130 | 0 | 0 | 145 | 0 | 250 | 17 | 10 | 94 | 67 | 91 | 0 | 1 | 95 | 1010 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 |  | 7327 | 3954 | 11281 | 4180 | 906 | 1354 | 57 | 2496 | 1339 | 158 | 290 | 478 | 148 | 5 | 110 | 95.44
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 300 | 92 | 0 | 405 | 267 |  | 0 | 260 | 0 | 7 | 0 | 30 | 93 | 0 | 34 | 7 | 8 | 119 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 19 | 33 | 32 | 40 | 0 | 88 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 43 | 51 | 10 | 81 | 38 | 11 | 16 | 0 | 0 | 0 | 310 | 305 | 206 | 55 | 143 | 39 | 52 | 0 | 43 | 0 | 47 | 1 | 22 | 10 | 33 | 18 | 158 | 127 | 0 | 22 | 0 | 44 | 30 | 5 | 3 | 0 | 0 | 55 | 81 | 0 | 207 | 0 | 0 | 10 | 290 | 8 | 0 | 193 | 240 | 299 | 90 | 113 | 0 | 149 | 0 | 10 | 162 | 132 | 403 | 68 | 105 | 87 | 0 | 175 | 54 | 110 | 34 | 27 | 10 | 390 | 10 | 0 | 162 | 108 | 0 | 35 | 0 | 70 | 55 | 0 | 0 | 0 |  | 906 | 0 | 155 | 0 | 16 | 227 | 0 | 0 | 37 | 52 | 0 | 150 | 27 | 32 | 0 | 0 | 0 | 32 | 37 | 82 | 0 | 0 | 25 | 8 | 33 | 21 | 0 | 11 | 83 | 0 | 250 | 0 | 0 | 174 | 0 | 0 | 150 | 0 | 27 | 149 | 0 | 305 | 20 | 64 | 94 | 67 | 91 | 0 | 0 | 95 | 1050 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 0 |  | 8287 | 4542 | 12829 | 4275 | 906 | 1527 | 673 | 2814 | 1383 | 158 | 377 | 708 | 158 | 0 | 388 | 95.41
19:30 | 0 | 0 | 0 | 180 | 300 | 93 | 0 | 405 | 256 |  | 0 | 260 | 0 | 8 | 0 | 30 | 92 | 0 | 34 | 7 | 8 | 118 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 27 | 33 | 32 | 40 | 0 | 87 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 43 | 51 | 10 | 94 | 38 | 11 | 18 | 0 | 0 | 0 | 345 | 330 | 203 | 55 | 143 | 37 | 52 | 0 | 51 | 0 | 47 | 8 | 22 | 10 | 33 | 18 | 164 | 127 | 0 | 22 | 0 | 43 | 30 | 5 | 5 | 0 | 0 | 59 | 81 | 0 | 193 | 0 | 0 | 10 | 320 | 8 | 0 | 195 | 240 | 300 | 90 | 113 | 0 | 149 | 0 | 10 | 200 | 136 | 403 | 68 | 105 | 87 | 0 | 178 | 54 | 110 | 34 | 29 | 10 | 380 | 17 | 0 | 162 | 108 | 0 | 35 | 0 | 97 | 55 | 0 | 0 | 0 |  | 906 | 0 | 155 | 0 | 16 | 223 | 0 | 0 | 51 | 61 | 0 | 146 | 27 | 32 | 0 | 0 | 0 | 32 | 37 | 82 | 0 | 0 | 32 | 8 | 33 | 21 | 0 | 11 | 80 | 0 | 250 | 0 | 0 | 175 | 0 | 0 | 197 | 0 | 93 | 149 | 0 | 310 | 35 | 170 | 94 | 67 | 84 | 0 | 0 | 95 | 1160 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 0 |  | 8469 | 4904 | 13373 | 4313 | 906 | 1564 | 848 | 2924 | 1490 | 157 | 420 | 784 | 164 | 0 | 301 | 0
20:00 | 0 | 0 | 0 | 180 | 300 | 93 | 0 | 409 | 257 |  | 0 | 260 | 0 | 8 | 0 | 30 | 93 | 0 | 35 | 7 | 8 | 119 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 27 | 33 | 32 | 40 | 0 | 86 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 43 | 51 | 10 | 94 | 38 | 11 | 25 | 0 | 0 | 0 | 310 | 305 | 206 | 73 | 144 | 40 | 54 | 0 | 51 | 0 | 47 | 8 | 22 | 10 | 33 | 18 | 156 | 127 | 0 | 22 | 0 | 43 | 20 | 5 | 5 | 0 | 0 | 62 | 81 | 0 | 193 | 0 | 0 | 10 | 295 | 8 | 0 | 195 | 243 | 300 | 91 | 106 | 91 | 149 | 0 | 10 | 200 | 138 | 405 | 68 | 105 | 87 | 0 | 181 | 54 | 110 | 34 | 29 | 10 | 391 | 17 | 0 | 162 | 108 | 0 | 35 | 0 | 96 | 55 | 0 | 0 | 0 |  | 905 | 0 | 155 | 0 | 16 | 225 | 0 | 0 | 40 | 64 | 0 | 150 | 28 | 32 | 0 | 0 | 0 | 32 | 40 | 82 | 0 | 0 | 32 | 8 | 32 | 21 | 0 | 11 | 81 | 0 | 251 | 0 | 0 | 174 | 0 | 0 | 196 | 0 | 92 | 148 | 0 | 316 | 35 | 172 | 94 | 67 | 91 | 0 | 0 | 95 | 1160 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 0 |  | 8515 | 4917 | 13432 | 4274 | 905 | 1574 | 941 | 2931 | 1492 | 156 | 421 | 778 | 156 | 0 | 431 | 95.42
21:00 | 0 | 0 | 0 | 180 | 300 | 90 | 0 | 410 | 257 |  | 0 | 260 | 0 | 8 | 0 | 30 | 93 | 0 | 35 | 7 | 8 | 119 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 22 | 25 | 27 | 33 | 32 | 40 | 0 | 81 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 43 | 51 | 10 | 94 | 38 | 11 | 28 | 0 | 0 | 0 | 310 | 305 | 206 | 92 | 143 | 37 | 55 | 0 | 51 | 0 | 46 | 8 | 22 | 10 | 33 | 20 | 166 | 127 | 0 | 22 | 0 | 43 | 20 | 5 | 5 | 0 | 0 | 62 | 81 | 0 | 193 | 0 | 0 | 10 | 300 | 8 | 0 | 194 | 243 | 300 | 92 | 107 | 91 | 149 | 0 | 10 | 200 | 142 | 404 | 68 | 105 | 87 | 0 | 181 | 54 | 110 | 34 | 29 | 10 | 390 | 17 | 0 | 162 | 94 | 0 | 35 | 0 | 97 | 55 | 0 | 0 | 0 |  | 906 | 0 | 160 | 0 | 16 | 225 | 0 | 0 | 27 | 58 | 0 | 150 | 28 | 32 | 0 | 0 | 0 | 32 | 40 | 82 | 0 | 0 | 32 | 8 | 32 | 21 | 0 | 11 | 80 | 0 | 251 | 0 | 0 | 174 | 0 | 0 | 210 | 0 | 93 | 150 | 0 | 317 | 35 | 165 | 94 | 67 | 92 | 0 | 0 | 95 | 1160 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 0 |  | 8514 | 4915 | 13429 | 4278 | 906 | 1600 | 935 | 2905 | 1491 | 151 | 435 | 772 | 166 | 0 | 480 | 95.41
22:00 | 0 | 0 | 0 | 180 | 300 | 90 | 0 | 411 | 263 |  | 0 | 260 | 0 | 7 | 0 | 30 | 95 | 0 | 0 | 7 | 8 | 120 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 27 | 33 | 32 | 40 | 0 | 83 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 43 | 51 | 10 | 94 | 38 | 11 | 35 | 0 | 0 | 0 | 315 | 310 | 208 | 102 | 143 | 39 | 55 | 0 | 51 | 0 | 44 | 8 | 22 | 10 | 33 | 20 | 168 | 127 | 0 | 22 | 0 | 43 | 30 | 5 | 5 | 0 | 0 | 62 | 81 | 0 | 193 | 0 | 0 | 10 | 305 | 8 | 0 | 194 | 243 | 300 | 92 | 106 | 91 | 149 | 0 | 10 | 200 | 145 | 403 | 68 | 105 | 87 | 0 | 181 | 54 | 110 | 34 | 29 | 10 | 392 | 17 | 0 | 162 | 100 | 0 | 35 | 0 | 97 | 55 | 0 | 0 | 0 |  | 907 | 0 | 160 | 0 | 16 | 227 | 0 | 0 | 20 | 58 | 0 | 150 | 30 | 32 | 0 | 0 | 0 | 32 | 37 | 82 | 0 | 0 | 32 | 8 | 32 | 21 | 0 | 11 | 80 | 0 | 250 | 0 | 0 | 175 | 0 | 0 | 214 | 0 | 93 | 150 | 0 | 326 | 35 | 165 | 94 | 67 | 92 | 0 | 0 | 95 | 1150 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 0 |  | 8565 | 4913 | 13478 | 4272 | 907 | 1639 | 935 | 2932 | 1480 | 153 | 441 | 765 | 168 | 0 | 388.9047 | 95.4
23:00 | 0 | 0 | 0 | 180 | 300 | 90 | 0 | 409 | 273 |  | 0 | 240 | 0 | 8 | 0 | 30 | 186 | 0 | 0 | 7 | 8 | 16 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 27 | 33 | 32 | 40 | 0 | 74 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 43 | 51 | 10 | 81 | 38 | 11 | 18 | 0 | 0 | 0 | 310 | 305 | 211 | 102 | 145 | 39 | 56 | 0 | 51 | 0 | 38 | 8 | 22 | 10 | 33 | 20 | 172 | 135 | 0 | 22 | 0 | 43 | 30 | 5 | 5 | 0 | 0 | 64 | 81 | 0 | 193 | 0 | 0 | 10 | 305 | 15 | 0 | 193 | 245 | 250 | 88 | 104 | 90 | 58 | 0 | 10 | 170 | 143 | 402 | 68 | 105 | 87 | 0 | 51 | 54 | 110 | 34 | 29 | 10 | 400 | 17 | 0 | 162 | 108 | 0 | 35 | 0 | 96 | 55 | 0 | 0 | 0 |  | 906 | 0 | 160 | 0 | 16 | 228 | 0 | 0 | 17 | 53 | 0 | 145 | 32 | 32 | 0 | 0 | 0 | 32 | 37 | 82 | 0 | 0 | 24 | 8 | 32 | 21 | 0 | 11 | 80 | 0 | 250 | 0 | 0 | 177 | 0 | 0 | 214 | 0 | 93 | 150 | 0 | 327 | 35 | 165 | 94 | 15 | 92 | 0 | 0 | 95 | 1160 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 0 |  | 8218 | 4855 | 13073 | 4377 | 906 | 1616 | 879 | 2622 | 1490 | 144 | 442 | 639 | 172 | 0 | 577.8275 | 95.39
24:00 | 0 | 0 | 0 | 180 | 300 | 90 | 0 | 416 | 253 |  | 0 | 240 | 0 | 7 | 0 | 30 | 188 | 0 | 0 | 7 | 8 | 16 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 27 | 33 | 33 | 24 | 0 | 80 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 40 | 51 | 10 | 10 | 27 | 11 | 22 | 0 | 0 | 0 | 340 | 330 | 207 | 102 | 144 | 37 | 56 | 0 | 51 | 0 | 38 | 8 | 22 | 10 | 33 | 20 | 164 | 135 | 0 | 22 | 0 | 43 | 30 | 5 | 5 | 0 | 0 | 62 | 78 | 0 | 193 | 0 | 0 | 10 | 265 | 15 | 0 | 150 | 155 | 181 | 70 | 38 | 70 | 17 | 0 | 10 | 170 | 137 | 401 | 39 | 52 | 74 | 0 | 52 | 41 | 110 | 17 | 29 | 10 | 392 | 16 | 0 | 144 | 108 | 0 | 35 | 0 | 96 | 55 | 0 | 0 | 0 |  | 907 | 0 | 160 | 0 | 16 | 226 | 0 | 0 | 17 | 52 | 0 | 145 | 32 | 32 | 0 | 0 | 0 | 32 | 37 | 82 | 0 | 0 | 16 | 0 | 13 | 22 | 0 | 11 | 80 | 0 | 250 | 0 | 0 | 176 | 0 | 0 | 218 | 0 | 10 | 152 | 0 | 317 | 17 | 50 | 50 | 15 | 56 | 0 | 0 | 55 | 1170 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 0 |  | 7606 | 4488 | 12094 | 4425 | 907 | 1548 | 531 | 2031 | 1500 | 150 | 444 | 612 | 164 | 0 | 927.1045 | 95.38
KWH | 0 | 0 | 0 | 4315500 | 4818345 | 2108681 | 0 | 9955330 | 7292000 |  | 0 | 6216100 | 0 | 202560 | 0 | 735992 | 3846438 | 0 | 232000 | 191 | 196992 | 1053120 | 0 | 0 | 0 | 0 | 603360 | 487189 | 697224 | 457056 | 600000 | 578160 | 785300 | 774700 | 675840 | 0 | 1991471 | 1624000 | 2600000 | 0 | 548811 | 0 | 0 | 0 | 0 |  | 292320 | 733824 | 763729 | 261600 | 694080 | 449280 | 285408 | 558240 | 0 | 0 | 0 | 7941100 | 7679000 | 4998000 | 1522181 | 3436270 | 835848 | 128880 | 0 | 1123951 | 0 | 1018264 | 45048 | 504180 | 185400 | 717600 | 332640 | 3602880 | 3151680 | 0 | 509148 | 13400 | 1022000 | 655304 | 90000 | 111528 | 0 | 0 | 1472256 | 990720 | 0 | 4980420 | 0 | 0 | 236880 | 7292000 | 124800 | 0 | 2794752 | 3665780 | 5644953 | 1567764 | 1776000 | 688242 | 1128816 | 102600 | 264000 | 3960960 | 2818545 | 9606000 | 1467600 | 1651200 | 1247854 | 31080 | 2669673 | 1056816 | 1966282 | 540360 | 364560 | 259200 | 932800 | 166080 | 339280 | 2331360 | 2266964 | 0 | 693000 | 198763 | 2180160 | 1334520 | 0 | 0 | 0 |  | 21930181 | 0 | 4020768 | 0 | 96960 | 4709760 | 0 | 0 | 215040 | 755584 | 0 | 3583217 | 542160 | 425184 | 0 | 0 | 0 | 512752 | 469946 | 1222576 | 0 | 0 | 135752 | 38400 | 133800 | 465360 | 0 | 263200 | 1886836 | 0 | 6032800 | 0 | 0 | 4483973 | 0 | 0 | 4349482 | 0 | 664320 | 3863109 | 0 | 7730509 | 352320 | 1603769 | 1655136 | 793296 | 1563571 | 0 | 45743 | 1645056 | 28048400 | 0 | 0 | 0 | 33360 | 398880 | 406848 | 0 | 0 | 0 |  | 167872183 | 105078048 | 272950231 | 94546950 | 21930181 | 36409190 | 12963800 | 46676988 | 35968036 | 3615471 | 9059242 | 7014387 | 3602880 | 1163106 | 0
Fuel Cost | 0 | 0 | 0 | 6430095 | 5396546.4 | 2804545.73 | 0 | 10453096.5 | 7875360 |  | 0 | 6775549 | 0 | 2264620.8 | 0 | 9751894 | 4308010.56 | 0 | 406000 | 2792.42 | 2771677.44 | 17071075.2 | 0 | 0 | 0 | 0 | 7674739.2 | 6577051.5 | 9349773.84 | 342792 | 450000 | 0 | 0 | 0 | 11496038.4 | 0 | 537697.17 | 438480 | 4914000 | 0 | 8973059.85 | 0 | 0 | 0 | 0 |  | 3814776 | 12240184.32 | 12998667.58 | 3534216 | 8800934.4 | 5198169.6 | 362468.16 | 1858939.2 | 0 | 0 | 0 | 8814621 | 8370110 | 5797680 | 1963613.49 | 4192249.4 | 944508.24 | 192031.2 | 0 | 1876998.17 | 0 | 17585419.28 | 605895.6 | 690726.6 | 139050 | 1255800 | 249480 | 25868678.4 | 3435331.2 | 0 | 692441.28 | 213596 | 1400140 | 865001.28 | 156600 | 192943.44 | 0 | 0 | 2856176.64 | 2258841.6 | 0 | 5030224.2 | 0 | 0 | 469022.4 | 7292000 | 93600 | 0 | 58578001.92 | 50037897 | 118318214.88 | 32405681.88 | 23940480 | 14225962.14 | 15634101.6 | 1199394 | 2724480 | 54106713.6 | 37402092.15 | 8837520 | 17846016 | 23876352 | 15785353.1 | 0 | 31341961.02 | 11508726.24 | 20901577.66 | 7332685.2 | 4699178.4 | 3053376 | 858176 | 2150736 | 4902596 | 29584958.4 | 25798050.32 | 0 | 9050580 | 2375217.85 | 32636995.2 | 17575628.4 | 0 | 0 | 0 |  | 65790543 | 0 | 4503260.16 | 0 | 1009353.6 | 77711040 | 0 | 0 | 3872870.4 | 13600512 | 0 | 4013203.04 | 1051790.4 | 4634505.6 | 0 | 0 | 0 | 8598851.04 | 8219355.54 | 19121088.64 | 0 | 0 | 2295566.32 | 523392 | 2257206 | 963295.2 | 0 | 199242.4 | 10962517.16 | 0 | 31913512 | 0 | 0 | 5201408.68 | 0 | 0 | 75941955.72 | 0 | 13937433.6 | 4481206.44 | 0 | 7653203.91 | 4735180.8 | 33631035.93 | 19580258.88 | 11463127.2 | 19857351.7 | 0 | 505460.15 | 19970979.84 | 252716084 | 0 | 0 | 0 | 377301.6 | 4678862.4 | 6236979.84 | 0 | 0 | 0 |  | 958064732.65 | 742208935.19 | 1700273667.84 | 105984165.18 | 65790543 | 43384733.74 | 271096330.35 | 605814706.8 | 295592113.16 | 976177.17 | 153652995.72 | 117860796.32 | 25868678.4 | 14252428 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 200 | 86 | 0 | 406 | 328 |  | 0 | 260 | 0 | 8 | 0 | 30 | 185 | 0 | 0 | 8 | 8 | 45 | 0 | 0 | 0 | 0 | 17 | 0 | 35 | 0 | 25 | 27 | 33 | 32 | 24 | 0 | 86 | 70 | 108 | 0 | 16 | 0 | 0 | 0 | 0 |  | 12 | 9 | 17 | 10 | 12 | 6 | 11 | 2 | 0 | 0 | 0 | 290 | 330 | 204 | 55 | 143 | 35 | 49 | 0 | 43 | 0 | 44 | 0 | 21 | 8 | 22 | 12 | 152 | 113 | 0 | 22 | 2 | 43 | 30 | 0 | 0 | 0 | 0 | 59 | 10 | 0 | 207 | 0 | 0 | 9 | 300 | 0 | 0 | 150 | 188 | 300 | 70 | 77 | 0 | 17 | 13 | 10 | 200 | 105 | 402 | 68 | 52 | 34 | 5 | 124 | 36 | 55 | 17 | 9 | 10 | 378 | 0 | 56 | 50 | 90 | 0 | 19 | 16 | 96 | 55 | 0 | 0 | 0 |  | 907 | 0 | 150 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 148 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 11 | 82 | 0 | 251 | 0 | 0 | 174 | 0 | 0 | 130 | 0 | 0 | 148 | 0 | 291 | 17 | 18 | 50 | 32 | 56 | 0 | 6 | 55 | 960 | 0 | 0 | 0 | 2 | 10 | 0 | 0 | 0 | 0 |  | 10924 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 300 | 93 | 0 | 409 | 257 | 0 | 0 | 260 | 0 | 8 | 0 | 30 | 93 | 0 | 35 | 7 | 8 | 119 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 27 | 33 | 32 | 40 | 0 | 86 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 12 | 43 | 51 | 10 | 94 | 38 | 11 | 25 | 0 | 0 | 0 | 310 | 305 | 206 | 73 | 144 | 40 | 54 | 0 | 51 | 0 | 47 | 8 | 22 | 10 | 33 | 18 | 156 | 127 | 0 | 22 | 0 | 43 | 20 | 5 | 5 | 0 | 0 | 62 | 81 | 0 | 193 | 0 | 0 | 10 | 295 | 8 | 0 | 195 | 243 | 300 | 91 | 106 | 91 | 149 | 0 | 10 | 200 | 138 | 405 | 68 | 105 | 87 | 0 | 181 | 54 | 110 | 34 | 29 | 10 | 391 | 17 | 0 | 162 | 108 | 0 | 35 | 0 | 96 | 55 | 0 | 0 | 0 |  | 905 | 0 | 155 | 0 | 16 | 225 | 0 | 0 | 40 | 64 | 0 | 150 | 28 | 32 | 0 | 0 | 0 | 32 | 40 | 82 | 0 | 0 | 32 | 8 | 32 | 21 | 0 | 11 | 81 | 0 | 251 | 0 | 0 | 174 | 0 | 0 | 196 | 0 | 92 | 148 | 0 | 316 | 35 | 172 | 94 | 67 | 91 | 0 | 0 | 95 | 1160 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 0 |  | 13432 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 300 | 87 | 0 | 412 | 275 | 0 | 0 | 240 | 0 | 8 | 0 | 30 | 200 | 0 | 0 | 8 | 8 | 120 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 27 | 33 | 33 | 40 | 0 | 80 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 12 | 40 | 51 | 10 | 93 | 37 | 11 | 25 | 0 | 0 | 0 | 320 | 310 | 210 | 36 | 145 | 35 | 55 | 0 | 51 | 0 | 45 | 8 | 21 | 10 | 33 | 18 | 165 | 100 | 0 | 22 | 0 | 43 | 30 | 5 | 5 | 0 | 0 | 62 | 80 | 0 | 193 | 0 | 0 | 10 | 310 | 0 | 0 | 200 | 285 | 300 | 0 | 180 | 90 | 149 | 0 | 10 | 200 | 140 | 400 | 68 | 105 | 85 | 0 | 178 | 54 | 110 | 114 | 26 | 10 | 400 | 17 | 0 | 162 | 108 | 0 | 35 |  | 96 | 55 |  |  |  |  | 904 | 0 | 155 | 0 | 16 | 225 | 0 | 0 | 43 | 50 | 0 | 151 | 25 | 48 | 0 | 0 | 0 | 32 | 40 | 80 | 0 | 0 | 32 | 8 | 32 | 21 | 0 | 11 | 80 | 0 | 250 | 0 | 0 | 180 | 0 | 0 | 220 | 0 | 95 | 150 | 0 | 305 | 35 | 170 | 94 | 67 | 90 | 0 | 0 | 95 | 1170 | 0 |  | 17 |  |  | 72
Forecast for Day | 0 | 0 | 0 | 180 | 300 | 87 | 0 | 412 | 275 | 0 | 0 | 240 | 0 | 8 | 0 | 30 | 200 | 0 | 0 | 8 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 35 | 22 | 25 | 27 | 33 | 33 | 24 | 0 | 80 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 12 | 40 | 17 | 10 | 12 | 25 | 11 | 10 | 0 | 0 | 0 | 300 | 300 | 210 | 36 | 145 | 35 | 55 | 0 | 43 | 0 | 37 | 8 | 21 | 10 | 33 | 18 | 143 | 85 | 0 | 22 | 1.6 | 43 | 30 | 0 | 0 | 0 | 0 | 62 | 10 | 0 | 193 | 0 | 0 | 10 | 300 | 0 | 0 | 200 | 110 | 230 | 0 | 80 | 70 | 16 | 20 | 10 | 100 | 140 | 400 | 48 | 52 | 69 | 5 | 85 | 36 | 110 | 17 | 9 | 10 | 400 | 17 | 50 | 35 | 108 | 0 | 35 | 30 | 96 | 55 |  |  |  |  | 904 | 0 | 155 | 0 | 16 | 225 | 0 | 0 | 20 | 40 | 0 | 151 | 16 | 32 | 0 | 0 | 0 | 32 | 0 | 35 | 0 | 0 | 0 | 8 | 0 | 21 | 0 | 11 | 80 | 0 | 250 | 0 | 0 | 180 | 0 | 0 | 220 | 0 | 50 | 150 | 0 | 305 | 17 | 120 | 50 | 15 | 55 | 0 | 8 | 55 | 1170 | 0 |  | 0 | 6 | 100 | 0
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 300 | 87 | 0 | 413 | 271 | 0 | 0 | 240 | 0 | 8 | 0 | 30 | 200 | 0 | 0 | 8 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 27 | 33 | 32 | 24 | 0 | 81 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 12 | 41 | 17 | 10 | 11 | 25 | 11 | 16 | 0 | 0 | 0 | 345 | 335 | 208 | 36 | 144 | 37 | 56 | 0 | 43 | 0 | 37 | 8 | 22 | 10 | 33 | 18 | 148 | 105 | 0 | 22 | 1 | 43 | 30 | 0 | 0 | 0 | 0 | 58 | 10 | 0 | 193 | 0 | 0 | 10 | 280 | 0 | 0 | 100 | 112 | 147 | 0 | 38 | 70 | 16 | 11 | 10 | 100 | 140 | 402 | 39 | 52 | 69 | 3 | 52 | 36 | 110 | 17 | 9 | 10 | 394 | 0 | 15 | 35 | 108 | 0 | 35 | 0 | 96 | 55 | 0 | 0 | 0 | 0 | 887 | 0 | 165 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 148 | 16 | 32 | 0 | 0 | 0 | 32 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 80 | 0 | 250 | 0 | 0 | 179 | 0 | 0 | 217 | 0 | 10 | 153 | 0 | 331 | 0 | 20 | 50 | 15 | 56 | 0 | 2 | 55 | 1060 | 0 | 0 | 0 | 1 | 39 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 75714417 |  | 0
75714417
| Minimum Generation |  | 10502 | 8:00
| Highest Generation |  | 13478 | 22:00
| Day Peak Generation |  | 10924 | 12:00
| Evening Peak Generation |  | 13432 | 20:00
| HVDC Max Flow |  | 908 | 1:00
| HVDC EvPeak Flow |  | 905 | 20:00
| Load factor L.F |  | 84.38% | [161 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2022-08-21
Till now the maximum generation is : - |  |  | 14782 | 21:00 | Hrs on | 2022-04-16
The Summary of Yesterday's |  | 2022-08-20 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 10924 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 10977 | MW
Evening Peak Generation : |  | 13432 | MW Hour : | 20:00 | Available Max Generation : |  | 13638 | MW
E.P. Demand (at gen end) : |  | 13950 | MW Hour : | 20:00 | Max Demand (Evening) : |  | 14200 | MW
Maximum Generation : |  | 13478 | MW Hour : | 22:00 | Reserve(Generation end) |  | - | MW
Total Gen. (MKWH) : |  | 272.9502 | System Load Factor : | 84.38% | Load Shed : |  | 518 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | 515 | MW at | 21:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2022-08-21
Actual : | 95.3 | Ft.(MSL) , | Rule curve : | 95.4 | Ft.( MSL )
Gas Consumed : | Total = | 1063.5 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 149368898.92
: |  | Coal : | 295592113.16 | Oil : | 1148424829.19 | Total : | 1593385841.27
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 60 | 1440:00 | 4547.5118 |  |  | 100 | 0.7733%
Chittagong Area | 0 | 0:00 | 1287.6983 |  |  | 58 | 3.067%
Khulna Area | 0 | 0:00 | 1699.9188 |  |  | 83 | 3.484%
Rajshahi Area | 0 | 0:00 | 1508.8579 |  |  | 82 | 4.07%
Cumilla Area | 71 | 1704:00 | 1283.7724 |  |  | 66 | 3.73%
Mymensingh Area | 300 | 7200:00 | 1061.3042 |  |  | 60 | 4.289%
Sylhet Area | 0 | 0:00 | 473.7264 |  |  | 22 | 3.088%
Barisal Area | 0 | 0:00 | 386.0478 |  |  | 0 | 1.291%
Rangpur Area | 0 | 0:00 | 837.5274 |  |  | 47 | 4.232%
Total | 431 |  | 13086.365 |  |  | 518
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-2
2) Ghorasal-3,4
3) Ashuganj-5
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
7) Sikalbaha 225 MW
8) Shajibazar 330 MW
9) Siddhirganj 335 MW ST
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Rangpur-Rangpur Confidence 132 kV Ckt-1 was under shut down from 08:13 to 19:07 for D/W.
b) Rangpur-Rangpur Confidence 132 kV Ckt-2 was under shut down from 08:16 to 19:08 for D/W.
c) Mymensingh-Netrokona 132 kV Ckt-1 was under shut down from 09:11 to 13:55 for C/M.
d) Mymensingh 132 kV Bus-B was under shut down from 10:30 to 14:52 for C/M.
e) Mirsharai BSRM 230/33 kV T-2 transformer was under shut down from 10:59 to 14:26 for C/M.
f) Barishal(S)-Patuakhali 132 kV Ckt tripped at 11:37 showing Dist. Z2,A,B at Patuakhali end and was switched | [5 empty] | About 90 MW power interruption occurred under
on at 11:51. | [5 empty] | Barisal(S) and Barguna S/S areas from 11:37 to 11:51.
g) Thakurgaon P/S-Thakurgaon S/S 132 kV Ckt-1 was under shut down from 11:24 to 11:38 for C/M.
h) Thakurgaon P/S-Thakurgaon S/S 132 kV Ckt-2 was under shut down from 11:41 to 11:54 for C/M.
i) Thakurgaon P/S-Purbasadipur 132 kV Ckt-1 was under shut down from 10:24 to 10:58 for C/M.
j) Thakurgaon P/S-Purbasadipur 132 kV Ckt-2 was under shut down from 11:00 to 11:20 for C/M.
k) Bagerhat 132/33 kV T-1 & T-2 transformers along with 33 kV Bus under shut down from 08:15 to 16:53 for C/M. | [5 empty] | About 35 MW power interruption occurred under
Bagerhat S/S area from 08:15 to 16:53.
l) Jhenaidah-Chuadanga 132 kV Ckt was under shut down from 11:49 to 14:22 for C/M. | [5 empty] | About 40 MW power interruption occurred under
Chuadanga S/S area from 11:49 to 14:22.
m) Barishal(N) 132/33 kV T-5 transformer was under shut down from 10:57 to 12:17 for C/M. | [5 empty] | About 27 MW power interruption occurred under
Barishal(N) S/S area from 10:57 to 12:17.
n) Chapainawabganj-Rohanpur 132 kV Ckt-1 was under shut down from 12:59 to 15:00 for C/M.
o) Payra S/S 132 kV spare Bay was under shut down from 13:25 to 15:24 for C/M.
p) Rampura-Ullon 132 kV Ckt-2 was opened from Ullon end at 10:40 due to CT oil leakage.
Q) Ghorashal Unit-7 STG was synchronized at 16:45.
r) Naogaon 132/33 kV T-3 transformer along with 33 kV Bus section-3 were under shut down from 07:07(21/8/2022) | [5 empty] | About 35 MW power interruption occurred under
to 08:56 for R/H maintenance by PBS. | [5 empty] | Naogaon S/S area from 07:07(21/8/2022) to 08:56.
| Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2022-08-20 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4315500
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 300 | 4818345 | Machine problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 93 | 2108681 | Engine problem
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 409 | 9955330
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 257 | 7292000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 260 | 6216100 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 8 | 202560 | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 0 | 0 | Under maint.
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 30 | 735992 | Engine problem
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 457056
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 35 | 232000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 7 | 191 | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 93 | 3846438 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 8 | 196992 | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 603360
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 119 | 1053120 | Engine problem
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 487189
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 697224 | Engine problem
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 52 | 1178160 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 785300
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 32 | 774700
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 40 | 675840 | #REF!
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 243 | 3665780 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 300 | 5644953
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 91 | 1567764 | Engine problem
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 91 | 688242 | Engine problem
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 1128816
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 1651200
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 17 | 166080 | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 2331360
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 198763
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 55 | 1334520
| Dhaka area Total |  |  |  | 5847 | 3335 | 65009556
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 110 | 2600000 | Machine problem
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 25 | 548811
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 102600
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 38 | 449280 | Engine problem
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 156 | 3615471 | Low water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | HGPI for 30 days.
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 87 | 1247854 | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 43 | 733824 | Fuel shortage
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 763729 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 10 | 261600 | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 10 | 264000 | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 11 | 285408 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 25 | 558240
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 94 | 694080 | Engine problem
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 31080
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 181 | 2669673 | Fuel shortage
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1056816
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 110 | 1966282
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 10 | 259200 | Engine problem
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 108 | 2266964 | Engine problem
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Chattogram area Total |  |  |  | 2382 | 1123 | 20374912
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 206 | 4998000 | #REF!
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 310 | 7941100 | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 305 | 7679000 | FGMO
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+136*1 | 284 | 0 | 0 | On test.
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 40 | 835848 | Engine problem
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 54 | 128880
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 73 | 1522181 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1123951
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 138 | 2818545 | Engine problem
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 47 | 1018264
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 144 | 3436270 | Machine problem
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 200 | 3960960
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 504180
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 10 | 185400
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 156 | 3602880
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 717600
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 8 | 45048 | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 18 | 332640 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 195 | 2794752
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 34 | 540360 | Fuel shortage
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 29 | 364560 | Fuel shortage
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 35 | 693000 | 33 kV feeder problem.
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 96 | 2180160 | Engine problem
| Cumilla Area Total |  |  |  | 3169 | 2204 | 47423579
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 127 | 3151680 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 509148
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 13400
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 106 | 1776000 | Engine problem
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 68 | 1467600 | Engine problem
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 339280
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 292320 | Engine problem
| Mymensingh Area Total |  |  |  | 614 | 335 | 7549428
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1022000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 20 | 655304 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Gas shortage
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 5 | 90000 | Gas shortage
| Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 5 | 111528 | Gas shortage
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 0 | 0 | Engine problem
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 62 | 1472256
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 990720
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 193 | 4980420
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50MW PP (EPL) |  | NENP | 27*2 | 50 | 0 | 0 | Gas shortage
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 8 | 124800 | Gas shortage
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 295 | 7292000 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 405 | 9606000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 236880
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 391 | 932800
| Sylhet Area Total |  |  |  | 2477 | 1518 | 27514708
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 905 | 21930181
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 16 | 96960 | Fuel shortage
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 40 | 215040 | Engine problem
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 225 | 4709760
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 64 | 755584 | Engine problem
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 155 | 4020768 | Gas shortage.
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 0 | 0 | Fuel shortage
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 92 | 664320 | Engine problem
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 35 | 352320 | Fuel shortage
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 67 | 793296 | Fuel shortage
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 398880
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 0 | 0 | 0 | On test.
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 2384 | 1599 | 33937109
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 32 | 425184 | Line O/L
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 28 | 542160 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 150 | 3583217 | Gas shortage
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1160 | 28048400 | Line O/L
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 0 | 0 | Under maint.
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Line O/L
| Barisal Area Total |  |  |  | 1958 | 1370 | 32598961
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 32 | 512752 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 40 | 469946 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contract Expired
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Fuel shortage
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 135752 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 174 | 4483973 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 196 | 4349482
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 148 | 3863109 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 316 | 7730509 | Gas shortage
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 133800 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 21 | 465360
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | .
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 263200
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 8 | 38400 | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 82 | 1222576 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 172 | 1603769 | Engine problem
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 94 | 1655136 | Engine problem
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 95 | 1645056 | Engine problem
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 33360
| Rajshahi Area Total |  |  |  | 2129 | 1453 | 28606180
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 81 | 1886836
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 251 | 6032800 | Machine problem
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 91 | 1563571 | Engine problem
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 45743
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 72 | 406848 | Fuel shortage
| Rangpur Area Total |  |  |  | 720 | 495 | 9935798
| Total |  |  |  | 21680 | 13432 | 272950231
| Eastern Grid Total |  |  |  | 14489 | 8515 | 167872183
| Western Grid Total |  |  |  | 7191 | 4917 | 105078048
| National Grid Total |  |  |  | 21680 | 13432 | 272950231
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2022-08-20
(a) ENTIRE EASTERN GRID : |  | 8640.08 | MW | (b) ENTIRE WESTERN GRID : |  | 4165.04 | MW
i) Dhaka area |  | 4735.32 | MW | i) Khulna area |  | 1522 | MW
ii) Chittagong area |  | 1233.76 | MW | ii) Rajshahi area |  | 1349.2 | MW
iii) Comilla area |  | 1184 | MW | iii) Barisal area |  | 367.84 | MW
iv) Mymensingh area |  | 874 | MW | iv) Rangpur area |  | 926 | MW
v) Sylhet area |  | 613 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 12805.12 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
AKS | 0 | 00:00 | Chowmuhani | 174 | 18:30 | Kaptai | 5 | 18:30 | Nawabganj | 36.9 | 19:00 | Siddhirganj | 108 | 22:00
AKSML | 148 | 07:00 | Chuadanga | 95 | 20:00 | Kazla | 95 | 19:30 | Netrakona | 96 | 19:00 | Sirajganj | 88 | 07:00
Aftabnagar | 32 | 19:00 | Coxsbazar | 122 | 20:00 | Keranigonj | 60 | 19:00 | New | 81 | 09:00 | Sonargaon | 80 | 12:00
Agargaon | 82 | 13:00 | Cumilla(N) | 169 | 00:00 | Khagrachori | 26 | 19:30 | Niamatpur | 64 | 06:00 | Sreemongol | 44 | 12:00
Agrabad | 74 | 19:30 | Cumilla(S) | 172 | 23:00 | Khulna | 91 | 19:00 | Noapara | 47 | 01:00 | Srinagar | 46.28 | 21:00
Amnura | 48 | 00:00 | Daudkandi | 148 | 23:00 | Khulshi | 181 | 14:00 | PHP | 11 | 10:00 | Sunamganj | 38 | 22:00
Ashuganj | 41 | 03:00 | Dhaka | 32 | 13:00 | Kishoreganj | 110 | 21:00 | Pabna | 89 | 00:00 | Sylhet | 136 | 00:00
BSRM | 149 | 05:00 | Dhamrai | 100 | 21:00 | Kodda | 300 | 19:00 | Palashbari | 108 | 23:00 | TK | 28.5 | 19:00
Bagerhat | 101 | 19:00 | Dhanmondi | 141.3 | 13:00 | Kulaura | 52 | 20:00 | Panchagarh | 46 | 08:00 | Tangail | 195 | 22:00
Bakulia | 104 | 19:00 | Dohazari | 100 | 19:00 | Kurigram | 70 | 19:30 | Patuakhali | 133 | 22:00 | Thakurgaon | 66 | 22:00
Banani | 52 | 15:00 | Faridpur | 150 | 22:00 | Kushtia | 130 | 19:30 | Payra | 1.02 | 16:00 | Tongi | 116 | 19:30
Bangabhaban | 10 | 11:00 | Fatullah | 71 | 23:00 | Lalbag | 92 | 11:00 | Purbachal | 20 | 21:00 | Ullon | 40 | 21:00
Barapukuria | 55 | 00:00 | Fenchuganj | 55 | 22:00 | Lalmonirhat | 53 | 19:30 | Purbasadipur | 96 | 05:00 | Uttara | 93 | 21:00
Barguna | 20 | 23:00 | Feni | 124 | 19:00 | Madanganj | 66 | 20:00 | Rahim | 26 | 08:00 | UttaraNew | 18 | 00:00
Barishal | 100 | 19:30 | GPH | 93 | 21:00 | Madaripur | 99 | 20:00 | Rajbari | 60 | 19:30 | Zigatola | 57 | 19:00
Barishal-230 | 76 | 23:00 | Ghorashal | 71 | 23:00 | Madartek | 85 | 23:00 | Rajendrapur | 92 | 05:00
Baroaulia | 70 | 13:00 | Goalpara | 26 | 12:00 | Madunaghat | 58 | 19:00 | Rajshahi | 132 | 22:00
Baroirhat | 55 | 19:00 | Gollamari | 52 | 19:00 | Magura | 56 | 19:00 | Rajshahi-230 | 26 | 02:00
Bashundhara | 166 | 16:00 | Gopalganj | 98 | 19:30 | Mahasthangarh | 74 | 21:00 | Ramganj | 88 | 19:00
BashundharaCement | 8 | 01:00 | Gulshan | 108 | 13:00 | Manikganj | 85 | 01:00 | Rampur | 16 | 00:00
Beanibazar | 70 | 19:00 | Halishahar | 94.5 | 16:00 | Maniknagar | 68 | 13:00 | Rangamati | 14 | 19:00
Benapole | 50 | 19:00 | HaripurSBU | 150 | 15:00 | Matarbari | 42 | 19:00 | Rangpur | 105 | 08:00
Bhaluka | 100 | 23:00 | Hasnabad | 87 | 00:00 | Matuail | 64 | 10:00 | Ruppur | 5 | 09:00
Bhandaria | 46 | 21:00 | Hathazari | 95 | 20:00 | Millgate | 64 | 17:00 | SSM | 3 | 05:00
Bhangura | 31 | 20:00 | Ishurdi | 73 | 19:00 | Mirpur | 127 | 17:00 | Saidpur | 93 | 08:00
Bheramara(GK) | 55 | 00:00 | Jaldhaka | 74 | 23:00 | Mirsorai | N/A | N/A | Satkhira | 95 | 06:00
Bhulta | 252 | 22:00 | Jamalpur | 118 | 20:00 | Mithapukur | 36 | 19:00 | Satmasjid | 101 | 19:00
Bog-Sherpur | 64 | 20:00 | Jashore | 120 | 19:30 | Modern | 0 | 00:00 | Savar | 156 | 09:00
Bogura | 174 | 22:00 | Jhenaidah | 110 | 19:00 | Mogbazar | 129 | 16:00 | Shahjadpur | 85 | 22:00
Borhanuddin | 40 | 23:00 | Joydebpur | 196 | 22:00 | Mongla | 30 | 09:00 | Shahjibazar | 95 | 00:00
Brahmanbaria | 180 | 19:30 | Joypurhat | 58 | 22:00 | Motijheel | 35 | 13:00 | Shahmirpur | 46.5 | 18:30
Cantonment | 150 | 13:00 | Juldah | 26 | 01:00 | Munshiganj | 105 | 22:00 | Shariatpur | 78 | 22:00
Chandpur | 67 | 22:00 | KSRM | 31.87 | 14:00 | Mymensingh | 226 | 18:00 | Sherpur | 100 | 19:00
Chandraghona | 34 | 19:00 | Kabirpur | 258 | 19:30 | Naogaon | 122 | 00:00 | Shikalbaha | 28 | 19:00
Chapai | 64 | 02:00 | Kachua | 74 | 20:00 | Narail | 42 | 20:00 | Shikalbaha-230 | N/A | N/A
Charsaidpur | 34 | 00:00 | Kallyanpur | 99 | 19:00 | Narinda | 74.4 | 13:00 | Shitalakhya | 114 | 12:00
Chauddagram | 47 | 23:00 | Kalurghat | 32 | 10:00 | Narshingdi | 174 | 22:00 | Sholosohor | N/A | N/A
Chhatak | 37 | 19:30 | Kamrangirchar | 49 | 00:00 | Natore | 133 | 00:00 | Shyampur | 144 | 01:00
Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
(1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2022-08-20 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Bhulta | 381 | 03:00 | 367 | 11:00 | Kaliakoir | 383 | 19:30 | 370 | 13:00
| Bibiana | 401 | 23:00 | 392 | 10:00 | Payra | 413 | 03:00 | 399 | 12:00
| BIPTC | 402 | 06:00 | 394 | 22:00 | Rahanpur_I | 380 | 03:00 | 378 | 00:00
| Gopalganj_I | 403 | 18:00 | 387 | 23:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 220 | 04:00 | 209 | 11:00 | Hasnabad | 222 | 22:00 | 209 | 09:00
| AKSML | 229 | 20:00 | 208 | 10:00 | Hathazari | 228 | 18:00 | 213 | 00:00
| Aminbazar | 221 | 20:00 | 213 | 16:00 | Ishurdi | 231 | 18:00 | 226 | 01:00
| Ashuganj | 235 | 19:00 | 229 | 09:00 | Jhenaidah | 228 | 18:00 | 219 | 00:00
| Baghabari | 232 | 17:00 | 226 | 01:00 | Kaliakoir | 221 | 07:00 | 212 | 10:00
| Barapukuria | 218 | 23:00 | 209 | 21:00 | Keranigonj | 221 | 23:00 | 209 | 10:00
| Barishal | 243 | 11:00 | 231 | 22:00 | Khulna(S) | 236 | 10:00 | 232 | 00:00
| Bheramara | 228 | 18:00 | 223 | 00:00 | Maniknagar | 222 | 06:00 | 213 | 10:00
| Bhulta | 225 | 03:00 | 215 | 14:00 | Meghnaghat | 226 | 20:00 | 218 | 09:00
| Bibiana | 235 | 23:00 | 228 | 16:00 | Mirsorai | N/A | N/A | N/A | N/A
| BIPTC | 232 | 17:00 | 224 | 02:00 | Rajshahi | 228 | 10:00 | 222 | 01:00
| Bogura | 225 | 18:00 | 215 | 22:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 246 | 07:00 | 235 | 23:00 | Rampura | 222 | 04:00 | 213 | 15:00
| BSRM | 227 | 20:00 | 212 | 05:00 | Shikalbaha | 228 | 20:00 | 214 | 01:00
| Cumilla(N) | 225 | 20:00 | 217 | 09:00 | Shyampur | 221 | 21:00 | 212 | 09:00
| Fenchuganj | 237 | 23:00 | 231 | 05:00 | Siddhirganj | 224 | 03:00 | 217 | 15:00
| Ghorashal | N/A | N/A | N/A | N/A | Sirajgonj | 257 | 02:00 | 226 | 00:00
| GPH | 230 | 02:00 | 213 | 00:00 | Tongi | 224 | 04:00 | 210 | 10:00
| Haripur | 221 | 04:00 | 212 | 15:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 136 | 23:00 | 128 | 11:00 | Lalbag | 139 | 23:00 | 128 | 09:00
| Agargaon | 136 | 04:00 | 128 | 11:00 | Lalmonirhat | 126 | 23:00 | 114 | 22:00
| Agrabad | 133 | 19:00 | 124 | 09:00 | Madanganj | 129 | 19:00 | 123 | 16:00
| AKS | 135 | 07:00 | 123 | 13:00 | Madaripur | 138 | 07:00 | 128 | 23:00
| Aminbazar | 132 | 20:00 | 128 | 02:00 | Madartek | 136 | 06:00 | 127 | 11:00
| Amnura | 131 | 06:00 | 125 | 13:00 | Madunaghat | 133 | 18:00 | 125 | 00:00
| Ashuganj | 135 | 08:00 | 133 | 09:00 | Magura | 139 | 17:00 | 132 | 19:30
| Bagerhat | 134 | 17:00 | 129 | 01:00 | Mahasthangarh | 135 | 17:00 | 123 | 03:00
| Bakulia | 135 | 16:00 | 123 | 09:00 | Manikganj | 132 | 19:00 | 121 | 08:00
| Banani | 130 | 04:00 | 122 | 09:00 | Maniknagar | 132 | 02:00 | 126 | 12:00
| Bangabhaban | 131 | 21:00 | 124 | 14:00 | Matarbari | 132 | 18:00 | 111 | 00:00
| Barapukuria | 133 | 23:00 | 125 | 20:00 | Matuail | 129 | 02:00 | 123.5 | 15:00
| Barguna | 135 | 09:00 | 128 | 23:00 | Millgate | 130 | 03:00 | 122 | 15:00
| Barishal | 138 | 09:00 | 127 | 13:00 | Mirpur | 132 | 23:00 | 121 | 11:00
| Barishal-230 | 139 | 08:00 | 129 | 22:00 | Mithapukur | 139 | 18:00 | 116 | 01:00
| Baroaulia | 134 | 18:30 | 125 | 09:00 | Modern | 132 | 16:00 | 125 | 05:00
| Baroirhat | 129 | 23:00 | 120 | 05:00 | Mogbazar | 137 | 06:00 | 130 | 10:00
| Bashundhara | 130 | 03:00 | 121 | 15:00 | Mongla | 133 | 16:00 | 127 | 23:00
| BashundharaCement | 129 | 19:00 | 123 | 16:00 | Motijheel | 131 | 21:00 | 124 | 14:00
| Beanibazar | 129 | 08:00 | 123 | 19:00 | Munshiganj | 129 | 03:00 | 124 | 15:00
| Benapole | 134 | 18:00 | 129 | 01:00 | Mymensingh | 131 | 23:00 | 114 | 20:00
| Bhaluka | 128 | 15:00 | 112 | 18:30 | Naogaon | 132 | 17:00 | 119 | 01:00
| Bhandaria | 137 | 08:00 | 124 | 22:00 | Narail | 136 | 10:00 | 130 | 00:00
| Bhangura | 137 | 18:00 | 132 | 01:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bheramara | 135 | 18:00 | 132 | 00:00 | Narshingdi | 125 | 05:00 | 117 | 11:00
| Bheramara(GK) | 136 | 05:00 | 133 | 20:00 | Natore | 133 | 17:00 | 126 | 01:00
| Bhulta | 120 | 00:00 | 114 | 11:00 | Nawabganj | 137 | 03:00 | 129 | 11:00
| Bog-Sherpur | 137 | 03:00 | 127 | 00:00 | Netrakona | 129 | 15:00 | 117 | 18:30
| Bogura | 136 | 18:30 | 126 | 21:00 | New | 130 | 23:00 | 122 | 15:00
| Bogura-230 | 137 | 18:00 | 128 | 01:00 | Niamatpur | 132 | 18:00 | 116 | 22:00
| Brahmanbaria | 131 | 10:00 | 128 | 00:00 | Noapara | 134 | 16:00 | 131 | 03:00
| Cantonment | 135 | 04:00 | 127 | 14:00 | Pabna | 134 | 18:00 | 130 | 00:00
| Chandpur | 135 | 12:00 | 128 | 00:00 | Palashbari | 135 | 16:00 | 117 | 21:00
| Chandraghona | 134 | 23:00 | 126 | 00:00 | Panchagarh | 119 | 09:00 | 111 | 04:00
| Chapai | 130 | 17:00 | 125 | 21:00 | Patuakhali | 135 | 09:00 | 130 | 00:00
| Charsaidpur | 130 | 23:00 | 124 | 15:00 | Payra | 137 | 09:00 | 134 | 21:00
| Chauddagram | 130 | 23:00 | 123 | 00:00 | PHP | 128 | 23:00 | 121 | 01:00
| Chhatak | 130 | 17:00 | 123 | 18:30 | Postogola | 139 | 04:00 | 133 | 09:00
| Chowmuhani | 126 | 19:00 | 117 | 05:00 | Purbachal | 131 | 04:00 | 121 | 17:00
| Chuadanga | 136 | 10:00 | 126 | 20:00 | Purbasadipur | 129 | 23:00 | 110 | 00:00
| Coxsbazar | 122 | 23:00 | 110 | 00:00 | Rahim | 130 | 04:00 | 125 | 15:00
| Cumilla(N) | 132 | 23:00 | 126 | 00:00 | Rajbari | 133 | 09:00 | 127 | 22:00
| Cumilla(S) | 130 | 01:00 | 125 | 13:00 | Rajendrapur | 130 | 19:00 | 117 | 09:00
| Daudkandi | 132 | 19:30 | 125 | 09:00 | Rajshahi | 131 | 17:00 | 126 | 01:00
| Dhaka | 136 | 03:00 | 128 | 11:00 | Rajshahi-230 | 132 | 18:00 | 125 | 22:00
| Dhamrai | 130 | 06:00 | 122 | 15:00 | Ramganj | 129 | 13:00 | 121 | 01:00
| Dhanmondi | 129 | 23:00 | 123 | 15:00 | Rampur | 132 | 20:00 | 124 | 10:00
| Dohazari | 132 | 16:00 | 123 | 00:00 | Rampura | 135 | 03:00 | 127 | 11:00
| Faridpur | 132 | 06:00 | 128 | 21:00 | Rangamati | 134 | 23:00 | 126 | 01:00
| Fatullah | 134 | 23:00 | 126 | 10:00 | Rangpur | 126 | 23:00 | 114 | 22:00
| Fenchuganj | 133 | 06:00 | 130 | 04:00 | Ruppur | 136 | 18:00 | 131 | 00:00
| Feni | 130 | 23:00 | 122 | 05:00 | Saidpur | 128 | 23:00 | 115 | 22:00
| Ghorashal | 137 | 19:00 | 132 | 07:00 | Satkhira | 138 | 15:00 | 127 | 21:00
| Goalpara | 135 | 10:00 | 132 | 05:00 | Satmasjid | 136 | 04:00 | 128 | 11:00
| Gollamari | 134 | 17:00 | 131 | 01:00 | Savar | 133 | 22:00 | 120 | 11:00
| Gopalganj | 138 | 18:00 | 132 | 23:00 | Shahjadpur | 139 | 18:00 | 134 | 00:00
| Gopalganj_I | 139 | 08:00 | 132 | 22:00 | Shahjibazar | 133 | 23:00 | 130 | 04:00
| Gulshan | 136 | 23:00 | 128 | 11:00 | Shahmirpur | 134 | 19:00 | 125 | 00:00
| Halishahar | 133 | 16:00 | 124 | 09:00 | Shariatpur | 137 | 11:00 | 127 | 21:00
| Haripur | 130 | 04:00 | 125 | 15:00 | Sherpur | 132 | 19:00 | 116 | 00:00
| HaripurSBU | 130 | 06:00 | 125 | 10:00 | Shikalbaha | 139 | 18:00 | 124 | 00:00
| Hasnabad | 140 | 23:00 | 133 | 11:00 | Shikalbaha-230 | 134 | 22:00 | 126 | 01:00
| Hathazari | 134 | 21:00 | 126 | 00:00 | Shitalakhya | 138 | 23:00 | 129 | 11:00
| Ishurdi | 135 | 17:00 | 132 | 1:00 | Sholosohor | N/A | N/A | N/A | N/A
| Jaldhaka | 125 | 23:00 | 113 | 20:00 | Shyampur | 132 | 06:00 | 127 | 10:00
| Jamalpur | 134 | 19:00 | 119 | 07:00 | Shyampur-230 | 133 | 20:00 | 127 | 09:00
| Jashore | 134 | 17:00 | 130 | 00:00 | Siddhirganj | 129 | 04:00 | 124 | 11:00
| Jhenaidah | 138 | 10:00 | 133 | 22:00 | Sirajganj | 135 | 18:00 | 127 | 21:00
| Jhenaidah-230 | 139 | 17:00 | 133 | 22:00 | Sonargaon | 130 | 20:00 | 123 | 11:00
| Joydebpur | 138 | 19:00 | 130 | 15:00 | Sreemongol | 134 | 11:00 | 131 | 18:00
| Joypurhat | 130 | 17:00 | 119 | 22:00 | Srinagar | 137 | 23:00 | 129 | 10:00
| Juldah | 134 | 23:00 | 125 | 00:00 | SSM | 136 | 19:00 | 125 | 07:00
| Kabirpur | 133 | 19:00 | 118 | 16:00 | Sunamganj | 128 | 11:00 | 119 | 20:00
| Kachua | 131 | 19:00 | 125 | 04:00 | Sylhet | 131 | 07:00 | 128 | 20:00
| Kaliakoir | 134 | 18:30 | 126 | 09:00 | Tangail | 133 | 19:00 | 124 | 07:00
| Kallyanpur | 132 | 06:00 | 122 | 10:00 | Thakurgaon | 127 | 23:00 | 107 | 03:00
| Kalurghat | 132 | 16:00 | 126 | 00:00 | TK | 134 | 21:00 | 125 | 10:00
| Kamrangirchar | 137 | 03:00 | 129 | 11:00 | Tongi | 132 | 04:00 | 122 | 17:00
| Kaptai | 133 | 00:00 | 128 | 07:00 | Ullon | 136 | 05:00 | 128 | 10:00
| Kazla | 132 | 04:00 | 125 | 12:00 | Uttara | 132 | 23:00 | 121 | 11:00
| Keranigonj | 139 | 23:00 | 129 | 10:00 | UttaraNew | 132 | 23:00 | 122 | 09:00
| Khagrachori | 132 | 21:00 | 124 | 10:00 | Zigatola | 137 | 04:00 | 129 | 10:00
| Khulna | 134 | 04:00 | 132 | 00:00
| Khulna(S) | 134 | 10:00 | 131 | 01:00
| Khulshi | 131 | 16:00 | 123 | 09:00
| Kishoreganj | 137 | 01:00 | 123 | 20:00
| Kodda | 138 | 18:30 | 119 | 09:00
| KSRM | 133 | 18:00 | 125 | 00:00
| Kulaura | 132 | 10:00 | 129 | 22:00
| Kurigram | 126 | 23:00 | 111 | 20:00
| Kushtia | 136 | 18:00 | 131 | 22:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2022-08-20
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 925 | 7606 | 4488 | 12094 |  |  |  | QF-LDC-11
0:30 | 817.5 | 7468 | 4458.5 | 11926.5 | Date: | 2022-08-20
1:00 | 710 | 7330 | 4429 | 11759
1:30 | 710 | 7322.5 | 4449.5 | 11772
2:00 | 710 | 7315 | 4470 | 11785
2:30 | 710 | 7297 | 4376 | 11673 | [5 empty] | Gen. at Eve. Peak | 13432 | 13432 MW (20:00 )
3:00 | 710 | 7279 | 4282 | 11561 | [6 empty] | 20:00
3:30 | 650 | 7169.5 | 4245.5 | 11415 | [5 empty] | Gen. at Day Peak | 10924 | 10924 MW (12:00 )
4:00 | 590 | 7060 | 4209 | 11269 | [6 empty] | 12:00
4:30 | 590 | 7035.5 | 4188 | 11223.5 | [5 empty] | Highest Generation | 13478
5:00 | 590 | 7011 | 4167 | 11178 | [6 empty] | 22:00
5:30 | 600 | 6920.5 | 4092 | 11012.5
6:00 | 610 | 6830 | 4017 | 10847
6:30 | 760 | 6703 | 4000.5 | 10703.5
7:00 | 910 | 6576 | 3984 | 10560
7:30 | 915 | 6571 | 3960 | 10531
8:00 | 920 | 6566 | 3936 | 10502
8:30 | 967.5 | 6627 | 3916.5 | 10543.5
9:00 | 1015 | 6688 | 3897 | 10585
9:30 | 965 | 6781.5 | 3855.5 | 10637
10:00 | 915 | 6875 | 3814 | 10689
10:30 | 940 | 6888.5 | 3778.5 | 10667
11:00 | 965 | 6902 | 3743 | 10645
11:30 | 947.5 | 7051.5 | 3733 | 10784.5
12:00 | 930 | 7201 | 3723 | 10924
12:30 | 910 | 7310 | 3797.5 | 11107.5
13:00 | 890 | 7419 | 3872 | 11291
13:30 | 922.5 | 7296 | 3899 | 11195
14:00 | 955 | 7173 | 3926 | 11099
14:30 | 1087.5 | 7223 | 4004.5 | 11227.5
15:00 | 1220 | 7273 | 4083 | 11356
15:30 | 1147.5 | 7243 | 4067 | 11310
16:00 | 1075 | 7213 | 4051 | 11264
16:30 | 1067.5 | 7198.5 | 4062 | 11260.5
17:00 | 1060 | 7184 | 4073 | 11257
17:30 | 1027.5 | 7255.5 | 4013.5 | 11269
18:00 | 995 | 7327 | 3954 | 11281
18:30 | 827.5 | 7807 | 4248 | 12055
19:00 | 660 | 8287 | 4542 | 12829
19:30 | 605 | 8469 | 4904 | 13373
20:00 | 615 | 8515 | 4917 | 13432 |  |  |  | Executive Engineer
20:30 | 565 | 8514.5 | 4916 | 13430.5 |  |  |  | Network Operation Division
21:00 | 515 | 8514 | 4915 | 13429
21:30 | 535 | 8539.5 | 4914 | 13453.5
22:00 | 555 | 8565 | 4913 | 13478 |  |  |  |  | Page 6 of 7
22:30 | 590 | 8391.5 | 4884 | 13275.5
23:00 | 625 | 8218 | 4855 | 13073
23:30 | 775 | 7912 | 4671.5 | 12583.5
24:00 | 925 | 7606 | 4488 | 12094
13432 MW (20:00 )
10924 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2022-08-20 |  | Energy |  | 272950231
[13 empty] | 2022-08-20 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 4425 | 907 | 1548 | 531 | 2031 | 1500 | 150 | 444 | 612 | 164 | 0 | 927.1045
0:30 | 4336.5 | 907.5 | 1717.5 | 644.5 | 1720 | 1480.5 | 148 | 441.5 | 592 | 154 | 0 | 897.1533 | Date: | 2022-08-20
1:00 | 4248 | 908 | 1887 | 758 | 1409 | 1461 | 146 | 439 | 572 | 144 | 0 | 867.2021
1:30 | 4270 | 907.5 | 1877 | 780.5 | 1404 | 1460.5 | 146.5 | 441.5 | 551.5 | 148 | 0 | 670.9066 | [8 empty] | Total Energy | 272.9502 | Total Energy Gen 272.950 MKWHr Energy Not Served 17.913 MKWHr Energy Requirement 290.863 MKWHr
2:00 | 4292 | 907 | 1867 | 803 | 1399 | 1460 | 147 | 444 | 531 | 152 | 0 | 474.6111 | [8 empty] | Energy not Served | 17.9125
2:30 | 4304.5 | 907.5 | 1844 | 722 | 1391.5 | 1460 | 147.5 | 443 | 519.5 | 150 | 0 | 439.5913 | [8 empty] | Energy Requirement | 290.8627
3:00 | 4317 | 908 | 1821 | 641 | 1384 | 1460 | 148 | 442 | 508 | 148 | 0 | 404.5714
3:30 | 4321.5 | 907.5 | 1815.5 | 523 | 1384 | 1430 | 148 | 442.5 | 512 | 147 | 0 | 354.8064 | [6 empty] | Shortage
4:00 | 4326 | 907 | 1810 | 405 | 1384 | 1400 | 148 | 443 | 516 | 146 | 0 | 305.0413
4:30 | 4354 | 906.5 | 1826 | 348 | 1376 | 1400 | 148 | 420.5 | 498.5 | 144 | 0 | 254.8155
5:00 | 4382 | 906 | 1842 | 291 | 1368 | 1400 | 148 | 398 | 481 | 142 | 0 | 204.5896
5:30 | 4356.5 | 906.5 | 1832 | 253 | 1353 | 1395 | 148 | 369 | 427.5 | 134 | 3 | 172.7953
6:00 | 4331 | 907 | 1822 | 215 | 1338 | 1390 | 148 | 340 | 374 | 126 | 6 | 141.001
6:30 | 4326 | 907.5 | 1696.5 | 215.5 | 1343 | 1374.5 | 147.5 | 330 | 356.5 | 125 | 21.5 | 135.0107 |  |  |  |  | Coal
7:00 | 4321 | 908 | 1571 | 216 | 1348 | 1359 | 147 | 320 | 339 | 124 | 37 | 129.0205
7:30 | 4320.5 | 907.5 | 1528 | 163 | 1413.5 | 1359.5 | 147.5 | 320 | 309 | 127 | 65.5 | 243.5103 |  |  |  | Oil |  |  |  | ,
8:00 | 4320 | 907 | 1485 | 110 | 1479 | 1360 | 148 | 320 | 279 | 130 | 94 | 358
8:30 | 4304 | 907 | 1486.5 | 142.5 | 1500 | 1351 | 148 | 320 | 278.5 | 133 | 103 | 518.5
9:00 | 4288 | 907 | 1488 | 175 | 1521 | 1342 | 148 | 320 | 278 | 136 | 112 | 679
9:30 | 4258 | 907.5 | 1508.5 | 239.5 | 1527 | 1341.5 | 146.5 | 310 | 278 | 136 | 114.5 | 827.5
10:00 | 4228 | 908 | 1529 | 304 | 1533 | 1341 | 145 | 300 | 278 | 136 | 117 | 976
10:30 | 4205 | 907.5 | 1511.5 | 337 | 1542 | 1326 | 145 | 275 | 286 | 139 | 123 | 1172.5
11:00 | 4182 | 907 | 1494 | 370 | 1551 | 1311 | 145 | 250 | 294 | 142 | 129 | 1369
11:30 | 4169.5 | 907 | 1482 | 454 | 1629.5 | 1302 | 150.5 | 265 | 288.5 | 147 | 119.5 | 1444
12:00 | 4157 | 907 | 1470 | 538 | 1708 | 1293 | 156 | 280 | 283 | 152 | 110 | 1519
12:30 | 4169 | 907 | 1469.5 | 549 | 1791.5 | 1327.5 | 156 | 300 | 311 | 156 | 121 | 1468.5
13:00 | 4181 | 907 | 1469 | 560 | 1875 | 1362 | 156 | 320 | 339 | 160 | 132 | 1418
13:30 | 4181 | 907 | 1469 | 560 | 1875 | 1362 | 156 | 320 | 339 | 160 | 132 | 1461
14:00 | 4181 | 907 | 1469 | 560 | 1875 | 1362 | 156 | 320 | 339 | 160 | 132 | 1504
14:30 | 4077 | 907 | 1468 | 629 | 1889.5 | 1396 | 156 | 335 | 366 | 154 | 116 | 1515
15:00 | 3973 | 907 | 1467 | 698 | 1904 | 1430 | 156 | 350 | 393 | 148 | 100 | 1526
15:30 | 4011.5 | 907.5 | 1446 | 638.5 | 1933 | 1420.5 | 157 | 330 | 381.5 | 151 | 93.5 | 1490
16:00 | 4050 | 908 | 1425 | 579 | 1962 | 1411 | 158 | 310 | 370 | 154 | 87 | 1454
16:30 | 4037 | 907.5 | 1418.5 | 512.5 | 2061 | 1411 | 158 | 300 | 376.5 | 153 | 59 | 839
17:00 | 4037 | 907 | 1412 | 446 | 2160 | 1411 | 158 | 290 | 383 | 152 | 31 | 224
17:30 | 4108.5 | 906.5 | 1383 | 251.5 | 2328 | 1375 | 158 | 290 | 430.5 | 150 | 18 | 167
18:00 | 4180 | 906 | 1354 | 57 | 2496 | 1339 | 158 | 290 | 478 | 148 | 5 | 110
18:30 | 4227.5 | 906 | 1440.5 | 365 | 2655 | 1361 | 158 | 333.5 | 593 | 153 | 2.5 | 249
19:00 | 4275 | 906 | 1527 | 673 | 2814 | 1383 | 158 | 377 | 708 | 158 | 0 | 388
19:30 | 4313 | 906 | 1564 | 848 | 2924 | 1490 | 157 | 420 | 784 | 164 | 0 | 301
20:00 | 4274 | 905 | 1574 | 941 | 2931 | 1492 | 156 | 421 | 778 | 156 | 0 | 431
20:30 | 4276 | 905.5 | 1587 | 938 | 2918 | 1491.5 | 153.5 | 428 | 775 | 161 | 0 | 455.5
21:00 | 4278 | 906 | 1600 | 935 | 2905 | 1491 | 151 | 435 | 772 | 166 | 0 | 480
21:30 | 4275 | 906.5 | 1619.5 | 935 | 2918.5 | 1485.5 | 152 | 438 | 768.5 | 167 | 0 | 796.5
22:00 | 4272 | 907 | 1639 | 935 | 2932 | 1480 | 153 | 441 | 765 | 168 | 0 | 1113
22:30 | 4324.5 | 906.5 | 1627.5 | 907 | 2777 | 1485 | 148.5 | 441.5 | 702 | 170 | 0 | 1059.5
23:00 | 4377 | 906 | 1616 | 879 | 2622 | 1490 | 144 | 442 | 639 | 172 | 0 | 1006
23:30 | 4401 | 906.5 | 1582 | 705 | 2326.5 | 1495 | 147 | 443 | 625.5 | 168 | 0 | 1127.5 | Max Temp. in Dhaka |  | 24.7° C | 34.3° C
24:00 | 4425 | 907 | 1548 | 531 | 2031 | 1500 | 150 | 444 | 612 | 164 | 0 | 1249
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 272.950 MKWHr Energy Not Served 17.913 MKWHr Energy Requirement 290.863 MKWHr
Note on W13: Author:

## Generation
g | 2022-08-20
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 81 | 82 | 83 | 83 | 83 | 83 | 82 | 83 | 83 | 80 | 80 | 86 | 86 | 86 | 86 | 88 | 88 | 88 |  | 88 | 87 | 86 | 81 | 83 | 74 | 80 | 1991471
2 | Karnaphuli Hydro PP Unit-4 & 5 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1624000
3 | Chattogram TPP-1 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2600000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 16 | 16 | 16 | 16 | 16 | 16 | 17 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 548811
| Teknaf 20MW PP (Solartech) | [5 empty] | 1 | 3 | 7 | 15 | 7 | 13 | 13 | 14 | 8 | 15 | 10 | 2 | 0 | [8 empty] | 102600
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 51 | 34 | 34 | 34 | 34 | 34 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 34 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 763729
12 | Hathazari 100 MW peaking PP | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 20 | 9 | 25 | 36 | 43 | 40 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 40 | 733824
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 34 | 87 | 87 | 87 | 87 | 87 | 87 |  | 87 | 87 | 87 | 87 | 87 | 87 | 74 | 1247854
| Daudkandi 200 MW PP (B.Trac) | 192 | 190 | 190 | 40 | 20 |  |  |  | 30 | 30 | 50 | 150 | 170 | 170 | 170 | 140 | 106 | 10 |  | 193 | 195 | 195 | 194 | 194 | 193 | 150 | 2794752
14 | Titas 50 MW Peaking PP | 45 | 37 | 35 | 43 | 44 | 43 | 45 | 45 | 44 | 44 | 44 | 44 | 40 | 43 | 43 | 36 | 42 | 43 |  | 47 | 47 | 47 | 46 | 44 | 38 | 38 | 1018264
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | [9 empty] | 0 | [5 empty] | 27 | 34 | 34 |  | 34 | 34 | 35 | 35 | 0 |  |  | 232000
17 | Siddhirganj 335 MW CCPP | 175 | 180 | 182 | 182 | 182 | 182 | 182 | 181 | 181 | 180 | 180 | 185 | 180 | 183 | 184 | 165 | 90 | 94 |  | 93 | 92 | 93 | 93 | 95 | 186 | 188 | 3846438
18 | Kodda 300 MW PP Unit-2 (Summit) | 115 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 188 | 194 | 130 | 112 | 112 | 115 | 188 |  | 240 | 240 | 243 | 243 | 243 | 245 | 155 | 3665780
19 | Ashuganj 195MW PP (APSCL-United) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 73 | 92 | 102 | 102 | 102 | 1522181
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4315500
24
25 | Ghorasal 365 MW CCPP Unit-7 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 0 | 20 | 70 | 120 | 250 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 4818345
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 37 | 37 | 37 | 37 | 37 | 36 | 33 | 33 | 36 | 33 | 35 | 35 | 35 | 35 | 31 | 31 | 28 | 34 |  | 39 | 37 | 40 | 37 | 39 | 39 | 37 | 835848
33 | Ashuganj 225 MW CCPP | 208 | 210 | 208 | 209 | 206 | 211 | 209 | 207 | 207 | 204 | 204 | 204 | 205 | 189 | 201 | 206 | 206 | 206 |  | 206 | 203 | 206 | 206 | 208 | 211 | 207 | 4998000
34 | Ashuganj 450 MW CCPP(South) | 310 | 310 | 310 | 310 | 340 | 310 | 310 | 315 | 310 | 335 | 320 | 330 | 305 | 310 | 325 | 305 | 305 | 305 |  | 305 | 330 | 305 | 305 | 310 | 305 | 330 | 7679000
| Ashuganj 450 MW CCPP(North) | 310 | 310 | 310 | 310 | 345 | 310 | 315 | 320 | 325 | 310 | 310 | 290 | 315 | 325 | 335 | 310 | 310 | 310 |  | 310 | 345 | 310 | 310 | 315 | 310 | 340 | 7941100
| Ashuganj 420 MW CCPP(East) | [26 empty] | 0
35 | Ashuganj 55 MW PP (Precision) | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 55 | 55 | 53 | 51 | 49 | 51 | 51 | 50 | 51 | 51 | 51 |  | 52 | 52 | 54 | 55 | 55 | 56 | 56 | 128880
36 | Chandpur 150 MW CCPP | 143 | 142 | 143 | 143 | 143 | 144 | 145 | 146 | 145 | 143 | 141 | 143 | 142 | 145 | 145 | 143 | 144 | 143 |  | 143 | 143 | 144 | 143 | 143 | 145 | 144 | 3436270
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 405 | 411 | 410 | 409 | 413 | 414 | 413 | 414 | 410 | 407 | 409 | 406 | 406 | 400 | 397 | 403 | 406 | 412 |  | 405 | 405 | 409 | 410 | 411 | 409 | 416 | 9955330
40 | Meghnaghat 450 MW CCPP(MPL) | 450 | 450 | 450 | 450 | 450 | 450 | 200 | 180 | 210 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 |  | 260 | 260 | 260 | 260 | 260 | 240 | 240 | 6216100
41 | Haripur 360MW CCPP(HPL) | 312 | 318 | 318 | 330 | 337 | 338 | 338 | 331 | 327 | 327 | 328 | 328 | 323 | 322 | 316 | 287 | 277 | 267 |  | 267 | 256 | 257 | 257 | 263 | 273 | 253 | 7292000
42 | RPCL 210MW CCPP | 158 | 158 | 157 | 157 | 154 | 159 | 157 | 157 | 155 | 127 | 128 | 113 | 113 | 102 | 101 | 117 | 115 | 129 |  | 127 | 127 | 127 | 127 | 127 | 135 | 135 | 3151680
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 2 | 13 | 12 | 27 | 46 | 36 | 56 | 28 | 16 | 40 | 6 | 17 | 1 |  | 0 | [6 empty] | 339280
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 42 | 42 | 43 | 43 | 43 | 43 | 42 | 42 | 42 |  | 44 | 43 | 43 | 43 | 43 | 43 | 43 | 1022000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 20 | 20 | 30 | 30 | 30 | 655304
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 63 | 64 | 63 | 64 | 64 | 64 | 62 | 61 | 60 | 60 | 60 | 59 | 60 | 58 | 59 | 61 | 60 | 60 |  | 55 | 59 | 62 | 62 | 62 | 64 | 62 | 1472256
48 | Shahjibazar 86MW PP (Shahjibazar) | 81 | 70 | 40 | 30 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 81 | 81 | 81 | 81 | 81 | 81 | 78 | 990720
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 207 | 207 | 207 | 207 | 207 | 207 | 207 | 207 | 207 | 207 | 207 | 207 | 208 | 207 | 207 | 207 | 207 | 207 |  | 207 | 193 | 193 | 193 | 193 | 193 | 193 | 4980420
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 9 | 10 | 8 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 236880
54 | Hobiganj 11MW PP Cofidence-E
55 | Fenchugonj 51 MW PP (Barakatullah) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | [8 empty] | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 90000
56 | Shahjahanulla 25 MW PP | [19 empty] | 8 | 8 | 8 | 8 | 8 | 15 | 15 | 124800
57 | Bibiana-II 341 MW CCPP (Summit) | 320 | 300 | 290 | 280 | 310 | 300 | 300 | 290 | 300 | 310 | 280 | 300 | 300 | 315 | 300 | 295 | 290 | 270 |  | 290 | 320 | 295 | 300 | 305 | 305 | 265 | 7292000
| Bibiyana South 400 MW | 398 | 400 | 400 | 400 | 394 | 400 | 394 | 394 | 392 | 385 | 380 | 378 | 385 | 366 | 377 | 390 | 386 | 393 |  | 390 | 380 | 391 | 390 | 392 | 400 | 392 | 932800
58 | Nababganj 55 MW PP (Southern power ) | [7 empty] | 26 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 55 | 55 | 55 | 697224
59 | Tangail Palli Power Gen 22 MW | 12 | 12 | 12 | 12 | 12 | 8 | 11 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 292320
60 | Barabkunda 22 MW PP (Regent) | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 285408
61 | Narshingdi 22 MW PP (Doreen) |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 0 | 0 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 457056
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 509148
63 | Impoprt (Tripura) | 144 | 152 | 148 | 146 | 142 | 126 | 124 | 130 | 136 | 136 | 142 | 152 | 160 | 150 | 148 | 154 | 152 | 148 |  | 158 | 164 | 156 | 166 | 168 | 172 | 164 | 3602880
64 | Malancha, Ctg. EPZ (United) | 42 | 42 | 42 | 42 | 42 | 38 | 36 | 10 | 2 | 6 | 2 | 2 | 2 | 2 | 10 | 4 | 6 | 9 |  | 16 | 18 | 25 | 28 | 35 | 18 | 22 | 558240
65 | Feni 22MW PP (Doreen) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 504180
66 | Feni 11 MW PP (Doreen) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 0 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 9 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 185400
67 | Jangalia 33MW PP (Summit) | 25 | 25 | 25 | 33 | 33 | 33 | 33 | 33 | 28 | 25 | 22 | 22 | 22 | 25 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 717600
68 | Cumilla 25 MW PP (Summit) | 14 | 14 | 14 | 14 | 14 | 14 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 13 | 17 | 17 |  | 18 | 18 | 18 | 20 | 20 | 20 | 20 | 332640
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 0 | 0 | 27 | 27 | 27 | 27 | 27 | 27 | 24 | 24 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 |  | 19 | 27 | 27 | 27 | 27 | 27 | 27 | 578160
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 785300
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 |  | 32 | 32 | 32 | 32 | 32 | 32 | 33 | 774700
73 | Ghorashal 108MW PP (Regent) | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 88 | 88 | 84 | 86 | 86 | 89 | 89 | 89 | 92 | 92 |  | 92 | 93 | 93 | 90 | 90 | 90 | 90 | 2108681
| Feni Lanka Power | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 34 | 34 |  | 34 | 34 | 34 | 34 | 34 | 34 | 17 | 540360
| Chowmuhani 113 MW | 15 | 13 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 8 | 9 | 9 | 21 |  | 27 | 29 | 29 | 29 | 29 | 29 | 29 | 364560
| Manikgonj 162MW PP(MPGL) | 54 | 54 | 54 | 54 | 54 | 54 | 35 | 35 | 35 | 35 | 40 | 50 | 108 | 108 | 108 | 115 | 162 | 162 |  | 162 | 162 | 162 | 162 | 162 | 162 | 144 | 2331360
77 | Siddhirganj 100 PP(Dutch Bangla) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 7 | 7 | 7 | 7 | 7 |  | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 191
78 | Gazipur 52 MW PP | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26 |  | 40 | 40 | 40 | 40 | 40 | 40 | 24 | 675840
79 | Kodda 150MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 110 |  | 119 | 118 | 119 | 119 | 120 | 16 | 16 | 1053120
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | [19 empty] | 1 | 8 | 8 | 8 | 8 | 8 | 8 | 45048
| Gazipur 100 MW PP | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 52 | 1651200
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 1 | 4 | 4 | 5 | 5 | 5 | 1 | 4 | 2 | 1 | 0 | [8 empty] | 31080
| Jodiac Power | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 43 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 41 | 1056816
| Karnaphuli Power Ltd. | 55 | 55 | 55 | 55 | 55 | 45 | 55 | 55 | 55 | 55 | 55 | 55 | 81 | 109 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 1966282
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL) | 7 | 8 | 7 | 8 | 8 | 7 | 8 | 7 | 8 | 11 | 9 | 8 | 8 | 8 | 7 | 8 | 7 | 8 |  | 7 | 8 | 8 | 8 | 7 | 8 | 7 | 202560
| Meghnaghat 104 MW PP (OPCL) | [6 empty] | 17 | 17 | 17 |  |  |  |  | 4 | 0 |  |  | 0 |  | 10 | 17 | 17 | 17 | 17 | 17 | 16 | 166080
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 261600
92 | Fenchuganj 44MW (Energyprima) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | [8 empty] | 3 | 5 | 5 | 5 | 5 | 5 | 5 | 111528
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 51 | 51 | 51 | 51 | 51 | 51 | 1123951
94 | Gagnagar 102 MW PP (Digital Power) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 196992
95 | Patenga 50MW PP (Baraka) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 3 | 6 | 6 | 25 | 25 | 25 | 27 | 38 |  | 38 | 38 | 38 | 38 | 38 | 38 | 27 | 449280
96 | Chattogram 108 MW PP (ECPV) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 11 | 11 | 24 |  | 81 | 94 | 94 | 94 | 94 | 81 | 10 | 694080
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 735992
100 | Manikganj 55 MW PP (Northern) | [14 empty] | 17 | 35 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 487189
101 | Kushiara 163 MW CCPP (KP)
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 1 | 2 | 1 | 3 | 2 | 1 | 2 | 2 | 0 | 0 | 0 | [8 empty] | 13400
103 | Kamalaghat 54 MW PP(Banco Energy) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 54 |  | 54 | 54 | 54 | 35 | 35 | 35 | 35 | 603360
104 | Keranigonj 300 MW PP (APR) | 302 | 303 | 301 | 225 | 201 | 165 | 166 | 85 | 120 | 204 | 250 | 300 | 300 | 300 | 300 | 249 | 180 | 12 |  | 299 | 300 | 300 | 300 | 300 | 250 | 181 | 5644953
105 | Bramhangoan 100 MW PP (Aggreko) | 70 | 70 | 70 | 70 | 70 | 50 | 50 | 25 | 25 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 25 |  | 90 | 90 | 91 | 92 | 92 | 88 | 70 | 1567764
106 | Mymensingh 200 MW PP (United) | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 76 | 77 | 77 | 77 | 77 | 77 | 80 | 78 | 82 | 83 | 107 |  | 113 | 113 | 106 | 107 | 106 | 104 | 38 | 1776000
112 | Aurahati 100MW PP (Aggreko) | 70 | 70 | 70 | 70 | 0 | 0 | [15 empty] | 91 | 91 | 91 | 90 | 70 | 688242
114 | Kodda 149 MW PP Unit-1 (Summit) | 17 | 17 | 17 | 17 | 17 | 18 | 17 | 17 | 18 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 24 | 142 |  | 149 | 149 | 149 | 149 | 149 | 58 | 17 | 1128816
115 | Juldah 100 MW PP Unit-3 (Acorn) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 264000
116 | Chandpur 200MW (Desh energy) | 136 | 135 | 136 | 136 | 136 | 120 | 120 | 120 | 127 | 138 | 158 | 200 | 200 | 200 | 200 | 200 | 200 | 155 |  | 162 | 200 | 200 | 200 | 200 | 170 | 170 | 3960960
117 | Ashuganj 150MW PP (Midland) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 102 | 105 | 113 | 120 | 122 | 123 | 117 | 123 |  | 132 | 136 | 138 | 142 | 145 | 143 | 137 | 2818545
118 | Bibiyana-III 400 MW CCPP | 402 | 402 | 403 | 403 | 403 | 402 | 403 | 403 | 404 | 402 | 395 | 402 | 404 | 375 | 382 | 400 | 404 | 370 |  | 403 | 403 | 405 | 404 | 403 | 402 | 401 | 9606000
| Jamalpur 115 MW PP (United) | 48 | 48 | 49 | 49 | 49 | 49 | 49 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 |  | 68 | 68 | 68 | 68 | 68 | 68 | 39 | 1467600
| Anwara 300 MW PP (United) | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 120 | 121 | 124 | 124 | 124 | 124 | 158 | 160 | 158 | 158 | 158 |  | 175 | 178 | 181 | 181 | 181 | 51 | 52 | 2669673
| Juldah unit-2 (Acorn) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 259200
| Anlima Energy Ltd. | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 105 |  | 108 | 108 | 108 | 94 | 100 | 108 | 108 | 2266964
| Bhairob 54.5 MW | 35 | 30 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 19 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 693000
| Spectra Solar Plant Ltd. | [5 empty] | 1 | 3 | 13 | 10 | 32 | 31 | 16 | 29 | 14 | 6 | 4 | 5 | 1 |  | 0 | [6 empty] | 198763
| Chandpur 115(Doreen) | 96 | 96 | 97 | 96 | 80 | 80 | 79 | 78 | 83 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 85 | 55 |  | 70 | 97 | 96 | 97 | 97 | 96 | 96 | 2180160
| Kanchan Purbachal Power Generation Ltd. | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1334520
Mirsharai 150 MW (Oil)
Mirsharai 150 MW (Gas)
120 | Eastern Zone Total | 7330 | 7315 | 7279 | 7060 | 7011 | 6830 | 6576 | 6566 | 6688 | 6875 | 6902 | 7201 | 7419 | 7173 | 7273 | 7213 | 7184 | 7327 |  | 8287 | 8469 | 8515 | 8514 | 8565 | 8218 | 7606 | 167872183
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | [19 empty] | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 96960
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 21 | 21 | 10 | 10 | 10 | [14 empty] | 37 | 51 | 40 | 27 | 20 | 17 | 17 | 215040
| Khulna 225 MW CCPP | 226 | 227 | 226 | 227 | 218 | 190 | 190 | 190 | 190 | 170 | 120 | 150 | 150 | 150 | 180 | 160 | 160 | 160 |  | 227 | 223 | 225 | 225 | 227 | 228 | 226 | 4709760
129 | Rupsha 105 MW PP (Orion rupsha) | [8 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 20 | 35 | 35 | 35 | 35 | 35 | 17 | 352320
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 2 | 16 | 58 | 52 | 21 | 30 | 10 | 44 | 5 | 27 | 59 | 4 | 2 |  | 0 | [6 empty] | 398880
131 | Rampal 1320 MW (BIFPCL)
132 | United Payra Power Ltd. | [26 empty] | 0
133 | Bhola Nutan Biddut BD LTD (GAS)
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  |  |  |  | 16 | 16 | 16 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 425184
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 151 | 152 | 151 | 150 | 149 | 147 | 149 | 150 | 150 | 150 | 149 | 148 | 147 | 137 | 146 | 147 | 148 | 150 |  | 150 | 146 | 150 | 150 | 150 | 145 | 145 | 3583217
140 | Bhola 33 MW PP (Venture) | 28 | 26 | 25 | 23 | 23 | 20 | 19 | 18 | 17 | 17 | 18 | 19 | 21 | 21 | 23 | 21 | 20 | 17 |  | 27 | 27 | 28 | 28 | 30 | 32 | 32 | 542160
141 | Noapara 100 MW PP (Bangla Trac) | 48 | 70 | [12 empty] | 17 | 20 | 10 | 0 |  | 27 | 93 | 92 | 93 | 93 | 93 | 10 | 664320
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP | 60 | 60 | 58 | 60 | 60 | 60 | 60 | [10 empty] | 11 |  | 52 | 61 | 64 | 58 | 58 | 53 | 52 | 755584
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 32 | 32 | 32 | 32 | 32 | 32 | 67 |  | 67 | 67 | 67 | 67 | 67 | 15 | 15 | 793296
146 | Bheramara HVDC | 908 | 907 | 908 | 907 | 906 | 907 | 908 | 907 | 907 | 908 | 907 | 907 | 907 | 908 | 907 | 908 | 907 | 906 |  | 906 | 906 | 905 | 906 | 907 | 906 | 907 | 21930181
147 | Bheramara 410 MW CCPP | 175 | 180 | 180 | 180 | 180 | 180 | 180 | 170 | 165 | 150 | 155 | 150 | 150 | 145 | 135 | 140 | 140 | 145 |  | 155 | 155 | 155 | 160 | 160 | 160 | 160 | 4020768
148 | Payra 1320 MW | 1140 | 1140 | 1140 | 1080 | 1080 | 1070 | 1030 | 1030 | 1010 | 1010 | 980 | 960 | 1030 | 1090 | 1100 | 1080 | 1080 | 1010 |  | 1050 | 1160 | 1160 | 1160 | 1150 | 1160 | 1170 | 28048400
149
150 | Barapukuria TPP Unit-1 | 81 | 80 | 80 | 80 | 80 | 80 | 79 | 80 | 81 | 80 | 80 | 82 | 82 | 81 | 80 | 81 | 81 | 79 |  | 83 | 80 | 81 | 80 | 80 | 80 | 80 | 1886836
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 240 | 240 | 240 | 240 | 240 | 240 | 250 | 250 | 251 | 251 | 251 | 251 | 250 | 250 | 250 | 250 | 250 | 250 |  | 250 | 250 | 251 | 251 | 250 | 250 | 250 | 6032800
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 30 | 31 | 31 | 31 | 31 | [7 empty] | 0 | 32 | 32 | 32 | 32 | 32 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 512752
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 0 | 2 | 2 | 3 | 4 | 2 | 4 | 5 | 0 | 2 | 0 | 0 | [8 empty] | 33360
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 183 | 183 | 182 | 183 | 183 | 183 | 182 | 183 | 182 | 177 | 177 | 174 | 174 | 173 | 170 | 169 | 169 | 170 |  | 174 | 175 | 174 | 174 | 175 | 177 | 176 | 4483973
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
| Sirajgonj 225 MW CCPP Unit-2 (Oil) | 213 | 217 | 216 | 216 | 180 | 150 | 130 | 130 | 130 | 130 | 130 | 130 | 170 | 160 | 170 | 150 | 130 | 130 |  | 150 | 197 | 196 | 210 | 214 | 214 | 218 | 4349482
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 155 | 156 | 157 | 157 | 157 | 157 | 157 | 156 | 152 | 149 | 148 | 148 | 145 | 142 | 140 | 141 | 143 | 145 |  | 149 | 149 | 148 | 150 | 150 | 150 | 152 | 3863109
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 360 | 366 | 361 | 360 | 365 | 361 | 363 | 342 | 322 | 312 | 315 | 291 | 290 | 275 | 283 | 282 | 280 | 250 |  | 305 | 310 | 316 | 317 | 326 | 327 | 317 | 7730509
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | 37 | 37 | 37 | 35 | 35 | [7 empty] | 4 | 5 | 5 | 12 | 36 | 37 |  | 37 | 37 | 40 | 40 | 37 | 37 | 37 | 469946
162 | Bogra 22 MW PP (GBB) | 21 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 20 |  | 21 | 21 | 21 | 21 | 21 | 21 | 22 | 465360
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 263200
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP | [19 empty] | 25 | 32 | 32 | 32 | 32 | 24 | 16 | 135752
168 | Santahar 50 MW Peaking PP | [19 empty] | 33 | 33 | 32 | 32 | 32 | 32 | 13 | 133800
169 | Natore 52 MW PP (Rajlanka) | [19 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 0 | 38400
170 | Chapainawabganj 100 MW Peaking PP | 73 | 52 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 |  | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 1222576
171 | Baghabari 200 MW PP (Paramount) | 76 | 100 | 10 | [8 empty] | 18 | 20 | 63 | 141 | 100 | 80 | 10 |  | 64 | 170 | 172 | 165 | 165 | 165 | 50 | 1603769
| Bagura 113 MW PP (Confidence)-2 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 94 | 94 |  | 94 | 94 | 94 | 94 | 94 | 94 | 50 | 1655136
172 | Confidence Power Bogura Unit-1 113 MW | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 95 | 95 |  | 95 | 95 | 95 | 95 | 95 | 95 | 55 | 1645056
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 52 | 56 | 56 | 56 | 50 | 56 | 80 | 91 |  | 91 | 84 | 91 | 92 | 92 | 92 | 56 | 1563571
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1 |  |  | 3 | 7 | 6 | 7 | 7 | 6 | 4 | 2 | 1 |  | 0 | [6 empty] | 45743
178 | Energypac Power Venture Thakurgaon Ltd. | [19 empty] | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 406848
178