## Forecast
8 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2022-08-25 | Thursday
|  |  | Date (day): | 2022-08-25 |  | Thursday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 12677.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14372 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2022-08-24 | 2022-08-25 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 300 | 300 | 300 | 300 |  | 65
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 87 | 91 | 91 | 91 |  | 17 | Engine problem
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 402 | 400 | 400 | 400
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 332 | 332 | 330 | 330 | 30 |  | Gas shortage
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 300 | 300 | 300 | 300 |  |  | Machine problem
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 0 | 41 | 7 | 41 | 59 |  | Fuel shortage
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 0 | 0 | 0 | 0 |  | 102 | Under maint
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55 |  | 25 | Engine problem
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 19 | 19 | 19
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 92 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 7 | 40 | 7 | 40 | 60 |  | Fuel shortage
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 338 | 335 | 335 | 0
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 8 | 40 | 8 | 40 | 62 |  | Fuel shortage
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 35 | 54 | 17 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 46 | 125 | 16 | 126 |  | 23 | Fuel shortage
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 55 | 35 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 35 | 35 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 35 | 52 | 50 | 50 |  | 30 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 26 | 30 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 8 | 31 | 24 | 40 |  | 12 | Engine problem
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 243 | 278 | 210 | 275 |  | 25 | Engine problem
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 225 | 122 | 225 | 225 |  |  | Transformer problem
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 80 | 90 | 50 | 90 | 100 |  | Fuel shortage
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 81 | 90 | 80 | 90 |  |  | Engine problem
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 149 | 140 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 17 | 105 | 35 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 17 | 55 | 17 | 54 | 50 |  | Fuel shortage
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 40 | 162 | 35 | 162
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 19 | 0 | 30 | 0
| 40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 55 | 55 | 55 | 55
|  | Dhaka area Total |  |  |  |  | 6263 | 5847 | 2908 | 3648 | 3161 | 3782 | 957 | 979
| 41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 110 | 110 | 110 | 110 | 70 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 25 | 25 | 25 | 25
| 43 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 19 | 0 | 20 | 0
| 44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 25 | 38 | 25 | 38 |  | 12 | Engine problem
| 45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 151 | 152 | 150 | 150 |  | 80 | Low Water Level
| 46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | S/D due to HGPI
| 47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
| 48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 69 | 87 | 69 | 105
| 49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 17 | 43 | 40 | 40 | 58 |  | Fuel shortage
| 50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 17 | 51 | 17 | 51 | 51 |  | Fuel shortage
| 51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 10 | 10 | 10 | 10 | 90 |  | Fuel shortage
| 52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 10 | 10 | 10 | 10 |  | 90 | Fuel shortage
| 53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 14 | 16 | 16 | 16 |  | 6 | Engine problem
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 30 | 10 | 30
| 54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 11 | 95 | 12 | 95 |  |  | Fuel shortage
| 55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5 | 0 | 5 | 0
| 56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 88 | 52 | 51 | 51 | 249 |  | Fuel shortage
| 57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 17 | 17 | 17 | 17
| 58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 110 | 110 | 110 | 110
| 59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 10 | 10 | 10 | 10 |  |  | Fuel shortage
| 60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 107 | 107 | 107 | 107 |  | 9 | Engine problem
|  | Mirsharai 150 MW |  | Gas/HSD | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 817 | 963 | 814 | 975 | 698 | 572
| 61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 207 | 209 | 210 | 210 | 11
| 63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 300 | 330 | 330 | 330 |  |  | Gas shortage
| 64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 300 | 305 | 300 | 305 |  |  | Gas shortage
|  | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+136*1 | 284 | 284 | 0 | 0 | 0 | 0 |  |  | On test.
| 65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 30 | 40 | 40 | 40 |  | 5 | Engine problem
| 66 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 55 | 52 | 56 | 55 | 55
| 67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 120 | 133 | 125 | 140 |  | 10 | Engine problem
| 70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 42 | 46 | 42 | 42 |  | 10 | Engine problem
| 71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 144 | 136 | 143 | 143 |  | 20 | Machine problem
| 72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 68 | 180 | 100 | 200
| 73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 22 | 22 | 22
| 74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 10 | 10 | 10 | 10
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 150 | 148 | 143 | 165
| 75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 24 | 25 | 25 | 25
| 76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 8 | 8 | 8 | 44 |  | Fuel shortage
| 77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 18 | 17 | 18 | 18 |  | 7 | Engine problem
| 78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 160 | 0 | 100 | 200
| 79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 0 | 0 |  |  | Fuel shortage
| 80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 28 | 115 | 57 | 110 | 3 |  | Fuel shortage
| 81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 35 | 35 | 35 | 35 |  | 19 | 33 kV feeder fault
| 82 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 68 | 77 | 96 | 96 | 19 |  | Fuel shortage
|  | Cumilla Area Total |  |  |  |  | 3193 | 3169 | 1835 | 1951 | 1918 | 2213 | 398 | 71
| 83 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 68 | 107 | 68 | 105 | 97 |  | Gas shortage
| 84 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  |  | Engine problem
| 85 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0 |  | 8 | Under maint.
| 86 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 3 | 0 | 1.6 | 0
| 87 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 96 | 97 | 96 | 95 |  | 105 | Engine problem
| 88 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 69 | 109 | 109 | 100 |  | 15 | Engine problem
| 89 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 50 | 0 | 50 | 0
| 90 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 10 | 12 | 12 | 12 |  | 10 | Engine problem
|  | Mymensingh Area Total |  |  |  |  | 717 | 614 | 296 | 325 | 336.6 | 312 | 97 | 138
| 91 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 43 | 43 | 43 |  | 27 | Machine problem.
| 92 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 41 | 42 | 42 |  | 48 | Machine problem
| 93 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 | 163 |  | Gas shortage
| 94 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
| 95 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 5 | 5 | 5 | 5 | 46 |  | Gas shortage
| 96 | Fenchuganj 44MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Gas shortage
| 97 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0
| 98 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 58 | 64 | 60 | 60
| 99 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 10 | 81 | 10 | 80
| 100 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
| 101 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 194 | 193 | 190 | 190 |  |  | Machine problem
| 102 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Gas shortage
| 103 | Sylhet 50MW PP (EPL) |  | Gas | NENP | 27*2 | 50 | 50 | 6 | 6 | 6 | 6 | 44 |  | Gas shortage
| 104 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 8 | 8 | 8 | 8 | 17 |  | Gas shortage
| 105 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 270 | 290 | 295 | 295 |  |  | FGMO
| 106 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 403 | 403 | 400 | 400
| 107 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| 108 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 401 | 401 | 400 | 400
|  | Sylhet Area Total |  |  |  |  | 2522 | 2477 | 1438 | 1545 | 1469 | 1539 | 340 | 505
| 109 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 894 | 887 | 910 | 910 |  |  | .
| 110 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 0 | 16 | 16 | 16 | 99 |  | Fuel shortage
| 111 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 26 | 0 | 50 |  | 4 | Engine problem
| 112 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 150 | 226 | 225 | 225
| 113 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 62 | 30 | 70 |  | 39 | Engine problem
| 114 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 250 | 280 | 280 | 280 | 130 |  | Gas shortage
| 115 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 0 | 0 | 0 | 40 |  | Fuel shortage
| 116 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 50 | 93
| 117 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 17 | 17 | 17 | 88 |  | Fuel shortage
| 118 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 15 | 67 | 15 | 67 |  |  | Fuel shortage
| 119 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 27 | 0 | 100 | 0
|  | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
|  | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
|  | Khulna Area Total |  |  |  |  | 2388 | 2384 | 1336 | 1581 | 1643 | 1728 | 373 | 43
| 120 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 32 | 32 | 48 |  |  | Line O/L
| 121 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 14 | 22 | 20 | 30 |  | 10 | Engine problem
| 122 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 112 | 86 | 100 | 151 |  |  | Machine problem
|  | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
| 123 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 890 | 1090 | 1170 | 1170
| 124 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 115 | 191 | 220 | 220 |  | 220 | Machine problem
| 125 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 0 | 17 |  |  | Line O/L
|  | Barisal Area Total |  |  |  |  | 1958 | 1958 | 1131 | 1421 | 1542 | 1636 | 0 | 230
| 126 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 127 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 32 | 32 | 32 | 32 |  | 20 | Engine problem
| 128 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 26 | 0 | 40 |  | 31 | Engine problem
| 129 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 130 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 42 | 42 | 42 | 42 |  |  | Fuel shortage
| 131 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 32 | 0 | 32 |  | 18 | Engine problem
| 132 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 192 | 214 | 200 | 214 | -4 |  | Gas shortage
| 133 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 204 | 216 | 220 | 220
| 134 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 202 | 190 | 190 | 190 | 30 |  | Gas shortage
| 135 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 414 | 419 | 410 | 410 | 4
| 136 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 32 | 0 | 32 |  | 18 | Engine problem
| 137 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 20 | 22 | 22 | 22
| 138 | Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 139 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 140 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 43 | 8 | 43 | 9 |  | Fuel shortage
| 141 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 82 | 35 | 80 |  | 24 | Engine problem
| 142 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 20 | 0 | 120 | 180 |  | 20 | Engine problem
| 143 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 50 | 94 | 50 | 90 |  | 23 | Engine problem
| 144 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 55 | 95 | 55 | 95 |  | 18 | Engine problem
| 145 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 3 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2129 | 1253 | 1550 | 1401 | 1733 | 210 | 172
| 146 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 79 | 81 | 80 | 80
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
| 147 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 250 | 245 | 250 | 250 | 24
| 148 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
| 149 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
| 150 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 55 | 90 | 55 | 90 |  |  | Engine problem
| 151 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 3 | 0 | 8 | 0
| 152 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 0 | 72 | 0 | 34 |  | 81 | Fuel shortage
|  | Intraco Solar 30 MW |  | Solar | IPP | 0 | 0 | 0 | 17 | 0 | 0 | 0
|  | Rangpur Area Total |  |  |  |  | 800 | 720 | 404 | 488 | 393 | 454 | 64 | 166
|  | Total |  |  |  |  | 22482 | 21680 | 11418 | 13472 | 12677.6 | 14372 | 3137 | 2876
| A. |  | 2022-08-24 | (Yesterday) |  |  |  |  | Wednesday
| 1 | Highest Generation : |  |  | 13472 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 10753 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 14100 | MW
| 3 | Day peak Generation : |  |  | 11418 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 13556.31 | MW
| 4 | Evening peak Generation : |  |  | 13472 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 579 | MW
| 5 | Total Energy Generation : |  | 289.9278 | MKWHr | By Solar | 1.3218 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
|  | By Gas : | 148.128 | MKWHr |  | By Oil: | 77.8001 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 34.0472 | MKWHr |  | By Hydro: | 3.5447 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 3137 | MW | Dhaka | 4849.4 | 4699.4 |  | 150 |  | 18:00 |  | 396
|  |  |  | For Plants S/D or M/C prob = |  |  | 2876 | MW | Chittagong | 1319.5 | 1319.5 |  | 0 |  | 19:00 |  | 676
|  |  |  | Total = |  |  | 6013 | MW | Khulna | 1580.6 | 1580.6 |  | 0 |  | 19:30 |  | 595
| 7 | Total Gas Supplied : |  |  | 1110.59 | MMCFD |  |  | Rajshahi | 1439 | 1439 |  | 0 |  | 20:00 |  | 535
| 8 | Fuel Cost : | i) Gas : | Taka | 166910033.776 | ii) Oil : | Taka | 1158902411.31 | Comilla | 1258 | 1228 |  | 30 |  | 21:00 |  | 579
|  |  | iii) Coal : |  | 278104299.42 | Total | Taka | 1603916744.506 | Mymensingh | 1222 | 902 |  | 320 |  | 22:00 |  | 495
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0 | MKWHr. | Sylhet | 608 | 529 |  | 79 |  | 23:00 |  | 445
|  | ii) During Peak Demand : |  |  | 515 | MW (E to W) at | 21:00 | hrs | Barisal | 355.81 | 355.81 |  | 0 |  | 24:00 |  | 875
|  | iii) Maximum : |  |  | 515 | MW at | 21:00 | hrs | Rangpur | 924 | 924 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 32.9° C |  |  | Total | 13556.31 | 12977.31 |  | 579
| B. |  | 2022-08-25 | (Today) |  |  |  | Thursday |  |  | Probable max. temperature in Dhaka |  |  | 33.3° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 14100 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14372 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 12200 | MW
| 4 | Reserve(Generation end) |  |  |  | 272 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 303.4429 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 11115 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.536 | MKWHr. | ii) HVDC Flow at Peak Time |  | 887 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.5501 | MKWHr. | iii) Maximum HVDC Flow : |  | 895 | MW at | 1:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 95.15 |  | (b) Today: | 95.27 |  | (c) Rule Curve: |  | 96.69
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2022-08-24
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 300 | 91 | 0 | 398 | 252 |  | 0 | 290 | 0 | 8 | 0 | 30 | 140 | 0 | 0 | 7 | 8 | 126 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 25 | 25 | 33 | 30 | 8 | 0 | 81 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 8 | 34 | 17 | 10 | 11 | 25 | 14 | 38 | 0 | 0 | 0 | 315 | 275 | 208 | 8 | 143 | 40 | 56 | 0 | 51 | 0 | 42 | 0 | 19 | 9 | 25 | 18 | 160 | 107 | 0 | 0 | 0 | 43 | 30 | 5 | 0 | 0 | 0 | 60 | 81 | 0 | 193 | 0 | 6 | 10 | 280 | 8 | 0 | 194 | 97 | 180 | 80 | 57 | 70 | 70 | 0 | 10 | 85 | 132 | 402 | 50 | 17 | 73 | 0 | 52 | 36 | 110 | 17 | 41 | 10 | 400 | 17 | 0 | 25 | 107 | 0 | 35 | 0 | 97 | 55 | 0 | 0 | 0 |  | 895 | 0 | 260 | 0 | 16 | 227 | 0 | 0 | 10 | 38 | 0 | 152 | 30 | 32 | 0 | 0 | 0 | 32 | 23 | 31 | 0 | 42 | 24 | 8 | 0 | 22 | 0 | 11 | 83 | 0 | 250 | 0 | 0 | 214 | 0 | 0 | 217 | 0 | 92 | 199 | 0 | 414 | 0 | 165 | 50 | 15 | 56 | 0 | 0 | 55 | 1160 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 7211 | 4831 | 12042 | 4405 | 895 | 1642 | 781 | 1694 | 1493 | 151 | 444 | 594 | 160 | 0 | 1343.6564 | 95.1
2:00 | 0 | 0 | 0 | 180 | 300 | 91 | 0 | 399 | 253 |  | 0 | 290 | 0 | 8 | 0 | 30 | 145 | 0 | 0 | 7 | 8 | 125 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 25 | 25 | 33 | 30 | 8 | 0 | 81 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 34 | 17 | 10 | 11 | 25 | 14 | 38 | 0 | 0 | 0 | 315 | 275 | 210 | 8 | 142 | 40 | 56 | 0 | 51 | 0 | 42 | 0 | 19 | 9 | 25 | 18 | 150 | 107 | 0 | 0 | 0 | 43 | 30 | 5 | 0 | 0 | 0 | 60 | 81 | 0 | 193 | 0 | 6 | 10 | 290 | 8 | 0 | 195 | 97 | 150 | 75 | 57 | 70 | 71 | 0 | 10 | 85 | 135 | 401 | 50 | 17 | 69 | 0 | 52 | 36 | 110 | 17 | 40 | 10 | 400 | 0 | 0 | 24 | 92 | 0 | 35 | 0 | 82 | 55 | 0 | 0 | 0 |  | 894 | 0 | 265 | 0 | 0 | 227 | 0 | 0 | 4 | 29 | 0 | 152 | 29 | 32 | 0 | 0 | 0 | 32 | 23 | 0 | 0 | 42 | 0 | 8 | 0 | 22 | 0 | 11 | 83 | 0 | 250 | 0 | 0 | 214 | 0 | 0 | 217 | 0 | 92 | 201 | 0 | 414 | 0 | 165 | 50 | 15 | 56 | 0 | 0 | 55 | 1170 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 7138 | 4760 | 11898 | 4418 | 894 | 1652 | 747 | 1633 | 1503 | 151 | 444 | 523 | 150 | 0 | 1199.8906 | 95.11
3:00 | 0 | 0 | 0 | 180 | 300 | 91 | 0 | 399 | 251 |  | 0 | 290 | 0 | 0 | 0 | 30 | 145 | 0 | 0 | 7 | 8 | 125 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 25 | 25 | 33 | 30 | 8 | 0 | 81 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 33 | 17 | 10 | 12 | 25 | 14 | 38 | 0 | 0 | 0 | 315 | 275 | 210 | 8 | 143 | 40 | 56 | 0 | 51 | 0 | 43 | 0 | 19 | 9 | 25 | 18 | 154 | 108 | 0 | 0 | 0 | 43 | 30 | 5 | 0 | 0 | 0 | 60 | 81 | 0 | 193 | 0 | 6 | 10 | 290 | 8 | 0 | 195 | 97 | 151 | 75 | 57 | 70 | 71 | 0 | 10 | 85 | 132 | 401 | 49 | 17 | 69 | 0 | 52 | 36 | 110 | 17 | 28 | 10 | 401 | 0 | 0 | 38 | 107 | 0 | 35 | 0 | 96 | 55 | 0 | 0 | 0 |  | 895 | 0 | 270 | 0 | 0 | 227 | 0 | 0 | 0 | 32 | 0 | 152 | 28 | 32 | 0 | 0 | 0 | 32 | 23 | 0 | 0 | 42 | 0 | 8 | 0 | 22 | 0 | 11 | 82 | 0 | 250 | 0 | 0 | 214 | 0 | 0 | 217 | 0 | 70 | 200 | 0 | 414 | 0 | 165 | 50 | 15 | 56 | 0 | 0 | 55 | 1130 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 7164 | 4722 | 11886 | 4425 | 895 | 1671 | 726 | 1653 | 1462 | 151 | 444 | 522 | 154 | 0 | 842.3196 | 95.12
4:00 | 0 | 0 | 0 | 180 | 300 | 91 | 0 | 398 | 252 |  | 0 | 290 | 0 | 0 | 0 | 30 | 145 | 0 | 0 | 7 | 8 | 62 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 25 | 26 | 33 | 30 | 8 | 0 | 79 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 33 | 17 | 10 | 11 | 25 | 14 | 39 | 0 | 0 | 0 | 315 | 275 | 209 | 8 | 143 | 40 | 56 | 0 | 51 | 0 | 43 | 0 | 19 | 9 | 25 | 18 | 152 | 108 | 0 | 0 | 0 | 43 | 30 | 5 | 0 | 0 | 0 | 60 | 81 | 0 | 193 | 0 | 6 | 10 | 280 | 8 | 0 | 195 | 97 | 101 | 80 | 57 | 70 | 71 | 0 | 10 | 85 | 133 | 401 | 49 | 17 | 69 | 0 | 52 | 22 | 110 | 17 | 28 | 10 | 400 | 0 | 0 | 36 | 107 | 0 | 35 | 0 | 96 | 55 | 0 | 0 | 0 |  | 895 | 0 | 275 | 0 | 0 | 227 | 0 | 0 | 0 | 32 | 0 | 152 | 27 | 32 | 0 | 0 | 0 | 32 | 23 | 0 | 0 | 42 | 0 | 8 | 0 | 22 | 0 | 11 | 81 | 0 | 250 | 0 | 0 | 214 | 0 | 0 | 218 | 0 | 50 | 201 | 0 | 414 | 0 | 171 | 50 | 15 | 56 | 0 | 0 | 55 | 1110 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 7026 | 4723 | 11749 | 4429 | 895 | 1692 | 667 | 1637 | 1441 | 149 | 445 | 460 | 152 | 0 | 692.1028 | 95.13
5:00 | 0 | 0 | 0 | 180 | 300 | 91 | 0 | 398 | 252 |  | 0 | 290 | 0 | 0 | 0 | 30 | 145 | 0 | 0 | 7 | 8 | 14 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 25 | 26 | 33 | 33 | 8 | 0 | 79 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 33 | 17 | 10 | 11 | 25 | 14 | 39 | 0 | 0 | 0 | 315 | 275 | 209 | 8 | 143 | 40 | 56 | 0 | 51 | 0 | 45 | 0 | 19 | 9 | 25 | 20 | 144 | 106 | 0 | 0 | 0 | 43 | 30 | 5 | 0 | 0 | 0 | 60 | 81 | 0 | 193 | 0 | 6 | 10 | 270 | 8 | 0 | 195 | 97 | 62 | 80 | 57 | 70 | 71 | 0 | 10 | 85 | 132 | 402 | 49 | 17 | 69 | 0 | 52 | 36 | 110 | 17 | 28 | 10 | 397 | 16 | 0 | 36 | 107 | 0 | 35 | 0 | 96 | 55 | 0 | 0 | 0 |  | 894 | 0 | 270 | 0 | 0 | 227 | 0 | 0 | 0 | 32 | 0 | 152 | 26 | 16 | 0 | 0 | 0 | 32 | 23 | 0 | 0 | 42 | 0 | 8 | 0 | 22 | 0 | 11 | 81 | 0 | 250 | 0 | 0 | 214 | 0 | 0 | 219 | 0 | 10 | 202 | 0 | 414 | 0 | 161 | 50 | 15 | 56 | 0 | 0 | 55 | 1070 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6953 | 4662 | 11615 | 4426 | 894 | 1731 | 578 | 1650 | 1401 | 149 | 446 | 415 | 144 | 0 | 539.1214 | 95.14
6:00 | 0 | 0 | 0 | 180 | 300 | 91 | 0 | 397 | 251 |  | 0 | 290 | 0 | 0 | 0 | 30 | 160 | 0 | 0 | 7 | 8 | 14 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 25 | 26 | 33 | 33 | 8 | 0 | 81 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 33 | 17 | 10 | 12 | 25 | 14 | 39 | 0 | 0 | 0 | 325 | 275 | 212 | 8 | 144 | 40 | 57 | 0 | 51 | 0 | 45 | 0 | 19 | 9 | 25 | 20 | 128 | 107 | 0 | 0 | 0 | 43 | 30 | 5 | 0 | 0 | 0 | 65 | 60 | 0 | 193 | 0 | 6 | 10 | 255 | 8 | 0 | 160 | 97 | 27 | 0 | 57 | 0 | 71 | 0 | 10 | 85 | 132 | 401 | 49 | 17 | 69 | 0 | 52 | 36 | 110 | 17 | 28 | 10 | 400 | 17 | 1 | 36 | 107 | 0 | 35 | 1 | 96 | 55 | 0 | 0 | 0 |  | 894 | 0 | 275 | 0 | 0 | 205 | 0 | 0 | 0 | 32 | 0 | 152 | 23 | 16 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 42 | 0 | 8 | 0 | 0 | 0 | 11 | 80 | 0 | 250 | 0 | 0 | 214 | 0 | 0 | 190 | 0 | 0 | 202 | 0 | 414 | 0 | 0 | 50 | 15 | 56 | 0 | 0 | 55 | 1020 | 110 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 |  | 6723 | 4348 | 11071 | 4467 | 894 | 1670 | 187 | 1652 | 1350 | 151 | 395 | 363 | 128 | 4 | 579.6707 | 95.15
7:00 | 0 | 0 | 0 | 180 | 300 | 91 | 0 | 398 | 242 |  | 0 | 290 | 0 | 0 | 0 | 30 | 160 | 0 | 0 | 7 | 8 | 15 | 0 | 0 | 0 | 0 | 17 | 17 | 35 | 19 | 25 | 26 | 33 | 33 | 8 | 0 | 81 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 33 | 17 | 10 | 11 | 26 | 14 | 35 | 0 | 0 | 0 | 322 | 275 | 209 | 8 | 143 | 37 | 56 | 0 | 51 | 0 | 43 | 0 | 19 | 9 | 25 | 20 | 124 | 107 | 0 | 0 | 0 | 43 | 30 | 5 | 0 | 0 | 0 | 60 | 10 | 0 | 193 | 0 | 6 | 10 | 295 | 8 | 0 | 160 | 95 | 0 | 0 | 57 | 0 | 71 | 1 | 10 | 85 | 128 | 402 | 49 | 17 | 69 | 1 | 52 | 36 | 110 | 17 | 28 | 10 | 400 | 17 | 12 | 35 | 107 | 0 | 35 | 4 | 96 | 55 | 0 | 0 | 0 |  | 894 | 0 | 275 | 0 | 0 | 194 | 0 | 0 | 0 | 27 | 0 | 107 | 20 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 42 | 0 | 8 | 0 | 18 | 0 | 11 | 80 | 0 | 250 | 0 | 0 | 214 | 0 | 0 | 130 | 0 | 0 | 203 | 0 | 414 | 2 | 0 | 50 | 15 | 56 | 0 | 1 | 55 | 990 | 110 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 4 |  | 6645 | 4215 | 10860 | 4410 | 894 | 1661 | 160 | 1613 | 1320 | 151 | 324 | 297 | 124 | 36 | 497.6505 | 95.16
8:00 | 0 | 0 | 0 | 180 | 300 | 91 | 0 | 392 | 240 |  | 0 | 290 | 0 | 0 | 0 | 38 | 160 | 0 | 0 | 7 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 17 | 35 | 19 | 25 | 10 | 33 | 33 | 8 | 0 | 78 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 33 | 17 | 10 | 11 | 25 | 14 | 13 | 0 | 0 | 0 | 305 | 325 | 198 | 8 | 144 | 37 | 56 | 0 | 51 | 0 | 42 | 0 | 19 | 10 | 25 | 18 | 124 | 81 | 0 | 0 | 1 | 43 | 30 | 5 | 0 | 0 | 0 | 58 | 10 | 0 | 193 | 0 | 6 | 10 | 280 | 8 | 0 | 60 | 95 | 0 | 0 | 57 | 0 | 71 | 4 | 10 | 85 | 125 | 400 | 49 | 17 | 69 | 1 | 52 | 36 | 110 | 17 | 28 | 10 | 395 | 17 | 29 | 35 | 107 | 0 | 35 | 10 | 80 | 55 | 0 | 0 | 0 |  | 894 | 0 | 265 | 0 | 0 | 190 | 0 | 0 | 0 | 27 | 0 | 100 | 17 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 42 | 0 | 8 | 0 | 22 | 0 | 11 | 80 | 0 | 250 | 0 | 0 | 214 | 0 | 0 | 130 | 0 | 0 | 206 | 0 | 414 | 17 | 0 | 50 | 15 | 56 | 0 | 2 | 55 | 1010 | 110 | 0 | 0 | 1 | 38 | 0 | 0 | 0 | 0 | 14 |  | 6483 | 4270 | 10753 | 4361 | 894 | 1623 | 60 | 1616 | 1340 | 148 | 320 | 297 | 124 | 100 | #REF! | 95.17
9:00 | 0 | 0 | 0 | 180 | 300 | 86 | 0 | 395 | 242 |  | 0 | 290 | 0 | 0 | 0 | 55 | 160 | 0 | 0 | 7 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 19 | 25 | 10 | 33 | 33 | 8 | 0 | 82 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 33 | 17 | 10 | 11 | 25 | 14 | 7 | 0 | 0 | 0 | 300 | 300 | 200 | 8 | 144 | 39 | 56 | 0 | 51 | 0 | 42 | 0 | 19 | 10 | 25 | 18 | 128 | 80 | 0 | 0 | 1 | 43 | 30 | 5 | 0 | 0 | 0 | 55 | 10 | 0 | 194 | 0 | 6 | 10 | 310 | 8 | 0 | 60 | 107 | 106 | 50 | 57 | 50 | 121 | 9 | 10 | 85 | 123 | 404 | 49 | 17 | 69 | 3 | 52 | 36 | 110 | 17 | 36 | 10 | 394 | 17 | 17 | 35 | 107 | 0 | 35 | 16 | 78 | 55 | 0 | 0 | 0 |  | 894 | 0 | 220 | 0 | 0 | 140 | 0 | 0 | 0 | 27 | 0 | 101 | 17 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 42 | 0 | 8 | 0 | 22 | 0 | 11 | 79 | 0 | 250 | 0 | 0 | 208 | 0 | 0 | 130 | 0 | 0 | 197 | 0 | 414 | 17 | 0 | 50 | 15 | 56 | 0 | 3 | 55 | 950 | 110 | 0 | 0 | 5 | 28 | 0 | 0 | 0 | 0 | 16 |  | 6744 | 4097 | 10841 | 4279 | 894 | 1644 | 266 | 1664 | 1279 | 152 | 270 | 297 | 128 | 98 | #REF! | 95.18
10:00 | 0 | 0 | 0 | 180 | 300 | 84 | 0 | 396 | 242 |  | 0 | 290 | 0 | 0 | 0 | 55 | 160 | 0 | 0 | 7 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 19 | 25 | 10 | 33 | 30 | 8 | 0 | 36 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 33 | 17 | 10 | 11 | 25 | 11 | 3 | 0 | 0 | 0 | 300 | 300 | 204 | 8 | 143 | 35 | 52 | 0 | 51 | 0 | 42 | 0 | 19 | 10 | 21 | 18 | 124 | 69 | 0 | 0 | 2 | 43 | 30 | 5 | 0 | 0 | 0 | 55 | 10 | 0 | 194 | 0 | 6 | 10 | 300 | 8 | 0 | 120 | 225 | 156 | 80 | 94 | 80 | 149 | 19 | 10 | 68 | 122 | 405 | 69 | 17 | 69 | 4 | 52 | 36 | 110 | 0 | 26 | 10 | 395 | 17 | 55 | 35 | 107 | 0 | 35 | 26 | 78 | 55 | 0 | 0 | 0 |  | 893 | 0 | 200 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 42 | 0 | 8 | 0 | 21 | 0 | 11 | 79 | 0 | 250 | 0 | 0 | 204 | 0 | 0 | 130 | 0 | 0 | 196 | 0 | 414 | 0 | 0 | 50 | 15 | 53 | 0 | 4 | 55 | 950 | 110 | 0 | 0 | 5 | 33 | 0 | 0 | 0 | 0 | 17 |  | 7043 | 4013 | 11056 | 4239 | 893 | 1622 | 436 | 1802 | 1279 | 106 | 250 | 270 | 124 | 165 | #REF! | 95.19
11:00 | 0 | 0 | 0 | 180 | 300 | 84 | 0 | 401 | 332 |  | 0 | 300 | 0 | 0 | 0 | 55 | 0 | 0 | 97 | 7 | 8 | 46 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 19 | 25 | 10 | 33 | 16 | 8 | 0 | 36 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 17 | 17 | 10 | 11 | 25 | 14 | 2 | 0 | 0 | 0 | 300 | 300 | 209 | 8 | 143 | 30 | 49 | 0 | 51 | 0 | 42 | 0 | 19 | 10 | 16 | 18 | 146 | 68 | 0 | 0 | 2 | 43 | 30 | 5 | 0 | 0 | 0 | 55 | 10 | 0 | 194 | 0 | 6 | 10 | 300 | 8 | 0 | 180 | 245 | 225 | 80 | 96 | 80 | 149 | 13 | 10 | 68 | 120 | 404 | 69 | 17 | 69 | 3 | 85 | 36 | 110 | 0 | 28 | 10 | 396 | 17 | 31 | 35 | 107 | 0 | 35 | 14 | 77 | 55 | 0 | 0 | 0 |  | 894 | 0 | 200 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 105 | 17 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 42 | 0 | 8 | 0 | 18 | 0 | 11 | 79 | 0 | 250 | 0 | 0 | 199 | 0 | 0 | 133 | 0 | 0 | 196 | 0 | 414 | 0 | 1 | 50 | 15 | 53 | 0 | 4 | 55 | 900 | 110 | 0 | 0 | 5 | 12 | 0 | 0 | 0 | 0 | 18 |  | 7240 | 3971 | 11211 | 4159 | 894 | 1716 | 566 | 1856 | 1229 | 106 | 283 | 287 | 146 | 102 | #REF! | 95.2
12:00 | 0 | 0 | 0 | 180 | 300 | 87 | 0 | 402 | 332 |  | 0 | 300 | 0 | 0 | 0 | 55 | 0 | 0 | 92 | 7 | 8 | 46 | 0 | 0 | 0 | 0 | 35 | 17 | 0 | 19 | 25 | 10 | 33 | 26 | 8 | 0 | 81 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 10 | 17 | 17 | 10 | 11 | 25 | 14 | 2 | 0 | 0 | 0 | 300 | 300 | 207 | 8 | 144 | 30 | 52 | 0 | 51 | 0 | 42 | 0 | 20 | 10 | 24 | 18 | 150 | 68 | 0 | 0 | 3 | 43 | 30 | 5 | 0 | 0 | 0 | 58 | 10 | 0 | 194 | 0 | 6 | 10 | 270 | 8 | 0 | 160 | 243 | 225 | 80 | 96 | 81 | 149 | 19 | 10 | 68 | 120 | 403 | 69 | 17 | 69 | 5 | 88 | 17 | 110 | 0 | 28 | 10 | 401 | 17 | 50 | 40 | 107 | 0 | 35 | 19 | 68 | 55 | 0 | 0 | 0 |  | 894 | 0 | 250 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 112 | 14 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 42 | 0 | 8 | 0 | 20 | 0 | 11 | 79 | 0 | 250 | 0 | 0 | 192 | 0 | 0 | 204 | 0 | 0 | 202 | 0 | 414 | 0 | 20 | 50 | 15 | 55 | 0 | 3 | 55 | 890 | 115 | 0 | 0 | 3 | 27 | 0 | 0 | 0 | 0 | 17 |  | 7294 | 4124 | 11418 | 4236 | 894 | 1696 | 566 | 1852 | 1219 | 151 | 354 | 358 | 150 | 146 | #REF! | 95.2
13:00 | 0 | 0 | 0 | 180 | 300 | 86 | 0 | 402 | 320 |  | 0 | 300 | 0 | 0 | 0 | 55 | 4 | 0 | 93 | 7 | 8 | 46 | 0 | 0 | 0 | 0 | 35 | 17 | 0 | 19 | 25 | 10 | 33 | 26 | 8 | 0 | 79 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 4 | 17 | 17 | 10 | 11 | 25 | 16 | 2 | 0 | 0 | 0 | 300 | 300 | 204 | 8 | 143 | 31 | 51 | 0 | 51 | 0 | 42 | 0 | 20 | 5 | 25 | 18 | 156 | 68 | 0 | 0 | 2 | 43 | 30 | 5 | 0 | 0 | 0 | 56 | 10 | 0 | 194 | 0 | 6 | 10 | 290 | 8 | 0 | 194 | 245 | 225 | 80 | 95 | 81 | 149 | 6 | 10 | 68 | 113 | 404 | 69 | 17 | 57 | 6 | 88 | 17 | 110 | 0 | 28 | 10 | 400 | 17 | 44 | 72 | 107 | 0 | 35 | 24 | 76 | 40 | 0 | 0 | 0 |  | 893 | 0 | 230 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 114 | 15 | 16 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 42 | 0 | 8 | 0 | 19 | 0 | 11 | 80 | 0 | 250 | 0 | 0 | 197 | 0 | 0 | 213 | 0 | 0 | 208 | 0 | 414 | 0 | 44 | 50 | 32 | 55 | 0 | 4 | 55 | 930 | 110 | 0 | 0 | 5 | 78 | 0 | 0 | 0 | 0 | 36 |  | 7323 | 4291 | 11614 | 4227 | 893 | 1697 | 624 | 1886 | 1260 | 149 | 363 | 367 | 156 | 205 | 632 | 95.22
14:00 | 0 | 0 | 0 | 180 | 300 | 89 | 0 | 401 | 320 |  | 0 | 300 | 0 | 0 | 0 | 55 | 4 | 0 | 97 | 8 | 8 | 46 | 0 | 0 | 0 | 0 | 35 | 35 | 0 | 19 | 25 | 14 | 33 | 26 | 8 | 0 | 76 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 7 | 17 | 17 | 10 | 11 | 25 | 16 | 2 | 0 | 0 | 0 | 300 | 300 | 202 | 8 | 143 | 28 | 51 | 0 | 51 | 0 | 40 | 0 | 19 | 10 | 25 | 12 | 162 | 68 | 0 | 0 | 0 | 43 | 30 | 5 | 0 | 0 | 0 | 58 | 10 | 0 | 194 | 0 | 6 | 10 | 280 | 8 | 0 | 193 | 245 | 108 | 80 | 95 | 80 | 149 | 17 | 10 | 68 | 113 | 405 | 69 | 17 | 63 | 2 | 88 | 17 | 110 | 0 | 28 | 10 | 391 | 17 | 55 | 82 | 107 | 0 | 35 | 6 | 76 | 55 | 0 | 0 | 0 |  | 886 | 0 | 250 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 114 | 18 | 16 | 0 | 0 | 0 | 32 | 5 | 0 | 0 | 42 | 0 | 8 | 0 | 19 | 0 | 11 | 79 | 0 | 250 | 0 | 0 | 210 | 0 | 0 | 212 | 0 | 0 | 205 | 0 | 414 | 0 | 80 | 50 | 32 | 55 | 0 | 6 | 55 | 930 | 151 | 0 | 0 | 3 | 33 | 0 | 0 | 0 | 0 | 0 |  | 7243 | 4316 | 11559 | 4251 | 886 | 1734 | 541 | 1939 | 1259 | 146 | 362 | 369 | 162 | 122 | 635.8867 | 95.23
15:00 | 0 | 0 | 0 | 180 | 300 | 84 | 0 | 402 | 320 |  | 0 | 300 | 0 | 4 | 0 | 55 | 1 | 0 | 97 | 8 | 8 | 45 | 0 | 0 | 0 | 0 | 35 | 35 | 0 | 19 | 25 | 27 | 33 | 28 | 8 | 0 | 73 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 11 | 17 | 16 | 10 | 11 | 25 | 16 | 3 | 0 | 0 | 0 | 325 | 320 | 203 | 8 | 138 | 28 | 50 | 0 | 51 | 0 | 44 | 0 | 19 | 10 | 25 | 17 | 166 | 99 | 0 | 0 | 1 | 43 | 30 | 5 | 0 | 0 | 0 | 58 | 10 | 0 | 194 | 0 | 6 | 10 | 300 | 8 | 0 | 194 | 253 | 225 | 80 | 95 | 80 | 149 | 15 | 10 | 68 | 118 | 405 | 69 | 17 | 69 | 3 | 88 | 36 | 110 | 0 | 28 | 10 | 386 | 17 | 44 | 108 | 107 | 0 | 35 | 29 | 77 | 55 | 0 | 0 | 0 |  | 886 | 0 | 220 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 115 | 18 | 16 | 0 | 0 | 0 | 32 | 5 | 0 | 0 | 42 | 0 | 8 | 0 | 18 | 0 | 11 | 78 | 0 | 250 | 0 | 0 | 207 | 0 | 0 | 211 | 0 | 0 | 203 | 0 | 414 | 0 | 20 | 50 | 32 | 55 | 0 | 5 | 55 | 910 | 167 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 9 |  | 7549 | 4217 | 11766 | 4302 | 886 | 1764 | 599 | 2012 | 1238 | 143 | 361 | 370 | 166 | 136 | 584.2785 | 95.24
16:00 | 0 | 0 | 0 | 180 | 300 | 85 | 0 | 401 | 320 |  | 0 | 300 | 0 | 7 | 0 | 55 | 9 | 0 | 97 | 8 | 8 | 45 | 0 | 0 | 0 | 0 | 35 | 48 | 0 | 19 | 25 | 27 | 33 | 28 | 8 | 0 | 73 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 17 | 16 | 10 | 11 | 25 | 16 | 5 | 0 | 0 | 0 | 325 | 305 | 205 | 8 | 137 | 25 | 51 | 0 | 43 | 0 | 43 | 0 | 19 | 10 | 25 | 17 | 152 | 99 | 0 | 0 | 0 | 43 | 30 | 5 | 0 | 0 | 0 | 58 | 10 | 0 | 194 | 0 | 6 | 10 | 290 | 8 | 0 | 150 | 250 | 227 | 80 | 95 | 80 | 142 | 10 | 10 | 68 | 120 | 404 | 69 | 31 | 69 | 1 | 87 | 36 | 110 | 0 | 40 | 10 | 393 | 17 | 12 | 108 | 90 | 0 | 35 | 19 | 78 | 55 | 0 | 0 | 0 |  | 886 | 0 | 220 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 116 | 18 | 16 | 0 | 0 | 0 | 32 | 7 | 0 | 0 | 34 | 0 | 8 | 0 | 18 | 0 | 11 | 80 | 0 | 250 | 0 | 0 | 214 | 0 | 0 | 214 | 0 | 0 | 203 | 0 | 418 | 10 | 0 | 72 | 32 | 55 | 0 | 3 | 90 | 900 | 162 | 0 | 0 | 3 | 62 | 0 | 0 | 0 | 0 | 7 |  | 7442 | 4291 | 11733 | 4306 | 886 | 1749 | 537 | 2089 | 1230 | 143 | 364 | 374 | 152 | 117 | 522.533 | 95.25
17:00 | 0 | 0 | 0 | 180 | 300 | 88 | 0 | 400 | 330 |  | 0 | 300 | 0 | 8 | 0 | 55 | 81 | 0 | 94 | 8 | 8 | 62 | 0 | 0 | 0 | 0 | 35 | 55 | 0 | 19 | 25 | 27 | 33 | 28 | 8 | 0 | 34 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 17 | 16 | 10 | 11 | 26 | 16 | 9 | 0 | 0 | 0 | 325 | 305 | 206 | 8 | 137 | 32 | 52 | 0 | 51 | 0 | 44 | 0 | 21 | 10 | 25 | 17 | 158 | 99 | 0 | 0 | 0 | 43 | 41 | 5 | 0 | 0 | 0 | 59 | 10 | 0 | 193 | 0 | 6 | 10 | 280 | 8 | 0 | 0 | 248 | 124 | 90 | 105 | 80 | 149 | 4 | 10 | 102 | 125 | 402 | 78 | 105 | 76 | 1 | 88 | 36 | 110 | 0 | 57 | 10 | 394 | 17 | 13 | 117 | 107 | 0 | 35 | 2 | 77 | 54 | 0 | 0 | 0 |  | 887 | 0 | 220 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 116 | 17 | 16 | 0 | 0 | 0 | 32 | 14 | 0 | 0 | 42 | 0 | 8 | 0 | 18 | 0 | 11 | 81 | 0 | 250 | 0 | 0 | 214 | 0 | 0 | 180 | 0 | 0 | 203 | 0 | 300 | 17 | 0 | 93 | 32 | 67 | 0 | 1 | 95 | 890 | 160 | 0 | 0 | 1 | 39 | 0 | 0 | 0 | 0 | 5 |  | 7461 | 4129 | 11590 | 4394 | 887 | 1644 | 294 | 2337 | 1221 | 104 | 300 | 365 | 158 | 66 | 470.0032 | 95.25
18:00 | 0 | 0 | 0 | 180 | 300 | 88 | 0 | 401 | 326 |  | 0 | 300 | 0 | 22 | 0 | 55 | 253 | 0 | 0 | 36 | 40 | 62 | 0 | 0 | 0 | 0 | 54 | 55 | 0 | 19 | 25 | 27 | 33 | 24 | 31 | 0 | 74 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 44 | 16 | 10 | 70 | 38 | 16 | 11 | 0 | 0 | 0 | 280 | 270 | 208 | 8 | 137 | 35 | 54 | 0 | 51 | 0 | 44 | 1 | 22 | 10 | 25 | 17 | 142 | 100 | 0 | 0 | 0 | 43 | 41 | 5 | 0 | 0 | 0 | 59 | 10 | 0 | 193 | 0 | 6 | 10 | 270 | 8 | 0 | 0 | 278 | 0 | 0 | 115 | 0 | 149 | 0 | 10 | 180 | 132 | 365 | 98 | 105 | 87 | 0 | 52 | 17 | 110 | 0 | 94 | 10 | 334 | 50 | 1 | 162 | 107 | 0 | 35 | 1 | 77 | 55 | 0 | 0 | 0 |  | 886 | 0 | 220 | 0 | 0 | 120 | 0 | 0 | 5 | 0 | 0 | 92 | 18 | 16 | 0 | 0 | 0 | 32 | 26 | 8 | 0 | 42 | 0 | 8 | 0 | 20 | 0 | 11 | 80 | 0 | 250 | 0 | 0 | 214 | 0 | 0 | 130 | 0 | 0 | 207 | 0 | 243 | 17 | 0 | 94 | 67 | 89 | 0 | 1 | 95 | 880 | 163 | 0 | 0 | 0 | 1 | 34 | 0 | 0 | 0 | 1 |  | 7500 | 4070 | 11570 | 4279 | 886 | 1583 | 0 | 2834 | 1210 | 144 | 250 | 367 | 142 | 5 | 396 | 95.25
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 300 | 88 | 0 | 396 | 332 |  | 0 | 300 | 0 | 40 | 0 | 55 | 337 | 0 | 0 | 40 | 40 | 110 | 0 | 0 | 0 | 0 | 54 | 55 | 0 | 19 | 25 | 24 | 33 | 24 | 40 | 0 | 75 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 44 | 51 | 10 | 95 | 38 | 16 | 16 | 0 | 0 | 0 | 280 | 270 | 210 | 8 | 137 | 35 | 54 | 0 | 51 | 0 | 45 | 8 | 22 | 10 | 25 | 17 | 142 | 101 | 0 | 0 | 0 | 43 | 41 | 5 | 0 | 0 | 0 | 64 | 78 | 0 | 193 | 0 | 6 | 10 | 280 | 8 | 0 | 20 | 278 | 25 | 90 | 96 | 90 | 149 | 0 | 10 | 180 | 135 | 402 | 108 | 105 | 87 | 0 | 52 | 17 | 110 | 0 | 113 | 10 | 395 | 55 | 0 | 162 | 107 | 0 | 35 | 0 | 78 | 55 | 0 | 0 | 0 |  | 886 | 0 | 275 | 0 | 16 | 170 | 0 | 0 | 38 | 7 | 0 | 106 | 20 | 32 | 0 | 0 | 0 | 32 | 26 | 30 | 0 | 50 | 32 | 43 | 32 | 21 | 0 | 11 | 80 | 0 | 250 | 0 | 0 | 203 | 0 | 0 | 146 | 0 | 10 | 192 | 0 | 418 | 17 | 15 | 94 | 67 | 89 | 0 | 0 | 95 | 910 | 161 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 |  | 8161 | 4608 | 12769 | 4504 | 886 | 1848 | 250 | 2991 | 1240 | 145 | 316 | 593 | 142 | 0 | 676 | 95.25
19:30 | 0 | 0 | 0 | 180 | 300 | 91 | 0 | 401 | 332 |  | 0 | 300 | 0 | 41 | 0 | 55 | 336 | 0 | 0 | 40 | 40 | 110 | 0 | 0 | 0 | 0 | 54 | 55 | 0 | 19 | 25 | 27 | 33 | 28 | 40 | 0 | 76 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 42 | 51 | 10 | 95 | 38 | 16 | 20 | 0 | 0 | 0 | 290 | 280 | 207 | 8 | 136 | 35 | 55 | 0 | 51 | 0 | 45 | 8 | 22 | 10 | 25 | 17 | 146 | 108 | 0 | 0 | 0 | 43 | 41 | 5 | 0 | 0 | 0 | 64 | 78 | 0 | 193 | 0 | 6 | 10 | 290 | 8 | 0 | 20 | 278 | 25 | 90 | 97 | 90 | 149 | 0 | 10 | 180 | 137 | 403 | 108 | 105 | 87 | 0 | 52 | 17 | 110 | 0 | 116 | 20 | 400 | 55 | 0 | 162 | 107 | 0 | 35 | 0 | 78 | 55 | 0 | 0 | 0 |  | 886 | 0 | 280 | 0 | 16 | 226 | 0 | 0 | 45 | 16 | 0 | 116 | 21 | 32 | 0 | 0 | 0 | 32 | 26 | 66 | 0 | 50 | 32 | 43 | 32 | 21 | 0 | 11 | 81 | 0 | 250 | 0 | 0 | 214 | 0 | 0 | 173 | 0 | 20 | 192 | 0 | 415 | 17 | 50 | 94 | 67 | 89 | 0 | 0 | 95 | 1010 | 163 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 |  | 8239 | 4915 | 13154 | 4570 | 886 | 1866 | 295 | 3008 | 1341 | 146 | 399 | 670 | 146 | 0 | 595 | 0
20:00 | 0 | 0 | 0 | 180 | 300 | 88 | 0 | 400 | 332 |  | 0 | 300 | 0 | 41 | 0 | 55 | 337 | 0 | 0 | 40 | 40 | 110 | 0 | 0 | 0 | 0 | 54 | 55 | 13 | 19 | 28 | 27 | 33 | 28 | 40 | 0 | 81 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 43 | 51 | 10 | 95 | 38 | 16 | 22 | 0 | 0 | 0 | 330 | 300 | 208 | 8 | 136 | 44 | 55 | 0 | 51 | 0 | 45 | 8 | 22 | 10 | 25 | 17 | 156 | 107 | 0 | 0 | 0 | 43 | 41 | 5 | 0 | 0 | 0 | 64 | 81 | 0 | 193 | 0 | 6 | 10 | 270 | 8 | 0 | 20 | 278 | 25 | 90 | 96 | 90 | 148 | 0 | 10 | 180 | 133 | 403 | 109 | 105 | 87 | 0 | 52 | 17 | 110 | 0 | 117 | 20 | 401 | 55 | 0 | 162 | 107 | 0 | 35 | 0 | 77 | 55 | 0 | 0 | 0 |  | 886 | 0 | 280 | 0 | 16 | 226 | 0 | 0 | 33 | 42 | 0 | 116 | 21 | 32 | 0 | 0 | 0 | 32 | 26 | 82 | 0 | 50 | 32 | 43 | 32 | 21 | 0 | 11 | 79 | 0 | 250 | 0 | 0 | 214 | 0 | 0 | 181 | 0 | 20 | 192 | 0 | 417 | 17 | 50 | 94 | 67 | 90 | 0 | 0 | 95 | 1030 | 164 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 |  | 8318 | 5001 | 13319 | 4643 | 886 | 1851 | 295 | 3043 | 1359 | 151 | 407 | 709 | 156 | 0 | 535 | 95.25
21:00 | 0 | 0 | 0 | 180 | 300 | 91 | 0 | 400 | 332 |  | 0 | 300 | 0 | 41 | 0 | 55 | 338 | 0 | 0 | 40 | 40 | 125 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 27 | 33 | 30 | 31 | 0 | 82 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 43 | 51 | 10 | 95 | 38 | 16 | 30 | 0 | 0 | 0 | 330 | 305 | 209 | 8 | 136 | 40 | 56 | 0 | 51 | 0 | 46 | 8 | 22 | 10 | 25 | 17 | 148 | 107 | 0 | 0 | 0 | 43 | 41 | 5 | 0 | 0 | 0 | 64 | 81 | 0 | 193 | 0 | 6 | 10 | 290 | 8 | 0 | 0 | 278 | 122 | 90 | 97 | 90 | 140 | 0 | 10 | 180 | 133 | 403 | 109 | 105 | 87 | 0 | 52 | 17 | 110 | 0 | 115 | 10 | 401 | 55 | 0 | 162 | 107 | 0 | 35 | 0 | 77 | 55 | 0 | 0 | 0 |  | 887 | 0 | 280 | 0 | 16 | 226 | 0 | 0 | 26 | 62 | 0 | 86 | 22 | 32 | 0 | 0 | 0 | 32 | 26 | 82 | 0 | 42 | 32 | 43 | 32 | 22 | 0 | 11 | 81 | 0 | 245 | 0 | 0 | 214 | 0 | 0 | 216 | 0 | 0 | 190 | 0 | 419 | 17 | 0 | 94 | 67 | 90 | 0 | 0 | 95 | 1090 | 191 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 0 | 0 |  | 8432 | 5040 | 13472 | 4613 | 887 | 1914 | 302 | 3041 | 1416 | 152 | 442 | 773 | 148 | 0 | 579 | 95.25
22:00 | 0 | 0 | 0 | 180 | 300 | 91 | 0 | 401 | 332 |  | 0 | 300 | 0 | 42 | 0 | 55 | 337 | 0 | 0 | 40 | 40 | 110 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 27 | 33 | 30 | 33 | 0 | 76 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 34 | 51 | 10 | 95 | 38 | 16 | 35 | 0 | 0 | 0 | 330 | 305 | 209 | 8 | 136 | 42 | 56 | 0 | 51 | 0 | 46 | 8 | 22 | 10 | 25 | 17 | 158 | 107 | 0 | 0 | 0 | 43 | 41 | 5 | 0 | 0 | 0 | 58 | 81 | 0 | 193 | 0 | 6 | 10 | 300 | 8 | 0 | 0 | 278 | 103 | 90 | 106 | 90 | 149 | 0 | 10 | 155 | 142 | 402 | 99 | 105 | 87 | 0 | 52 | 17 | 110 | 0 | 117 | 10 | 401 | 55 | 0 | 162 | 107 | 0 | 35 | 0 | 77 | 55 | 0 | 0 | 0 |  | 886 | 0 | 280 | 0 | 16 | 226 | 0 | 0 | 21 | 73 | 0 | 86 | 22 | 32 | 0 | 0 | 0 | 31 | 26 | 82 | 0 | 42 | 32 | 43 | 32 | 22 | 0 | 11 | 80 | 0 | 240 | 0 | 0 | 214 | 0 | 0 | 217 | 0 | 0 | 188 | 0 | 421 | 17 | 0 | 94 | 67 | 90 | 0 | 0 | 95 | 1060 | 225 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 0 | 0 |  | 8400 | 5043 | 13443 | 4606 | 886 | 1965 | 283 | 3038 | 1380 | 146 | 443 | 755 | 158 | 0 | 495 | 95.25
23:00 | 0 | 0 | 0 | 180 | 300 | 91 | 0 | 401 | 331 |  | 0 | 300 | 0 | 34 | 0 | 55 | 337 | 0 | 0 | 40 | 40 | 90 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 27 | 33 | 30 | 33 | 0 | 76 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 30 | 51 | 10 | 48 | 38 | 16 | 36 | 0 | 0 | 0 | 325 | 305 | 209 | 8 | 136 | 42 | 56 | 0 | 51 | 0 | 46 | 8 | 22 | 10 | 25 | 17 | 158 | 107 | 0 | 0 | 0 | 43 | 41 | 5 | 0 | 0 | 0 | 59 | 81 | 0 | 193 | 0 | 6 | 10 | 300 | 8 | 0 | 100 | 278 | 206 | 90 | 107 | 90 | 149 | 0 | 10 | 155 | 143 | 402 | 99 | 105 | 87 | 0 | 52 | 17 | 110 | 0 | 115 | 10 | 401 | 55 | 0 | 162 | 92 | 0 | 35 | 0 | 78 | 55 | 0 | 0 | 0 |  | 886 | 0 | 280 | 0 | 16 | 227 | 0 | 0 | 15 | 70 | 0 | 86 | 23 | 32 | 0 | 0 | 0 | 32 | 26 | 67 | 0 | 42 | 32 | 8 | 32 | 22 | 0 | 11 | 81 | 0 | 240 | 0 | 0 | 214 | 0 | 0 | 216 | 0 | 3 | 189 | 0 | 420 | 17 | 6 | 94 | 32 | 90 | 0 | 0 | 95 | 1060 | 225 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 0 | 0 |  | 8506 | 4961 | 13467 | 4603 | 886 | 1965 | 495 | 2899 | 1381 | 146 | 443 | 707 | 158 | 0 | 445 | 95.25
24:00 | 0 | 0 | 0 | 180 | 300 | 91 | 0 | 399 | 334 |  | 0 | 300 | 0 | 11 | 0 | 55 | 335 | 0 | 0 | 16 | 8 | 90 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 19 | 25 | 25 | 33 | 30 | 8 | 0 | 76 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 34 | 51 | 10 | 10 | 28 | 16 | 37 | 0 | 0 | 0 | 325 | 305 | 212 | 8 | 137 | 42 | 56 | 0 | 51 | 0 | 46 | 8 | 22 | 10 | 25 | 17 | 158 | 107 | 0 | 0 | 0 | 43 | 41 | 5 | 0 | 0 | 0 | 65 | 81 | 0 | 193 | 0 | 6 | 10 | 270 | 8 | 0 | 110 | 278 | 102 | 80 | 107 | 70 | 149 | 0 | 10 | 107 | 140 | 401 | 99 | 17 | 90 | 0 | 52 | 17 | 110 | 0 | 102 | 10 | 401 | 38 | 0 | 48 | 107 | 0 | 35 | 0 | 79 | 55 | 0 | 0 | 0 |  | 887 | 0 | 280 | 0 | 16 | 229 | 0 | 0 | 15 | 55 | 0 | 86 | 23 | 32 | 0 | 0 | 0 | 32 | 26 | 23 | 0 | 42 | 24 | 8 | 32 | 22 | 0 | 11 | 80 | 0 | 250 | 0 | 0 | 214 | 0 | 0 | 219 | 0 | 40 | 189 | 0 | 425 | 0 | 88 | 50 | 15 | 56 | 0 | 0 | 55 | 1030 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 7927 | 4774 | 12701 | 4606 | 887 | 1939 | 490 | 2239 | 1360 | 146 | 448 | 647 | 158 | 0 | 875 | 95.25
KWH | 0 | 0 | 0 | 4284000 | 7227564 | 2107636 | 0 | 9728000 | 7002000 |  | 0 | 6613650 | 0 | 271680 | 0 | 1145451 | 3838283 | 0 | 673000 | 383702 | 384624 | 1565760 | 0 | 0 | 0 | 0 | 792720 | 887778 | 460572 | 426924 | 600000 | 519480 | 801100 | 707800 | 320640 | 0 | 1856669 | 1688000 | 2600000 | 0 | 624898 | 0 | 0 | 0 | 0 |  | 278160 | 713424 | 628480 | 261960 | 657600 | 690720 | 356784 | 507360 | 0 | 0 | 0 | 7882300 | 7196000 | 5000000 | 200727 | 3343770 | 851112 | 1300800 | 0 | 1208656 | 0 | 1053432 | 54034 | 471456 | 226980 | 590100 | 437980 | 3550080 | 2216640 | 0 | 0 | 13900 | 1024000 | 737808 | 128400 | 0 | 0 | 0 | 1420608 | 1111680 | 0 | 4682210 | 0 | 170200 | 243000 | 7020000 | 186144 | 0 | 2865408 | 4787344 | 2919533 | 1582573 | 1999200 | 1524872 | 2967552 | 118530 | 257280 | 2542080 | 3092872 | 9598000 | 1711200 | 1086600 | 1819091 | 29664 | 1462800 | 710766 | 2685552 | 172140 | 1340640 | 264000 | 9431100 | 584640 | 350030 | 1946880 | 2531673 | 0 | 887760 | 210110 | 1983360 | 1325160 | 0 | 0 | 0 |  | 21536000 | 0 | 6302880 | 0 | 94080 | 4527360 | 0 | 0 | 154080 | 539136 | 0 | 2860636 | 498847 | 463392 | 0 | 0 | 0 | 760880 | 307721 | 396728 | 0 | 969072 | 170290 | 313925 | 179240 | 462480 | 0 | 247068 | 1926982 | 0 | 6046900 | 0 | 0 | 5322291 | 0 | 0 | 4755145 | 0 | 460800 | 5024445 | 0 | 9750327 | 159360 | 1332808 | 1660320 | 791280 | 1555353 | 0 | 41715 | 1656480 | 26073300 | 2985820 | 0 | 0 | 37800 | 374400 | 326016 | 0 | 0 | 0 | 145640 |  | 178716846 | 111210997 | 289927843 | 106816463 | 21536000 | 41311583 | 10685994 | 51362407 | 34047182 | 3544669 | 9282505 | 6469171 | 3550080 | 1321789 | 0
Fuel Cost | 0 | 0 | 0 | 6383160 | 8094871.68 | 2803155.88 | 0 | 10214400 | 7562160 |  | 0 | 7208878.5 | 0 | 3037382.4 | 0 | 15177225.75 | 4298876.96 | 0 | 1177750 | 5609723.24 | 5411659.68 | 25380969.6 | 0 | 0 | 0 | 0 | 10083398.4 | 11985003 | 6176270.52 | 320193 | 450000 | 0 | 0 | 0 | 5454086.4 | 0 | 501300.63 | 455760 | 4914000 | 0 | 10217082.3 | 0 | 0 | 0 | 0 |  | 3629988 | 11899912.32 | 10696729.6 | 3539079.6 | 8338368 | 7991630.4 | 453115.68 | 1689508.8 | 0 | 0 | 0 | 8749353 | 7843640 | 5800000 | 258937.83 | 4079399.4 | 961756.56 | 1938192 | 0 | 2018455.52 | 0 | 18192770.64 | 726757.3 | 645894.72 | 170235 | 1032675 | 328485 | 25489574.4 | 2416137.6 | 0 | 0 | 221566 | 1402880 | 973906.56 | 223416 | 0 | 0 | 0 | 2755979.52 | 2534630.4 | 0 | 4729032.1 | 0 | 253598 | 481140 | 7020000 | 139608 | 0 | 60058951.68 | 65347245.6 | 61193411.68 | 32711783.91 | 26949216 | 31519104.24 | 41100595.2 | 1385615.7 | 2655129.6 | 34724812.8 | 41042411.44 | 8830160 | 20808192 | 15712236 | 23011501.15 | 0 | 17173272 | 7740241.74 | 28547417.76 | 2335939.8 | 17280849.6 | 3109920 | 8676612 | 7571088 | 5057933.5 | 24705907.2 | 28810438.74 | 0 | 11594145.6 | 2510814.5 | 29690899.2 | 17452357.2 | 0 | 0 | 0 |  | 64608000 | 0 | 7059225.6 | 0 | 979372.8 | 74701440 | 0 | 0 | 2774980.8 | 9704448 | 0 | 3203912.32 | 967763.18 | 5050972.8 | 0 | 0 | 0 | 12759957.6 | 5382040.29 | 6204825.92 | 0 | 16047832.32 | 2879603.9 | 4278797.75 | 3023778.8 | 957333.6 | 0 | 187030.476 | 11195765.42 | 0 | 31988101 | 0 | 0 | 6173857.56 | 0 | 0 | 83024831.7 | 0 | 9667584 | 5828356.2 | 0 | 9652823.73 | 2141798.4 | 27948983.76 | 19641585.6 | 11433996 | 19752983.1 | 0 | 460950.75 | 20109667.2 | 234920433 | 3045536.4 | 0 | 0 | 427518 | 4391712 | 4997825.28 | 0 | 0 | 0 | 0 |  | 981851864.73 | 727575625.256 | 1709427489.986 | 118294503.936 | 64608000 | 48615529.84 | 223099819.27 | 669176302.87 | 278104299.42 | 957060.63 | 157726271.7 | 108900017.47 | 25489574.4 | 14456110.45 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 300 | 87 | 0 | 402 | 332 |  | 0 | 300 | 0 | 0 | 0 | 55 | 0 | 0 | 92 | 7 | 8 | 46 | 0 | 0 | 0 | 0 | 35 | 17 | 0 | 19 | 25 | 10 | 33 | 26 | 8 | 0 | 81 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 10 | 17 | 17 | 10 | 11 | 25 | 14 | 2 | 0 | 0 | 0 | 300 | 300 | 207 | 8 | 144 | 30 | 52 | 0 | 51 | 0 | 42 | 0 | 20 | 10 | 24 | 18 | 150 | 68 | 0 | 0 | 3 | 43 | 30 | 5 | 0 | 0 | 0 | 58 | 10 | 0 | 194 | 0 | 6 | 10 | 270 | 8 | 0 | 160 | 243 | 225 | 80 | 96 | 81 | 149 | 19 | 10 | 68 | 120 | 403 | 69 | 17 | 69 | 5 | 88 | 17 | 110 | 0 | 28 | 10 | 401 | 17 | 50 | 40 | 107 | 0 | 35 | 19 | 68 | 55 | 0 | 0 | 0 |  | 894 | 0 | 250 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 112 | 14 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 42 | 0 | 8 | 0 | 20 | 0 | 11 | 79 | 0 | 250 | 0 | 0 | 192 | 0 | 0 | 204 | 0 | 0 | 202 | 0 | 414 | 0 | 20 | 50 | 15 | 55 | 0 | 3 | 55 | 890 | 115 | 0 | 0 | 3 | 27 | 0 | 0 | 0 | 0 | 17 |  | 11418 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 300 | 91 | 0 | 400 | 332 | 0 | 0 | 300 | 0 | 41 | 0 | 55 | 338 | 0 | 0 | 40 | 40 | 125 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 27 | 33 | 30 | 31 | 0 | 82 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 12 | 43 | 51 | 10 | 95 | 38 | 16 | 30 | 0 | 0 | 0 | 330 | 305 | 209 | 8 | 136 | 40 | 56 | 0 | 51 | 0 | 46 | 8 | 22 | 10 | 25 | 17 | 148 | 107 | 0 | 0 | 0 | 43 | 41 | 5 | 0 | 0 | 0 | 64 | 81 | 0 | 193 | 0 | 6 | 10 | 290 | 8 | 0 | 0 | 278 | 122 | 90 | 97 | 90 | 140 | 0 | 10 | 180 | 133 | 403 | 109 | 105 | 87 | 0 | 52 | 17 | 110 | 0 | 115 | 10 | 401 | 55 | 0 | 162 | 107 | 0 | 35 | 0 | 77 | 55 | 0 | 0 | 0 |  | 887 | 0 | 280 | 0 | 16 | 226 | 0 | 0 | 26 | 62 | 0 | 86 | 22 | 32 | 0 | 0 | 0 | 32 | 26 | 82 | 0 | 42 | 32 | 43 | 32 | 22 | 0 | 11 | 81 | 0 | 245 | 0 | 0 | 214 | 0 | 0 | 216 | 0 | 0 | 190 | 0 | 419 | 17 | 0 | 94 | 67 | 90 | 0 | 0 | 95 | 1090 | 191 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 0 | 0 |  | 13472 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 300 | 91 | 0 | 400 | 330 | 0 | 0 | 300 | 0 | 41 | 0 | 55 | 335 | 0 | 0 | 40 | 40 | 126 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 25 | 33 | 33 | 40 | 0 | 80 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 12 | 40 | 51 | 10 | 95 | 38 | 16 | 30 | 0 | 0 | 0 | 330 | 305 | 210 | 8 | 143 | 40 | 55 | 0 | 51 | 0 | 42 | 8 | 22 | 10 | 25 | 18 | 165 | 105 | 0 | 0 | 0 | 43 | 42 | 5 | 0 | 0 | 0 | 60 | 80 | 0 | 190 | 0 | 6 | 10 | 295 | 8 | 0 | 200 | 275 | 225 | 90 | 95 | 90 | 149 | 0 | 10 | 200 | 140 | 400 | 100 | 105 | 105 | 0 | 51 | 17 | 110 | 0 | 110 | 10 | 400 | 54 | 0 | 162 | 107 | 0 | 35 |  | 96 | 55 |  |  |  |  | 910 | 0 | 280 | 0 | 16 | 225 | 0 | 0 | 50 | 70 | 0 | 151 | 30 | 48 | 0 | 0 | 0 | 32 | 40 | 80 | 0 | 42 | 32 | 43 | 32 | 22 | 0 | 11 | 80 | 0 | 250 | 0 | 0 | 214 | 0 | 0 | 220 | 0 | 93 | 190 | 0 | 410 | 17 | 180 | 90 | 67 | 90 | 0 | 0 | 95 | 1170 | 220 |  | 17 |  |  | 34
Forecast for Day | 0 | 0 | 0 | 180 | 300 | 91 | 0 | 400 | 330 | 0 | 0 | 300 | 0 | 7 | 0 | 55 | 335 | 0 | 0 | 7 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 25 | 25 | 33 | 33 | 24 | 0 | 80 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 12 | 40 | 17 | 10 | 12 | 25 | 16 | 10 | 0 | 0 | 0 | 330 | 300 | 210 | 8 | 143 | 40 | 55 | 0 | 51 | 0 | 42 | 8 | 22 | 10 | 25 | 18 | 143 | 68 | 0 | 0 | 1.6 | 43 | 42 | 5 | 0 | 0 | 0 | 60 | 10 | 0 | 190 | 0 | 6 | 10 | 295 | 8 | 0 | 100 | 210 | 225 | 50 | 96 | 80 | 149 | 20 | 10 | 100 | 125 | 400 | 109 | 35 | 69 | 5 | 51 | 17 | 110 | 0 | 57 | 10 | 400 | 17 | 50 | 35 | 107 | 0 | 35 | 30 | 96 | 55 |  |  |  |  | 910 | 0 | 280 | 0 | 16 | 225 | 0 | 0 | 0 | 30 | 0 | 100 | 20 | 32 | 0 | 0 | 0 | 32 | 0 | 35 | 0 | 42 | 0 | 8 | 0 | 22 | 0 | 11 | 80 | 0 | 250 | 0 | 0 | 200 | 0 | 0 | 220 | 0 | 50 | 190 | 0 | 410 | 17 | 120 | 50 | 15 | 55 | 0 | 8 | 55 | 1170 | 220 |  | 0 | 6 | 100 | 0
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 300 | 90 | 0 | 400 | 327 | 0 | 0 | 300 | 0 | 7 | 0 | 55 | 335 | 0 | 0 | 7 | 8 | 15 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 0 | 25 | 27 | 33 | 28 | 8 | 0 | 75 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 12 | 26 | 17 | 10 | 11 | 25 | 16 | 13 | 0 | 0 | 0 | 335 | 305 | 207 | 8 | 143 | 40 | 54 | 0 | 51 | 0 | 45 | 0 | 22 | 10 | 25 | 18 | 122 | 68 | 0 | 0 | 1 | 43 | 42 | 5 | 0 | 0 | 0 | 56 | 10 | 0 | 193 | 0 | 6 | 10 | 295 | 0 | 0 | 0 | 211 | 0 | 25 | 96 | 0 | 149 | 11 | 10 | 68 | 125 | 403 | 109 | 17 | 69 | 3 | 52 | 17 | 110 | 0 | 57 | 10 | 400 | 0 | 27 | 35 | 107 | 0 | 35 | 16 | 78 | 55 | 0 | 0 | 0 | 0 | 886 | 0 | 280 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 85 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 8 | 0 | 22 | 0 | 11 | 80 | 0 | 250 | 0 | 0 | 214 | 0 | 0 | 159 | 0 | 0 | 184 | 0 | 419 | 2 | 0 | 50 | 15 | 56 | 0 | 2 | 55 | 880 | 220 | 0 | 0 | 2 | 49 | 0 | 0 | 0 | 0 | 6 | 0 |  |  |  |  | 77800077 |  | 0
77800077
| Minimum Generation |  | 10753 | 8:00
| Highest Generation |  | 13472 | 21:00
| Day Peak Generation |  | 11418 | 12:00
| Evening Peak Generation |  | 13472 | 21:00
| HVDC Max Flow |  | 895 | 1:00
| HVDC EvPeak Flow |  | 887 | 21:00
| Load factor L.F |  | 89.67% | [161 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2022-08-25
Till now the maximum generation is : - |  |  | 14782 | 21:00 | Hrs on | 2022-04-16
The Summary of Yesterday's |  | 2022-08-24 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 11418 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 11115 | MW
Evening Peak Generation : |  | 13472 | MW Hour : | 21:00 | Available Max Generation : |  | 14372 | MW
E.P. Demand (at gen end) : |  | 14100 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 14100 | MW
Maximum Generation : |  | 13472 | MW Hour : | 21:00 | Reserve(Generation end) |  | 272 | MW
Total Gen. (MKWH) : |  | 289.9278 | System Load Factor : | 89.67% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | 515 | MW at | 21:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2022-08-25
Actual : | 95.27 | Ft.(MSL) , | Rule curve : | 96.69 | Ft.( MSL )
Gas Consumed : | Total = | 1110.59 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 166910033.776
: |  | Coal : | 278104299.42 | Oil : | 1158902411.31 | Total : | 1603916744.506
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 150 | 3600:00 | 4515.4871 |  |  | 0 | -1.395%
Chittagong Area | 0 | 0:00 | 1278.63 |  |  | 0 | 0.9171%
Khulna Area | 0 | 0:00 | 1687.9476 |  |  | 0 | 1.338%
Rajshahi Area | 0 | 0:00 | 1498.2321 |  |  | 0 | 1.93%
Cumilla Area | 30 | 720:00 | 1274.7318 |  |  | 0 | 1.586%
Mymensingh Area | 320 | 7680:00 | 1053.8302 |  |  | 0 | 2.151%
Sylhet Area | 79 | 1896:00 | 470.3903 |  |  | 0 | 0.9376%
Barisal Area | 0 | 0:00 | 383.3291 |  |  | 0 | -0.8291%
Rangpur Area | 0 | 0:00 | 831.6293 |  |  | 0 | 2.092%
Total | 579 |  | 12994.2075 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-2
2) Ghorasal-3,4
3) Ashuganj-5
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
7) Sikalbaha 225 MW
8) Shajibazar 330 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Adani Power 400 kV bus-1 was switched on at 09:57.
b) Savar 33 kV bus-A was under shut down from 08:54 to 11:02 due to red hot maintenance at P/P bus DS.
c) Hasnabad 33 kV reserve bus was under shut down from 08:45 to 19:03 due to red hot maintenance DS clamp.
d) Aminbazar-Kallayanpur 132 kV Ckt-2 was under shut down from 11:05 to 21:21 for red hot maint.
e) Aminbazar 400 kV T0-1 transformer was under shut down since at 10:51 for D/W.
f) Barapukuria 132/33 kV T-4 transformer with 33 kV bus was under shut down from 11:30 to 14:12 for C/M. | [5 empty] | About 18 MW power interruption occurred under
Barapukuria S/S area from 11:30 to 14:12.
g) Soloshahar 132/33 kV T-1 transformer with 33 kV bus was under shut down from 11:42 to 17:58 for D/W by PDB.
h) Faridpur 132/33 kV T-2 transformer with 33 kV bus was under shut down from 09:21 to 12:14 for C/M.
i) Noapara-Khulna(C) 132 kV Ckt-1 mid CB was switched on at 11:37.
j) Siddhirganj 335 MW GT was under shut down at 10:48 due to ST Sync process and was synchronized at 16:16.16:23 respectively.
k) Siddhirganj peaking GT-2 was synchronized at 10:40 and shut down 17:39 due to Gas shortage.
l) Bhola Nutun Biddut GT-1 was synchronized at 11:28.
m) Bibiyana-Kaliakoir 400 kV Ckt-1 mid CB 2005 was shut down since 11:50 due to C/M.
n) Keraniganj-Kamrangirchar 132 kv Ckt tripped at 10:15 showing O/C relay and was switched on at 10:26.
o) Haripur-Meghnaghat 230 kV Ckt-2 mid CB was shut down from 09:36 to 13:16 for C/M.
p) Faridpur 132/33 kV T-1 transformer with 33 kV bus was under shut down from 12:31 to 14:50 due to 33 kV bus
DS RY-phase red hot.
q) HVDC 20DF12 filter was under shut down from 13:11 to 13:55 for C/M.
r) Kallyanpur 33 kV reserve bus was under shut down from 11:01 to 21:22 for C/M.
s) Gopalganj(N) 400/132 kV-T01 was switched on at 16:43.
t) Gopalganj(N) 132 kV bus was switched on at 17:23 and shut down at 17:50.
u) Gopalganj(N) 33/415V 500 kVA aux transformer was switched on at 17:06.
v) Bhola CCPP GT-1 was shut down at 20:36 due to gas shortage.
w) Shajadpur 132/33 kV T-3 transformer was switched on at 00:08.
x) Baraulia-Hathazari 132 kV Ckt-1 was under shut down since at 06:14 for C/M.
y) Hasnabad 132/33 kV T-1 tripped at 07:11(25-08-22) due to Zinzira feeder fault and was switched on at 07:21. | [5 empty] | About 20 MW power interruption occurred under
Hasnabad S/S area from 07:11 to 07:21.
z) Aminbazar-Kallyanpur 132 kV Ckt-1 was under shut down since at 07:25(25-08-22) for C/M.
| Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2022-08-24 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4284000
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 300 | 7227564 | Machine problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 91 | 2107636 | Engine problem
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 400 | 9728000 | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 332 | 7002000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 300 | 6613650 | Dirty gas
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 41 | 271680 | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 0 | 0 | Under maint.
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 55 | 1145451
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 426924 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 673000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 40 | 383702 | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 338 | 3838283
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 40 | 384624 | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 792720
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 125 | 1565760 | Engine problem
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 887778
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 460572 | Engine problem
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 52 | 1119480 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 801100
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 30 | 707800
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 31 | 320640 | #REF!
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 278 | 4787344 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 122 | 2919533 | Engine problem
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 90 | 1582573 | Engine problem
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 90 | 1524872 | Engine problem
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 140 | 2967552
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 1086600
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 55 | 584640 | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 1946880
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 210110
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 55 | 1325160
| Dhaka area Total |  |  |  | 5847 | 3648 | 69677628
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 110 | 2600000 | Machine problem
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 25 | 624898
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 118530
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 38 | 690720 | Engine problem
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 152 | 3544669 | Low water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | HGPI for 30 days.
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 87 | 1819091 | Engine problem
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 43 | 713424 | Fuel shortage
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 628480 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 10 | 261960 | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 10 | 257280 | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 16 | 356784 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 30 | 507360
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 95 | 657600 | Engine problem
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 29664
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 52 | 1462800 | Fuel shortage
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 17 | 710766 | Engine problem
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 110 | 2685552
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 10 | 264000 | Engine problem
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 107 | 2531673 | Engine problem
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Chattogram area Total |  |  |  | 2382 | 963 | 20465251
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 209 | 5000000 | #REF!
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 330 | 7882300 | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 305 | 7196000 | FGMO
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+136*1 | 284 | 0 | 0 | On test.
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 40 | 851112 | Engine problem
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 56 | 1300800
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 200727 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1208656
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 133 | 3092872 | Engine problem
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 46 | 1053432 | Engine problem
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 136 | 3343770 | Machine problem
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 180 | 2542080 | Line O/L
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 471456
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 10 | 226980
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 148 | 3550080
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 25 | 590100 | Engine problem
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 8 | 54034 | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 17 | 437980 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 2865408 | Reserve.
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 172140 | Fuel shortage
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 115 | 1340640
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 35 | 887760 | 33 kV feeder problem.
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 77 | 1983360 | Engine problem
| Cumilla Area Total |  |  |  | 3169 | 1951 | 46251687
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 107 | 2216640 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 0 | Gas shortage
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 13900
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 97 | 1999200 | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 109 | 1711200 | Engine problem
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 350030
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 278160 | Engine problem
| Mymensingh Area Total |  |  |  | 614 | 325 | 6569130
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1024000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 41 | 737808 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Gas shortage
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 5 | 128400 | Gas shortage
| Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 0 | 0 | Gas shortage
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 0 | 0 | Engine problem
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 64 | 1420608
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1111680
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 193 | 4682210 | Machine problem
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50MW PP (EPL) |  | NENP | 27*2 | 50 | 6 | 170200 | Gas shortage
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 8 | 186144 | Gas shortage
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 7020000 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 403 | 9598000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 243000
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 401 | 9431100
| Sylhet Area Total |  |  |  | 2477 | 1545 | 35753150
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 887 | 21536000
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 16 | 94080 | Fuel shortage
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 26 | 154080 | Engine problem
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 226 | 4527360
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 62 | 539136 | Engine problem
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 280 | 6302880 | Gas shortage.
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 0 | 0 | Fuel shortage
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 460800 | Engine problem
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 159360 | Fuel shortage
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 67 | 791280 | Fuel shortage
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 374400
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 0 | 0 | 0 | On test.
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 2384 | 1581 | 34939376
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 32 | 463392 | Line O/L
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 22 | 498847 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 86 | 2860636 | Gas shortage
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1090 | 26073300 | Line O/L
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 191 | 2985820 | Under maint.
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Line O/L
| Barisal Area Total |  |  |  | 1958 | 1421 | 32881995
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 32 | 760880 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 26 | 307721 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contract Expired
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 42 | 969072 | Engine problem
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 170290 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 214 | 5322291
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 216 | 4755145
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 190 | 5024445 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 419 | 9750327
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 179240 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 462480
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | .
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 247068
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 43 | 313925 | Engine problem
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 82 | 396728 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 1332808 | Reserve.
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 94 | 1660320 | Engine problem
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 95 | 1656480 | Engine problem
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 37800
| Rajshahi Area Total |  |  |  | 2129 | 1550 | 33347020
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 81 | 1926982
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 245 | 6046900 | Machine problem
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 90 | 1555353 | Engine problem
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 41715
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 72 | 326016 | Fuel shortage
| Intraco Solar 30 MW |  | IPP | 0 | 0 | 0 | 145640
| Rangpur Area Total |  |  |  | 720 | 488 | 10042606
| Total |  |  |  | 21680 | 13472 | 289927843
| Eastern Grid Total |  |  |  | 14489 | 8432 | 178716846
| Western Grid Total |  |  |  | 7191 | 5040 | 111210997
| National Grid Total |  |  |  | 21680 | 13472 | 289927843
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2022-08-24
(a) ENTIRE EASTERN GRID : |  | 8677.9 | MW | (b) ENTIRE WESTERN GRID : |  | 4299.41 | MW
i) Dhaka area |  | 4699.4 | MW | i) Khulna area |  | 1580.6 | MW
ii) Chittagong area |  | 1319.5 | MW | ii) Rajshahi area |  | 1439 | MW
iii) Comilla area |  | 1228 | MW | iii) Barisal area |  | 355.81 | MW
iv) Mymensingh area |  | 902 | MW | iv) Rangpur area |  | 924 | MW
v) Sylhet area |  | 529 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 12977.31 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
AKS | 0 | 00:00 | Chowmuhani | 194 | 21:00 | Kaptai | 5 | 19:00 | Nawabganj | 36.9 | 19:00 | Siddhirganj | 108 | 22:00
AKSML | 145 | 15:00 | Chuadanga | 102 | 19:30 | Kazla | 92 | 10:00 | Netrakona | 96 | 19:00 | Sirajganj | 88 | 07:00
Aftabnagar | 32 | 00:00 | Coxsbazar | 120 | 20:00 | Keranigonj | 68 | 18:00 | New | 81 | 09:00 | Sonargaon | 80 | 12:00
Agargaon | 90 | 12:00 | Cumilla(N) | 175 | 21:00 | Khagrachori | 30 | 19:00 | Niamatpur | 64 | 06:00 | Sreemongol | 44 | 12:00
Agrabad | 64 | 17:00 | Cumilla(S) | 166 | 15:00 | Khulna | 95 | 19:30 | Noapara | 47 | 01:00 | Srinagar | 46.28 | 21:00
Amnura | 52 | 21:00 | Daudkandi | 136 | 23:00 | Khulshi | 169 | 16:00 | PHP | 11 | 10:00 | Sunamganj | 38 | 22:00
Ashuganj | 73 | 19:00 | Dhaka | 42 | 12:00 | Kishoreganj | 154 | 19:30 | Pabna | 89 | 00:00 | Sylhet | 136 | 00:00
BSRM | 162 | 09:00 | Dhamrai | 110 | 20:00 | Kodda | 297 | 21:00 | Palashbari | 108 | 23:00 | TK | 28.5 | 19:00
Bagerhat | 98 | 19:30 | Dhanmondi | 157 | 13:00 | Kulaura | 44 | 00:00 | Panchagarh | 46 | 08:00 | Tangail | 195 | 22:00
Bakulia | 103 | 19:00 | Dohazari | 86 | 19:00 | Kurigram | 68 | 20:00 | Patuakhali | 133 | 22:00 | Thakurgaon | 66 | 22:00
Banani | 60 | 13:00 | Faridpur | 151 | 19:30 | Kushtia | 126 | 20:00 | Payra | 1.02 | 16:00 | Tongi | 116 | 19:30
Bangabhaban | 20 | 09:00 | Fatullah | 69 | 00:00 | Lalbag | 89 | 18:30 | Purbachal | 20 | 21:00 | Ullon | 40 | 21:00
Barapukuria | 57 | 23:00 | Fenchuganj | 47 | 00:00 | Lalmonirhat | 53 | 20:00 | Purbasadipur | 96 | 05:00 | Uttara | 93 | 21:00
Barguna | 18 | 22:00 | Feni | 84 | 19:30 | Madanganj | 94 | 12:00 | Rahim | 26 | 08:00 | UttaraNew | 18 | 00:00
Barishal | 95 | 00:00 | GPH | 89 | 04:00 | Madaripur | 100 | 00:00 | Rajbari | 60 | 19:30 | Zigatola | 57 | 19:00
Barishal-230 | 72 | 19:30 | Ghorashal | 76 | 21:00 | Madartek | 86 | 00:00 | Rajendrapur | 92 | 05:00
Baroaulia | 70 | 22:00 | Goalpara | 25 | 13:00 | Madunaghat | 58 | 19:00 | Rajshahi | 132 | 22:00
Baroirhat | 51 | 19:00 | Gollamari | 52 | 19:30 | Magura | 62 | 19:30 | Rajshahi-230 | 26 | 02:00
Bashundhara | 164 | 13:00 | Gopalganj | 99 | 19:00 | Mahasthangarh | 74 | 21:00 | Ramganj | 88 | 19:00
BashundharaCement | 6 | 00:00 | Gulshan | 120 | 12:00 | Manikganj | 91 | 15:00 | Rampur | 16 | 00:00
Beanibazar | 68 | 00:00 | Halishahar | 83.5 | 12:00 | Maniknagar | 80 | 13:00 | Rangamati | 14 | 19:00
Benapole | 54 | 22:00 | HaripurSBU | 159 | 16:00 | Matarbari | 37 | 19:00 | Rangpur | 105 | 08:00
Bhaluka | 102 | 19:00 | Hasnabad | 93 | 23:00 | Matuail | 60 | 00:00 | Ruppur | 5 | 09:00
Bhandaria | 47 | 00:00 | Hathazari | 94 | 19:00 | Millgate | 65 | 09:00 | SSM | 3 | 05:00
Bhangura | 36 | 21:00 | Ishurdi | 83 | 19:00 | Mirpur | 125 | 19:00 | Saidpur | 93 | 08:00
Bheramara(GK) | 59 | 22:00 | Jaldhaka | 64 | 20:00 | Mirsorai | N/A | N/A | Satkhira | 95 | 06:00
Bhulta | 210 | 05:00 | Jamalpur | 118 | 19:00 | Mithapukur | 34 | 20:00 | Satmasjid | 101 | 19:00
Bog-Sherpur | 64 | 20:00 | Jashore | 129 | 19:30 | Modern | 0 | 01:00 | Savar | 156 | 09:00
Bogura | 172 | 21:00 | Jhenaidah | 122 | 19:30 | Mogbazar | 135 | 12:00 | Shahjadpur | 85 | 22:00
Borhanuddin | 41 | 01:00 | Joydebpur | 191 | 21:00 | Mongla | 22 | 01:00 | Shahjibazar | 95 | 00:00
Brahmanbaria | 150 | 21:00 | Joypurhat | 59 | 23:00 | Motijheel | 38 | 12:00 | Shahmirpur | 46.5 | 18:30
Cantonment | 154 | 13:00 | Juldah | 25 | 13:00 | Munshiganj | 108 | 00:00 | Shariatpur | 78 | 22:00
Chandpur | 62 | 22:00 | KSRM | 33.5 | 13:00 | Mymensingh | 239 | 19:30 | Sherpur | 100 | 19:00
Chandraghona | 30 | 19:00 | Kabirpur | 274 | 18:00 | Naogaon | 124 | 21:00 | Shikalbaha | 28 | 19:00
Chapai | 65 | 22:00 | Kachua | 69 | 21:00 | Narail | 47 | 21:00 | Shikalbaha-230 | N/A | N/A
Charsaidpur | 40 | 00:00 | Kallyanpur | 96 | 00:00 | Narinda | 75.4 | 13:00 | Shitalakhya | 114 | 12:00
Chauddagram | 55 | 23:00 | Kalurghat | 32 | 09:00 | Narshingdi | 174 | 23:00 | Sholosohor | N/A | N/A
Chhatak | 37 | 21:00 | Kamrangirchar | 63 | 13:00 | Natore | 132 | 21:00 | Shyampur | 144 | 01:00
Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
(1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2022-08-24 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Bhulta | 374 | 22:00 | 363 | 10:00 | Kaliakoir | 378 | 19:00 | 366 | 08:00
| Bibiana | 397 | 13:00 | 390 | 01:00 | Payra | 418 | 18:00 | 409 | 00:00
| BIPTC | 401 | 04:00 | 395 | 13:00 | Rahanpur_I | 400 | 18:00 | 379 | 22:00
| Gopalganj_I | 410 | 18:00 | 394 | 01:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 214 | 21:00 | 206 | 17:00 | Hasnabad | 216 | 22:00 | 207 | 08:00
| AKSML | 224 | 00:00 | 212 | 03:00 | Hathazari | 224 | 00:00 | 216 | 03:00
| Aminbazar | 215 | 21:00 | 209 | 10:00 | Ishurdi | 232 | 18:00 | 225 | 20:00
| Ashuganj | 230 | 18:30 | 225 | 03:00 | Jhenaidah | 229 | 18:00 | 218 | 21:00
| Baghabari | 230 | 00:00 | 225 | 19:00 | Kaliakoir | 218 | 01:00 | 208 | 08:00
| Barapukuria | 221 | 18:00 | 208 | 21:00 | Keranigonj | 214 | 21:00 | 206 | 09:00
| Barishal | 248 | 18:00 | 237 | 01:00 | Khulna(S) | 240 | 12:00 | 227 | 21:00
| Bheramara | 228 | 18:00 | 220 | 21:00 | Maniknagar | 216 | 03:00 | 210 | 09:00
| Bhulta | 219 | 04:00 | 213 | 08:00 | Meghnaghat | 220 | 21:00 | 213 | 16:00
| Bibiana | 232 | 01:00 | 228 | 08:00 | Mirsorai | N/A | N/A | N/A | N/A
| BIPTC | 232 | 18:00 | 222 | 21:00 | Rajshahi | 232 | 18:00 | 221 | 23:00
| Bogura | 224 | 18:00 | 215 | 21:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 248 | 12:00 | 239 | 03:00 | Rampura | 222 | 00:00 | 211 | 09:00
| BSRM | 222 | 11:00 | 214 | 09:00 | Shikalbaha | 226 | 00:00 | 218 | 18:00
| Cumilla(N) | 220 | 19:00 | 214 | 10:00 | Shyampur | 215 | 21:00 | 208 | 08:00
| Fenchuganj | 235 | 18:00 | 230 | 00:00 | Siddhirganj | 219 | 21:00 | 212 | 08:00
| Ghorashal | N/A | N/A | N/A | N/A | Sirajgonj | 230 | 18:00 | 225 | 21:00
| GPH | 222 | 00:00 | 214 | 16:00 | Tongi | 218 | 01:00 | 206 | 08:00
| Haripur | 217 | 21:00 | 210 | 08:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 132 | 03:00 | 125 | 10:00 | Lalbag | 138 | 13:00 | 128 | 11:00
| Agargaon | 132 | 03:00 | 126 | 10:00 | Lalmonirhat | 127 | 18:00 | 115 | 22:00
| Agrabad | 130 | 00:00 | 124 | 16:00 | Madanganj | 128 | 19:00 | 123 | 09:00
| AKS | 130 | 00:00 | 123 | 14:00 | Madaripur | 140 | 07:00 | 132 | 21:00
| Aminbazar | 132 | 21:00 | 126 | 17:00 | Madartek | 132 | 04:00 | 125 | 10:00
| Amnura | 134 | 18:00 | 126 | 23:00 | Madunaghat | 132 | 00:00 | 126 | 23:00
| Ashuganj | 135 | 06:00 | 132 | 02:00 | Magura | 140 | 18:00 | 130 | 21:00
| Bagerhat | 136 | 18:00 | 126 | 21:00 | Mahasthangarh | 134 | 18:00 | 124 | 21:00
| Bakulia | 131 | 00:00 | 124 | 14:00 | Manikganj | 134 | 19:00 | 126 | 02:00
| Banani | 127 | 19:00 | 122 | 08:00 | Maniknagar | 129 | 03:00 | 123 | 11:00
| Bangabhaban | 131 | 07:00 | 123 | 11:00 | Matarbari | 121 | 00:00 | 110 | 19:30
| Barapukuria | 135 | 18:00 | 123 | 22:00 | Matuail | 127 | 02:00 | 123 | 09:00
| Barguna | 134 | 13:00 | 129 | 23:00 | Millgate | 127 | 19:30 | 122 | 08:00
| Barishal | 140 | 18:00 | 129 | 22:00 | Mirpur | 131 | 19:00 | 124 | 10:00
| Barishal-230 | 140 | 08:00 | 134 | 01:00 | Mithapukur | 130 | 17:00 | 119 | 22:00
| Baroaulia | 132 | 00:00 | 127 | 16:00 | Modern | 131 | 11:00 | 126 | 09:00
| Baroirhat | 125 | 00:00 | 119 | 23:00 | Mogbazar | 137 | 04:00 | 125 | 14:00
| Bashundhara | 128 | 06:00 | 121 | 16:00 | Mongla | 135 | 17:00 | 127 | 21:00
| BashundharaCement | 129 | 10:00 | 123 | 11:00 | Motijheel | 131 | 07:00 | 123 | 11:00
| Beanibazar | 128 | 09:00 | 124 | 00:00 | Munshiganj | 128 | 19:00 | 124 | 08:00
| Benapole | 137 | 18:00 | 128 | 22:00 | Mymensingh | 130 | 19:00 | 104 | 03:00
| Bhaluka | 129 | 10:00 | 118 | 13:00 | Naogaon | 131 | 18:00 | 120 | 21:00
| Bhandaria | 139 | 08:00 | 129 | 00:00 | Narail | 138 | 18:00 | 127 | 21:00
| Bhangura | 136 | 00:00 | 132 | 20:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bheramara | 136 | 18:00 | 131 | 21:00 | Narshingdi | 122 | 00:00 | 118 | 09:00
| Bheramara(GK) | 139 | 06:00 | 132 | 21:00 | Natore | 135 | 18:00 | 127 | 22:00
| Bhulta | 120 | 02:00 | 116 | 12:00 | Nawabganj | 133 | 04:00 | 128 | 08:00
| Bog-Sherpur | 135 | 18:00 | 125 | 21:00 | Netrakona | 126 | 20:00 | 108 | 02:00
| Bogura | 136 | 18:00 | 126 | 22:00 | New | 128 | 21:00 | 122 | 08:00
| Bogura-230 | 136 | 18:00 | 128 | 21:00 | Niamatpur | 130 | 00:00 | 116 | 22:00
| Brahmanbaria | 129 | 00:00 | 127 | 10:00 | Noapara | 138 | 18:00 | 130 | 21:00
| Cantonment | 131 | 04:00 | 125 | 09:00 | Pabna | 134 | 18:00 | 128 | 23:00
| Chandpur | 132 | 18:30 | 125 | 03:00 | Palashbari | 131 | 18:00 | 116 | 22:00
| Chandraghona | 132 | 00:00 | 127 | 16:00 | Panchagarh | 127 | 18:00 | 107 | 22:00
| Chapai | 135 | 18:00 | 127 | 14:00 | Patuakhali | 135 | 18:30 | 130 | 21:00
| Charsaidpur | 130 | 19:00 | 123 | 10:00 | Payra | 137 | 18:00 | 134 | 21:00
| Chauddagram | 127 | 18:00 | 120 | 23:00 | PHP | 127 | 18:00 | 119 | 23:00
| Chhatak | 130 | 05:00 | 126 | 17:00 | Postogola | 136 | 21:00 | 129 | 09:00
| Chowmuhani | 125 | 18:00 | 116 | 03:00 | Purbachal | 127 | 04:00 | 121 | 14:00
| Chuadanga | 136 | 18:00 | 123 | 21:00 | Purbasadipur | 128 | 18:00 | 112 | 21:00
| Coxsbazar | 121 | 11:00 | 105 | 22:00 | Rahim | 132 | 18:00 | 124 | 08:00
| Cumilla(N) | 129 | 18:00 | 125 | 09:00 | Rajbari | 135 | 18:00 | 127 | 21:00
| Cumilla(S) | 131 | 06:00 | 123 | 22:00 | Rajendrapur | 133 | 19:30 | 126 | 03:00
| Daudkandi | 130 | 05:00 | 123 | 17:00 | Rajshahi | 134 | 18:00 | 126 | 22:00
| Dhaka | 132 | 03:00 | 126 | 10:00 | Rajshahi-230 | 133 | 18:00 | 127 | 21:00
| Dhamrai | 125 | 19:00 | 120 | 17:00 | Ramganj | 129 | 18:00 | 119 | 23:00
| Dhanmondi | 127 | 22:00 | 122 | 10:00 | Rampur | 130 | 00:00 | 124 | 13:00
| Dohazari | 128 | 00:00 | 122 | 23:00 | Rampura | 132 | 00:00 | 126 | 09:00
| Faridpur | 135 | 18:00 | 128 | 21:00 | Rangamati | 131 | 00:00 | 126 | 16:00
| Fatullah | 130 | 05:00 | 125 | 08:00 | Rangpur | 129 | 18:00 | 116 | 20:00
| Fenchuganj | 133 | 00:00 | 131 | 09:00 | Ruppur | 135 | 00:00 | 131 | 23:00
| Feni | 127 | 18:00 | 121 | 15:00 | Saidpur | 129 | 18:00 | 115 | 22:00
| Ghorashal | 135 | 00:00 | 129 | 08:00 | Satkhira | 136 | 18:00 | 126 | 21:00
| Goalpara | 139 | 18:00 | 132 | 21:00 | Satmasjid | 132 | 04:00 | 126 | 09:00
| Gollamari | 138 | 18:00 | 131 | 21:00 | Savar | 132 | 00:00 | 122 | 10:00
| Gopalganj | 140 | 18:00 | 133 | 23:00 | Shahjadpur | 138 | 18:00 | 133 | 20:00
| Gopalganj_I | 140 | 06:00 | 133 | 21:00 | Shahjibazar | 133 | 06:00 | 129 | 16:00
| Gulshan | 132 | 04:00 | 125 | 10:00 | Shahmirpur | 131 | 02:00 | 125 | 10:00
| Halishahar | 131 | 00:00 | 124 | 16:00 | Shariatpur | 139 | 08:00 | 130 | 21:00
| Haripur | 127 | 19:00 | 124 | 08:00 | Sherpur | 133 | 19:00 | 116 | 05:00
| HaripurSBU | 128 | 19:00 | 125 | 08:00 | Shikalbaha | 131 | 00:00 | 125 | 14:00
| Hasnabad | 135 | 00:00 | 130 | 09:00 | Shikalbaha-230 | 131 | 00:00 | 126 | 13:00
| Hathazari | 132 | 00:00 | 126 | 23:00 | Shitalakhya | 135 | 21:00 | 127 | 09:00
| Ishurdi | 136 | 18:30 | 131 | 20:00 | Sholosohor | N/A | N/A | N/A | N/A
| Jaldhaka | 128 | 18:00 | 114 | 22:00 | Shyampur | 129 | 04:00 | 124 | 09:00
| Jamalpur | 134 | 21:00 | 119 | 05:00 | Shyampur-230 | 130 | 19:00 | 125 | 08:00
| Jashore | 138 | 18:00 | 128 | 21:00 | Siddhirganj | 127 | 06:00 | 123 | 09:00
| Jhenaidah | 140 | 18:00 | 131 | 21:00 | Sirajganj | 134 | 18:00 | 125 | 21:00
| Jhenaidah-230 | 141 | 18:00 | 132 | 21:00 | Sonargaon | 129 | 01:00 | 123 | 09:00
| Joydebpur | 140 | 19:00 | 125 | 08:00 | Sreemongol | 132 | 00:00 | 130 | 13:00
| Joypurhat | 131 | 18:00 | 118 | 23:00 | Srinagar | 134 | 04:00 | 128 | 09:00
| Juldah | 131 | 00:00 | 125 | 14:00 | SSM | 135 | 01:00 | 128 | 13:00
| Kabirpur | 136 | 19:00 | 120 | 08:00 | Sunamganj | 128 | 06:00 | 123 | 22:00
| Kachua | 130 | 18:00 | 123 | 05:00 | Sylhet | 131 | 06:00 | 129 | 13:00
| Kaliakoir | 137 | 19:00 | 131 | 07:00 | Tangail | 135 | 19:00 | 125 | 13:00
| Kallyanpur | 132 | 21:00 | 125 | 08:00 | Thakurgaon | 124 | 18:00 | 110 | 22:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2022-08-24
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 925 | 7927 | 4774 | 12701 |  |  |  | QF-LDC-11
0:30 | 997.5 | 7569 | 4802.5 | 12371.5 | Date: | 2022-08-24
1:00 | 1070 | 7211 | 4831 | 12042
1:30 | 1050 | 7174.5 | 4795.5 | 11970
2:00 | 1030 | 7138 | 4760 | 11898
2:30 | 1030 | 7151 | 4741 | 11892 | [5 empty] | Gen. at Eve. Peak | 13472 | 13472 MW (21:00 )
3:00 | 1030 | 7164 | 4722 | 11886 | [6 empty] | 21:00
3:30 | 1050 | 7095 | 4722.5 | 11817.5 | [5 empty] | Gen. at Day Peak | 11418 | 11418 MW (12:00 )
4:00 | 1070 | 7026 | 4723 | 11749 | [6 empty] | 12:00
4:30 | 1060 | 6989.5 | 4692.5 | 11682 | [5 empty] | Highest Generation | 13472
5:00 | 1050 | 6953 | 4662 | 11615 | [6 empty] | 21:00
5:30 | 1032.5 | 6838 | 4505 | 11343
6:00 | 1015 | 6723 | 4348 | 11071
6:30 | 1035 | 6684 | 4281.5 | 10965.5
7:00 | 1055 | 6645 | 4215 | 10860
7:30 | 1087.5 | 6564 | 4242.5 | 10806.5
8:00 | 1120 | 6483 | 4270 | 10753
8:30 | 1145 | 6613.5 | 4183.5 | 10797
9:00 | 1170 | 6744 | 4097 | 10841
9:30 | 1080 | 6893.5 | 4055 | 10948.5
10:00 | 990 | 7043 | 4013 | 11056
10:30 | 920 | 7141.5 | 3992 | 11133.5
11:00 | 850 | 7240 | 3971 | 11211
11:30 | 892.5 | 7267 | 4047.5 | 11314.5
12:00 | 935 | 7294 | 4124 | 11418
12:30 | 952.5 | 7308.5 | 4207.5 | 11516
13:00 | 970 | 7323 | 4291 | 11614
13:30 | 975 | 7283 | 4303.5 | 11586.5
14:00 | 980 | 7243 | 4316 | 11559
14:30 | 945 | 7396 | 4266.5 | 11662.5
15:00 | 910 | 7549 | 4217 | 11766
15:30 | 1000 | 7495.5 | 4254 | 11749.5
16:00 | 1090 | 7442 | 4291 | 11733
16:30 | 1052.5 | 7451.5 | 4210 | 11661.5
17:00 | 1015 | 7461 | 4129 | 11590
17:30 | 1002.5 | 7480.5 | 4099.5 | 11580
18:00 | 990 | 7500 | 4070 | 11570
18:30 | 890 | 7830.5 | 4339 | 12169.5
19:00 | 790 | 8161 | 4608 | 12769
19:30 | 675 | 8239 | 4915 | 13154
20:00 | 625 | 8318 | 5001 | 13319 |  |  |  | Executive Engineer
20:30 | 570 | 8375 | 5020.5 | 13395.5 |  |  |  | Network Operation Division
21:00 | 515 | 8432 | 5040 | 13472
21:30 | 605 | 8416 | 5041.5 | 13457.5
22:00 | 695 | 8400 | 5043 | 13443 |  |  |  |  | Page 6 of 7
22:30 | 802.5 | 8453 | 5002 | 13455
23:00 | 910 | 8506 | 4961 | 13467
23:30 | 917.5 | 8216.5 | 4867.5 | 13084
24:00 | 925 | 7927 | 4774 | 12701
13472 MW (21:00 )
11418 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2022-08-24 |  | Energy |  | 289927843
[13 empty] | 2022-08-24 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 4606 | 887 | 1939 | 490 | 2239 | 1360 | 146 | 448 | 647 | 158 | 0 | 875
0:30 | 4505.5 | 891 | 1790.5 | 635.5 | 1966.5 | 1426.5 | 148.5 | 446 | 620.5 | 159 | 0 | 1109.3282 | Date: | 2022-08-24
1:00 | 4405 | 895 | 1642 | 781 | 1694 | 1493 | 151 | 444 | 594 | 160 | 0 | 1343.6564
1:30 | 4411.5 | 894.5 | 1647 | 764 | 1663.5 | 1498 | 151 | 444 | 558.5 | 155 | 0 | 1271.7735 | [8 empty] | Total Energy | 289.9278 | Total Energy Gen 289.928 MKWHr Energy Not Served 21.946 MKWHr Energy Requirement 311.874 MKWHr
2:00 | 4418 | 894 | 1652 | 747 | 1633 | 1503 | 151 | 444 | 523 | 150 | 0 | 1199.8906 | [8 empty] | Energy not Served | 21.9458
2:30 | 4421.5 | 894.5 | 1661.5 | 736.5 | 1643 | 1482.5 | 151 | 444 | 522.5 | 152 | 0 | 1021.1051 | [8 empty] | Energy Requirement | 311.8736
3:00 | 4425 | 895 | 1671 | 726 | 1653 | 1462 | 151 | 444 | 522 | 154 | 0 | 842.3196
3:30 | 4427 | 895 | 1681.5 | 696.5 | 1645 | 1451.5 | 150 | 444.5 | 491 | 153 | 0 | 767.2112 | [6 empty] | Shortage
4:00 | 4429 | 895 | 1692 | 667 | 1637 | 1441 | 149 | 445 | 460 | 152 | 0 | 692.1028
4:30 | 4427.5 | 894.5 | 1711.5 | 622.5 | 1643.5 | 1421 | 149 | 445.5 | 437.5 | 148 | 0 | 615.6121
5:00 | 4426 | 894 | 1731 | 578 | 1650 | 1401 | 149 | 446 | 415 | 144 | 0 | 539.1214
5:30 | 4446.5 | 894 | 1700.5 | 382.5 | 1651 | 1375.5 | 150 | 420.5 | 389 | 136 | 2 | 559.396
6:00 | 4467 | 894 | 1670 | 187 | 1652 | 1350 | 151 | 395 | 363 | 128 | 4 | 579.6707
6:30 | 4438.5 | 894 | 1665.5 | 173.5 | 1632.5 | 1335 | 151 | 359.5 | 330 | 126 | 20 | 538.6606 |  |  |  |  | Coal
7:00 | 4410 | 894 | 1661 | 160 | 1613 | 1320 | 151 | 324 | 297 | 124 | 36 | 497.6505
7:30 | 4385.5 | 894 | 1642 | 110 | 1614.5 | 1330 | 149.5 | 322 | 297 | 124 | 68 | 427.8253 |  |  |  | Oil |  |  |  | ,
8:00 | 4361 | 894 | 1623 | 60 | 1616 | 1340 | 148 | 320 | 297 | 124 | 100 | 358
8:30 | 4320 | 894 | 1633.5 | 163 | 1640 | 1309.5 | 150 | 295 | 297 | 126 | 99 | 518.5
9:00 | 4279 | 894 | 1644 | 266 | 1664 | 1279 | 152 | 270 | 297 | 128 | 98 | 679
9:30 | 4259 | 893.5 | 1633 | 351 | 1733 | 1279 | 129 | 260 | 283.5 | 126 | 131.5 | 827.5
10:00 | 4239 | 893 | 1622 | 436 | 1802 | 1279 | 106 | 250 | 270 | 124 | 165 | 976
10:30 | 4199 | 893.5 | 1669 | 501 | 1829 | 1254 | 106 | 266.5 | 278.5 | 135 | 133.5 | 1172.5
11:00 | 4159 | 894 | 1716 | 566 | 1856 | 1229 | 106 | 283 | 287 | 146 | 102 | 1369
11:30 | 4197.5 | 894 | 1706 | 566 | 1854 | 1224 | 128.5 | 318.5 | 322.5 | 148 | 124 | 1444
12:00 | 4236 | 894 | 1696 | 566 | 1852 | 1219 | 151 | 354 | 358 | 150 | 146 | 1519
12:30 | 4231.5 | 893.5 | 1696.5 | 595 | 1869 | 1239.5 | 150 | 358.5 | 362.5 | 153 | 175.5 | 1468.5
13:00 | 4227 | 893 | 1697 | 624 | 1886 | 1260 | 149 | 363 | 367 | 156 | 205 | 1418
13:30 | 4227 | 893 | 1697 | 624 | 1886 | 1260 | 149 | 363 | 367 | 156 | 205 | 1461
14:00 | 4227 | 893 | 1697 | 624 | 1886 | 1260 | 149 | 363 | 367 | 156 | 205 | 1504
14:30 | 4264.5 | 889.5 | 1730.5 | 611.5 | 1949 | 1249 | 146 | 362 | 368.5 | 161 | 170.5 | 1515
15:00 | 4302 | 886 | 1764 | 599 | 2012 | 1238 | 143 | 361 | 370 | 166 | 136 | 1526
15:30 | 4304 | 886 | 1756.5 | 568 | 2050.5 | 1234 | 143 | 362.5 | 372 | 159 | 126.5 | 1490
16:00 | 4306 | 886 | 1749 | 537 | 2089 | 1230 | 143 | 364 | 374 | 152 | 117 | 1454
16:30 | 4394 | 886.5 | 1696.5 | 415.5 | 2213 | 1225.5 | 123.5 | 332 | 369.5 | 155 | 91.5 | 962.0016
17:00 | 4394 | 887 | 1644 | 294 | 2337 | 1221 | 104 | 300 | 365 | 158 | 66 | 470.0032
17:30 | 4336.5 | 886.5 | 1613.5 | 147 | 2585.5 | 1215.5 | 124 | 275 | 366 | 150 | 35.5 | 433.0016
18:00 | 4279 | 886 | 1583 | 0 | 2834 | 1210 | 144 | 250 | 367 | 142 | 5 | 396
18:30 | 4391.5 | 886 | 1715.5 | 125 | 2912.5 | 1225 | 144.5 | 283 | 480 | 142 | 2.5 | 536
19:00 | 4504 | 886 | 1848 | 250 | 2991 | 1240 | 145 | 316 | 593 | 142 | 0 | 676
19:30 | 4570 | 886 | 1866 | 295 | 3008 | 1341 | 146 | 399 | 670 | 146 | 0 | 595
20:00 | 4643 | 886 | 1851 | 295 | 3043 | 1359 | 151 | 407 | 709 | 156 | 0 | 535
20:30 | 4628 | 886.5 | 1882.5 | 298.5 | 3042 | 1387.5 | 151.5 | 424.5 | 741 | 152 | 0 | 557
21:00 | 4613 | 887 | 1914 | 302 | 3041 | 1416 | 152 | 442 | 773 | 148 | 0 | 579
21:30 | 4609.5 | 886.5 | 1939.5 | 292.5 | 3039.5 | 1398 | 149 | 442.5 | 764 | 153 | 0 | 846
22:00 | 4606 | 886 | 1965 | 283 | 3038 | 1380 | 146 | 443 | 755 | 158 | 0 | 1113
22:30 | 4604.5 | 886 | 1965 | 389 | 2968.5 | 1380.5 | 146 | 443 | 731 | 158 | 0 | 1059.5
23:00 | 4603 | 886 | 1965 | 495 | 2899 | 1381 | 146 | 443 | 707 | 158 | 0 | 1006
23:30 | 4604.5 | 886.5 | 1952 | 492.5 | 2569 | 1370.5 | 146 | 445.5 | 677 | 158 | 0 | 1127.5 | Max Temp. in Dhaka |  | 24.7° C | 32.9° C
24:00 | 4606 | 887 | 1939 | 490 | 2239 | 1360 | 146 | 448 | 647 | 158 | 0 | 1249
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 289.928 MKWHr Energy Not Served 21.946 MKWHr Energy Requirement 311.874 MKWHr
Load shed
Note on W13: Author:

## Generation
g | 2022-08-24
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 81 | 81 | 81 | 79 | 79 | 81 | 81 | 78 | 82 | 36 | 36 | 81 | 79 | 76 | 73 | 73 | 34 | 74 |  | 75 | 76 | 81 | 82 | 76 | 76 | 76 | 1856669
2 | Karnaphuli Hydro PP Unit-4 & 5 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1688000
3 | Chattogram TPP-1 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2600000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 624898
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 1 | 4 | 9 | 19 | 13 | 19 | 6 | 17 | 15 | 10 | 4 | 0 | [8 empty] | 118530
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 16 | 16 | 16 | 16 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 628480
12 | Hathazari 100 MW peaking PP | 34 | 34 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 44 |  | 44 | 42 | 43 | 43 | 34 | 30 | 34 | 713424
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 73 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 57 | 63 | 69 | 69 | 76 | 87 |  | 87 | 87 | 87 | 87 | 87 | 87 | 90 | 1819091
| Daudkandi 200 MW PP (B.Trac) | 194 | 195 | 195 | 195 | 195 | 160 | 160 | 60 | 60 | 120 | 180 | 160 | 194 | 193 | 194 | 150 | 0 | 0 |  | 20 | 20 | 20 | 0 |  | 100 | 110 | 2865408
14 | Titas 50 MW Peaking PP | 42 | 42 | 43 | 43 | 45 | 45 | 43 | 42 | 42 | 42 | 42 | 42 | 42 | 40 | 44 | 43 | 44 | 44 |  | 45 | 45 | 45 | 46 | 46 | 46 | 46 | 1053432
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | [10 empty] | 97 | 92 | 93 | 97 | 97 | 97 | 94 | 0 | [7 empty] | 0 | 673000
17 | Siddhirganj 335 MW CCPP | 140 | 145 | 145 | 145 | 145 | 160 | 160 | 160 | 160 | 160 |  |  | 4 | 4 | 1 | 9 | 81 | 253 |  | 337 | 336 | 337 | 338 | 337 | 337 | 335 | 3838283
18 | Kodda 300 MW PP Unit-2 (Summit) | 97 | 97 | 97 | 97 | 97 | 97 | 95 | 95 | 107 | 225 | 245 | 243 | 245 | 245 | 253 | 250 | 248 | 278 |  | 278 | 278 | 278 | 278 | 278 | 278 | 278 | 4787344
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 200727
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4284000
24
25 | Ghorasal 365 MW CCPP Unit-7 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 7227564
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 40 | 40 | 40 | 40 | 40 | 40 | 37 | 37 | 39 | 35 | 30 | 30 | 31 | 28 | 28 | 25 | 32 | 35 |  | 35 | 35 | 44 | 40 | 42 | 42 | 42 | 851112
33 | Ashuganj 225 MW CCPP | 208 | 210 | 210 | 209 | 209 | 212 | 209 | 198 | 200 | 204 | 209 | 207 | 204 | 202 | 203 | 205 | 206 | 208 |  | 210 | 207 | 208 | 209 | 209 | 209 | 212 | 5000000
34 | Ashuganj 450 MW CCPP(South) | 275 | 275 | 275 | 275 | 275 | 275 | 275 | 325 | 300 | 300 | 300 | 300 | 300 | 300 | 320 | 305 | 305 | 270 |  | 270 | 280 | 300 | 305 | 305 | 305 | 305 | 7196000
| Ashuganj 450 MW CCPP(North) | 315 | 315 | 315 | 315 | 315 | 325 | 322 | 305 | 300 | 300 | 300 | 300 | 300 | 300 | 325 | 325 | 325 | 280 |  | 280 | 290 | 330 | 330 | 330 | 325 | 325 | 7882300
Ashuganj 420 MW CCPP(East)
35 | Ashuganj 55 MW PP (Precision) | 56 | 56 | 56 | 56 | 56 | 57 | 56 | 56 | 56 | 52 | 49 | 52 | 51 | 51 | 50 | 51 | 52 | 54 |  | 54 | 55 | 55 | 56 | 56 | 56 | 56 | 1300800
36 | Chandpur 150 MW CCPP | 143 | 142 | 143 | 143 | 143 | 144 | 143 | 144 | 144 | 143 | 143 | 144 | 143 | 143 | 138 | 137 | 137 | 137 |  | 137 | 136 | 136 | 136 | 136 | 136 | 137 | 3343770
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 398 | 399 | 399 | 398 | 398 | 397 | 398 | 392 | 395 | 396 | 401 | 402 | 402 | 401 | 402 | 401 | 400 | 401 |  | 396 | 401 | 400 | 400 | 401 | 401 | 399 | 9728000
40 | Meghnaghat 450 MW CCPP(MPL) | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 6613650
41 | Haripur 360MW CCPP(HPL) | 252 | 253 | 251 | 252 | 252 | 251 | 242 | 240 | 242 | 242 | 332 | 332 | 320 | 320 | 320 | 320 | 330 | 326 |  | 332 | 332 | 332 | 332 | 332 | 331 | 334 | 7002000
42 | RPCL 210MW CCPP | 107 | 107 | 108 | 108 | 106 | 107 | 107 | 81 | 80 | 69 | 68 | 68 | 68 | 68 | 99 | 99 | 99 | 100 |  | 101 | 108 | 107 | 107 | 107 | 107 | 107 | 2216640
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 1 | 12 | 29 | 17 | 55 | 31 | 50 | 44 | 55 | 44 | 12 | 13 | 1 |  | 0 | [6 empty] | 350030
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1024000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 41 | 41 |  | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 737808
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 60 | 60 | 60 | 60 | 60 | 65 | 60 | 58 | 55 | 55 | 55 | 58 | 56 | 58 | 58 | 58 | 59 | 59 |  | 64 | 64 | 64 | 64 | 58 | 59 | 65 | 1420608
48 | Shahjibazar 86MW PP (Shahjibazar) | 81 | 81 | 81 | 81 | 81 | 60 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 78 | 78 | 81 | 81 | 81 | 81 | 81 | 1111680
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 194 | 194 | 194 | 194 | 194 | 194 | 194 | 194 | 193 | 193 |  | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 4682210
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 170200
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 243000
54 | Hobiganj 11MW PP Cofidence-E | [25 empty] | 0 | 0
55 | Fenchugonj 51 MW PP (Barakatullah) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 128400
56 | Shahjahanulla 25 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 186144
57 | Bibiana-II 341 MW CCPP (Summit) | 280 | 290 | 290 | 280 | 270 | 255 | 295 | 280 | 310 | 300 | 300 | 270 | 290 | 280 | 300 | 290 | 280 | 270 |  | 280 | 290 | 270 | 290 | 300 | 300 | 270 | 7020000
| Bibiyana South 400 MW | 400 | 400 | 401 | 400 | 397 | 400 | 400 | 395 | 394 | 395 | 396 | 401 | 400 | 391 | 386 | 393 | 394 | 334 |  | 395 | 400 | 401 | 401 | 401 | 401 | 401 | 9431100
58 | Nababganj 55 MW PP (Southern power ) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 0 | [11 empty] | 0 | 13 | 35 | 35 | 35 | 35 | 460572
59 | Tangail Palli Power Gen 22 MW | 8 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 10 | 4 | 7 | 11 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 278160
60 | Barabkunda 22 MW PP (Regent) | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 11 | 14 | 14 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 356784
61 | Narshingdi 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 426924
62 | Tangail 22 MW PP (Doreen)
63 | Impoprt (Tripura) | 160 | 150 | 154 | 152 | 144 | 128 | 124 | 124 | 128 | 124 | 146 | 150 | 156 | 162 | 166 | 152 | 158 | 142 |  | 142 | 146 | 156 | 148 | 158 | 158 | 158 | 3550080
64 | Malancha, Ctg. EPZ (United) | 38 | 38 | 38 | 39 | 39 | 39 | 35 | 13 | 7 | 3 | 2 | 2 | 2 | 2 | 3 | 5 | 9 | 11 |  | 16 | 20 | 22 | 30 | 35 | 36 | 37 | 507360
65 | Feni 22MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 20 | 20 | 19 | 19 | 19 | 21 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 471456
66 | Feni 11 MW PP (Doreen) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 10 | 10 | 10 | 10 | 10 | 5 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 226980
67 | Jangalia 33MW PP (Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 21 | 16 | 24 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 590100
68 | Cumilla 25 MW PP (Summit) | 18 | 18 | 18 | 18 | 20 | 20 | 20 | 18 | 18 | 18 | 18 | 18 | 18 | 12 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 437980
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 28 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 25 | 25 | 25 | 26 | 26 | 26 | 26 | 10 | 10 | 10 | 10 | 10 | 10 | 14 | 27 | 27 | 27 | 27 |  | 24 | 27 | 27 | 27 | 27 | 27 | 25 | 519480
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 801100
72 | Rupganj 33 MW PP(Summit) | 30 | 30 | 30 | 30 | 33 | 33 | 33 | 33 | 33 | 30 | 16 | 26 | 26 | 26 | 28 | 28 | 28 | 24 |  | 24 | 28 | 28 | 30 | 30 | 30 | 30 | 707800
73 | Ghorashal 108MW PP (Regent) | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 86 | 84 | 84 | 87 | 86 | 89 | 84 | 85 | 88 | 88 |  | 88 | 91 | 88 | 91 | 91 | 91 | 91 | 2107636
| Feni Lanka Power | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 0 | [15 empty] | 0 | 172140
| Chowmuhani 113 MW | 41 | 40 | 28 | 28 | 28 | 28 | 28 | 28 | 36 | 26 | 28 | 28 | 28 | 28 | 28 | 40 | 57 | 94 |  | 113 | 116 | 117 | 115 | 117 | 115 | 102 | 1340640
| Manikgonj 162MW PP(MPGL) | 25 | 24 | 38 | 36 | 36 | 36 | 35 | 35 | 35 | 35 | 35 | 40 | 72 | 82 | 108 | 108 | 117 | 162 |  | 162 | 162 | 162 | 162 | 162 | 162 | 48 | 1946880
77 | Siddhirganj 100 PP(Dutch Bangla) | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 8 | 8 | 8 | 8 | 36 |  | 40 | 40 | 40 | 40 | 40 | 40 | 16 | 383702
78 | Gazipur 52 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 31 |  | 40 | 40 | 40 | 31 | 33 | 33 | 8 | 320640
79 | Kodda 150MW PP | 126 | 125 | 125 | 62 | 14 | 14 | 15 | 16 | 16 | 16 | 46 | 46 | 46 | 46 | 45 | 45 | 62 | 62 |  | 110 | 110 | 110 | 125 | 110 | 90 | 90 | 1565760
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | [17 empty] | 1 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 54034
| Gazipur 100 MW PP | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 31 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 17 | 1086600
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 1 | 3 | 4 | 3 | 5 | 6 | 2 | 3 | 1 | 1 | 0 |  | 0 | [6 empty] | 29664
| Jodiac Power | 36 | 36 | 36 | 22 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 17 | 17 | 17 | 36 | 36 | 36 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 710766
| Karnaphuli Power Ltd. | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2685552
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL) | 8 | 8 | [11 empty] | 0 | 4 | 7 | 8 | 22 |  | 40 | 41 | 41 | 41 | 42 | 34 | 11 | 271680
| Meghnaghat 104 MW PP (OPCL) | 17 |  |  |  | 16 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 50 |  | 55 | 55 | 55 | 55 | 55 | 55 | 38 | 584640
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 261960
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 43 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1208656
94 | Gagnagar 102 MW PP (Digital Power) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 8 | 384624
95 | Patenga 50MW PP (Baraka) | 25 | 25 | 25 | 25 | 25 | 25 | 26 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 26 | 38 |  | 38 | 38 | 38 | 38 | 38 | 38 | 28 | 690720
96 | Chattogram 108 MW PP (ECPV) | 11 | 11 | 12 | 11 | 11 | 12 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 70 |  | 95 | 95 | 95 | 95 | 95 | 48 | 10 | 657600
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 38 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1145451
100 | Manikganj 55 MW PP (Northern) | 35 | 35 | 35 | 35 | 35 | 35 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 35 | 48 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 35 | 887778
101 | Kushiara 163 MW CCPP (KP)
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 1 | 1 | 2 | 2 | 3 | 2 | 0 | 1 | 0 | 0 | 0 | [8 empty] | 13900
103 | Kamalaghat 54 MW PP(Banco Energy) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 792720
104 | Keranigonj 300 MW PP (APR) | 180 | 150 | 151 | 101 | 62 | 27 |  |  | 106 | 156 | 225 | 225 | 225 | 108 | 225 | 227 | 124 | 0 |  | 25 | 25 | 25 | 122 | 103 | 206 | 102 | 2919533
105 | Bramhangoan 100 MW PP (Aggreko) | 80 | 75 | 75 | 80 | 80 |  |  |  | 50 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 90 | 0 |  | 90 | 90 | 90 | 90 | 90 | 90 | 80 | 1582573
106 | Mymensingh 200 MW PP (United) | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 94 | 96 | 96 | 95 | 95 | 95 | 95 | 105 | 115 |  | 96 | 97 | 96 | 97 | 106 | 107 | 107 | 1999200
112 | Aurahati 100MW PP (Aggreko) | 70 | 70 | 70 | 70 | 70 |  |  |  | 50 | 80 | 80 | 81 | 81 | 80 | 80 | 80 | 80 | 0 |  | 90 | 90 | 90 | 90 | 90 | 90 | 70 | 1524872
114 | Kodda 149 MW PP Unit-1 (Summit) | 70 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 121 | 149 | 149 | 149 | 149 | 149 | 149 | 142 | 149 | 149 |  | 149 | 149 | 148 | 140 | 149 | 149 | 149 | 2967552
115 | Juldah 100 MW PP Unit-3 (Acorn) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 257280
116 | Chandpur 200MW (Desh energy) | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 102 | 180 |  | 180 | 180 | 180 | 180 | 155 | 155 | 107 | 2542080
117 | Ashuganj 150MW PP (Midland) | 132 | 135 | 132 | 133 | 132 | 132 | 128 | 125 | 123 | 122 | 120 | 120 | 113 | 113 | 118 | 120 | 125 | 132 |  | 135 | 137 | 133 | 133 | 142 | 143 | 140 | 3092872
118 | Bibiyana-III 400 MW CCPP | 402 | 401 | 401 | 401 | 402 | 401 | 402 | 400 | 404 | 405 | 404 | 403 | 404 | 405 | 405 | 404 | 402 | 365 |  | 402 | 403 | 403 | 403 | 402 | 402 | 401 | 9598000
| Jamalpur 115 MW PP (United) | 50 | 50 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 78 | 98 |  | 108 | 108 | 109 | 109 | 99 | 99 | 99 | 1711200
| Anwara 300 MW PP (United) | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 85 | 88 | 88 | 88 | 88 | 87 | 88 | 52 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 1462800
| Juldah unit-2 (Acorn) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 20 | 20 | 10 | 10 | 10 | 10 | 264000
| Anlima Energy Ltd. | 107 | 92 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 90 | 107 | 107 |  | 107 | 107 | 107 | 107 | 107 | 92 | 107 | 2531673
| Bhairob 54.5 MW | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 887760
| Spectra Solar Plant Ltd. | [5 empty] | 1 | 4 | 10 | 16 | 26 | 14 | 19 | 24 | 6 | 29 | 19 | 2 | 1 |  | 0 | [6 empty] | 210110
| Chandpur 115(Doreen) | 97 | 82 | 96 | 96 | 96 | 96 | 96 | 80 | 78 | 78 | 77 | 68 | 76 | 76 | 77 | 78 | 77 | 77 |  | 78 | 78 | 77 | 77 | 77 | 78 | 79 | 1983360
| Kanchan Purbachal Power Generation Ltd. | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 40 | 55 | 55 | 55 | 54 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1325160
Mirsharai 150 MW (Oil)
Mirsharai 150 MW (Gas)
120 | Eastern Zone Total | 7211 | 7138 | 7164 | 7026 | 6953 | 6723 | 6645 | 6483 | 6744 | 7043 | 7240 | 7294 | 7323 | 7243 | 7549 | 7442 | 7461 | 7500 |  | 8161 | 8239 | 8318 | 8432 | 8400 | 8506 | 7927 | 178716846
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | 16 | [16 empty] | 0 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 94080
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 10 | 4 | [14 empty] | 0 | 5 |  | 38 | 45 | 33 | 26 | 21 | 15 | 15 | 154080
| Khulna 225 MW CCPP | 227 | 227 | 227 | 227 | 227 | 205 | 194 | 190 | 140 | 120 | 150 | 150 | 150 | 150 | 150 | 150 | 120 | 120 |  | 170 | 226 | 226 | 226 | 226 | 227 | 229 | 4527360
129 | Rupsha 105 MW PP (Orion rupsha) | [6 empty] | 2 | 17 | 17 | [6 empty] | 10 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 0 | 159360
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 2 | 13 | 38 | 28 | 33 | 12 | 27 | 78 | 33 | 30 | 62 | 39 | 1 |  | 0 | [6 empty] | 374400
131 | Rampal 1320 MW (BIFPCL)
132 | United Payra Power Ltd. | [25 empty] | 0 | 0
133 | Bhola Nutan Biddut BD LTD (GAS) | 8 | 8 | 30 | 60 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 115 | 110 | 151 | 167 | 162 | 160 | 163 |  | 161 | 163 | 164 | 191 | 225 | 225 | 220 | 2985820
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 32 | 32 | 32 | 32 | 16 | 16 | [6 empty] | 16 | 16 | 16 | 16 | 16 | 16 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 463392
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 152 | 152 | 152 | 152 | 152 | 152 | 107 | 100 | 101 | 105 | 105 | 112 | 114 | 114 | 115 | 116 | 116 | 92 |  | 106 | 116 | 116 | 86 | 86 | 86 | 86 | 2860636
140 | Bhola 33 MW PP (Venture) | 30 | 29 | 28 | 27 | 26 | 23 | 20 | 17 | 17 | 16 | 17 | 14 | 15 | 18 | 18 | 18 | 17 | 18 |  | 20 | 21 | 21 | 22 | 22 | 23 | 23 | 498847
141 | Noapara 100 MW PP (Bangla Trac) | 92 | 92 | 70 | 50 | 10 | [11 empty] | 0 | 0 |  | 10 | 20 | 20 | 0 |  | 3 | 40 | 460800
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP | 38 | 29 | 32 | 32 | 32 | 32 | 27 | 27 | 27 | 0 | [6 empty] | 0 | 0 |  | 7 | 16 | 42 | 62 | 73 | 70 | 55 | 539136
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 32 | 32 | 32 | 32 | 32 | 67 |  | 67 | 67 | 67 | 67 | 67 | 32 | 15 | 791280
146 | Bheramara HVDC | 895 | 894 | 895 | 895 | 894 | 894 | 894 | 894 | 894 | 893 | 894 | 894 | 893 | 886 | 886 | 886 | 887 | 886 |  | 886 | 886 | 886 | 887 | 886 | 886 | 887 | 21536000
147 | Bheramara 410 MW CCPP | 260 | 265 | 270 | 275 | 270 | 275 | 275 | 265 | 220 | 200 | 200 | 250 | 230 | 250 | 220 | 220 | 220 | 220 |  | 275 | 280 | 280 | 280 | 280 | 280 | 280 | 6302880
148 | Payra 1320 MW | 1160 | 1170 | 1130 | 1110 | 1070 | 1020 | 990 | 1010 | 950 | 950 | 900 | 890 | 930 | 930 | 910 | 900 | 890 | 880 |  | 910 | 1010 | 1030 | 1090 | 1060 | 1060 | 1030 | 26073300
149
150 | Barapukuria TPP Unit-1 | 83 | 83 | 82 | 81 | 81 | 80 | 80 | 80 | 79 | 79 | 79 | 79 | 80 | 79 | 78 | 80 | 81 | 80 |  | 80 | 81 | 79 | 81 | 80 | 81 | 80 | 1926982
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 |  | 250 | 250 | 250 | 245 | 240 | 240 | 250 | 6046900
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 |  | 32 | 32 | 32 | 32 | 31 | 32 | 32 | 760880
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 0 | 1 | 5 | 5 | 5 | 3 | 5 | 3 | 0 | 3 | 1 | 0 | [8 empty] | 37800
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 214 | 214 | 214 | 214 | 214 | 214 | 214 | 214 | 208 | 204 | 199 | 192 | 197 | 210 | 207 | 214 | 214 | 214 |  | 203 | 214 | 214 | 214 | 214 | 214 | 214 | 5322291
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
| Sirajgonj 225 MW CCPP Unit-2 (Oil) | 217 | 217 | 217 | 218 | 219 | 190 | 130 | 130 | 130 | 130 | 133 | 204 | 213 | 212 | 211 | 214 | 180 | 130 |  | 146 | 173 | 181 | 216 | 217 | 216 | 219 | 4755145
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 199 | 201 | 200 | 201 | 202 | 202 | 203 | 206 | 197 | 196 | 196 | 202 | 208 | 205 | 203 | 203 | 203 | 207 |  | 192 | 192 | 192 | 190 | 188 | 189 | 189 | 5024445
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 414 | 414 | 414 | 414 | 414 | 414 | 414 | 414 | 414 | 414 | 414 | 414 | 414 | 414 | 414 | 418 | 300 | 243 |  | 418 | 415 | 417 | 419 | 421 | 420 | 425 | 9750327
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | 23 | 23 | 23 | 23 | 23 | 0 | [6 empty] | 0 | 5 | 5 | 7 | 14 | 26 |  | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 307721
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 0 | 18 | 22 | 22 | 21 | 18 | 20 | 19 | 19 | 18 | 18 | 18 | 20 |  | 21 | 21 | 21 | 22 | 22 | 22 | 22 | 462480
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 247068
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 34 | 42 | 42 |  | 50 | 50 | 50 | 42 | 42 | 42 | 42 | 969072
167 | Katakhali 50 MW Peaking PP | 24 | [16 empty] | 0 |  | 32 | 32 | 32 | 32 | 32 | 32 | 24 | 170290
168 | Santahar 50 MW Peaking PP | [19 empty] | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 179240
169 | Natore 52 MW PP (Rajlanka) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 43 | 43 | 43 | 43 | 43 | 8 | 8 | 313925
170 | Chapainawabganj 100 MW Peaking PP | 31 | [16 empty] | 8 |  | 30 | 66 | 82 | 82 | 82 | 67 | 23 | 396728
171 | Baghabari 200 MW PP (Paramount) | 165 | 165 | 165 | 171 | 161 | [5 empty] | 1 | 20 | 44 | 80 | 20 | 0 |  | 0 |  | 15 | 50 | 50 | 0 |  | 6 | 88 | 1332808
| Bagura 113 MW PP (Confidence)-2 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 72 | 93 | 94 |  | 94 | 94 | 94 | 94 | 94 | 94 | 50 | 1660320
172 | Confidence Power Bogura Unit-1 113 MW | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 90 | 95 | 95 |  | 95 | 95 | 95 | 95 | 95 | 95 | 55 | 1656480
173 | Rangpur 20 MW GTPP | [19 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 53 | 53 | 55 | 55 | 55 | 55 | 55 | 67 | 89 |  | 89 | 89 | 90 | 90 | 90 | 90 | 56 | 1555353
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1 | 2 | 3 | 4 | 4 | 3 | 4 | 6 | 5 | 3 | 1 | 1 |  | 0 | [6 empty] | 41715
178 | Energypac Power Venture Thakurgaon Ltd. | [17 empty] | 34 |  | 34 | 34 | 60 | 72 | 72 | 72 | 0 | 326016
178 | Intraco Solar 30 MW | [5 empty] | 0 | 4 | 14 | 16 | 17 | 18 | 17 | 36 | 0 | 9 | 7 | 5 | 1 |  | 0 | [6 empty] | 145640