## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on forecasted generation & Demand of national grid on | [6 empty] | 2019-05-30 | Thursday
|  | Date (day): | 2019-05-30 |  | Thursday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 14810 | MW |  |  | (b) At Evening Peak Hour : |  | 15029 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2019-05-29 | 2019-05-30 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | Gas | PDB | 2*55 | 110 | 85 | 35 | 35 | 35 | 35 |  | 50 | ST-1 under maint.
| Ghorasal GT: Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 94 | 94 | 94 | 134 |  |  | On test.
| Ghorasal GT: Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 100 | 100 | 100 | 80 |  | Gas shortage
| Ghorasal ST: Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 110 | 110 | 110 | 110 | 80 |  | Gas shoetage
2 | Ghorasal ST: Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 300 | 300 | 360 | 360
3 | Ghorashal 78MW (MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 |  |  | Gas Shortage
4 | Ghorashal (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 6 | 6 | 108 | 108
5 | Haripur GT: Unit-1, 2 |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 | 40 |  | Gas shortage
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 328 | 330 | 412 | 412 |  |  | FGMO
7 | Haripur NEPC 110MW |  | HFO | IPP | 8*15 | 110 | 110 | 13 | 110 | 110 | 110
8 | Haripur Power CCPP 360MW |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 320 | 344 | 360 | 360
9 | Meghnaghat CCPP 450MW |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 380 | 430 | 450 | 450
10 | Meghnaghat (IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 22 | 100 | 100 | 100
11 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 290 | 285 | 335 | 335 |  |  | FGMO
12 | Madanganj 102MW |  | HFO | QRPP | 6*17 | 102 | 100 | 15 | 97 | 100 | 100
13 | Madanganj-55 MW |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 12 | 55 | 55 | 55
14 | Keraniganj (Powerpac) 100MW |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 50 | 100 | 100
15 | Narshingdi (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 16 | 19 | 19 | 19
16 | Siddhirgonj ST 210MW |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 115 |  | Gas shortage
17 | Siddhirgonj GT Unit-1& 2 |  | Gas | EGCB | 2*105 | 210 | 210 | 59 | 52 | 100 | 100 | 110 |  | Gas shortage
| Siddhirganj Desh |  | HSD | QRPP | 96*1.2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
18 | Siddhirganj (Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 23 | 98 | 100 | 100
19 | Siddhirganj CCPP-335 MW |  | Gas | EGCB | 1*217 | 217 | 217 | 0 | 0 | 0 | 0 | 37 |  | Gas shortage
0 | Pagla (DPA ) |  | HSD | QRPP | 100*0.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
20 | Gagnagar (Orion) |  | HFO | IPP | 12*8.924 | 102 | 102 | 50 | 100 | 102 | 102
21 | Katpotti 51 MW |  | HFO | IPP | 7*7.9 | 51 | 51 | 6 | 49 | 49 | 49
22 | Banco Energy 54MW |  | HFO | IPP | 3*18 | 54 | 54 | 35 | 35 | 35 | 35 |  | 19 | Engine problem
23 | Kodda 149MW |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 48 | 145 | 149 | 149
24 | Northern 55 MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 56 | 56 | 55 | 55
25 | Southern 55MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
26 | Bosila 108MW |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 63 | 56 | 65 | 65 |  | 43 | Engine problem
27 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 53 | 57 | 58 | 58 |  | 22 | Engine problem
28 | Summit Maona |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
29 | Summit Rupganj |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 33 | 33
30 | Gazipur (RPCL) |  | HFO | IPP | 6*8.9 | 52 | 52 | 47 | 48 | 48 | 48 |  | 4
31 | Tongi GT |  | Gas | PDB | 1* 105 | 105 | 105 | 40 | 40 | 40 | 40 | 65 |  | Gas shortage
32 | Summit Gazipur -2 |  | HFO | IPP | 18*17.076 | 300 | 300 | 15 | 216 | 300 | 300
33 | APR Energy , Keranigonj |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 300 | 300
34 | Bramhangoan 100 MW (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 100 | 100
35 | Aggreko Aurahati 100MW |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 100 | 100
36 | Summit Gazipur-1 150MW |  | HFO | IPP | 149 | 149 | 149 | 68 | 149 | 149 | 149
| Gazipur 100 MW |  | HFO | RPCL | 100 MW | 0 | 0 | 91 | 109 | 100 | 100
| Dhaka area Total |  |  |  |  | 5934 | 5698 | 2800 | 3788 | 4819 | 4859 | 527 | 138
37 | Chattogram ST-1 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 100 | 100 | 100 | 80 |  | Gas shortage
| Chittgong ST-2 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
38 | Raozan 25 MW (RPCL) |  | HFO | IPP | 3*8.9 | 25 | 25 | 16 | 25 | 25 | 25
39 | Teknaf Solartech 20MW |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 4.3 | 0 | 20 | 0
40 | Patenga 50MW |  | HFO | IPP | 8*6.98 | 50 | 50 | 40 | 47 | 45 | 45
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 30 | 36 | 36 | 36 |  | 194 | Low water lavel
42 | Sikalbaha ST 60MW |  | Gas | PDB | 1*60 | 60 | 40 | 0 | 0 | 0 | 0 |  | 40 | Under S/D
43 | Sikalbaha 225MW |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 218 | 217 | 225 | 225
44 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 147 | 140 | 140 | 140
45 | Sikalbaha (Energis) |  | HFO | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 51 | 16 | 24 | 16 | 16 |  | 35 | Engine problem
| Baraka Sikalbaha PL |  | HFO | IPP | 105 MW | 0 | 0 | 91 | 105 | 105 | 105
46 | Hathazari peaking |  | HFO | PDB | 11*8.9 | 98 | 98 | 2 | 84 | 74 | 74
47 | Dohazari Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 17 | 83 | 85 | 85
48 | Juldah (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 10 | 98 | 100 | 100
49 | Juldah 100 MW Unit-3 |  | HFO | IPP | 0 | 100 | 100 | 100 | 100 | 100 | 100
50 | Barabkunda (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 16 | 18 | 17 | 17 |  | 5
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 33 | 10 | 20
51 | Chattogram ECPV 108 MW |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 90 | 100 | 100
| Kaptai Solar |  | Solar | PDB | 7.4 MW | 0 | 0 | 2.1 | 0 | 3 | 0
| Anwara United |  | HFO | United Group | 300 MW | 0 | 0 | 84 | 75 | 84 | 84
| Chattogram area Total |  |  |  |  | 1761 | 1681 | 895.4 | 1275 | 1285 | 1272 | 260 | 274
52 | Ashuganj ST: Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
| Ashuganj ST: Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
| Ashuganj ST: Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 125 | 125 | 120 | 120 | 54 |  | Gas shortage
53 | Ashuganj CCPP 225 MW |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 196 | 214 | 221 | 221
54 | Ashuganj CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 320 | 320 | 360 | 360
55 | Ashuganj CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 300 | 320 | 360 | 360
56 | Ashuganj Engines TSK |  | Gas | APSCL | 14*3.968 | 53 | 45 | 32 | 36 | 33 | 33 |  | 12 | Engine problem
57 | Ashuganj (Precision) 55MW |  | Gas | RPP | 15*4 | 55 | 55 | 55 | 55 | 55 | 55 | 0
58 | Ashuganj (United) 53MW |  | Gas | QRPP | 14*4 | 53 | 53 | 5 | 5 | 5 | 5 | 48 |  | Gas Shortage
59 | Ashuganj 195MW Modular |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
60 | Ashuganj (Midland) 51MW |  | Gas | IPP | 6*9.34 | 51 | 51 | 35 | 35 | 35 | 35 |  | 16 | Engine problem
61 | Midland 150MW |  | HFO | IPP | 23*7.015 | 150 | 150 | 100 | 150 | 133 | 133
62 | B.Baria (Aggreko) 85MW |  | Gas | QRPP | 86*1.10 | 85 | 85 | 0 | 0 | 0 | 0 |  |  | Contract expired
63 | Daudkandi Peaking 52MW |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 50 | 0 | 50
64 | Chandpur CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 100 | 100 | 100 | 100
65 | Chandpur Desh 200MW |  | HFO | IPP | 0 | 200 | 200 | 200 | 200 | 200 | 200
66 | Feni (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 22 | 22 | 22
67 | Feni, Mohipal (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
** | Tripura |  |  | Imported power | 0 | 160 | 160 | 164 | 186 | 152 | 189
68 | Jangalia (Summit) 33MW |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 0 | 25 | 33 | 33
69 | Lakdhanvi 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 52 | 52 | 52 | 52
70 | Summit Cumilla 25MW |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 20 | 20
71 | Daudkandi bangla trak |  | HSD | IPP | 154*1.4 | 200 | 200 | 200 | 0 | 200 | 200
| Cumilla Area Total |  |  |  |  | 2951 | 2891 | 1941 | 1934 | 2120 | 2207 | 553 | 28
72 | Mymensingh RPCL 210MW |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 144 | 145 | 150 | 150 | 52 |  | Gas shortage
73 | Tangail (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 20 | 20
74 | Jamalpur 95MW |  | HFO | IPP | 12*8.924 | 95 | 95 | 80 | 91 | 70 | 95
75 | Sarishabari (Solar) |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 2 | 0
76 | United Mymensingh PPL |  | HFO | IPP | 200 | 200 | 200 | 50 | 150 | 200 | 200
77 | United Jamalpur PPL |  | HFO | IPP | 115 MW | 115 | 115 | 96 | 86 | 100 | 100 |  | 15 | Engine problem
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 392 | 492 | 542 | 565 | 52 | 0
78 | Fenchugonj CCPP-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 56 | 56 | 57 | 57
79 | Fenchugonj CCPP-2 |  | Gas | PDB | !F71 | 104 | 90 | 58 | 58 | 58 | 58
80 | Kushiara 163 MW CCPP GT |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 130 | 163 | 163
81 | Shajibazar 330 MW |  | Gas | PDB | 3*110 | 330 | 330 | 251 | 250 | 330 | 330 |  |  | FGMO
82 | Fenchugonj (Barakatullah) 51MW |  | Gas | RPP | 19*2.90 | 51 | 51 | 47 | 53 | 50 | 50
83 | Fenchuganj (EPL) 44MW |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 50 | 50 | 44 | 44
84 | Hobiganj 11MW |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
85 | Shahjibazar GT: Unit- 8, 9 |  | Gas | PDB | 2*35 | 70 | 66 | 61 | 61 | 66 | 66 |  |  | FGMO
86 | Shahjibazar 86MW |  | Gas | RPP | 32*2.90 | 86 | 86 | 71 | 75 | 86 | 86
87 | Shahjibazar (EPL) 50MW |  | Gas | RPP | 27*2.0 | 50 | 50 | 44 | 45 | 46 | 46
88 | Sylhet GT 150 MW |  | Gas | PDB | 1*142 | 142 | 142 | 112 | 104 | 130 | 130
89 | Sylhet GT 20 MW |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18
90 | Sylhet (EPL) 50MW |  | Gas | RPP | 27*2 | 50 | 50 | 46 | 45 | 50 | 50
91 | Shahjahanulla 25 MW |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 7 | 22 | 25 | 25
92 | Summit Bibiana- 2 |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 250 | 255 | 341 | 341 |  |  | FGMO
| Bibiyana-3 285 MW |  | Gas | PDB | 285 MW | 0 | 0 | 240 | 280 | 269 | 269 |  |  | On test
93 | Sylhet (Desh) 10MW |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1594 | 1549 | 1462 | 1523 | 1754 | 1754 | 0 | 0
94 | Bheramara GT-1,2,3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 48 | 0 | 32
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 928 | 929 | 948 | 948
| Khulna (KPCL-1 & 3) |  | HFO | IPP | 19*6.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
95 | Khulna (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 16 | 99 | 115 | 115
96 | Faridpur Peaking |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 36 | 33 | 33
97 | Khulna CCPP 225MW |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 120 | 233 | 225 | 225
98 | Gopalganj Peaking |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 58 | 50 | 80
99 | Bheramara 360 MW |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 |  | 410 | Under maint. |  | 28/05/2019
100 | Noapara (KZA) 40MW |  | HFO | QRPP | 5*8.5 | 40 | 40 | 8 | 40 | 40 | 40
0 | Khulna (Aggreeco) 55MW |  | HSD | QRPP | 71*0.85 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
101 | Bangla Trak Noapara |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 96 | 100 | 100
102 | Labon Chora 105 MW |  | HFO | IPP | 6*18.445 | 105 | 105 | 53 | 105 | 105 | 105
103 | Madhumati Power Plant |  | HFO | IPP | 100 MW | 105 | 105 | 88 | 90 | 102 | 102
| Khulna Area Total |  |  |  |  | 2328 | 2314 | 1213 | 1734 | 1718 | 1780 | 0 | 410
104 | Summit Barisal 110 MW |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 110 | 110 | 110
105 | Barisal GT: Unit-1, 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 12 | 0 | 20
106 | Bhola (Venture) 33MW |  | Gas | RPP | 1*34.50 | 33 | 33 | 26 | 33 | 39 | 39
107 | Bhola CCPP 194MW |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 174 | 173 | 173 | 173
108 | Bhola Aggreko 95MW |  | Gas | QRPP | 96*1.10 | 95 | 95 | 91 | 97 | 90 | 90
| Barisal Area Total |  |  |  |  | 472 | 462 | 291 | 425 | 412 | 432 | 0 | 0
109 | Baghabari GT 71MW |  | Gas | PDB | 1*71 | 71 | 71 | 55 | 55 | 60 | 60
| Baghabari GT 100MW |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
110 | Baghabari Peaking 50MW |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 50 | 50
111 | Bera Peaking |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 32 | 35 | 35
112 | Amnura 50MW |  | HFO | QRPP | 7*7.79 | 50 | 50 | 12 | 50 | 50 | 50
113 | Katakhali (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 50 | 50 | 50
114 | Katakhali Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 47 | 47 | 47
115 | Sirajgonj Unit-1 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 181 | 168 | 200 | 200 |  |  | FGMO
116 | Sirajgonj Unit-2 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 185 | 154 | 200 | 200 |  |  | FGMO
117 | Sirajgonj Unit-3 225MW |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 185 | 186 | 220 | 220 |  |  | FGMO
118 | Sirajgonj Unit-4 414 MW(Gas) |  | Gas | SNWPGCL | 1*282+1*132 | 414 | 414 | 320 | 300 | 414 | 414
119 | Santahar Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 35 | 35 | 35
120 | Bogra (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 21 | 22 | 22 | 22
121 | Bogra (EPL) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 13 | 16 | 16 | 16
122 | Ullapara (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
123 | Rajlanka 52 MW |  | HFO | IPP | 52 | 52 | 52 | 8 | 50 | 52 | 52
124 | Chapainawabganj-100 MW |  | HFO | PDB | 104 | 104 | 104 | 0 | 91 | 95 | 95
125 | Paramount Baghabari |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
126 | Confidence Bogura-2 (CPBL) |  | HFO | IPP | 113 MW | 113 | 113 | 120 | 107 | 100 | 100
| Rajshahi Area Total |  |  |  |  | 2080 | 2070 | 1105 | 1424 | 1857 | 1857 | 0 | 100
127 | Barapukuria Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under overhauling
| Barapukuria Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 66 | 65 | 70 | 70
128 | Barapukuria Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 199 | 199 | 199 | 199 | 75
129 | Rangpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 17 | 16 | 16
130 | Saidpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 17 | 18 | 18
| Confidence Rangpur |  | HFO | IPP | 113 MW | 0 | 0 | 0 | 0 | 0 | 0
| Rangpur Area Total |  |  |  |  | 564 | 484 | 265 | 298 | 303 | 303 | 75 | 85
| Total |  |  |  |  | 18329 | 17786 | 10364.4 | 12893 | 14810 | 15029 | 1467 | 1035
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 9734.1596 | 12109 | 13909.4307 | 14115.1137
A. |  | 2019-05-29 | (Yesterday) |  |  |  |  | Wednesday
1 | Highest Generation : |  |  | 12893 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 8842.06 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 12893 | MW
3 | Day peak Generation : |  |  | 10364.4 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 12109 | MW
4 | Evening peak Generation : |  |  | 12893 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 264.4497 | MKWHr | By Solar | 0.16976 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas: | 158.2907 | MKWHr |  | By Oil: | 72.6779 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal: | 6.4695 | MKWHr |  | By Hydro: | 0.71238 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1467 | MW | Dhaka | 4451 | 4451 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1035 | MW | Chittagong | 1108 | 1108 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 2502 | MW | Khulna | 1542 | 1542 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1386.68 | MMCFD |  |  | Rajshahi | 1297 | 1297 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 108673920.784 | ii) Oil : | Taka | 554940157.04 | Comilla | 1216 | 1216 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 28565454.37 | Total | Taka | 692179532.194 | Mymensingh | 928 | 928 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0.6885 | MKWHr. | Sylhet | 511 | 511 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -320 | MW (E to W) at | 21:00 | hrs | Barisal | 357 | 357 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -320 | MW at | 21:00 | hrs | Rangpur | 699 | 699 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 36.6° C |  |  | Total | 12109 | 12109 |  | 0
B. |  | 2019-05-30 | (Today) |  |  |  | Thursday |  |  | Probable max. temperature in Dhaka |  |  | 36.4° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 13000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 15029 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 10300 | MW
4 | Reserve(Generation end) |  |  |  | 2029 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 266.6444 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 8599.5 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 22.2924 | MKWHr. | ii) HVDC Flow at Peak Time |  | 929 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.8371 | MKWHr. | iii) Maximum HVDC Flow : |  | 930 | MW at | 11:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 73.84 |  | (b) Today: | 73.9 |  | (c) Rule Curve: |  | 76.4
.
** Wapda control unable to give gas reading.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2019-05-29
Plant Name | Ghorasal ST: Unit-1,2 | Ghorasal GT: Unit-3 | Ghorasal GT: Unit-4 | Ghorasal ST: Unit-5 | Ghorasal ST: Unit-7 | Ghorashal (Regent) | Ghorashal 78MW (MAX) | Haripur 412 MW CCPP | Haripur Power CCPP 360MW | Haripur NEPC 110MW | Haripur GT: Unit-1, 2 | Meghnaghat CCPP 450MW | Meghnaghat CCPP(Summit) | Meghnaghat (IEL) | Madanganj 102MW | Madanganj-55 MW | Siddhirganj CCPP-335 MW | Siddhirgonj ST 210MW | Siddhirgonj GT Unit-1& 2 | Siddhirganj Desh | Siddhirganj (Dutch Bangla) | Gagnagar (Orion) | Kodda 149MW | Keraniganj (Powerpac) 100MW | Bosila 108MW | Pagla (DPA ) | Katpotti 51 MW | Banco Energy 54MW | Northern 55 MW | Southern 55MW | Narshingdi (Doreen) | Summit Ashulia | Summit Madhabdi | Summit Maona | Summit Rupganj | Gazipur (RPCL) | Tongi GT | Kaptai Unit-1, 2 & 3 | Kaptai Unit-4 & 5 | Chattogram ST-1 (Raozan) | Chittgong ST-2 (Raozan) | Raozan 25 MW (RPCL) | Sikalbaha 225MW (Gas) | Sikalbaha 225MW (Oil) | Sikalbaha GT 150MW (Gas) | Sikalbaha GT 150MW (Oil) | Sikalbaha ST 60MW | Sikalbaha (Energis) | Hathazari peaking | Dohazari Peaking | Juldah (Acorn) | Chattogram ECPV 108 MW | Patenga 50MW | Barabkunda (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj ST: Unit- 3 | Ashuganj ST: Unit- 4 | Ashuganj ST: Unit- 5 | Ashuganj CCPP(North) | Ashuganj CCPP(South) | Ashuganj CCPP 225 MW | Ashuganj 195MW Modular | Chandpur CCPP | Ashuganj Engines TSK | Ashuganj (Precision) 55MW | Ashuganj (United) 53MW | Ashuganj (Midland) 51MW | B.Baria (Aggreko) 85MW | Daudkandi Peaking 52MW | Lakdhanvi 52 MW | Feni (Doreen) 22MW | Feni, Mohipal (Doreen) | Jangalia (Summit) 33MW | Summit Cumilla 25MW | Tripura | Mymensingh RPCL 210MW | Jamalpur 95MW | Tangail (Doreen) 22MW | Sarishabari (Solar) | Fenchugonj CCPP-1 | Fenchugonj CCPP-2 | Fenchugonj (Barakatullah) 51MW | Fenchuganj (EPL) 44MW | Kushiara 163 MW CCPP GT | Shajibazar 330 MW | Shahjibazar GT: Unit- 8, 9 | Shahjibazar 86MW | Shahjibazar (EPL) 50MW | Sylhet GT 150 MW | Sylhet GT 20 MW | Sylhet (EPL) 50MW | Sylhet (Desh) 10MW | Summit Bibiana- 2 | Shahjahanulla 25 MW | Hobiganj 11MW | Daudkandi bangla trak | Summit Gazipur -2 | APR Energy , Keranigonj | Bramhangoan 100 MW (Aggreko) | United Mymensingh PPL | Aggreko Aurahati 100MW | Summit Gazipur-1 150MW | Teknaf Solartech 20MW | Juldah 100 MW Unit-3 | Chandpur Desh 200MW | Midland 150MW | Bibiyana-3 285 MW | United Jamalpur PPL | Gazipur 100 MW | Baraka Sikalbaha PL | Kaptai Solar | Anwara United | EasternBlank | Bheramara (HVDC ) | Bheramara GT-1,2,3 | Bheramara 360 MW | Khulna (KPCL-1 & 3) | Khulna (KPCL-2) | Khulna CCPP 225MW | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur Peaking | Gopalganj Peaking | Noapara (KZA) 40MW | Bhola CCPP 194MW | Bhola (Venture) 33MW | Summit Barisal 110 MW | Barisal GT: Unit-1, 2 | Baghabari GT 100MW | Baghabari GT 71MW | Baghabari Peaking 50MW | Bera Peaking | Chapainawabganj-100 MW | Amnura 50MW | Katakhali (Northern) | Katakhali Peaking | Rajlanka 52 MW | Santahar Peaking | Bogra (GBB) | Bogra (EPL) | Ullapara (Summit) | Barapukuria Unit-1 | Barapukuria Unit-2 | Barapukuria Unit-3 | Rangpur GT | Saidpur GT | Sirajgonj Unit-1 225MW (Gas) | Sirajgonj Unit-1 225MW (Oil) | Sirajgonj Unit-2 225MW (Gas) | Sirajgonj Unit-2 225MW (Oil) | Bhola Aggreko 95MW | Bangla Trak Noapara | Sirajgonj Unit-3 225 MW(Gas) | Sirajgonj Unit-3 225 MW(Oil) | Sirajgonj Unit-4 414 MW(Gas) | Labon Chora 105 MW | Paramount Baghabari | Confidence Bogura-2 (CPBL) | Madhumati Power Plant | Confidence Rangpur | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 35 | 133 | 100 | 110 | 300 | 6 | 0 | 328 | 353 | 0 | 0 | 450 | 260 | 10 | 15 | 0 | 0 | 0 | 91 | 0 | 0 | 7 | 149 | 0 | 65 | 0 | 20 | 35 | 56 | 55 | 19 | 25 | 28 | 33 | 25 | 47 | 40 | 34 | 0 | 100 | 0 | 25 | 217 | 0 | 140 | 0 | 0 | 16 | 7 | 85 | 78 | 95 | 47 | 16 | 38 | 0 | 0 | 120 | 330 | 356 | 182 | 8 | 50 | 33 | 56 | 5 | 35 | 0 | 0 | 52 | 22 | 11 | 24 | 20 | 162 | 148 | 94 | 20 | 0 | 57 | 58 | 50 | 50 | 130 | 251 | 56 | 78 | 45 | 105 | 18 | 46 | 10 | 250 | 22 | 11 | 0 | 0 | 0 | 0 | 194 | 0 | 149 | 0 | 100 | 200 | 150 | 297 | 93 | 90 | 109 | 0 | 68 |  | 929 | 0 | 0 | 0 | 49 | 120 | 0 | 0 | 31 | 57 | 40 | 173 | 38 | 110 | 0 | 0 | 60 | 0 | 0 | 91 | 50 | 16 | 0 | 52 | 35 | 22 | 16 | 0 | 0 | 71 | 199 | 0 | 16 | 181 | 0 | 178 | 0 | 89 | 0 | 189 | 0 | 400 | 105 | 0 | 108 | 88 | 0 |  | 8108 | 3513 | 11621 | 4712 | 929 | 2175 | 2748 | 270 | 34 | 591 | 162 | 0 | 0 | 73.82
2:00 | 35 | 134 | 100 | 110 | 300 | 6 | 0 | 328 | 354 | 0 | 0 | 450 | 260 | 0 | 15 | 0 | 0 | 0 | 58 | 0 | 0 | 7 | 149 | 0 | 65 | 0 | 20 | 35 | 56 | 55 | 19 | 25 | 28 | 33 | 17 | 45 | 40 | 34 | 0 | 100 | 0 | 25 | 220 | 0 | 139 | 0 | 0 | 16 | 0 | 85 | 78 | 95 | 47 | 16 | 39 | 0 | 0 | 120 | 330 | 330 | 182 | 8 | 50 | 33 | 55 | 5 | 35 | 0 | 0 | 52 | 22 | 11 | 24 | 20 | 160 | 148 | 94 | 20 | 0 | 57 | 58 | 50 | 50 | 130 | 252 | 49 | 78 | 46 | 104 | 18 | 46 | 10 | 250 | 22 | 11 | 0 | 0 | 0 | 0 | 150 | 0 | 141 | 0 | 100 | 200 | 150 | 250 | 99 | 90 | 109 | 0 | 68 |  | 928 | 0 | 0 | 0 | 49 | 120 | 0 | 0 | 31 | 57 | 32 | 173 | 36 | 110 | 0 | 0 | 60 | 0 | 0 | 91 | 18 | 0 | 0 | 52 | 0 | 22 | 16 | 0 | 0 | 71 | 199 | 0 | 16 | 184 | 0 | 180 | 0 | 89 | 0 | 188 | 0 | 380 | 105 | 0 | 108 | 88 | 0 |  | 7925 | 3403 | 11328 | 4598 | 928 | 2155 | 2634 | 270 | 34 | 549 | 160 | 0 | 0 | 73.82
3:00 | 35 | 94 | 100 | 110 | 300 | 6 | 0 | 331 | 333 | 0 | 0 | 450 | 285 | 0 | 15 | 0 | 0 | 0 | 60 | 0 | 0 | 7 | 149 | 0 | 65 | 0 | 20 | 35 | 56 | 55 | 19 | 25 | 28 | 33 | 17 | 39 | 40 | 35 | 0 | 100 | 0 | 25 | 217 | 0 | 140 | 0 | 0 | 16 | 0 | 85 | 10 | 96 | 47 | 16 | 40 | 0 | 0 | 120 | 330 | 330 | 187 | 8 | 50 | 33 | 55 | 5 | 35 | 0 | 0 | 52 | 22 | 11 | 24 | 20 | 162 | 100 | 94 | 20 | 0 | 57 | 58 | 50 | 50 | 130 | 250 | 63 | 78 | 46 | 105 | 18 | 46 | 10 | 245 | 22 | 11 | 0 | 0 | 0 | 0 | 150 | 0 | 43 | 0 | 100 | 200 | 150 | 269 | 99 | 90 | 109 | 0 | 68 |  | 928 | 0 | 0 | 0 | 49 | 120 | 0 | 0 | 31 | 52 | 40 | 173 | 38 | 110 | 0 | 0 | 60 | 0 | 0 | 91 | 0 | 0 | 0 | 52 | 0 | 22 | 16 | 0 | 0 | 71 | 200 | 0 | 18 | 188 | 0 | 184 | 0 | 89 | 0 | 186 | 0 | 380 | 105 | 0 | 108 | 89 | 0 |  | 7709 | 3400 | 11109 | 4556 | 928 | 2132 | 2479 | 271 | 35 | 546 | 162 | 0 | 0 | 73.83
4:00 | 35 | 94 | 100 | 110 | 300 | 6 | 0 | 328 | 335 | 0 | 0 | 450 | 245 | 0 | 15 | 0 | 0 | 0 | 59 | 0 | 0 | 0 | 100 | 0 | 65 | 0 | 20 | 35 | 56 | 17 | 19 | 25 | 24 | 33 | 25 | 24 | 40 | 35 | 0 | 100 | 0 | 8 | 218 | 0 | 140 | 0 | 0 | 16 | 0 | 85 | 10 | 95 | 47 | 17 | 40 | 0 | 0 | 120 | 330 | 330 | 183 | 8 | 50 | 33 | 56 | 5 | 35 | 0 | 0 | 52 | 22 | 11 | 24 | 20 | 158 | 99 | 94 | 20 | 0 | 57 | 58 | 50 | 50 | 130 | 247 | 51 | 79 | 46 | 105 | 19 | 46 | 10 | 250 | 22 | 11 | 0 | 0 | 0 | 0 | 100 | 0 | 11 | 0 | 100 | 200 | 150 | 269 | 99 | 90 | 109 | 0 | 68 |  | 928 | 0 | 0 | 0 | 49 | 120 | 0 | 0 | 21 | 0 | 0 | 173 | 38 | 110 | 0 | 0 | 60 | 0 | 0 | 61 | 0 | 0 | 0 | 8 | 0 | 22 | 16 | 0 | 0 | 71 | 199 | 0 | 0 | 182 | 0 | 179 | 0 | 90 | 0 | 190 | 0 | 380 | 105 | 0 | 108 | 88 | 0 |  | 7448 | 3198 | 10646 | 4532 | 928 | 2142 | 2194 | 270 | 35 | 387 | 158 | 0 | 0 | 73.83
5:00 | 35 | 94 | 100 | 110 | 300 | 6 | 0 | 328 | 307 | 0 | 0 | 450 | 260 | 0 | 15 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 80 | 0 | 13 | 0 | 20 | 35 | 56 | 17 | 19 | 25 | 24 | 33 | 25 | 0 | 40 | 36 | 0 | 100 | 0 | 8 | 204 | 0 | 140 | 0 | 0 | 16 | 0 | 85 | 10 | 10 | 47 | 17 | 40 | 0 | 0 | 120 | 300 | 330 | 182 | 8 | 50 | 33 | 55 | 5 | 35 | 0 | 0 | 8 | 22 | 11 | 24 | 20 | 158 | 101 | 94 | 20 | 0 | 57 | 58 | 50 | 50 | 100 | 249 | 64 | 79 | 46 | 105 | 19 | 46 | 10 | 245 | 22 | 11 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 100 | 165 | 5 | 270 | 99 | 90 | 71 | 0 | 85 |  | 928 | 0 | 0 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 0 | 173 | 35 | 110 | 0 | 0 | 60 | 0 | 0 | 61 | 0 | 0 | 0 | 8 | 0 | 22 | 16 | 0 | 0 | 71 | 199 | 0 | 0 | 189 | 0 | 178 | 0 | 90 | 0 | 192 | 0 | 340 | 53 | 0 | 40 | 89 | 0 |  | 6912 | 2990 | 9902 | 4489 | 928 | 2035 | 1640 | 270 | 36 | 346 | 158 | 0 | 0 | 73.84
6:00 | 35 | 94 | 100 | 110 | 300 | 6 | 0 | 280 | 275 | 0 | 0 | 450 | 265 | 0 | 15 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 20 | 17 | 56 | 17 | 19 | 25 | 27 | 33 | 25 | 0 | 40 | 36 | 0 | 100 | 0 | 8 | 198 | 0 | 140 | 0 | 0 | 16 | 0 | 85 | 10 | 0 | 47 | 17 | 38 | 0 | 0 | 120 | 240 | 300 | 188 | 8 | 100 | 33 | 55 | 5 | 5 | 0 | 0 | 0 | 22 | 11 | 8 | 20 | 150 | 104 | 94 | 20 | 0.1 | 57 | 58 | 50 | 50 | 100 | 249 | 63 | 50 | 46 | 115 | 0 | 46 | 0 | 240 | 22 | 11 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 100 | 65 | 0 | 269 | 99 | 54 | 0 | 0 | 85 |  | 927 | 0 | 0 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 0 | 173 | 33 | 16 | 0 | 0 | 60 | 0 | 0 | 61 | 0 | 0 | 0 | 8 | 0 | 5 | 16 | 0 | 0 | 71 | 199 | 0 | 0 | 163 | 0 | 155 | 0 | 89 | 0 | 176 | 0 | 270 | 17 | 0 | 0 | 53 | 0 |  | 6363.1 | 2628 | 8991.1 | 4315 | 927 | 1837 | 1110 | 270 | 36 | 346 | 150 | 0.1 | 0 | 73.84
7:00 | 35 | 44 | 100 | 110 | 300 | 6 | 0 | 280 | 275 | 0 | 0 | 450 | 290 | 0 | 15 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 20 | 17 | 18 | 17 | 19 | 25 | 28 | 33 | 25 | 0 | 40 | 30 | 0 | 100 | 0 | 8 | 205 | 0 | 140 | 0 | 0 | 16 | 0 | 51 | 10 | 0 | 47 | 17 | 13 | 0 | 0 | 120 | 240 | 300 | 198 | 8 | 100 | 30 | 56 | 5 | 5 | 0 | 0 | 0 | 22 | 11 | 8 | 20 | 146 | 151 | 70 | 20 | 0.5 | 57 | 58 | 50 | 50 | 100 | 248 | 64 | 50 | 46 | 109 | 0 | 46 | 0 | 260 | 21 | 11 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 5.08 | 100 | 17 | 0 | 268 | 99 | 54 | 0 | 1.48 | 82 |  | 928 | 0 | 0 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 0 | 173 | 25 | 16 | 0 | 0 | 60 | 0 | 0 | 61 | 0 | 0 | 0 | 8 | 0 | 5 | 16 | 0 | 0 | 71 | 199 | 0 | 0 | 158 | 0 | 149 | 0 | 88 | 0 | 171 | 0 | 270 | 17 | 0 | 0 | 53 | 0 |  | 6238.06 | 2604 | 8842.06 | 4303 | 928 | 1824 | 1022 | 270 | 30 | 312 | 146 | 7.06 | 0 | 73.85
8:00 | 35 | 45 | 100 | 110 | 300 | 6 | 0 | 335 | 275 | 0 | 0 | 450 | 290 | 0 | 15 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 20 | 17 | 18 | 17 | 19 | 25 | 28 | 33 | 25 | 14 | 40 | 30 | 0 | 100 | 0 | 8 | 218 | 0 | 140 | 0 | 0 | 16 | 0 | 51 | 10 | 0 | 47 | 17 | 4 | 0 | 0 | 120 | 240 | 300 | 197 | 8 | 100 | 30 | 56 | 5 | 5 | 0 | 0 | 0 | 22 | 11 | 8 | 20 | 146 | 150 | 70 | 20 | 1 | 57 | 58 | 50 | 50 | 100 | 251 | 63 | 50 | 46 | 117 | 0 | 46 | 0 | 260 | 21 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 100 | 17 | 0 | 269 | 99 | 91 | 0 | 2.8 | 84 |  | 929 | 0 | 0 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 0 | 173 | 23 | 16 | 0 | 0 | 60 | 0 | 0 | 61 | 0 | 0 | 0 | 8 | 0 | 5 | 16 | 0 | 0 | 70 | 199 | 0 | 0 | 166 | 0 | 157 | 0 | 88 | 0 | 172 | 0 | 320 | 17 | 0 | 0 | 53 | 0 |  | 6336.8 | 2669 | 9005.8 | 4399 | 929 | 1863 | 1043 | 269 | 30 | 312 | 146 | 14.8 | 0 | 73.85
9:00 | 35 | 94 | 100 | 110 | 300 | 6 | 0 | 344 | 320 | 0 | 0 | 450 | 290 | 0 | 15 | 0 | 0 | 0 | 80 | 0 | 0 | 10 | 80 | 0 | 46 | 0 | 20 | 17 | 31 | 17 | 19 | 25 | 28 | 25 | 25 | 49 | 40 | 30 | 0 | 100 | 0 | 18 | 219 | 0 | 140 | 0 | 0 | 16 | 0 | 44 | 50 | 0 | 46 | 17 | 3 | 0 | 0 | 120 | 360 | 300 | 199 | 8 | 100 | 30 | 56 | 5 | 5 | 0 | 0 | 0 | 22 | 11 | 15 | 20 | 148 | 148 | 40 | 20 | 1 | 57 | 58 | 50 | 50 | 100 | 250 | 61 | 79 | 46 | 110 | 0 | 46 | 10 | 255 | 15 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 14.7 | 100 | 17 | 0 | 270 | 99 | 91 | 41 | 4.3 | 84 |  | 929 | 0 | 0 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 0 | 173 | 25 | 0 | 0 | 0 | 60 | 0 | 0 | 39 | 0 | 0 | 0 | 8 | 0 | 18 | 16 | 0 | 0 | 65 | 199 | 0 | 0 | 174 | 0 | 161 | 0 | 86 | 0 | 173 | 0 | 360 | 17 | 0 | 0 | 53 | 0 |  | 6801 | 2692 | 9493 | 4619 | 929 | 1994 | 1206 | 264 | 30 | 283 | 148 | 20 | 0 | 73.85
10:00 | 35 | 94 | 100 | 110 | 300 | 6 | 0 | 335 | 344 | 0 | 0 | 450 | 260 | 0 | 15 | 0 | 0 | 0 | 80 | 0 | 0 | 24 | 48 | 0 | 64 | 0 | 20 | 17 | 37 | 17 | 19 | 25 | 27 | 25 | 25 | 47 | 40 | 30 | 0 | 100 | 0 | 25 | 231 | 0 | 150 | 0 | 0 | 16 | 0 | 17 | 50 | 0 | 47 | 17 | 2 | 0 | 0 | 110 | 360 | 300 | 183 | 8 | 100 | 30 | 56 | 5 | 35 | 0 | 0 | 3 | 18 | 11 | 0 | 20 | 150 | 148 | 38 | 20 | 1.9 | 58 | 58 | 47 | 50 | 130 | 250 | 62 | 73 | 44 | 104 | 0 | 45 | 10 | 240 | 14 | 11 | 200 | 0 | 0 | 0 | 0 | 0 | 35 | 10.2 | 100 | 20 | 1 | 268 | 98 | 91 | 55 | 3.9 | 85 |  | 929 | 0 | 0 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 0 | 173 | 26 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 13 | 3 | 0 | 65 | 199 | 0 | 0 | 200 | 0 | 169 | 0 | 90 | 0 | 195 | 0 | 360 | 17 | 0 | 19 | 55 | 0 |  | 7009 | 2739 | 9748 | 4638 | 929 | 2056 | 1480 | 264 | 30 | 185 | 150 | 16 | 0 | 73.86
11:00 | 35 | 94 | 100 | 110 | 300 | 6 | 0 | 337 | 341 | 13 | 0 | 380 | 250 | 1 | 15 | 0 | 0 | 0 | 82 | 0 | 0 | 32 | 48 | 0 | 64 | 0 | 13 | 35 | 55 | 35 | 19 | 25 | 27 | 25 | 25 | 47 | 40 | 30 | 0 | 100 | 0 | 16 | 217 | 0 | 150 | 0 | 0 | 16 | 0 | 17 | 30 | 0 | 47 | 17 | 2 | 0 | 0 | 125 | 360 | 300 | 183 | 8 | 100 | 29 | 55 | 5 | 35 | 0 | 0 | 29 | 18 | 11 | 0 | 20 | 154 | 148 | 38 | 20 | 2.1 | 55 | 58 | 47 | 50 | 130 | 250 | 49 | 72 | 44 | 103 | 18 | 46 | 10 | 250 | 0 | 11 | 200 | 0 | 0 | 0 | 0 | 0 | 47 | 9.5 | 100 | 136 | 35 | 269 | 87 | 91 | 91 | 0 | 84 |  | 930 | 0 | 0 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 0 | 173 | 26 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 12 | 0 | 0 | 8 | 0 | 22 | 13 | 3 | 0 | 65 | 199 | 0 | 0 | 190 | 0 | 193 | 0 | 90 | 0 | 186 | 0 | 360 | 17 | 0 | 86 | 89 | 0 |  | 7178.6 | 2853 | 10031.6 | 4630 | 930 | 1992 | 1835 | 264 | 30 | 185 | 154 | 11.6 | 0 | 73.86
12:00 | 35 | 94 | 100 | 110 | 300 | 6 | 0 | 328 | 320 | 13 | 0 | 380 | 290 | 22 | 15 | 12 | 0 | 0 | 59 | 0 | 23 | 50 | 48 | 0 | 63 | 0 | 6 | 35 | 56 | 55 | 16 | 25 | 28 | 25 | 25 | 47 | 40 | 30 | 0 | 100 | 0 | 16 | 218 | 0 | 147 | 0 | 0 | 16 | 2 | 17 | 10 | 0 | 40 | 16 | 2 | 0 | 0 | 125 | 320 | 300 | 196 | 8 | 100 | 32 | 55 | 5 | 35 | 0 | 0 | 52 | 18 | 11 | 0 | 20 | 164 | 144 | 80 | 20 | 2 | 56 | 58 | 47 | 50 | 130 | 251 | 61 | 71 | 44 | 112 | 18 | 46 | 10 | 250 | 7 | 11 | 200 | 15 | 0 | 0 | 50 | 0 | 68 | 4.3 | 100 | 200 | 100 | 240 | 96 | 91 | 91 | 2.1 | 84 |  | 928 | 0 | 0 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 8 | 174 | 26 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 12 | 0 | 0 | 8 | 0 | 21 | 13 | 5 | 0 | 66 | 199 | 0 | 0 | 181 | 0 | 185 | 0 | 91 | 0 | 185 | 0 | 320 | 53 | 0 | 120 | 88 | 0 |  | 7490.4 | 2874 | 10364.4 | 4551 | 928 | 1930 | 2301 | 265 | 30 | 187 | 164 | 8.4 | 0 | 73.86
13:00 | 35 | 94 | 100 | 110 | 300 | 6 | 0 | 350 | 320 | 13 | 0 | 400 | 280 | 24 | 15 | 11 | 0 | 0 | 87 | 0 | 23 | 50 | 48 | 0 | 62 | 0 | 0 | 35 | 56 | 55 | 14 | 25 | 28 | 25 | 25 | 47 | 40 | 30 | 0 | 100 | 0 | 24 | 220 | 0 | 142 | 0 | 0 | 16 | 50 | 16 | 10 | 0 | 43 | 17 | 7 | 0 | 0 | 125 | 320 | 330 | 202 | 8 | 100 | 32 | 55 | 5 | 35 | 0 | 0 | 52 | 18 | 5 | 0 | 20 | 154 | 144 | 86 | 20 | 1.8 | 54 | 58 | 50 | 50 | 130 | 250 | 59 | 68 | 44 | 110 | 18 | 45 | 10 | 270 | 8 | 11 | 200 | 15 | 0 | 0 | 60 | 0 | 70 | 18.5 | 100 | 200 | 103 | 269 | 96 | 91 | 91 | 5 | 84 |  | 929 | 0 | 0 | 0 | 36 | 120 | 0 | 0 | 0 | 0 | 32 | 174 | 26 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 18 | 0 | 0 | 16 | 0 | 21 | 13 | 5 | 0 | 65 | 199 | 0 | 0 | 195 | 0 | 199 | 0 | 93 | 0 | 196 | 0 | 350 | 53 | 0 | 15 | 87 | 0 |  | 7703.3 | 2892 | 10595.3 | 4684 | 929 | 2006 | 2269 | 264 | 30 | 234 | 154 | 25.3 | 0 | 73.87
14:00 | 35 | 94 | 100 | 110 | 300 | 6 | 0 | 340 | 320 | 13 | 0 | 400 | 280 | 38 | 40 | 20 | 0 | 0 | 82 | 0 | 23 | 66 | 95 | 0 | 61 | 0 | 0 | 35 | 56 | 55 | 16 | 25 | 27 | 25 | 25 | 47 | 40 | 30 | 0 | 100 | 0 | 24 | 218 | 0 | 146 | 0 | 0 | 16 | 50 | 16 | 10 | 0 | 46 | 17 | 2 | 0 | 0 | 125 | 320 | 330 | 194 | 8 | 95 | 29 | 53 | 5 | 35 | 0 | 0 | 52 | 18 | 5 | 0 | 20 | 154 | 141 | 95 | 20 | 1.3 | 55 | 58 | 47 | 50 | 130 | 251 | 60 | 71 | 44 | 112 | 18 | 45 | 10 | 290 | 8 | 11 | 200 | 15 | 0 | 0 | 77 | 0 | 80 | 16.7 | 100 | 200 | 128 | 270 | 86 | 108 | 109 | 4.6 | 84 |  | 929 | 0 | 0 | 0 | 49 | 120 | 0 | 0 | 0 | 0 | 40 | 174 | 27 | 16 | 0 | 0 | 50 | 0 | 0 | 0 | 50 | 16 | 0 | 50 | 0 | 21 | 13 | 0 | 0 | 63 | 199 | 0 | 0 | 192 | 0 | 197 | 0 | 90 | 0 | 200 | 0 | 350 | 105 | 0 | 0 | 88 | 0 |  | 7887.6 | 3039 | 10926.6 | 4653 | 929 | 2017 | 2578 | 262 | 30 | 281 | 154 | 22.6 | 0 | 73.87
15:00 | 35 | 94 | 100 | 110 | 300 | 6 | 0 | 359 | 335 | 13 | 0 | 420 | 280 | 50 | 60 | 30 | 0 | 0 | 90 | 0 | 23 | 66 | 94 | 0 | 61 | 0 | 0 | 35 | 56 | 55 | 16 | 25 | 28 | 33 | 25 | 47 | 40 | 30 | 0 | 100 | 0 | 24 | 218 | 0 | 135 | 0 | 0 | 16 | 50 | 16 | 10 | 1 | 46 | 17 | 2 | 0 | 0 | 125 | 355 | 330 | 205 | 8 | 95 | 36 | 53 | 5 | 35 | 0 | 0 | 52 | 20 | 11 | 21 | 20 | 158 | 140 | 95 | 20 | 0.9 | 56 | 57 | 52 | 50 | 130 | 252 | 58 | 71 | 44 | 118 | 18 | 42 | 0 | 285 | 8 | 11 | 200 | 15 | 0 | 0 | 80 | 0 | 101 | 13.3 | 100 | 200 | 141 | 282 | 86 | 91 | 109 | 3.5 | 82 |  | 930 | 0 | 0 | 0 | 49 | 120 | 0 | 0 | 0 | 0 | 40 | 172 | 24 | 16 | 0 | 0 | 50 | 0 | 0 | 0 | 50 | 16 | 0 | 50 | 0 | 21 | 16 | 5 | 0 | 63 | 199 | 0 | 0 | 196 | 0 | 200 | 0 | 90 | 0 | 193 | 0 | 380 | 105 | 0 | 0 | 87 | 0 |  | 8091.7 | 3072 | 11163.7 | 4779 | 930 | 2069 | 2638 | 262 | 30 | 280 | 158 | 17.7 | 0 | 73.87
16:00 | 35 | 94 | 101 | 110 | 300 | 5 | 0 | 336 | 336 | 13 | 0 | 420 | 290 | 50 | 65 | 55 | 0 | 0 | 92 | 0 | 23 | 66 | 94 | 0 | 61 | 0 | 0 | 35 | 56 | 55 | 16 | 25 | 28 | 33 | 17 | 47 | 40 | 34 | 0 | 100 | 0 | 24 | 219 | 0 | 143 | 0 | 0 | 16 | 49 | 16 | 10 | 66 | 47 | 14 | 7 | 0 | 0 | 125 | 360 | 330 | 188 | 8 | 100 | 36 | 53 | 5 | 35 | 0 | 0 | 52 | 20 | 11 | 24 | 20 | 144 | 141 | 94 | 20 | 0.5 | 56 | 57 | 51 | 50 | 130 | 247 | 57 | 71 | 44 | 103 | 18 | 44 | 0 | 260 | 8 | 11 | 200 | 75 | 0 | 0 | 80 | 0 | 101 | 8.4 | 90 | 200 | 135 | 285 | 86 | 108 | 105 | 2.3 | 82 |  | 929 | 0 | 0 | 0 | 83 | 120 | 0 | 0 | 0 | 11 | 40 | 173 | 23 | 16 | 0 | 0 | 50 | 0 | 0 | 0 | 50 | 16 | 0 | 49 | 0 | 21 | 16 | 8 | 0 | 63 | 200 | 0 | 0 | 195 | 0 | 0 | 0 | 90 | 0 | 188 | 0 | 380 | 105 | 0 | 0 | 88 | 20 |  | 8174.2 | 2934 | 11108.2 | 4534 | 929 | 2049 | 2854 | 263 | 34 | 290 | 144 | 11.2 | 0 | 73.88
17:00 | 35 | 94 | 100 | 110 | 300 | 6 | 0 | 330 | 336 | 13 | 0 | 420 | 290 | 15 | 30 | 55 | 0 | 0 | 92 | 0 | 7 | 24 | 70 | 10 | 61 | 0 | 0 | 35 | 56 | 55 | 16 | 25 | 28 | 33 | 25 | 47 | 40 | 34 | 0 | 100 | 0 | 24 | 219 | 0 | 145 | 0 | 0 | 16 | 49 | 16 | 10 | 88 | 47 | 14 | 2 | 0 | 0 | 125 | 360 | 330 | 191 | 8 | 100 | 36 | 53 | 5 | 10 | 0 | 0 | 52 | 21 | 11 | 25 | 20 | 142 | 142 | 93 | 20 | 0.5 | 56 | 57 | 11 | 10 | 130 | 250 | 75 | 73 | 44 | 106 | 18 | 44 | 10 | 280 | 16 | 11 | 10 | 95 | 0 | 0 | 50 | 0 | 101 | 3.3 | 90 | 200 | 90 | 285 | 95 | 108 | 105 | 0.6 | 82 |  | 930 | 0 | 0 | 0 | 51 | 120 | 0 | 0 | 3 | 26 | 40 | 173 | 21 | 16 | 0 | 0 | 50 | 0 | 0 | 0 | 50 | 16 | 0 | 16 | 0 | 21 | 16 | 8 | 0 | 63 | 199 | 0 | 0 | 195 | 0 | 0 | 0 | 94 | 0 | 191 | 0 | 380 | 105 | 0 | 75 | 56 | 16 |  | 7772.4 | 2931 | 10703.4 | 4578 | 930 | 1974 | 2495 | 262 | 34 | 284 | 142 | 4.4 | 0 | 73.88
18:00 | 35 | 93 | 100 | 110 | 300 | 6 | 0 | 330 | 255 | 13 | 0 | 340 | 290 | 7 | 30 | 55 | 0 | 0 | 34 | 0 | 7 | 24 | 70 | 10 | 61 | 0 | 0 | 35 | 56 | 55 | 19 | 25 | 28 | 33 | 25 | 47 | 40 | 34 | 0 | 100 | 0 | 24 | 219 | 0 | 142 | 0 | 0 | 24 | 49 | 17 | 10 | 89 | 47 | 15 | 16 | 0 | 0 | 125 | 275 | 270 | 185 | 8 | 96 | 36 | 54 | 5 | 10 | 0 | 0 | 52 | 21 | 11 | 25 | 20 | 160 | 141 | 93 | 20 | 0 | 56 | 57 | 11 | 10 | 130 | 246 | 61 | 10 | 10 | 104 | 18 | 43 | 10 | 255 | 16 | 11 | 10 | 95 | 0 | 0 | 50 | 0 | 101 | 0.6 | 100 | 200 | 70 | 200 | 86 | 109 | 105 | 0 | 85 |  | 930 | 16 | 0 | 0 | 49 | 120 | 0 | 0 | 27 | 40 | 40 | 173 | 22 | 16 | 0 | 0 | 50 | 0 | 0 | 0 | 50 | 16 | 0 | 16 | 0 | 22 | 16 | 8 | 0 | 64 | 199 | 0 | 0 | 196 | 0 | 35 | 0 | 52 | 0 | 200 | 0 | 270 | 105 | 0 | 107 | 53 | 36 |  | 7185.6 | 2928 | 10113.6 | 4304 | 930 | 1555 | 2528 | 263 | 34 | 339 | 160 | 0.6 | 0 | 73.88
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 35 | 94 | 100 | 110 | 300 | 6 | 0 | 348 | 255 | 55 | 0 | 340 | 295 | 27 | 30 | 55 | 0 | 0 | 34 | 0 | 19 | 58 | 100 | 32 | 62 | 0 | 3 | 35 | 56 | 55 | 19 | 25 | 28 | 33 | 25 | 47 | 40 | 35 | 0 | 100 | 0 | 25 | 219 | 0 | 142 | 0 | 0 | 24 | 78 | 85 | 66 | 89 | 46 | 15 | 29 | 0 | 0 | 125 | 260 | 270 | 211 | 8 | 100 | 36 | 54 | 5 | 10 | 0 | 30 | 52 | 21 | 11 | 25 | 20 | 180 | 143 | 93 | 20 | 0 | 56 | 57 | 11 | 21 | 100 | 249 | 59 | 50 | 10 | 115 | 18 | 43 | 10 | 290 | 16 | 11 | 10 | 137 | 0 | 0 | 72 | 0 | 115 | 0 | 100 | 200 | 81 | 201 | 86 | 109 | 105 | 0 | 97 |  | 930 | 16 | 0 | 0 | 49 | 125 | 0 | 0 | 37 | 60 | 40 | 173 | 32 | 110 | 0 | 0 | 50 | 50 | 6 | 90 | 50 | 16 | 35 | 50 | 27 | 22 | 16 | 11 | 0 | 64 | 199 | 16 | 18 | 195 | 0 | 117 | 0 | 58 | 30 | 200 | 0 | 270 | 105 | 0 | 107 | 54 | 38 |  | 7777 | 3466 | 11243 | 4437 | 930 | 1640 | 2985 | 263 | 35 | 773 | 180 | 0 | 0 | 73.89
19:30 | 35 | 94 | 100 | 110 | 300 | 6 | 0 | 327 | 300 | 80 | 0 | 420 | 230 | 100 | 40 | 55 | 0 | 0 | 52 | 0 | 50 | 84 | 140 | 56 | 63 | 0 | 23 | 35 | 56 | 55 | 19 | 25 | 28 | 33 | 25 | 47 | 40 | 35 | 0 | 100 | 0 | 25 | 218 | 0 | 140 | 0 | 0 | 24 | 82 | 81 | 76 | 90 | 46 | 15 | 29 | 0 | 0 | 125 | 320 | 320 | 215 | 8 | 97 | 36 | 53 | 5 | 20 | 0 | 50 | 52 | 21 | 11 | 25 | 20 | 174 | 147 | 93 | 20 | 0 | 56 | 58 | 49 | 50 | 163 | 251 | 40 | 74 | 40 | 118 | 18 | 43 | 10 | 240 | 22 | 11 | 10 | 138 | 0 | 0 | 151 | 0 | 140 | 0 | 100 | 200 | 150 | 297 | 85 | 109 | 105 | 0 | 98 |  | 929 | 16 | 0 | 0 | 115 | 165 | 0 | 0 | 39 | 63 | 40 | 173 | 31 | 110 | 10 | 0 | 55 | 50 | 17 | 95 | 50 | 43 | 35 | 50 | 35 | 22 | 16 | 11 | 0 | 64 | 199 | 16 | 17 | 203 | 0 | 170 | 0 | 97 | 96 | 200 | 0 | 315 | 105 | 0 | 107 | 78 | 44 |  | 8627 | 3881 | 12508 | 4701 | 929 | 1991 | 3504 | 263 | 35 | 911 | 174 | 0 | 0 | 73.89
20:00 | 35 | 94 | 100 | 110 | 300 | 6 | 0 | 335 | 300 | 110 | 0 | 340 | 235 | 80 | 65 | 55 | 0 | 0 | 52 | 0 | 65 | 101 | 145 | 68 | 63 | 0 | 48 | 35 | 56 | 55 | 19 | 25 | 28 | 33 | 25 | 47 | 40 | 36 | 0 | 100 | 0 | 25 | 217 | 0 | 120 | 0 | 0 | 24 | 84 | 83 | 78 | 90 | 47 | 15 | 30 | 0 | 0 | 125 | 320 | 320 | 215 | 8 | 100 | 36 | 54 | 5 | 20 | 0 | 50 | 52 | 21 | 11 | 25 | 20 | 176 | 146 | 92 | 20 | 0 | 56 | 58 | 52 | 50 | 130 | 254 | 43 | 75 | 44 | 104 | 18 | 43 | 10 | 240 | 22 | 11 | 0 | 195 | 0 | 0 | 144 | 0 | 149 | 0 | 100 | 200 | 136 | 280 | 85 | 109 | 105 | 0 | 98 |  | 930 | 26 | 0 | 0 | 99 | 195 | 0 | 0 | 31 | 62 | 40 | 173 | 34 | 110 | 24 | 0 | 55 | 50 | 32 | 95 | 50 | 50 | 39 | 50 | 36 | 22 | 16 | 11 | 0 | 64 | 199 | 16 | 17 | 199 | 0 | 174 | 0 | 95 | 95 | 198 | 0 | 270 | 105 | 0 | 107 | 90 | 45 |  | 8646 | 3904 | 12550 | 4663 | 930 | 1844 | 3653 | 263 | 36 | 985 | 176 | 0 | 0 | 73.89
21:00 | 35 | 94 | 100 | 110 | 300 | 6 | 0 | 330 | 344 | 110 | 0 | 430 | 285 | 100 | 97 | 55 | 0 | 0 | 52 | 0 | 98 | 100 | 145 | 50 | 56 | 0 | 49 | 35 | 56 | 55 | 19 | 25 | 32 | 33 | 25 | 48 | 40 | 36 | 0 | 100 | 0 | 25 | 217 | 0 | 140 | 0 | 0 | 24 | 84 | 83 | 98 | 90 | 47 | 18 | 33 | 0 | 0 | 125 | 320 | 320 | 214 | 8 | 100 | 36 | 55 | 5 | 35 | 0 | 50 | 52 | 22 | 11 | 25 | 20 | 186 | 145 | 91 | 20 | 0 | 56 | 58 | 53 | 50 | 130 | 250 | 61 | 75 | 45 | 104 | 18 | 45 | 10 | 255 | 22 | 11 | 0 | 216 | 0 | 0 | 150 | 0 | 149 | 0 | 100 | 200 | 150 | 280 | 86 | 109 | 105 | 0 | 75 |  | 929 | 48 | 0 | 0 | 99 | 233 | 0 | 0 | 36 | 58 | 40 | 173 | 33 | 110 | 12 | 0 | 55 | 50 | 32 | 91 | 50 | 50 | 47 | 50 | 35 | 22 | 16 | 11 | 0 | 65 | 199 | 17 | 17 | 168 | 0 | 154 | 0 | 97 | 96 | 186 | 0 | 300 | 105 | 0 | 107 | 90 | 0 |  | 9012 | 3881 | 12893 | 4635 | 929 | 2047 | 3758 | 264 | 36 | 1038 | 186 | 0 | 0 | 73.89
22:00 | 35 | 94 | 100 | 110 | 300 | 6 | 0 | 328 | 353 | 110 | 0 | 430 | 255 | 100 | 100 | 55 | 0 | 0 | 82 | 0 | 100 | 100 | 145 | 10 | 61 | 0 | 48 | 35 | 56 | 55 | 19 | 25 | 32 | 33 | 17 | 43 | 40 | 36 | 0 | 100 | 0 | 25 | 218 | 0 | 140 | 0 | 0 | 24 | 84 | 83 | 98 | 90 | 47 | 18 | 36 | 0 | 0 | 125 | 360 | 320 | 215 | 8 | 100 | 36 | 56 | 5 | 35 | 0 | 50 | 52 | 22 | 11 | 25 | 20 | 182 | 149 | 92 | 20 | 0 | 56 | 58 | 53 | 50 | 130 | 250 | 61 | 75 | 45 | 104 | 18 | 46 | 10 | 260 | 22 | 11 | 0 | 155 | 0 | 0 | 150 | 0 | 149 | 0 | 100 | 196 | 150 | 280 | 86 | 109 | 105 | 0 | 85 |  | 930 | 48 | 0 | 0 | 99 | 236 | 0 | 0 | 36 | 56 | 40 | 173 | 33 | 110 | 24 | 0 | 55 | 50 | 33 | 92 | 50 | 50 | 44 | 50 | 35 | 22 | 16 | 11 | 0 | 65 | 199 | 17 | 17 | 155 | 0 | 143 | 0 | 97 | 95 | 176 | 0 | 350 | 105 | 0 | 107 | 90 | 0 |  | 8973 | 3909 | 12882 | 4667 | 930 | 2116 | 3637 | 264 | 36 | 1050 | 182 | 0 | 0 | 73.89
23:00 | 35 | 94 | 100 | 110 | 300 | 6 | 0 | 330 | 351 | 110 | 0 | 400 | 293 | 100 | 64 | 55 | 0 | 0 | 87 | 0 | 50 | 100 | 144 | 10 | 64 | 0 | 19 | 35 | 56 | 55 | 19 | 25 | 32 | 33 | 25 | 40 | 40 | 35 | 0 | 100 | 0 | 25 | 217 | 0 | 140 | 0 | 0 | 16 | 84 | 83 | 89 | 94 | 47 | 18 | 36 | 0 | 0 | 125 | 360 | 320 | 215 | 8 | 100 | 36 | 55 | 5 | 35 | 0 | 0 | 52 | 22 | 11 | 25 | 20 | 162 | 147 | 85 | 20 | 0 | 56 | 58 | 53 | 50 | 130 | 249 | 61 | 76 | 45 | 115 | 18 | 45 | 10 | 250 | 22 | 11 | 0 | 132 | 0 | 0 | 150 | 0 | 149 | 0 | 100 | 200 | 150 | 281 | 95 | 109 | 105 | 0 | 85 |  | 929 | 28 | 0 | 0 | 83 | 235 | 0 | 0 | 36 | 58 | 40 | 173 | 32 | 110 | 12 | 0 | 55 | 50 | 33 | 92 | 50 | 50 | 43 | 50 | 35 | 22 | 16 | 11 | 0 | 65 | 199 | 17 | 17 | 157 | 0 | 148 | 0 | 97 | 94 | 176 | 0 | 350 | 105 | 0 | 107 | 108 | 0 |  | 8774 | 3883 | 12657 | 4697 | 929 | 2072 | 3531 | 264 | 35 | 967 | 162 | 0 | 0 | 73.9
24:00 | 35 | 94 | 100 | 110 | 300 | 6 | 0 | 337 | 354 | 110 | 0 | 400 | 285 | 100 | 60 | 55 | 0 | 0 | 87 | 0 | 48 | 100 | 147 | 10 | 65 | 0 | 13 | 35 | 56 | 55 | 19 | 25 | 27 | 33 | 25 | 40 | 40 | 35 | 0 | 100 | 0 | 25 | 217 | 0 | 139 | 0 | 0 | 16 | 84 | 83 | 89 | 90 | 47 | 18 | 36 | 0 | 0 | 125 | 360 | 320 | 215 | 8 | 100 | 36 | 55 | 5 | 35 | 0 | 0 | 52 | 22 | 11 | 25 | 20 | 172 | 149 | 61 | 20 | 0 | 56 | 58 | 50 | 50 | 130 | 248 | 60 | 76 | 45 | 112 | 18 | 43 | 10 | 260 | 22 | 11 | 0 | 95 | 0 | 0 | 150 | 0 | 149 | 0 | 100 | 197 | 150 | 281 | 95 | 109 | 105 | 0 | 117 |  | 930 | 32 | 0 | 0 | 83 | 236 | 0 | 0 | 36 | 53 | 40 | 173 | 35 | 110 | 12 | 0 | 55 | 50 | 33 | 85 | 50 | 50 | 27 | 51 | 35 | 22 | 16 | 11 | 0 | 65 | 199 | 17 | 17 | 164 | 0 | 155 | 0 | 95 | 94 | 175 | 0 | 350 | 105 | 0 | 107 | 107 | 0 |  | 8738 | 3875 | 12613 | 4708 | 930 | 2081 | 3476 | 264 | 35 | 947 | 172 | 0 | 0 | 73.9
KWH | 674000 | 2420400 | 2395000 | 2756250 | 7200763 | 149500 | 0 | 8128510 | 7664000 | 630700 | 0 | 9828500 | 6619316 | 753600 | 947328 | 586288 | 0 | 0 | 1704000 | 0 | 574080 | 978768 | 2390400 | 260656 | 1226880 | 0 | 413328 | 775440 | 1114328 | 1061012 | 400176 | 600000 | 634320 | 694800 | 571200 | 922584 | 997923 | 712380 | 0 | 2500000 | 0 | 497720 | 5140044 | 0 | 3353944 | 0 | 0 | 435840 | 807848 | 1295934 | 892560 | 1195200 | 1112640 | 386544 | 464160 | 0 | 0 | 2945292 | 8031000 | 7784000 | 4722000 | 200727 | 2031680 | 765288 | 1317600 | 120000 | 586288 | 0 | 160480 | 935040 | 494820 | 242460 | 407100 | 514990 | 3837120 | 3262720 | 2033280 | 448776 | 14600 | 1348000 | 1362840 | 1111200 | 1091000 | 3227506 | 5694000 | 1391520 | 1684320 | 966960 | 2643850 | 342000 | 342000 | 193680 | 6347000 | 392736 | 255840 | 1610880 | 1287160 | 0 | 0 | 2217600 | 0 | 1949760 | 125415 | 2394240 | 3790560 | 2373600 | 6465000 | 2222400 | 2243052 | 1983840 | 29748 | 1977160 |  | 22292364 | 188400 | 0 | 0 | 1152000 | 3515520 | 0 | 0 | 336480 | 594304 | 583500 | 4237315 | 712184 | 1352160 | 89055 | 0 | 1335000 | 287232 | 150364 | 1146012 | 655000 | 354797 | 198900 | 2710400 | 216400 | 465840 | 369180 | 102222 | 0 | 1625891 | 4843600 | 120000 | 162000 | 4644318 | 0 | 3894227 | 0 | 2132343 | 504960 | 4703082 | 0 | 8296727 | 1919520 | 0 | 1573248 | 1890864 | 305280 |  | 184788992 | 79660689 | 264449681 | 111019950 | 22292364 | 47270715 | 61018569 | 6469491 | 712380 | 11659329 | 3837120 | 169763 | 0
Fuel Cost | 579640 | 2081544 | 2059700 | 2370375 | 4608488.32 | 121095 | 0 | 4958391.1 | 4675040 | 6061027 | 0 | 6585095 | 100547410.04 | 4732608 | 6328151.04 | 3582219.68 | 0 | 0 | 1891440 | 0 | 3588000 | 6450081.12 | 23115168 | 1660378.72 | 7349011.2 | 0 | 2756897.76 | 5528887.2 | 6964550 | 6652545.24 | 300132 | 450000 | 0 | 0 | 0 | 8727644.64 | 1147611.45 | 0 | 0 | 2750000 | 0 | 4713408.4 | 3392429.04 | 0 | 3857035.6 | 0 | 0 | 3831033.6 | 8700522.96 | 12609437.82 | 5524946.4 | 7720992 | 7276665.6 | 328562.4 | 0 | 0 | 0 | 2680215.72 | 4979220 | 5370960 | 3305400 | 138501.63 | 1950412.8 | 512742.96 | 1133136 | 110400 | 480756.16 | 0 | 1739603.2 | 6937996.8 | 381011.4 | 181845 | 313467 | 386242.5 | 26245900.8 | 2447040 | 18685843.2 | 345557.52 | 0 | 1401920 | 1417353.6 | 1066752 | 981900 | 2517454.68 | 3985800 | 1586332.8 | 1802222.4 | 1063656 | 3013989 | 437760 | 318060 | 180122.4 | 4062080 | 294552 | 194438.4 | 27916550.4 | 9344781.6 | 0 | 0 | 15855840 | 0 | 0 | 0 | 0 | 35403830.4 | 22169424 | 5624550 | 0 | 0 | 0 | 0 | 0 |  | 113691056.4 | 5491860 | 0 | 0 | 9550080 | 56529561.6 | 0 | 0 | 3788764.8 | 7000901.12 | 4597980 | 2923747.35 | 705062.16 | 10005984 | 2999372.4 | 0 | 1401750 | 3288806.4 | 1611902.08 | 10268267.52 | 5665750 | 3157693.3 | 2118285 | 26887168 | 2547028 | 512424 | 347029.2 | 77382.054 | 0 | 9869158.37 | 18696296 | 3867600 | 4336740 | 3158136.24 | 0 | 2725958.9 | 0 | 0 | 8750956.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 505543787.7 | 326572701.694 | 832116489.394 | 81873134.154 | 113691056.4 | 26800786.63 | 404926336.14 | 28565454.37 | 0 | 150013820.9 | 26245900.8 | 0 | 0
Yesterday Day Peak | 35 | 94 | 100 | 110 | 300 | 6 | 0 | 328 | 320 | 13 | 0 | 380 | 290 | 22 | 15 | 12 | 0 | 0 | 59 | 0 | 23 | 50 | 48 | 0 | 63 | 0 | 6 | 35 | 56 | 55 | 16 | 25 | 28 | 25 | 25 | 47 | 40 | 30 | 0 | 100 | 0 | 16 | 218 | 0 | 147 | 0 | 0 | 16 | 2 | 17 | 10 | 0 | 40 | 16 | 2 | 0 | 0 | 125 | 320 | 300 | 196 | 8 | 100 | 32 | 55 | 5 | 35 | 0 | 0 | 52 | 18 | 11 | 0 | 20 | 164 | 144 | 80 | 20 | 2 | 56 | 58 | 47 | 50 | 130 | 251 | 61 | 71 | 44 | 112 | 18 | 46 | 10 | 250 | 7 | 11 | 200 | 15 | 0 | 0 | 50 | 0 | 68 | 4.3 | 100 | 200 | 100 | 240 | 96 | 91 | 91 | 2.1 | 84 |  | 928 | 0 | 0 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 8 | 174 | 26 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 12 | 0 | 0 | 8 | 0 | 21 | 13 | 5 | 0 | 66 | 199 | 0 | 0 | 181 | 0 | 185 | 0 | 91 | 0 | 185 | 0 | 320 | 53 | 0 | 120 | 88 | 0 |  | 10364.4 | DayPeak
Yesterday Evening Peak | 35 | 94 | 100 | 110 | 300 | 6 | 0 | 330 | 344 | 110 | 0 | 430 | 285 | 100 | 97 | 55 | 0 | 0 | 52 | 0 | 98 | 100 | 145 | 50 | 56 | 0 | 49 | 35 | 56 | 55 | 19 | 25 | 32 | 33 | 25 | 48 | 40 | 36 | 0 | 100 | 0 | 25 | 217 | 0 | 140 | 0 | 0 | 24 | 84 | 83 | 98 | 90 | 47 | 18 | 33 | 0 | 0 | 125 | 320 | 320 | 214 | 8 | 100 | 36 | 55 | 5 | 35 | 0 | 50 | 52 | 22 | 11 | 25 | 20 | 186 | 145 | 91 | 20 | 0 | 56 | 58 | 53 | 50 | 130 | 250 | 61 | 75 | 45 | 104 | 18 | 45 | 10 | 255 | 22 | 11 | 0 | 216 | 0 | 0 | 150 | 0 | 149 | 0 | 100 | 200 | 150 | 280 | 86 | 109 | 105 | 0 | 75 |  | 929 | 48 | 0 | 0 | 99 | 233 | 0 | 0 | 36 | 58 | 40 | 173 | 33 | 110 | 12 | 0 | 55 | 50 | 32 | 91 | 50 | 50 | 47 | 50 | 35 | 22 | 16 | 11 | 0 | 65 | 199 | 17 | 17 | 168 | 0 | 154 | 0 | 97 | 96 | 186 | 0 | 300 | 105 | 0 | 107 | 90 | 0 |  | 12893 | EvPeak
Forecast for Evening | 35 | 134 | 100 | 110 | 360 | 108 | 0 | 412 | 360 | 110 | 0 | 450 | 335 | 100 | 100 | 55 | 0 | 0 | 100 | 0 | 100 | 102 | 149 | 100 | 65 | 0 | 49 | 35 | 55 | 55 | 19 | 25 | 33 | 33 | 33 | 48 | 40 | 36 | 0 | 100 | 0 | 25 | 225 |  | 140 | 0 | 0 | 16 | 74 | 85 | 100 | 100 | 45 | 17 | 20 | 0 | 0 | 120 | 360 | 360 | 221 | 8 | 100 | 33 | 55 | 5 | 35 | 0 | 50 | 52 | 22 | 11 | 33 | 20 | 189 | 150 | 95 | 20 | 0 | 57 | 58 | 50 | 44 | 163 | 330 | 66 | 86 | 46 | 130 | 18 | 50 | 10 | 341 | 25 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 133 | 269 | 100 | 100 | 105 |  | 84 |  | 948 | 32 | 0 | 0 | 115 | 225 | 0 | 0 | 33 | 80 | 40 | 173 | 39 | 110 | 20 | 0 | 60 | 50 | 35 | 95 | 50 | 50 | 47 | 52 | 35 | 22 | 16 | 11 | 0 | 70 | 199 | 16 | 18 | 200 | 0 | 200 | 0 | 90 | 100 | 220 | 0 | 414 | 105 | 200 | 100 | 102 | 0
Forecast for Day | 35 | 94 | 100 | 110 | 360 | 108 | 0 | 412 | 360 | 110 | 0 | 450 | 335 | 100 | 100 | 55 | 0 | 0 | 100 | 0 | 100 | 102 | 149 | 100 | 65 | 0 | 49 | 35 | 55 | 55 | 19 | 25 | 33 | 33 | 33 | 48 | 40 | 36 | 0 | 100 | 0 | 25 |  | 225 | 140 | 0 | 0 | 16 | 74 | 85 | 100 | 100 | 45 | 17 | 10 | 0 | 0 | 120 | 360 | 360 | 221 | 8 | 100 | 33 | 55 | 5 | 35 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 152 | 150 | 70 | 20 | 2 | 57 | 58 | 50 | 44 | 163 | 330 | 66 | 86 | 46 | 130 | 18 | 50 | 10 | 341 | 25 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 20 | 100 | 200 | 133 | 269 | 100 | 100 | 105 | 3 | 84 |  | 948 | 0 | 0 | 0 | 115 | 225 | 0 | 0 | 33 | 50 | 40 | 173 | 39 | 110 | 0 | 0 | 60 | 50 | 35 | 95 | 50 | 50 | 47 | 52 | 35 | 22 | 16 | 11 | 0 | 70 | 199 | 16 | 18 | 200 | 0 | 200 | 0 | 90 | 100 | 220 | 0 | 414 | 105 | 0 | 100 | 102 | 0
Generation at 08:00(Today) | 35 | 95 | 100 | 115 | 250 | 6 | 0 | 349 | 278 | 0 | 0 | 350 | 285 | 7 | 2 | 0 | 0 | 0 | 60 | 0 | 0 | 7 | 15 | 0 | 24 | 0 | 13 | 35 | 36 | 17 | 19 | 25 | 31 | 0 | 25 | 24 | 40 | 36 | 0 | 100 | 0 | 8 | 0 | 229 | 90 | 0 | 0 | 16 | 0 | 17 | 10 | 20 | 47 | 18 | 6 | 0 | 0 | 80 | 270 | 270 | 190 | 8 | 100 | 30 | 20 | 5 | 10 | 0 | 0 | 25 | 22 | 11 | 25 | 20 | 136 | 151 | 8 | 20 | 0 | 59 | 58 | 11 | 10 | 100 | 250 | 63 | 10 | 45 | 113 | 19 | 43 | 10 | 250 | 16 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 15 | 10.5 | 100 | 88 | 0 | 200 | 45 | 80 | 70 | 2.8 | 116 | 0 | 937 | 0 | 0 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 16 | 173 | 20 | 16 | 0 | 0 | 60 | 0 | 0 | 16 | 12 | 0 | 0 | 8 | 0 | 5 | 3 | 8 | 0 | 66 | 199 | 0 | 0 | 171 | 0 | 161 | 0 | 95 | 0 | 175 | 0 | 350 | 35 | 0 | 17 | 53 | 0 | 0
199
| Minimum Generation |  | 8842.06 | 7:00
| Highest Generation |  | 12893 | 21:00
| Day Peak Generation |  | 10364.4 | 12:00
| Evening Peak Generation |  | 12893 | 21:00
| HVDC Max Flow |  | 930 | 11:00
| HVDC EvPeak Flow |  | 929 | 21:00
| Load factor L.F |  | 85.46%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2019-05-30
Till now the maximum generation is : - |  |  | 12539 MW | 21:00 | Hrs on | 2019-05-21
The Summary of Yesterday's |  | 2019-05-29 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 10364.4 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 8599.5 | MW
Evening Peak Generation : |  | 12893 | MW Hour : | 21:00 | Available Max Generation : |  | 15029 | MW
E.P. Demand (at gen end) : |  | 12893 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 13000 | MW
Maximum Generation : |  | 12893 | MW Hour : | 21:00 | Reserve(Generation end) |  | 2029 | MW
Total Gen. (MKWH) : |  | 264.4497 | System Load Factor : | 85.46% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -320 | MW at | 21:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2019-05-30
Actual : | 73.9 | Ft.(MSL) , | Rule curve : | 76.4 | Ft.( MSL )
Gas Consumed : | Total = | 1386.68 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 108673920.784
|  | Coal : | 28565454.37 | Oil : | 554940157.04 | Total : | 692179532.194
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4539.5032 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1547.9712 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1387.6951 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1254.1709 |  |  | 0 | 0%
Comilla Area | 0 | 0:00 | 1133.2264 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 914.4845 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 505.8157 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 235.3091 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 705.3222 |  |  | 0 | 0%
Total | 0 |  | 12223.4981 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1 | 7) Baghabari 100 MW
|  |  |  | 2) Khulna ST 110 MW | 8) Ghorasal Unit-1 ST
|  |  |  | 3) Sikalbaha ST 60 MW | 9) Haripur GT-1 & 2
4) Bheramara 410 MW.
5) Siddhirganj ST
6) Ashuganj #3,4
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Naogaon 132/33 kV T3 & associated 33 kV bus were under shut down from 08:15 to 08:58 for C/M. |  |  |  |  | About 25 MW Power interruption occurred under Naogaon S/S area
from 08:15 to 08:58.
b) Kishoreganj 132/33 kV T2 transformer was under shut down from 09:27 to 11:40 for C/M.
c) Kishoreganj 132/33 kV T1 transformer was under shut down from 11:58 to 12:29 for C/M.
d) Bhulta 400/230/132 kV ATR1 transformer was switched on at 11:52.
e) Kishoreganj 132/33 kV T3 transformer was under shut down from 12:40 to 13:13 for C/M.
f) Sirajganj Unit-2 tripped at 15:33 and was synchronized at 17:14.
g) Khulna(C ) 132/33 kV T1 ,T2 & T3 transformers tripped at 21:08 from both sides due to 33 kV feeder fault |  |  |  |  | About 99 MW Power interruption occurred under Khulna(C ) S/S area
and were switched on at 21:16. |  |  |  |  | from 21:08 to 21:16.
h) Sylhet-Fenchuganj 132 kV tripped at 06:29 (30/05/2019) from both sides showing Dist Z1 A-phase and
was switched on at 06:27.
i) Mymensingh-Jamalpur 132 kV Ckt-2 was shut down at 07:28 (30/05/2019) for C/M.
j) New Tongi 132/33 kV T1 transformer was shut down at 07:48(30/05/2019) for C/M.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2019-05-29 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | PDB | 2*55 | 85 | 35 | 674000 | #1 Under maint.
| Ghorasal GT: Unit-3 |  | PDB | 1*210 | 170 | 94 | 2420400 | Gas shortage
| Ghorasal GT: Unit-4 |  | PDB | 1*210 | 180 | 100 | 2395000 | Gas shortage
| Ghorasal ST: Unit-5 |  | PDB | 1*210 | 190 | 110 | 2756250 | Gas shortage
2 | Ghorasal ST: Unit-7 |  | PDB | 1*243+1*122 | 365 | 300 | 7200763
3 | Ghorashal 78MW (MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage
4 | Ghorashal (Regent) |  | IPP | 34*3.35 | 108 | 6 | 149500 | Gas shortage
5 | Haripur GT: Unit-1, 2 |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Gas shortage
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 330 | 8128510 | FGMO
7 | Haripur NEPC 110MW |  | IPP | 8*15 | 110 | 110 | 630700
8 | Haripur Power CCPP 360MW |  | IPP | 1*235+1*125 | 360 | 344 | 7664000
9 | Meghnaghat CCPP 450MW |  | IPP | 2*150+1*150 | 450 | 430 | 9828500 | Frequency control
10 | Meghnaghat (IEL) |  | QRPP | 12*8.9 | 100 | 100 | 753600
11 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 285 | 6619316 | FGMO
12 | Madanganj 102MW |  | QRPP | 6*17 | 100 | 97 | 947328
13 | Madanganj-55 MW |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 586288
14 | Keraniganj (Powerpac) 100MW |  | QRPP | 8*13.45 | 100 | 50 | 260656 | Engine problem
15 | Narshingdi (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 400176
16 | Siddhirgonj ST 210MW |  | PDB | 1*210 | 115 | 0 | 0 | Gas shortage
17 | Siddhirgonj GT Unit-1& 2 |  | EGCB | 2*105 | 210 | 52 | 1704000 | Gas shortage
| Siddhirganj Desh |  | QRPP | 96*1.2 | 0 | 0 | 0 | Contract Expired
18 | Siddhirganj (Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 98 | 574080
19 | Siddhirganj CCPP-335 MW |  | EGCB | 1*217 | 217 | 0 | 0 | Gas shortage
0 | Pagla (DPA ) |  | QRPP | 100*0.5 | 0 | 0 | 0 | Contract Expired
20 | Gagnagar (Orion) |  | IPP | 12*8.924 | 102 | 100 | 978768
21 | Katpotti 51 MW |  | IPP | 7*7.9 | 51 | 49 | 413328
22 | Banco Energy 54MW |  | IPP | 3*18 | 54 | 35 | 775440 | Engine problem
23 | Kodda 149MW |  | BPDB-RPCL | 9*17.06 | 149 | 145 | 2390400
24 | Northern 55 MW |  | IPP | 3*19.3 | 55 | 56 | 1114328
25 | Southern 55MW |  | IPP | 3*19.3 | 55 | 55 | 1061012
26 | Bosila 108MW |  | IPP | 12*8.775+1*3.5 | 108 | 56 | 1226880 | Engine problem
27 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 57 | 1234320 | Engine problem
28 | Summit Maona |  | SIPP,REB | 4*8.73 | 33 | 33 | 694800
29 | Summit Rupganj |  | SIPP,REB | 4*8.73 | 33 | 25 | 571200 | Engine problem
30 | Gazipur (RPCL) |  | IPP | 6*8.9 | 52 | 48 | 922584
31 | Tongi GT |  | PDB | 1* 105 | 105 | 40 | 997923 | Gas shortage
32 | Summit Gazipur -2 |  | IPP | 18*17.076 | 300 | 216 | 1287160 | Low demand
33 | APR Energy , Keranigonj |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
34 | Bramhangoan 100 MW (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
35 | Aggreko Aurahati 100MW |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
36 | Summit Gazipur-1 150MW |  | IPP | 149 | 149 | 149 | 1949760
| Gazipur 100 MW |  | RPCL | 100 MW | 0 | 109 | 2243052 | on test
| Dhaka area Total |  |  |  | 5698 | 3788 | 71554022
37 | Chattogram ST-1 (Raozan) |  | PDB | 1*210 | 180 | 100 | 2500000
| Chittgong ST-2 (Raozan) |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
38 | Raozan 25 MW (RPCL) |  | IPP | 3*8.9 | 25 | 25 | 497720
39 | Teknaf Solartech 20MW |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 125415
40 | Patenga 50MW |  | IPP | 8*6.98 | 50 | 47 | 1112640
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 36 | 712380 | Low water level
42 | Sikalbaha ST 60MW |  | PDB | 1*60 | 40 | 0 | 0 | Under maint.
43 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 217 | 5140044 | FGMO
44 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 140 | 3353944 | FGMO
45 | Sikalbaha (Energis) |  | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 24 | 435840 | Engine problem
| Baraka Sikalbaha PL |  | IPP | 105 MW | 0 | 105 | 1983840
46 | Hathazari peaking |  | PDB | 11*8.9 | 98 | 84 | 807848
47 | Dohazari Peaking |  | PDB | 6*17 | 102 | 83 | 1295934
48 | Juldah (Acorn) |  | QRPP | 8*13.45 | 100 | 98 | 892560
49 | Juldah 100 MW Unit-3 |  | IPP | 0 | 100 | 100 | 2394240
50 | Barabkunda (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 386544 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 33 | 464160
51 | Chattogram ECPV 108 MW |  | IPP | 16*7 | 108 | 90 | 1195200 | Engine problem
| Kaptai Solar |  | PDB | 7.4 MW | 0 | 0 | 29748 | on test
| Anwara United |  | United Group | 300 MW | 0 | 75 | 1977160 | on test
| Chattogram area Total |  |  |  | 1681 | 1275 | 25305217
52 | Ashuganj ST: Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage
| Ashuganj ST: Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj ST: Unit- 5 |  | APSCL | 1*150 | 134 | 125 | 2945292
53 | Ashuganj CCPP 225 MW |  | APSCL | 1*142+1*75 | 221 | 214 | 4722000 | FGMO
54 | Ashuganj CCPP(North) |  | APSCL | 1*360 | 360 | 320 | 8031000
55 | Ashuganj CCPP(South) |  | APSCL | 1*360 | 360 | 320 | 7784000
56 | Ashuganj Engines TSK |  | APSCL | 14*3.968 | 45 | 36 | 765288 | Engine problem
57 | Ashuganj (Precision) 55MW |  | RPP | 15*4 | 55 | 55 | 1317600
58 | Ashuganj (United) 53MW |  | QRPP | 14*4 | 53 | 5 | 120000 | Gas shortage
59 | Ashuganj 195MW Modular |  | IPP | 20*9.73+1*16 | 195 | 8 | 200727 | Gas shortage
60 | Ashuganj (Midland) 51MW |  | IPP | 6*9.34 | 51 | 35 | 586288 | Engine problem
61 | Midland 150MW |  | IPP | 23*7.015 | 150 | 150 | 2373600
62 | B.Baria (Aggreko) 85MW |  | QRPP | 86*1.10 | 85 | 0 | 0 | Contract Expired
63 | Daudkandi Peaking 52MW |  | PDB | 6*8.92 | 52 | 50 | 160480
64 | Chandpur CCPP |  | PDB | 1*106+1*57 | 163 | 100 | 2031680
65 | Chandpur Desh 200MW |  | IPP | 0 | 200 | 200 | 3790560
66 | Feni (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 22 | 494820
67 | Feni, Mohipal (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 242460
** | Tripura |  | Imported power | 0 | 160 | 186 | 3837120
68 | Jangalia (Summit) 33MW |  | SIPP, PDB | 4*8.73 | 33 | 25 | 407100
69 | Lakdhanvi 52 MW |  | IPP | 6*8.92 | 52 | 52 | 935040
70 | Summit Cumilla 25MW |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 20 | 514990 | Engine problem
71 | Daudkandi bangla trak |  | IPP | 154*1.4 | 200 | 0 | 1610880 | Reserve
| Cumilla Area Total |  |  |  | 2891 | 1934 | 42870925
72 | Mymensingh RPCL 210MW |  | IPP | 4*35+1*70 | 202 | 145 | 3262720 | GT-3 Under maint
73 | Tangail (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 20 | 448776
74 | Jamalpur 95MW |  | IPP | 12*8.924 | 95 | 91 | 2033280
75 | Sarishabari (Solar) |  | IPP | 1*3 | 3 | 0 | 14600
76 | United Mymensingh PPL |  | IPP | 200 | 200 | 150 | 2217600 | High Voltage
77 | United Jamalpur PPL |  | IPP | 115 MW | 115 | 86 | 2222400 | Engine problem
| Mymensingh Area Total |  |  |  | 637 | 492 | 10199376
78 | Fenchugonj CCPP-1 |  | PDB | 2*32+1*33 | 70 | 56 | 1348000
79 | Fenchugonj CCPP-2 |  | PDB | 2*35+1*35 | 90 | 58 | 1362840
80 | Kushiara 163 MW CCPP GT |  | IPP | 1*109+1*54 | 163 | 130 | 3227506 | Frequency control
81 | Shajibazar 330 MW |  | PDB | 3*110 | 330 | 250 | 5694000 | Machine problem
82 | Fenchugonj (Barakatullah) 51MW |  | RPP | 19*2.90 | 51 | 53 | 1111200
83 | Fenchuganj (EPL) 44MW |  | RPP | 12*3.3+5*2 | 44 | 50 | 1091000
84 | Hobiganj 11MW |  | SIPP, REB | 4*2.90 | 11 | 11 | 255840
85 | Shahjibazar GT: Unit- 8, 9 |  | PDB | 2*35 | 66 | 61 | 1391520 | FGMO
86 | Shahjibazar 86MW |  | RPP | 32*2.90 | 86 | 75 | 1684320
87 | Shahjibazar (EPL) 50MW |  | RPP | 27*2.0 | 50 | 45 | 966960
88 | Sylhet GT 150 MW |  | PDB | 1*142 | 142 | 104 | 2643850 | Frequency control
89 | Sylhet GT 20 MW |  | PDB | 1*20 | 20 | 18 | 342000
90 | Sylhet (EPL) 50MW |  | RPP | 27*2 | 50 | 45 | 342000
91 | Shahjahanulla 25 MW |  | SIPP, REB | 3*9.34 | 25 | 22 | 392736
92 | Summit Bibiana- 2 |  | IPP | 1*222+1*119 | 341 | 255 | 6347000 | FGMO
| Bibiyana-3 285 MW |  | PDB | 285 MW | 0 | 280 | 6465000 | On test
93 | Sylhet (Desh) 10MW |  | RPP | 6*1.95 | 10 | 10 | 193680
| Sylhet Area Total |  |  |  | 1549 | 1523 | 34859452
94 | Bheramara GT-1,2,3 |  | PDB | 3*20 | 46 | 48 | 188400
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 929 | 22292364
| Khulna (KPCL-1 & 3) |  | IPP | 19*6.5 | 0 | 0 | 0 | Contract Expired
95 | Khulna (KPCL-2) |  | QRPP | 7*17 | 115 | 99 | 1152000
96 | Faridpur Peaking |  | PDB | 8*6.89 | 54 | 36 | 336480
97 | Khulna CCPP 225MW |  | NWPGCL | 1*150+1*75 | 230 | 233 | 3515520
98 | Gopalganj Peaking |  | PDB | 16*6.98 | 109 | 58 | 594304
99 | Bheramara 360 MW |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Under maint.
100 | Noapara (KZA) 40MW |  | QRPP | 5*8.5 | 40 | 40 | 583500
0 | Khulna (Aggreeco) 55MW |  | QRPP | 71*0.85 | 0 | 0 | 0 | Contract Expired
101 | Bangla Trak Noapara |  | IPP | 70*1.4 | 100 | 96 | 504960
102 | Labon Chora 105 MW |  | IPP | 6*18.445 | 105 | 105 | 1919520
103 | Madhumati Power Plant |  | IPP | 100 MW | 105 | 90 | 1890864 | Engine problem
| Khulna Area Total |  |  |  | 2314 | 1734 | 32977912
104 | Summit Barisal 110 MW |  | IPP | 7*17.076 | 110 | 110 | 1352160
105 | Barisal GT: Unit-1, 2 |  | PDB | 2*20 | 30 | 12 | 89055
106 | Bhola (Venture) 33MW |  | RPP | 1*34.50 | 33 | 33 | 712184
107 | Bhola CCPP 194MW |  | PDB | 2*63+1*68 | 194 | 173 | 4237315 | FGMO
108 | Bhola Aggreko 95MW |  | QRPP | 96*1.10 | 95 | 97 | 2132343
| Barisal Area Total |  |  |  | 462 | 425 | 8523057
109 | Baghabari GT 71MW |  | PDB | 1*71 | 71 | 55 | 1335000
| Baghabari GT 100MW |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
110 | Baghabari Peaking 50MW |  | PDB | 6*8.9 | 52 | 50 | 287232
111 | Bera Peaking |  | PDB | 9*8.29 | 71 | 32 | 150364
112 | Amnura 50MW |  | QRPP | 7*7.79 | 50 | 50 | 655000
113 | Katakhali (Northern) |  | QRPP | 6*8.9 | 50 | 50 | 354797
114 | Katakhali Peaking |  | PDB | 6*8.7 | 50 | 47 | 198900
115 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 168 | 4644318 | FGMO
116 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 154 | 3894227 | FGMO
117 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 186 | 4703082 | FGMO
118 | Sirajgonj Unit-4 414 MW(Gas) |  | SNWPGCL | 1*282+1*132 | 414 | 300 | 8296727 | Frequency control
119 | Santahar Peaking |  | PDB | 6*8.7 | 50 | 35 | 216400
120 | Bogra (GBB) |  | RPP | 6*4 | 22 | 22 | 465840
121 | Bogra (EPL) |  | RPP | 5*3.3+5*2 | 10 | 16 | 369180
122 | Ullapara (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 102222
123 | Rajlanka 52 MW |  | IPP | 6*8.92 | 52 | 50 | 2710400
124 | Chapainawabganj-100 MW |  | PDB | 12*8.924 | 104 | 91 | 1146012
125 | Paramount Baghabari |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
126 | Confidence Bogura-2 (CPBL) |  | IPP | 113 MW | 113 | 107 | 1573248
| Rajshahi Area Total |  |  |  | 2070 | 1424 | 31102949
107 | Barapukuria Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under overhauling
| Barapukuria Unit-2 |  | PDB | 1*125 | 85 | 65 | 1625891
108 | Barapukuria Unit-3 |  | PDB | 1*275 | 274 | 199 | 4843600
129 | Rangpur GT |  | PDB | 1*20 | 20 | 17 | 120000
130 | Saidpur GT |  | PDB | 1*20 | 20 | 17 | 162000
| Confidence Rangpur |  | IPP | 113 MW | 0 | 0 | 305280
| Rangpur Area Total |  |  |  | 484 | 298 | 7056771
| Total |  |  |  | 17786 | 12893 | 264449681
| Eastern Grid Total |  |  |  | 12456 | 9012 | 184788992
| Western Grid Total |  |  |  | 5330 | 3881 | 79660689
| National Grid Total |  |  |  | 17786 | 12893 | 264449681
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date: | 2019-05-29
| (a) ENTIRE EASTERN GRID : |  | 8214 | MW | (b) ENTIRE WESTERN GRID : |  | 3895 | MW
| i) Dhaka area |  | 4451 | MW | i) Khulna area |  | 1542 | MW
| ii) Chittagong area |  | 1108 | MW | ii) Rajshahi area |  | 1297 | MW
| iii) Comilla area |  | 1216 | MW | iii) Barisal area |  | 357 | MW
| iv) Mymensingh area |  | 928 | MW | iv) Rangpur area |  | 699 | MW
| v) Sylhet area |  | 511 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 12109 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
SL NO | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
1 | Siddhirganj | 132 | 1000 | Jamalpur | 113 | 1900 | Jessore | 120 | 2000
2 | Munsiganj | 130 | 2100 | Sherpur | 96 | 2200 | Jhenida | 113 | 1930
3 | Sonargaon | 72 | 300 | Srimongal | 42 | 2200 | Bottail | 136 | 2100
4 | Shyampur | 200 | 900 | Shahjibazar | 126 | 2200 | G.K Project | 56 | 2000
5 | Bhulta | 191 | 100 | Fenchuganj | 51 | 2300 | Faridpur | 186 | 1930
6 | Madanganj | 64 | 1300 | Kulawara | 50 | 1900 | Madaripur | 122 | 2100
7 | Shitalakhya | 120 | 1600 | Sylhet | 144 | 2200 | Gopalganj | 104 | 2200
8 | Rahim steel | 10 | 1930 | Chatak | 36 | 2100 | Bagerhat | 85 | 2200
9 | Matuail | 102 | 900 | Sunamganj | 39 | 2100 | Mongla | 38 | 100
10 | Ghorasal | 87 | 1930 | Biani Bazar | 48 | 1900 | Satkhira | 108 | 2100
11 | Narsingdi | 140 | 1930 | Comilla (S) | 186 | 2100 | Gallamari | 54 | 1930
12 | Haripur (SBU) | 111 | 1600 | Comilla(N) | 145 | 2300 | Magura | 62 | 2200
13 | Ullon | 98 | 1930 | Chandpur | 109 | 2200 | Chuadanga | 27 | 2300
14 | Hasnabad | 236 | 2100 | Feni | 161 | 2100 | Barisal | 118 | 2200
15 | Magbazar | 147 | 1400 | Chowmuhani | 190 | 2100 | Patuakhali | 105 | 2100
16 | Maniknagar | 116 | 1200 | Ashuganj | 56 | 2000 | Bhandaria | 60 | 2100
17 | Bangabhaban | 38 | 1100 | Daudkandi | 146 | 2200 | Barisal (N) | 43 | 2100
18 | Narinda | 100 | 1100 | B.Baria | 149 | 2200 | Sariatpur | 42 | 2200
19 | Dhanmondi | 178 | 1200 | Ramganj | 104 | 2100 | Benapol | 46 | 2100
20 | Lalbag | 85 | 1300 | Madunaghat | 72 | 1500 | Borhan Uddin | 37 | 2200
21 | Madartek | 84 | 1930 | Hathazari | 104 | 2000 | Ishurdi | 68 | 2100
22 | Mirpur | 122 | 1930 | Khulshi | 106 | 1000 | Ruppur Paromanobik | 1 | 100
23 | Kalyanpur | 129 | 1900 | Halishahar | 150 | 1400 | Natore | 131 | 2100
24 | Gulshan | 176 | 1600 | Baraulia | 160 | 1500 | Bogra | 143 | 2100
25 | Uttara | 94 | 2000 | Sikalbaha | 39 | 2100 | Noagaon | 126 | 2100
26 | Uttara New | 20 | 1500 | Dohazari | 100 | 100 | Rajshahi | 162 | 1930
27 | Kamrangirchar | 81 | 1930 | Cox'sbazar | 95 | 2000 | C.Nawabganj | 76 | 2100
28 | Savar | 153 | 1500 | Chandraghona | 30 | 1930 | Amnura | 37 | 2100
29 | Bhasantec | 179 | 2000 | Kaptai | 4.2 | 1930 | Pabna | 132 | 2100
30 | Agargaon | 63 | 1500 | A. Khaer Stl. | 0 | 0 | Shahjadpur | 72 | 2100
31 | Satmosjid | 117 | 2000 | Bakulia | 119 | 2000 | Serajganj | 114 | 2100
32 | Tongi | 161 | 2100 | Julda | 22 | 1100 | Niyamatpur | 60 | 2100
33 | Kabirpur | 231 | 1500 | TK chemical | 3.2 | 1000 | Joypurhat | 54 | 2100
34 | Basundhara | 140 | 1500 | Modern Steel | 12 | 1100 | Mohastangor | 16 | 2100
35 | Manikganj | 104 | 2100 | Shahmirpur | 34 | 200 | Rangpur | 140 | 1900
36 | Joydevpur | 236 | 1900 | Khagrachhari | 20 | 1900 | Lalmonirhat | 81 | 2100
37 | New Tongi | 107 | 1500 | Matarbari | 29 | 100 | Saidpur | 111 | 2100
38 | Korda | 261 | 900 | Baroiar Hat | 26 | 100 | Purbasadipur | 102 | 2100
39 | Dhamrai | 60 | 2100 | Rangamati | 12 | 1900 | Thakurgaon | 78 | 2000
40 | Valuka | 102 | 2100 | Abul Khair 230 | 126 | 900 | Palashbari | 102 | 1930
41 | Tangail | 197 | 2100 | BSRM | 158 | 700 | Barapukuria | 55 | 2100
42 | Mymensing | 225 | 2000 | Goalpara | 30 | 2000 | Panchagar | 42 | 2100
43 | Kishorganj | 134 | 2300 | Central (S) | 102 | 2200 | Joldhaka | 17 | 1930
44 | Netrokona | 87 | 2000 | Noapara | 111 | 2200
| Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  | (24) Director,System Planning,PDB.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2019-05-29
| Sub-Station | Max Voltage | Hour | Min | Hour |  | Sub-Station | Maxm | Hour
|  |  |  | Voltage |  |  |  | Voltage
SL NO | 400 KV | KV |  | KV |  | SL NO |  | KV
1 | Bibiyana | 382 | 22:00 | 374 | 11:00 | 4 | Kaliakoir | 361 | 3:00
2 | Bheramara | 396 | 7:00 | 385 | 16:00 | 5 | Bhulta | 384 | 3:00
3 | Ashuganj(N) | 389 | 2:00 | 375 | 12:00
SL NO | 230 KV | KV |  | KV |  | SL NO | 230 KV | KV
1 | Ghorasal | 228 | 1:00 | 222 | 12:00 | 15 | Hathazari | 217 | 18:00
2 | Ishurdi | 237 | 4:00 | 227 | 11:00 | 16 | Megnaghat | 220 | 23:00
3 | Ashuganj | 235 | 1:00 | 230 | 8:00 | 17 | Fenchuganj | 232 | 22:00
4 | Serajganj | 236 | 15:00 | 227 | 20:00 | 18 | Siddhirganj | 218 | 20:00
5 | Baghabari | 232 | 4:00 | 225 | 19:30 | 19 | Maniknagar | 215 | 19:00
6 | Barapukuria | 235 | 6:00 | 218 | 21:00 | 20 | Old Airport | 215 | 19:00
7 | Bogra | 228 | 5:00 | 215 | 21:00 | 21 | Barisal | 235 | 5:00
8 | Khulna South | 234 | 18:30 | 221 | 12:00 | 22 | AKSML | 213 | 18:00
9 | Rampura | 218 | 21:00 | 211 | 11:00 | 23 | BSRM | 215 | 21:00
10 | Haripur | 218 | 19:00 | 210 | 10:00 | 24 | Bibiyana | 229 | 1:00
11 | Hasnabad | 215 | 18:30 | 208 | 9:00 | 25 | Bhulta | 219 | 20:00
12 | Aminbazar | 216 | 20:00 | 207 | 12:00 | 26 | Ashuganj (S) | 233 | 2:00
13 | Tongi | 217 | 24:00 | 207 | 7:00 | 27 | Kaliakoir | 219 | 2:00
14 | Comilla (N) | 225 | 18:30 | 217 | 9:00
SL NO | 132 kV | KV |  | KV |  | SL NO | 132 kV | KV
1 | Siddhirganj | 132 | 2000 | 126 | 900 | 65 | Hathazari | 129 | 1800
2 | Munsiganj | 134 | 1830 | 124 | 800 | 66 | Khulshi | 127 | 800
3 | Megnaghat | 130 | 2100 | 125 | 100 | 67 | Halishahar | 130 | 1800
4 | Shyampur | 131 | 1930 | 124 | 900 | 68 | Baraulia | 129 | 1800
5 | Bhulta | 126 | 2100 | 116 | 300 | 69 | Sikalbaha | 132 | 1800
6 | Madanganj | 133 | 2000 | 122 | 1000 | 70 | Dohazari | 129 | 1800
7 | Shitalakhya | 136 | 2000 | 122 | 1000 | 71 | Cox'sbazar | 122 | 1800
8 | Rahim steal | 133 | 1900 | 126 | 900 | 72 | Chandraghona | 130 | 2100
9 | Matuail | 131 | 1900 | 124 | 900 | 73 | Kaptai | 128 | 1800
10 | Ghorasal | 135 | 100 | 132 | 1200 | 74 | A. Khaer Stl. | 126 | 100
11 | Narsinghdi | 128 | 1600 | 119 | 1000 | 75 | Bakulia | 130 | 1800
12 | Haripur (SBU) | 133 | 1000 | 126 | 800 | 76 | Julda | 131 | 1800
13 | Ullon | 130 | 200 | 122 | 1200 | 77 | TK Chemical | 133 | 1800
14 | Hasnabad | 132 | 1900 | 124 | 1000 | 78 | Modern Steel | 130 | 500
15 | Magbazar | 130 | 200 | 121 | 1300 | 79 | Shahmirpur | 130 | 2100
16 | Maniknagar | 131 | 2000 | 125 | 1000 | 80 | Khagrachhari | 130 | 1800
17 | Bangabhaban | 131 | 2000 | 125 | 1000 | 81 | Matarbari | 123 | 1100
18 | Narinda | 131 | 2000 | 125 | 1000 | 82 | Baroiar Hat | 124 | 1100
19 | Dhanmondi | 130 | 200 | 122 | 1200 | 83 | Rangamati | 129 | 1830
20 | Lalbag | 130 | 1900 | 119 | 1100 | 84 | Goalpara | 138 | 1800
21 | Madartek | 130 | 600 | 122 | 1100 | 85 | Central s/s | 138 | 1800
22 | Mirpur | 128 | 200 | 129 | 1200 | 86 | Noapara | 134 | 1830
23 | Kalyanpur | 130 | 200 | 123 | 1200 | 87 | Jessore | 132 | 1800
24 | Gulshan | 130 | 500 | 122 | 1200 | 88 | Jhenida | 129 | 500
25 | Uttara | 125 | 100 | 119 | 1100 | 89 | Bottail | 134 | 500
26 | Uttara New | 130 | 100 | 122 | 1100 | 90 | G.K.Project | 143 | 1800
27 | Kamrangirchar | 128 | 100 | 121 | 1100 | 91 | Faridpur | 132 | 700
28 | Savar | 127 | 300 | 120 | 1100 | 92 | Madaripur | 134 | 1830
29 | Bhasantec | 130 | 600 | 123 | 1100 | 93 | Gopalganj | 139 | 500
30 | Agargaon | 131 | 500 | 125 | 1100 | 94 | Bagerhat | 131 | 1830
31 | Satmosjid | 130 | 100 | 123 | 1300 | 95 | Mongla | 133 | 2100
32 | Tongi | 133 | 1830 | 125 | 1000 | 96 | Satkhira | 136 | 1830
33 | Kabirpur | 130 | 100 | 123 | 2100 | 97 | Gallamari | 138 | 1800
34 | Basundhara | 127 | 500 | 118 | 1300 | 98 | Magura | 128 | 700
35 | Manikganj | 136 | 1900 | 127 | 1800 | 99 | Chuadanga | 124 | 700
36 | Joydevpur | 138 | 300 | 130 | 1200 | 100 | Barisal | 137 | 600
37 | New Tongi | 132 | 1900 | 123 | 1000 | 101 | Patuakhali | 135 | 800
38 | Kodda | 133 | 2000 | 118 | 700 | 102 | Bhandaria | 135 | 1830
39 | Dhamrai | 131 | 400 | 124 | 2100 | 103 | Barisal (N) | 139 | 500
40 | Valuka | 131 | 600 | 114 | 2100 | 104 | Sariatpur | 133 | 800
41 | Tangail | 135 | 500 | 123 | 2300 | 105 | Benapol | 131 | 1800
42 | Mymensing | 132 | 600 | 115 | 2100 | 106 | Ishurdi | 139 | 500
43 | Kishorganj | 130 | 700 | 120 | 2100 | 107 | Ruppur Paromanobik | 139 | 400
44 | Netrokona | 135 | 500 | 118 | 2100 | 108 | Natore | 134 | 500
45 | Jamalpur | 140 | 700 | 128 | 1100 | 109 | Bogra | 135 | 600
46 | Sherpur | 137 | 400 | 130 | 1100 | 110 | Noagaon | 130 | 500
47 | Srimongal | 136 | 500 | 130 | 2100 | 111 | Rajshahi | 133 | 1830
48 | Shahjibazar | 135 | 600 | 129 | 2100 | 112 | C.Nawabganj | 128 | 1800
49 | Fenchuganj | 134 | 700 | 130 | 2100 | 113 | Amnura | 134 | 1830
50 | Khulawara | 133 | 500 | 129 | 2100 | 114 | Pabna | 137 | 400
51 | Sylhet | 134 | 600 | 129 | 2100 | 115 | Shahjadpur | 142 | 400
52 | Chatak | 134 | 500 | 128 | 1930 | 116 | Serajganj | 138 | 400
53 | Sunamganj | 135 | 800 | 125 | 2100 | 117 | Niyamatpur | 128 | 500
54 | Biani Bazar | 132 | 600 | 126 | 2100 | 118 | Joypurhat | 129 | 600
55 | Comilla(s) | 123 | 600 | 119 | 1100 | 119 | Mohastangor | 134 | 400
56 | Comilla(n) | 133 | 1200 | 128 | 800 | 120 | Rangpur | 131 | 400
57 | Chandpur | 132 | 1600 | 125 | 700 | 121 | Lalmonirhat | 130 | 500
58 | Feni | 126 | 1100 | 120 | 2300 | 122 | Saidpur | 130 | 500
59 | Chowmuhani | 122 | 1100 | 115 | 1900 | 123 | Purbasadipur | 130 | 300
60 | Ashuganj | 136 | 700 | 131 | 2100 | 124 | Thakurgaon | 123 | 500
61 | Daudkandi | 134 | 1100 | 123 | 700 | 125 | Palashbari | 134 | 500
62 | B.Baria | 132 | 500 | 124 | 2100 | 126 | Barapukuria | 135 | 600

## L-Curve
Date | 2019-05-29
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 210 | 8738 | 3875 | 12613 |  |  |  | QF-LDC-12
0:30 | 165 | 8423 | 3694 | 12117 | Date: | 2019-05-29
1:00 | 120 | 8108 | 3513 | 11621
1:30 | 120 | 8016.5 | 3458 | 11474.5
2:00 | 120 | 7925 | 3403 | 11328
2:30 | 115 | 7817 | 3401.5 | 11218.5 | [5 empty] | Gen. at Eve. Peak | 12893 | 10933 MW (20:00 )
3:00 | 110 | 7709 | 3400 | 11109 | [6 empty] | 21:00
3:30 | 145 | 7578.5 | 3299 | 10877.5 | [5 empty] | Gen. at Day Peak | 10364.4 | 8751.9 MW (12:00 )
4:00 | 180 | 7448 | 3198 | 10646 | [6 empty] | 12:00
4:30 | 200 | 7180 | 3094 | 10274 | [5 empty] | Highest Generation | 12893
5:00 | 220 | 6912 | 2990 | 9902 | [6 empty] | 21:00
5:30 | 240 | 6637.55 | 2809 | 9446.55
6:00 | 260 | 6363.1 | 2628 | 8991.1
6:30 | 290 | 6300.58 | 2616 | 8916.58
7:00 | 320 | 6238.06 | 2604 | 8842.06
7:30 | 360 | 6287.43 | 2636.5 | 8923.93
8:00 | 400 | 6336.8 | 2669 | 9005.8
8:30 | 390 | 6568.9 | 2680.5 | 9249.4
9:00 | 380 | 6801 | 2692 | 9493
9:30 | 355 | 6905 | 2715.5 | 9620.5
10:00 | 330 | 7009 | 2739 | 9748
10:30 | 295 | 7093.8 | 2796 | 9889.8
11:00 | 260 | 7178.6 | 2853 | 10031.6
11:30 | 225 | 7334.5 | 2863.5 | 10198
12:00 | 190 | 7490.4 | 2874 | 10364.4
12:30 | 135 | 7596.85 | 2883 | 10479.85
13:00 | 80 | 7703.3 | 2892 | 10595.3
13:30 | 57.5 | 7795.45 | 2965.5 | 10760.95
14:00 | 35 | 7887.6 | 3039 | 10926.6
14:30 | 57.5 | 7989.65 | 3055.5 | 11045.15
15:00 | 80 | 8091.7 | 3072 | 11163.7
15:30 | 140 | 8132.95 | 3003 | 11135.95
16:00 | 200 | 8174.2 | 2934 | 11108.2
16:30 | 160 | 7973.3 | 2932.5 | 10905.8
17:00 | 120 | 7772.4 | 2931 | 10703.4
17:30 | 95 | 7479 | 2929.5 | 10408.5
18:00 | 70 | 7185.6 | 2928 | 10113.6
18:30 | 105 | 7481.3 | 3197 | 10678.3
19:00 | 140 | 7777 | 3466 | 11243
19:30 | 160 | 8627 | 3881 | 12508
20:00 | 240 | 8646 | 3904 | 12550 |  |  |  | Executive Engineer
20:30 | 280 | 8829 | 3892.5 | 12721.5 |  |  |  | Network Operation Division
21:00 | 320 | 9012 | 3881 | 12893
21:30 | 290 | 8992.5 | 3895 | 12887.5
22:00 | 260 | 8973 | 3909 | 12882 |  |  |  |  | Page 6 of 7
22:30 | 245 | 8873.5 | 3896 | 12769.5
23:00 | 230 | 8774 | 3883 | 12657
23:30 | 220 | 8756 | 3879 | 12635
24:00 | 210 | 8738 | 3875 | 12613
10933 MW (20:00 )
8751.9 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2019-05-29 |  | Energy | 264449681
[10 empty] | 2019-05-29 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 4708 | 930 | 2081 | 3476 | 264 | 35 | 947 | 0 | 172
0:30 | 4710 | 929.5 | 2128 | 3112 | 267 | 34.5 | 769 | 0 | 167 | Date: | 2019-05-29
1:00 | 4712 | 929 | 2175 | 2748 | 270 | 34 | 591 | 0 | 162
1:30 | 4655 | 928.5 | 2165 | 2691 | 270 | 34 | 570 | 0 | 161 | [7 empty] | Total Energy | 264.4497 | Total Energy Gen 165.409 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 165.409 MKWHr
2:00 | 4598 | 928 | 2155 | 2634 | 270 | 34 | 549 | 0 | 160 | [7 empty] | Energy not Served | 0
2:30 | 4577 | 928 | 2143.5 | 2556.5 | 270.5 | 34.5 | 547.5 | 0 | 161 | [7 empty] | Energy Requirement | 264.4497
3:00 | 4556 | 928 | 2132 | 2479 | 271 | 35 | 546 | 0 | 162
3:30 | 4544 | 928 | 2137 | 2336.5 | 270.5 | 35 | 466.5 | 0 | 160 | [6 empty] | Shortage
4:00 | 4532 | 928 | 2142 | 2194 | 270 | 35 | 387 | 0 | 158
4:30 | 4510.5 | 928 | 2088.5 | 1917 | 270 | 35.5 | 366.5 | 0 | 158
5:00 | 4489 | 928 | 2035 | 1640 | 270 | 36 | 346 | 0 | 158
5:30 | 4402 | 927.5 | 1936 | 1375 | 270 | 36 | 346 | 0 | 154
6:00 | 4315 | 927 | 1837 | 1110 | 270 | 36 | 346 | 0 | 150
6:30 | 4309 | 927.5 | 1830.5 | 1066 | 270 | 33 | 329 | 0 | 148 |  |  |  |  | Coal
7:00 | 4303 | 928 | 1824 | 1022 | 270 | 30 | 312 | 0 | 146
7:30 | 4351 | 928.5 | 1843.5 | 1032.5 | 269.5 | 30 | 312 | 0 | 146 |  |  |  | Oil |  |  |  | ,
8:00 | 4399 | 929 | 1863 | 1043 | 269 | 30 | 312 | 0 | 146
8:30 | 4509 | 929 | 1928.5 | 1124.5 | 266.5 | 30 | 297.5 | 0 | 147
9:00 | 4619 | 929 | 1994 | 1206 | 264 | 30 | 283 | 0 | 148
9:30 | 4628.5 | 929 | 2025 | 1343 | 264 | 30 | 234 | 0 | 149
10:00 | 4638 | 929 | 2056 | 1480 | 264 | 30 | 185 | 0 | 150
10:30 | 4634 | 929.5 | 2024 | 1657.5 | 264 | 30 | 185 | 0 | 152
11:00 | 4630 | 930 | 1992 | 1835 | 264 | 30 | 185 | 0 | 154
11:30 | 4590.5 | 929 | 1961 | 2068 | 264.5 | 30 | 186 | 0 | 159
12:00 | 4551 | 928 | 1930 | 2301 | 265 | 30 | 187 | 0 | 164
12:30 | 4617.5 | 928.5 | 1968 | 2285 | 264.5 | 30 | 210.5 | 0 | 159
13:00 | 4684 | 929 | 2006 | 2269 | 264 | 30 | 234 | 0 | 154
13:30 | 4684 | 929 | 2006 | 2269 | 264 | 30 | 234 | 0 | 154
14:00 | 4684 | 929 | 2006 | 2269 | 264 | 30 | 234 | 0 | 154
14:30 | 4731.5 | 929.5 | 2037.5 | 2453.5 | 263 | 30 | 257 | 0 | 156
15:00 | 4779 | 930 | 2069 | 2638 | 262 | 30 | 280 | 0 | 158
15:30 | 4656.5 | 929.5 | 2059 | 2746 | 262.5 | 32 | 285 | 0 | 151
16:00 | 4534 | 929 | 2049 | 2854 | 263 | 34 | 290 | 0 | 144
16:30 | 4556 | 929.5 | 2011.5 | 2674.5 | 262.5 | 34 | 287 | 0 | 143
17:00 | 4578 | 930 | 1974 | 2495 | 262 | 34 | 284 | 0 | 142
17:30 | 4441 | 930 | 1764.5 | 2511.5 | 262.5 | 34 | 311.5 | 0 | 151
18:00 | 4304 | 930 | 1555 | 2528 | 263 | 34 | 339 | 0 | 160
18:30 | 4370.5 | 930 | 1597.5 | 2756.5 | 263 | 34.5 | 556 | 0 | 170
19:00 | 4437 | 930 | 1640 | 2985 | 263 | 35 | 773 | 0 | 180
19:30 | 4701 | 929 | 1991 | 3504 | 263 | 35 | 911 | 0 | 174
20:00 | 4663 | 930 | 1844 | 3653 | 263 | 36 | 985 | 0 | 176
20:30 | 4649 | 929.5 | 1945.5 | 3705.5 | 263.5 | 36 | 1011.5 | 0 | 181
21:00 | 4635 | 929 | 2047 | 3758 | 264 | 36 | 1038 | 0 | 186
21:30 | 4651 | 929.5 | 2081.5 | 3697.5 | 264 | 36 | 1044 | 0 | 184
22:00 | 4667 | 930 | 2116 | 3637 | 264 | 36 | 1050 | 0 | 182
22:30 | 4682 | 929.5 | 2094 | 3584 | 264 | 35.5 | 1008.5 | 0 | 172
23:00 | 4697 | 929 | 2072 | 3531 | 264 | 35 | 967 | 0 | 162
23:30 | 4702.5 | 929.5 | 2076.5 | 3503.5 | 264 | 35 | 957 | 0 | 167 | Max Temp. in Dhaka |  | 36.6° C
24:00 | 4708 | 930 | 2081 | 3476 | 264 | 35 | 947 | 0 | 172
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 165.409 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 165.409 MKWHr
Note on W13: Author:

## Generation
2019-05-29
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Kaptai Unit-1, 2 & 3 | 34 | 34 | 35 | 35 | 36 | 36 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 34 | 34 | 34 |  | 35 | 35 | 36 | 36 | 36 | 35 | 35 | 712380
2 | Kaptai Unit-4 & 5
3 | Chattogram ST-1 (Raozan) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2500000
4 | Chittgong ST-2 (Raozan)
5 | Raozan 25 MW (RPCL) | 25 | 25 | 25 | 8 | 8 | 8 | 8 | 8 | 18 | 25 | 16 | 16 | 24 | 24 | 24 | 24 | 24 | 24 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 497720
| Teknaf Solartech 20MW | [5 empty] | 0 | 5.08 | 11 | 14.7 | 10.2 | 9.5 | 4.3 | 18.5 | 16.7 | 13.3 | 8.4 | 3.3 | 0.6 |  | 0 | [6 empty] | 125415
6 | Sikalbaha 225MW (Gas) | 217 | 220 | 217 | 218 | 204 | 198 | 205 | 218 | 219 | 231 | 217 | 218 | 220 | 218 | 218 | 219 | 219 | 219 |  | 219 | 218 | 217 | 217 | 218 | 217 | 217 | 5140044
7 | Sikalbaha 225MW (Oil)
8 | Sikalbaha ST 60MW
9 | Sikalbaha GT 150MW (Gas) | 140 | 139 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 150 | 150 | 147 | 142 | 146 | 135 | 143 | 145 | 142 |  | 142 | 140 | 120 | 140 | 140 | 140 | 139 | 3353944
10 | Sikalbaha GT 150MW (Oil)
| Dohazari Peaking | 85 | 85 | 85 | 85 | 85 | 85 | 51 | 51 | 44 | 17 | 17 | 17 | 16 | 16 | 16 | 16 | 16 | 17 |  | 85 | 81 | 83 | 83 | 83 | 83 | 83 | 1295934
12 | Hathazari peaking | 7 | [9 empty] | 0 | 2 | 50 | 50 | 50 | 49 | 49 | 49 |  | 78 | 82 | 84 | 84 | 84 | 84 | 84 | 807848
| Baraka Sikalbaha PL | 109 | 109 | 109 | 109 | 71 | 0 |  |  | 41 | 55 | 91 | 91 | 91 | 109 | 109 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 1983840
| Daudkandi bangla trak | [9 empty] | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 10 | 10 |  | 10 | 10 | 0 |  |  |  |  | 1610880
14 | Daudkandi Peaking 52MW | [19 empty] | 30 | 50 | 50 | 50 | 50 | 0 |  | 160480
15 | Siddhirgonj ST 210MW
16 | Siddhirgonj GT Unit-1& 2 | 91 | 58 | 60 | 59 | 35 | 35 | 35 | 36 | 80 | 80 | 82 | 59 | 87 | 82 | 90 | 92 | 92 | 34 |  | 34 | 52 | 52 | 52 | 82 | 87 | 87 | 1704000
17 | Siddhirganj CCPP-335 MW
18 | Summit Gazipur -2 | [11 empty] | 15 | 15 | 15 | 15 | 75 | 95 | 95 |  | 137 | 138 | 195 | 216 | 155 | 132 | 95 | 1287160
19 | Ashuganj 195MW Modular | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 200727
20 | Ghorasal ST: Unit-1,2 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 674000
21 | Ghorasal GT: Unit-3 | 133 | 134 | 94 | 94 | 94 | 94 | 44 | 45 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 93 |  | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 2420400
22 | Ghorasal GT: Unit-4 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 101 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2395000
23 | Ghorasal ST: Unit-5 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2756250
24
25 | Ghorasal ST: Unit-7 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 7200763
26
28 | Ashuganj ST: Unit- 3
29 | Ashuganj ST: Unit- 4
30 | Ashuganj ST: Unit- 5 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 110 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 |  | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 2945292
32 | Ashuganj Engines TSK | 33 | 33 | 33 | 33 | 33 | 33 | 30 | 30 | 30 | 30 | 29 | 32 | 32 | 29 | 36 | 36 | 36 | 36 |  | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 765288
33 | Ashuganj CCPP 225 MW | 182 | 182 | 187 | 183 | 182 | 188 | 198 | 197 | 199 | 183 | 183 | 196 | 202 | 194 | 205 | 188 | 191 | 185 |  | 211 | 215 | 215 | 214 | 215 | 215 | 215 | 4722000
34 | Ashuganj CCPP(South) | 356 | 330 | 330 | 330 | 330 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 330 | 330 | 330 | 330 | 330 | 270 |  | 270 | 320 | 320 | 320 | 320 | 320 | 320 | 7784000
| Ashuganj CCPP(North) | 330 | 330 | 330 | 330 | 300 | 240 | 240 | 240 | 360 | 360 | 360 | 320 | 320 | 320 | 355 | 360 | 360 | 275 |  | 260 | 320 | 320 | 320 | 360 | 360 | 360 | 8031000
35 | Ashuganj (Precision) 55MW | 56 | 55 | 55 | 56 | 55 | 55 | 56 | 56 | 56 | 56 | 55 | 55 | 55 | 53 | 53 | 53 | 53 | 54 |  | 54 | 53 | 54 | 55 | 56 | 55 | 55 | 1317600
36 | Chandpur CCPP | 50 | 50 | 50 | 50 | 50 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 95 | 95 | 100 | 100 | 96 |  | 100 | 97 | 100 | 100 | 100 | 100 | 100 | 2031680
37 | Tongi GT | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 997923
38 | Haripur GT: Unit-1, 2
39 | Haripur 412 MW CCPP | 328 | 328 | 331 | 328 | 328 | 280 | 280 | 335 | 344 | 335 | 337 | 328 | 350 | 340 | 359 | 336 | 330 | 330 |  | 348 | 327 | 335 | 330 | 328 | 330 | 337 | 8128510
40 | Meghnaghat CCPP 450MW | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 380 | 380 | 400 | 400 | 420 | 420 | 420 | 340 |  | 340 | 420 | 340 | 430 | 430 | 400 | 400 | 9828500
41 | Haripur Power CCPP 360MW | 353 | 354 | 333 | 335 | 307 | 275 | 275 | 275 | 320 | 344 | 341 | 320 | 320 | 320 | 335 | 336 | 336 | 255 |  | 255 | 300 | 300 | 344 | 353 | 351 | 354 | 7664000
42 | Mymensingh RPCL 210MW | 148 | 148 | 100 | 99 | 101 | 104 | 151 | 150 | 148 | 148 | 148 | 144 | 144 | 141 | 140 | 141 | 142 | 141 |  | 143 | 147 | 146 | 145 | 149 | 147 | 149 | 3262720
43 | Haripur NEPC 110MW | [9 empty] | 0 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 |  | 55 | 80 | 110 | 110 | 110 | 110 | 110 | 630700
44 | Fenchugonj CCPP-1 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 58 | 55 | 56 | 54 | 55 | 56 | 56 | 56 | 56 |  | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 1348000
45 | Fenchugonj CCPP-2 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 57 | 57 | 57 | 57 |  | 57 | 58 | 58 | 58 | 58 | 58 | 58 | 1362840
46 | Shajibazar 330 MW | 251 | 252 | 250 | 247 | 249 | 249 | 248 | 251 | 250 | 250 | 250 | 251 | 250 | 251 | 252 | 247 | 250 | 246 |  | 249 | 251 | 254 | 250 | 250 | 249 | 248 | 5694000
47 | Shahjibazar GT: Unit- 8, 9 | 56 | 49 | 63 | 51 | 64 | 63 | 64 | 63 | 61 | 62 | 49 | 61 | 59 | 60 | 58 | 57 | 75 | 61 |  | 59 | 40 | 43 | 61 | 61 | 61 | 60 | 1391520
48 | Shahjibazar 86MW | 78 | 78 | 78 | 79 | 79 | 50 | 50 | 50 | 79 | 73 | 72 | 71 | 68 | 71 | 71 | 71 | 73 | 10 |  | 50 | 74 | 75 | 75 | 75 | 76 | 76 | 1684320
49 | Shahjibazar (EPL) 50MW | 45 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 10 |  | 10 | 40 | 44 | 45 | 45 | 45 | 45 | 966960
50 | Sylhet GT 150 MW | 105 | 104 | 105 | 105 | 105 | 115 | 109 | 117 | 110 | 104 | 103 | 112 | 110 | 112 | 118 | 103 | 106 | 104 |  | 115 | 118 | 104 | 104 | 104 | 115 | 112 | 2643850
51 | Sylhet GT 20 MW | 18 | 18 | 18 | 19 | 19 | 0 |  |  |  | 0 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 342000
52 | Sylhet (EPL) 50MW | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 45 | 46 | 46 | 45 | 45 | 42 | 44 | 44 | 43 |  | 43 | 43 | 43 | 45 | 46 | 45 | 43 | 342000
53 | Sylhet (Desh) 10MW | 10 | 10 | 10 | 10 | 10 | 0 |  | 0 | 10 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 193680
54 | Hobiganj 11MW | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 255840
55 | Fenchugonj (Barakatullah) 51MW | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 47 | 47 | 47 | 50 | 47 | 52 | 51 | 11 | 11 |  | 11 | 49 | 52 | 53 | 53 | 53 | 50 | 1111200
56 | Shahjahanulla 25 MW | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 21 | 15 | 14 | 0 | 7 | 8 | 8 | 8 | 8 | 16 | 16 |  | 16 | 22 | 22 | 22 | 22 | 22 | 22 | 392736
57 | Summit Bibiana- 2 | 250 | 250 | 245 | 250 | 245 | 240 | 260 | 260 | 255 | 240 | 250 | 250 | 270 | 290 | 285 | 260 | 280 | 255 |  | 290 | 240 | 240 | 255 | 260 | 250 | 260 | 6347000
58 | Southern 55MW | 55 | 55 | 55 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1061012
59 | Sikalbaha (Energis) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 24 |  | 24 | 24 | 24 | 24 | 24 | 16 | 16 | 435840
60 | Barabkunda (Regent) | 16 | 16 | 16 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 16 | 17 | 17 | 17 | 14 | 14 | 15 |  | 15 | 15 | 15 | 18 | 18 | 18 | 18 | 386544
61 | Narshingdi (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 16 | 14 | 16 | 16 | 16 | 16 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 400176
62 | Tangail (Doreen) 22MW | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 448776
63 | Tripura | 162 | 160 | 162 | 158 | 158 | 150 | 146 | 146 | 148 | 150 | 154 | 164 | 154 | 154 | 158 | 144 | 142 | 160 |  | 180 | 174 | 176 | 186 | 182 | 162 | 172 | 3837120
64 | Malancha, Ctg. EPZ (United) | 38 | 39 | 40 | 40 | 40 | 38 | 13 | 4 | 3 | 2 | 2 | 2 | 7 | 2 | 2 | 7 | 2 | 16 |  | 29 | 29 | 30 | 33 | 36 | 36 | 36 | 464160
65 | Feni (Doreen) 22MW | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 18 | 18 | 18 | 18 | 18 | 20 | 20 | 21 | 21 |  | 21 | 21 | 21 | 22 | 22 | 22 | 22 | 494820
66 | Feni, Mohipal (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 5 | 5 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 242460
67 | Jangalia (Summit) 33MW | 24 | 24 | 24 | 24 | 24 | 8 | 8 | 8 | 15 | 0 | 0 | 0 | 0 | 0 | 21 | 24 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 407100
68 | Summit Cumilla 25MW | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 514990
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 28 | 28 | 28 | 24 | 24 | 27 | 28 | 28 | 28 | 27 | 27 | 28 | 28 | 27 | 28 | 28 | 28 | 28 |  | 28 | 28 | 28 | 32 | 32 | 32 | 27 | 634320
71 | Summit Maona | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 25 | 25 | 25 | 25 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 694800
72 | Summit Rupganj | 25 | 17 | 17 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 17 | 25 | 25 |  | 25 | 25 | 25 | 25 | 17 | 25 | 25 | 571200
73 | Ghorashal (Regent) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 5 | 6 | 6 |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 149500
76 | Siddhirganj Desh
77 | Siddhirganj (Dutch Bangla) | [10 empty] | 0 | 23 | 23 | 23 | 23 | 23 | 7 | 7 |  | 19 | 50 | 65 | 98 | 100 | 50 | 48 | 574080
78 | Gazipur (RPCL) | 47 | 45 | 39 | 24 | 0 |  |  | 14 | 49 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 |  | 47 | 47 | 47 | 48 | 43 | 40 | 40 | 922584
79 | Kodda 149MW | 149 | 149 | 149 | 100 | 80 | 80 | 80 | 80 | 80 | 48 | 48 | 48 | 48 | 95 | 94 | 94 | 70 | 70 |  | 100 | 140 | 145 | 145 | 145 | 144 | 147 | 2390400
80 | Jamalpur 95MW | 94 | 94 | 94 | 94 | 94 | 94 | 70 | 70 | 40 | 38 | 38 | 80 | 86 | 95 | 95 | 94 | 93 | 93 |  | 93 | 93 | 92 | 91 | 92 | 85 | 61 | 2033280
81 | Lakdhanvi 52 MW | 52 | 52 | 52 | 52 | 8 | 0 |  |  | 0 | 3 | 29 | 52 | 52 | 52 | 52 | 52 | 52 | 52 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 935040
| Gazipur 100 MW | 90 | 90 | 90 | 90 | 90 | 54 | 54 | 91 | 91 | 91 | 91 | 91 | 91 | 108 | 91 | 108 | 108 | 109 |  | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 2243052
| Kaptai Solar | [6 empty] | 1.48 | 2.8 | 4.3 | 3.9 | 0 | 2.1 | 5 | 4.6 | 3.5 | 2.3 | 0.6 | 0 | [8 empty] | 29748
82 | Madanganj 102MW | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 40 | 60 | 65 | 30 | 30 |  | 30 | 40 | 65 | 97 | 100 | 64 | 60 | 947328
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj (Powerpac) 100MW | [15 empty] | 0 | 10 | 10 |  | 32 | 56 | 68 | 50 | 10 | 10 | 10 | 260656
86 | Meghnaghat CCPP(Summit) | 260 | 260 | 285 | 245 | 260 | 265 | 290 | 290 | 290 | 260 | 250 | 290 | 280 | 280 | 280 | 290 | 290 | 290 |  | 295 | 230 | 235 | 285 | 255 | 293 | 285 | 6619316
87 | Meghnaghat (IEL) | 10 | 0 | [8 empty] | 1 | 22 | 24 | 38 | 50 | 50 | 15 | 7 |  | 27 | 100 | 80 | 100 | 100 | 100 | 100 | 753600
88 | Ghorashal 78MW (MAX)
90 | Ashuganj (United) 53MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 120000
91 | Juldah (Acorn) | 78 | 78 | 10 | 10 | 10 | 10 | 10 | 10 | 50 | 50 | 30 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 66 | 76 | 78 | 98 | 98 | 89 | 89 | 892560
92 | Fenchuganj (EPL) 44MW | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 10 | 10 |  | 21 | 50 | 50 | 50 | 50 | 50 | 50 | 1091000
93 | Ashuganj (Midland) 51MW | 35 | 35 | 35 | 35 | 35 | 5 | 5 | 5 | 5 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 10 | 10 |  | 10 | 20 | 20 | 35 | 35 | 35 | 35 | 586288
94 | Gagnagar (Orion) | 7 | 7 | 7 | 0 |  |  |  | 0 | 10 | 24 | 32 | 50 | 50 | 66 | 66 | 66 | 24 | 24 |  | 58 | 84 | 101 | 100 | 100 | 100 | 100 | 978768
95 | Patenga 50MW | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 46 | 47 | 47 | 40 | 43 | 46 | 46 | 47 | 47 | 47 |  | 46 | 46 | 47 | 47 | 47 | 47 | 47 | 1112640
96 | Chattogram ECPV 108 MW | 95 | 95 | 96 | 95 | 10 | 0 | [8 empty] | 1 | 66 | 88 | 89 |  | 89 | 90 | 90 | 90 | 90 | 94 | 90 | 1195200
97 | Katpotti 51 MW | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 13 | 6 | [5 empty] | 0 |  | 3 | 23 | 48 | 49 | 48 | 19 | 13 | 413328
98 | Bosila 108MW | 65 | 65 | 65 | 65 | 13 | 0 |  |  | 46 | 64 | 64 | 63 | 62 | 61 | 61 | 61 | 61 | 61 |  | 62 | 63 | 63 | 56 | 61 | 64 | 65 | 1226880
99 | Madanganj-55 MW | [11 empty] | 12 | 11 | 20 | 30 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 586288
100 | Northern 55 MW | 56 | 56 | 56 | 56 | 56 | 56 | 18 | 18 | 31 | 37 | 55 | 56 | 56 | 56 | 56 | 56 | 56 | 56 |  | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 1114328
101 | Kushiara 163 MW CCPP GT | 130 | 130 | 130 | 130 | 100 | 100 | 100 | 100 | 100 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 |  | 100 | 163 | 130 | 130 | 130 | 130 | 130 | 3227506
102 | Sarishabari (Solar) |  |  |  |  | 0 | 0.1 | 0.5 | 1 | 1 | 1.9 | 2.1 | 2 | 1.8 | 1.3 | 0.9 | 0.5 | 0.5 | 0 |  | 0 | [6 empty] | 14600
103 | Banco Energy 54MW | 35 | 35 | 35 | 35 | 35 | 17 | 17 | 17 | 17 | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 775440
104 | APR Energy , Keranigonj
105 | Bramhangoan 100 MW (Aggreko)
106 | United Mymensingh PPL | 194 | 150 | 150 | 100 | 100 | 32 | 32 | 0 |  |  | 0 | 50 | 60 | 77 | 80 | 80 | 50 | 50 |  | 72 | 151 | 144 | 150 | 150 | 150 | 150 | 2217600
112 | Aggreko Aurahati 100MW
114 | Summit Gazipur-1 150MW | 149 | 141 | 43 | 11 | 0 |  |  | 0 | 15 | 35 | 47 | 68 | 70 | 80 | 101 | 101 | 101 | 101 |  | 115 | 140 | 149 | 149 | 149 | 149 | 149 | 1949760
115 | Juldah 100 MW Unit-3 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 90 | 90 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2394240
116 | Chandpur Desh 200MW | 200 | 200 | 200 | 200 | 165 | 65 | 17 | 17 | 17 | 20 | 136 | 200 | 200 | 200 | 200 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 196 | 200 | 197 | 3790560
117 | Midland 150MW | 150 | 150 | 150 | 150 | 5 | 0 |  |  |  | 1 | 35 | 100 | 103 | 128 | 141 | 135 | 90 | 70 |  | 81 | 150 | 136 | 150 | 150 | 150 | 150 | 2373600
118 | Bibiyana-3 285 MW | 297 | 250 | 269 | 269 | 270 | 269 | 268 | 269 | 270 | 268 | 269 | 240 | 269 | 270 | 282 | 285 | 285 | 200 |  | 201 | 297 | 280 | 280 | 280 | 281 | 281 | 6465000
| United Jamalpur PPL | 93 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 98 | 87 | 96 | 96 | 86 | 86 | 86 | 95 | 86 |  | 86 | 85 | 85 | 86 | 86 | 95 | 95 | 2222400
| Anwara United | 68 | 68 | 68 | 68 | 85 | 85 | 82 | 84 | 84 | 85 | 84 | 84 | 84 | 84 | 82 | 82 | 82 | 85 |  | 97 | 98 | 98 | 75 | 85 | 85 | 117 | 1977160
120 | Eastern Zone Total | 8108 | 7925 | 7709 | 7448 | 6912 | 6363.1 | 6238.06 | 6336.8 | 6801 | 7009 | 7178.6 | 7490.4 | 7703.3 | 7887.6 | 8091.7 | 8174.2 | 7772.4 | 7185.6 |  | 7777 | 8627 | 8646 | 9012 | 8973 | 8774 | 8738 | 184788992
121
122
123 | Khulna 60MW
124 | Khulna (KPCL-1 & 3)
125 | Khulna (KPCL-2) | 49 | 49 | 49 | 49 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 36 | 49 | 49 | 83 | 51 | 49 |  | 49 | 115 | 99 | 99 | 99 | 83 | 83 | 1152000
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur Peaking | 31 | 31 | 31 | 21 | 0 | [11 empty] | 3 | 27 |  | 37 | 39 | 31 | 36 | 36 | 36 | 36 | 336480
| Khulna CCPP 225MW | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 125 | 165 | 195 | 233 | 236 | 235 | 236 | 3515520
129 | Labon Chora 105 MW | 105 | 105 | 105 | 105 | 53 | 17 | 17 | 17 | 17 | 17 | 17 | 53 | 53 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 1919520
130
131
132
133
| Summit Barisal 110 MW | 110 | 110 | 110 | 110 | 110 | 16 | 16 | 16 | 0 |  |  |  | 0 | 16 | 16 | 16 | 16 | 16 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 1352160
136 | Barisal GT: Unit-1, 2 | [20 empty] | 10 | 24 | 12 | 24 | 12 | 12 | 89055
137 | Bhola Aggreko 95MW | 89 | 89 | 89 | 90 | 90 | 89 | 88 | 88 | 86 | 90 | 90 | 91 | 93 | 90 | 90 | 90 | 94 | 52 |  | 58 | 97 | 95 | 97 | 97 | 97 | 95 | 2132343
| Bhola CCPP 194MW | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 174 | 174 | 174 | 172 | 173 | 173 | 173 |  | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 4237315
140 | Bhola (Venture) 33MW | 38 | 36 | 38 | 38 | 35 | 33 | 25 | 23 | 25 | 26 | 26 | 26 | 26 | 27 | 24 | 23 | 21 | 22 |  | 32 | 31 | 34 | 33 | 33 | 32 | 35 | 712184
141 | Bangla Trak Noapara | [19 empty] | 30 | 96 | 95 | 96 | 95 | 94 | 94 | 504960
142 | Noapara (KZA) 40MW | 40 | 32 | 40 | 0 | [6 empty] | 0 | 8 | 32 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 583500
143 | Gopalganj Peaking | 57 | 57 | 52 | 0 | [11 empty] | 11 | 26 | 40 |  | 60 | 63 | 62 | 58 | 56 | 58 | 53 | 594304
144 | Bheramara GT-1,2,3 | [17 empty] | 16 |  | 16 | 16 | 26 | 48 | 48 | 28 | 32 | 188400
145 | Madhumati Power Plant | 88 | 88 | 89 | 88 | 89 | 53 | 53 | 53 | 53 | 55 | 89 | 88 | 87 | 88 | 87 | 88 | 56 | 53 |  | 54 | 78 | 90 | 90 | 90 | 108 | 107 | 1890864
146 | Bheramara HVDC | 929 | 928 | 928 | 928 | 928 | 927 | 928 | 929 | 929 | 929 | 930 | 928 | 929 | 929 | 930 | 929 | 930 | 930 |  | 930 | 929 | 930 | 929 | 930 | 929 | 930 | 22292364
147 | Bheramara 360 MW
148
149
150 | Barapukuria Unit-1
151 | Barapukuria Unit-2 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 70 | 65 | 65 | 65 | 66 | 65 | 63 | 63 | 63 | 63 | 64 |  | 64 | 64 | 64 | 65 | 65 | 65 | 65 | 1625891
152 | Barapukuria Unit-3 | 199 | 199 | 200 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 200 | 199 | 199 |  | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 4843600
153 | Baghabari GT 71MW | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 55 | 55 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 55 | 55 | 55 | 55 | 55 | 55 | 1335000
156 | Baghabari GT 100MW
| Baghabari Peaking 50MW | [16 empty] | 0 | 0 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 287232
157 | Sirajgonj Unit-1 225MW (Gas) | 181 | 184 | 188 | 182 | 189 | 163 | 158 | 166 | 174 | 200 | 190 | 181 | 195 | 192 | 196 | 195 | 195 | 196 |  | 195 | 203 | 199 | 168 | 155 | 157 | 164 | 4644318
158 | Sirajgonj Unit-1 225MW (Oil)
| Sirajgonj Unit-2 225MW (Gas) | 178 | 180 | 184 | 179 | 178 | 155 | 149 | 157 | 161 | 169 | 193 | 185 | 199 | 197 | 200 | 0 | 0 | 35 |  | 117 | 170 | 174 | 154 | 143 | 148 | 155 | 3894227
Sirajgonj Unit-2 225MW (Oil)
159 | Sirajgonj Unit-3 225 MW(Gas) | 189 | 188 | 186 | 190 | 192 | 176 | 171 | 172 | 173 | 195 | 186 | 185 | 196 | 200 | 193 | 188 | 191 | 200 |  | 200 | 200 | 198 | 186 | 176 | 176 | 175 | 4703082
Sirajgonj Unit-3 225 MW(Oil)
160 | Sirajgonj Unit-4 414 MW(Gas) | 400 | 380 | 380 | 380 | 340 | 270 | 270 | 320 | 360 | 360 | 360 | 320 | 350 | 350 | 380 | 380 | 380 | 270 |  | 270 | 315 | 270 | 300 | 350 | 350 | 350 | 8296727
161 | Bera Peaking | [17 empty] | 0 |  | 6 | 17 | 32 | 32 | 33 | 33 | 33 | 150364
162 | Bogra (GBB) | 22 | 22 | 22 | 22 | 22 | 5 | 5 | 5 | 18 | 22 | 22 | 21 | 21 | 21 | 21 | 21 | 21 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 465840
163 | Bogra (EPL) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 13 | 13 | 13 | 13 | 13 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 369180
164 | Ullapara (Summit) | [9 empty] | 3 | 3 | 5 | 5 | 0 | 5 | 8 | 8 | 8 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 102222
165 | Amnura 50MW | 50 | 18 | 0 | [7 empty] | 12 | 12 | 18 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 655000
166 | Katakhali (Northern) | 16 | 0 | [11 empty] | 16 | 16 | 16 | 16 | 16 |  | 16 | 43 | 50 | 50 | 50 | 50 | 50 | 354797
167 | Katakhali Peaking | [17 empty] | 0 |  | 35 | 35 | 39 | 47 | 44 | 43 | 27 | 198900
168 | Santahar Peaking | 35 | 0 | [15 empty] | 0 |  | 27 | 35 | 36 | 35 | 35 | 35 | 35 | 216400
169 | Rajlanka 52 MW | 52 | 52 | 52 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 16 | 50 | 50 | 49 | 16 | 16 |  | 50 | 50 | 50 | 50 | 50 | 50 | 51 | 2710400
170 | Chapainawabganj-100 MW | 91 | 91 | 91 | 61 | 61 | 61 | 61 | 61 | 39 | 0 | [9 empty] | 90 | 95 | 95 | 91 | 92 | 92 | 85 | 1146012
171 | Paramount Baghabari
172 | Confidence Bogura-2 (CPBL) | 108 | 108 | 108 | 108 | 40 | 0 |  |  |  | 19 | 86 | 120 | 15 | 0 |  |  | 75 | 107 |  | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 1573248
173 | Rangpur GT | [19 empty] | 16 | 16 | 16 | 17 | 17 | 17 | 17 | 120000
175 | Saidpur GT | 16 | 16 | 18 | 0 | [15 empty] | 18 | 17 | 17 | 17 | 17 | 17 | 17 | 162000
176 | Confidence Rangpur | [13 empty] | 0 | 0 | 20 | 16 | 36 |  | 38 | 44 | 45 | 0 | 0 | 0 | 0 | 305280
177
178
178 | Western Zone Total | 3513 | 3403 | 3400 | 3198 | 2990 | 2628 | 2604 | 2669 | 2692 | 2739 | 2853 | 2874 | 2892 | 3039 | 3072 | 2934 | 2931 | 2928 | 0 | 3466 | 3881 | 3904 | 3881 | 3909 | 3883 | 3875 | 79660689