## Forecast
8 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2022-08-27 | Saturday
|  |  | Date (day): | 2022-08-27 |  | Saturday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 12930.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14555 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2022-08-26 | 2022-08-27 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 300 | 300 | 300 | 300 |  | 65 | Machine problem
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 90 | 99 | 95 | 99 |  | 9 | Engine problem
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 403 | 405 | 412 | 412
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 333 | 320 | 330 | 330 |  | 30 | Machine problem
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 330 | 330 | 330 | 330 | 120 |  | Dirty fuel
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 8 | 86 | 7 | 90 | 10 |  | Fuel shortage
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 0 | 0 | 0 | 0 |  | 102 | Under maint
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 40 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 19 | 19 | 19
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 94 | 97 | 95 | 95 | 115 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 8 | 95 | 7 | 100 |  |  | Fuel shortage
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 331 | 330 | 335 | 335
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 8 | 93 | 8 | 94 | 8 |  | Fuel shortage
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 54 | 17 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 30 | 108 | 32 | 110 | 39 |  | Fuel shortage
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 55 | 17 | 55 |  |  | Fuel shortage
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 35 | 35 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 44 | 51 | 50 | 50 |  | 30 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 32 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 8 | 40 | 8 | 42 |  | 10 | Engine problem
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 260 | 260 | 275 | 275 |  | 25 | Engine problem
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 120 | 152 | 245 | 245
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 50 | 90 | 90 | 90 |  |  | Engine problem
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 50 | 90 | 80 | 90 |  |  | Engine problem
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 147 | 149 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 17 | 105 | 17 | 105 |  |  | Fuel shortage
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 4 | 92 | 0 | 90 | 14 |  | Fuel shortage
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 35 | 162 | 35 | 162 |  |  | Fuel shortage
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 34 | 0 | 30 | 0
| 40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 16 | 17 | 55 |  |  | Fuel shortage
|  | Dhaka area Total |  |  |  |  | 6263 | 5847 | 3059 | 3933 | 3336 | 4132 | 692 | 951
| 41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 110 | 110 | 110 | 110 | 70 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 25 | 25 | 25 | 25
| 43 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 12 | 0 | 20 | 0
| 44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 26 | 38 | 25 | 38 |  | 12 | Engine problem
| 45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 144 | 148 | 144 | 144 |  | 86 | Low Water Level
| 46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | S/D due to HGPI
| 47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
| 48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 52 | 105 | 52 | 105
| 49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 34 | 26 | 26 | 34 | 64 |  | Fuel shortage
| 50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 17 | 51 | 17 | 51 | 51 |  | Fuel shortage
| 51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 10 | 10 | 10 | 10 | 90 |  | Fuel shortage
| 52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 10 | 10 | 10 | 10 |  | 90 | Fuel shortage
| 53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 17 | 17 | 17 |  | 5 | Engine problem
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 33 | 42 | 20 | 30
| 54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 12 | 93 | 12 | 95 | 13 |  | Fuel shortage
| 55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 1 | 0 | 5 | 0
| 56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 52 | 52 | 51 | 51 | 249 |  | Fuel shortage
| 57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 36 | 54 | 34 | 34 |  |  | Engine problem
| 58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 110 | 110 | 110 | 110
| 59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 10 | 10 | 10 | 10 | 90 |  | Fuel shortage
| 60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 107 | 107 | 107 | 107 |  | 9 | Engine problem
|  | Mirsharai 150 MW |  | Gas/HSD | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 818 | 1008 | 805 | 981 | 807 | 577
| 61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 203 | 205 | 205 | 205
| 63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 330 | 310 | 330 | 310
| 64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 310 | 310 | 310 | 310
|  | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+136*1 | 284 | 284 | 0 | 0 | 0 | 0 |  |  | On test.
| 65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 40 | 39 | 40 | 40 |  | 5 | Engine problem
| 66 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 55 | 55 | 54 | 55 | 55
| 67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 122 | 124 | 130 | 142 |  | 8 | Engine problem
| 70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 31 | 39 | 32 | 42 |  | 10 | Engine problem
| 71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 88 | 90 | 90 |  | 73 | Machine problem
| 72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 68 | 179 | 68 | 200 |  |  | Fuel shortage
| 73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 19 | 22 | 22
| 74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 10 | 9 | 10 | 10
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 134 | 158 | 143 | 165
| 75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25
| 76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 8 | 0 | 8 | 44 |  | Fuel shortage
| 77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 17 | 17 | 18 | 18 |  | 7 | Engine problem
| 78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 30 | 100 | 200 | 200
| 79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 17 | 0 | 34 | 80 |  | Fuel shortage
| 80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 98 | 112 | 98 | 113 |  |  | Fuel shortage
| 81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 35 | 35 | 35 | 35 |  | 19 | 33 kV feeder fault
| 82 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 74 | 96 | 96 | 96 | 19 |  | Fuel shortage
|  | Cumilla Area Total |  |  |  |  | 3193 | 3169 | 1680 | 2003 | 1966 | 2179 | 464 | 122
| 83 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 104 | 136 | 105 | 140 | 62 |  | Gas shortage
| 84 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  |  | Engine problem
| 85 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0 |  | 8 | Under maint.
| 86 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1 | 0 | 1.6 | 0
| 87 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 113 | 95 | 115 | 115 | 85 |  | Fuel shortage
| 88 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 87 | 107 | 88 | 107 |  | 8 | Engine problem
| 89 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 15 | 0 | 50 | 0
| 90 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 10 | 12 | 12 | 12 |  | 10 | Engine problem
|  | Mymensingh Area Total |  |  |  |  | 717 | 614 | 330 | 350 | 371.6 | 374 | 62 | 26
| 91 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 43 | 43 | 43 |  | 27 | Machine problem.
| 92 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 |  | 60 | Machine problem
| 93 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 | 163 |  | Gas shortage
| 94 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
| 95 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 5 | 5 | 5 | 5 | 46 |  | Gas shortage
| 96 | Fenchuganj 44MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 0 | 0 | 5 | 5 | 45 |  | Gas shortage
| 97 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0
| 98 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 55 | 58 | 60 | 60
| 99 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 10 | 81 | 10 | 80
| 100 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
| 101 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 194 | 194 | 193 | 194 |  | 37 | Machine problem
| 102 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Gas shortage
| 103 | Sylhet 50MW PP (EPL) |  | Gas | NENP | 27*2 | 50 | 50 | 6 | 6 | 6 | 6 | 44 |  | Gas shortage
| 104 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 8 | 8 | 8 | 8 | 17 |  | Gas shortage
| 105 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 290 | 290 | 300 |  |  | FGMO
| 106 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 384 | 403 | 400 | 400
| 107 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| 108 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 392 | 400 | 400 | 400
|  | Sylhet Area Total |  |  |  |  | 2522 | 2477 | 1447 | 1528 | 1460 | 1541 | 335 | 554
| 109 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 894 | 893 | 911 | 911 |  |  | .
| 110 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 0 | 16 | 0 | 0 | 115 |  | Fuel shortage
| 111 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 41 | 0 | 41 |  | 13 | Engine problem
| 112 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 210 | 221 | 225 | 225
| 113 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 54 | 30 | 70 |  | 39 | Engine problem
| 114 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 280 | 285 | 280 | 285 | 125 |  | Gas shortage
| 115 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 0 | 0 | 0 | 40 |  | Fuel shortage
| 116 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 93 | 93 |  | 7 | Engine problem
| 117 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 17 | 17 | 17 | 88 |  | Fuel shortage
| 118 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 15 | 50 | 15 | 50 | 55 |  | Fuel shortage
| 119 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 100 | 0 | 100 | 0
|  | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
|  | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
|  | Khulna Area Total |  |  |  |  | 2388 | 2384 | 1499 | 1577 | 1671 | 1692 | 439 | 59
| 120 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 16 | 16 | 32 | 48 |  |  | Line O/L
| 121 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 17 | 34 | 20 | 30 |  | 10 | Engine problem
| 122 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 83 | 84 | 85 | 85 |  |  | Machine problem
|  | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
| 123 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 710 | 1050 | 1170 | 1170 |  |  | Line O/L
| 124 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 223 | 220 | 220 | 220
| 125 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 0 | 17 |  |  | Line O/L
|  | Barisal Area Total |  |  |  |  | 1958 | 1958 | 1049 | 1404 | 1527 | 1570 | 0 | 10
| 126 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 127 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 24 | 24 | 24 | 32 |  | 20 | Engine problem
| 128 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 30 | 0 | 40 |  | 31 | Engine problem
| 129 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 130 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage
| 131 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 32 | 0 | 32 |  | 18 | Engine problem
| 132 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 205 | 205 | 200 | 200 | 10 |  | Gas shortage
| 133 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 138 | 196 | 220 | 220
| 134 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 208 | 210 | 210 | 200 | 20 |  | Gas shortage
| 135 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 414 | 416 | 410 | 410 | 4 |  | Gas shortage
| 136 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 0 |  | 50 | Under maintenance
| 137 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 20 | 21 | 22 | 22
| 138 | Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 139 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 140 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 16 | 8 | 16 | 36 |  | Fuel shortage
| 141 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 74 | 35 | 80 |  | 24 | Engine problem
| 142 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 38 | 150 | 180 |  | 20 | Engine problem
| 143 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 50 | 94 | 50 | 94 |  | 19 | Engine problem
| 144 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 55 | 95 | 55 | 95 |  | 18 | Engine problem
| 145 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2129 | 1138 | 1462 | 1401 | 1632 | 291 | 200
| 146 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 78 | 81 | 80 | 80
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
| 147 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 250 | 250 | 250 | 250 | 24
| 148 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
| 149 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
| 150 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 56 | 91 | 55 | 90 |  | 23 | Engine problem
| 151 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 4 | 0 | 8 | 0
| 152 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 0 | 90 | 0 | 34 |  | 81 | Fuel shortage
|  | Intraco Solar 30 MW |  | Solar | IPP | 0 | 0 | 0 | 22 | 0 | 0 | 0
|  | Rangpur Area Total |  |  |  |  | 800 | 720 | 410 | 512 | 393 | 454 | 64 | 189
|  | Total |  |  |  |  | 22482 | 21680 | 11430 | 13777 | 12930.6 | 14555 | 3154 | 2688
| A. |  | 2022-08-26 | (Yesterday) |  |  |  |  | Friday
| 1 | Highest Generation : |  |  | 13855 | MW at | 23:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 11149 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 14112 | MW
| 3 | Day peak Generation : |  |  | 11430 | MW at | 11:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 13701.11 | MW
| 4 | Evening peak Generation : |  |  | 13777 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 309 | MW
| 5 | Total Energy Generation : |  | 310.8928 | MKWHr | By Solar | 1.3825 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
|  | By Gas : | 155.6499 | MKWHr |  | By Oil: | 94.2447 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 31.485 | MKWHr |  | By Hydro: | 3.4588 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 3154 | MW | Dhaka | 4682.74 | 4636.74 |  | 46 |  | 18:00 |  | 146
|  |  |  | For Plants S/D or M/C prob = |  |  | 2688 | MW | Chittagong | 1292.93 | 1292.93 |  | 0 |  | 19:00 |  | 341.9043
|  |  |  | Total = |  |  | 5842 | MW | Khulna | 1684.8 | 1684.8 |  | 0 |  | 19:30 |  | 328.0807
| 7 | Total Gas Supplied : |  |  | 1136.52 | MMCFD |  |  | Rajshahi | 1456.9 | 1456.9 |  | 0 |  | 20:00 |  | 330.8454
| 8 | Fuel Cost : | i) Gas : | Taka | 176420622.53 | ii) Oil : | Taka | 1350772089.22 | Comilla | 1398 | 1378 |  | 20 |  | 21:00 |  | 309
|  |  | iii) Coal : |  | 255320111.32 | Total | Taka | 1782512823.07 | Mymensingh | 1218 | 996 |  | 222 |  | 22:00 |  | 281
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0 | MKWHr. | Sylhet | 619 | 619 |  | 0 |  | 23:00 |  | 318
|  | ii) During Peak Demand : |  |  | 170 | MW (E to W) at | 21:00 | hrs | Barisal | 406.74 | 406.74 |  | 0 |  | 24:00 |  | 977
|  | iii) Maximum : |  |  | 170 | MW at | 21:00 | hrs | Rangpur | 942 | 921 |  | 21
| 10 | Maximum Temperature in Dhaka was |  |  |  | 35° C |  |  | Total | 13701.11 | 13392.11 |  | 309
| B. |  | 2022-08-27 | (Today) |  |  |  | Saturday |  |  | Probable max. temperature in Dhaka |  |  | 33.8° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 14400 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14555 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 11800 | MW
| 4 | Reserve(Generation end) |  |  |  | 155 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 323.1221 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 11380 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.5942 | MKWHr. | ii) HVDC Flow at Peak Time |  | 893 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.0778 | MKWHr. | iii) Maximum HVDC Flow : |  | 895 | MW at | 19:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 95.29 |  | (b) Today: | 95.27 |  | (c) Rule Curve: |  | 97.35
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2022-08-26
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 300 | 100 | 0 | 401 | 317 |  | 0 | 300 | 0 | 23 | 0 | 55 | 335 | 0 | 97 | 8 | 8 | 90 | 0 | 0 | 0 | 0 | 23 | 35 | 35 | 19 | 25 | 26 | 33 | 33 | 8 | 0 | 75 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 34 | 34 | 10 | 12 | 25 | 17 | 37 | 0 | 0 | 0 | 310 | 305 | 206 | 8 | 0 | 41 | 55 | 0 | 51 | 0 | 40 | 0 | 22 | 10 | 25 | 20 | 120 | 158 | 0 | 0 | 0 | 43 | 30 | 5 | 0 | 0 | 0 | 63 | 81 | 0 | 193 | 0 | 6 | 10 | 320 | 8 | 0 | 195 | 276 | 246 | 80 | 105 | 70 | 140 | 0 | 10 | 128 | 143 | 402 | 98 | 17 | 68 | 0 | 52 | 34 | 92 | 17 | 95 | 10 | 393 | 0 | 0 | 35 | 107 | 0 | 35 | 0 | 96 | 55 | 0 | 0 | 0 |  | 892 | 0 | 270 | 0 | 0 | 226 | 0 | 0 | 10 | 46 | 0 | 84 | 30 | 48 | 0 | 0 | 0 | 24 | 31 | 0 | 0 | 42 | 24 | 8 | 0 | 22 | 0 | 11 | 81 | 0 | 240 | 0 | 0 | 205 | 0 | 0 | 211 | 0 | 89 | 209 | 0 | 415 | 0 | 167 | 50 | 15 | 56 | 0 | 0 | 95 | 1090 | 224 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 |  | 8041 | 4949 | 12990 | 4584 | 892 | 1981 | 847 | 2240 | 1411 | 145 | 437 | 544 | 120 | 0 | 562.1608 | 95.29
2:00 | 0 | 0 | 0 | 180 | 300 | 100 | 0 | 403 | 319 |  | 0 | 300 | 0 | 9 | 0 | 55 | 335 | 0 | 92 | 8 | 8 | 90 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 25 | 26 | 33 | 33 | 8 | 0 | 75 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 34 | 17 | 10 | 12 | 25 | 17 | 38 | 0 | 0 | 0 | 310 | 310 | 207 | 8 | 0 | 41 | 55 | 0 | 51 | 0 | 40 | 0 | 22 | 10 | 25 | 20 | 120 | 160 | 0 | 0 | 0 | 43 | 30 | 5 | 0 | 0 | 0 | 65 | 50 | 0 | 193 | 0 | 6 | 10 | 280 | 8 | 0 | 100 | 276 | 246 | 80 | 105 | 70 | 146 | 0 | 10 | 85 | 142 | 402 | 98 | 17 | 68 | 0 | 52 | 34 | 92 | 17 | 95 | 10 | 400 | 0 | 0 | 35 | 107 | 0 | 35 | 0 | 96 | 55 | 0 | 0 | 0 |  | 893 | 0 | 270 | 0 | 0 | 225 | 0 | 0 | 5 | 46 | 0 | 86 | 29 | 32 | 0 | 0 | 0 | 24 | 31 | 0 | 0 | 42 | 0 | 8 | 0 | 22 | 0 | 11 | 81 | 0 | 240 | 0 | 0 | 204 | 0 | 0 | 217 | 0 | 40 | 212 | 0 | 422 | 0 | 120 | 50 | 15 | 56 | 0 | 0 | 95 | 1060 | 224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 7817 | 4760 | 12577 | 4602 | 893 | 1919 | 656 | 2132 | 1381 | 145 | 442 | 504 | 120 | 0 | 666.2987 | 95.29
3:00 | 0 | 0 | 0 | 180 | 300 | 100 | 0 | 404 | 327 |  | 0 | 300 | 0 | 7 | 0 | 55 | 335 | 0 | 97 | 8 | 8 | 90 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 25 | 26 | 33 | 33 | 8 | 0 | 75 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 34 | 17 | 10 | 12 | 25 | 17 | 38 | 0 | 0 | 0 | 310 | 305 | 205 | 8 | 0 | 41 | 55 | 0 | 51 | 0 | 39 | 0 | 22 | 10 | 25 | 20 | 116 | 160 | 0 | 0 | 0 | 43 | 30 | 5 | 0 | 0 | 0 | 65 | 40 | 0 | 193 | 0 | 6 | 10 | 290 | 8 | 0 | 100 | 278 | 242 | 80 | 105 | 70 | 143 | 0 | 10 | 85 | 137 | 403 | 99 | 17 | 68 | 0 | 53 | 34 | 93 | 17 | 89 | 10 | 396 | 0 | 0 | 35 | 107 | 0 | 35 | 0 | 96 | 55 | 0 | 0 | 0 |  | 892 | 0 | 275 | 0 | 0 | 225 | 0 | 0 | 0 | 46 | 0 | 85 | 27 | 32 | 0 | 0 | 0 | 24 | 31 | 0 | 0 | 42 | 0 | 8 | 0 | 22 | 0 | 11 | 80 | 0 | 240 | 0 | 0 | 206 | 0 | 0 | 216 | 0 | 10 | 211 | 0 | 419 | 0 | 50 | 50 | 15 | 56 | 0 | 0 | 95 | 1060 | 224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 7801 | 4652 | 12453 | 4603 | 892 | 1922 | 552 | 2121 | 1380 | 145 | 441 | 497 | 116 | 0 | 504.1015 | 95.29
4:00 | 0 | 0 | 0 | 180 | 300 | 100 | 0 | 404 | 333 |  | 0 | 300 | 0 | 8 | 0 | 55 | 335 | 0 | 97 | 8 | 8 | 90 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 25 | 26 | 33 | 33 | 8 | 0 | 75 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 34 | 17 | 10 | 11 | 25 | 17 | 39 | 0 | 0 | 0 | 325 | 320 | 204 | 8 | 0 | 41 | 56 | 0 | 51 | 0 | 39 | 0 | 22 | 10 | 25 | 20 | 128 | 157 | 0 | 0 | 0 | 43 | 30 | 5 | 0 | 0 | 0 | 63 | 20 | 0 | 193 | 0 | 6 | 10 | 290 | 8 | 0 | 100 | 278 | 100 | 80 | 105 | 70 | 149 | 0 | 10 | 85 | 130 | 402 | 99 | 17 | 68 | 0 | 52 | 34 | 93 | 17 | 95 | 10 | 395 | 0 | 0 | 35 | 107 | 0 | 35 | 0 | 96 | 55 | 0 | 0 | 0 |  | 892 | 0 | 280 | 0 | 0 | 224 | 0 | 0 | 0 | 40 | 0 | 86 | 26 | 32 | 0 | 0 | 0 | 24 | 31 | 0 | 0 | 42 | 0 | 8 | 0 | 22 | 0 | 11 | 79 | 0 | 240 | 0 | 0 | 205 | 0 | 0 | 217 | 0 | 10 | 210 | 0 | 419 | 0 | 20 | 50 | 15 | 56 | 0 | 0 | 95 | 1050 | 224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 7685 | 4608 | 12293 | 4629 | 892 | 1909 | 380 | 2125 | 1369 | 145 | 441 | 492 | 128 | 0 | 467.2385 | 95.29
5:00 | 0 | 0 | 0 | 180 | 300 | 100 | 0 | 404 | 321 |  | 0 | 300 | 0 | 8 | 0 | 55 | 335 | 0 | 96 | 8 | 8 | 90 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 25 | 26 | 33 | 33 | 8 | 0 | 75 | 70 | 110 | 0 | 17 | 0 | 0 | 0 | 0 |  | 12 | 34 | 17 | 10 | 12 | 25 | 17 | 39 | 0 | 0 | 0 | 310 | 305 | 205 | 8 | 0 | 41 | 56 | 0 | 51 | 0 | 33 | 0 | 22 | 10 | 25 | 20 | 132 | 157 | 0 | 0 | 0 | 43 | 30 | 5 | 0 | 0 | 0 | 63 | 20 | 0 | 193 | 0 | 6 | 10 | 300 | 8 | 0 | 150 | 278 | 150 | 80 | 105 | 70 | 149 | 0 | 10 | 85 | 132 | 402 | 99 | 17 | 76 | 0 | 52 | 34 | 92 | 17 | 95 | 10 | 395 | 0 | 0 | 35 | 107 | 0 | 35 | 0 | 96 | 55 | 0 | 0 | 0 |  | 892 | 0 | 280 | 0 | 0 | 225 | 0 | 0 | 0 | 27 | 0 | 86 | 25 | 32 | 0 | 0 | 0 | 24 | 31 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 80 | 0 | 240 | 0 | 0 | 205 | 0 | 0 | 200 | 0 | 0 | 209 | 0 | 422 | 0 | 0 | 50 | 15 | 56 | 0 | 0 | 95 | 1050 | 224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 7753 | 4509 | 12262 | 4598 | 892 | 1909 | 450 | 2085 | 1370 | 145 | 425 | 456 | 132 | 0 | 449.7286 | 95.29
6:00 | 0 | 0 | 0 | 180 | 300 | 100 | 0 | 403 | 322 |  | 0 | 300 | 0 | 7 | 0 | 55 | 335 | 0 | 96 | 8 | 8 | 15 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 25 | 19 | 33 | 33 | 8 | 0 | 75 | 70 | 110 | 0 | 18 | 0 | 0 | 0 | 0 |  | 12 | 34 | 17 | 10 | 12 | 26 | 17 | 39 | 0 | 0 | 0 | 325 | 315 | 205 | 8 | 0 | 37 | 56 | 0 | 51 | 0 | 40 | 0 | 22 | 10 | 25 | 20 | 126 | 158 | 0 | 0 | 0 | 43 | 30 | 5 | 0 | 0 | 0 | 59 | 10 | 0 | 193 | 0 | 6 | 10 | 290 | 8 | 0 | 0 | 278 | 0 | 40 | 105 | 30 | 149 | 0 | 10 | 85 | 135 | 404 | 99 | 17 | 105 | 0 | 52 | 34 | 84 | 17 | 94 | 10 | 400 | 0 | 1 | 35 | 107 | 0 | 35 | 1 | 96 | 34 | 0 | 0 | 0 |  | 893 | 0 | 280 | 0 | 0 | 226 | 0 | 0 | 0 | 0 | 0 | 86 | 21 | 32 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 80 | 0 | 240 | 0 | 0 | 206 | 0 | 0 | 201 | 0 | 0 | 209 | 0 | 372 | 0 | 0 | 50 | 15 | 56 | 0 | 0 | 0 | 970 | 224 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 |  | 7302 | 4228 | 11530 | 4616 | 893 | 1836 | 70 | 1993 | 1290 | 145 | 427 | 331 | 126 | 4 | 340.0612 | 95.29
7:00 | 0 | 0 | 0 | 180 | 280 | 91 | 0 | 403 | 328 |  | 0 | 300 | 0 | 8 | 0 | 55 | 337 | 0 | 97 | 8 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 25 | 19 | 33 | 33 | 8 | 0 | 75 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 34 | 17 | 10 | 12 | 26 | 17 | 42 | 0 | 0 | 0 | 310 | 305 | 207 | 8 | 0 | 37 | 56 | 0 | 51 | 0 | 31 | 0 | 22 | 10 | 25 | 20 | 120 | 138 | 0 | 0 | 0 | 43 | 30 | 5 | 0 | 0 | 0 | 56 | 10 | 0 | 193 | 0 | 6 | 10 | 290 | 8 | 0 | 0 | 263 | 0 | 0 | 105 | 0 | 149 | 3 | 10 | 85 | 135 | 404 | 99 | 17 | 105 | 0 | 52 | 34 | 102 | 17 | 104 | 10 | 398 | 0 | 11 | 35 | 107 | 0 | 35 | 5 | 96 | 34 | 0 | 0 | 0 |  | 892 | 0 | 280 | 0 | 0 | 226 | 0 | 0 | 0 | 0 | 0 | 85 | 18 | 16 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 79 | 0 | 240 | 0 | 0 | 205 | 0 | 0 | 182 | 0 | 0 | 211 | 0 | 421 | 0 | 0 | 50 | 15 | 56 | 0 | 1 | 0 | 790 | 224 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 5 |  | 7191 | 4073 | 11264 | 4551 | 892 | 1882 | 0 | 1998 | 1109 | 145 | 408 | 304 | 120 | 37 | 291.2177 | 95.29
8:00 | 0 | 0 | 0 | 180 | 300 | 98 | 0 | 404 | 332 |  | 0 | 300 | 0 | 8 | 0 | 55 | 335 | 0 | 60 | 8 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 25 | 19 | 33 | 33 | 8 | 0 | 74 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 34 | 17 | 10 | 12 | 26 | 17 | 42 | 0 | 0 | 0 | 330 | 320 | 205 | 8 | 0 | 38 | 56 | 0 | 51 | 0 | 31 | 0 | 22 | 10 | 25 | 18 | 120 | 108 | 0 | 0 | 1 | 43 | 30 | 5 | 0 | 0 | 0 | 58 | 10 | 0 | 193 | 0 | 6 | 10 | 280 | 8 | 0 | 0 | 278 | 0 | 0 | 114 | 0 | 147 | 5 | 10 | 85 | 130 | 403 | 88 | 17 | 66 | 2 | 52 | 34 | 110 | 17 | 107 | 10 | 390 | 17 | 23 | 35 | 107 | 0 | 35 | 15 | 96 | 34 | 0 | 0 | 0 |  | 892 | 0 | 275 | 0 | 0 | 226 | 0 | 0 | 0 | 0 | 0 | 85 | 19 | 16 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 20 | 0 | 11 | 80 | 0 | 243 | 0 | 0 | 205 | 0 | 0 | 155 | 0 | 0 | 209 | 0 | 323 | 0 | 0 | 50 | 15 | 56 | 0 | 2 | 0 | 770 | 224 | 0 | 0 | 3 | 38 | 0 | 0 | 0 | 0 | 10 |  | 7190 | 3959 | 11149 | 4521 | 892 | 1784 | 0 | 1993 | 1093 | 144 | 381 | 277 | 120 | 99 | #REF! | 95.29
9:00 | 0 | 0 | 0 | 180 | 300 | 94 | 0 | 405 | 324 |  | 0 | 300 | 0 | 8 | 0 | 55 | 335 | 0 | 97 | 8 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 17 | 35 | 19 | 25 | 19 | 33 | 33 | 8 | 0 | 74 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 11 | 34 | 17 | 10 | 12 | 26 | 17 | 42 | 0 | 0 | 0 | 310 | 305 | 206 | 8 | 0 | 35 | 55 | 0 | 51 | 0 | 31 | 0 | 22 | 10 | 25 | 17 | 122 | 105 | 0 | 0 | 1 | 43 | 30 | 5 | 0 | 0 | 0 | 55 | 10 | 0 | 193 | 0 | 6 | 10 | 300 | 8 | 0 | 0 | 278 | 0 | 0 | 114 | 0 | 149 | 8 | 10 | 85 | 127 | 402 | 88 | 17 | 52 | 2 | 52 | 34 | 110 | 17 | 105 | 10 | 395 | 0 | 13 | 35 | 107 | 0 | 23 | 23 | 96 | 34 | 0 | 0 | 0 |  | 892 | 0 | 280 | 0 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 85 | 19 | 16 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 20 | 0 | 11 | 79 | 0 | 250 | 0 | 0 | 204 | 0 | 0 | 130 | 0 | 0 | 210 | 0 | 403 | 0 | 0 | 50 | 15 | 56 | 0 | 3 | 55 | 720 | 224 | 0 | 0 | 3 | 67 | 0 | 0 | 0 | 0 | 18 |  | 7133 | 4047 | 11180 | 4524 | 892 | 1871 | 0 | 1983 | 1049 | 144 | 335 | 252 | 122 | 138 | #REF! | 95.29
10:00 | 0 | 0 | 0 | 180 | 300 | 95 | 0 | 406 | 329 |  | 0 | 320 | 0 | 8 | 0 | 55 | 335 | 0 | 95 | 8 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 17 | 35 | 19 | 25 | 19 | 33 | 33 | 8 | 0 | 74 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 7 | 34 | 17 | 10 | 12 | 26 | 17 | 33 | 0 | 0 | 0 | 310 | 305 | 204 | 8 | 0 | 38 | 53 | 0 | 51 | 0 | 31 | 0 | 22 | 10 | 25 | 17 | 126 | 105 | 0 | 0 | 1 | 43 | 30 | 5 | 0 | 0 | 0 | 55 | 10 | 0 | 194 | 0 | 6 | 10 | 290 | 8 | 0 | 0 | 273 | 0 | 0 | 114 | 0 | 149 | 10 | 10 | 68 | 122 | 403 | 88 | 17 | 52 | 2 | 51 | 34 | 110 | 17 | 97 | 10 | 394 | 0 | 31 | 35 | 107 | 0 | 33 | 29 | 75 | 0 | 0 | 0 | 0 |  | 892 | 0 | 280 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 85 | 17 | 16 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 20 | 0 | 11 | 79 | 0 | 250 | 0 | 0 | 205 | 0 | 0 | 130 | 0 | 0 | 211 | 0 | 417 | 0 | 0 | 50 | 15 | 55 | 0 | 4 | 55 | 720 | 225 | 0 | 0 | 4 | 89 | 0 | 0 | 0 | 0 | 17 |  | 7084 | 4069 | 11153 | 4527 | 892 | 1889 | 0 | 1897 | 1049 | 144 | 320 | 252 | 126 | 187 | #REF! | 95.29
11:00 | 0 | 0 | 0 | 180 | 300 | 90 | 0 | 403 | 333 |  | 0 | 330 | 0 | 8 | 0 | 40 | 331 | 0 | 94 | 8 | 8 | 30 | 0 | 0 | 0 | 0 | 17 | 17 | 35 | 0 | 25 | 19 | 33 | 33 | 8 | 0 | 74 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 10 | 34 | 17 | 10 | 12 | 26 | 17 | 33 | 0 | 0 | 0 | 330 | 310 | 203 | 8 | 0 | 40 | 55 | 0 | 51 | 0 | 31 | 0 | 22 | 10 | 25 | 17 | 134 | 104 | 0 | 0 | 1 | 43 | 30 | 5 | 0 | 0 | 0 | 55 | 10 | 0 | 194 | 0 | 6 | 10 | 310 | 8 | 0 | 30 | 260 | 120 | 50 | 113 | 50 | 147 | 12 | 10 | 68 | 122 | 384 | 87 | 17 | 52 | 1 | 52 | 36 | 110 | 17 | 98 | 10 | 392 | 4 | 15 | 35 | 107 | 0 | 35 | 34 | 74 | 0 | 0 | 0 | 0 |  | 894 | 0 | 280 | 0 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 83 | 17 | 16 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 20 | 0 | 11 | 78 | 0 | 250 | 0 | 0 | 205 | 0 | 0 | 138 | 0 | 0 | 208 | 0 | 414 | 0 | 0 | 50 | 15 | 56 | 0 | 4 | 55 | 710 | 223 | 0 | 0 | 5 | 100 | 0 | 0 | 0 | 0 | 22 |  | 7334 | 4096 | 11430 | 4499 | 894 | 1915 | 250 | 1878 | 1038 | 144 | 348 | 274 | 134 | 194 | #REF! | 95.29
12:00 | 0 | 0 | 0 | 180 | 300 | 90 | 0 | 400 | 318 |  | 0 | 330 | 0 | 7 | 0 | 40 | 329 | 0 | 0 | 8 | 8 | 32 | 0 | 0 | 0 | 0 | 17 | 17 | 35 | 0 | 25 | 16 | 33 | 33 | 8 | 0 | 70 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 17 | 10 | 12 | 26 | 17 | 24 | 0 | 0 | 0 | 310 | 305 | 204 | 8 | 0 | 39 | 54 | 0 | 51 | 0 | 29 | 0 | 22 | 10 | 25 | 17 | 96 | 72 | 0 | 0 | 2 | 43 | 30 | 5 | 0 | 0 | 0 | 55 | 10 | 0 | 194 | 0 | 6 | 10 | 285 | 8 | 0 | 110 | 260 | 158 | 80 | 105 | 80 | 46 | 5 | 10 | 68 | 120 | 402 | 97 | 17 | 52 | 3 | 52 | 36 | 110 | 17 | 105 | 10 | 393 | 17 | 52 | 58 | 107 | 0 | 2 | 36 | 75 | 0 | 0 | 0 | 0 |  | 893 | 0 | 270 | 0 | 0 | 219 | 0 | 0 | 0 | 0 | 0 | 83 | 20 | 16 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 18 | 0 | 11 | 80 | 0 | 250 | 0 | 0 | 205 | 0 | 0 | 188 | 0 | 2 | 206 | 0 | 414 | 0 | 31 | 50 | 15 | 55 | 0 | 5 | 55 | 740 | 223 | 0 | 0 | 5 | 76 | 0 | 0 | 0 | 0 | 30 |  | 7218 | 4192 | 11410 | 4347 | 893 | 1866 | 461 | 1788 | 1070 | 140 | 407 | 316 | 96 | 214 | #REF! | 95.29
13:00 | 0 | 0 | 0 | 180 | 300 | 93 | 0 | 403 | 318 |  | 0 | 330 | 0 | 8 | 0 | 45 | 331 | 0 | 94 | 8 | 8 | 32 | 0 | 0 | 0 | 0 | 35 | 17 | 35 | 19 | 25 | 18 | 33 | 33 | 8 | 0 | 70 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 17 | 10 | 12 | 26 | 17 | 32 | 0 | 0 | 0 | 310 | 305 | 204 | 8 | 0 | 39 | 54 | 0 | 51 | 0 | 29 | 0 | 22 | 10 | 25 | 17 | 96 | 67 | 0 | 0 | 2 | 43 | 30 | 5 | 0 | 0 | 0 | 60 | 10 | 0 | 193 | 0 | 6 | 10 | 280 | 8 | 0 | 80 | 270 | 100 | 50 | 106 | 57 | 140 | 18 | 10 | 68 | 118 | 404 | 96 | 17 | 78 | 3 | 52 | 41 | 110 | 17 | 105 | 10 | 393 | 17 | 34 | 72 | 107 | 0 | 18 | 33 | 74 | 0 | 0 | 0 | 0 |  | 892 | 0 | 275 | 0 | 0 | 218 | 0 | 0 | 0 | 0 | 0 | 83 | 20 | 16 | 0 | 0 | 0 | 24 | 5 | 0 | 0 | 0 | 0 | 8 | 0 | 16 | 0 | 11 | 79 | 0 | 249 | 0 | 0 | 205 | 0 | 0 | 195 | 0 | 50 | 205 | 0 | 417 | 0 | 100 | 50 | 15 | 55 | 0 | 6 | 55 | 760 | 216 | 0 | 0 | 4 | 71 | 0 | 0 | 0 | 0 | 32 |  | 7382 | 4332 | 11714 | 4472 | 892 | 1866 | 437 | 1974 | 1088 | 140 | 413 | 328 | 96 | 203 | 264 | 95.29
14:00 | 0 | 0 | 0 | 180 | 300 | 93 | 0 | 403 | 318 |  | 0 | 330 | 0 | 8 | 0 | 55 | 322 | 0 | 95 | 8 | 8 | 32 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 19 | 25 | 20 | 33 | 32 | 8 | 0 | 73 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 17 | 10 | 12 | 26 | 17 | 32 | 0 | 0 | 0 | 340 | 325 | 197 | 8 | 0 | 39 | 54 | 0 | 51 | 0 | 35 | 0 | 21 | 9 | 25 | 17 | 100 | 69 | 0 | 0 | 2 | 43 | 30 | 5 | 0 | 0 | 0 | 59 | 10 | 0 | 194 | 0 | 6 | 10 | 270 | 8 | 0 | 10 | 278 | 11 | 80 | 108 | 25 | 145 | 12 | 10 | 68 | 115 | 396 | 96 | 17 | 87 | 2 | 52 | 54 | 110 | 17 | 105 | 10 | 380 | 17 | 30 | 106 | 107 | 0 | 21 | 26 | 92 | 0 | 0 | 0 | 0 |  | 894 | 0 | 275 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 81 | 20 | 16 | 0 | 0 | 0 | 24 | 6 | 0 | 0 | 0 | 0 | 8 | 0 | 16 | 0 | 11 | 80 | 0 | 249 | 0 | 0 | 205 | 0 | 0 | 161 | 0 | 10 | 204 | 0 | 414 | 0 | 10 | 50 | 15 | 55 | 0 | 6 | 55 | 790 | 218 | 0 | 0 | 4 | 78 | 0 | 0 | 0 | 0 | 27 |  | 7338 | 4152 | 11490 | 4484 | 894 | 1855 | 146 | 2091 | 1119 | 143 | 331 | 301 | 100 | 187 | 286 | 0
15:00 | 0 | 0 | 0 | 180 | 300 | 90 | 0 | 399 | 318 |  | 0 | 330 | 0 | 8 | 0 | 55 | 327 | 0 | 95 | 8 | 8 | 32 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 19 | 25 | 17 | 33 | 32 | 8 | 0 | 38 | 70 | 110 | 0 | 22 | 0 | 0 | 0 | 0 |  | 5 | 26 | 17 | 10 | 12 | 26 | 17 | 27 | 0 | 0 | 0 | 320 | 310 | 201 | 8 | 0 | 37 | 52 | 0 | 51 | 0 | 37 | 0 | 21 | 9 | 25 | 17 | 138 | 68 | 0 | 0 | 1 | 43 | 30 | 5 | 0 | 0 | 0 | 55 | 10 | 0 | 194 | 0 | 6 | 10 | 300 | 8 | 0 | 150 | 268 | 211 | 80 | 102 | 80 | 27 | 9 | 10 | 68 | 115 | 404 | 96 | 17 | 89 | 1 | 52 | 54 | 110 | 17 | 104 | 10 | 380 | 16 | 30 | 108 | 107 | 0 | 35 | 20 | 96 | 0 | 0 | 0 | 0 |  | 894 | 0 | 270 | 0 | 0 | 215 | 0 | 0 | 0 | 0 | 0 | 82 | 23 | 16 | 0 | 0 | 0 | 24 | 6 | 0 | 0 | 0 | 0 | 8 | 0 | 16 | 0 | 11 | 80 | 0 | 250 | 0 | 0 | 205 | 0 | 0 | 178 | 0 | 10 | 201 | 0 | 414 | 0 | 48 | 50 | 15 | 54 | 0 | 4 | 55 | 790 | 216 | 0 | 0 | 3 | 65 | 0 | 0 | 0 | 0 | 21 |  | 7591 | 4224 | 11815 | 4445 | 894 | 1876 | 579 | 1966 | 1120 | 108 | 393 | 320 | 138 | 154 | 309 | 0
16:00 | 0 | 0 | 0 | 180 | 300 | 91 | 0 | 404 | 318 |  | 0 | 330 | 0 | 8 | 0 | 55 | 327 | 0 | 95 | 8 | 8 | 32 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 19 | 25 | 18 | 33 | 15 | 8 | 0 | 74 | 70 | 110 | 0 | 24 | 0 | 0 | 0 | 0 |  | 8 | 26 | 17 | 10 | 12 | 26 | 17 | 29 | 0 | 0 | 0 | 320 | 305 | 200 | 8 | 0 | 37 | 52 | 0 | 51 | 0 | 37 | 0 | 21 | 9 | 25 | 17 | 136 | 85 | 0 | 0 | 1 | 43 | 30 | 5 | 0 | 0 | 0 | 55 | 10 | 0 | 194 | 0 | 6 | 10 | 275 | 8 | 0 | 70 | 255 | 161 | 80 | 103 | 80 | 10 | 5 | 10 | 68 | 117 | 404 | 96 | 48 | 105 | 0 | 52 | 54 | 110 | 17 | 102 | 10 | 382 | 17 | 26 | 108 | 107 | 0 | 25 | 14 | 86 | 0 | 0 | 0 | 0 |  | 894 | 0 | 270 | 0 | 0 | 217 | 0 | 0 | 0 | 0 | 0 | 80 | 20 | 16 | 0 | 0 | 0 | 24 | 26 | 0 | 0 | 0 | 0 | 8 | 0 | 16 | 0 | 11 | 81 | 0 | 250 | 0 | 0 | 205 | 0 | 0 | 187 | 0 | 10 | 201 | 0 | 414 | 0 | 30 | 65 | 15 | 55 | 0 | 3 | 90 | 790 | 201 | 0 | 0 | 2 | 37 | 0 | 0 | 0 | 0 | 0 |  | 7464 | 4218 | 11682 | 4445 | 894 | 1836 | 431 | 2021 | 1121 | 144 | 404 | 349 | 136 | 88 | 281 | 0
17:00 | 0 | 0 | 0 | 180 | 300 | 95 | 0 | 406 | 318 |  | 0 | 330 | 0 | 16 | 0 | 55 | 322 | 0 | 92 | 8 | 8 | 32 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 17 | 33 | 32 | 8 | 0 | 75 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 7 | 26 | 17 | 10 | 12 | 33 | 17 | 29 | 0 | 0 | 0 | 320 | 305 | 202 | 8 | 0 | 38 | 53 | 0 | 51 | 0 | 37 | 0 | 21 | 9 | 25 | 17 | 118 | 98 | 0 | 0 | 0 | 43 | 30 | 5 | 0 | 0 | 0 | 56 | 10 | 0 | 194 | 0 | 6 | 10 | 265 | 8 | 0 | 0 | 258 | 0 | 0 | 104 | 0 | 128 | 1 | 10 | 127 | 117 | 404 | 96 | 90 | 105 | 0 | 52 | 54 | 110 | 17 | 103 | 10 | 385 | 17 | 10 | 116 | 107 | 0 | 32 | 5 | 95 | 0 | 0 | 0 | 0 |  | 894 | 0 | 270 | 0 | 0 | 177 | 0 | 0 | 19 | 2 | 0 | 70 | 18 | 16 | 0 | 0 | 0 | 24 | 25 | 0 | 0 | 0 | 0 | 8 | 0 | 17 | 0 | 11 | 81 | 0 | 250 | 0 | 0 | 205 | 0 | 0 | 130 | 0 | 0 | 203 | 0 | 414 | 0 | 0 | 95 | 15 | 90 | 0 | 2 | 95 | 790 | 195 | 0 | 0 | 1 | 11 | 0 | 0 | 0 | 0 | 7 |  | 7334 | 4135 | 11469 | 4467 | 894 | 1824 | 0 | 2374 | 1121 | 145 | 307 | 312 | 118 | 37 | 213 | 0
18:00 | 0 | 0 | 0 | 180 | 300 | 70 | 0 | 408 | 267 |  | 0 | 330 | 0 | 72 | 0 | 55 | 330 | 0 | 34 | 8 | 8 | 32 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 17 | 0 | 32 | 40 | 0 | 75 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 7 | 28 | 17 | 10 | 19 | 38 | 17 | 38 | 0 | 0 | 0 | 280 | 280 | 204 | 8 | 0 | 39 | 53 | 0 | 51 | 0 | 37 | 1 | 0 | 9 | 25 | 17 | 128 | 95 | 0 | 0 | 0 | 43 | 30 | 5 | 0 | 0 | 0 | 56 | 10 | 0 | 194 | 0 | 6 | 10 | 260 | 8 | 0 | 0 | 268 | 0 | 0 | 103 | 0 | 149 | 0 | 10 | 140 | 117 | 375 | 96 | 105 | 105 | 0 | 52 | 54 | 68 | 17 | 85 | 10 | 390 | 39 | 1 | 144 | 92 | 0 | 35 | 1 | 72 | 0 | 0 | 0 | 0 |  | 894 | 0 | 275 | 0 | 0 | 120 | 0 | 0 | 40 | 40 | 0 | 76 | 19 | 16 | 0 | 0 | 0 | 24 | 24 | 0 | 0 | 0 | 0 | 8 | 0 | 18 | 0 | 0 | 80 | 0 | 250 | 0 | 0 | 170 | 0 | 0 | 130 | 0 | 0 | 170 | 0 | 328 | 3 | 0 | 50 | 50 | 52 | 0 | 1 | 50 | 770 | 195 | 0 | 0 | 0 | 2 | 34 | 0 | 0 | 0 | 1 |  | 7202 | 3890 | 11092 | 4208 | 894 | 1668 | 0 | 2451 | 1100 | 145 | 250 | 372 | 128 | 6 | 146 | 0
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 300 | 98 | 0 | 403 | 334 |  | 0 | 330 | 0 | 84 | 0 | 55 | 331 | 0 | 95 | 8 | 93 | 112 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 19 | 33 | 32 | 40 | 0 | 75 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 10 | 34 | 51 | 10 | 65 | 38 | 17 | 38 | 0 | 0 | 0 | 310 | 310 | 205 | 8 | 91 | 39 | 52 | 0 | 51 | 0 | 37 | 8 | 0 | 9 | 25 | 17 | 146 | 106 | 0 | 0 | 0 | 43 | 30 | 5 | 0 | 0 | 0 | 56 | 81 | 0 | 194 | 0 | 6 | 10 | 280 | 8 | 0 | 100 | 276 | 105 | 85 | 104 | 90 | 149 | 0 | 10 | 155 | 119 | 403 | 97 | 105 | 105 | 0 | 52 | 54 | 94 | 17 | 94 | 10 | 400 | 89 | 0 | 158 | 107 | 0 | 35 | 0 | 74 | 0 | 0 | 0 | 0 |  | 895 | 0 | 285 | 0 | 16 | 178 | 0 | 0 | 40 | 44 | 0 | 77 | 27 | 16 | 0 | 0 | 0 | 24 | 24 | 60 | 0 | 0 | 32 | 16 | 0 | 21 | 0 | 8 | 82 | 0 | 250 | 0 | 0 | 195 | 0 | 0 | 147 | 0 | 0 | 191 | 0 | 415 | 17 | 7 | 70 | 50 | 91 | 0 | 0 | 95 | 830 | 200 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 |  | 8492 | 4437 | 12929 | 4566 | 895 | 1956 | 387 | 2889 | 1162 | 145 | 325 | 605 | 146 | 0 | 341.9043 | 0
19:30 | 0 | 0 | 0 | 180 | 300 | 98 | 0 | 408 | 335 |  | 0 | 330 | 0 | 84 | 0 | 55 | 328 | 0 | 95 | 60 | 93 | 112 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 26 | 33 | 32 | 40 | 0 | 75 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 51 | 10 | 93 | 38 | 17 | 38 | 0 | 0 | 0 | 310 | 310 | 202 | 8 | 91 | 39 | 52 | 0 | 51 | 0 | 37 | 8 | 14 | 9 | 22 | 17 | 152 | 105 | 0 | 0 | 0 | 43 | 30 | 5 | 0 | 0 | 0 | 55 | 81 | 0 | 194 | 0 | 6 | 10 | 300 | 8 | 0 | 30 | 260 | 104 | 90 | 95 | 90 | 149 | 0 | 10 | 180 | 119 | 404 | 106 | 105 | 105 | 0 | 52 | 54 | 110 | 17 | 112 | 10 | 392 | 90 | 0 | 162 | 107 | 0 | 35 | 0 | 96 | 0 | 0 | 0 | 0 |  | 895 | 0 | 285 | 0 | 16 | 218 | 0 | 0 | 50 | 45 | 0 | 83 | 30 | 16 | 0 | 0 | 0 | 24 | 24 | 60 | 0 | 0 | 32 | 16 | 0 | 21 | 0 | 8 | 81 | 0 | 250 | 0 | 0 | 206 | 0 | 0 | 197 | 0 | 0 | 210 | 0 | 414 | 17 | 20 | 94 | 50 | 90 | 0 | 0 | 95 | 900 | 220 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 0 | 0 |  | 8605 | 4739 | 13344 | 4610 | 895 | 1999 | 334 | 3102 | 1231 | 145 | 415 | 658 | 152 | 0 | 328.0807 | 0
20:00 | 0 | 0 | 0 | 180 | 300 | 98 | 0 | 408 | 328 |  | 0 | 330 | 0 | 84 | 0 | 55 | 330 | 0 | 97 | 93 | 93 | 108 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 26 | 33 | 32 | 40 | 0 | 84 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 51 | 10 | 93 | 38 | 17 | 38 | 0 | 0 | 0 | 310 | 310 | 204 | 8 | 91 | 39 | 52 | 0 | 51 | 0 | 39 | 8 | 19 | 9 | 25 | 17 | 148 | 104 | 0 | 0 | 0 | 43 | 30 | 5 | 0 | 0 | 0 | 61 | 81 | 0 | 194 | 0 | 6 | 10 | 290 | 8 | 0 | 30 | 260 | 54 | 90 | 95 | 90 | 149 | 0 | 10 | 180 | 119 | 404 | 107 | 105 | 105 | 0 | 52 | 54 | 110 | 17 | 111 | 10 | 396 | 92 | 0 | 162 | 107 | 0 | 35 | 0 | 96 | 1 | 0 | 0 | 0 |  | 894 | 0 | 285 | 0 | 16 | 220 | 0 | 0 | 41 | 55 | 0 | 84 | 30 | 16 | 0 | 0 | 0 | 24 | 24 | 74 | 0 | 0 | 32 | 16 | 0 | 21 | 0 | 11 | 82 | 0 | 250 | 0 | 0 | 205 | 0 | 0 | 197 | 0 | 0 | 210 | 0 | 416 | 17 | 20 | 94 | 50 | 90 | 0 | 0 | 95 | 1030 | 220 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 0 | 0 |  | 8600 | 4891 | 13491 | 4636 | 894 | 1984 | 284 | 3138 | 1362 | 154 | 417 | 671 | 148 | 0 | 330.8454 | 0
21:00 | 0 | 0 | 0 | 180 | 300 | 99 | 0 | 405 | 320 |  | 0 | 330 | 0 | 86 | 0 | 55 | 330 | 0 | 97 | 95 | 93 | 108 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 26 | 33 | 32 | 40 | 0 | 78 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 51 | 10 | 93 | 38 | 17 | 42 | 0 | 0 | 0 | 310 | 310 | 205 | 8 | 88 | 39 | 54 | 0 | 51 | 0 | 39 | 8 | 19 | 9 | 25 | 17 | 158 | 136 | 0 | 0 | 0 | 43 | 30 | 5 | 0 | 0 | 0 | 58 | 81 | 0 | 194 | 0 | 6 | 10 | 290 | 8 | 0 | 100 | 260 | 152 | 90 | 95 | 90 | 149 | 0 | 10 | 179 | 124 | 403 | 107 | 105 | 105 | 0 | 52 | 54 | 110 | 17 | 112 | 10 | 400 | 92 | 0 | 162 | 107 | 0 | 35 | 0 | 96 | 16 | 0 | 0 | 0 |  | 893 | 0 | 285 | 0 | 16 | 221 | 0 | 0 | 41 | 54 | 0 | 84 | 34 | 16 | 0 | 0 | 0 | 24 | 30 | 74 | 0 | 0 | 32 | 16 | 0 | 21 | 0 | 11 | 81 | 0 | 250 | 0 | 0 | 205 | 0 | 0 | 196 | 0 | 0 | 210 | 0 | 416 | 17 | 38 | 94 | 50 | 91 | 0 | 0 | 95 | 1050 | 220 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 0 |  | 8822 | 4955 | 13777 | 4663 | 893 | 1987 | 470 | 3181 | 1381 | 148 | 417 | 675 | 158 | 0 | 309 | 0
22:00 | 0 | 0 | 0 | 180 | 300 | 99 | 0 | 403 | 324 |  | 0 | 330 | 0 | 92 | 0 | 55 | 327 | 0 | 98 | 95 | 93 | 78 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 26 | 33 | 33 | 40 | 0 | 74 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 7 | 26 | 51 | 10 | 93 | 38 | 17 | 42 | 0 | 0 | 0 | 335 | 330 | 202 | 8 | 91 | 40 | 55 | 0 | 51 | 0 | 40 | 8 | 21 | 9 | 25 | 17 | 162 | 150 | 0 | 0 | 0 | 43 | 30 | 5 | 0 | 0 | 0 | 55 | 81 | 0 | 194 | 0 | 6 | 10 | 280 | 8 | 0 | 100 | 276 | 154 | 90 | 96 | 90 | 149 | 0 | 10 | 179 | 128 | 404 | 107 | 105 | 105 | 0 | 52 | 54 | 110 | 17 | 111 | 10 | 390 | 91 | 0 | 162 | 107 | 0 | 35 | 0 | 96 | 17 | 0 | 0 | 0 |  | 894 | 0 | 285 | 0 | 16 | 221 | 0 | 0 | 41 | 53 | 0 | 83 | 30 | 26 | 0 | 0 | 0 | 24 | 30 | 74 | 0 | 0 | 32 | 8 | 0 | 22 | 0 | 11 | 82 | 0 | 250 | 0 | 0 | 204 | 0 | 0 | 180 | 0 | 0 | 211 | 0 | 414 | 17 | 20 | 94 | 50 | 90 | 0 | 0 | 95 | 1070 | 220 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 0 |  | 8858 | 4937 | 13795 | 4709 | 894 | 1977 | 454 | 3203 | 1402 | 144 | 401 | 629 | 162 | 0 | 281 | 95.27
23:00 | 0 | 0 | 0 | 180 | 300 | 99 | 0 | 404 | 324 |  | 0 | 330 | 0 | 92 | 0 | 55 | 332 | 0 | 92 | 95 | 92 | 78 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 19 | 25 | 26 | 0 | 33 | 41 | 0 | 74 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 10 | 26 | 51 | 10 | 75 | 38 | 17 | 42 | 0 | 0 | 0 | 310 | 305 | 205 | 8 | 90 | 40 | 54 | 0 | 51 | 0 | 38 | 8 | 21 | 9 | 25 | 17 | 166 | 148 | 0 | 0 | 0 | 43 | 30 | 5 | 0 | 0 | 0 | 56 | 81 | 0 | 193 | 0 | 6 | 10 | 305 | 8 | 0 | 180 | 276 | 254 | 90 | 96 | 89 | 149 | 0 | 10 | 178 | 127 | 402 | 107 | 105 | 105 | 0 | 52 | 54 | 110 | 17 | 111 | 10 | 400 | 91 | 0 | 162 | 107 | 0 | 35 | 0 | 96 | 17 | 0 | 0 | 0 |  | 894 | 0 | 285 | 0 | 16 | 223 | 0 | 0 | 31 | 50 | 0 | 84 | 35 | 32 | 0 | 0 | 0 | 24 | 24 | 52 | 0 | 0 | 32 | 8 | 0 | 22 | 0 | 11 | 82 | 0 | 250 | 0 | 0 | 201 | 0 | 0 | 184 | 0 | 5 | 210 | 0 | 418 | 17 | 25 | 94 | 15 | 91 | 0 | 0 | 95 | 1100 | 222 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 0 | 0 |  | 8951 | 4904 | 13855 | 4631 | 894 | 2012 | 643 | 3120 | 1432 | 144 | 407 | 590 | 166 | 0 | 318 | 95.27
24:00 | 0 | 0 | 0 | 180 | 300 | 99 | 0 | 400 | 323 |  | 0 | 330 | 0 | 17 | 0 | 45 | 335 | 0 | 92 | 95 | 8 | 93 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 19 | 25 | 26 | 10 | 33 | 8 | 0 | 74 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 51 | 10 | 11 | 30 | 17 | 42 | 0 | 0 | 0 | 310 | 305 | 207 | 8 | 90 | 40 | 55 | 0 | 51 | 0 | 38 | 8 | 21 | 9 | 25 | 17 | 160 | 151 | 0 | 0 | 0 | 43 | 30 | 5 | 0 | 0 | 0 | 64 | 81 | 0 | 193 | 0 | 6 | 10 | 280 | 8 | 0 | 140 | 276 | 12 | 80 | 97 | 70 | 149 | 0 | 10 | 117 | 127 | 400 | 106 | 17 | 105 | 0 | 52 | 54 | 110 | 17 | 97 | 10 | 400 | 91 | 0 | 69 | 107 | 0 | 35 | 0 | 96 | 17 | 0 | 0 | 0 |  | 894 | 0 | 285 | 0 | 0 | 225 | 0 | 0 | 20 | 56 | 0 | 85 | 35 | 32 | 0 | 0 | 0 | 24 | 24 | 30 | 0 | 0 | 24 | 8 | 0 | 22 | 0 | 11 | 82 | 0 | 250 | 0 | 0 | 202 | 0 | 0 | 199 | 0 | 85 | 212 | 0 | 423 | 0 | 121 | 50 | 15 | 56 | 0 | 0 | 55 | 1080 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 8116 | 4825 | 12941 | 4655 | 894 | 1990 | 508 | 2368 | 1412 | 144 | 424 | 585 | 160 | 0 | 977 | 95.27
KWH | 0 | 0 | 0 | 4274550 | 7149018 | 2237273 | 0 | 9836550 | 7688000 |  | 0 | 7471750 | 0 | 695040 | 0 | 1292208 | 8045613 | 0 | 2180000 | 664330 | 603072 | 1320480 | 0 | 0 | 0 | 0 | 774720 | 896773 | 882669 | 392868 | 600000 | 497340 | 702000 | 748500 | 368640 | 0 | 1766765 | 1692000 | 2700000 | 0 | 588321 | 0 | 0 | 0 | 0 |  | 259920 | 701424 | 624565 | 259320 | 659520 | 708960 | 403776 | 898560 | 0 | 0 | 0 | 7949100 | 7556000 | 4936000 | 200727 | 470820 | 921888 | 1301760 | 0 | 1194689 | 0 | 853896 | 54811 | 446442 | 215640 | 600900 | 455780 | 3077760 | 2767680 | 0 | 0 | 14700 | 1023000 | 720000 | 13140 | 0 | 0 | 0 | 1381440 | 864960 | 0 | 4690780 | 0 | 167680 | 241740 | 7110000 | 179808 | 0 | 1870656 | 6506070 | 2789733 | 1367461 | 2522400 | 1262548 | 3201696 | 81540 | 263040 | 2610720 | 3024290 | 9600000 | 2335200 | 1094400 | 2079199 | 15959 | 1254545 | 1087285 | 2521634 | 424080 | 2445240 | 249600 | 9351200 | 724800 | 324640 | 1955520 | 2570564 | 0 | 785160 | 243593 | 2171520 | 522000 | 0 | 0 | 0 |  | 21594181 | 0 | 6665760 | 0 | 69120 | 5118257 | 0 | 0 | 268320 | 546432 | 0 | 2011108 | 578929 | 557664 | 0 | 0 | 0 | 558736 | 388653 | 365744 | 0 | 173216 | 178258 | 214565 | 0 | 460080 | 0 | 248940 | 1896872 | 0 | 5991800 | 0 | 0 | 5253209 | 0 | 0 | 4481836 | 0 | 447360 | 5228636 | 0 | 9818072 | 96000 | 1087084 | 1620000 | 597600 | 15532608 | 0 | 48652 | 1603296 | 23596300 | 5198209 | 0 | 0 | 37140 | 616320 | 491904 | 0 | 0 | 0 | 0 |  | 187251959 | 123640861 | 310892820 | 110204346 | 21594181 | 45445569 | 8824842 | 70013240 | 31484972 | 3458765 | 9600093 | 5806508 | 3077760 | 1382544 | 0
Fuel Cost | 0 | 0 | 0 | 6369079.5 | 8006900.16 | 2975573.09 | 0 | 10328377.5 | 8303040 |  | 0 | 8144207.5 | 0 | 7770547.2 | 0 | 17121756 | 9011086.56 | 0 | 3815000 | 9712504.6 | 8485223.04 | 21404980.8 | 0 | 0 | 0 | 0 | 9854438.4 | 12106435.5 | 11836591.29 | 294651 | 450000 | 0 | 0 | 0 | 6270566.4 | 0 | 477026.55 | 456840 | 5103000 | 0 | 9619048.35 | 0 | 0 | 0 | 0 |  | 3391956 | 11699752.32 | 10630096.3 | 3503413.2 | 8362713.6 | 8202667.2 | 512795.52 | 2992204.8 | 0 | 0 | 0 | 8823501 | 8236040 | 5725760 | 258937.83 | 574400.4 | 1041733.44 | 1939622.4 | 0 | 1995130.63 | 0 | 14746783.92 | 737207.95 | 611625.54 | 161730 | 1051575 | 341835 | 22098316.8 | 3016771.2 | 0 | 0 | 234318 | 1401510 | 950400 | 22863.6 | 0 | 0 | 0 | 2679993.6 | 1972108.8 | 0 | 4737687.8 | 0 | 249843.2 | 478645.2 | 7110000 | 134856 | 0 | 39208949.76 | 88807855.5 | 58472803.68 | 28265418.87 | 34001952 | 26096867.16 | 44343489.6 | 953202.6 | 2714572.8 | 35662435.2 | 40132328.3 | 8832000 | 28396032 | 15825024 | 26301867.35 | 0 | 14728358.3 | 11840533.65 | 26804969.42 | 5754765.6 | 31519143.6 | 2940288 | 8603104 | 9386160 | 4691048 | 24815548.8 | 29253018.32 | 0 | 10254189.6 | 2910936.35 | 32507654.4 | 6874740 | 0 | 0 | 0 |  | 64782543 | 0 | 7465651.2 | 0 | 719539.2 | 84451240.5 | 0 | 0 | 4832443.2 | 9835776 | 0 | 2252440.96 | 1123122.26 | 6078537.6 | 0 | 0 | 0 | 9370002.72 | 6797540.97 | 5720236.16 | 0 | 2868456.96 | 3014342.78 | 2924520.95 | 0 | 952365.6 | 0 | 188447.58 | 11020826.32 | 0 | 31696622 | 0 | 0 | 6093722.44 | 0 | 0 | 78252856.56 | 0 | 9385612.8 | 6065217.76 | 0 | 9719891.28 | 1290240 | 22796151.48 | 19164600 | 8635320 | 197264121.6 | 0 | 537604.6 | 19464013.44 | 212602663 | 5302173.18 | 0 | 0 | 420053.4 | 7229433.6 | 7540888.32 | 0 | 0 | 0 | 0 |  | 1019444926.55 | 867859219.42 | 1887304145.97 | 122880893.16 | 64782543 | 53539729.37 | 184225803.75 | 905790233.24 | 255320111.32 | 933866.55 | 162704097.06 | 98051955.17 | 22098316.8 | 16976596.55 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 300 | 90 | 0 | 403 | 333 |  | 0 | 330 | 0 | 8 | 0 | 40 | 331 | 0 | 94 | 8 | 8 | 30 | 0 | 0 | 0 | 0 | 17 | 17 | 35 | 0 | 25 | 19 | 33 | 33 | 8 | 0 | 74 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 10 | 34 | 17 | 10 | 12 | 26 | 17 | 33 | 0 | 0 | 0 | 330 | 310 | 203 | 8 | 0 | 40 | 55 | 0 | 51 | 0 | 31 | 0 | 22 | 10 | 25 | 17 | 134 | 104 | 0 | 0 | 1 | 43 | 30 | 5 | 0 | 0 | 0 | 55 | 10 | 0 | 194 | 0 | 6 | 10 | 310 | 8 | 0 | 30 | 260 | 120 | 50 | 113 | 50 | 147 | 12 | 10 | 68 | 122 | 384 | 87 | 17 | 52 | 1 | 52 | 36 | 110 | 17 | 98 | 10 | 392 | 4 | 15 | 35 | 107 | 0 | 35 | 34 | 74 | 0 | 0 | 0 | 0 |  | 894 | 0 | 280 | 0 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 83 | 17 | 16 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 20 | 0 | 11 | 78 | 0 | 250 | 0 | 0 | 205 | 0 | 0 | 138 | 0 | 0 | 208 | 0 | 414 | 0 | 0 | 50 | 15 | 56 | 0 | 4 | 55 | 710 | 223 | 0 | 0 | 5 | 100 | 0 | 0 | 0 | 0 | 22 |  | 11430 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 300 | 99 | 0 | 405 | 320 | 0 | 0 | 330 | 0 | 86 | 0 | 55 | 330 | 0 | 97 | 95 | 93 | 108 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 26 | 33 | 32 | 40 | 0 | 78 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 12 | 26 | 51 | 10 | 93 | 38 | 17 | 42 | 0 | 0 | 0 | 310 | 310 | 205 | 8 | 88 | 39 | 54 | 0 | 51 | 0 | 39 | 8 | 19 | 9 | 25 | 17 | 158 | 136 | 0 | 0 | 0 | 43 | 30 | 5 | 0 | 0 | 0 | 58 | 81 | 0 | 194 | 0 | 6 | 10 | 290 | 8 | 0 | 100 | 260 | 152 | 90 | 95 | 90 | 149 | 0 | 10 | 179 | 124 | 403 | 107 | 105 | 105 | 0 | 52 | 54 | 110 | 17 | 112 | 10 | 400 | 92 | 0 | 162 | 107 | 0 | 35 | 0 | 96 | 16 | 0 | 0 | 0 |  | 893 | 0 | 285 | 0 | 16 | 221 | 0 | 0 | 41 | 54 | 0 | 84 | 34 | 16 | 0 | 0 | 0 | 24 | 30 | 74 | 0 | 0 | 32 | 16 | 0 | 21 | 0 | 11 | 81 | 0 | 250 | 0 | 0 | 205 | 0 | 0 | 196 | 0 | 0 | 210 | 0 | 416 | 17 | 38 | 94 | 50 | 91 | 0 | 0 | 95 | 1050 | 220 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 0 |  | 13777 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 300 | 99 | 0 | 412 | 330 | 0 | 0 | 330 | 0 | 90 | 0 | 55 | 335 | 0 | 95 | 100 | 94 | 110 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 25 | 33 | 33 | 42 | 0 | 74 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 12 | 34 | 51 | 10 | 95 | 38 | 17 | 30 | 0 | 0 | 0 | 310 | 310 | 205 | 8 | 90 | 40 | 55 | 0 | 51 | 0 | 42 | 8 | 22 | 10 | 25 | 18 | 165 | 140 | 0 | 0 | 0 | 43 | 30 | 5 | 5 | 0 | 0 | 60 | 80 | 0 | 194 | 0 | 6 | 10 | 300 | 8 | 0 | 200 | 275 | 245 | 90 | 115 | 90 | 149 | 0 | 10 | 200 | 142 | 400 | 107 | 105 | 105 | 0 | 51 | 34 | 110 | 34 | 113 | 10 | 400 | 90 | 0 | 162 | 107 | 0 | 35 |  | 96 | 55 |  |  |  |  | 911 | 0 | 285 | 0 | 0 | 225 | 0 | 0 | 41 | 70 | 0 | 85 | 30 | 48 | 0 | 0 | 0 | 32 | 40 | 80 | 0 | 0 | 32 | 16 | 0 | 22 | 0 | 11 | 80 | 0 | 250 | 0 | 0 | 200 | 0 | 0 | 220 | 0 | 93 | 200 | 0 | 410 | 17 | 180 | 94 | 50 | 90 | 0 | 0 | 95 | 1170 | 220 |  | 17 |  |  | 34
Forecast for Day | 0 | 0 | 0 | 180 | 300 | 95 | 0 | 412 | 330 | 0 | 0 | 330 | 0 | 7 | 0 | 55 | 335 | 0 | 95 | 7 | 8 | 32 | 0 | 0 | 0 | 0 | 17 | 17 | 35 | 19 | 25 | 25 | 33 | 33 | 8 | 0 | 74 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 12 | 26 | 17 | 10 | 12 | 25 | 17 | 20 | 0 | 0 | 0 | 330 | 310 | 205 | 8 | 90 | 40 | 55 | 0 | 51 | 0 | 32 | 0 | 22 | 10 | 25 | 18 | 143 | 105 | 0 | 0 | 1.6 | 43 | 30 | 5 | 5 | 0 | 0 | 60 | 10 | 0 | 193 | 0 | 6 | 10 | 290 | 8 | 0 | 200 | 275 | 245 | 90 | 115 | 80 | 149 | 20 | 10 | 68 | 130 | 400 | 88 | 17 | 52 | 5 | 51 | 34 | 110 | 0 | 98 | 10 | 400 | 0 | 50 | 35 | 107 | 0 | 35 | 30 | 96 | 17 |  |  |  |  | 911 | 0 | 280 | 0 | 0 | 225 | 0 | 0 | 0 | 30 | 0 | 85 | 20 | 32 | 0 | 0 | 0 | 24 | 0 | 35 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 80 | 0 | 250 | 0 | 0 | 200 | 0 | 0 | 220 | 0 | 93 | 210 | 0 | 410 | 17 | 150 | 50 | 15 | 55 | 0 | 8 | 55 | 1170 | 220 |  | 0 | 6 | 100 | 0
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 300 | 95 | 0 | 407 | 330 | 0 | 0 | 330 | 0 | 7 | 0 | 55 | 338 | 0 | 97 | 7 | 8 | 15 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 25 | 26 | 33 | 33 | 8 | 0 | 70 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 12 | 26 | 17 | 10 | 11 | 25 | 17 | 0 | 0 | 0 | 0 | 310 | 310 | 207 | 8 | 31 | 41 | 52 | 0 | 51 | 0 | 38 | 0 | 19 | 9 | 25 | 17 | 136 | 122 | 0 | 0 | 0 | 43 | 30 | 5 | 5 | 0 | 0 | 61 | 10 | 0 | 193 | 0 | 6 | 10 | 280 | 0 | 0 | 10 | 265 | 58 | 25 | 97 | 31 | 123 | 4 | 10 | 85 | 122 | 401 | 107 | 17 | 69 | 0 | 52 | 54 | 110 | 0 | 88 | 10 | 400 | 0 | 4 | 35 | 107 | 0 | 35 | 9 | 93 | 17 | 0 | 0 | 0 | 0 | 894 | 0 | 280 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 83 | 21 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 81 | 0 | 250 | 0 | 0 | 201 | 0 | 0 | 146 | 0 | 30 | 214 | 0 | 425 | 18 | 4 | 50 | 15 | 56 | 0 | 2 | 55 | 820 | 165 | 0 | 0 | 1 | 26 | 0 | 0 | 0 | 0 | 11 | 0 |  |  |  |  | 94244683 |  | 0
94244683
| Minimum Generation |  | 11149 | 8:00
| Highest Generation |  | 13855 | 23:00
| Day Peak Generation |  | 11430 | 11:00
| Evening Peak Generation |  | 13777 | 21:00
| HVDC Max Flow |  | 895 | 19:00
| HVDC EvPeak Flow |  | 893 | 21:00
| Load factor L.F |  | 93.5% | [161 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2022-08-27
Till now the maximum generation is : - |  |  | 14782 | 21:00 | Hrs on | 2022-04-16
The Summary of Yesterday's |  | 2022-08-26 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 11430 | MW Hour : | 11:00 | Min. Gen. at | 8:00 | 11380 | MW
Evening Peak Generation : |  | 13777 | MW Hour : | 21:00 | Available Max Generation : |  | 14555 | MW
E.P. Demand (at gen end) : |  | 14112 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 14400 | MW
Maximum Generation : |  | 13855 | MW Hour : | 23:00 | Reserve(Generation end) |  | 155 | MW
Total Gen. (MKWH) : |  | 310.8928 | System Load Factor : | 93.5% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | 170 | MW at | 21:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2022-08-27
Actual : | 95.27 | Ft.(MSL) , | Rule curve : | 97.35 | Ft.( MSL )
Gas Consumed : | Total = | 1136.52 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 176420622.53
: |  | Coal : | 255320111.32 | Oil : | 1350772089.22 | Total : | 1782512823.07
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 46 | 1104:00 | 4611.5613 |  |  | 0 | 0.7174%
Chittagong Area | 0 | 0:00 | 1305.8349 |  |  | 0 | 2.981%
Khulna Area | 0 | 0:00 | 1723.8613 |  |  | 0 | 3.393%
Rajshahi Area | 0 | 0:00 | 1530.1094 |  |  | 0 | 3.973%
Cumilla Area | 20 | 480:00 | 1301.8537 |  |  | 0 | 3.636%
Mymensingh Area | 222 | 5328:00 | 1076.2521 |  |  | 0 | 4.189%
Sylhet Area | 0 | 0:00 | 480.3986 |  |  | 0 | 3.001%
Barisal Area | 0 | 0:00 | 391.4851 |  |  | 0 | 1.271%
Rangpur Area | 21 | 504:00 | 849.3235 |  |  | 0 | 4.132%
Total | 309 |  | 13270.68 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-2
2) Ghorasal-3,4
3) Ashuganj-5
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
7) Sikalbaha 225 MW
8) Shajibazar 330 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Kabirpur-Kodda 132 kV Ckt-2 tripped at 11:10 from both ends showing Dist. at Kabirpur end & | [5 empty] | About 235 MW power interruption occurred under
Dist. Z1, 2.18 km at Kodda end and was switched on at 11:26. | [5 empty] | Kodda & Rajendrapur S/S area from 11:10 to 11:26.
b) Siddhirganj GT-1 tripped at 11:43 due to problem with control system and GT-2 was synchronized at 12:26.
c) Khulna(S)-Rampal 230 kV Ckt-1 was under shut down from 10:15 to 16:35 for C/M.
d) Khulna(S)-Rampal 230 kV Ckt-2 was under shut down from 10:32 to 16:08 for C/M.
e) Kabirpur-Kodda 132 kV Ckt-2 tripped at 14:15 from both ends showing Dist. Z1, T-φ at Kabirpur end & | [5 empty] | About 208 MW power interruption occurred under
Dist. Z1 at Kodda end and was switched on at 17:59. | [5 empty] | Kodda & Rajendrapur S/S area from 14:15 to 14:33.
f) Chandpur 150 MW GT was synchronized at 18:33.
g) Gollamari 132/33 kV T-1 transformer was shutdown at 07:07(27/08/2022) for C/M.
h) Faridpur-Gopalganj 132 kV Ckt-1 was shutdown at 07:43(27/08/2022) for D/W.
| Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2022-08-26 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4274550
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 300 | 7149018 | Machine problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 99 | 2237273 | Engine problem
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 405 | 9836550
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 320 | 7688000 | Machine problem
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 330 | 7471750 | Dirty gas
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 86 | 695040 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 0 | 0 | Under maint.
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 55 | 1292208
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 392868 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 97 | 2180000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 95 | 664330
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 330 | 8045613
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 93 | 603072 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 774720
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 108 | 1320480 | Engine problem
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 896773
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 882669 | Engine problem
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 51 | 1097340 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 702000
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 32 | 748500
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 40 | 368640 | #REF!
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 260 | 6506070 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 152 | 2789733 | Low demand
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 90 | 1367461 | Engine problem
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 90 | 1262548 | Engine problem
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 3201696
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 1094400
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 92 | 724800 | Engine problem
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 1955520
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 243593
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 16 | 522000 | Engine problem
| Dhaka area Total |  |  |  | 5847 | 3933 | 78989215
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 110 | 2700000 | Machine problem
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 25 | 588321
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 81540
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 38 | 708960 | Engine problem
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 148 | 3458765 | Low water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | HGPI for 30 days.
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 105 | 2079199
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 26 | 701424 | Fuel shortage
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 624565 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 10 | 259320 | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 10 | 263040 | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 17 | 403776 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 42 | 898560
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 93 | 659520 | Engine problem
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 15959
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 52 | 1254545 | Fuel shortage
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1087285
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 110 | 2521634
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 10 | 249600 | Engine problem
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 107 | 2570564 | Engine problem
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Chattogram area Total |  |  |  | 2382 | 1008 | 21126577
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 205 | 4936000 | #REF!
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 310 | 7949100 | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 310 | 7556000 | FGMO
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+136*1 | 284 | 0 | 0 | On test.
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 39 | 921888 | Engine problem
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 54 | 1301760
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 200727 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1194689
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 124 | 3024290 | Engine problem
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 39 | 853896 | Engine problem
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 88 | 470820 | Machine problem
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 179 | 2610720 | Line O/L
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 446442
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 9 | 215640
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 158 | 3077760
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 25 | 600900 | Engine problem
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 8 | 54811 | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 17 | 455780 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 100 | 1870656 | Low demand
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 17 | 424080 | Fuel shortage
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 112 | 2445240
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 35 | 785160 | 33 kV feeder problem.
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 96 | 2171520 | Engine problem
| Cumilla Area Total |  |  |  | 3169 | 2003 | 43567879
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 136 | 2767680 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 0 | Gas shortage
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 14700
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 95 | 2522400 | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 107 | 2335200 | Engine problem
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 324640
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 259920 | Engine problem
| Mymensingh Area Total |  |  |  | 614 | 350 | 8224540
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1023000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 720000 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Gas shortage
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 5 | 13140 | Gas shortage
| Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 0 | 0 | Gas shortage
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 0 | 0 | Engine problem
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 58 | 1381440
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 864960
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 194 | 4690780 | Machine problem
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50MW PP (EPL) |  | NENP | 27*2 | 50 | 6 | 167680 | Gas shortage
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 8 | 179808 | Gas shortage
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 7110000 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 403 | 9600000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 241740
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 400 | 9351200
| Sylhet Area Total |  |  |  | 2477 | 1528 | 35343748
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 893 | 21594181
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 16 | 69120 | Fuel shortage
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 41 | 268320 | Engine problem
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 221 | 5118257
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 54 | 546432 | Engine problem
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 285 | 6665760 | Gas shortage.
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 0 | 0 | Fuel shortage
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 447360 | Reserve.
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 96000 | Fuel shortage
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 50 | 597600 | Fuel shortage
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 616320
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 0 | 0 | 0 | On test.
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 2384 | 1577 | 36019350
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 16 | 557664 | Line O/L
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 34 | 578929 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 84 | 2011108 | Gas shortage
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1050 | 23596300 | Line O/L
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 5198209
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Line O/L
| Barisal Area Total |  |  |  | 1958 | 1404 | 31942210
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 24 | 558736 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 30 | 388653 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contract Expired
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 173216 | Fuel shortage
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 178258 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 205 | 5253209
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 196 | 4481836
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 210 | 5228636
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 416 | 9818072
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 21 | 460080
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | .
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 248940
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 16 | 214565 | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 74 | 365744 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 38 | 1087084 | Low demand
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 94 | 1620000 | Engine problem
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 95 | 1603296 | Engine problem
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 37140
| Rajshahi Area Total |  |  |  | 2129 | 1462 | 31717465
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 81 | 1896872
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 250 | 5991800 | Machine problem
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 91 | 15532608 | Engine problem
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 48652
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 90 | 491904 | Fuel shortage
| Intraco Solar 30 MW |  | IPP | 0 | 0 | 0 | 0
| Rangpur Area Total |  |  |  | 720 | 512 | 23961836
| Total |  |  |  | 21680 | 13777 | 310892820
| Eastern Grid Total |  |  |  | 14489 | 8822 | 187251959
| Western Grid Total |  |  |  | 7191 | 4955 | 123640861
| National Grid Total |  |  |  | 21680 | 13777 | 310892820
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2022-08-26
(a) ENTIRE EASTERN GRID : |  | 8922.67 | MW | (b) ENTIRE WESTERN GRID : |  | 4469.44 | MW
i) Dhaka area |  | 4636.74 | MW | i) Khulna area |  | 1684.8 | MW
ii) Chittagong area |  | 1292.93 | MW | ii) Rajshahi area |  | 1456.9 | MW
iii) Comilla area |  | 1378 | MW | iii) Barisal area |  | 406.74 | MW
iv) Mymensingh area |  | 996 | MW | iv) Rangpur area |  | 921 | MW
v) Sylhet area |  | 619 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 13392.11 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
AKS | 0 | 00:00 | Chowmuhani | 214 | 23:00 | Kaptai | 5 | 18:30 | Nawabganj | 36.9 | 19:00 | Siddhirganj | 108 | 22:00
AKSML | 145 | 08:00 | Chuadanga | 108 | 21:00 | Kazla | 90 | 12:00 | Netrakona | 96 | 19:00 | Sirajganj | 88 | 07:00
Aftabnagar | 32 | 00:00 | Coxsbazar | 115 | 13:00 | Keranigonj | 58 | 12:00 | New | 81 | 09:00 | Sonargaon | 80 | 12:00
Agargaon | 81 | 23:00 | Cumilla(N) | 255 | 16:00 | Khagrachori | 26 | 19:30 | Niamatpur | 64 | 06:00 | Sreemongol | 44 | 12:00
Agrabad | 64 | 00:00 | Cumilla(S) | 166 | 23:00 | Khulna | 95 | 23:00 | Noapara | 47 | 01:00 | Srinagar | 46.28 | 21:00
Amnura | 58 | 22:00 | Daudkandi | 148 | 21:00 | Khulshi | 151 | 00:00 | PHP | 11 | 10:00 | Sunamganj | 38 | 22:00
Ashuganj | 74 | 23:00 | Dhaka | 18 | 00:00 | Kishoreganj | 132 | 00:00 | Pabna | 89 | 00:00 | Sylhet | 136 | 00:00
BSRM | 162 | 21:00 | Dhamrai | 114 | 21:00 | Kodda | 280 | 18:00 | Palashbari | 108 | 23:00 | TK | 28.5 | 19:00
Bagerhat | 102 | 22:00 | Dhanmondi | 119 | 18:30 | Kulaura | 52 | 22:00 | Panchagarh | 46 | 08:00 | Tangail | 195 | 22:00
Bakulia | 92 | 00:00 | Dohazari | 92 | 20:00 | Kurigram | 64 | 22:00 | Patuakhali | 133 | 22:00 | Thakurgaon | 66 | 22:00
Banani | 62 | 15:00 | Faridpur | 165 | 00:00 | Kushtia | 144 | 21:00 | Payra | 1.02 | 16:00 | Tongi | 116 | 19:30
Bangabhaban | 5 | 00:00 | Fatullah | 74 | 00:00 | Lalbag | 69 | 01:00 | Purbachal | 20 | 21:00 | Ullon | 40 | 21:00
Barapukuria | 59 | 23:00 | Fenchuganj | 52 | 19:00 | Lalmonirhat | 52 | 22:00 | Purbasadipur | 96 | 05:00 | Uttara | 93 | 21:00
Barguna | 20 | 22:00 | Feni | 116 | 20:00 | Madanganj | 98 | 23:00 | Rahim | 26 | 08:00 | UttaraNew | 18 | 00:00
Barishal | 98 | 22:00 | GPH | 86 | 02:00 | Madaripur | 108 | 22:00 | Rajbari | 60 | 19:30 | Zigatola | 57 | 19:00
Barishal-230 | 82 | 22:00 | Ghorashal | 75 | 01:00 | Madartek | 90 | 23:00 | Rajendrapur | 92 | 05:00
Baroaulia | 75 | 00:00 | Goalpara | 26 | 00:00 | Madunaghat | 65 | 19:30 | Rajshahi | 132 | 22:00
Baroirhat | 61 | 18:30 | Gollamari | 50 | 00:00 | Magura | 62 | 19:00 | Rajshahi-230 | 26 | 02:00
Bashundhara | 162 | 15:00 | Gopalganj | 101.4 | 19:00 | Mahasthangarh | 76 | 00:00 | Ramganj | 88 | 19:00
BashundharaCement | 6 | 01:00 | Gulshan | 90 | 19:00 | Manikganj | 73 | 00:00 | Rampur | 16 | 00:00
Beanibazar | 72 | 22:00 | Halishahar | 71 | 11:00 | Maniknagar | 64 | 23:00 | Rangamati | 14 | 19:00
Benapole | 58 | 22:00 | HaripurSBU | 162 | 00:00 | Matarbari | 38 | 19:30 | Rangpur | 105 | 08:00
Bhaluka | 128 | 23:00 | Hasnabad | 100 | 00:00 | Matuail | 58 | 00:00 | Ruppur | 5 | 09:00
Bhandaria | 50 | 21:00 | Hathazari | 94 | 20:00 | Millgate | 52 | 12:00 | SSM | 3 | 05:00
Bhangura | 34 | 23:00 | Ishurdi | 71 | 21:00 | Mirpur | 147 | 19:00 | Saidpur | 93 | 08:00
Bheramara(GK) | 65 | 21:00 | Jaldhaka | 67 | 19:30 | Mirsorai | N/A | N/A | Satkhira | 95 | 06:00
Bhulta | 240 | 00:00 | Jamalpur | 130 | 12:00 | Mithapukur | 36 | 19:00 | Satmasjid | 101 | 19:00
Bog-Sherpur | 66 | 19:00 | Jashore | 139 | 22:00 | Modern | 0 | 00:00 | Savar | 156 | 09:00
Bogura | 179 | 23:00 | Jhenaidah | 130 | 19:00 | Mogbazar | 111 | 18:30 | Shahjadpur | 85 | 22:00
Borhanuddin | 42 | 23:00 | Joydebpur | 189 | 21:00 | Mongla | 24 | 12:00 | Shahjibazar | 95 | 00:00
Brahmanbaria | 180 | 22:00 | Joypurhat | 62 | 21:00 | Motijheel | 29 | 18:30 | Shahmirpur | 46.5 | 18:30
Cantonment | 128 | 00:00 | Juldah | 27 | 16:00 | Munshiganj | 114 | 00:00 | Shariatpur | 78 | 22:00
Chandpur | 72 | 23:00 | KSRM | 34 | 06:00 | Mymensingh | 230 | 21:00 | Sherpur | 100 | 19:00
Chandraghona | 30 | 00:00 | Kabirpur | 279 | 11:00 | Naogaon | 130 | 21:00 | Shikalbaha | 28 | 19:00
Chapai | 67 | 23:00 | Kachua | 80 | 22:00 | Narail | 46 | 19:30 | Shikalbaha-230 | N/A | N/A
Charsaidpur | 48 | 06:00 | Kallyanpur | 111 | 19:30 | Narinda | 54 | 00:00 | Shitalakhya | 114 | 12:00
Chauddagram | 49 | 21:00 | Kalurghat | 24 | 00:00 | Narshingdi | 190 | 21:00 | Sholosohor | N/A | N/A
Chhatak | 36 | 20:00 | Kamrangirchar | 58 | 12:00 | Natore | 136 | 21:00 | Shyampur | 144 | 01:00
Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
(1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2022-08-26 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Bhulta | 379 | 19:00 | 368 | 10:00 | Kaliakoir | 384 | 16:00 | 370 | 10:00
| Bibiana | 399 | 21:00 | 391 | 10:00 | Payra | 419 | 18:00 | 407 | 23:00
| BIPTC | 400 | 04:00 | 394 | 15:00 | Rahanpur_I | 396 | 17:00 | 371 | 03:00
| Gopalganj_I | 410 | 17:00 | 390 | 23:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 217 | 21:00 | 207 | 11:00 | Hasnabad | 218 | 19:00 | 207 | 10:00
| AKSML | 229 | 20:00 | 213 | 00:00 | Hathazari | 228 | 17:00 | 216 | 03:00
| Aminbazar | 217 | 02:00 | 214 | 05:00 | Ishurdi | 233 | 17:00 | 224 | 00:00
| Ashuganj | 232 | 18:00 | 226 | 11:00 | Jhenaidah | 230 | 18:00 | 217 | 00:00
| Baghabari | 232 | 17:00 | 225 | 02:00 | Kaliakoir | 227 | 18:30 | 210 | 10:00
| Barapukuria | 229 | 17:00 | 209 | 00:00 | Keranigonj | 217 | 19:00 | 208 | 10:00
| Barishal | 246 | 17:00 | 237 | 00:00 | Khulna(S) | 240 | 18:00 | 226 | 22:00
| Bheramara | 230 | 17:00 | 220 | 00:00 | Maniknagar | 220 | 19:00 | 213 | 11:00
| Bhulta | 223 | 19:00 | 216 | 11:00 | Meghnaghat | 224 | 21:00 | 218 | 10:00
| Bibiana | 233 | 18:00 | 228 | 11:00 | Mirsorai | N/A | N/A | N/A | N/A
| BIPTC | 233 | 17:00 | 222 | 00:00 | Rajshahi | 232 | 18:00 | 220 | 23:00
| Bogura | 224 | 17:00 | 213 | 01:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 249 | 18:00 | 242 | 22:00 | Rampura | 221 | 19:00 | 214 | 11:00
| BSRM | 226 | 17:00 | 215 | 00:00 | Shikalbaha | 229 | 18:30 | 217 | 03:00
| Cumilla(N) | 223 | 19:00 | 216 | 11:00 | Shyampur | 219 | 20:00 | 213 | 13:00
| Fenchuganj | 235 | 17:00 | 230 | 09:00 | Siddhirganj | 222 | 20:00 | 215 | 11:00
| Ghorashal | N/A | N/A | N/A | N/A | Sirajgonj | 230 | 18:00 | 225 | 19:30
| GPH | 227 | 19:00 | 213 | 03:00 | Tongi | 222 | 05:00 | 214 | 11:00
| Haripur | 220 | 19:00 | 214 | 10:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 134 | 05:00 | 130 | 10:00 | Lalbag | 136 | 19:00 | 128 | 10:00
| Agargaon | 134 | 21:00 | 124 | 11:00 | Lalmonirhat | 127 | 17:00 | 114 | 00:00
| Agrabad | 132 | 17:00 | 124 | 00:00 | Madanganj | 131 | 18:30 | 123 | 11:00
| AKS | 132 | 17:00 | 123 | 00:00 | Madaripur | 140 | 18:00 | 130 | 23:00
| Aminbazar | 132 | 03:00 | 130 | 02:00 | Madartek | 134 | 05:00 | 128 | 12:00
| Amnura | 133 | 18:00 | 124 | 00:00 | Madunaghat | 134 | 20:00 | 125 | 03:00
| Ashuganj | 135 | 19:30 | 132 | 11:00 | Magura | 140 | 18:00 | 127 | 22:00
| Bagerhat | 135 | 17:00 | 125 | 21:00 | Mahasthangarh | 132 | 17:00 | 121 | 22:00
| Bakulia | 133 | 17:00 | 125 | 00:00 | Manikganj | 133 | 19:30 | 126 | 03:00
| Banani | 129 | 23:00 | 121 | 11:00 | Maniknagar | 131 | 04:00 | 127 | 11:00
| Bangabhaban | 131 | 06:00 | 127 | 10:00 | Matarbari | 122 | 17:00 | 106 | 00:00
| Barapukuria | 134 | 18:00 | 125 | 03:00 | Matuail | 129 | 18:30 | 124 | 11:00
| Barguna | 140 | 09:00 | 130 | 21:00 | Millgate | 129 | 05:00 | 122 | 12:00
| Barishal | 141 | 09:00 | 130 | 21:00 | Mirpur | 133 | 21:00 | 125 | 11:00
| Barishal-230 | 139 | 07:00 | 132 | 00:00 | Mithapukur | 131 | 17:00 | 116 | 05:00
| Baroaulia | 133 | 18:30 | 127 | 00:00 | Modern | 132 | 17:00 | 125 | 00:00
| Baroirhat | 130 | 17:00 | 120 | 04:00 | Mogbazar | 134 | 04:00 | 130 | 10:00
| Bashundhara | 130 | 06:00 | 122 | 12:00 | Mongla | 135 | 18:00 | 124 | 22:00
| BashundharaCement | 131 | 18:30 | 123 | 11:00 | Motijheel | 131 | 06:00 | 127 | 11:00
| Beanibazar | 128 | 08:00 | 123 | 22:00 | Munshiganj | 131 | 18:30 | 124 | 10:00
| Benapole | 138 | 18:00 | 126 | 22:00 | Mymensingh | 126 | 17:00 | 107 | 20:00
| Bhaluka | 126 | 18:30 | 112 | 03:00 | Naogaon | 130 | 17:00 | 115 | 23:00
| Bhandaria | 138 | 07:00 | 127 | 22:00 | Narail | 138 | 18:00 | 126 | 22:00
| Bhangura | 136 | 09:00 | 132 | 00:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bheramara | 136 | 17:00 | 131 | 00:00 | Narshingdi | 125 | 18:30 | 116 | 11:00
| Bheramara(GK) | 136 | 17:00 | 132 | 00:00 | Natore | 134 | 17:00 | 125 | 00:00
| Bhulta | 120 | 03:00 | 114 | 10:00 | Nawabganj | 136 | 19:00 | 129 | 11:00
| Bog-Sherpur | 135 | 17:00 | 124 | 22:00 | Netrakona | 121 | 04:00 | 104 | 21:00
| Bogura | 135 | 17:00 | 125 | 21:00 | New | 130 | 21:00 | 123 | 11:00
| Bogura-230 | 135 | 17:00 | 126 | 01:00 | Niamatpur | 129 | 17:00 | 111 | 22:00
| Brahmanbaria | 130 | 18:30 | 126 | 22:00 | Noapara | 139 | 18:00 | 129 | 22:00
| Cantonment | 133 | 21:00 | 123 | 11:00 | Pabna | 135 | 18:00 | 128 | 00:00
| Chandpur | 133 | 08:00 | 123 | 13:00 | Palashbari | 128 | 18:00 | 116 | 00:00
| Chandraghona | 134 | 17:00 | 126 | 03:00 | Panchagarh | 125 | 18:00 | 104 | 19:00
| Chapai | 133 | 17:00 | 125 | 00:00 | Patuakhali | 138 | 09:00 | 130 | 21:00
| Charsaidpur | 132 | 19:00 | 124 | 11:00 | Payra | 139 | 09:00 | 134 | 19:30
| Chauddagram | 130 | 17:00 | 121 | 02:00 | PHP | 130 | 17:00 | 120 | 02:00
| Chhatak | 128 | 04:00 | 123 | 19:30 | Postogola | 139 | 19:30 | 130 | 11:00
| Chowmuhani | 126 | 09:00 | 120 | 01:00 | Purbachal | 129 | 18:30 | 122 | 10:00
| Chuadanga | 135 | 18:00 | 121 | 23:00 | Purbasadipur | 130 | 18:00 | 111 | 04:00
| Coxsbazar | 121 | 17:00 | 106 | 00:00 | Rahim | 130 | 18:30 | 125 | 11:00
| Cumilla(N) | 131 | 17:00 | 125 | 02:00 | Rajbari | 136 | 18:00 | 126 | 23:00
| Cumilla(S) | 130 | 00:00 | 123 | 01:00 | Rajendrapur | 134 | 20:00 | 127 | 11:00
| Daudkandi | 130 | 00:00 | 123 | 10:00 | Rajshahi | 132 | 18:30 | 123 | 17:00
| Dhaka | 134 | 05:00 | 129 | 12:00 | Rajshahi-230 | 132 | 18:00 | 125 | 00:00
| Dhamrai | 125 | 05:00 | 116 | 11:00 | Ramganj | 134 | 17:00 | 119 | 15:00
| Dhanmondi | 129.5 | 21:00 | 124.4 | 12:00 | Rampur | 132 | 18:30 | 124 | 00:00
| Dohazari | 132 | 13:00 | 120 | 00:00 | Rampura | 134 | 04:00 | 129 | 11:00
| Faridpur | 137 | 18:00 | 127 | 00:00 | Rangamati | 134 | 17:00 | 126 | 03:00
| Fatullah | 132 | 19:00 | 125 | 10:00 | Rangpur | 129 | 14:00 | 115 | 23:00
| Fenchuganj | 133 | 18:00 | 130 | 09:00 | Ruppur | 135 | 01:00 | 132 | 03:00
| Feni | 130 | 17:00 | 120 | 02:00 | Saidpur | 127 | 17:00 | 115 | 22:00
| Ghorashal | 136 | 01:00 | 131 | 09:00 | Satkhira | 136 | 18:00 | 124 | 22:00
| Goalpara | 137 | 10:00 | 129 | 23:00 | Satmasjid | 133 | 03:00 | 124 | 11:00
| Gollamari | 138 | 18:00 | 130 | 22:00 | Savar | 134 | 21:00 | 123 | 11:00
| Gopalganj | 141 | 18:00 | 132 | 00:00 | Shahjadpur | 137 | 13:00 | 134 | 19:00
| Gopalganj_I | 141 | 17:00 | 133 | 23:00 | Shahjibazar | 131 | 00:00 | 127 | 19:00
| Gulshan | 134 | 05:00 | 128 | 12:00 | Shahmirpur | 133 | 17:00 | 124 | 00:00
| Halishahar | 133 | 17:00 | 124 | 00:00 | Shariatpur | 138 | 18:00 | 127 | 23:00
| Haripur | 130 | 19:00 | 125 | 11:00 | Sherpur | 132 | 18:30 | 113 | 03:00
| HaripurSBU | 137 | 14:00 | 125 | 12:00 | Shikalbaha | 134 | 18:00 | 126 | 00:00
| Hasnabad | 140 | 19:30 | 132 | 08:00 | Shikalbaha-230 | 133 | 18:00 | 125 | 03:00
| Hathazari | 135 | 17:00 | 127 | 00:00 | Shitalakhya | 140 | 19:00 | 130 | 10:00
| Ishurdi | 136 | 17:00 | 130 | 22:00 | Sholosohor | N/A | N/A | N/A | N/A
| Jaldhaka | 128 | 18:00 | 111 | 00:00 | Shyampur | 132 | 05:00 | 125 | 10:00
| Jamalpur | 130 | 17:00 | 116 | 03:00 | Shyampur-230 | 133 | 20:00 | 127 | 17:00
| Jashore | 138 | 18:00 | 127 | 22:00 | Siddhirganj | 130 | 18:30 | 125 | 10:00
| Jhenaidah | 140 | 17:00 | 130 | 21:00 | Sirajganj | 135 | 17:00 | 126 | 00:00
| Jhenaidah-230 | 141 | 18:00 | 131 | 23:00 | Sonargaon | 131 | 02:00 | 124 | 09:00
| Joydebpur | 139 | 19:00 | 129 | 09:00 | Sreemongol | 132 | 13:00 | 130 | 03:00
| Joypurhat | 130 | 17:00 | 114 | 22:00 | Srinagar | 136 | 19:00 | 127 | 10:00
| Juldah | 132 | 17:00 | 124 | 00:00 | SSM | 134 | 09:00 | 128 | 00:00
| Kabirpur | 135 | 21:00 | 125 | 06:00 | Sunamganj | 129 | 23:00 | 119 | 20:00
| Kachua | 134 | 17:00 | 122 | 02:00 | Sylhet | 131 | 09:00 | 128 | 21:00
| Kaliakoir | 135 | 00:00 | 132 | 10:00 | Tangail | 130 | 17:00 | 121 | 15:00
| Kallyanpur | 134 | 21:00 | 126 | 11:00 | Thakurgaon | 128 | 18:30 | 107 | 15:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2022-08-26
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 690 | 8116 | 4825 | 12941 |  |  |  | QF-LDC-11
0:30 | 675 | 8078.5 | 4887 | 12965.5 | Date: | 2022-08-26
1:00 | 660 | 8041 | 4949 | 12990
1:30 | 660 | 7929 | 4854.5 | 12783.5
2:00 | 660 | 7817 | 4760 | 12577
2:30 | 660 | 7809 | 4706 | 12515 | [5 empty] | Gen. at Eve. Peak | 13777 | 13777 MW (21:00 )
3:00 | 660 | 7801 | 4652 | 12453 | [6 empty] | 21:00
3:30 | 635 | 7743 | 4630 | 12373 | [5 empty] | Gen. at Day Peak | 11430 | 11430 MW (11:00 )
4:00 | 610 | 7685 | 4608 | 12293 | [6 empty] | 11:00
4:30 | 610 | 7719 | 4558.5 | 12277.5 | [5 empty] | Highest Generation | 13855
5:00 | 610 | 7753 | 4509 | 12262 | [6 empty] | 23:00
5:30 | 600 | 7527.5 | 4368.5 | 11896
6:00 | 590 | 7302 | 4228 | 11530
6:30 | 610 | 7246.5 | 4150.5 | 11397
7:00 | 630 | 7191 | 4073 | 11264
7:30 | 580 | 7190.5 | 4016 | 11206.5
8:00 | 530 | 7190 | 3959 | 11149
8:30 | 615 | 7161.5 | 4003 | 11164.5
9:00 | 700 | 7133 | 4047 | 11180
9:30 | 767.5 | 7108.5 | 4058 | 11166.5
10:00 | 835 | 7084 | 4069 | 11153
10:30 | 820 | 7209 | 4082.5 | 11291.5
11:00 | 805 | 7334 | 4096 | 11430
11:30 | 820 | 7276 | 4144 | 11420
12:00 | 835 | 7218 | 4192 | 11410
12:30 | 715 | 7300 | 4262 | 11562
13:00 | 595 | 7382 | 4332 | 11714
13:30 | 542.5 | 7360 | 4242 | 11602
14:00 | 490 | 7338 | 4152 | 11490
14:30 | 540 | 7464.5 | 4188 | 11652.5
15:00 | 590 | 7591 | 4224 | 11815
15:30 | 690 | 7527.5 | 4221 | 11748.5
16:00 | 790 | 7464 | 4218 | 11682
16:30 | 800 | 7399 | 4176.5 | 11575.5
17:00 | 810 | 7334 | 4135 | 11469
17:30 | 800 | 7268 | 4012.5 | 11280.5
18:00 | 790 | 7202 | 3890 | 11092
18:30 | 485 | 7847 | 4163.5 | 12010.5
19:00 | 180 | 8492 | 4437 | 12929
19:30 | 290 | 8605 | 4739 | 13344
20:00 | 240 | 8600 | 4891 | 13491 |  |  |  | Executive Engineer
20:30 | 205 | 8711 | 4923 | 13634 |  |  |  | Network Operation Division
21:00 | 170 | 8822 | 4955 | 13777
21:30 | 170 | 8840 | 4946 | 13786
22:00 | 170 | 8858 | 4937 | 13795 |  |  |  |  | Page 6 of 7
22:30 | 200 | 8904.5 | 4920.5 | 13825
23:00 | 230 | 8951 | 4904 | 13855
23:30 | 460 | 8533.5 | 4864.5 | 13398
24:00 | 690 | 8116 | 4825 | 12941
13777 MW (21:00 )
11430 MW (11:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2022-08-26 |  | Energy |  | 310892820
[13 empty] | 2022-08-26 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 4655 | 894 | 1990 | 508 | 2368 | 1412 | 144 | 424 | 585 | 160 | 0 | 977
0:30 | 4619.5 | 893 | 1985.5 | 677.5 | 2304 | 1411.5 | 144.5 | 430.5 | 564.5 | 140 | 0 | 769.5804 | Date: | 2022-08-26
1:00 | 4584 | 892 | 1981 | 847 | 2240 | 1411 | 145 | 437 | 544 | 120 | 0 | 562.1608
1:30 | 4593 | 892.5 | 1950 | 751.5 | 2186 | 1396 | 145 | 439.5 | 524 | 120 | 0 | 614.2297 | [8 empty] | Total Energy | 310.8928 | Total Energy Gen 310.893 MKWHr Energy Not Served 18.441 MKWHr Energy Requirement 329.333 MKWHr
2:00 | 4602 | 893 | 1919 | 656 | 2132 | 1381 | 145 | 442 | 504 | 120 | 0 | 666.2987 | [8 empty] | Energy not Served | 18.4406
2:30 | 4602.5 | 892.5 | 1920.5 | 604 | 2126.5 | 1380.5 | 145 | 441.5 | 500.5 | 118 | 0 | 585.2001 | [8 empty] | Energy Requirement | 329.3334
3:00 | 4603 | 892 | 1922 | 552 | 2121 | 1380 | 145 | 441 | 497 | 116 | 0 | 504.1015
3:30 | 4616 | 892 | 1915.5 | 466 | 2123 | 1374.5 | 145 | 441 | 494.5 | 122 | 0 | 485.67 | [6 empty] | Shortage
4:00 | 4629 | 892 | 1909 | 380 | 2125 | 1369 | 145 | 441 | 492 | 128 | 0 | 467.2385
4:30 | 4613.5 | 892 | 1909 | 415 | 2105 | 1369.5 | 145 | 433 | 474 | 130 | 0 | 458.4836
5:00 | 4598 | 892 | 1909 | 450 | 2085 | 1370 | 145 | 425 | 456 | 132 | 0 | 449.7286
5:30 | 4607 | 892.5 | 1872.5 | 260 | 2039 | 1330 | 145 | 426 | 393.5 | 129 | 2 | 394.8949
6:00 | 4616 | 893 | 1836 | 70 | 1993 | 1290 | 145 | 427 | 331 | 126 | 4 | 340.0612
6:30 | 4583.5 | 892.5 | 1859 | 35 | 1995.5 | 1199.5 | 145 | 417.5 | 317.5 | 123 | 20.5 | 315.6394 |  |  |  |  | Coal
7:00 | 4551 | 892 | 1882 | 0 | 1998 | 1109 | 145 | 408 | 304 | 120 | 37 | 291.2177
7:30 | 4536 | 892 | 1833 | 0 | 1995.5 | 1101 | 144.5 | 394.5 | 290.5 | 120 | 68 | 324.6088 |  |  |  | Oil |  |  |  | ,
8:00 | 4521 | 892 | 1784 | 0 | 1993 | 1093 | 144 | 381 | 277 | 120 | 99 | 358
8:30 | 4522.5 | 892 | 1827.5 | 0 | 1988 | 1071 | 144 | 358 | 264.5 | 121 | 118.5 | 518.5
9:00 | 4524 | 892 | 1871 | 0 | 1983 | 1049 | 144 | 335 | 252 | 122 | 138 | 679
9:30 | 4525.5 | 892 | 1880 | 0 | 1940 | 1049 | 144 | 327.5 | 252 | 124 | 162.5 | 827.5
10:00 | 4527 | 892 | 1889 | 0 | 1897 | 1049 | 144 | 320 | 252 | 126 | 187 | 976
10:30 | 4513 | 893 | 1902 | 125 | 1887.5 | 1043.5 | 144 | 334 | 263 | 130 | 190.5 | 1172.5
11:00 | 4499 | 894 | 1915 | 250 | 1878 | 1038 | 144 | 348 | 274 | 134 | 194 | 1369
11:30 | 4423 | 893.5 | 1890.5 | 355.5 | 1833 | 1054 | 142 | 377.5 | 295 | 115 | 204 | 1444
12:00 | 4347 | 893 | 1866 | 461 | 1788 | 1070 | 140 | 407 | 316 | 96 | 214 | 1519
12:30 | 4409.5 | 892.5 | 1866 | 449 | 1881 | 1079 | 140 | 410 | 322 | 96 | 208.5 | 1468.5
13:00 | 4472 | 892 | 1866 | 437 | 1974 | 1088 | 140 | 413 | 328 | 96 | 203 | 1418
13:30 | 4472 | 892 | 1866 | 437 | 1974 | 1088 | 140 | 413 | 328 | 96 | 203 | 1461
14:00 | 4472 | 892 | 1866 | 437 | 1974 | 1088 | 140 | 413 | 328 | 96 | 203 | 1504
14:30 | 4458.5 | 893 | 1871 | 508 | 1970 | 1104 | 124 | 403 | 324 | 117 | 178.5 | 1515
15:00 | 4445 | 894 | 1876 | 579 | 1966 | 1120 | 108 | 393 | 320 | 138 | 154 | 1526
15:30 | 4445 | 894 | 1856 | 505 | 1993.5 | 1120.5 | 126 | 398.5 | 334.5 | 137 | 121 | 1490
16:00 | 4445 | 894 | 1836 | 431 | 2021 | 1121 | 144 | 404 | 349 | 136 | 88 | 1454
16:30 | 4467 | 894 | 1830 | 215.5 | 2197.5 | 1121 | 144.5 | 355.5 | 330.5 | 127 | 62.5 | 833.5
17:00 | 4467 | 894 | 1824 | 0 | 2374 | 1121 | 145 | 307 | 312 | 118 | 37 | 213
17:30 | 4337.5 | 894 | 1746 | 0 | 2412.5 | 1110.5 | 145 | 278.5 | 342 | 123 | 21.5 | 179.5
18:00 | 4208 | 894 | 1668 | 0 | 2451 | 1100 | 145 | 250 | 372 | 128 | 6 | 146
18:30 | 4387 | 894.5 | 1812 | 193.5 | 2670 | 1131 | 145 | 287.5 | 488.5 | 137 | 3 | 243.9522
19:00 | 4566 | 895 | 1956 | 387 | 2889 | 1162 | 145 | 325 | 605 | 146 | 0 | 341.9043
19:30 | 4610 | 895 | 1999 | 334 | 3102 | 1231 | 145 | 415 | 658 | 152 | 0 | 328.0807
20:00 | 4636 | 894 | 1984 | 284 | 3138 | 1362 | 154 | 417 | 671 | 148 | 0 | 330.8454
20:30 | 4649.5 | 893.5 | 1985.5 | 377 | 3159.5 | 1371.5 | 151 | 417 | 673 | 153 | 0 | 319.9227
21:00 | 4663 | 893 | 1987 | 470 | 3181 | 1381 | 148 | 417 | 675 | 158 | 0 | 309
21:30 | 4686 | 893.5 | 1982 | 462 | 3192 | 1391.5 | 146 | 409 | 652 | 160 | 0 | 711
22:00 | 4709 | 894 | 1977 | 454 | 3203 | 1402 | 144 | 401 | 629 | 162 | 0 | 1113
22:30 | 4670 | 894 | 1994.5 | 548.5 | 3161.5 | 1417 | 144 | 404 | 609.5 | 164 | 0 | 1059.5
23:00 | 4631 | 894 | 2012 | 643 | 3120 | 1432 | 144 | 407 | 590 | 166 | 0 | 1006
23:30 | 4643 | 894 | 2001 | 575.5 | 2744 | 1422 | 144 | 415.5 | 587.5 | 163 | 0 | 1127.5 | Max Temp. in Dhaka |  | 24.7° C | 35° C
24:00 | 4655 | 894 | 1990 | 508 | 2368 | 1412 | 144 | 424 | 585 | 160 | 0 | 1249
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 310.893 MKWHr Energy Not Served 18.441 MKWHr Energy Requirement 329.333 MKWHr
Note on W13: Author:

## Generation
g | 2022-08-26
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 74 | 74 | 74 | 74 | 70 | 70 | 73 | 38 | 74 | 75 | 75 |  | 75 | 75 | 84 | 78 | 74 | 74 | 74 | 1766765
2 | Karnaphuli Hydro PP Unit-4 & 5 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1692000
3 | Chattogram TPP-1 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2700000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 25 | 25 | 25 | 25 | 17 | 18 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 22 | 24 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 588321
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 3 | 5 | 8 | 10 | 12 | 5 | 18 | 12 | 9 | 5 | 1 | [9 empty] | 81540
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 34 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 624565
12 | Hathazari 100 MW peaking PP | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 26 | 26 | 26 | 26 | 26 | 26 | 28 |  | 34 | 26 | 26 | 26 | 26 | 26 | 26 | 701424
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 68 | 68 | 68 | 68 | 76 | 105 | 105 | 66 | 52 | 52 | 52 | 52 | 78 | 87 | 89 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2079199
| Daudkandi 200 MW PP (B.Trac) | 195 | 100 | 100 | 100 | 150 | 0 |  |  |  |  | 30 | 110 | 80 | 10 | 150 | 70 |  |  |  | 100 | 30 | 30 | 100 | 100 | 180 | 140 | 1870656
14 | Titas 50 MW Peaking PP | 40 | 40 | 39 | 39 | 33 | 40 | 31 | 31 | 31 | 31 | 31 | 29 | 29 | 35 | 37 | 37 | 37 | 37 |  | 37 | 37 | 39 | 39 | 40 | 38 | 38 | 853896
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 97 | 92 | 97 | 97 | 96 | 96 | 97 | 60 | 97 | 95 | 94 | 0 | 94 | 95 | 95 | 95 | 92 | 34 |  | 95 | 95 | 97 | 97 | 98 | 92 | 92 | 2180000
17 | Siddhirganj 335 MW CCPP | 335 | 335 | 335 | 335 | 335 | 335 | 337 | 335 | 335 | 335 | 331 | 329 | 331 | 322 | 327 | 327 | 322 | 330 |  | 331 | 328 | 330 | 330 | 327 | 332 | 335 | 8045613
18 | Kodda 300 MW PP Unit-2 (Summit) | 276 | 276 | 278 | 278 | 278 | 278 | 263 | 278 | 278 | 273 | 260 | 260 | 270 | 278 | 268 | 255 | 258 | 268 |  | 276 | 260 | 260 | 260 | 276 | 276 | 276 | 6506070
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 200727
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4274550
24
25 | Ghorasal 365 MW CCPP Unit-7 | 300 | 300 | 300 | 300 | 300 | 300 | 280 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 7149018
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 41 | 41 | 41 | 41 | 41 | 37 | 37 | 38 | 35 | 38 | 40 | 39 | 39 | 39 | 37 | 37 | 38 | 39 |  | 39 | 39 | 39 | 39 | 40 | 40 | 40 | 921888
33 | Ashuganj 225 MW CCPP | 206 | 207 | 205 | 204 | 205 | 205 | 207 | 205 | 206 | 204 | 203 | 204 | 204 | 197 | 201 | 200 | 202 | 204 |  | 205 | 202 | 204 | 205 | 202 | 205 | 207 | 4936000
34 | Ashuganj 450 MW CCPP(South) | 305 | 310 | 305 | 320 | 305 | 315 | 305 | 320 | 305 | 305 | 310 | 305 | 305 | 325 | 310 | 305 | 305 | 280 |  | 310 | 310 | 310 | 310 | 330 | 305 | 305 | 7556000
| Ashuganj 450 MW CCPP(North) | 310 | 310 | 310 | 325 | 310 | 325 | 310 | 330 | 310 | 310 | 330 | 310 | 310 | 340 | 320 | 320 | 320 | 280 |  | 310 | 310 | 310 | 310 | 335 | 310 | 310 | 7949100
Ashuganj 420 MW CCPP(East)
35 | Ashuganj 55 MW PP (Precision) | 55 | 55 | 55 | 56 | 56 | 56 | 56 | 56 | 55 | 53 | 55 | 54 | 54 | 54 | 52 | 52 | 53 | 53 |  | 52 | 52 | 52 | 54 | 55 | 54 | 55 | 1301760
36 | Chandpur 150 MW CCPP | [19 empty] | 91 | 91 | 91 | 88 | 91 | 90 | 90 | 470820
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 401 | 403 | 404 | 404 | 404 | 403 | 403 | 404 | 405 | 406 | 403 | 400 | 403 | 403 | 399 | 404 | 406 | 408 |  | 403 | 408 | 408 | 405 | 403 | 404 | 400 | 9836550
40 | Meghnaghat 450 MW CCPP(MPL) | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 320 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 330 |  | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 7471750
41 | Haripur 360MW CCPP(HPL) | 317 | 319 | 327 | 333 | 321 | 322 | 328 | 332 | 324 | 329 | 333 | 318 | 318 | 318 | 318 | 318 | 318 | 267 |  | 334 | 335 | 328 | 320 | 324 | 324 | 323 | 7688000
42 | RPCL 210MW CCPP | 158 | 160 | 160 | 157 | 157 | 158 | 138 | 108 | 105 | 105 | 104 | 72 | 67 | 69 | 68 | 85 | 98 | 95 |  | 106 | 105 | 104 | 136 | 150 | 148 | 151 | 2767680
43 | Sutiakhali 50 MW Solar PP |  |  |  |  | 0 | 1 | 11 | 23 | 13 | 31 | 15 | 52 | 34 | 30 | 30 | 26 | 10 | 1 | [8 empty] | 324640
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1023000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720000
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 63 | 65 | 65 | 63 | 63 | 59 | 56 | 58 | 55 | 55 | 55 | 55 | 60 | 59 | 55 | 55 | 56 | 56 |  | 56 | 55 | 61 | 58 | 55 | 56 | 64 | 1381440
48 | Shahjibazar 86MW PP (Shahjibazar) | 81 | 50 | 40 | 20 | 20 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 864960
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 194 | 194 | 194 | 193 | 194 | 194 | 194 | 194 | 194 |  | 194 | 194 | 194 | 194 | 194 | 193 | 193 | 4690780
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 167680
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 241740
54 | Hobiganj 11MW PP Cofidence-E | [25 empty] | 0 | 0
55 | Fenchugonj 51 MW PP (Barakatullah) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 13140
56 | Shahjahanulla 25 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 179808
57 | Bibiana-II 341 MW CCPP (Summit) | 320 | 280 | 290 | 290 | 300 | 290 | 290 | 280 | 300 | 290 | 310 | 285 | 280 | 270 | 300 | 275 | 265 | 260 |  | 280 | 300 | 290 | 290 | 280 | 305 | 280 | 7110000
| Bibiyana South 400 MW | 393 | 400 | 396 | 395 | 395 | 400 | 398 | 390 | 395 | 394 | 392 | 393 | 393 | 380 | 380 | 382 | 385 | 390 |  | 400 | 392 | 396 | 400 | 390 | 400 | 400 | 9351200
58 | Nababganj 55 MW PP (Southern power ) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 882669
59 | Tangail Palli Power Gen 22 MW | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 11 | 7 | 10 | 12 | 12 | 12 | 5 | 8 | 7 | 7 |  | 10 | 12 | 12 | 12 | 7 | 10 | 12 | 259920
60 | Barabkunda 22 MW PP (Regent) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 403776
61 | Narshingdi 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  |  | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 392868
62 | Tangail 22 MW PP (Doreen)
63 | Impoprt (Tripura) | 120 | 120 | 116 | 128 | 132 | 126 | 120 | 120 | 122 | 126 | 134 | 96 | 96 | 100 | 138 | 136 | 118 | 128 |  | 146 | 152 | 148 | 158 | 162 | 166 | 160 | 3077760
64 | Malancha, Ctg. EPZ (United) | 37 | 38 | 38 | 39 | 39 | 39 | 42 | 42 | 42 | 33 | 33 | 24 | 32 | 32 | 27 | 29 | 29 | 38 |  | 38 | 38 | 38 | 42 | 42 | 42 | 42 | 898560
65 | Feni 22MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 21 | 21 | 21 |  |  | 0 | 14 | 19 | 19 | 21 | 21 | 21 | 446442
66 | Feni 11 MW PP (Doreen) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 215640
67 | Jangalia 33MW PP (Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 22 | 25 | 25 | 25 | 25 | 25 | 600900
68 | Cumilla 25 MW PP (Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 18 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 455780
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 26 | 26 | 26 | 26 | 26 | 19 | 19 | 19 | 19 | 19 | 19 | 16 | 18 | 20 | 17 | 18 | 17 | 17 |  | 19 | 26 | 26 | 26 | 26 | 26 | 26 | 497340
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 0 |  | 33 | 33 | 33 | 33 | 33 | 0 | 10 | 702000
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 32 | 32 | 15 | 32 | 32 |  | 32 | 32 | 32 | 32 | 33 | 33 | 33 | 748500
73 | Ghorashal 108MW PP (Regent) | 100 | 100 | 100 | 100 | 100 | 100 | 91 | 98 | 94 | 95 | 90 | 90 | 93 | 93 | 90 | 91 | 95 | 70 |  | 98 | 98 | 98 | 99 | 99 | 99 | 99 | 2237273
| Feni Lanka Power | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 424080
| Chowmuhani 113 MW | 95 | 95 | 89 | 95 | 95 | 94 | 104 | 107 | 105 | 97 | 98 | 105 | 105 | 105 | 104 | 102 | 103 | 85 |  | 94 | 112 | 111 | 112 | 111 | 111 | 97 | 2445240
| Manikgonj 162MW PP(MPGL) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 58 | 72 | 106 | 108 | 108 | 116 | 144 |  | 158 | 162 | 162 | 162 | 162 | 162 | 69 | 1955520
77 | Siddhirganj 100 PP(Dutch Bangla) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 60 | 93 | 95 | 95 | 95 | 95 | 664330
78 | Gazipur 52 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 40 |  | 40 | 40 | 40 | 40 | 40 | 41 | 8 | 368640
79 | Kodda 150MW PP | 90 | 90 | 90 | 90 | 90 | 15 | 16 | 16 | 16 | 16 | 30 | 32 | 32 | 32 | 32 | 32 | 32 | 32 |  | 112 | 112 | 108 | 108 | 78 | 78 | 93 | 1320480
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | [17 empty] | 1 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 54811
| Gazipur 100 MW PP | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 48 | 90 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 17 | 1094400
| Kaptai 7 MW Solar PP | [5 empty] | 0 |  | 2 | 2 | 2 | 1 | 3 | 3 | 2 | 1 | 0 | 0 | [9 empty] | 15959
| Jodiac Power | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 36 | 36 | 41 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1087285
| Karnaphuli Power Ltd. | 92 | 92 | 93 | 93 | 92 | 84 | 102 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 68 |  | 94 | 110 | 110 | 110 | 110 | 110 | 110 | 2521634
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL) | 23 | 9 | 7 | 8 | 8 | 7 | 8 | 8 | 8 | 8 | 8 | 7 | 8 | 8 | 8 | 8 | 16 | 72 |  | 84 | 84 | 84 | 86 | 92 | 92 | 17 | 695040
| Meghnaghat 104 MW PP (OPCL) | [7 empty] | 17 |  |  | 4 | 17 | 17 | 17 | 16 | 17 | 17 | 39 |  | 89 | 90 | 92 | 92 | 91 | 91 | 91 | 724800
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 259320
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1194689
94 | Gagnagar 102 MW PP (Digital Power) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 93 | 93 | 93 | 93 | 93 | 92 | 8 | 603072
95 | Patenga 50MW PP (Baraka) | 25 | 25 | 25 | 25 | 25 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 33 | 38 |  | 38 | 38 | 38 | 38 | 38 | 38 | 30 | 708960
96 | Chattogram 108 MW PP (ECPV) | 12 | 12 | 12 | 11 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 19 |  | 65 | 93 | 93 | 93 | 93 | 75 | 11 | 659520
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 40 | 40 | 45 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 45 | 1292208
100 | Manikganj 55 MW PP (Northern) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 17 | 17 | 17 | 17 | 17 | 35 | 35 | 35 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 35 | 35 | 896773
101 | Kushiara 163 MW CCPP (KP)
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 1 | 1 | 0 | 0 | [8 empty] | 14700
103 | Kamalaghat 54 MW PP(Banco Energy) | 23 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 35 | 35 | 35 | 35 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 774720
104 | Keranigonj 300 MW PP (APR) | 246 | 246 | 242 | 100 | 150 | 0 |  |  |  |  | 120 | 158 | 100 | 11 | 211 | 161 |  |  |  | 105 | 104 | 54 | 152 | 154 | 254 | 12 | 2789733
105 | Bramhangoan 100 MW PP (Aggreko) | 80 | 80 | 80 | 80 | 80 | 40 | 0 |  |  |  | 50 | 80 | 50 | 80 | 80 | 80 |  |  |  | 85 | 90 | 90 | 90 | 90 | 90 | 80 | 1367461
106 | Mymensingh 200 MW PP (United) | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 114 | 114 | 114 | 113 | 105 | 106 | 108 | 102 | 103 | 104 | 103 |  | 104 | 95 | 95 | 95 | 96 | 96 | 97 | 2522400
112 | Aurahati 100MW PP (Aggreko) | 70 | 70 | 70 | 70 | 70 | 30 | 0 |  |  |  | 50 | 80 | 57 | 25 | 80 | 80 |  |  |  | 90 | 90 | 90 | 90 | 90 | 89 | 70 | 1262548
114 | Kodda 149 MW PP Unit-1 (Summit) | 140 | 146 | 143 | 149 | 149 | 149 | 149 | 147 | 149 | 149 | 147 | 46 | 140 | 145 | 27 | 10 | 128 | 149 |  | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 3201696
115 | Juldah 100 MW PP Unit-3 (Acorn) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 263040
116 | Chandpur 200MW (Desh energy) | 128 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 127 | 140 |  | 155 | 180 | 180 | 179 | 179 | 178 | 117 | 2610720
117 | Ashuganj 150MW PP (Midland) | 143 | 142 | 137 | 130 | 132 | 135 | 135 | 130 | 127 | 122 | 122 | 120 | 118 | 115 | 115 | 117 | 117 | 117 |  | 119 | 119 | 119 | 124 | 128 | 127 | 127 | 3024290
118 | Bibiyana-III 400 MW CCPP | 402 | 402 | 403 | 402 | 402 | 404 | 404 | 403 | 402 | 403 | 384 | 402 | 404 | 396 | 404 | 404 | 404 | 375 |  | 403 | 404 | 404 | 403 | 404 | 402 | 400 | 9600000
| Jamalpur 115 MW PP (United) | 98 | 98 | 99 | 99 | 99 | 99 | 99 | 88 | 88 | 88 | 87 | 97 | 96 | 96 | 96 | 96 | 96 | 96 |  | 97 | 106 | 107 | 107 | 107 | 107 | 106 | 2335200
| Anwara 300 MW PP (United) | 52 | 52 | 53 | 52 | 52 | 52 | 52 | 52 | 52 | 51 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 1254545
| Juldah unit-2 (Acorn) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 249600
| Anlima Energy Ltd. | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 92 |  | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 2570564
| Bhairob 54.5 MW | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 23 | 33 | 35 | 2 | 18 | 21 | 35 | 25 | 32 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 785160
| Spectra Solar Plant Ltd. |  |  |  |  | 0 | 1 | 5 | 15 | 23 | 29 | 34 | 36 | 33 | 26 | 20 | 14 | 5 | 1 | [8 empty] | 243593
| Chandpur 115(Doreen) | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 75 | 74 | 75 | 74 | 92 | 96 | 86 | 95 | 72 |  | 74 | 96 | 96 | 96 | 96 | 96 | 96 | 2171520
| Kanchan Purbachal Power Generation Ltd. | 55 | 55 | 55 | 55 | 55 | 34 | 34 | 34 | 34 | [12 empty] | 1 | 16 | 17 | 17 | 17 | 522000
Mirsharai 150 MW (Oil)
Mirsharai 150 MW (Gas)
120 | Eastern Zone Total | 8041 | 7817 | 7801 | 7685 | 7753 | 7302 | 7191 | 7190 | 7133 | 7084 | 7334 | 7218 | 7382 | 7338 | 7591 | 7464 | 7334 | 7202 |  | 8492 | 8605 | 8600 | 8822 | 8858 | 8951 | 8116 | 187251959
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | [19 empty] | 16 | 16 | 16 | 16 | 16 | 16 | 0 | 69120
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 10 | 5 | 0 | [13 empty] | 19 | 40 |  | 40 | 50 | 41 | 41 | 41 | 31 | 20 | 268320
| Khulna 225 MW CCPP | 226 | 225 | 225 | 224 | 225 | 226 | 226 | 226 | 205 | 190 | 210 | 219 | 218 | 170 | 215 | 217 | 177 | 120 |  | 178 | 218 | 220 | 221 | 221 | 223 | 225 | 5118257
129 | Rupsha 105 MW PP (Orion rupsha) | [17 empty] | 3 |  | 17 | 17 | 17 | 17 | 17 | 17 | 0 | 96000
130 | Mongla Orion 100 MW Solar PP |  |  |  |  | 0 | 1 | 12 | 38 | 67 | 89 | 100 | 76 | 71 | 78 | 65 | 37 | 11 | 2 | [8 empty] | 616320
131 | Rampal 1320 MW (BIFPCL)
132 | United Payra Power Ltd.
133 | Bhola Nutan Biddut BD LTD (GAS) | 224 | 224 | 224 | 224 | 224 | 224 | 224 | 224 | 224 | 225 | 223 | 223 | 216 | 218 | 216 | 201 | 195 | 195 |  | 200 | 220 | 220 | 220 | 220 | 222 | 220 | 5198209
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 48 | 32 | 32 | 32 | 32 | 32 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 26 | 32 | 32 | 557664
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 84 | 86 | 85 | 86 | 86 | 86 | 85 | 85 | 85 | 85 | 83 | 83 | 83 | 81 | 82 | 80 | 70 | 76 |  | 77 | 83 | 84 | 84 | 83 | 84 | 85 | 2011108
140 | Bhola 33 MW PP (Venture) | 30 | 29 | 27 | 26 | 25 | 21 | 18 | 19 | 19 | 17 | 17 | 20 | 20 | 20 | 23 | 20 | 18 | 19 |  | 27 | 30 | 30 | 34 | 30 | 35 | 35 | 578929
141 | Noapara 100 MW PP (Bangla Trac) | 89 | 40 | 10 | 10 | 0 | [6 empty] | 2 | 50 | 10 | 10 | 10 | [8 empty] | 5 | 85 | 447360
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP | 46 | 46 | 46 | 40 | 27 | 0 | [10 empty] | 2 | 40 |  | 44 | 45 | 55 | 54 | 53 | 50 | 56 | 546432
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 50 |  | 50 | 50 | 50 | 50 | 50 | 15 | 15 | 597600
146 | Bheramara HVDC | 892 | 893 | 892 | 892 | 892 | 893 | 892 | 892 | 892 | 892 | 894 | 893 | 892 | 894 | 894 | 894 | 894 | 894 |  | 895 | 895 | 894 | 893 | 894 | 894 | 894 | 21594181
147 | Bheramara 410 MW CCPP | 270 | 270 | 275 | 280 | 280 | 280 | 280 | 275 | 280 | 280 | 280 | 270 | 275 | 275 | 270 | 270 | 270 | 275 |  | 285 | 285 | 285 | 285 | 285 | 285 | 285 | 6665760
148 | Payra 1320 MW | 1090 | 1060 | 1060 | 1050 | 1050 | 970 | 790 | 770 | 720 | 720 | 710 | 740 | 760 | 790 | 790 | 790 | 790 | 770 |  | 830 | 900 | 1030 | 1050 | 1070 | 1100 | 1080 | 23596300
149
150 | Barapukuria TPP Unit-1 | 81 | 81 | 80 | 79 | 80 | 80 | 79 | 80 | 79 | 79 | 78 | 80 | 79 | 80 | 80 | 81 | 81 | 80 |  | 82 | 81 | 82 | 81 | 82 | 82 | 82 | 1896872
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 243 | 250 | 250 | 250 | 250 | 249 | 249 | 250 | 250 | 250 | 250 |  | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 5991800
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 558736
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 0 | 3 | 3 | 4 | 5 | 5 | 4 | 4 | 3 | 2 | 1 | 0 | [8 empty] | 37140
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 205 | 204 | 206 | 205 | 205 | 206 | 205 | 205 | 204 | 205 | 205 | 205 | 205 | 205 | 205 | 205 | 205 | 170 |  | 195 | 206 | 205 | 205 | 204 | 201 | 202 | 5253209
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
| Sirajgonj 225 MW CCPP Unit-2 (Oil) | 211 | 217 | 216 | 217 | 200 | 201 | 182 | 155 | 130 | 130 | 138 | 188 | 195 | 161 | 178 | 187 | 130 | 130 |  | 147 | 197 | 197 | 196 | 180 | 184 | 199 | 4481836
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 209 | 212 | 211 | 210 | 209 | 209 | 211 | 209 | 210 | 211 | 208 | 206 | 205 | 204 | 201 | 201 | 203 | 170 |  | 191 | 210 | 210 | 210 | 211 | 210 | 212 | 5228636
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 415 | 422 | 419 | 419 | 422 | 372 | 421 | 323 | 403 | 417 | 414 | 414 | 417 | 414 | 414 | 414 | 414 | 328 |  | 415 | 414 | 416 | 416 | 414 | 418 | 423 | 9818072
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | 31 | 31 | 31 | 31 | 31 | 0 | [6 empty] | 5 | 6 | 6 | 26 | 25 | 24 |  | 24 | 24 | 24 | 30 | 30 | 24 | 24 | 388653
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 20 | 20 | 20 | 18 | 16 | 16 | 16 | 16 | 17 | 18 |  | 21 | 21 | 21 | 21 | 22 | 22 | 22 | 460080
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  |  | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 248940
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | 42 | 42 | 42 | 42 | 0 | [21 empty] | 173216
167 | Katakhali 50 MW Peaking PP | 24 | 0 | [17 empty] | 32 | 32 | 32 | 32 | 32 | 32 | 24 | 178258
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 16 | 16 | 16 | 16 | 8 | 8 | 8 | 214565
170 | Chapainawabganj 100 MW Peaking PP | [19 empty] | 60 | 60 | 74 | 74 | 74 | 52 | 30 | 365744
171 | Baghabari 200 MW PP (Paramount) | 167 | 120 | 50 | 20 | 0 | [6 empty] | 31 | 100 | 10 | 48 | 30 |  |  |  | 7 | 20 | 20 | 38 | 20 | 25 | 121 | 1087084
| Bagura 113 MW PP (Confidence)-2 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 65 | 95 | 50 |  | 70 | 94 | 94 | 94 | 94 | 94 | 50 | 1620000
172 | Confidence Power Bogura Unit-1 113 MW | 95 | 95 | 95 | 95 | 95 | 0 |  |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 90 | 95 | 50 |  | 95 | 95 | 95 | 95 | 95 | 95 | 55 | 1603296
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 55 | 56 | 55 | 55 | 55 | 54 | 55 | 90 | 52 |  | 91 | 90 | 90 | 91 | 90 | 91 | 56 | 15532608
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1 | 2 | 3 | 4 | 4 | 5 | 6 | 6 | 4 | 3 | 2 | 1 | [8 empty] | 48652
178 | Energypac Power Venture Thakurgaon Ltd. | 34 | 0 | [15 empty] | 34 |  | 34 | 72 | 72 | 90 | 90 | 72 | 0 | 491904
178 | Intraco Solar 30 MW |  |  |  |  | 0 | 1 | 5 | 10 | 18 | 17 | 22 | 30 | 32 | 27 | 21 |  | 7 | 1