## Forecast
8 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2022-09-01 | Thursday
|  |  | Date (day): | 2022-09-01 |  | Thursday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 12099.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14071 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2022-08-31 | 2022-09-01 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 110 | 106 | 110 | 110 | 70 |  | Gas shortage
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 170 | 170 | 170 | 170
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 270 | 250 | 270 | 260 | 105 |  | Gas shortage
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas Shortage.
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 408 | 400 | 390 | 400 | 12 |  | Gas shortage
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 257 | 323 | 320 | 320 | 40 |  | Gas shortage
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 225 | 225 | 225 |  | Dirty fuel
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 57 | 92 | 60 | 92 | 8 |  | Fuel shortage
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 138 | 144 | 150 | 150 | 185 |  | Gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 0 | 0 | 0 | 0 |  | 102 | Under maint
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 16 | 19 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 61 | 89 | 24 | 89 | 11 |  | Fuel shortage
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 275 | 332 | 290 | 330 | 5 |  | Gas shortage
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 58 | 92 | 58 | 92 | 10 |  | Fuel shortage
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 54 | 35 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 15 | 110 | 15 | 110 | 39 |  | Fuel shortage
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 55 | 35 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 35 | 35 | 35
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 25 | 52 | 50 | 52 |  | 28 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 18 | 18 | 25 | 25 |  | 8 | Engine problem
| 29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 16 | 40 | 16 | 40 |  | 12 | Engine problem
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 276 | 249 | 260 | 286 |  | 14 | Engine problem
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 175 | 218 | 180 | 218 |  | 82 | Engine problem
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 80 | 90 | 90 | 90 |  | 10 | Engine problem
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 80 | 90 | 80 | 90 |  | 10 | Engine problem
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 149 | 149 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 34 | 105 | 34 | 105 |  |  | Fuel shortage
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 55 | 93 | 55 | 92 | 12 |  | Fuel shortage
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 35 | 144 | 35 | 144 | 18 |  | Fuel shortage
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 22 | 0 | 30 | 0
| 40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 0 | 55
|  | Dhaka area Total |  |  |  |  | 6263 | 5847 | 3182 | 3832 | 3301 | 3948 | 1109 | 766
| 41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 110 | 110 | 110 | 110 | 70 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 25 | 25 | 25 | 25
| 43 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 16 | 0 | 20 | 0
| 44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 25 | 37 | 25 | 37 |  | 13 | Engine problem
| 45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 145 | 146 | 144 | 146 |  | 84 | Low Water Level
| 46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | S/D due to HGPI
| 47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
| 48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 69 | 105 | 69 | 105 |  |  | Fuel shortage
| 49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 26 | 17 | 26 | 26 | 72 |  | Fuel shortage
| 50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 17 | 51 | 17 | 51 | 51 |  | Fuel shortage
| 51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 10 | 10 | 10 | 10 | 90 |  | Fuel shortage
| 52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 10 | 10 | 10 | 10 | 90 |  | Fuel shortage
| 53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 17 | 17 | 17 |  | 5 | Engine problem
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 5 | 30 | 10 | 30
| 54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 11 | 91 | 11 | 100 | 8 |  | Fuel shortage
| 55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 2 | 0 | 5 | 0
| 56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 52 | 70 | 52 | 70 | 230 |  | Fuel shortage
| 57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 36 | 36 | 35 | 36
| 58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 110 | 110 | 92 | 110
| 59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 10 | 10 | 10 | 10 | 90 |  | Fuel shortage
| 60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 107 | 107 | 107 | 107 |  | 9 | Engine problem
|  | Mirsharai 150 MW |  | Gas/HSD | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 803 | 982 | 795 | 1000 | 881 | 486
| 61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 203 | 206 | 210 | 210 | 11 |  | Gas shortage
| 63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 320 | 315 | 310 | 300 | 60 |  | Gas shortage
| 64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 310 | 305 | 310 | 300 | 60 |  | Gas shortage
|  | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+136*1 | 284 | 284 | 0 | 0 | 0 | 0 |  |  | On test.
| 65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 39 | 39 | 35 | 39 |  | 6 | Engine problem
| 66 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 55 | 50 | 54 | 55 | 55
| 67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 129 | 123 | 122 | 123 |  | 27 | Engine problem
| 70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 36 | 36 | 29 | 36 |  | 16 | Engine problem
| 71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 90 | 90 |  | 73 | ST under S/D
| 72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 17 | 100 | 17 | 100 | 100 |  | Fuel shortage
| 73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 9 | 7 | 10 | 10
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 148 | 156 | 143 | 166
| 75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 24 | 33 | 30 | 33
| 76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 8 | 0 | 8 | 44 |  | Fuel shortage
| 77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 14 | 14 | 14 | 14 |  | 11 | Engine problem
| 78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 140 | 190 | 190 | 190
| 79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 0 | 0 | 114 |  | Fuel shortage
| 80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 105 | 112 | 105 | 113
| 81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 15 | 17 | 35 | 35 |  | 19 | 33 kV feeder fault
| 82 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 53 | 87 | 55 | 87 | 28 |  | Fuel shortage
|  | Cumilla Area Total |  |  |  |  | 3193 | 3169 | 1693 | 1883 | 1841 | 1990 | 738 | 152
| 83 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 68 | 102 | 70 | 110 | 92 |  | Gas shortage
| 84 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  |  | Engine problem
| 85 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0 |  | 8 | Under maint.
| 86 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 87 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 87 | 144 | 90 | 144 | 56 |  | Fuel shortage
| 88 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 115 | 97 | 97 | 115
| 89 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 32 | 0 | 50 | 0
| 90 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 6 | 12 |  | 10 | Engine problem
|  | Mymensingh Area Total |  |  |  |  | 717 | 614 | 316 | 355 | 314.6 | 381 | 92 | 18
| 91 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 43 | 43 | 43 |  | 27 | Machine problem.
| 92 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 41 | 41 | 41 | 41 |  | 49 | Machine problem
| 93 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 112 | 112 | 112 |  | 51 | ST under S/D
| 94 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
| 95 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 11 | 17 | 17 | 17 | 34
| 96 | Fenchuganj 44MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 10 | 16 | 16 | 16 |  | 34 | Engine problem
| 97 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| 98 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 60 | 61 | 60 | 63
| 99 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 78 | 81 | 81 | 81
| 100 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
| 101 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 193 | 193 | 193 | 193 |  | 38 | Machine problem
| 102 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18 | 2
| 103 | Sylhet 50MW PP (EPL) |  | Gas | NENP | 27*2 | 50 | 50 | 22 | 25 | 25 | 25 | 25 |  | Gas shortage
| 104 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 8 | 8 | 8 | 8 | 17
| 105 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 310 | 300 | 310 |  |  | FGMO
| 106 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 140 | 0 | 0 | 0 |  |  | Under maint
| 107 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| 108 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 398 | 400 | 400 | 400
|  | Sylhet Area Total |  |  |  |  | 2522 | 2477 | 1340 | 1346 | 1335 | 1348 | 78 | 629
| 109 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 896 | 805 | 912 | 918 |  |  | .
| 110 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 0 | 16 | 0 | 16 | 99 |  | Fuel shortage
| 111 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 41 | 0 | 41 |  | 13 | Engine problem
| 112 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 222 | 222 | 225 | 225
| 113 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 55 | 0 | 55 |  | 54 | Engine problem
| 114 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 200 | 175 | 180 | 200 | 210 |  | Gas shortage
| 115 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 0 | 0 | 0 | 40 |  | Fuel shortage
| 116 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 20 | 92 | 90 | 93 |  | 7 | Engine problem
| 117 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 56 | 74 | 53 | 74 | 31 |  | Fuel shortage
| 118 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 15 | 32 | 15 | 32 | 73 |  | Fuel shortage
| 119 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 71 | 0 | 100 | 0
|  | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
|  | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
|  | Khulna Area Total |  |  |  |  | 2388 | 2384 | 1480 | 1512 | 1575 | 1654 | 469 | 74
| 120 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 16 | 48 | 32 | 48 |  |  | Line O/L
| 121 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 22 | 35 | 22 | 35 |  | 5 | Engine problem
| 122 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 84 | 85 | 83 | 85 |  |  | Machine problem
|  | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
| 123 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 970 | 1120 | 1000 | 1170 |  |  | Line O/L
| 124 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 223 | 221 | 220 | 220
| 125 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 0 | 17 |  |  | Line O/L
|  | Barisal Area Total |  |  |  |  | 1958 | 1958 | 1315 | 1509 | 1357 | 1575 | 0 | 5
| 126 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 127 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 24 | 0 | 24 |  | 28 | Engine problem
| 128 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 24 | 36 | 0 | 36 |  | 35 | Engine problem
| 129 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 130 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 34 | 42 | 34 | 42 |  | 8 | Engine problem
| 131 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 32 | 0 | 32 |  | 18 | Engine problem
| 132 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 205 | 191 | 190 | 206 | 4 |  | Gas shortage
| 133 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 216 | 217 | 220 | 220
| 134 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 176 | 183 | 165 | 185 | 35 |  | Gas shortage
| 135 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 416 | 419 | 285 | 412 |  |  | Gas shortage
| 136 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 32 | 0 | 32 |  | 18 | Under maintenance
| 137 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
| 138 | Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 139 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 140 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 8 | 8 | 8 | 44 |  | Fuel shortage
| 141 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 81 | 0 | 80 |  | 24 | Engine problem
| 142 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 86 | 160 | 130 | 161 |  | 39 | Engine problem
| 143 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 50 | 94 | 50 | 94 |  | 19 | Engine problem
| 144 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 55 | 95 | 55 | 95 |  | 18 | Engine problem
| 145 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 4 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2129 | 1307 | 1647 | 1176 | 1660 | 254 | 207
| 146 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 80 | 83 | 80 | 83
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
| 147 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 250 | 250 | 250 | 250 | 24
| 148 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
| 149 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
| 150 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 55 | 92 | 55 | 92 |  | 21 | Engine problem
| 151 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 1 | 0 | 8 | 0
| 152 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 0 | 90 | 0 | 90 |  | 25 | Fuel shortage
|  | Intraco Solar 30 MW |  | Solar | IPP | 0 | 0 | 0 | 0 | 0 | 12 | 0
|  | Rangpur Area Total |  |  |  |  | 800 | 720 | 386 | 515 | 405 | 515 | 64 | 131
|  | Total |  |  |  |  | 22482 | 21680 | 11822 | 13581 | 12099.6 | 14071 | 3685 | 2468
| A. |  | 2022-08-31 | (Yesterday) |  |  |  |  | Wednesday
| 1 | Highest Generation : |  |  | 13750 | MW at | 22:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 11567 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 14745 | MW
| 3 | Day peak Generation : |  |  | 11822 | MW at | 9:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 13989.31 | MW
| 4 | Evening peak Generation : |  |  | 13581 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 1073 | MW
| 5 | Total Energy Generation : |  | 298.9292 | MKWHr | By Solar | 1.319 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
|  | By Gas : | 141.6133 | MKWHr |  | By Oil: | 92.0895 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 35.3534 | MKWHr |  | By Hydro: | 3.502 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 3685 | MW | Dhaka | 5013.47 | 4686.47 |  | 327 |  | 18:00 |  | 558
|  |  |  | For Plants S/D or M/C prob = |  |  | 2468 | MW | Chittagong | 1362.6 | 1362.6 |  | 0 |  | 19:00 |  | 871.81
|  |  |  | Total = |  |  | 6153 | MW | Khulna | 1739 | 1443 |  | 296 |  | 19:30 |  | 996.2226
| 7 | Total Gas Supplied : |  |  | 1085.51 | MMCFD |  |  | Rajshahi | 1412.7 | 1412.7 |  | 0 |  | 20:00 |  | 1057.9681
| 8 | Fuel Cost : | i) Gas : | Taka | 163367392.704 | ii) Oil : | Taka | 1395049073.12 | Comilla | 1446 | 1260 |  | 186 |  | 21:00 |  | 1072.7133
|  |  | iii) Coal : |  | 289831004.55 | Total | Taka | 1848247470.374 | Mymensingh | 1203 | 997 |  | 206 |  | 22:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0 | MKWHr. | Sylhet | 587 | 529 |  | 58 |  | 23:00 |  | 0
|  | ii) During Peak Demand : |  |  | 1320 | MW (E to W) at | 21:00 | hrs | Barisal | 402.54 | 402.54 |  | 0 |  | 24:00 |  | 0
|  | iii) Maximum : |  |  | 990 | MW at | 24:00 | hrs | Rangpur | 823 | 823 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 35.6° C |  |  | Total | 13989.31 | 12916.31 |  | 1073
| B. |  | 2022-09-01 | (Today) |  |  |  | Thursday |  |  | Probable max. temperature in Dhaka |  |  | 32.9° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 14700 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 580 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14071 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 12900 | MW
| 4 | Reserve(Generation end) |  |  |  | - | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 319.5825 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 11508 | MW at | 8:00 | 134 | 43 | 91 | 42 | 85 | 116 | 24 | 0 | 45
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.216 | MKWHr. | ii) HVDC Flow at Peak Time |  | 805 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.8362 | MKWHr. | iii) Maximum HVDC Flow : |  | 897 | MW at | 8:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 96.43 |  | (b) Today: | 96.38 |  | (c) Rule Curve: |  | 99
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2022-08-31
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 104 | 170 | 260 | 0 | 0 | 375 | 175 |  | 0 | 225 | 123 | 59 | 0 | 55 | 250 | 0 | 0 | 66 | 50 | 46 | 0 | 0 | 0 | 0 | 54 | 17 | 35 | 19 | 25 | 27 | 33 | 18 | 16 | 0 | 77 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 17 | 10 | 11 | 25 | 17 | 35 | 0 | 0 | 0 | 335 | 320 | 204 | 8 | 0 | 44 | 53 | 0 | 51 | 0 | 39 | 0 | 22 | 9 | 33 | 14 | 162 | 131 | 0 | 0 | 0 | 43 | 41 | 11 | 10 | 0 | 0 | 62 | 81 | 0 | 193 | 18 | 22 | 10 | 320 | 8 | 11 | 190 | 281 | 175 | 80 | 87 | 80 | 136 | 0 | 10 | 17 | 142 | 140 | 115 | 34 | 97 | 0 | 52 | 36 | 103 | 0 | 103 | 10 | 395 | 55 | 0 | 35 | 96 | 0 | 17 | 0 | 95 | 0 | 0 | 0 | 0 |  | 896 | 0 | 215 | 0 | 0 | 222 | 0 | 0 | 10 | 42 | 0 | 85 | 33 | 32 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 34 | 24 | 8 | 0 | 22 | 0 | 11 | 80 | 0 | 250 | 0 | 0 | 205 | 0 | 0 | 214 | 0 | 20 | 177 | 0 | 416 | 56 | 163 | 50 | 15 | 56 | 0 | 0 | 95 | 1140 | 222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 7473 | 4797 | 12270 | 4124 | 896 | 1817 | 708 | 2302 | 1470 | 147 | 436 | 422 | 162 | 0 | 1410.0097 | 96.43
2:00 | 0 | 0 | 97 | 170 | 260 | 0 | 0 | 379 | 186 |  | 0 | 225 | 128 | 58 | 0 | 55 | 250 | 0 | 0 | 61 | 50 | 46 | 0 | 0 | 0 | 0 | 54 | 17 | 35 | 19 | 25 | 27 | 33 | 18 | 16 | 0 | 77 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 17 | 10 | 11 | 25 | 17 | 36 | 0 | 0 | 0 | 315 | 300 | 206 | 8 | 0 | 44 | 55 | 0 | 51 | 0 | 34 | 0 | 22 | 9 | 33 | 12 | 162 | 141 | 0 | 0 | 0 | 43 | 41 | 11 | 10 | 0 | 0 | 62 | 81 | 0 | 193 | 19 | 22 | 10 | 325 | 8 | 11 | 190 | 286 | 175 | 80 | 87 | 80 | 135 | 0 | 10 | 17 | 142 | 140 | 115 | 34 | 81 | 0 | 52 | 36 | 100 | 0 | 104 | 10 | 396 | 45 | 0 | 35 | 107 | 0 | 17 | 0 | 95 | 0 | 0 | 0 | 0 |  | 896 | 0 | 215 | 0 | 0 | 224 | 0 | 0 | 10 | 42 | 0 | 84 | 34 | 32 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 34 | 0 | 8 | 0 | 22 | 0 | 11 | 80 | 0 | 250 | 0 | 0 | 206 | 0 | 0 | 214 | 0 | 65 | 177 | 0 | 415 | 56 | 163 | 50 | 15 | 56 | 0 | 0 | 95 | 1140 | 224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 7442 | 4822 | 12264 | 4093 | 896 | 1843 | 753 | 2283 | 1470 | 147 | 438 | 393 | 162 | 0 | 1231.2242 | 96.43
3:00 | 0 | 0 | 105 | 170 | 260 | 0 | 0 | 385 | 192 |  | 0 | 225 | 128 | 58 | 0 | 55 | 260 | 0 | 0 | 61 | 50 | 46 | 0 | 0 | 0 | 0 | 54 | 17 | 35 | 19 | 25 | 27 | 33 | 21 | 16 | 0 | 75 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 17 | 10 | 11 | 25 | 17 | 37 | 0 | 0 | 0 | 345 | 330 | 205 | 8 | 0 | 44 | 55 | 0 | 51 | 0 | 33 | 0 | 22 | 9 | 33 | 12 | 160 | 143 | 0 | 0 | 0 | 43 | 41 | 11 | 10 | 0 | 0 | 60 | 81 | 0 | 193 | 18 | 22 | 10 | 320 | 8 | 11 | 191 | 296 | 175 | 80 | 87 | 80 | 134 | 0 | 10 | 17 | 143 | 140 | 115 | 34 | 87 | 0 | 52 | 36 | 110 | 0 | 105 | 10 | 396 | 55 | 0 | 35 | 107 | 0 | 17 | 0 | 74 | 0 | 0 | 0 | 0 |  | 895 | 0 | 220 | 0 | 0 | 223 | 0 | 0 | 0 | 42 | 0 | 84 | 33 | 32 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 34 | 0 | 8 | 0 | 22 | 0 | 11 | 80 | 0 | 250 | 0 | 0 | 205 | 0 | 0 | 214 | 0 | 93 | 177 | 0 | 414 | 56 | 163 | 50 | 15 | 56 | 0 | 0 | 95 | 1130 | 224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 7541 | 4830 | 12371 | 4182 | 895 | 1843 | 782 | 2299 | 1460 | 145 | 437 | 382 | 160 | 0 | 1040.4582 | 96.43
4:00 | 0 | 0 | 110 | 170 | 260 | 0 | 0 | 386 | 200 |  | 0 | 225 | 132 | 59 | 0 | 55 | 260 | 0 | 0 | 61 | 50 | 46 | 0 | 0 | 0 | 0 | 54 | 17 | 35 | 19 | 25 | 27 | 33 | 21 | 16 | 0 | 75 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 17 | 10 | 11 | 25 | 17 | 38 | 0 | 0 | 0 | 320 | 305 | 206 | 8 | 0 | 44 | 55 | 0 | 51 | 0 | 38 | 0 | 22 | 9 | 33 | 12 | 158 | 144 | 0 | 0 | 0 | 43 | 41 | 11 | 10 | 0 | 0 | 60 | 81 | 0 | 193 | 18 | 22 | 10 | 315 | 8 | 11 | 190 | 296 | 175 | 80 | 87 | 80 | 142 | 0 | 10 | 17 | 137 | 140 | 115 | 34 | 87 | 0 | 52 | 36 | 110 | 0 | 105 | 10 | 398 | 55 | 0 | 35 | 107 | 0 | 17 | 0 | 73 | 0 | 0 | 0 | 0 |  | 895 | 0 | 220 | 0 | 0 | 224 | 0 | 0 | 0 | 37 | 0 | 86 | 30 | 16 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 34 | 0 | 8 | 0 | 22 | 0 | 11 | 80 | 0 | 250 | 0 | 0 | 205 | 0 | 0 | 214 | 0 | 93 | 177 | 0 | 417 | 56 | 163 | 50 | 15 | 56 | 0 | 0 | 95 | 1100 | 224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 7513 | 4816 | 12329 | 4144 | 895 | 1851 | 781 | 2285 | 1430 | 145 | 438 | 416 | 158 | 0 | 940.9281 | 96.43
5:00 | 0 | 0 | 110 | 170 | 270 | 0 | 0 | 391 | 207 |  | 0 | 225 | 128 | 59 | 0 | 55 | 260 | 0 | 0 | 61 | 50 | 15 | 0 | 0 | 0 | 0 | 17 | 17 | 35 | 19 | 25 | 27 | 33 | 21 | 16 | 0 | 75 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 17 | 10 | 11 | 25 | 17 | 39 | 0 | 0 | 0 | 325 | 310 | 206 | 8 | 0 | 44 | 55 | 0 | 51 | 0 | 46 | 0 | 22 | 9 | 33 | 12 | 156 | 144 | 0 | 0 | 0 | 43 | 41 | 11 | 10 | 0 | 0 | 60 | 81 | 0 | 193 | 18 | 22 | 10 | 320 | 8 | 11 | 188 | 288 | 176 | 80 | 87 | 80 | 149 | 0 | 10 | 17 | 135 | 140 | 115 | 34 | 87 | 0 | 52 | 36 | 110 | 0 | 105 | 10 | 395 | 56 | 0 | 35 | 107 | 0 | 17 | 0 | 74 | 0 | 0 | 0 | 0 |  | 895 | 0 | 220 | 0 | 0 | 224 | 0 | 0 | 0 | 37 | 0 | 84 | 30 | 16 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 34 | 0 | 8 | 0 | 22 | 0 | 11 | 82 | 0 | 250 | 0 | 0 | 206 | 0 | 0 | 214 | 0 | 93 | 177 | 0 | 417 | 56 | 163 | 50 | 15 | 56 | 0 | 0 | 95 | 1090 | 224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 7480 | 4798 | 12278 | 4165 | 895 | 1860 | 780 | 2247 | 1422 | 145 | 438 | 384 | 156 | 0 | 573.2196 | 96.43
6:00 | 0 | 0 | 108 | 170 | 270 | 0 | 0 | 391 | 212 |  | 0 | 225 | 128 | 58 | 0 | 55 | 260 | 0 | 0 | 61 | 50 | 15 | 0 | 0 | 0 | 0 | 17 | 17 | 35 | 19 | 25 | 27 | 33 | 21 | 16 | 0 | 75 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 17 | 10 | 11 | 25 | 17 | 37 | 0 | 0 | 0 | 285 | 270 | 207 | 8 | 0 | 44 | 55 | 0 | 51 | 0 | 29 | 0 | 22 | 9 | 33 | 12 | 146 | 131 | 0 | 0 | 0 | 43 | 41 | 11 | 10 | 0 | 0 | 60 | 81 | 0 | 193 | 18 | 22 | 10 | 295 | 8 | 11 | 189 | 286 | 176 | 80 | 87 | 80 | 149 | 0 | 10 | 17 | 137 | 140 | 115 | 34 | 73 | 0 | 52 | 36 | 110 | 0 | 105 | 10 | 400 | 55 | 1 | 35 | 107 | 0 | 17 | 1 | 74 | 0 | 0 | 0 | 0 |  | 895 | 0 | 210 | 0 | 0 | 225 | 0 | 0 | 0 | 30 | 0 | 85 | 25 | 16 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 34 | 0 | 8 | 0 | 22 | 0 | 11 | 79 | 0 | 250 | 0 | 0 | 206 | 0 | 0 | 217 | 0 | 60 | 176 | 0 | 402 | 56 | 162 | 50 | 15 | 56 | 0 | 0 | 55 | 1050 | 224 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 |  | 7329 | 4644 | 11973 | 4066 | 895 | 1818 | 747 | 2191 | 1379 | 145 | 442 | 358 | 146 | 3 | 301.355 | 96.43
7:00 | 0 | 0 | 103 | 170 | 270 | 0 | 0 | 391 | 207 |  | 0 | 225 | 128 | 56 | 0 | 55 | 260 | 0 | 0 | 61 | 50 | 15 | 0 | 0 | 0 | 0 | 17 | 17 | 35 | 16 | 25 | 27 | 33 | 0 | 16 | 0 | 75 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 17 | 10 | 11 | 25 | 17 | 33 | 0 | 0 | 0 | 280 | 270 | 207 | 8 | 0 | 44 | 55 | 0 | 51 | 0 | 27 | 0 | 22 | 9 | 33 | 14 | 146 | 104 | 0 | 0 | 0 | 43 | 41 | 11 | 10 | 0 | 0 | 60 | 78 | 0 | 193 | 18 | 22 | 10 | 300 | 8 | 11 | 190 | 278 | 176 | 80 | 87 | 80 | 149 | 4 | 10 | 17 | 132 | 140 | 115 | 34 | 69 | 0 | 52 | 36 | 110 | 0 | 106 | 10 | 400 | 55 | 9 | 35 | 107 | 0 | 17 | 4 | 54 | 0 | 0 | 0 | 0 |  | 896 | 0 | 210 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 85 | 24 | 16 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 34 | 0 | 8 | 0 | 22 | 0 | 11 | 81 | 0 | 250 | 0 | 0 | 205 | 0 | 0 | 217 | 0 | 50 | 176 | 0 | 420 | 56 | 161 | 50 | 15 | 56 | 0 | 0 | 55 | 1010 | 224 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 |  | 7239 | 4596 | 11835 | 4006 | 896 | 1828 | 737 | 2153 | 1341 | 145 | 442 | 326 | 146 | 32 | 474.6111 | 96.43
8:00 | 0 | 0 | 110 | 170 | 270 | 0 | 0 | 391 | 251 |  | 0 | 225 | 132 | 56 | 0 | 55 | 270 | 0 | 0 | 61 | 58 | 15 | 0 | 0 | 0 | 0 | 17 | 17 | 35 | 16 | 25 | 0 | 33 | 21 | 16 | 0 | 78 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 17 | 10 | 11 | 25 | 17 | 14 | 0 | 0 | 0 | 280 | 270 | 205 | 8 | 0 | 43 | 55 | 0 | 51 | 0 | 30 | 0 | 22 | 9 | 30 | 14 | 142 | 68 | 0 | 0 | 1 | 43 | 41 | 11 | 10 | 0 | 0 | 61 | 78 | 0 | 193 | 18 | 22 | 10 | 280 | 8 | 11 | 150 | 278 | 175 | 80 | 87 | 80 | 149 | 10 | 10 | 17 | 129 | 140 | 115 | 34 | 69 | 1 | 52 | 36 | 110 | 0 | 106 | 10 | 400 | 55 | 13 | 35 | 107 | 0 | 6 | 14 | 53 | 0 | 0 | 0 | 0 |  | 897 | 0 | 205 | 0 | 0 | 224 | 0 | 0 | 0 | 0 | 0 | 86 | 23 | 16 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 34 | 0 | 8 | 0 | 22 | 0 | 11 | 80 | 0 | 250 | 0 | 0 | 206 | 0 | 0 | 219 | 0 | 20 | 176 | 0 | 370 | 56 | 50 | 50 | 15 | 55 | 0 | 1 | 55 | 980 | 214 | 0 | 0 | 1 | 24 | 0 | 0 | 0 | 0 | 0 |  | 7194 | 4373 | 11567 | 3973 | 897 | 1776 | 555 | 2145 | 1310 | 148 | 443 | 332 | 142 | 65 | #REF! | 96.42
9:00 | 0 | 0 | 110 | 170 | 270 | 0 | 0 | 408 | 257 |  | 0 | 225 | 138 | 57 | 0 | 55 | 275 | 0 | 0 | 61 | 58 | 15 | 0 | 0 | 0 | 0 | 17 | 17 | 35 | 16 | 25 | 0 | 33 | 18 | 16 | 0 | 75 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 17 | 10 | 11 | 25 | 17 | 5 | 0 | 0 | 0 | 320 | 310 | 203 | 8 | 0 | 39 | 50 | 0 | 51 | 0 | 36 | 0 | 22 | 9 | 24 | 14 | 148 | 68 | 0 | 0 | 2 | 43 | 41 | 11 | 10 | 0 | 0 | 60 | 78 | 0 | 193 | 18 | 22 | 10 | 300 | 8 | 8 | 140 | 276 | 175 | 80 | 87 | 80 | 149 | 16 | 10 | 17 | 129 | 140 | 115 | 34 | 69 | 2 | 52 | 36 | 110 | 0 | 105 | 10 | 398 | 55 | 32 | 35 | 107 | 0 | 15 | 22 | 53 | 0 | 0 | 0 | 0 |  | 896 | 0 | 200 | 0 | 0 | 222 | 0 | 0 | 0 | 0 | 0 | 84 | 22 | 16 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 34 | 0 | 8 | 0 | 22 | 0 | 11 | 80 | 0 | 250 | 0 | 0 | 205 | 0 | 0 | 216 | 0 | 20 | 176 | 0 | 416 | 56 | 86 | 50 | 15 | 55 | 0 | 1 | 55 | 970 | 223 | 0 | 0 | 4 | 71 | 0 | 0 | 0 | 0 | 0 |  | 7334 | 4488 | 11822 | 4046 | 896 | 1848 | 581 | 2152 | 1300 | 145 | 438 | 334 | 148 | 150 | #REF! | 96.42
10:00 | 0 | 0 | 110 | 170 | 270 | 0 | 0 | 408 | 217 |  | 0 | 225 | 130 | 58 | 0 | 55 | 275 | 0 | 0 | 61 | 58 | 15 | 0 | 0 | 0 | 0 | 17 | 17 | 35 | 16 | 25 | 0 | 33 | 18 | 16 | 0 | 76 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 17 | 10 | 11 | 25 | 17 | 2 | 0 | 0 | 0 | 310 | 305 | 202 | 8 | 0 | 33 | 49 | 0 | 51 | 0 | 36 | 0 | 22 | 8 | 22 | 14 | 154 | 68 | 0 | 0 | 1 | 43 | 41 | 11 | 10 | 0 | 0 | 60 | 78 | 0 | 193 | 18 | 22 | 10 | 290 | 5 | 11 | 180 | 273 | 130 | 80 | 86 | 80 | 147 | 18 | 10 | 17 | 127 | 140 | 105 | 34 | 69 | 5 | 52 | 20 | 110 | 0 | 103 | 10 | 400 | 60 | 42 | 35 | 107 | 0 | 17 | 23 | 53 | 0 | 0 | 0 | 0 |  | 895 | 0 | 200 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 85 | 22 | 16 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 34 | 0 | 8 | 0 | 22 | 0 | 11 | 81 | 0 | 250 | 0 | 0 | 194 | 0 | 0 | 216 | 0 | 10 | 175 | 0 | 415 | 56 | 100 | 50 | 15 | 51 | 0 | 1 | 55 | 970 | 223 | 0 | 0 | 5 | 88 | 0 | 0 | 0 | 0 | 0 |  | 7238 | 4492 | 11730 | 4012 | 895 | 1785 | 580 | 2120 | 1301 | 146 | 436 | 334 | 154 | 183 | #REF! | 96.41
11:00 | 0 | 0 | 112 | 170 | 260 | 0 | 0 | 399 | 208 |  | 0 | 225 | 130 | 59 | 0 | 55 | 275 | 0 | 0 | 61 | 58 | 15 | 0 | 0 | 0 | 0 | 17 | 17 | 35 | 13 | 25 | 0 | 33 | 18 | 16 | 0 | 77 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 17 | 10 | 11 | 25 | 17 | 2 | 0 | 0 | 0 | 310 | 310 | 205 | 8 | 0 | 30 | 49 | 0 | 51 | 0 | 24 | 0 | 21 | 8 | 25 | 14 | 154 | 68 | 0 | 0 | 1 | 43 | 41 | 11 | 10 | 78 | 0 | 62 | 78 | 0 | 193 | 18 | 22 | 10 | 300 | 8 | 11 | 186 | 263 | 170 | 80 | 97 | 80 | 140 | 15 | 10 | 17 | 124 | 0 | 105 | 34 | 69 | 5 | 52 | 17 | 91 | 0 | 94 | 10 | 395 | 61 | 53 | 35 | 107 | 0 | 17 | 31 | 53 | 0 | 0 | 0 | 0 |  | 895 | 0 | 200 | 0 | 0 | 222 | 0 | 0 | 0 | 0 | 0 | 81 | 22 | 16 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 34 | 0 | 8 | 0 | 18 | 0 | 11 | 80 | 0 | 250 | 0 | 0 | 192 | 0 | 0 | 212 | 0 | 30 | 137 | 0 | 418 | 56 | 131 | 50 | 15 | 55 | 0 | 1 | 55 | 970 | 202 | 0 | 0 | 5 | 91 | 0 | 0 | 0 | 0 | 0 |  | 7177 | 4481 | 11658 | 3815 | 895 | 1842 | 677 | 2086 | 1300 | 147 | 434 | 318 | 154 | 202 | #REF! | 96.42
12:00 | 0 | 0 | 110 | 170 | 250 | 0 | 0 | 391 | 196 |  | 0 | 225 | 128 | 58 | 0 | 55 | 275 | 0 | 0 | 61 | 58 | 28 | 0 | 0 | 0 | 0 | 17 | 17 | 35 | 13 | 25 | 0 | 33 | 18 | 16 | 0 | 77 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 0 | 17 | 10 | 11 | 25 | 17 | 2 | 0 | 0 | 0 | 320 | 310 | 200 | 8 | 0 | 32 | 51 | 0 | 51 | 0 | 29 | 0 | 21 | 8 | 25 | 14 | 158 | 68 | 0 | 0 | 2 | 43 | 41 | 11 | 10 | 112 | 0 | 59 | 78 | 0 | 194 | 18 | 22 | 10 | 310 | 8 | 11 | 182 | 260 | 172 | 80 | 95 | 80 | 149 | 16 | 10 | 17 | 122 | 0 | 106 | 34 | 69 | 5 | 52 | 17 | 90 | 0 | 89 | 10 | 392 | 70 | 36 | 37 | 107 | 0 | 17 | 31 | 51 | 0 | 0 | 0 | 0 |  | 897 | 0 | 190 | 0 | 0 | 219 | 0 | 0 | 0 | 0 | 0 | 83 | 22 | 16 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 34 | 5 | 8 | 0 | 18 | 0 | 11 | 82 | 0 | 249 | 0 | 0 | 191 | 0 | 0 | 190 | 0 | 70 | 143 | 0 | 414 | 56 | 117 | 50 | 15 | 56 | 0 | 2 | 55 | 980 | 220 | 0 | 0 | 4 | 70 | 0 | 0 | 0 | 0 | 1 |  | 7175 | 4491 | 11666 | 3794 | 897 | 1888 | 701 | 2092 | 1311 | 147 | 409 | 292 | 158 | 167 | #REF! | 96.42
13:00 | 0 | 0 | 111 | 170 | 250 | 0 | 0 | 386 | 196 |  | 0 | 225 | 128 | 58 | 0 | 55 | 270 | 0 | 0 | 61 | 58 | 15 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 13 | 25 | 0 | 33 | 15 | 16 | 0 | 77 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 0 | 17 | 10 | 11 | 0 | 17 | 2 | 0 | 0 | 0 | 325 | 305 | 197 | 8 | 0 | 32 | 48 | 0 | 51 | 0 | 29 | 0 | 21 | 8 | 25 | 14 | 158 | 66 | 0 | 0 | 1 | 43 | 41 | 17 | 15 | 112 | 0 | 57 | 81 | 0 | 194 | 18 | 27 | 10 | 310 | 8 | 11 | 182 | 260 | 172 | 80 | 105 | 80 | 149 | 13 | 10 | 17 | 120 | 0 | 106 | 34 | 69 | 4 | 52 | 17 | 110 | 0 | 89 | 10 | 384 | 73 | 44 | 69 | 101 | 0 | 17 | 34 | 48 | 0 | 0 | 0 | 0 |  | 896 | 0 | 190 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 81 | 23 | 16 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 34 | 16 | 8 | 0 | 21 | 0 | 11 | 81 | 0 | 250 | 0 | 0 | 190 | 0 | 0 | 209 | 0 | 92 | 149 | 0 | 414 | 56 | 156 | 50 | 15 | 56 | 0 | 1 | 55 | 1000 | 212 | 0 | 0 | 5 | 100 | 0 | 0 | 0 | 0 | 3 |  | 7224 | 4629 | 11853 | 3770 | 896 | 1900 | 762 | 2159 | 1331 | 147 | 423 | 311 | 158 | 205 | 964.889 | 96.42
14:00 | 0 | 0 | 110 | 170 | 250 | 0 | 0 | 385 | 198 |  | 0 | 225 | 128 | 58 | 0 | 55 | 270 | 0 | 0 | 61 | 58 | 15 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 13 | 25 | 0 | 33 | 15 | 16 | 0 | 78 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 0 | 17 | 10 | 10 | 6 | 17 | 2 | 0 | 0 | 0 | 315 | 305 | 203 | 8 | 0 | 34 | 47 | 0 | 51 | 0 | 30 | 0 | 21 | 8 | 30 | 14 | 166 | 65 | 0 | 0 | 0 | 43 | 41 | 17 | 15 | 112 | 0 | 59 | 81 | 0 | 194 | 18 | 27 | 10 | 300 | 8 | 11 | 185 | 260 | 172 | 80 | 105 | 80 | 149 | 5 | 10 | 17 | 119 | 0 | 98 | 34 | 69 | 4 | 52 | 17 | 110 | 0 | 99 | 10 | 400 | 84 | 24 | 70 | 107 | 0 | 17 | 31 | 35 | 0 | 0 | 0 | 0 |  | 896 | 0 | 190 | 0 | 0 | 216 | 0 | 0 | 0 | 0 | 0 | 83 | 25 | 16 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 34 | 16 | 8 | 0 | 21 | 0 | 11 | 81 | 0 | 250 | 0 | 0 | 192 | 0 | 0 | 209 | 0 | 92 | 162 | 0 | 414 | 56 | 156 | 50 | 15 | 56 | 0 | 2 | 55 | 1010 | 208 | 0 | 0 | 2 | 11 | 90 | 0 | 0 | 0 | 8 |  | 7225 | 4657 | 11882 | 3805 | 896 | 1889 | 765 | 2260 | 1341 | 148 | 425 | 309 | 166 | 87 | 984.2421 | 96.42
15:00 | 0 | 0 | 110 | 170 | 250 | 0 | 0 | 384 | 198 |  | 0 | 225 | 127 | 58 | 0 | 55 | 256 | 0 | 0 | 61 | 58 | 15 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 13 | 25 | 0 | 33 | 15 | 16 | 0 | 78 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 0 | 17 | 10 | 10 | 20 | 17 | 2 | 0 | 0 | 0 | 330 | 320 | 199 | 8 | 0 | 35 | 47 | 0 | 51 | 0 | 34 | 0 | 21 | 8 | 30 | 14 | 170 | 65 | 0 | 0 | 1 | 43 | 41 | 17 | 15 | 112 | 0 | 60 | 78 | 0 | 194 | 18 | 27 | 10 | 300 | 8 | 11 | 185 | 260 | 174 | 80 | 114 | 80 | 149 | 7 | 10 | 17 | 118 | 0 | 87 | 34 | 65 | 3 | 52 | 17 | 110 | 0 | 100 | 10 | 392 | 91 | 34 | 108 | 107 | 0 | 17 | 15 | 52 | 0 | 0 | 0 | 0 |  | 896 | 0 | 185 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 82 | 25 | 16 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 34 | 21 | 8 | 0 | 21 | 0 | 11 | 81 | 0 | 250 | 0 | 0 | 191 | 0 | 0 | 187 | 0 | 92 | 167 | 0 | 414 | 56 | 120 | 50 | 15 | 50 | 0 | 2 | 55 | 1010 | 216 | 0 | 0 | 3 | 18 | 91 | 0 | 0 | 0 | 8 |  | 7302 | 4611 | 11913 | 3808 | 896 | 1893 | 731 | 2325 | 1341 | 148 | 401 | 296 | 170 | 91 | 1001.752 | 96.41
16:00 | 0 | 0 | 110 | 170 | 250 | 0 | 0 | 384 | 199 |  | 0 | 225 | 127 | 58 | 0 | 55 | 256 | 0 | 0 | 61 | 50 | 15 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 13 | 25 | 3 | 33 | 18 | 16 | 0 | 76 | 70 | 110 | 0 | 19 | 0 | 0 | 0 | 0 |  | 12 | 0 | 17 | 10 | 10 | 24 | 17 | 2 | 0 | 0 | 0 | 315 | 305 | 201 | 8 | 0 | 35 | 46 | 0 | 51 | 0 | 34 | 0 | 0 | 0 | 33 | 14 | 168 | 71 | 0 | 0 | 1 | 43 | 41 | 25 | 30 | 112 | 0 | 63 | 81 | 0 | 193 | 18 | 0 | 10 | 300 | 8 | 11 | 190 | 258 | 170 | 80 | 115 | 80 | 149 | 7 | 10 | 17 | 118 | 0 | 88 | 34 | 69 | 1 | 52 | 21 | 110 | 0 | 104 | 10 | 400 | 92 | 23 | 124 | 107 | 0 | 17 | 8 | 72 | 0 | 0 | 0 | 0 |  | 896 | 0 | 185 | 0 | 0 | 217 | 0 | 0 | 0 | 0 | 0 | 85 | 23 | 16 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 34 | 32 | 8 | 0 | 20 | 0 | 11 | 83 | 0 | 250 | 0 | 0 | 191 | 0 | 0 | 170 | 0 | 60 | 176 | 0 | 414 | 56 | 80 | 57 | 15 | 56 | 0 | 4 | 95 | 1010 | 213 | 0 | 0 | 1 | 51 | 90 | 0 | 0 | 0 | 14 |  | 7303 | 4635 | 11938 | 3788 | 896 | 1886 | 660 | 2434 | 1343 | 146 | 387 | 290 | 168 | 110 | 886.5552 | 96.41
17:00 | 0 | 0 | 110 | 170 | 240 | 0 | 0 | 381 | 198 |  | 0 | 225 | 125 | 66 | 0 | 55 | 259 | 0 | 0 | 61 | 50 | 15 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 13 | 33 | 15 | 16 | 0 | 75 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 0 | 17 | 10 | 10 | 24 | 17 | 13 | 0 | 0 | 0 | 310 | 305 | 202 | 8 | 0 | 36 | 47 | 0 | 51 | 0 | 38 | 0 | 5 | 7 | 33 | 14 | 162 | 71 | 0 | 0 | 0 | 43 | 41 | 25 | 30 | 112 | 0 | 61 | 81 | 0 | 193 | 18 | 13 | 10 | 310 | 8 | 11 | 189 | 252 | 182 | 90 | 115 | 80 | 149 | 2 | 10 | 32 | 115 | 0 | 88 | 105 | 81 | 0 | 52 | 36 | 110 | 0 | 109 | 10 | 400 | 92 | 5 | 144 | 107 | 0 | 17 | 7 | 73 | 0 | 0 | 0 | 0 |  | 896 | 0 | 175 | 0 | 0 | 218 | 0 | 0 | 0 | 20 | 0 | 84 | 23 | 16 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 42 | 32 | 8 | 0 | 20 | 0 | 11 | 82 | 0 | 250 | 0 | 0 | 192 | 0 | 0 | 130 | 0 | 30 | 173 | 0 | 414 | 56 | 40 | 70 | 15 | 91 | 0 | 2 | 95 | 1010 | 211 | 0 | 0 | 1 | 25 | 90 | 0 | 0 | 0 | 4 |  | 7481 | 4548 | 12029 | 3785 | 896 | 1916 | 611 | 2634 | 1342 | 145 | 348 | 274 | 162 | 46 | 710.5343 | 96.41
18:00 | 0 | 0 | 110 | 170 | 240 | 0 | 0 | 377 | 196 |  | 0 | 225 | 125 | 86 | 0 | 55 | 257 | 0 | 0 | 76 | 50 | 60 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 26 | 33 | 18 | 16 | 0 | 75 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 0 | 27 | 10 | 24 | 36 | 17 | 12 | 0 | 0 | 0 | 315 | 305 | 202 | 8 | 0 | 34 | 52 | 0 | 51 | 0 | 41 | 1 | 21 | 7 | 33 | 14 | 168 | 71 | 0 | 0 | 0 | 43 | 41 | 25 | 30 | 112 | 0 | 63 | 81 | 0 | 193 | 18 | 22 | 10 | 280 | 8 | 11 | 150 | 257 | 120 | 90 | 140 | 91 | 149 | 0 | 10 | 47 | 110 | 0 | 87 | 105 | 85 | 0 | 68 | 36 | 110 | 0 | 110 | 10 | 400 | 92 | 1 | 144 | 107 | 0 | 17 | 1 | 76 | 0 | 0 | 0 | 0 |  | 897 | 0 | 170 | 0 | 0 | 219 | 0 | 0 | 5 | 35 | 0 | 84 | 24 | 16 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 42 | 32 | 8 | 13 | 21 | 0 | 11 | 80 | 0 | 250 | 0 | 0 | 191 | 0 | 0 | 130 | 0 | 10 | 174 | 0 | 359 | 72 | 40 | 75 | 32 | 91 | 0 | 1 | 95 | 980 | 217 | 0 | 0 | 0 | 3 | 90 | 0 | 0 | 0 | 1 |  | 7599 | 4495 | 12094 | 3811 | 897 | 1850 | 501 | 2816 | 1310 | 145 | 349 | 370 | 168 | 7 | 558 | 96.41
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 100 | 170 | 235 | 0 | 0 | 378 | 232 |  | 0 | 225 | 131 | 90 | 0 | 55 | 254 | 0 | 0 | 90 | 92 | 100 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 24 | 33 | 14 | 32 | 0 | 75 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 12 | 51 | 10 | 74 | 37 | 17 | 16 | 0 | 0 | 0 | 315 | 305 | 207 | 8 | 0 | 39 | 53 | 0 | 51 | 0 | 41 | 8 | 21 | 7 | 33 | 14 | 152 | 97 | 0 | 0 | 0 | 43 | 41 | 25 | 30 | 112 | 0 | 64 | 81 | 0 | 193 | 18 | 24 | 10 | 290 | 8 | 11 | 191 | 257 | 160 | 90 | 152 | 90 | 149 | 0 | 10 | 72 | 113 | 0 | 87 | 105 | 86 | 0 | 69 | 36 | 110 | 0 | 110 | 10 | 382 | 93 | 0 | 144 | 107 | 0 | 17 | 0 | 79 | 0 | 0 | 0 | 0 |  | 885 | 0 | 170 | 0 | 16 | 222 | 0 | 0 | 39 | 45 | 0 | 77 | 31 | 48 | 0 | 0 | 0 | 24 | 40 | 60 | 0 | 42 | 32 | 8 | 32 | 22 | 0 | 11 | 81 | 0 | 250 | 0 | 0 | 190 | 0 | 0 | 166 | 0 | 92 | 182 | 0 | 356 | 74 | 91 | 94 | 32 | 92 | 0 | 0 | 95 | 990 | 182 | 0 | 0 | 0 | 0 | 91 | 0 | 0 | 0 | 0 |  | 7992 | 4862 | 12854 | 3807 | 885 | 1879 | 714 | 3087 | 1321 | 145 | 388 | 642 | 152 | 0 | 871.81 | 96.41
19:30 | 0 | 0 | 110 | 170 | 235 | 0 | 0 | 404 | 272 |  | 0 | 225 | 140 | 92 | 0 | 55 | 316 | 0 | 0 | 90 | 92 | 110 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 24 | 33 | 14 | 42 | 0 | 75 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 18 | 51 | 10 | 89 | 37 | 17 | 21 | 0 | 0 | 0 | 315 | 305 | 207 | 8 | 0 | 39 | 53 | 0 | 51 | 0 | 0 | 8 | 21 | 7 | 33 | 14 | 156 | 103 | 0 | 0 | 0 | 43 | 41 | 15 | 16 | 112 | 0 | 64 | 81 | 0 | 193 | 18 | 24 | 10 | 260 | 8 | 11 | 100 | 245 | 82 | 60 | 152 | 60 | 149 | 0 | 10 | 100 | 120 | 0 | 87 | 105 | 87 | 0 | 70 | 36 | 110 | 0 | 110 | 10 | 396 | 93 | 0 | 144 | 107 | 0 | 17 | 0 | 96 | 0 | 0 | 0 | 0 |  | 806 | 0 | 175 | 0 | 16 | 223 | 0 | 0 | 42 | 62 | 0 | 76 | 34 | 48 | 0 | 0 | 0 | 24 | 36 | 81 | 0 | 42 | 32 | 8 | 32 | 22 | 0 | 11 | 82 | 0 | 250 | 0 | 0 | 190 | 0 | 0 | 207 | 0 | 60 | 188 | 0 | 414 | 74 | 141 | 94 | 32 | 92 | 0 | 0 | 95 | 990 | 221 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 0 |  | 7929 | 4990 | 12919 | 3935 | 806 | 1979 | 503 | 3155 | 1322 | 145 | 430 | 695 | 156 | 0 | 996.2226 | 0
20:00 | 0 | 0 | 100 | 170 | 250 | 0 | 0 | 401 | 302 |  | 0 | 225 | 140 | 91 | 0 | 55 | 331 | 0 | 0 | 90 | 92 | 110 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 24 | 33 | 14 | 40 | 0 | 76 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 17 | 51 | 10 | 88 | 37 | 17 | 25 | 0 | 0 | 0 | 330 | 325 | 203 | 8 | 0 | 39 | 54 | 0 | 51 | 0 | 0 | 8 | 22 | 7 | 33 | 14 | 160 | 101 | 0 | 0 | 0 | 43 | 41 | 17 | 16 | 112 | 0 | 61 | 81 | 0 | 193 | 18 | 25 | 10 | 270 | 8 | 11 | 180 | 249 | 146 | 90 | 144 | 88 | 149 | 0 | 10 | 100 | 118 | 0 | 97 | 105 | 92 | 0 | 70 | 36 | 110 | 0 | 113 | 10 | 400 | 92 | 0 | 144 | 107 | 0 | 17 | 0 | 92 | 0 | 0 | 0 | 0 |  | 805 | 0 | 170 | 0 | 16 | 222 | 0 | 0 | 47 | 55 | 0 | 84 | 34 | 48 | 0 | 0 | 0 | 24 | 35 | 81 | 0 | 42 | 32 | 8 | 32 | 22 | 0 | 11 | 82 | 0 | 250 | 0 | 0 | 191 | 0 | 0 | 211 | 0 | 60 | 174 | 0 | 414 | 74 | 160 | 94 | 32 | 92 | 0 | 0 | 95 | 1110 | 221 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 0 |  | 8234 | 5118 | 13352 | 3973 | 805 | 2027 | 724 | 3158 | 1442 | 146 | 433 | 695 | 160 | 0 | 1057.9681 | 96.41
21:00 | 0 | 0 | 106 | 170 | 250 | 0 | 0 | 400 | 323 |  | 0 | 225 | 144 | 92 | 0 | 55 | 332 | 0 | 0 | 89 | 92 | 110 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 27 | 33 | 18 | 40 | 0 | 76 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 17 | 51 | 10 | 91 | 37 | 17 | 30 | 0 | 0 | 0 | 315 | 305 | 206 | 8 | 0 | 39 | 54 | 0 | 51 | 0 | 36 | 8 | 22 | 7 | 33 | 14 | 156 | 102 | 0 | 0 | 0 | 43 | 41 | 17 | 16 | 112 | 0 | 61 | 81 | 0 | 193 | 18 | 25 | 10 | 310 | 8 | 11 | 190 | 249 | 218 | 90 | 144 | 90 | 149 | 0 | 10 | 100 | 123 | 0 | 97 | 105 | 105 | 0 | 70 | 36 | 110 | 0 | 112 | 10 | 400 | 93 | 0 | 144 | 107 | 0 | 17 | 0 | 87 | 0 | 0 | 0 | 0 |  | 805 | 0 | 175 | 0 | 16 | 222 | 0 | 0 | 41 | 55 | 0 | 85 | 35 | 48 | 0 | 0 | 0 | 24 | 36 | 81 | 0 | 42 | 32 | 8 | 32 | 22 | 0 | 11 | 83 | 0 | 250 | 0 | 0 | 191 | 0 | 0 | 217 | 0 | 92 | 183 | 0 | 419 | 74 | 160 | 94 | 32 | 92 | 0 | 0 | 95 | 1120 | 221 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 0 |  | 8398 | 5183 | 13581 | 3970 | 805 | 2103 | 840 | 3154 | 1453 | 146 | 439 | 732 | 156 | 0 | 1072.7133 | 96.41
22:00 | 0 | 0 | 110 | 170 | 250 | 0 | 0 | 400 | 332 |  | 0 | 225 | 146 | 92 | 0 | 55 | 330 | 0 | 0 | 89 | 92 | 110 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 27 | 33 | 18 | 40 | 0 | 76 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 17 | 51 | 10 | 99 | 37 | 17 | 35 | 0 | 0 | 0 | 340 | 320 | 203 | 8 | 90 | 45 | 54 | 0 | 51 | 0 | 44 | 8 | 22 | 7 | 33 | 14 | 170 | 116 | 0 | 0 | 0 | 43 | 41 | 17 | 17 | 112 | 0 | 58 | 81 | 0 | 193 | 18 | 25 | 10 | 300 | 8 | 11 | 190 | 248 | 221 | 90 | 144 | 90 | 149 | 0 | 10 | 100 | 125 | 0 | 97 | 105 | 105 | 0 | 70 | 36 | 110 | 0 | 115 | 10 | 395 | 93 | 0 | 144 | 107 | 0 | 17 | 0 | 79 | 0 | 0 | 0 | 0 |  | 805 | 0 | 175 | 0 | 16 | 222 | 0 | 0 | 41 | 51 | 0 | 84 | 35 | 48 | 0 | 0 | 0 | 24 | 31 | 82 | 0 | 42 | 24 | 8 | 32 | 22 | 0 | 11 | 82 | 0 | 250 | 0 | 0 | 190 | 0 | 0 | 217 | 0 | 92 | 187 | 0 | 415 | 74 | 161 | 94 | 32 | 92 | 0 | 0 | 95 | 1130 | 221 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 0 |  | 8575 | 5175 | 13750 | 4113 | 805 | 2106 | 844 | 3158 | 1462 | 146 | 439 | 724 | 170 | 0 | 0 | 96.41
23:00 | 0 | 0 | 110 | 170 | 250 | 0 | 0 | 400 | 338 |  | 0 | 225 | 150 | 85 | 0 | 55 | 335 | 0 | 0 | 89 | 92 | 46 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 27 | 33 | 18 | 40 | 0 | 76 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 17 | 51 | 10 | 45 | 37 | 17 | 35 | 0 | 0 | 0 | 280 | 305 | 207 | 8 | 90 | 42 | 54 | 0 | 51 | 0 | 44 | 8 | 22 | 7 | 33 | 14 | 162 | 140 | 0 | 0 | 0 | 43 | 41 | 17 | 16 | 112 | 0 | 62 | 81 | 0 | 193 | 18 | 25 | 10 | 300 | 8 | 11 | 190 | 245 | 152 | 90 | 144 | 90 | 149 | 0 | 10 | 100 | 127 | 0 | 98 | 105 | 105 | 0 | 71 | 36 | 110 | 0 | 113 | 10 | 400 | 93 | 0 | 144 | 107 | 0 | 17 | 0 | 76 | 0 | 0 | 0 | 0 |  | 805 | 0 | 185 | 0 | 16 | 224 | 0 | 0 | 30 | 49 | 0 | 85 | 33 | 48 | 0 | 0 | 0 | 16 | 30 | 82 | 0 | 42 | 24 | 8 | 32 | 22 | 0 | 11 | 82 | 0 | 250 | 0 | 0 | 190 | 0 | 0 | 218 | 0 | 92 | 183 | 0 | 422 | 56 | 120 | 94 | 32 | 92 | 0 | 0 | 95 | 1140 | 221 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 0 |  | 8342 | 5119 | 13461 | 4084 | 805 | 2120 | 734 | 3075 | 1472 | 146 | 442 | 639 | 162 | 0 | 0 | 96.4
24:00 | 0 | 0 | 111 | 170 | 270 | 0 | 0 | 399 | 332 |  | 0 | 225 | 148 | 61 | 0 | 55 | 330 | 0 | 0 | 62 | 50 | 46 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 27 | 33 | 20 | 16 | 0 | 77 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 17 | 51 | 10 | 5 | 27 | 17 | 36 | 0 | 0 | 0 | 305 | 330 | 201 | 8 | 90 | 43 | 54 | 0 | 51 | 0 | 42 | 8 | 22 | 7 | 33 | 14 | 174 | 139 | 0 | 0 | 0 | 43 | 41 | 17 | 16 | 112 | 0 | 61 | 81 | 0 | 193 | 19 | 25 | 10 | 315 | 8 | 11 | 190 | 245 | 225 | 80 | 144 | 80 | 143 | 0 | 10 | 48 | 132 | 0 | 98 | 59 | 105 | 0 | 71 | 36 | 110 | 0 | 99 | 10 | 394 | 72 | 0 | 42 | 107 | 0 | 17 | 0 | 77 | 0 | 0 | 0 | 0 |  | 805 | 0 | 180 | 0 | 0 | 223 | 0 | 0 | 16 | 49 | 0 | 83 | 35 | 48 | 0 | 0 | 0 | 16 | 24 | 30 | 0 | 42 | 24 | 8 | 32 | 22 | 0 | 11 | 81 | 0 | 250 | 0 | 0 | 191 | 0 | 0 | 214 | 0 | 92 | 182 | 0 | 417 | 56 | 148 | 50 | 15 | 56 | 0 | 0 | 95 | 1160 | 221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 8067 | 4876 | 12943 | 4132 | 805 | 2125 | 815 | 2470 | 1491 | 147 | 437 | 561 | 174 | 0 | 0 | 96.4
KWH | 0 | 0 | 2598000 | 4142250 | 6028573 | 0 | 0 | 9504760 | 5460000 |  | 0 | 4785000 | 3176844 | 1601280 | 0 | 1333440 | 6645330 | 0 | 0 | 1645440 | 1447776 | 912480 | 0 | 0 | 0 | 0 | 859680 | 873576 | 900781 | 390600 | 600000 | 365400 | 788300 | 431400 | 509760 | 0 | 1821992 | 1680000 | 2600000 | 0 | 594239 | 0 | 0 | 0 | 0 |  | 297360 | 368184 | 623297 | 258840 | 618240 | 642720 | 408288 | 485280 | 0 | 0 | 0 | 7985600 | 7557000 | 4913000 | 217454 | 235440 | 934056 | 1248480 | 0 | 1196594 | 0 | 794512 | 54340 | 461232 | 173520 | 745800 | 327420 | 3836160 | 2317440 | 0 | 0 | 14600 | 1025000 | 939944 | 362400 | 435960 | 1484754 | 0 | 1447968 | 1914240 | 0 | 4607400 | 429000 | 552700 | 238680 | 7449000 | 178416 | 256100 | 4335936 | 6420761 | 4063031 | 1940976 | 2608800 | 1955361 | 3552048 | 101790 | 249600 | 905280 | 3044363 | 1452000 | 2473200 | 1376628 | 1977999 | 25201 | 1382509 | 782117 | 2643734 | 0 | 2514120 | 252480 | 9447400 | 1746240 | 293110 | 1844640 | 2566800 | 0 | 423720 | 209188 | 1663680 | 0 | 0 | 0 | 0 |  | 21216000 | 0 | 4802112 | 0 | 67200 | 5276160 | 0 | 0 | 221280 | 558080 | 0 | 2006127 | 666602 | 632736 | 0 | 0 | 0 | 126736 | 538134 | 383776 | 0 | 862400 | 288381 | 193440 | 189980 | 484320 | 0 | 236862 | 1947055 | 0 | 6040900 | 0 | 0 | 5035655 | 0 | 0 | 5038309 | 0 | 1482240 | 4387827 | 0 | 9773745 | 1423680 | 3211574 | 1618656 | 524880 | 1582713 | 0 | 16395 | 1929504 | 27365400 | 5275991 | 0 | 16800 | 34920 | 583200 | 862848 | 0 | 0 | 0 | 40577 |  | 181986032 | 116943195 | 298929227 | 96405220 | 21216000 | 45208044 | 16989118 | 59781048 | 35353355 | 3501992 | 10314469 | 5004840 | 3836160 | 1318981 | 0
Fuel Cost | 0 | 0 | 3793080 | 6171952.5 | 6752001.76 | 0 | 0 | 9979998 | 5896800 |  | 0 | 5215650 | 3526296.84 | 17902310.4 | 0 | 17668080 | 7442769.6 | 0 | 0 | 24056332.8 | 20370208.32 | 14791300.8 | 0 | 0 | 0 | 0 | 10935129.6 | 11793276 | 12079473.21 | 292950 | 450000 | 0 | 0 | 0 | 8671017.6 | 0 | 491937.84 | 453600 | 4914000 | 0 | 9715807.65 | 0 | 0 | 0 | 0 |  | 3880548 | 6141309.12 | 10608514.94 | 3496928.4 | 7839283.2 | 7436270.4 | 518525.76 | 1615982.4 | 0 | 0 | 0 | 8864016 | 8237130 | 5699080 | 280515.66 | 287236.8 | 1055483.28 | 1860235.2 | 0 | 1998311.98 | 0 | 13721222.24 | 730873 | 631887.84 | 130140 | 1305150 | 245565 | 27543628.8 | 2526009.6 | 0 | 0 | 232724 | 1404250 | 1240726.08 | 630576 | 754210.8 | 1707467.1 | 0 | 2809057.92 | 4364467.2 | 0 | 4653474 | 922350 | 823523 | 472586.4 | 7449000 | 133812 | 194636 | 90881218.56 | 87643387.65 | 85161129.76 | 40119973.92 | 35166624 | 40417311.87 | 49195864.8 | 1189925.1 | 2575872 | 12366124.8 | 40398697.01 | 1335840 | 30074112 | 19906040.88 | 25021687.35 | 0 | 16230655.66 | 8517254.13 | 28102892.42 | 0 | 32407006.8 | 2974214.4 | 8691608 | 22613808 | 4235439.5 | 23408481.6 | 29210184 | 0 | 5533783.2 | 2499796.6 | 24905289.6 | 0 | 0 | 0 | 0 |  | 63648000 | 0 | 5378365.44 | 0 | 699552 | 87056640 | 0 | 0 | 3985252.8 | 10045440 | 0 | 2246862.24 | 1293207.88 | 6896822.4 | 0 | 0 | 0 | 2125362.72 | 9411963.66 | 6002256.64 | 0 | 14281344 | 4876522.71 | 2636587.2 | 3204962.6 | 1002542.4 | 0 | 179304.534 | 11312389.55 | 0 | 31956361 | 0 | 0 | 5841359.8 | 0 | 0 | 87968875.14 | 0 | 31097395.2 | 5089879.32 | 0 | 9676007.55 | 19134259.2 | 67346706.78 | 19148700.48 | 7584516 | 20100455.1 | 0 | 181164.75 | 23424178.56 | 246562254 | 5381510.82 | 0 | 124320 | 394945.2 | 6840936 | 13227459.84 | 0 | 0 | 0 | 0 |  | 1118594904.65 | 837364663.514 | 1955959568.164 | 109418501.474 | 63648000 | 53948891.23 | 355023736.09 | 780085713.66 | 289831004.55 | 945537.84 | 175025515.14 | 84914108.23 | 27543628.8 | 15574931.15 | 0
Yesterday Day Peak | 0 | 0 | 110 | 170 | 270 | 0 | 0 | 408 | 257 |  | 0 | 225 | 138 | 57 | 0 | 55 | 275 | 0 | 0 | 61 | 58 | 15 | 0 | 0 | 0 | 0 | 17 | 17 | 35 | 16 | 25 | 0 | 33 | 18 | 16 | 0 | 75 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 17 | 10 | 11 | 25 | 17 | 5 | 0 | 0 | 0 | 320 | 310 | 203 | 8 | 0 | 39 | 50 | 0 | 51 | 0 | 36 | 0 | 22 | 9 | 24 | 14 | 148 | 68 | 0 | 0 | 2 | 43 | 41 | 11 | 10 | 0 | 0 | 60 | 78 | 0 | 193 | 18 | 22 | 10 | 300 | 8 | 8 | 140 | 276 | 175 | 80 | 87 | 80 | 149 | 16 | 10 | 17 | 129 | 140 | 115 | 34 | 69 | 2 | 52 | 36 | 110 | 0 | 105 | 10 | 398 | 55 | 32 | 35 | 107 | 0 | 15 | 22 | 53 | 0 | 0 | 0 | 0 |  | 896 | 0 | 200 | 0 | 0 | 222 | 0 | 0 | 0 | 0 | 0 | 84 | 22 | 16 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 34 | 0 | 8 | 0 | 22 | 0 | 11 | 80 | 0 | 250 | 0 | 0 | 205 | 0 | 0 | 216 | 0 | 20 | 176 | 0 | 416 | 56 | 86 | 50 | 15 | 55 | 0 | 1 | 55 | 970 | 223 | 0 | 0 | 4 | 71 | 0 | 0 | 0 | 0 | 0 |  | 11822 | DayPeak
Yesterday Evening Peak | 0 | 0 | 106 | 170 | 250 | 0 | 0 | 400 | 323 | 0 | 0 | 225 | 144 | 92 | 0 | 55 | 332 | 0 | 0 | 89 | 92 | 110 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 27 | 33 | 18 | 40 | 0 | 76 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 12 | 17 | 51 | 10 | 91 | 37 | 17 | 30 | 0 | 0 | 0 | 315 | 305 | 206 | 8 | 0 | 39 | 54 | 0 | 51 | 0 | 36 | 8 | 22 | 7 | 33 | 14 | 156 | 102 | 0 | 0 | 0 | 43 | 41 | 17 | 16 | 112 | 0 | 61 | 81 | 0 | 193 | 18 | 25 | 10 | 310 | 8 | 11 | 190 | 249 | 218 | 90 | 144 | 90 | 149 | 0 | 10 | 100 | 123 | 0 | 97 | 105 | 105 | 0 | 70 | 36 | 110 | 0 | 112 | 10 | 400 | 93 | 0 | 144 | 107 | 0 | 17 | 0 | 87 | 0 | 0 | 0 | 0 |  | 805 | 0 | 175 | 0 | 16 | 222 | 0 | 0 | 41 | 55 | 0 | 85 | 35 | 48 | 0 | 0 | 0 | 24 | 36 | 81 | 0 | 42 | 32 | 8 | 32 | 22 | 0 | 11 | 83 | 0 | 250 | 0 | 0 | 191 | 0 | 0 | 217 | 0 | 92 | 183 | 0 | 419 | 74 | 160 | 94 | 32 | 92 | 0 | 0 | 95 | 1120 | 221 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 0 |  | 13581 | EvPeak
Forecast for Evening | 0 | 0 | 110 | 170 | 260 | 0 | 0 | 400 | 320 | 0 | 0 | 225 | 150 | 92 | 0 | 55 | 330 | 0 | 0 | 89 | 92 | 110 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 27 | 33 | 25 | 40 | 0 | 76 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 12 | 26 | 51 | 10 | 100 | 37 | 17 | 30 | 0 | 0 | 0 | 300 | 300 | 210 | 8 | 90 | 39 | 55 | 0 | 51 | 0 | 36 | 8 | 22 | 10 | 33 | 14 | 166 | 110 | 0 | 0 | 0 | 43 | 41 | 17 | 16 | 112 | 0 | 63 | 81 | 0 | 193 | 18 | 25 | 10 | 310 | 8 | 11 | 190 | 286 | 218 | 90 | 144 | 90 | 149 | 0 | 10 | 100 | 123 | 0 | 115 | 105 | 105 | 0 | 70 | 36 | 110 | 0 | 113 | 10 | 400 | 92 | 0 | 144 | 107 | 0 | 35 |  | 87 | 55 |  |  |  |  | 918 | 0 | 200 | 0 | 16 | 225 | 0 | 0 | 41 | 55 | 0 | 85 | 35 | 48 | 0 | 0 | 0 | 24 | 36 | 80 | 0 | 42 | 32 | 8 | 32 | 22 | 0 | 11 | 83 | 0 | 250 | 0 | 0 | 206 | 0 | 0 | 220 | 0 | 93 | 185 | 0 | 412 | 74 | 161 | 94 | 32 | 92 | 0 | 0 | 95 | 1170 | 220 |  | 17 |  |  | 90
Forecast for Day | 0 | 0 | 110 | 170 | 270 | 0 | 0 | 390 | 320 | 0 | 0 | 225 | 150 | 60 | 0 | 55 | 290 | 0 | 0 | 24 | 58 | 15 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 22 | 25 | 25 | 33 | 25 | 16 | 0 | 74 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 6 | 26 | 17 | 10 | 11 | 25 | 17 | 10 | 0 | 0 | 0 | 310 | 310 | 210 | 8 | 90 | 35 | 55 | 0 | 51 | 0 | 29 | 0 | 22 | 10 | 30 | 14 | 143 | 70 | 0 | 0 | 1.6 | 43 | 41 | 17 | 16 | 112 | 0 | 60 | 81 | 0 | 193 | 18 | 25 | 10 | 300 | 8 | 11 | 190 | 260 | 180 | 90 | 90 | 80 | 149 | 20 | 10 | 17 | 122 | 0 | 97 | 34 | 69 | 5 | 52 | 35 | 92 | 0 | 105 | 10 | 400 | 55 | 50 | 35 | 107 | 0 | 35 | 30 | 55 | 0 |  |  |  |  | 912 | 0 | 180 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 83 | 22 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 8 | 0 | 22 | 0 | 11 | 80 | 0 | 250 | 0 | 0 | 190 | 0 | 0 | 220 | 0 | 90 | 165 | 0 | 285 | 53 | 130 | 50 | 15 | 55 | 0 | 8 | 55 | 1000 | 220 |  | 0 | 6 | 100 | 0 |  |  |  | 12
Generation at 08:00(Today) | 0 | 0 | 110 | 170 | 270 | 0 | 0 | 402 | 321 | 0 | 0 | 225 | 150 | 54 | 0 | 40 | 335 | 0 | 0 | 62 | 58 | 15 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 25 | 28 | 33 | 17 | 16 | 0 | 74 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 12 | 9 | 17 | 10 | 6 | 25 | 17 | 14 | 0 | 0 | 0 | 315 | 305 | 207 | 8 | 90 | 36 | 56 | 0 | 51 | 0 | 28 | 0 | 0 | 0 | 33 | 14 | 148 | 70 | 0 | 0 | 0 | 43 | 41 | 17 | 16 | 111 | 0 | 63 | 78 | 0 | 179 | 18 | 24 | 10 | 290 | 8 | 11 | 70 | 260 | 11 | 80 | 97 | 25 | 140 | 9 | 10 | 17 | 122 | 0 | 88 | 34 | 69 | 4 | 49 | 36 | 92 | 0 | 105 | 10 | 400 | 55 | 3 | 38 | 107 | 0 | 17 | 9 | 75 | 0 | 0 | 0 | 0 | 0 | 902 | 0 | 195 | 0 | 0 | 224 | 0 | 0 | 0 | 35 | 0 | 86 | 24 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 8 | 82 | 0 | 250 | 0 | 0 | 192 | 0 | 0 | 217 | 0 | 10 | 205 | 0 | 420 | 37 | 10 | 50 | 15 | 56 | 0 | 0 | 55 | 960 | 223 | 0 | 0 | 0 | 57 | 0 | 0 | 0 | 0 | 5 | 0 |  |  |  |  | 92089475 |  | 0
92089475
| Minimum Generation |  | 11567 | 8:00
| Highest Generation |  | 13750 | 22:00
| Day Peak Generation |  | 11822 | 9:00
| Evening Peak Generation |  | 13581 | 21:00
| HVDC Max Flow |  | 897 | 8:00
| HVDC EvPeak Flow |  | 805 | 21:00
| Load factor L.F |  | 90.58% | [161 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2022-09-01
Till now the maximum generation is : - |  |  | 14782 | 21:00 | Hrs on | 2022-04-16
The Summary of Yesterday's |  | 2022-08-31 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 11822 | MW Hour : | 9:00 | Min. Gen. at | 8:00 | 11508 | MW
Evening Peak Generation : |  | 13581 | MW Hour : | 21:00 | Available Max Generation : |  | 14071 | MW
E.P. Demand (at gen end) : |  | 14745 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 14700 | MW
Maximum Generation : |  | 13750 | MW Hour : | 22:00 | Reserve(Generation end) |  | - | MW
Total Gen. (MKWH) : |  | 298.9292 | System Load Factor : | 90.58% | Load Shed : |  | 580 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | 990 | MW at | 24:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2022-09-01
Actual : | 96.38 | Ft.(MSL) , | Rule curve : | 99 | Ft.( MSL )
Gas Consumed : | Total = | 1085.51 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 163367392.704
: |  | Coal : | 289831004.55 | Oil : | 1395049073.12 | Total : | 1848247470.374
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 327 | 7848:00 | 4707.6355 |  |  | 134 | 2.63%
Chittagong Area | 0 | 0:00 | 1333.0398 |  |  | 43 | 4.787%
Khulna Area | 296 | 7104:00 | 1759.7751 |  |  | 91 | 5.18%
Rajshahi Area | 0 | 0:00 | 1561.9867 |  |  | 42 | 5.734%
Cumilla Area | 186 | 4464:00 | 1328.9757 |  |  | 85 | 5.412%
Mymensingh Area | 206 | 4944:00 | 1098.6741 |  |  | 116 | 5.941%
Sylhet Area | 58 | 1392:00 | 490.4069 |  |  | 24 | 4.805%
Barisal Area | 0 | 0:00 | 399.641 |  |  | 0 | -0.1191%
Rangpur Area | 0 | 0:00 | 867.0178 |  |  | 45 | 5.885%
Total | 1073 |  | 13547.1525 |  |  | 580
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-2
2) Ghorasal-3,
3) Ashuganj-5
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
7) Sikalbaha 225 MW
8) Shajibazar 330 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Tongi 230 kV S/S-Tongi 80 MW P.P. 132 kV Ckt was under shut down from 09:25 to 13:40 for C/M.
b) Haripur 230 kV S/S 230 kV CB-808 was under shut down from 09:48 to 10:53 due to R/H maintenance.
c) Rajshahi(New) 230/132 kV ATR-1 transformer was under shut down from 09:41 to 10:26 for C/M.
d) Munshiganj 132/33 kV T-1 transformer was under shut down from 10:48 to 13:34 for C/M.
e) Rajshahi(New) 230/132 kV ATR-2 transformer was under shut down from 10:33 to 11:14 for C/M.
f) Rajshahi(New)-HVDC 230 kV Ckt-1 was under shut down from 11:28 to 12:01 for C/M.
g) Rampura-Bashundhara 132 kV Ckt-2 was under shut down from 12:04 to 13:01 due to energy meter replacement work at
Bashundhara S/S.
h) Bibiyana-3 was shutdown at 10:42 for emergency maintenance.
i) Kushiara 163 MW GT was synchronized at 10:28.
j) Feni 132/33 kV T-1 transformer was under shut down from 15:28 to 15:49 due to 33 kV CB to DS loop measurement. | [5 empty] | About 34 MW power interruption occurred under
Feni S/S area from 15:28 to 15:49.
k) Sylhet S/S-Sylhet 50 MW P.P. 132 kV Ckt was under shut down from 15:36 to 15:59 due to SF6 gas filling by P.P.
l) Baroaulia-Hathazari 132 kV Ckt-2 is under shut down since 06:23(01/09/2022) due to R/H maintenance.
m) Natore-Rajshahi 132 kV Ckt-1 tripped at 07:48(01/09/2022) from both ends due to PT burst at Rajshahi end
showing Dist. Z2, C-φ , E/F at Natore end.
| Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2022-08-31 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 106 | 2598000 | Machine problem
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 170 | 4142250 | Machine problem
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 250 | 6028573 | Machine problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 400 | 9504760
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 323 | 5460000 | Machine problem
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 4785000 | Dirty gas
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 92 | 1601280 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 144 | 3176844 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 0 | 0 | Under maint.
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 55 | 1333440
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 390600 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 89 | 1645440 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 332 | 6645330
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 92 | 1447776 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 859680
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 110 | 912480 | Engine problem
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 873576
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 900781 | Engine problem
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 52 | 965400 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 788300
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 18 | 431400 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 40 | 509760 | #REF!
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 249 | 6420761 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 218 | 4063031
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 90 | 1940976 | Engine problem
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 90 | 1955361 | Engine problem
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 3552048
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 1376628
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 93 | 1746240 | Engine problem
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 144 | 1844640 | Engine problem
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 209188
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 0 | Fuel shortage
| Dhaka area Total |  |  |  | 5847 | 3832 | 78109543
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 110 | 2600000 | Machine problem
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 25 | 594239
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 101790
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 37 | 642720 | Engine problem
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 146 | 3501992 | Low water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | HGPI for 30 days.
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 105 | 1977999
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 17 | 368184 | Fuel shortage
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 623297 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 10 | 258840 | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 10 | 249600 | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 17 | 408288 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 30 | 485280
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 91 | 618240 | Engine problem
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 25201
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 70 | 1382509 | Fuel shortage
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 36 | 782117 | Engine problem
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 110 | 2643734
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 10 | 252480 | Engine problem
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 107 | 2566800 | Engine problem
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Chattogram area Total |  |  |  | 2382 | 982 | 20083310
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 206 | 4913000 | #REF!
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 315 | 7985600 | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 305 | 7557000 | FGMO
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+136*1 | 284 | 0 | 0 | On test.
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 39 | 934056 | Engine problem
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 54 | 1248480
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 217454 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1196594
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 123 | 3044363 | Engine problem
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 36 | 794512 | Engine problem
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 235440 | Machine problem
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 100 | 905280 | Fuel shortage
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 461232
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 7 | 173520 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 156 | 3836160
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 745800
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 8 | 54340 | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 14 | 327420 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 190 | 4335936 | Engine problem
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Fuel shortage
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 112 | 2514120
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 423720 | 33 kV feeder problem.
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 87 | 1663680 | Fuel shortage
| Cumilla Area Total |  |  |  | 3169 | 1883 | 43567707
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 102 | 2317440 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 0 | Gas shortage
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 14600
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 144 | 2608800 | Engine problem
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 97 | 2473200 | Engine problem
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 293110
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 297360 | Engine problem
| Mymensingh Area Total |  |  |  | 614 | 355 | 8004510
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1025000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 41 | 939944 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 112 | 1484754 | Gas shortage
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 17 | 362400 | Gas shortage
| Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 16 | 435960 | Gas shortage
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 256100
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 61 | 1447968
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1914240
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 193 | 4607400 | Machine problem
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 429000
| Sylhet 50MW PP (EPL) |  | NENP | 27*2 | 50 | 25 | 552700 | Gas shortage
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 8 | 178416 | Gas shortage
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7449000 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 0 | 1452000 | Under maint.
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 238680
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 400 | 9447400
| Sylhet Area Total |  |  |  | 2477 | 1346 | 32220962
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 805 | 21216000
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 16 | 67200 | Fuel shortage
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 41 | 221280 | Engine problem
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 222 | 5276160
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 55 | 558080 | Engine problem
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 175 | 4802112 | Gas shortage.
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 0 | 0 | Fuel shortage
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 92 | 1482240 | Engine problem
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 74 | 1423680 | Fuel shortage
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 32 | 524880 | Fuel shortage
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 583200
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 0 | 0 | 0 | On test.
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 2384 | 1512 | 36154832
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 48 | 632736 | Line O/L
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 35 | 666602 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 85 | 2006127 | Gas shortage
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1120 | 27365400 | Line O/L
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 221 | 5275991
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 16800 | Line O/L
| Barisal Area Total |  |  |  | 1958 | 1509 | 35963656
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 24 | 126736 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 36 | 538134 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contract Expired
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 42 | 862400 | Engine problem
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 288381 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 191 | 5035655 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 217 | 5038309
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 183 | 4387827 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 419 | 9773745
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 189980 | Under maint.
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 484320
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | .
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 236862
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 8 | 193440 | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 81 | 383776 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 160 | 3211574
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 94 | 1618656 | Engine problem
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 95 | 1929504 | Engine problem
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 34920
| Rajshahi Area Total |  |  |  | 2129 | 1647 | 34334219
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 83 | 1947055
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 250 | 6040900 | Machine problem
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 92 | 1582713 | Engine problem
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 16395
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 90 | 862848 | Fuel shortage
| Intraco Solar 30 MW |  | IPP | 0 | 0 | 0 | 40577
| Rangpur Area Total |  |  |  | 720 | 515 | 10490488
| Total |  |  |  | 21680 | 13581 | 298929227
| Eastern Grid Total |  |  |  | 14489 | 8398 | 181986032
| Western Grid Total |  |  |  | 7191 | 5183 | 116943195
| National Grid Total |  |  |  | 21680 | 13581 | 298929227
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2022-08-31
(a) ENTIRE EASTERN GRID : |  | 8835.07 | MW | (b) ENTIRE WESTERN GRID : |  | 4081.24 | MW
i) Dhaka area |  | 4686.47 | MW | i) Khulna area |  | 1443 | MW
ii) Chittagong area |  | 1362.6 | MW | ii) Rajshahi area |  | 1412.7 | MW
iii) Comilla area |  | 1260 | MW | iii) Barisal area |  | 402.54 | MW
iv) Mymensingh area |  | 997 | MW | iv) Rangpur area |  | 823 | MW
v) Sylhet area |  | 529 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 12916.31 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
AKS | 0 | 00:00 | Chowmuhani | 180 | 22:00 | Kaptai | 5 | 18:30 | Nawabganj | 36.9 | 19:00 | Siddhirganj | 108 | 22:00
AKSML | 138 | 06:00 | Chuadanga | 95 | 06:00 | Kazla | 99 | 17:00 | Netrakona | 96 | 19:00 | Sirajganj | 88 | 07:00
Aftabnagar | 35 | 14:00 | Coxsbazar | 108 | 10:00 | Keranigonj | 56 | 19:30 | New | 81 | 09:00 | Sonargaon | 80 | 12:00
Agargaon | 98 | 12:00 | Cumilla(N) | 186 | 19:00 | Khagrachori | 28 | 20:00 | Niamatpur | 64 | 06:00 | Sreemongol | 44 | 12:00
Agrabad | 74 | 12:00 | Cumilla(S) | 174 | 18:30 | Khulna | 92 | 13:00 | Noapara | 47 | 01:00 | Srinagar | 46.28 | 21:00
Amnura | 51 | 21:00 | Daudkandi | 155 | 21:00 | Khulshi | 174 | 00:00 | PHP | 11 | 10:00 | Sunamganj | 38 | 22:00
Ashuganj | 66 | 00:00 | Dhaka | 50 | 12:00 | Kishoreganj | 134 | 21:00 | Pabna | 89 | 00:00 | Sylhet | 136 | 00:00
BSRM | 161 | 10:00 | Dhamrai | 122 | 09:00 | Kodda | 280 | 18:30 | Palashbari | 108 | 23:00 | TK | 28.5 | 19:00
Bagerhat | 88 | 22:00 | Dhanmondi | 135 | 17:00 | Kulaura | 42 | 05:00 | Panchagarh | 46 | 08:00 | Tangail | 195 | 22:00
Bakulia | 103 | 20:00 | Dohazari | 102 | 20:00 | Kurigram | 56 | 21:00 | Patuakhali | 133 | 22:00 | Thakurgaon | 66 | 22:00
Banani | 60 | 10:00 | Faridpur | 138 | 23:00 | Kushtia | 138 | 02:00 | Payra | 1.02 | 16:00 | Tongi | 116 | 19:30
Bangabhaban | 22 | 09:00 | Fatullah | 73 | 00:00 | Lalbag | 100 | 17:00 | Purbachal | 20 | 21:00 | Ullon | 40 | 21:00
Barapukuria | 54 | 19:00 | Fenchuganj | 43 | 20:00 | Lalmonirhat | 38 | 20:00 | Purbasadipur | 96 | 05:00 | Uttara | 93 | 21:00
Barguna | 20 | 00:00 | Feni | 102 | 21:00 | Madanganj | 95 | 23:00 | Rahim | 26 | 08:00 | UttaraNew | 18 | 00:00
Barishal | 120 | 19:00 | GPH | 102 | 12:00 | Madaripur | 116 | 22:00 | Rajbari | 60 | 19:30 | Zigatola | 57 | 19:00
Barishal-230 | 77 | 00:00 | Ghorashal | 68 | 23:00 | Madartek | 99 | 23:00 | Rajendrapur | 92 | 05:00
Baroaulia | 69 | 19:00 | Goalpara | 28 | 02:00 | Madunaghat | 61 | 18:30 | Rajshahi | 132 | 22:00
Baroirhat | 63 | 19:00 | Gollamari | 52 | 12:00 | Magura | 54 | 07:00 | Rajshahi-230 | 26 | 02:00
Bashundhara | 164 | 17:00 | Gopalganj | 108 | 22:00 | Mahasthangarh | 74 | 20:00 | Ramganj | 88 | 19:00
BashundharaCement | 1 | 19:30 | Gulshan | 132 | 17:00 | Manikganj | 78 | 19:00 | Rampur | 16 | 00:00
Beanibazar | 60 | 21:00 | Halishahar | 99 | 11:00 | Maniknagar | 82 | 10:00 | Rangamati | 14 | 19:00
Benapole | 56 | 07:00 | HaripurSBU | 157 | 17:00 | Matarbari | 40 | 21:00 | Rangpur | 105 | 08:00
Bhaluka | 112 | 08:00 | Hasnabad | 96 | 19:00 | Matuail | 62 | 01:00 | Ruppur | 5 | 09:00
Bhandaria | 50 | 00:00 | Hathazari | 98 | 20:00 | Millgate | 64 | 15:00 | SSM | 3 | 05:00
Bhangura | 36 | 20:00 | Ishurdi | 76 | 20:00 | Mirpur | 134.5 | 18:30 | Saidpur | 93 | 08:00
Bheramara(GK) | 55 | 00:00 | Jaldhaka | 59 | 20:00 | Mirsorai | N/A | N/A | Satkhira | 95 | 06:00
Bhulta | 216 | 06:00 | Jamalpur | 148 | 06:00 | Mithapukur | 44 | 20:00 | Satmasjid | 101 | 19:00
Bog-Sherpur | 64 | 20:00 | Jashore | 133 | 12:00 | Modern | 0 | 00:00 | Savar | 156 | 09:00
Bogura | 172 | 22:00 | Jhenaidah | 114 | 05:00 | Mogbazar | 142 | 17:00 | Shahjadpur | 85 | 22:00
Borhanuddin | 43 | 00:00 | Joydebpur | 181 | 21:00 | Mongla | 36 | 11:00 | Shahjibazar | 95 | 00:00
Brahmanbaria | 160 | 22:00 | Joypurhat | 59 | 21:00 | Motijheel | 41 | 15:00 | Shahmirpur | 46.5 | 18:30
Cantonment | 156 | 18:30 | Juldah | 25 | 23:00 | Munshiganj | 114 | 23:00 | Shariatpur | 78 | 22:00
Chandpur | 65 | 21:00 | KSRM | 30 | 00:00 | Mymensingh | 231 | 22:00 | Sherpur | 100 | 19:00
Chandraghona | 34 | 19:30 | Kabirpur | 277 | 18:00 | Naogaon | 126 | 21:00 | Shikalbaha | 28 | 19:00
Chapai | 61 | 21:00 | Kachua | 70 | 18:30 | Narail | 40 | 07:00 | Shikalbaha-230 | N/A | N/A
Charsaidpur | 47 | 00:00 | Kallyanpur | 108 | 23:00 | Narinda | 80 | 17:00 | Shitalakhya | 114 | 12:00
Chauddagram | 59 | 18:30 | Kalurghat | 36 | 11:00 | Narshingdi | 170 | 04:00 | Sholosohor | N/A | N/A
Chhatak | 29 | 18:30 | Kamrangirchar | 60 | 17:00 | Natore | 138 | 20:00 | Shyampur | 144 | 01:00
Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
(1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2022-08-31 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Bhulta | 379 | 07:00 | 365 | 09:00 | Kaliakoir | 380 | 07:00 | 375 | 06:00
| Bibiana | 394 | 11:00 | 388 | 01:00 | Payra | 417 | 18:00 | 409 | 01:00
| BIPTC | 400 | 07:00 | 393 | 00:00 | Rahanpur_I | 408 | 19:30 | 376 | 12:00
| Gopalganj_I | 407 | 18:00 | 394 | 03:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 216 | 19:00 | 208 | 09:00 | Hasnabad | 218 | 19:00 | 208 | 10:00
| AKSML | 220 | 17:00 | 207 | 06:00 | Hathazari | 224 | 23:00 | 213 | 09:00
| Aminbazar | 218 | 19:00 | 209 | 09:00 | Ishurdi | 236 | 19:00 | 226 | 13:00
| Ashuganj | 231 | 19:00 | 225 | 01:00 | Jhenaidah | 231 | 19:00 | 219 | 12:00
| Baghabari | 233 | 19:00 | 227 | 12:00 | Kaliakoir | 217 | 07:00 | 209 | 09:00
| Barapukuria | 225 | 17:00 | 215 | 00:00 | Keranigonj | 216 | 07:00 | 208 | 09:00
| Barishal | 245 | 11:00 | 238 | 00:00 | Khulna(S) | 239 | 19:00 | 227 | 13:00
| Bheramara | 235 | 10:00 | 222 | 13:00 | Maniknagar | 219 | 04:00 | 213 | 09:00
| Bhulta | 223 | 07:00 | 215 | 09:00 | Meghnaghat | 222 | 04:00 | 218 | 09:00
| Bibiana | 233 | 12:00 | 228 | 03:00 | Mirsorai | N/A | N/A | N/A | N/A
| BIPTC | 237 | 19:00 | 224 | 13:00 | Rajshahi | 237 | 19:30 | 223 | 12:00
| Bogura | 227 | 18:30 | 219 | 21:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 248 | 08:00 | 243 | 00:00 | Rampura | 221 | 18:30 | 212 | 09:00
| BSRM | 219 | 17:00 | 209 | 13:00 | Shikalbaha | 221 | 00:00 | 214 | 12:00
| Cumilla(N) | 219 | 07:00 | 212 | 09:00 | Shyampur | 218 | 19:00 | 210 | 09:00
| Fenchuganj | 236 | 18:00 | 230 | 01:00 | Siddhirganj | 221 | 05:00 | 215 | 10:00
| Ghorashal | N/A | N/A | N/A | N/A | Sirajgonj | 231 | 19:00 | 227 | 01:00
| GPH | 221 | 17:00 | 210 | 13:00 | Tongi | 220 | 05:00 | 211 | 09:00
| Haripur | 218 | 03:00 | 212 | 10:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 135 | 07:00 | 126 | 17:00 | Lalbag | 136 | 19:00 | 125 | 07:00
| Agargaon | 133 | 04:00 | 127 | 09:00 | Lalmonirhat | 132 | 15:00 | 120 | 22:00
| Agrabad | 128 | 08:00 | 121 | 09:00 | Madanganj | 130 | 19:00 | 124 | 09:00
| AKS | 127 | 00:00 | 122 | 06:00 | Madaripur | 139 | 18:00 | 133 | 00:00
| Aminbazar | 133 | 19:00 | 126 | 08:00 | Madartek | 135 | 07:00 | 126 | 17:00
| Amnura | 138 | 19:30 | 125 | 12:00 | Madunaghat | 129 | 07:00 | 123 | 13:00
| Ashuganj | 134 | 14:00 | 131 | 03:00 | Magura | 140 | 19:00 | 130 | 13:00
| Bagerhat | 138 | 19:00 | 129 | 13:00 | Mahasthangarh | 136 | 18:00 | 128 | 03:00
| Bakulia | 129 | 17:00 | 122 | 09:00 | Manikganj | 137 | 07:00 | 125 | 09:00
| Banani | 131 | 05:00 | 124 | 10:00 | Maniknagar | 131 | 07:00 | 124 | 17:00
| Bangabhaban | 132 | 07:00 | 125 | 09:00 | Matarbari | 120 | 12:00 | 104 | 19:30
| Barapukuria | 138 | 15:00 | 130 | 00:00 | Matuail | 129 | 19:00 | 124 | 09:00
| Barguna | 136 | 18:00 | 131 | 15:00 | Millgate | 131 | 03:00 | 124 | 10:00
| Barishal | 138 | 07:00 | 131 | 12:00 | Mirpur | 131 | 19:00 | 123 | 09:00
| Barishal-230 | 139 | 11:00 | 133 | 00:00 | Mithapukur | 135 | 16:00 | 123 | 03:00
| Baroaulia | 130 | 17:00 | 124 | 13:00 | Modern | 128 | 19:00 | 122 | 09:00
| Baroirhat | 127 | 17:00 | 117 | 05:00 | Mogbazar | 135 | 01:00 | 127 | 17:00
| Bashundhara | 130 | 04:00 | 123 | 10:00 | Mongla | 136 | 19:00 | 129 | 12:00
| BashundharaCement | 130 | 19:00 | 124 | 09:00 | Motijheel | 132 | 07:00 | 125 | 09:00
| Beanibazar | 130 | 16:00 | 127 | 00:00 | Munshiganj | 130 | 19:00 | 124 | 13:00
| Benapole | 136 | 19:00 | 127 | 12:00 | Mymensingh | 135 | 11:00 | 105 | 21:00
| Bhaluka | 135 | 11:00 | 119 | 18:30 | Naogaon | 132 | 16:00 | 123 | 21:00
| Bhandaria | 138 | 11:00 | 129 | 00:00 | Narail | 138 | 19:00 | 128 | 13:00
| Bhangura | 138 | 19:00 | 133 | 12:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bheramara | 137 | 19:00 | 132 | 12:00 | Narshingdi | 123 | 18:00 | 118 | 09:00
| Bheramara(GK) | 138 | 19:00 | 133 | 12:00 | Natore | 135 | 18:00 | 128 | 13:00
| Bhulta | 119 | 07:00 | 115 | 15:00 | Nawabganj | 136 | 19:00 | 129 | 09:00
| Bog-Sherpur | 137 | 19:00 | 130 | 21:00 | Netrakona | 127 | 14:00 | 104 | 02:00
| Bogura | 138 | 18:00 | 129 | 21:00 | New | 131 | 05:00 | 124 | 10:00
| Bogura-230 | 137 | 18:30 | 131 | 21:00 | Niamatpur | 130 | 09:00 | 119 | 03:00
| Brahmanbaria | 130 | 14:00 | 126 | 03:00 | Noapara | 139 | 19:00 | 131 | 12:00
| Cantonment | 131 | 04:00 | 125 | 10:00 | Pabna | 136 | 19:00 | 129 | 12:00
| Chandpur | 127 | 17:00 | 116 | 03:00 | Palashbari | 132 | 16:00 | 123 | 21:00
| Chandraghona | 129 | 00:00 | 123 | 23:00 | Panchagarh | 133 | 14:00 | 111 | 01:00
| Chapai | 136 | 19:30 | 126 | 12:00 | Patuakhali | 135 | 07:00 | 130 | 22:00
| Charsaidpur | 130 | 19:00 | 125 | 09:00 | Payra | 136 | 00:00 | 135 | 01:00
| Chauddagram | 127 | 17:00 | 118 | 06:00 | PHP | 125 | 17:00 | 116 | 06:00
| Chhatak | 130 | 12:00 | 126 | 18:30 | Postogola | 139 | 19:00 | 132 | 09:00
| Chowmuhani | 125 | 17:00 | 115 | 03:00 | Purbachal | 131 | 19:00 | 123 | 10:00
| Chuadanga | 136 | 19:00 | 123 | 13:00 | Purbasadipur | 135 | 15:00 | 118 | 00:00
| Coxsbazar | 119 | 14:00 | 103 | 23:00 | Rahim | 128 | 14:00 | 126 | 09:00
| Cumilla(N) | 128 | 19:00 | 123 | 09:00 | Rajbari | 135 | 19:00 | 129 | 03:00
| Cumilla(S) | 130 | 06:00 | 121 | 06:00 | Rajendrapur | 137 | 08:00 | 132 | 09:00
| Daudkandi | 131 | 11:00 | 127 | 08:00 | Rajshahi | 134 | 19:00 | 127 | 12:00
| Dhaka | 135 | 06:00 | 120 | 14:00 | Rajshahi-230 | 134 | 16:00 | 127 | 12:00
| Dhamrai | 132 | 04:00 | 125 | 09:00 | Ramganj | 124 | 19:00 | 111 | 03:00
| Dhanmondi | 129.6 | 07:00 | 124 | 10:00 | Rampur | 127 | 21:00 | 123 | 11:00
| Dohazari | 126 | 17:00 | 118 | 09:00 | Rampura | 134 | 05:00 | 126 | 10:00
| Faridpur | 135 | 19:00 | 129 | 13:00 | Rangamati | 131 | 17:00 | 124 | 20:00
| Fatullah | 132 | 08:00 | 127 | 10:00 | Rangpur | 133 | 17:00 | 121 | 21:00
| Fenchuganj | 135 | 19:00 | 131 | 01:00 | Ruppur | 137 | 19:00 | 132 | 10:00
| Feni | 126 | 17:00 | 120 | 06:00 | Saidpur | 135 | 16:00 | 124 | 00:00
| Ghorashal | 135 | 00:00 | 130 | 09:00 | Satkhira | 135 | 19:00 | 127 | 12:00
| Goalpara | 140 | 19:00 | 133 | 12:00 | Satmasjid | 132 | 04:00 | 126 | 09:00
| Gollamari | 138 | 19:00 | 132 | 12:00 | Savar | 133 | 19:30 | 125 | 09:00
| Gopalganj | 139 | 19:00 | 132 | 13:00 | Shahjadpur | 139 | 19:30 | 135 | 04:00
| Gopalganj_I | 139 | 15:00 | 135 | 02:00 | Shahjibazar | 134 | 17:00 | 130 | 02:00
| Gulshan | 135 | 05:00 | 126 | 10:00 | Shahmirpur | 128 | 00:00 | 122 | 09:00
| Halishahar | 128 | 19:00 | 122 | 09:00 | Shariatpur | 137 | 18:00 | 129 | 00:00
| Haripur | 130 | 21:00 | 126 | 09:00 | Sherpur | 134 | 11:00 | 118 | 05:00
| HaripurSBU | 130 | 19:00 | 120 | 08:00 | Shikalbaha | 130 | 17:00 | 122 | 09:00
| Hasnabad | 139 | 18:30 | 132 | 09:00 | Shikalbaha-230 | 128 | 00:00 | 124 | 12:00
| Hathazari | 132 | 23:00 | 125 | 04:00 | Shitalakhya | 138 | 07:00 | 131 | 17:00
| Ishurdi | 137 | 19:00 | 132 | 12:00 | Sholosohor | N/A | N/A | N/A | N/A
| Jaldhaka | 135 | 16:00 | 119 | 03:00 | Shyampur | 132 | 19:00 | 126 | 09:00
| Jamalpur | 138 | 11:00 | 122 | 05:00 | Shyampur-230 | 132 | 19:00 | 127 | 09:00
| Jashore | 137 | 19:00 | 128 | 12:00 | Siddhirganj | 130 | 19:00 | 125 | 09:00
| Jhenaidah | 140 | 19:00 | 132 | 12:00 | Sirajganj | 136 | 19:00 | 128 | 21:00
| Jhenaidah-230 | 141 | 19:00 | 132 | 13:00 | Sonargaon | 132 | 18:30 | 128 | 01:00
| Joydebpur | 140 | 19:00 | 128 | 09:00 | Sreemongol | 134 | 00:00 | 132 | 09:00
| Joypurhat | 134 | 18:00 | 122 | 22:00 | Srinagar | 135 | 07:00 | 129 | 09:00
| Juldah | 128 | 19:00 | 122 | 13:00 | SSM | 130 | 00:00 | 124 | 23:00
| Kabirpur | 138 | 00:00 | 119 | 10:00 | Sunamganj | 128 | 07:00 | 124 | 18:30
| Kachua | 127 | 17:00 | 116 | 04:00 | Sylhet | 132 | 07:00 | 130 | 00:00
| Kaliakoir | 140 | 07:00 | 135 | 08:00 | Tangail | 137 | 11:00 | 129 | 05:00
| Kallyanpur | 132 | 19:00 | 125 | 10:00 | Thakurgaon | 140 | 14:00 | 114 | 00:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2022-08-31
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 990 | 8067 | 4876 | 12943 |  |  |  | QF-LDC-11
0:30 | 1167.5 | 7770 | 4836.5 | 12606.5 | Date: | 2022-08-31
1:00 | 1345 | 7473 | 4797 | 12270
1:30 | 1295 | 7457.5 | 4809.5 | 12267
2:00 | 1245 | 7442 | 4822 | 12264
2:30 | 1265 | 7491.5 | 4826 | 12317.5 | [5 empty] | Gen. at Eve. Peak | 13581 | 13581 MW (21:00 )
3:00 | 1285 | 7541 | 4830 | 12371 | [6 empty] | 21:00
3:30 | 1157.5 | 7527 | 4823 | 12350 | [5 empty] | Gen. at Day Peak | 11822 | 11822 MW (09:00 )
4:00 | 1030 | 7513 | 4816 | 12329 | [6 empty] | 9:00
4:30 | 1050 | 7496.5 | 4807 | 12303.5 | [5 empty] | Highest Generation | 13750
5:00 | 1070 | 7480 | 4798 | 12278 | [6 empty] | 22:00
5:30 | 1092.5 | 7404.5 | 4721 | 12125.5
6:00 | 1115 | 7329 | 4644 | 11973
6:30 | 1132.5 | 7284 | 4620 | 11904
7:00 | 1150 | 7239 | 4596 | 11835
7:30 | 1220 | 7216.5 | 4484.5 | 11701
8:00 | 1290 | 7194 | 4373 | 11567
8:30 | 1420 | 7264 | 4430.5 | 11694.5
9:00 | 1550 | 7334 | 4488 | 11822
9:30 | 1550 | 7286 | 4490 | 11776
10:00 | 1550 | 7238 | 4492 | 11730
10:30 | 1415 | 7207.5 | 4486.5 | 11694
11:00 | 1280 | 7177 | 4481 | 11658
11:30 | 1287.5 | 7176 | 4486 | 11662
12:00 | 1295 | 7175 | 4491 | 11666
12:30 | 1277.5 | 7199.5 | 4560 | 11759.5
13:00 | 1260 | 7224 | 4629 | 11853
13:30 | 1275 | 7224.5 | 4643 | 11867.5
14:00 | 1290 | 7225 | 4657 | 11882
14:30 | 1325 | 7263.5 | 4634 | 11897.5
15:00 | 1360 | 7302 | 4611 | 11913
15:30 | 1357.5 | 7302.5 | 4623 | 11925.5
16:00 | 1355 | 7303 | 4635 | 11938
16:30 | 1405 | 7392 | 4591.5 | 11983.5
17:00 | 1455 | 7481 | 4548 | 12029
17:30 | 1487.5 | 7540 | 4521.5 | 12061.5
18:00 | 1520 | 7599 | 4495 | 12094
18:30 | 1475 | 7795.5 | 4678.5 | 12474
19:00 | 1430 | 7992 | 4862 | 12854
19:30 | 1400 | 7929 | 4990 | 12919
20:00 | 1365 | 8234 | 5118 | 13352 |  |  |  | Executive Engineer
20:30 | 1342.5 | 8316 | 5150.5 | 13466.5 |  |  |  | Network Operation Division
21:00 | 1320 | 8398 | 5183 | 13581
21:30 | 1345 | 8486.5 | 5179 | 13665.5
22:00 | 1370 | 8575 | 5175 | 13750 |  |  |  |  | Page 6 of 7
22:30 | 1380 | 8458.5 | 5147 | 13605.5
23:00 | 1390 | 8342 | 5119 | 13461
23:30 | 1190 | 8204.5 | 4997.5 | 13202
24:00 | 990 | 8067 | 4876 | 12943
13581 MW (21:00 )
11822 MW (09:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2022-08-31 |  | Energy |  | 298929227
[13 empty] | 2022-08-31 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 4132 | 805 | 2125 | 815 | 2470 | 1491 | 147 | 437 | 561 | 174 | 0 | 0
0:30 | 4128 | 850.5 | 1971 | 761.5 | 2386 | 1480.5 | 147 | 436.5 | 491.5 | 168 | 0 | 705.0049 | Date: | 2022-08-31
1:00 | 4124 | 896 | 1817 | 708 | 2302 | 1470 | 147 | 436 | 422 | 162 | 0 | 1410.0097
1:30 | 4108.5 | 896 | 1830 | 730.5 | 2292.5 | 1470 | 147 | 437 | 407.5 | 162 | 0 | 1320.617 | [8 empty] | Total Energy | 298.9292 | Total Energy Gen 298.929 MKWHr Energy Not Served 23.153 MKWHr Energy Requirement 322.082 MKWHr
2:00 | 4093 | 896 | 1843 | 753 | 2283 | 1470 | 147 | 438 | 393 | 162 | 0 | 1231.2242 | [8 empty] | Energy not Served | 23.1526
2:30 | 4137.5 | 895.5 | 1843 | 767.5 | 2291 | 1465 | 146 | 437.5 | 387.5 | 161 | 0 | 1135.8412 | [8 empty] | Energy Requirement | 322.0818
3:00 | 4182 | 895 | 1843 | 782 | 2299 | 1460 | 145 | 437 | 382 | 160 | 0 | 1040.4582
3:30 | 4163 | 895 | 1847 | 781.5 | 2292 | 1445 | 145 | 437.5 | 399 | 159 | 0 | 990.6931 | [6 empty] | Shortage
4:00 | 4144 | 895 | 1851 | 781 | 2285 | 1430 | 145 | 438 | 416 | 158 | 0 | 940.9281
4:30 | 4154.5 | 895 | 1855.5 | 780.5 | 2266 | 1426 | 145 | 438 | 400 | 157 | 0 | 757.0739
5:00 | 4165 | 895 | 1860 | 780 | 2247 | 1422 | 145 | 438 | 384 | 156 | 0 | 573.2196
5:30 | 4115.5 | 895 | 1839 | 763.5 | 2219 | 1400.5 | 145 | 440 | 371 | 151 | 1.5 | 437.2873
6:00 | 4066 | 895 | 1818 | 747 | 2191 | 1379 | 145 | 442 | 358 | 146 | 3 | 301.355
6:30 | 4036 | 895.5 | 1823 | 742 | 2172 | 1360 | 145 | 442 | 342 | 146 | 17.5 | 387.9831 |  |  |  |  | Coal
7:00 | 4006 | 896 | 1828 | 737 | 2153 | 1341 | 145 | 442 | 326 | 146 | 32 | 474.6111
7:30 | 3989.5 | 896.5 | 1802 | 646 | 2149 | 1325.5 | 146.5 | 442.5 | 329 | 144 | 48.5 | 416.3056 |  |  |  | Oil |  |  |  | ,
8:00 | 3973 | 897 | 1776 | 555 | 2145 | 1310 | 148 | 443 | 332 | 142 | 65 | 358
8:30 | 4009.5 | 896.5 | 1812 | 568 | 2148.5 | 1305 | 146.5 | 440.5 | 333 | 145 | 107.5 | 518.5
9:00 | 4046 | 896 | 1848 | 581 | 2152 | 1300 | 145 | 438 | 334 | 148 | 150 | 679
9:30 | 4029 | 895.5 | 1816.5 | 580.5 | 2136 | 1300.5 | 145.5 | 437 | 334 | 151 | 166.5 | 827.5
10:00 | 4012 | 895 | 1785 | 580 | 2120 | 1301 | 146 | 436 | 334 | 154 | 183 | 976
10:30 | 3913.5 | 895 | 1813.5 | 628.5 | 2103 | 1300.5 | 146.5 | 435 | 326 | 154 | 192.5 | 1172.5
11:00 | 3815 | 895 | 1842 | 677 | 2086 | 1300 | 147 | 434 | 318 | 154 | 202 | 1369
11:30 | 3804.5 | 896 | 1865 | 689 | 2089 | 1305.5 | 147 | 421.5 | 305 | 156 | 184.5 | 1444
12:00 | 3794 | 897 | 1888 | 701 | 2092 | 1311 | 147 | 409 | 292 | 158 | 167 | 1519
12:30 | 3782 | 896.5 | 1894 | 731.5 | 2125.5 | 1321 | 147 | 416 | 301.5 | 158 | 186 | 1468.5
13:00 | 3770 | 896 | 1900 | 762 | 2159 | 1331 | 147 | 423 | 311 | 158 | 205 | 1418
13:30 | 3770 | 896 | 1900 | 762 | 2159 | 1331 | 147 | 423 | 311 | 158 | 205 | 1461
14:00 | 3770 | 896 | 1900 | 762 | 2159 | 1331 | 147 | 423 | 311 | 158 | 205 | 1504
14:30 | 3789 | 896 | 1896.5 | 746.5 | 2242 | 1336 | 147.5 | 412 | 303.5 | 164 | 148 | 1515
15:00 | 3808 | 896 | 1893 | 731 | 2325 | 1341 | 148 | 401 | 296 | 170 | 91 | 1526
15:30 | 3798 | 896 | 1889.5 | 695.5 | 2379.5 | 1342 | 147 | 394 | 293 | 169 | 100.5 | 1490
16:00 | 3788 | 896 | 1886 | 660 | 2434 | 1343 | 146 | 387 | 290 | 168 | 110 | 1454
16:30 | 3785 | 896 | 1901 | 635.5 | 2534 | 1342.5 | 145.5 | 367.5 | 282 | 165 | 78 | 1082.2672
17:00 | 3785 | 896 | 1916 | 611 | 2634 | 1342 | 145 | 348 | 274 | 162 | 46 | 710.5343
17:30 | 3798 | 896.5 | 1883 | 556 | 2725 | 1326 | 145 | 348.5 | 322 | 165 | 26.5 | 634.2672
18:00 | 3811 | 897 | 1850 | 501 | 2816 | 1310 | 145 | 349 | 370 | 168 | 7 | 558
18:30 | 3809 | 891 | 1864.5 | 607.5 | 2951.5 | 1315.5 | 145 | 368.5 | 506 | 160 | 3.5 | 714.905
19:00 | 3807 | 885 | 1879 | 714 | 3087 | 1321 | 145 | 388 | 642 | 152 | 0 | 871.81
19:30 | 3935 | 806 | 1979 | 503 | 3155 | 1322 | 145 | 430 | 695 | 156 | 0 | 996.2226
20:00 | 3973 | 805 | 2027 | 724 | 3158 | 1442 | 146 | 433 | 695 | 160 | 0 | 1057.9681
20:30 | 3971.5 | 805 | 2065 | 782 | 3156 | 1447.5 | 146 | 436 | 713.5 | 158 | 0 | 1065.3407
21:00 | 3970 | 805 | 2103 | 840 | 3154 | 1453 | 146 | 439 | 732 | 156 | 0 | 1072.7133
21:30 | 4041.5 | 805 | 2104.5 | 842 | 3156 | 1457.5 | 146 | 439 | 728 | 163 | 0 | 1092.8567
22:00 | 4113 | 805 | 2106 | 844 | 3158 | 1462 | 146 | 439 | 724 | 170 | 0 | 1113
22:30 | 4098.5 | 805 | 2113 | 789 | 3116.5 | 1467 | 146 | 440.5 | 681.5 | 166 | 0 | 1059.5
23:00 | 4084 | 805 | 2120 | 734 | 3075 | 1472 | 146 | 442 | 639 | 162 | 0 | 1006
23:30 | 4108 | 805 | 2122.5 | 774.5 | 2772.5 | 1481.5 | 146.5 | 439.5 | 600 | 168 | 0 | 1127.5 | Max Temp. in Dhaka |  | 24.7° C | 35.6° C
24:00 | 4132 | 805 | 2125 | 815 | 2470 | 1491 | 147 | 437 | 561 | 174 | 0 | 1249
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 298.929 MKWHr Energy Not Served 23.153 MKWHr Energy Requirement 322.082 MKWHr
Note on W13: Author:

## Generation
g | 2022-08-31
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 77 | 77 | 75 | 75 | 75 | 75 | 75 | 78 | 75 | 76 | 77 | 77 | 77 | 78 | 78 | 76 | 75 | 75 |  | 75 | 75 | 76 | 76 | 76 | 76 | 77 | 1821992
2 | Karnaphuli Hydro PP Unit-4 & 5 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1680000
3 | Chattogram TPP-1 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2600000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 19 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 594239
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 4 | 10 | 16 | 18 | 15 | 16 | 13 | 5 | 7 | 7 | 2 | [9 empty] | 101790
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 27 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 623297
12 | Hathazari 100 MW peaking PP | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 0 | 0 | [6 empty] | 12 | 18 | 17 | 17 | 17 | 17 | 17 | 368184
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 97 | 81 | 87 | 87 | 87 | 73 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 65 | 69 | 81 | 85 |  | 86 | 87 | 92 | 105 | 105 | 105 | 105 | 1977999
| Daudkandi 200 MW PP (B.Trac) | 190 | 190 | 191 | 190 | 188 | 189 | 190 | 150 | 140 | 180 | 186 | 182 | 182 | 185 | 185 | 190 | 189 | 150 |  | 191 | 100 | 180 | 190 | 190 | 190 | 190 | 4335936
14 | Titas 50 MW Peaking PP | 39 | 34 | 33 | 38 | 46 | 29 | 27 | 30 | 36 | 36 | 24 | 29 | 29 | 30 | 34 | 34 | 38 | 41 |  | 41 | 0 |  | 36 | 44 | 44 | 42 | 794512
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 250 | 250 | 260 | 260 | 260 | 260 | 260 | 270 | 275 | 275 | 275 | 275 | 270 | 270 | 256 | 256 | 259 | 257 |  | 254 | 316 | 331 | 332 | 330 | 335 | 330 | 6645330
18 | Kodda 300 MW PP Unit-2 (Summit) | 281 | 286 | 296 | 296 | 288 | 286 | 278 | 278 | 276 | 273 | 263 | 260 | 260 | 260 | 260 | 258 | 252 | 257 |  | 257 | 245 | 249 | 249 | 248 | 245 | 245 | 6420761
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 217454
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4 | 104 | 97 | 105 | 110 | 110 | 108 | 103 | 110 | 110 | 110 | 112 | 110 | 111 | 110 | 110 | 110 | 110 | 110 |  | 100 | 110 | 100 | 106 | 110 | 110 | 111 | 2598000
23 | Ghorasal TPP Unit-5 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 |  | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 4142250
24
25 | Ghorasal 365 MW CCPP Unit-7 | 260 | 260 | 260 | 260 | 270 | 270 | 270 | 270 | 270 | 270 | 260 | 250 | 250 | 250 | 250 | 250 | 240 | 240 |  | 235 | 235 | 250 | 250 | 250 | 250 | 270 | 6028573
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 43 | 39 | 33 | 30 | 32 | 32 | 34 | 35 | 35 | 36 | 34 |  | 39 | 39 | 39 | 39 | 45 | 42 | 43 | 934056
33 | Ashuganj 225 MW CCPP | 204 | 206 | 205 | 206 | 206 | 207 | 207 | 205 | 203 | 202 | 205 | 200 | 197 | 203 | 199 | 201 | 202 | 202 |  | 207 | 207 | 203 | 206 | 203 | 207 | 201 | 4913000
34 | Ashuganj 450 MW CCPP(South) | 320 | 300 | 330 | 305 | 310 | 270 | 270 | 270 | 310 | 305 | 310 | 310 | 305 | 305 | 320 | 305 | 305 | 305 |  | 305 | 305 | 325 | 305 | 320 | 305 | 330 | 7557000
| Ashuganj 450 MW CCPP(North) | 335 | 315 | 345 | 320 | 325 | 285 | 280 | 280 | 320 | 310 | 310 | 320 | 325 | 315 | 330 | 315 | 310 | 315 |  | 315 | 315 | 330 | 315 | 340 | 280 | 305 | 7985600
Ashuganj 420 MW CCPP(East)
35 | Ashuganj 55 MW PP (Precision) | 53 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 50 | 49 | 49 | 51 | 48 | 47 | 47 | 46 | 47 | 52 |  | 53 | 53 | 54 | 54 | 54 | 54 | 54 | 1248480
36 | Chandpur 150 MW CCPP | [23 empty] | 90 | 90 | 90 | 235440
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 375 | 379 | 385 | 386 | 391 | 391 | 391 | 391 | 408 | 408 | 399 | 391 | 386 | 385 | 384 | 384 | 381 | 377 |  | 378 | 404 | 401 | 400 | 400 | 400 | 399 | 9504760
40 | Meghnaghat 450 MW CCPP(MPL) | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 |  | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 4785000
41 | Haripur 360MW CCPP(HPL) | 175 | 186 | 192 | 200 | 207 | 212 | 207 | 251 | 257 | 217 | 208 | 196 | 196 | 198 | 198 | 199 | 198 | 196 |  | 232 | 272 | 302 | 323 | 332 | 338 | 332 | 5460000
42 | RPCL 210MW CCPP | 131 | 141 | 143 | 144 | 144 | 131 | 104 | 68 | 68 | 68 | 68 | 68 | 66 | 65 | 65 | 71 | 71 | 71 |  | 97 | 103 | 101 | 102 | 116 | 140 | 139 | 2317440
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 1 | 9 | 13 | 32 | 42 | 53 | 36 | 44 | 24 | 34 | 23 | 5 | 1 | [8 empty] | 293110
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1025000
45 | Fenchugonj CCPP Phase-2 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 |  | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 939944
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 62 | 62 | 60 | 60 | 60 | 60 | 60 | 61 | 60 | 60 | 62 | 59 | 57 | 59 | 60 | 63 | 61 | 63 |  | 64 | 64 | 61 | 61 | 58 | 62 | 61 | 1447968
48 | Shahjibazar 86MW PP (Shahjibazar) | 81 | 81 | 81 | 81 | 81 | 81 | 78 | 78 | 78 | 78 | 78 | 78 | 81 | 81 | 78 | 81 | 81 | 81 |  | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 1914240
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 194 | 194 | 194 | 194 | 193 | 193 | 193 |  | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 4607400
51 | Sylhet 20 MW GTPP | 18 | 19 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 19 | 429000
52 | Sylhet 50MW PP (EPL) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 27 | 27 | 27 | 0 | 13 | 22 |  | 24 | 24 | 25 | 25 | 25 | 25 | 25 | 552700
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 238680
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 256100
55 | Fenchugonj 51 MW PP (Barakatullah) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 17 | 17 | 17 | 25 | 25 | 25 |  | 25 | 15 | 17 | 17 | 17 | 17 | 17 | 362400
56 | Shahjahanulla 25 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 178416
57 | Bibiana-II 341 MW CCPP (Summit) | 320 | 325 | 320 | 315 | 320 | 295 | 300 | 280 | 300 | 290 | 300 | 310 | 310 | 300 | 300 | 300 | 310 | 280 |  | 290 | 260 | 270 | 310 | 300 | 300 | 315 | 7449000
| Bibiyana South 400 MW | 395 | 396 | 396 | 398 | 395 | 400 | 400 | 400 | 398 | 400 | 395 | 392 | 384 | 400 | 392 | 400 | 400 | 400 |  | 382 | 396 | 400 | 400 | 395 | 400 | 394 | 9447400
58 | Nababganj 55 MW PP (Southern power ) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 55 | 55 | 55 | 35 | 35 | 35 | 35 | 900781
59 | Tangail Palli Power Gen 22 MW | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 297360
60 | Barabkunda 22 MW PP (Regent) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 408288
61 | Narshingdi 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 16 | 16 | 16 | 16 | 13 | 13 | 13 | 13 | 13 | 13 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 390600
62 | Tangail 22 MW PP (Doreen)
63 | Impoprt (Tripura) | 162 | 162 | 160 | 158 | 156 | 146 | 146 | 142 | 148 | 154 | 154 | 158 | 158 | 166 | 170 | 168 | 162 | 168 |  | 152 | 156 | 160 | 156 | 170 | 162 | 174 | 3836160
64 | Malancha, Ctg. EPZ (United) | 35 | 36 | 37 | 38 | 39 | 37 | 33 | 14 | 5 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 13 | 12 |  | 16 | 21 | 25 | 30 | 35 | 35 | 36 | 485280
65 | Feni 22MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 21 | 21 | 21 | 21 | 0 | 5 | 21 |  | 21 | 21 | 22 | 22 | 22 | 22 | 22 | 461232
66 | Feni 11 MW PP (Doreen) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 8 | 8 | 8 | 8 | 8 | 8 | 0 | 7 | 7 |  | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 173520
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 30 | 24 | 22 | 25 | 25 | 25 | 30 | 30 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 745800
68 | Cumilla 25 MW PP (Summit) | 14 | 12 | 12 | 12 | 12 | 12 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 |  | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 327420
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 3 | 13 | 26 |  | 24 | 24 | 24 | 27 | 27 | 27 | 27 | 365400
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 788300
72 | Rupganj 33 MW PP(Summit) | 18 | 18 | 21 | 21 | 21 | 21 | 0 | 21 | 18 | 18 | 18 | 18 | 15 | 15 | 15 | 18 | 15 | 18 |  | 14 | 14 | 14 | 18 | 18 | 18 | 20 | 431400
73 | Ghorashal 108MW PP (Regent) | [25 empty] | 0 | 0
| Feni Lanka Power | [25 empty] | 0 | 0
| Chowmuhani 113 MW | 103 | 104 | 105 | 105 | 105 | 105 | 106 | 106 | 105 | 103 | 94 | 89 | 89 | 99 | 100 | 104 | 109 | 110 |  | 110 | 110 | 113 | 112 | 115 | 113 | 99 | 2514120
| Manikgonj 162MW PP(MPGL) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 37 | 69 | 70 | 108 | 124 | 144 | 144 |  | 144 | 144 | 144 | 144 | 144 | 144 | 42 | 1844640
77 | Siddhirganj 100 PP(Dutch Bangla) | 66 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 76 |  | 90 | 90 | 90 | 89 | 89 | 89 | 62 | 1645440
78 | Gazipur 52 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 32 | 42 | 40 | 40 | 40 | 40 | 16 | 509760
79 | Kodda 150MW PP | 46 | 46 | 46 | 46 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 28 | 15 | 15 | 15 | 15 | 15 | 60 |  | 100 | 110 | 110 | 110 | 110 | 46 | 46 | 912480
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | [17 empty] | 1 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 54340
| Gazipur 100 MW PP | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 59 | 1376628
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 0 | 1 | 2 | 5 | 5 | 5 | 4 | 4 | 3 | 1 | 0 | [9 empty] | 25201
| Jodiac Power | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 20 | 17 | 17 | 17 | 17 | 17 | 21 | 36 | 36 |  | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 782117
| Karnaphuli Power Ltd. | 103 | 100 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 91 | 90 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2643734
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP ( Summit) | 123 | 128 | 128 | 132 | 128 | 128 | 128 | 132 | 138 | 130 | 130 | 128 | 128 | 128 | 127 | 127 | 125 | 125 |  | 131 | 140 | 140 | 144 | 146 | 150 | 148 | 3176844
87 | Meghnaghat 100 MW(IEL) | 59 | 58 | 58 | 59 | 59 | 58 | 56 | 56 | 57 | 58 | 59 | 58 | 58 | 58 | 58 | 58 | 66 | 86 |  | 90 | 92 | 91 | 92 | 92 | 85 | 61 | 1601280
| Meghnaghat 104 MW PP (OPCL) | 55 | 45 | 55 | 55 | 56 | 55 | 55 | 55 | 55 | 60 | 61 | 70 | 73 | 84 | 91 | 92 | 92 | 92 |  | 93 | 93 | 92 | 93 | 93 | 93 | 72 | 1746240
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 258840
92 | Fenchuganj 44MW (Energyprima) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 15 | 15 | 15 | 30 | 30 | 30 |  | 30 | 16 | 16 | 16 | 17 | 16 | 16 | 435960
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1196594
94 | Gagnagar 102 MW PP (Digital Power) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 50 | 50 | 50 |  | 92 | 92 | 92 | 92 | 92 | 92 | 50 | 1447776
95 | Patenga 50MW PP (Baraka) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 0 | 6 | 20 | 24 | 24 | 36 |  | 37 | 37 | 37 | 37 | 37 | 37 | 27 | 642720
96 | Chattogram 108 MW PP (ECPV) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 10 | 10 | 10 | 10 | 24 |  | 74 | 89 | 88 | 91 | 99 | 45 | 5 | 618240
97 | katpotti 52 MW
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1333440
100 | Manikganj 55 MW PP (Northern) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 873576
101 | Kushiara 163 MW CCPP (KP) | [9 empty] | 0 | 78 | 112 | 112 | 112 | 112 | 112 | 112 | 112 |  | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 1484754
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 1 | 2 | 1 | 1 | 2 | 1 | 0 | 1 | 1 | 0 | 0 | [8 empty] | 14600
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 54 | 54 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 35 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 859680
104 | Keranigonj 300 MW PP (APR) | 175 | 175 | 175 | 175 | 176 | 176 | 176 | 175 | 175 | 130 | 170 | 172 | 172 | 172 | 174 | 170 | 182 | 120 |  | 160 | 82 | 146 | 218 | 221 | 152 | 225 | 4063031
105 | Bramhangoan 100 MW PP (Aggreko) | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 90 | 90 |  | 90 | 60 | 90 | 90 | 90 | 90 | 80 | 1940976
106 | Mymensingh 200 MW PP (United) | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 86 | 97 | 95 | 105 | 105 | 114 | 115 | 115 | 140 |  | 152 | 152 | 144 | 144 | 144 | 144 | 144 | 2608800
112 | Aurahati 100MW PP (Aggreko) | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 91 |  | 90 | 60 | 88 | 90 | 90 | 90 | 80 | 1955361
114 | Kodda 149 MW PP Unit-1 (Summit) | 136 | 135 | 134 | 142 | 149 | 149 | 149 | 149 | 149 | 147 | 140 | 149 | 149 | 149 | 149 | 149 | 149 | 149 |  | 149 | 149 | 149 | 149 | 149 | 149 | 143 | 3552048
115 | Juldah 100 MW PP Unit-3 (Acorn) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 249600
116 | Chandpur 200MW (Desh energy) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 32 | 47 |  | 72 | 100 | 100 | 100 | 100 | 100 | 48 | 905280
117 | Ashuganj 150MW PP (Midland) | 142 | 142 | 143 | 137 | 135 | 137 | 132 | 129 | 129 | 127 | 124 | 122 | 120 | 119 | 118 | 118 | 115 | 110 |  | 113 | 120 | 118 | 123 | 125 | 127 | 132 | 3044363
118 | Bibiyana-III 400 MW CCPP | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 0 | 0 | 0 | [12 empty] | 0 | 1452000
| Jamalpur 115 MW PP (United) | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 105 | 105 | 106 | 106 | 98 | 87 | 88 | 88 | 87 |  | 87 | 87 | 97 | 97 | 97 | 98 | 98 | 2473200
| Anwara 300 MW PP (United) | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 68 |  | 69 | 70 | 70 | 70 | 70 | 71 | 71 | 1382509
| Juldah unit-2 (Acorn) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 252480
| Anlima Energy Ltd. | 96 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 101 | 107 | 107 | 107 | 107 | 107 |  | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 2566800
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 6 | 15 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 423720
| Spectra Solar Plant Ltd. | [5 empty] | 1 | 4 | 14 | 22 | 23 | 31 | 31 | 34 | 31 | 15 | 8 | 7 | 1 | [8 empty] | 209188
| Chandpur 115(Doreen) | 95 | 95 | 74 | 73 | 74 | 74 | 54 | 53 | 53 | 53 | 53 | 51 | 48 | 35 | 52 | 72 | 73 | 76 |  | 79 | 96 | 92 | 87 | 79 | 76 | 77 | 1663680
| Kanchan Purbachal Power Generation Ltd. | [25 empty] | 0 | 0
Mirsharai 150 MW (Oil)
Mirsharai 150 MW (Gas)
120 | Eastern Zone Total | 7473 | 7442 | 7541 | 7513 | 7480 | 7329 | 7239 | 7194 | 7334 | 7238 | 7177 | 7175 | 7224 | 7225 | 7302 | 7303 | 7481 | 7599 |  | 7992 | 7929 | 8234 | 8398 | 8575 | 8342 | 8067 | 181986032
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | [19 empty] | 16 | 16 | 16 | 16 | 16 | 16 | 0 | 67200
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 10 | 10 | [15 empty] | 5 |  | 39 | 42 | 47 | 41 | 41 | 30 | 16 | 221280
| Khulna 225 MW CCPP | 222 | 224 | 223 | 224 | 224 | 225 | 225 | 224 | 222 | 220 | 222 | 219 | 214 | 216 | 214 | 217 | 218 | 219 |  | 222 | 223 | 222 | 222 | 222 | 224 | 223 | 5276160
129 | Rupsha 105 MW PP (Orion rupsha) | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 72 |  | 74 | 74 | 74 | 74 | 74 | 56 | 56 | 1423680
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 1 | 15 | 24 | 71 | 88 | 91 | 70 | 100 | 11 | 18 | 51 | 25 | 3 | [8 empty] | 583200
131 | Rampal 1320 MW (BIFPCL)
132 | United Payra Power Ltd. | [25 empty] | 0 | 16800
133 | Bhola Nutan Biddut BD LTD (GAS) | 222 | 224 | 224 | 224 | 224 | 224 | 224 | 214 | 223 | 223 | 202 | 220 | 212 | 208 | 216 | 213 | 211 | 217 |  | 182 | 221 | 221 | 221 | 221 | 221 | 221 | 5275991
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 32 | 32 | 32 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 632736
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 85 | 84 | 84 | 86 | 84 | 85 | 85 | 86 | 84 | 85 | 81 | 83 | 81 | 83 | 82 | 85 | 84 | 84 |  | 77 | 76 | 84 | 85 | 84 | 85 | 83 | 2006127
140 | Bhola 33 MW PP (Venture) | 33 | 34 | 33 | 30 | 30 | 25 | 24 | 23 | 22 | 22 | 22 | 22 | 23 | 25 | 25 | 23 | 23 | 24 |  | 31 | 34 | 34 | 35 | 35 | 33 | 35 | 666602
141 | Noapara 100 MW PP (Bangla Trac) | 20 | 65 | 93 | 93 | 93 | 60 | 50 | 20 | 20 | 10 | 30 | 70 | 92 | 92 | 92 | 60 | 30 | 10 |  | 92 | 60 | 60 | 92 | 92 | 92 | 92 | 1482240
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP | 42 | 42 | 42 | 37 | 37 | 30 | [10 empty] | 20 | 35 |  | 45 | 62 | 55 | 55 | 51 | 49 | 49 | 558080
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 32 |  | 32 | 32 | 32 | 32 | 32 | 32 | 15 | 524880
146 | Bheramara HVDC | 896 | 896 | 895 | 895 | 895 | 895 | 896 | 897 | 896 | 895 | 895 | 897 | 896 | 896 | 896 | 896 | 896 | 897 |  | 885 | 806 | 805 | 805 | 805 | 805 | 805 | 21216000
147 | Bheramara 410 MW CCPP | 215 | 215 | 220 | 220 | 220 | 210 | 210 | 205 | 200 | 200 | 200 | 190 | 190 | 190 | 185 | 185 | 175 | 170 |  | 170 | 175 | 170 | 175 | 175 | 185 | 180 | 4802112
148 | Payra 1320 MW | 1140 | 1140 | 1130 | 1100 | 1090 | 1050 | 1010 | 980 | 970 | 970 | 970 | 980 | 1000 | 1010 | 1010 | 1010 | 1010 | 980 |  | 990 | 990 | 1110 | 1120 | 1130 | 1140 | 1160 | 27365400
149
150 | Barapukuria TPP Unit-1 | 80 | 80 | 80 | 80 | 82 | 79 | 81 | 80 | 80 | 81 | 80 | 82 | 81 | 81 | 81 | 83 | 82 | 80 |  | 81 | 82 | 82 | 83 | 82 | 82 | 81 | 1947055
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 249 | 250 | 250 | 250 | 250 | 250 | 250 |  | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 6040900
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [19 empty] | 24 | 24 | 24 | 24 | 24 | 16 | 16 | 126736
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 0 | 1 | 4 | 5 | 5 | 4 | 5 | 2 | 3 | 1 | 1 | 0 | [8 empty] | 34920
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 205 | 206 | 205 | 205 | 206 | 206 | 205 | 206 | 205 | 194 | 192 | 191 | 190 | 192 | 191 | 191 | 192 | 191 |  | 190 | 190 | 191 | 191 | 190 | 190 | 191 | 5035655
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
| Sirajgonj 225 MW CCPP Unit-2 (Oil) | 214 | 214 | 214 | 214 | 214 | 217 | 217 | 219 | 216 | 216 | 212 | 190 | 209 | 209 | 187 | 170 | 130 | 130 |  | 166 | 207 | 211 | 217 | 217 | 218 | 214 | 5038309
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 177 | 177 | 177 | 177 | 177 | 176 | 176 | 176 | 176 | 175 | 137 | 143 | 149 | 162 | 167 | 176 | 173 | 174 |  | 182 | 188 | 174 | 183 | 187 | 183 | 182 | 4387827
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 416 | 415 | 414 | 417 | 417 | 402 | 420 | 370 | 416 | 415 | 418 | 414 | 414 | 414 | 414 | 414 | 414 | 359 |  | 356 | 414 | 414 | 419 | 415 | 422 | 417 | 9773745
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | 4 | 4 | 4 | 38 | 29 | 24 | 24 | 25 | 24 | 24 | 24 | 23 | 25 | 22 | 22 | 22 | 22 | 27 |  | 40 | 36 | 35 | 36 | 31 | 30 | 24 | 538134
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 18 | 18 | 21 | 21 | 21 | 20 | 20 | 21 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 484320
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 236862
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 862400
167 | Katakhali 50 MW Peaking PP | 24 | [10 empty] | 5 | 16 | 16 | 21 | 32 | 32 | 32 |  | 32 | 32 | 32 | 32 | 24 | 24 | 24 | 288381
168 | Santahar 50 MW Peaking PP | [17 empty] | 13 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 189980
169 | Natore 52 MW PP (Rajlanka) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 193440
170 | Chapainawabganj 100 MW Peaking PP | [19 empty] | 60 | 81 | 81 | 81 | 82 | 82 | 30 | 383776
171 | Baghabari 200 MW PP (Paramount) | 163 | 163 | 163 | 163 | 163 | 162 | 161 | 50 | 86 | 100 | 131 | 117 | 156 | 156 | 120 | 80 | 40 | 40 |  | 91 | 141 | 160 | 160 | 161 | 120 | 148 | 3211574
| Bagura 113 MW PP (Confidence)-2 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 57 | 70 | 75 |  | 94 | 94 | 94 | 94 | 94 | 94 | 50 | 1618656
172 | Confidence Power Bogura Unit-1 113 MW | 95 | 95 | 95 | 95 | 95 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 95 | 95 | 95 |  | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 1929504
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 55 | 55 | 51 | 55 | 56 | 56 | 56 | 50 | 56 | 91 | 91 |  | 92 | 92 | 92 | 92 | 92 | 92 | 56 | 1582713
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 0 | 1 | 1 | 1 | 1 | 2 | 1 | 2 | 2 | 4 | 2 | 1 | [8 empty] | 16395
178 | Energypac Power Venture Thakurgaon Ltd. | [13 empty] | 90 | 91 | 90 | 90 | 90 |  | 91 | 90 | 90 | 90 | 90 | 90 | 0 | 862848
178 | Intraco Solar 30 MW | [7 empty] | 0 | 0 | 0 | 0 | 1 | 3 | 8 | 8 | 14 | 4 | 1 | [8 empty] | 40577