## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2022-09-06 | Tuesday
|  | Date (day): | 2022-09-06 |  | Tuesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 12372.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14114 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2022-09-05 | 2022-09-06 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 230 | 230 | 230 | 230
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint.
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 260 | 240 | 260 | 260 | 105 |  | Gas shortage
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 72 | 77 | 90 | 90 | 18 |  | Gas Shortage.
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 398 | 351 | 400 | 360 | 52 |  | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 186 | 166 | 200 | 170 | 190 |  | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 215 | 200 | 200 | 200 | 250 |  | Dirty fuel
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 51 | 75 | 50 | 75 | 25 |  | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 122 | 115 | 120 | 120 | 215 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 0 | 0 | 0 | 0 |  | 102 | Under maint
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 22 | 19 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 62 | 80 | 62 | 80 | 20 |  | Engine problem
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 264 | 224 | 280 | 300 | 35 |  | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 50 | 92 | 50 | 92 | 10 |  | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 54 | 17 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 17 | 116 | 17 | 115 | 34 |  | Fuel shortage
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 35 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 35 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 46 | 49 | 51 | 51 |  | 29 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 8 | 12 | 21 | 21 |  | 12 | Engine problem
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 16 | 16 | 16 | 32 |  | 20 | Engine problem
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 192 | 255 | 260 | 285 |  | 15 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 225 | 226 | 220 | 220 |  | 80 | Engine problem
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 80 | 90 | 90 | 90 |  | 10 | Engine problem
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 81 | 90 | 80 | 90 |  | 10 | Engine problem
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 149 | 149 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 50 | 85 | 50 | 85 |  | 20 | Engine problem
37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 54 | 74 | 55 | 93 | 11 |  | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 72 | 162 | 72 | 162
39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 9 | 0 | 30 | 0
40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 18 | 18 | 18 | 18 | 37 |  | Fuel shortage
| Dhaka area Total |  |  |  |  | 6263 | 5847 | 3121 | 3466 | 3265 | 3662 | 1263 | 988
41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 105 | 105 | 105 | 105 | 75 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 17 | 25 | 25 | 25
43 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 20 | 0 | 20 | 0
44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 26 | 38 | 25 | 38 |  | 12 | Engine problem
45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 150 | 144 | 150 | 150 |  | 80 | Low Water Level
46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | S/D due to HGPI
47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 51 | 105 | 55 | 105
49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 25 | 24 | 26 | 26 | 72 |  | Fuel shortage
50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 13 | 47 | 17 | 47 | 55 |  | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 33 | 78 | 33 | 80 |  | 20 | Engine problem
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 32 | 90 | 33 | 90 |  | 10 | Engine problem
53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 15 | 15 | 15 | 15 |  | 7 | Engine problem
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 9 | 23 | 10 | 20
54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 7 | 94 | 11 | 94 | 14 |  | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 3 | 0 | 5 | 0
56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 52 | 160 | 160 | 160 | 140 |  | Fuel shortage
57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 17 | 36 | 35 | 36 |  | 18 | Engine prolem
58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 110 | 110 | 110 | 110
59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 38 | 90 | 38 | 90
60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 89 | 107 | 107 | 107 |  | 9 | Engine problem
| Mirsharai 150 MW |  | Gas/HSD | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0
| Chattogram area Total |  |  |  |  | 2442 | 2382 | 812 | 1291 | 980 | 1298 | 536 | 531
61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 205 | 209 | 205 | 210 | 11 |  | Gas shortage
63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 345 | 280 | 330 | 280 | 80 |  | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 325 | 280 | 330 | 280 | 80 |  | Gas shortage
| Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+136*1 | 284 | 284 | 0 | 0 | 0 | 0 |  |  | On test.
65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 39 | 45 | 43 | 45
66 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 55 | 48 | 56 | 55 | 55
67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 16 | 8 | 8 | 8 | 187 |  | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 51 | 51 | 51
69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 122 | 142 | 130 | 145 |  | 5 | Engine problem
70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 15 | 30 | 25 | 35 |  | 17 | Engine problem
71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 0 | 0 | 0 |  | 163 | Under maint
72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 27 | 150 | 17 | 200
73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 19 | 19
74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 10 | 10 | 10 | 10
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 134 | 94 | 143 | 166
75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 14 | 29 | 33 | 33
76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 34 | 8 | 34 | 18 |  | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 21 | 21 | 21 |  | 4 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 185 | 150 | 100 | 190 |  | 10 | Engine problem
79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 17 | 0 | 52 | 62 |  | Fuel shortage
80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 96 | 106 | 105 | 105
81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 17 |  | 37 | 33 kV feeder fault
82 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 38 | 96 | 40 | 96 | 19 |  | Fuel shortage
| Cumilla Area Total |  |  |  |  | 3193 | 3169 | 1793 | 1844 | 1690 | 2052 | 591 | 236
83 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 65 | 93 | 68 | 100 | 102 |  | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  |  | Engine problem
85 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0 |  | 8 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 0 | 0 | 1.6 | 0
87 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 91 | 95 | 90 | 95 | 105 |  | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 91 | 107 | 90 | 108
89 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 5 | 0 | 50 | 0
90 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 12 | 12 |  | 10 | Engine problem
| Mymensingh Area Total |  |  |  |  | 717 | 614 | 264 | 307 | 311.6 | 315 | 102 | 18
91 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 43 | 43 | 43 |  | 27 | Machine problem.
92 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 41 | 41 | 41 | 41 |  | 49 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 | 163 |  | Gas shortage
94 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 31 | 47 | 31 | 47
96 | Fenchuganj 44MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 28 | 37 | 20 | 44 |  | 6
97 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 8 | 11 | 11
98 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 60 | 62 | 60 | 64
99 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 78 | 81 | 81 | 81
100 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
101 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 0 | 0 | 0 |  | 231 | Under Maint.
102 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Gas shortage
103 | Sylhet 50MW PP (EPL) |  | Gas | NENP | 27*2 | 50 | 50 | 20 | 25 | 25 | 25 | 25 |  | Gas shortage
104 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 10 | 24 | 24 | 24
105 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 260 | 300 | 300 | 41 |  | FGMO
106 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 400 | 401 | 400 | 400
107 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
108 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 395 | 401 | 400 | 400
| Sylhet Area Total |  |  |  |  | 2522 | 2477 | 1427 | 1440 | 1446 | 1490 | 249 | 743
109 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 892 | 891 | 908 | 908 |  |  | .
110 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 0 | 0 | 0 | 0 | 115 |  | Fuel shortage
111 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 45 | 0 | 50 |  | 4 | Engine problem
112 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 218 | 227 | 225 | 225
113 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 65 | 0 | 60 |  | 49 | Engine problem
114 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 250 | 230 | 250 | 250 | 160 |  | Gas shortage
115 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 0 | 0 | 0 | 40 |  | Fuel shortage
116 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 50 | 60 | 20 | 94 |  | 6 | Engine problem
117 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 37 | 75 | 35 | 75 | 30 |  | Fuel shortage
118 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 15 | 15 | 15 | 90 |  | Fuel shortage
119 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 24 | 0 | 100 | 0
| Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 0 | 0 | 0 | 107 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 2388 | 2384 | 1578 | 1608 | 1553 | 1677 | 451 | 59
120 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 16 | 32 | 32 | 32 |  |  | Line O/L
121 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 19 | 28 | 20 | 30 |  | 10 | Engine problem
122 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 83 | 86 | 85 | 85 |  | 109 | Machine problem
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
123 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 820 | 1080 | 1110 | 1110 |  |  | Line O/L
124 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 218 | 220 | 220 | 220
125 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 0 | 17 |  |  | Line O/L
| Barisal Area Total |  |  |  |  | 1958 | 1958 | 1156 | 1446 | 1467 | 1494 | 0 | 119
126 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
127 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 32 | 0 | 32 |  | 20 | Engine problem
128 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 25 |  | 46 | Engine problem
129 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
130 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage
131 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 16 | 32 | 16 | 32 |  | 18 | Engine problem
132 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 193 | 192 | 194 | 194 | 16 |  | Gas shortage
133 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 204 | 217 | 220 | 220
134 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 199 | 178 | 195 | 190 | 30 |  | Gas shortage
135 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 417 | 428 | 414 | 414
136 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 33 | 0 | 33 |  | 17 | Engine problem
137 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
138 | Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
139 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 10 | 10 | 10 | 10
140 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 8 | 8 | 8
141 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 81 | 0 | 80 |  | 24 | Engine problem
142 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 50 | 80 | 60 | 165 |  | 35 | Engine problem
143 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 50 | 94 | 50 | 94 |  | 19 | Engine problem
144 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 75 | 95 | 60 | 95 |  | 18 | Engine problem
145 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 1 | 0 | 6 | 0
| Rajshahi Area Total |  |  |  |  | 2199 | 2129 | 1245 | 1502 | 1255 | 1614 | 267 | 197
146 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 80 | 82 | 80 | 80
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
147 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 249 | 250 | 250 | 250 | 24
148 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
149 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
150 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 54 | 91 | 55 | 92 |  | 21 | Engine problem
151 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 4 | 0 | 8 | 0
152 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 0 | 90 | 0 | 90 |  | 25 | Fuel shortage
| Intraco Solar 30 MW |  | Solar | IPP | 0 | 0 | 0 | 23 | 0 | 12 | 0
| Rangpur Area Total |  |  |  |  | 800 | 720 | 410 | 513 | 405 | 512 | 64 | 131
| Total |  |  |  |  | 22482 | 21680 | 11806 | 13417 | 12372.6 | 14114 | 3523 | 3022
A. |  | 2022-09-05 | (Yesterday) |  |  |  |  | Monday
1 | Highest Generation : |  |  | 13417 | MW at | 19:30 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:30 | hrs.
2 | Minimum Generation : |  |  | 10580 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 13522 | MW
3 | Day peak Generation : |  |  | 11806 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 12999.89 | MW
4 | Evening peak Generation : |  |  | 13417 | MW at | 19:30 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 97 | MW
5 | Total Energy Generation : |  | 287.4694 | MKWHr | By Solar | 0.87364 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Gas : | 141.9451 | MKWHr |  | By Oil: | 83.7041 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 33.0863 | MKWHr |  | By Hydro: | 3.511 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 3523 | MW | Dhaka | 4711.34 | 4711.34 |  | 0 |  | 18:00 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 3022 | MW | Chittagong | 1377.9 | 1377.9 |  | 0 |  | 19:00 |  | 117.9616
|  |  | Total = |  |  | 6545 | MW | Khulna | 1551.4 | 1551.4 |  | 0 |  | 19:30 |  | 96.7654
7 | Total Gas Supplied : |  |  | 1051.99 | MMCFD |  |  | Rajshahi | 1325.3 | 1325.3 |  | 0 |  | 20:00 |  | 67.275
8 | Fuel Cost : | i) Gas : | Taka | 162471264.552 | ii) Oil : | Taka | 1228910641.13 | Comilla | 1268 | 1268 |  | 0 |  | 21:00 |  | 0
|  | iii) Coal : |  | 264347817.94 | Total | Taka | 1655729723.622 | Mymensingh | 990 | 893 |  | 97 |  | 22:00 |  | 0
9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0 | MKWHr. | Sylhet | 509 | 509 |  | 0 |  | 23:00 |  | 0
| ii) During Peak Demand : |  |  | 1295 | MW (E to W) at | 19:30 | hrs | Barisal | 392.95 | 392.95 |  | 0 |  | 24:00 |  | 0
| iii) Maximum : |  |  | 1115 | MW at | 21:00 | hrs | Rangpur | 874 | 874 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 34° C |  |  | Total | 12999.89 | 12902.89 |  | 97
B. |  | 2022-09-06 | (Today) |  |  |  | Tuesday |  |  | Probable max. temperature in Dhaka |  |  | 32.6° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 13400 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 14114 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 11800 | MW
4 | Reserve(Generation end) |  |  |  | 714 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 287.1052 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 10615 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.5556 | MKWHr. | ii) HVDC Flow at Peak Time |  | 891 | MW at | 19:30 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.7936 | MKWHr. | iii) Maximum HVDC Flow : |  | 893 | MW at | 7:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 96.17 |  | (b) Today: | 96.23 |  | (c) Rule Curve: |  | 100.15
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2022-09-05
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 231 | 0 | 260 | 92 | 0 | 370 | 163 |  | 0 | 210 | 112 | 50 | 0 | 55 | 253 | 0 | 0 | 62 | 50 | 50 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 25 | 27 | 33 | 14 | 16 | 0 | 82 | 70 | 105 | 0 | 20 | 0 | 0 | 0 | 0 |  | 12 | 25 | 13 | 33 | 11 | 26 | 15 | 38 | 0 | 0 | 0 | 280 | 275 | 208 | 8 | 51 | 45 | 51 | 0 | 51 | 0 | 31 | 8 | 22 | 10 | 33 | 20 | 140 | 150 | 0 | 0 | 0 | 43 | 41 | 31 | 30 | 0 | 0 | 62 | 81 | 0 | 0 | 0 | 24 | 10 | 305 | 24 | 11 | 189 | 213 | 225 | 80 | 95 | 80 | 149 | 0 | 32 | 45 | 132 | 403 | 97 | 50 | 69 | 0 | 52 | 36 | 110 | 17 | 104 | 38 | 400 | 55 | 0 | 17 | 107 | 0 | 17 | 0 | 38 | 18 | 0 | 0 | 0 |  | 887 | 0 | 185 | 0 | 0 | 224 | 0 | 0 | 10 | 0 | 0 | 84 | 34 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 8 | 30 | 22 | 0 | 10 | 80 | 0 | 249 | 0 | 0 | 192 | 0 | 0 | 50 | 0 | 90 | 185 | 0 | 417 | 35 | 153 | 50 | 0 | 56 | 0 | 0 | 55 | 1080 | 224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 7542 | 4466 | 12008 | 4086 | 887 | 1903 | 817 | 2157 | 1409 | 152 | 274 | 233 | 140 | 0 | 868.1237 | 96.17
2:00 | 0 | 0 | 231 | 0 | 260 | 92 | 0 | 378 | 163 |  | 0 | 210 | 118 | 50 | 0 | 55 | 253 | 0 | 0 | 62 | 50 | 50 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 25 | 27 | 33 | 14 | 16 | 0 | 83 | 70 | 105 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 25 | 13 | 33 | 11 | 26 | 15 | 38 | 0 | 0 | 0 | 290 | 285 | 207 | 8 | 50 | 45 | 52 | 0 | 51 | 0 | 31 | 8 | 22 | 10 | 33 | 20 | 138 | 146 | 0 | 0 | 0 | 43 | 41 | 31 | 30 | 0 | 0 | 63 | 81 | 0 | 0 | 0 | 24 | 10 | 300 | 24 | 11 | 130 | 195 | 226 | 80 | 96 | 80 | 149 | 0 | 32 | 17 | 132 | 402 | 98 | 50 | 69 | 0 | 52 | 36 | 110 | 17 | 99 | 38 | 400 | 55 | 0 | 17 | 107 | 0 | 17 | 0 | 38 | 18 | 0 | 0 | 0 |  | 888 | 0 | 190 | 0 | 0 | 224 | 0 | 0 | 10 | 0 | 0 | 84 | 34 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 30 | 22 | 0 | 10 | 80 | 0 | 250 | 0 | 0 | 193 | 0 | 0 | 33 | 0 | 90 | 185 | 0 | 421 | 35 | 160 | 50 | 0 | 56 | 0 | 0 | 55 | 1050 | 224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 7463 | 4414 | 11877 | 4114 | 888 | 1909 | 766 | 2113 | 1380 | 153 | 257 | 192 | 138 | 0 | 712.3775 | 96.17
3:00 | 0 | 0 | 231 | 0 | 260 | 92 | 0 | 378 | 166 |  | 0 | 210 | 125 | 50 | 0 | 55 | 251 | 0 | 0 | 62 | 50 | 50 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 25 | 27 | 33 | 16 | 16 | 0 | 84 | 70 | 105 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 25 | 13 | 33 | 12 | 26 | 15 | 39 | 0 | 0 | 0 | 270 | 265 | 210 | 8 | 51 | 45 | 51 | 0 | 51 | 0 | 31 | 8 | 22 | 10 | 33 | 20 | 136 | 148 | 0 | 0 | 0 | 43 | 41 | 31 | 30 | 0 | 0 | 63 | 81 | 0 | 0 | 0 | 24 | 10 | 295 | 24 | 11 | 130 | 195 | 225 | 80 | 94 | 80 | 149 | 0 | 32 | 17 | 137 | 402 | 98 | 50 | 69 | 0 | 52 | 36 | 110 | 17 | 99 | 38 | 400 | 54 | 0 | 17 | 107 | 0 | 17 | 0 | 37 | 18 | 0 | 0 | 0 |  | 888 | 0 | 195 | 0 | 0 | 226 | 0 | 0 | 10 | 0 | 0 | 82 | 32 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 28 | 22 | 0 | 10 | 80 | 0 | 250 | 0 | 0 | 192 | 0 | 0 | 68 | 0 | 91 | 186 | 0 | 426 | 35 | 160 | 50 | 0 | 56 | 0 | 0 | 55 | 1000 | 222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 7434 | 4388 | 11822 | 4083 | 888 | 1915 | 766 | 2099 | 1330 | 154 | 294 | 225 | 136 | 0 | 440.5129 | 96.17
4:00 | 0 | 0 | 230 | 0 | 260 | 92 | 0 | 377 | 172 |  | 0 | 210 | 125 | 49 | 0 | 55 | 258 | 0 | 0 | 62 | 50 | 50 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 25 | 27 | 33 | 16 | 16 | 0 | 84 | 70 | 105 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 25 | 13 | 33 | 12 | 26 | 15 | 39 | 0 | 0 | 0 | 300 | 300 | 207 | 8 | 50 | 45 | 52 | 0 | 51 | 0 | 31 | 8 | 22 | 10 | 33 | 20 | 132 | 150 | 0 | 0 | 0 | 43 | 41 | 31 | 30 | 0 | 0 | 64 | 81 | 0 | 0 | 0 | 24 | 10 | 290 | 24 | 11 | 100 | 195 | 136 | 80 | 94 | 80 | 149 | 0 | 32 | 17 | 135 | 402 | 98 | 50 | 69 | 0 | 52 | 36 | 110 | 17 | 94 | 38 | 400 | 55 | 0 | 17 | 107 | 0 | 17 | 0 | 38 | 17 | 0 | 0 | 0 |  | 892 | 0 | 200 | 0 | 0 | 224 | 0 | 0 | 10 | 0 | 0 | 85 | 32 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 10 | 80 | 0 | 250 | 0 | 0 | 193 | 0 | 0 | 206 | 0 | 70 | 188 | 0 | 419 | 35 | 0 | 50 | 0 | 56 | 0 | 0 | 55 | 980 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 7375 | 4306 | 11681 | 4163 | 892 | 1913 | 466 | 2092 | 1310 | 154 | 430 | 335 | 132 | 0 | 86.628 | 96.17
5:00 | 0 | 0 | 231 | 0 | 260 | 92 | 0 | 378 | 174 |  | 0 | 210 | 125 | 51 | 0 | 55 | 262 | 0 | 0 | 62 | 50 | 50 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 25 | 27 | 33 | 16 | 16 | 0 | 83 | 70 | 105 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 25 | 13 | 33 | 11 | 26 | 15 | 40 | 0 | 0 | 0 | 280 | 270 | 210 | 8 | 50 | 45 | 51 | 0 | 51 | 0 | 31 | 8 | 22 | 10 | 33 | 20 | 130 | 149 | 0 | 0 | 0 | 43 | 41 | 31 | 30 | 0 | 0 | 64 | 81 | 0 | 0 | 0 | 24 | 10 | 280 | 24 | 11 | 100 | 195 | 131 | 80 | 55 | 80 | 141 | 0 | 32 | 17 | 137 | 402 | 98 | 50 | 69 | 0 | 52 | 36 | 110 | 17 | 94 | 38 | 400 | 55 | 0 | 17 | 107 | 0 | 17 | 0 | 37 | 18 | 0 | 0 | 0 |  | 892 | 0 | 200 | 0 | 0 | 226 | 0 | 0 | 10 | 0 | 0 | 86 | 29 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 10 | 80 | 0 | 250 | 0 | 0 | 192 | 0 | 0 | 217 | 0 | 70 | 191 | 0 | 428 | 35 | 0 | 50 | 0 | 56 | 0 | 0 | 55 | 980 | 227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 7273 | 4330 | 11603 | 4124 | 892 | 1913 | 461 | 2048 | 1310 | 153 | 443 | 346 | 130 | 0 | 39.6277 | 96.17
6:00 | 0 | 0 | 230 | 0 | 270 | 92 | 0 | 381 | 177 |  | 0 | 225 | 125 | 49 | 0 | 55 | 262 | 0 | 0 | 62 | 50 | 17 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 25 | 27 | 33 | 16 | 16 | 0 | 82 | 70 | 105 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 25 | 13 | 33 | 12 | 26 | 15 | 40 | 0 | 0 | 0 | 280 | 265 | 210 | 8 | 52 | 42 | 51 | 0 | 51 | 0 | 31 | 8 | 22 | 10 | 33 | 20 | 122 | 149 | 0 | 0 | 0 | 43 | 41 | 31 | 30 | 0 | 0 | 64 | 81 | 0 | 0 | 0 | 24 | 10 | 270 | 24 | 11 | 0 | 195 | 0 | 0 | 55 | 0 | 135 | 0 | 32 | 17 | 135 | 401 | 98 | 50 | 69 | 0 | 52 | 36 | 110 | 17 | 95 | 38 | 400 | 54 | 0 | 17 | 107 | 0 | 17 | 0 | 37 | 5 | 0 | 0 | 0 |  | 892 | 0 | 205 | 0 | 0 | 220 | 0 | 0 | 4 | 0 | 0 | 72 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 10 | 80 | 0 | 250 | 0 | 0 | 192 | 0 | 0 | 219 | 0 | 0 | 195 | 0 | 429 | 35 | 0 | 50 | 0 | 56 | 0 | 0 | 55 | 950 | 227 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 |  | 6831 | 4198 | 11029 | 4124 | 892 | 1919 | 0 | 2010 | 1280 | 152 | 439 | 309 | 122 | 1 | 39.6277 | 96.17
7:00 | 0 | 0 | 230 | 0 | 260 | 88 | 0 | 385 | 177 |  | 0 | 225 | 125 | 50 | 0 | 55 | 265 | 0 | 0 | 62 | 50 | 17 | 0 | 0 | 0 | 0 | 17 | 17 | 35 | 19 | 25 | 0 | 33 | 15 | 16 | 0 | 81 | 70 | 105 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 25 | 13 | 33 | 12 | 26 | 15 | 31 | 0 | 0 | 0 | 308 | 285 | 207 | 8 | 50 | 41 | 51 | 0 | 51 | 0 | 0 | 8 | 22 | 10 | 33 | 20 | 112 | 106 | 0 | 0 | 0 | 43 | 41 | 31 | 30 | 0 | 0 | 62 | 81 | 0 | 0 | 0 | 21 | 10 | 290 | 7 | 11 | 0 | 195 | 0 | 0 | 38 | 0 | 122 | 0 | 32 | 17 | 133 | 402 | 98 | 50 | 54 | 0 | 52 | 36 | 110 | 17 | 96 | 38 | 400 | 32 | 4 | 17 | 107 | 0 | 17 | 5 | 38 | 18 | 0 | 0 | 0 |  | 893 | 0 | 205 | 0 | 0 | 155 | 0 | 0 | 0 | 0 | 0 | 86 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 10 | 79 | 0 | 250 | 0 | 0 | 193 | 0 | 0 | 130 | 0 | 0 | 197 | 0 | 415 | 35 | 0 | 35 | 0 | 35 | 0 | 0 | 35 | 950 | 226 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 2 |  | 6681 | 3990 | 10671 | 4091 | 893 | 1903 | 0 | 1883 | 1279 | 151 | 285 | 185 | 112 | 19 | 0 | 96.17
8:00 | 0 | 0 | 230 | 0 | 260 | 86 | 0 | 378 | 175 |  | 0 | 225 | 125 | 50 | 0 | 55 | 257 | 0 | 0 | 62 | 50 | 17 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 25 | 0 | 33 | 8 | 16 | 0 | 81 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 25 | 13 | 33 | 12 | 26 | 15 | 17 | 0 | 0 | 0 | 355 | 265 | 207 | 8 | 50 | 41 | 52 | 0 | 51 | 0 | 0 | 8 | 19 | 10 | 23 | 20 | 118 | 69 | 0 | 0 | 0 | 43 | 41 | 31 | 6 | 0 | 0 | 62 | 81 | 0 | 0 | 0 | 15 | 10 | 300 | 0 | 11 | 0 | 195 | 0 | 0 | 85 | 0 | 112 | 0 | 32 | 17 | 130 | 403 | 106 | 50 | 51 | 1 | 52 | 36 | 110 | 17 | 95 | 38 | 400 | 17 | 5 | 17 | 107 | 0 | 17 | 9 | 38 | 17 | 0 | 0 | 0 |  | 892 | 0 | 135 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 86 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 10 | 80 | 0 | 250 | 0 | 0 | 198 | 0 | 0 | 130 | 0 | 0 | 201 | 0 | 419 | 35 | 0 | 35 | 0 | 34 | 0 | 1 | 60 | 880 | 226 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 7 |  | 6650 | 3930 | 10580 | 3984 | 892 | 1867 | 0 | 1947 | 1210 | 151 | 300 | 185 | 118 | 56 | 0 | 96.18
9:00 | 0 | 0 | 230 | 0 | 260 | 81 | 0 | 397 | 206 |  | 0 | 225 | 125 | 49 | 0 | 55 | 295 | 0 | 0 | 62 | 50 | 17 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 25 | 6 | 33 | 14 | 16 | 0 | 81 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 25 | 13 | 33 | 12 | 26 | 15 | 8 | 0 | 0 | 0 | 310 | 300 | 209 | 8 | 50 | 37 | 51 | 0 | 51 | 0 | 0 | 8 | 19 | 10 | 15 | 20 | 124 | 69 | 0 | 0 | 1 | 43 | 41 | 31 | 12 | 0 | 0 | 62 | 78 | 0 | 0 | 0 | 0 | 9 | 290 | 0 | 11 | 70 | 193 | 53 | 80 | 85 | 81 | 119 | 1 | 32 | 17 | 125 | 401 | 106 | 50 | 51 | 2 | 52 | 36 | 110 | 17 | 95 | 38 | 401 | 31 | 12 | 29 | 107 | 0 | 17 | 10 | 38 | 17 | 0 | 0 | 0 |  | 892 | 0 | 120 | 0 | 0 | 223 | 0 | 0 | 0 | 0 | 0 | 86 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 10 | 80 | 0 | 250 | 0 | 0 | 195 | 0 | 0 | 165 | 0 | 10 | 197 | 0 | 424 | 35 | 27 | 50 | 0 | 49 | 0 | 4 | 75 | 890 | 225 | 0 | 0 | 1 | 52 | 0 | 0 | 0 | 0 | 17 |  | 7017 | 4140 | 11157 | 4010 | 892 | 1863 | 321 | 2033 | 1220 | 151 | 388 | 220 | 124 | 100 | 0 | 96.18
10:00 | 0 | 0 | 230 | 0 | 260 | 77 | 0 | 404 | 213 |  | 0 | 225 | 125 | 50 | 0 | 55 | 290 | 0 | 0 | 62 | 50 | 17 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 25 | 23 | 33 | 13 | 16 | 0 | 81 | 70 | 110 | 0 | 17 | 0 | 0 | 0 | 0 |  | 12 | 25 | 13 | 33 | 12 | 26 | 12 | 8 | 0 | 0 | 0 | 315 | 280 | 206 | 8 | 50 | 40 | 52 | 0 | 51 | 0 | 0 | 8 | 19 | 10 | 15 | 20 | 124 | 66 | 0 | 0 | 1 | 43 | 41 | 31 | 21 | 0 | 0 | 61 | 78 | 0 | 0 | 0 | 0 | 9 | 280 | 6 | 11 | 70 | 195 | 148 | 80 | 94 | 80 | 149 | 3 | 32 | 17 | 125 | 402 | 91 | 50 | 51 | 3 | 51 | 17 | 110 | 17 | 95 | 38 | 400 | 53 | 41 | 72 | 91 | 0 | 17 | 18 | 38 | 18 | 0 | 0 | 0 |  | 892 | 0 | 120 | 0 | 0 | 222 | 0 | 0 | 0 | 0 | 0 | 86 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 8 | 0 | 22 | 0 | 10 | 81 | 0 | 250 | 0 | 0 | 193 | 0 | 0 | 215 | 0 | 10 | 198 | 0 | 420 | 37 | 10 | 50 | 0 | 56 | 0 | 4 | 75 | 830 | 226 | 0 | 0 | 1 | 85 | 0 | 0 | 0 | 0 | 29 |  | 7205 | 4172 | 11377 | 4011 | 892 | 1862 | 398 | 2091 | 1161 | 151 | 437 | 280 | 124 | 185 | 0 | 96.18
11:00 | 0 | 0 | 230 | 0 | 260 | 75 | 0 | 403 | 203 |  | 0 | 225 | 125 | 50 | 0 | 55 | 275 | 0 | 0 | 62 | 50 | 17 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 25 | 23 | 33 | 13 | 16 | 0 | 81 | 70 | 108 | 0 | 17 | 0 | 0 | 0 | 0 |  | 12 | 25 | 13 | 33 | 12 | 26 | 15 | 9 | 0 | 0 | 0 | 315 | 285 | 206 | 16 | 50 | 38 | 51 | 0 | 35 | 0 | 0 | 8 | 19 | 10 | 15 | 20 | 130 | 66 | 0 | 0 | 0 | 43 | 41 | 31 | 27 | 0 | 0 | 60 | 78 | 0 | 0 | 0 | 5 | 10 | 290 | 3 | 11 | 185 | 195 | 225 | 80 | 94 | 80 | 149 | 8 | 32 | 20 | 125 | 402 | 91 | 50 | 51 | 4 | 52 | 17 | 110 | 17 | 95 | 38 | 401 | 55 | 19 | 72 | 90 | 0 | 17 | 18 | 38 | 17 | 0 | 0 | 0 |  | 892 | 0 | 255 | 0 | 0 | 221 | 0 | 0 | 0 | 0 | 0 | 84 | 19 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 8 | 0 | 22 | 0 | 10 | 80 | 0 | 250 | 0 | 0 | 193 | 0 | 0 | 216 | 0 | 50 | 199 | 0 | 421 | 37 | 33 | 50 | 0 | 52 | 0 | 5 | 75 | 820 | 224 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 19 |  | 7377 | 4291 | 11668 | 4130 | 892 | 1866 | 653 | 2091 | 1150 | 151 | 437 | 287 | 130 | 97 | 0 | 96.18
12:00 | 0 | 0 | 230 | 0 | 260 | 72 | 0 | 398 | 186 |  | 0 | 215 | 122 | 51 | 0 | 55 | 264 | 0 | 0 | 62 | 50 | 17 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 25 | 21 | 33 | 8 | 16 | 0 | 80 | 70 | 105 | 0 | 17 | 0 | 0 | 0 | 0 |  | 12 | 25 | 13 | 33 | 7 | 26 | 15 | 9 | 0 | 0 | 0 | 345 | 325 | 205 | 16 | 50 | 39 | 48 | 0 | 43 | 0 | 15 | 8 | 19 | 10 | 14 | 20 | 134 | 65 | 0 | 0 | 0 | 43 | 41 | 31 | 28 | 0 | 0 | 60 | 78 | 0 | 0 | 0 | 20 | 10 | 300 | 10 | 11 | 185 | 192 | 225 | 80 | 91 | 81 | 149 | 20 | 32 | 27 | 122 | 400 | 91 | 50 | 51 | 3 | 52 | 17 | 110 | 17 | 96 | 38 | 395 | 54 | 5 | 72 | 89 | 0 | 17 | 9 | 38 | 18 | 0 | 0 | 0 |  | 892 | 0 | 250 | 0 | 0 | 218 | 0 | 0 | 0 | 0 | 0 | 83 | 19 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 8 | 0 | 22 | 0 | 10 | 80 | 0 | 249 | 0 | 0 | 193 | 0 | 0 | 204 | 0 | 50 | 199 | 0 | 417 | 37 | 50 | 50 | 0 | 54 | 0 | 4 | 75 | 820 | 218 | 0 | 0 | 1 | 24 | 0 | 0 | 0 | 107 | 23 |  | 7417 | 4389 | 11806 | 4165 | 892 | 1854 | 671 | 2087 | 1256 | 150 | 422 | 290 | 134 | 89 | 122 | 96.18
13:00 | 0 | 0 | 229 | 0 | 240 | 72 | 0 | 378 | 175 |  | 0 | 215 | 122 | 49 | 0 | 55 | 255 | 0 | 0 | 62 | 50 | 17 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 25 | 25 | 33 | 13 | 16 | 0 | 82 | 70 | 105 | 0 | 17 | 0 | 0 | 0 | 0 |  | 12 | 25 | 13 | 33 | 7 | 26 | 15 | 13 | 0 | 0 | 0 | 340 | 325 | 207 | 16 | 48 | 41 | 50 | 0 | 43 | 0 | 19 | 8 | 19 | 10 | 14 | 20 | 134 | 65 | 0 | 0 | 0 | 43 | 41 | 31 | 28 | 0 | 0 | 60 | 81 | 0 | 0 | 0 | 25 | 0 | 280 | 0 | 11 | 152 | 190 | 123 | 80 | 92 | 80 | 149 | 0 | 32 | 35 | 125 | 402 | 101 | 50 | 59 | 2 | 51 | 17 | 110 | 17 | 94 | 38 | 396 | 51 | 4 | 72 | 89 | 0 | 0 | 0 | 38 | 18 | 0 | 0 | 0 |  | 892 | 0 | 245 | 0 | 0 | 219 | 0 | 0 | 0 | 0 | 0 | 83 | 11 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 8 | 0 | 22 | 0 | 10 | 80 | 0 | 250 | 0 | 0 | 193 | 0 | 0 | 215 | 0 | 10 | 193 | 0 | 418 | 37 | 10 | 50 | 0 | 57 | 0 | 5 | 75 | 820 | 220 | 0 | 0 | 3 | 21 | 0 | 0 | 0 | 100 | 28 |  | 7181 | 4307 | 11488 | 4103 | 892 | 1822 | 455 | 2093 | 1250 | 152 | 434 | 305 | 134 | 63 | 0 | 96.18
14:00 | 0 | 0 | 230 | 0 | 240 | 77 | 0 | 367 | 168 |  | 0 | 210 | 120 | 49 | 0 | 55 | 250 | 0 | 0 | 62 | 50 | 17 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 0 | 25 | 0 | 33 | 12 | 16 | 0 | 81 | 70 | 105 | 0 | 17 | 0 | 0 | 0 | 0 |  | 12 | 24 | 13 | 33 | 11 | 26 | 15 | 10 | 0 | 0 | 0 | 335 | 320 | 205 | 16 | 50 | 41 | 56 | 0 | 43 | 0 | 15 | 8 | 19 | 10 | 10 | 20 | 144 | 66 | 0 | 0 | 0 | 43 | 41 | 31 | 30 | 0 | 0 | 61 | 81 | 0 | 0 | 0 | 24 | 10 | 290 | 22 | 11 | 100 | 190 | 102 | 40 | 92 | 30 | 149 | 0 | 32 | 35 | 127 | 402 | 101 | 50 | 69 | 3 | 52 | 17 | 110 | 17 | 94 | 38 | 398 | 51 | 7 | 72 | 89 | 0 | 11 | 3 | 38 | 18 | 0 | 0 | 0 |  | 892 | 0 | 235 | 0 | 0 | 215 | 0 | 0 | 0 | 0 | 0 | 83 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 8 | 0 | 21 | 0 | 10 | 80 | 0 | 249 | 0 | 0 | 193 | 0 | 0 | 205 | 0 | 10 | 182 | 0 | 419 | 37 | 10 | 50 | 0 | 56 | 0 | 5 | 75 | 790 | 220 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 100 | 15 |  | 7024 | 4238 | 11262 | 4034 | 892 | 1843 | 292 | 2120 | 1219 | 151 | 420 | 290 | 144 | 62 | 0 | 96.18
15:00 | 0 | 0 | 230 | 0 | 240 | 77 | 0 | 362 | 163 |  | 0 | 210 | 115 | 44 | 0 | 55 | 245 | 0 | 0 | 62 | 40 | 17 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 0 | 25 | 0 | 33 | 12 | 16 | 0 | 76 | 70 | 105 | 0 | 17 | 0 | 0 | 0 | 0 |  | 12 | 24 | 13 | 33 | 11 | 26 | 15 | 7 | 0 | 0 | 0 | 300 | 300 | 196 | 16 | 50 | 37 | 55 | 0 | 51 | 0 | 23 | 8 | 19 | 10 | 8 | 20 | 144 | 44 | 0 | 0 | 0 | 43 | 41 | 31 | 30 | 0 | 0 | 61 | 81 | 0 | 0 | 0 | 23 | 10 | 300 | 22 | 11 | 190 | 195 | 180 | 80 | 93 | 80 | 149 | 0 | 32 | 35 | 128 | 401 | 105 | 49 | 69 | 3 | 52 | 17 | 110 | 17 | 95 | 38 | 391 | 55 | 8 | 72 | 89 | 0 | 12 | 1 | 37 | 18 | 0 | 0 | 0 |  | 892 | 0 | 235 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 82 | 14 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 8 | 0 | 21 | 0 | 10 | 80 | 0 | 249 | 0 | 0 | 193 | 0 | 0 | 190 | 0 | 10 | 180 | 0 | 422 | 40 | 12 | 50 | 0 | 56 | 0 | 4 | 75 | 780 | 220 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 100 | 21 |  | 7159 | 4177 | 11336 | 3921 | 892 | 1846 | 552 | 2105 | 1209 | 146 | 350 | 283 | 144 | 78 | 0 | 96.18
16:00 | 0 | 0 | 230 | 0 | 240 | 77 | 0 | 361 | 157 |  | 0 | 200 | 115 | 41 | 0 | 55 | 236 | 0 | 0 | 62 | 40 | 17 | 0 | 0 | 0 | 0 | 17 | 16 | 17 | 0 | 25 | 24 | 33 | 12 | 16 | 0 | 74 | 70 | 105 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 24 | 13 | 33 | 11 | 27 | 15 | 10 | 0 | 0 | 0 | 300 | 300 | 192 | 16 | 31 | 38 | 55 | 0 | 51 | 0 | 22 | 10 | 19 | 10 | 8 | 20 | 82 | 44 | 0 | 0 | 0 | 43 | 41 | 31 | 30 | 0 | 0 | 61 | 81 | 0 | 0 | 0 | 24 | 10 | 300 | 24 | 8 | 170 | 195 | 170 | 80 | 102 | 50 | 149 | 11 | 32 | 35 | 128 | 403 | 89 | 66 | 69 | 1 | 52 | 25 | 110 | 17 | 102 | 38 | 391 | 55 | 4 | 72 | 89 | 0 | 17 | 0 | 37 | 18 | 0 | 0 | 0 |  | 892 | 0 | 230 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 82 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 8 | 0 | 21 | 0 | 10 | 80 | 0 | 249 | 0 | 0 | 193 | 0 | 0 | 195 | 0 | 0 | 160 | 0 | 394 | 56 | 0 | 50 | 0 | 56 | 0 | 3 | 35 | 780 | 218 | 0 | 0 | 0 | 32 | 34 | 0 | 0 | 100 | 8 |  | 7038 | 4055 | 11093 | 3889 | 892 | 1807 | 470 | 2134 | 1209 | 144 | 315 | 287 | 82 | 59 | 0 | 96.19
17:00 | 0 | 0 | 240 | 0 | 240 | 75 | 0 | 361 | 166 |  | 0 | 200 | 115 | 41 | 0 | 55 | 242 | 0 | 0 | 62 | 40 | 17 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 0 | 25 | 24 | 33 | 12 | 16 | 0 | 74 | 70 | 105 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 24 | 13 | 33 | 11 | 30 | 15 | 17 | 0 | 0 | 0 | 300 | 300 | 180 | 16 | 0 | 43 | 56 | 0 | 51 | 0 | 29 | 8 | 19 | 10 | 16 | 15 | 78 | 44 | 0 | 0 | 0 | 43 | 41 | 31 | 32 | 0 | 0 | 61 | 81 | 0 | 0 | 0 | 25 | 10 | 300 | 24 | 8 | 120 | 195 | 80 | 90 | 101 | 50 | 149 | 1 | 32 | 92 | 132 | 402 | 98 | 84 | 95 | 0 | 52 | 36 | 110 | 17 | 104 | 38 | 401 | 58 | 3 | 80 | 95 | 0 | 17 | 0 | 49 | 18 | 0 | 0 | 0 |  | 892 | 0 | 230 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 84 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 8 | 0 | 21 | 0 | 10 | 80 | 0 | 249 | 0 | 0 | 160 | 0 | 0 | 188 | 0 | 0 | 160 | 0 | 360 | 56 | 0 | 35 | 0 | 80 | 0 | 2 | 35 | 780 | 222 | 0 | 0 | 0 | 10 | 34 | 0 | 0 | 100 | 5 |  | 7100 | 3973 | 11073 | 3848 | 892 | 1798 | 340 | 2336 | 1209 | 144 | 308 | 287 | 78 | 21 | 0 | 96.19
18:00 | 0 | 0 | 225 | 0 | 240 | 71 | 0 | 361 | 172 |  | 0 | 200 | 115 | 48 | 0 | 55 | 244 | 0 | 0 | 72 | 40 | 67 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 0 | 25 | 24 | 33 | 12 | 21 | 0 | 74 | 70 | 105 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 24 | 13 | 78 | 24 | 38 | 15 | 7 | 0 | 0 | 0 | 280 | 270 | 197 | 8 | 0 | 44 | 56 | 0 | 51 | 0 | 33 | 8 | 19 | 10 | 16 | 21 | 82 | 42 | 0 | 0 | 0 | 43 | 41 | 31 | 32 | 0 | 0 | 60 | 81 | 0 | 0 | 0 | 25 | 10 | 290 | 24 | 8 | 0 | 200 | 50 | 25 | 91 | 50 | 149 | 0 | 90 | 150 | 142 | 404 | 107 | 84 | 105 | 0 | 101 | 36 | 110 | 17 | 104 | 38 | 386 | 71 | 0 | 162 | 85 | 0 | 17 | 0 | 96 | 18 | 0 | 0 | 0 |  | 892 | 0 | 235 | 0 | 0 | 120 | 0 | 0 | 12 | 13 | 0 | 82 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 24 | 8 | 0 | 22 | 0 | 10 | 80 | 0 | 249 | 0 | 0 | 169 | 0 | 0 | 195 | 0 | 0 | 160 | 0 | 415 | 56 | 0 | 35 | 0 | 92 | 0 | 1 | 35 | 780 | 218 | 0 | 0 | 0 | 1 | 34 | 0 | 0 | 100 | 1 |  | 7304 | 4084 | 11388 | 3805 | 892 | 1824 | 125 | 2794 | 1209 | 144 | 315 | 390 | 82 | 3 | 0 | 96.19
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 230 | 0 | 240 | 74 | 0 | 365 | 171 |  | 0 | 200 | 115 | 72 | 0 | 55 | 238 | 0 | 0 | 80 | 92 | 105 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 19 | 33 | 12 | 33 | 0 | 74 | 70 | 105 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 24 | 47 | 78 | 79 | 39 | 15 | 20 | 0 | 0 | 0 | 280 | 280 | 204 | 8 | 0 | 45 | 56 | 0 | 51 | 0 | 30 | 14 | 19 | 10 | 25 | 21 | 94 | 72 | 0 | 0 | 0 | 43 | 41 | 47 | 37 | 0 | 0 | 62 | 81 | 0 | 0 | 0 | 25 | 10 | 300 | 24 | 8 | 191 | 255 | 226 | 90 | 95 | 90 | 149 | 0 | 90 | 150 | 143 | 401 | 108 | 85 | 105 | 0 | 155 | 36 | 110 | 17 | 105 | 90 | 401 | 74 | 0 | 162 | 89 | 0 | 17 | 0 | 96 | 18 | 0 | 0 | 0 |  | 891 | 0 | 230 | 0 | 0 | 227 | 0 | 0 | 37 | 50 | 0 | 84 | 28 | 26 | 0 | 0 | 0 | 32 | 0 | 56 | 0 | 0 | 24 | 8 | 33 | 22 | 0 | 10 | 80 | 0 | 250 | 0 | 0 | 193 | 0 | 0 | 207 | 0 | 91 | 172 | 0 | 430 | 60 | 77 | 71 | 15 | 92 | 0 | 0 | 95 | 930 | 222 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 0 |  | 8368 | 4833 | 13201 | 3929 | 891 | 1897 | 765 | 3349 | 1260 | 144 | 434 | 645 | 94 | 0 | 117.9616 | 96.2
19:30 | 0 | 0 | 230 | 0 | 240 | 77 | 0 | 351 | 166 |  | 0 | 200 | 115 | 75 | 0 | 55 | 224 | 0 | 0 | 80 | 92 | 116 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 24 | 33 | 12 | 16 | 0 | 74 | 70 | 105 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 24 | 47 | 78 | 94 | 38 | 15 | 23 | 0 | 0 | 0 | 280 | 280 | 209 | 8 | 0 | 45 | 56 | 0 | 51 | 0 | 30 | 34 | 19 | 10 | 29 | 21 | 94 | 93 | 0 | 0 | 0 | 43 | 41 | 47 | 37 | 0 | 0 | 62 | 81 | 0 | 0 | 0 | 25 | 10 | 260 | 24 | 8 | 150 | 255 | 226 | 90 | 95 | 90 | 149 | 0 | 90 | 150 | 142 | 401 | 107 | 85 | 105 | 0 | 160 | 36 | 110 | 17 | 106 | 90 | 401 | 74 | 0 | 162 | 107 | 0 | 17 | 0 | 96 | 18 | 0 | 0 | 0 |  | 891 | 0 | 230 | 0 | 0 | 227 | 0 | 0 | 45 | 65 | 0 | 86 | 28 | 32 | 0 | 0 | 0 | 32 | 0 | 81 | 0 | 0 | 32 | 8 | 33 | 22 | 0 | 10 | 82 | 0 | 250 | 0 | 0 | 192 | 0 | 0 | 217 | 0 | 60 | 178 | 0 | 428 | 75 | 80 | 94 | 15 | 91 | 0 | 0 | 95 | 1080 | 220 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 0 |  | 8348 | 5069 | 13417 | 3943 | 891 | 1854 | 696 | 3434 | 1412 | 144 | 444 | 722 | 94 | 0 | 96.7654 | 0
20:00 | 0 | 0 | 230 | 0 | 240 | 81 | 0 | 356 | 160 |  | 0 | 200 | 115 | 74 | 0 | 55 | 224 | 0 | 0 | 80 | 92 | 116 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 24 | 33 | 12 | 18 | 0 | 74 | 70 | 105 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 17 | 47 | 78 | 94 | 39 | 15 | 28 | 0 | 0 | 0 | 280 | 280 | 210 | 8 | 0 | 45 | 56 | 0 | 51 | 0 | 30 | 33 | 19 | 10 | 32 | 20 | 94 | 107 | 0 | 0 | 0 | 43 | 41 | 47 | 40 | 0 | 0 | 61 | 81 | 0 | 0 | 0 | 25 | 10 | 270 | 24 | 0 | 150 | 278 | 180 | 90 | 96 | 90 | 149 | 0 | 90 | 150 | 142 | 400 | 108 | 85 | 105 | 0 | 161 | 36 | 110 | 17 | 105 | 90 | 401 | 73 | 0 | 162 | 107 | 0 | 17 | 0 | 96 | 18 | 0 | 0 | 0 |  | 893 | 0 | 230 | 0 | 0 | 227 | 0 | 0 | 35 | 61 | 0 | 85 | 30 | 32 | 0 | 0 | 0 | 32 | 0 | 81 | 0 | 0 | 32 | 8 | 33 | 22 | 0 | 10 | 82 | 0 | 250 | 0 | 0 | 192 | 0 | 0 | 217 | 0 | 10 | 178 | 0 | 427 | 75 | 10 | 94 | 15 | 91 | 0 | 0 | 95 | 1090 | 220 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 0 |  | 8348 | 4947 | 13295 | 3954 | 893 | 1871 | 530 | 3459 | 1422 | 144 | 444 | 701 | 94 | 0 | 67.275 | 96.2
21:00 | 0 | 0 | 230 | 0 | 260 | 81 | 0 | 338 | 138 |  | 0 | 200 | 90 | 74 | 0 | 55 | 213 | 0 | 0 | 80 | 92 | 116 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 24 | 33 | 13 | 32 | 0 | 78 | 70 | 105 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 24 | 47 | 78 | 94 | 38 | 15 | 32 | 0 | 0 | 0 | 280 | 280 | 207 | 8 | 0 | 45 | 55 | 0 | 51 | 0 | 23 | 34 | 19 | 10 | 33 | 21 | 96 | 106 | 0 | 0 | 0 | 43 | 41 | 47 | 48 | 0 | 0 | 59 | 81 | 0 | 0 | 0 | 25 | 10 | 305 | 24 | 8 | 120 | 278 | 150 | 90 | 95 | 90 | 149 | 0 | 90 | 150 | 145 | 401 | 108 | 85 | 105 | 0 | 161 | 36 | 110 | 17 | 105 | 90 | 397 | 72 | 0 | 162 | 107 | 0 | 17 | 0 | 96 | 18 | 0 | 0 | 0 |  | 893 | 0 | 230 | 0 | 0 | 225 | 0 | 0 | 27 | 59 | 0 | 84 | 31 | 32 | 0 | 0 | 0 | 32 | 0 | 81 | 0 | 0 | 32 | 8 | 33 | 22 | 0 | 10 | 81 | 0 | 250 | 0 | 0 | 193 | 0 | 0 | 218 | 0 | 10 | 179 | 0 | 421 | 75 | 10 | 94 | 0 | 92 | 0 | 0 | 95 | 1100 | 220 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 0 |  | 8278 | 4927 | 13205 | 3945 | 893 | 1865 | 470 | 3440 | 1431 | 148 | 443 | 692 | 96 | 0 | 0 | 96.2
22:00 | 0 | 0 | 230 | 0 | 260 | 85 | 0 | 317 | 139 |  | 0 | 200 | 95 | 73 | 0 | 55 | 150 | 0 | 0 | 80 | 92 | 116 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 19 | 25 | 28 | 33 | 8 | 32 | 0 | 78 | 70 | 105 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 24 | 47 | 78 | 94 | 39 | 13 | 35 | 0 | 0 | 0 | 280 | 280 | 208 | 8 | 0 | 45 | 56 | 0 | 51 | 0 | 23 | 34 | 19 | 10 | 33 | 21 | 100 | 118 | 0 | 0 | 0 | 43 | 41 | 47 | 49 | 0 | 0 | 58 | 81 | 0 | 0 | 0 | 25 | 10 | 305 | 24 | 8 | 150 | 278 | 185 | 90 | 96 | 90 | 149 | 0 | 90 | 150 | 145 | 401 | 108 | 84 | 105 | 0 | 161 | 36 | 110 | 17 | 105 | 90 | 401 | 66 | 0 | 162 | 107 | 0 | 17 | 0 | 96 | 18 | 0 | 0 | 0 |  | 892 | 0 | 230 | 0 | 0 | 226 | 0 | 0 | 17 | 59 | 0 | 85 | 32 | 32 | 0 | 0 | 0 | 32 | 0 | 81 | 0 | 0 | 32 | 8 | 27 | 22 | 0 | 10 | 82 | 0 | 249 | 0 | 0 | 193 | 0 | 0 | 218 | 0 | 10 | 182 | 0 | 425 | 75 | 10 | 94 | 0 | 92 | 0 | 0 | 95 | 1100 | 226 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 0 |  | 8265 | 4926 | 13191 | 3878 | 892 | 1891 | 535 | 3414 | 1431 | 148 | 444 | 676 | 100 | 0 | 0 | 96.2
23:00 | 0 | 0 | 230 | 0 | 260 | 88 | 0 | 336 | 151 |  | 0 | 200 | 108 | 74 | 0 | 55 | 150 | 0 | 0 | 80 | 92 | 50 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 19 | 25 | 28 | 33 | 16 | 32 | 0 | 77 | 70 | 105 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 25 | 47 | 78 | 46 | 39 | 13 | 35 | 0 | 0 | 0 | 280 | 280 | 210 | 8 | 0 | 45 | 56 | 0 | 51 | 0 | 22 | 8 | 19 | 10 | 33 | 21 | 104 | 141 | 0 | 0 | 0 | 43 | 41 | 47 | 49 | 0 | 0 | 64 | 81 | 0 | 0 | 0 | 25 | 10 | 285 | 24 | 8 | 150 | 278 | 180 | 85 | 95 | 90 | 134 | 0 | 90 | 150 | 145 | 402 | 108 | 70 | 105 | 0 | 161 | 36 | 110 | 17 | 104 | 90 | 401 | 72 | 0 | 162 | 107 | 0 | 17 | 0 | 96 | 17 | 0 | 0 | 0 |  | 891 | 0 | 230 | 0 | 0 | 226 | 0 | 0 | 17 | 59 | 0 | 86 | 32 | 32 | 0 | 0 | 0 | 32 | 0 | 45 | 0 | 0 | 24 | 8 | 27 | 22 | 0 | 10 | 81 | 0 | 249 | 0 | 0 | 194 | 0 | 0 | 219 | 0 | 25 | 183 | 0 | 427 | 75 | 13 | 94 | 0 | 92 | 0 | 0 | 95 | 1090 | 227 | 0 | 0 | 0 | 0 | 91 | 0 | 0 | 0 | 0 |  | 8160 | 4896 | 13056 | 3940 | 891 | 1902 | 543 | 3316 | 1420 | 147 | 445 | 567 | 104 | 0 | 0 | 96.21
24:00 | 0 | 0 | 230 | 0 | 260 | 88 | 0 | 343 | 154 |  | 0 | 200 | 120 | 43 | 0 | 55 | 150 | 0 | 0 | 46 | 40 | 50 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 25 | 28 | 33 | 16 | 16 | 0 | 77 | 70 | 105 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 24 | 47 | 33 | 12 | 25 | 13 | 34 | 0 | 0 | 0 | 280 | 280 | 208 | 8 | 0 | 45 | 56 | 0 | 51 | 0 | 22 | 8 | 19 | 10 | 33 | 21 | 102 | 141 | 0 | 0 | 0 | 43 | 41 | 47 | 49 | 0 | 0 | 64 | 81 | 0 | 0 | 0 | 25 | 10 | 290 | 24 | 8 | 190 | 278 | 225 | 80 | 95 | 80 | 145 | 0 | 33 | 68 | 143 | 401 | 108 | 50 | 78 | 0 | 161 | 36 | 78 | 17 | 96 | 40 | 401 | 72 | 0 | 17 | 107 | 0 | 17 | 0 | 49 | 18 | 0 | 0 | 0 |  | 891 | 0 | 230 | 0 | 0 | 225 | 0 | 0 | 11 | 47 | 0 | 86 | 32 | 32 | 0 | 0 | 0 | 32 | 0 | 22 | 0 | 0 | 24 | 8 | 27 | 22 | 0 | 10 | 81 | 0 | 250 | 0 | 0 | 194 | 0 | 0 | 220 | 0 | 89 | 187 | 0 | 424 | 37 | 131 | 50 | 0 | 56 | 0 | 0 | 95 | 980 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 7529 | 4718 | 12247 | 3948 | 891 | 1916 | 795 | 2386 | 1311 | 147 | 445 | 526 | 102 | 0 | 0 | 96.21
KWH | 0 | 0 | 5528000 | 0 | 6079045 | 1947681 | 0 | 8992770 | 4104000 |  | 0 | 4438400 | 2811520 | 1298880 | 0 | 1339932 | 5873157 | 0 | 0 | 1578355 | 1340640 | 1059840 | 0 | 0 | 0 | 0 | 646920 | 873206 | 859749 | 341064 | 600000 | 481140 | 816600 | 306000 | 475680 | 0 | 1823013 | 1688000 | 2500000 | 0 | 549565 | 0 | 0 | 0 | 0 |  | 297360 | 578208 | 517867 | 1044840 | 643200 | 711360 | 353856 | 575040 | 0 | 0 | 0 | 7450800 | 7006000 | 4967000 | 284363 | 790950 | 1005624 | 1279680 | 0 | 1182422 | 0 | 487296 | 294744 | 461952 | 236160 | 584000 | 496280 | 2793600 | 2219520 | 0 | 0 | 6250 | 1022000 | 964048 | 840600 | 783288 | 0 | 0 | 1480800 | 1936320 | 0 | 0 | 0 | 461660 | 224820 | 7224000 | 417528 | 229100 | 2906880 | 5178764 | 3495906 | 1683223 | 2114400 | 1640039 | 3484656 | 33615 | 1094400 | 1483200 | 3223345 | 9640000 | 2395200 | 1413600 | 1830792 | 25680 | 1909418 | 782848 | 2659625 | 417240 | 2380560 | 1169280 | 9542900 | 1362240 | 102830 | 1774080 | 2399945 | 0 | 420480 | 93197 | 1286400 | 419400 | 0 | 0 | 0 |  | 21555636 | 0 | 5160384 | 0 | 0 | 4915200 | 0 | 0 | 198240 | 317312 | 0 | 2031872 | 569850 | 482496 | 0 | 0 | 0 | 198464 | 0 | 358448 | 0 | 0 | 296990 | 193714 | 251251 | 504240 | 0 | 223236 | 1947054 | 0 | 6062800 | 0 | 0 | 4827491 | 0 | 0 | 4663855 | 0 | 826560 | 4711609 | 0 | 10038036 | 1137120 | 1073682 | 1519488 | 28512 | 1525785 | 0 | 39408 | 1642944 | 24524220 | 5398309 | 0 | 0 | 11040 | 374400 | 550464 | 0 | 0 | 552270 | 187220 |  | 178569836 | 108899600 | 287469436 | 97340886 | 21555636 | 44604229 | 11626290 | 58234827 | 33086344 | 3511013 | 9579055 | 4263916 | 2793600 | 873640 | 0
Fuel Cost | 0 | 0 | 8070880 | 0 | 6808530.4 | 2590415.73 | 0 | 9442408.5 | 4432320 |  | 0 | 4837856 | 3120787.2 | 14521478.4 | 0 | 17754099 | 6577935.84 | 0 | 0 | 23075550.1 | 18862804.8 | 17180006.4 | 0 | 0 | 0 | 0 | 8228822.4 | 11788281 | 11529234.09 | 255798 | 450000 | 0 | 0 | 0 | 8091316.8 | 0 | 492213.51 | 455760 | 4725000 | 0 | 8985387.75 | 0 | 0 | 0 | 0 |  | 3880548 | 9644509.44 | 8814096.34 | 14115788.4 | 8155776 | 8230435.2 | 449397.12 | 1914883.2 | 0 | 0 | 0 | 8270388 | 7636540 | 5761720 | 366828.27 | 964959 | 1136355.12 | 1906723.2 | 0 | 1974644.74 | 0 | 8415601.92 | 3964306.8 | 632874.24 | 177120 | 1022000 | 372210 | 20058048 | 2419276.8 | 0 | 0 | 99625 | 1400140 | 1272543.36 | 1462644 | 1355088.24 | 0 | 0 | 2872752 | 4414809.6 | 0 | 0 | 0 | 687873.4 | 445143.6 | 7224000 | 313146 | 174116 | 60928204.8 | 70690128.6 | 73274189.76 | 34792219.41 | 28502112 | 33899606.13 | 48262485.6 | 392959.35 | 11294208 | 20260512 | 42773788.15 | 8868800 | 29125632 | 20440656 | 23159518.8 | 0 | 22416567.32 | 8525214.72 | 28271813.75 | 5661946.8 | 30685418.4 | 13774118.4 | 8779468 | 17641008 | 1485893.5 | 22513075.2 | 27311374.1 | 0 | 5491468.8 | 1113704.15 | 19257408 | 5523498 | 0 | 0 | 0 |  | 64666908 | 0 | 5779630.08 | 0 | 0 | 81100800 | 0 | 0 | 3570302.4 | 5711616 | 0 | 2275696.64 | 1105509 | 5259206.4 | 0 | 0 | 0 | 3328241.28 | 0 | 5606126.72 | 0 | 0 | 5022100.9 | 2640321.82 | 4238604.37 | 1043776.8 | 0 | 168989.652 | 11312383.74 | 0 | 32072212 | 0 | 0 | 5599889.56 | 0 | 0 | 81430908.3 | 0 | 17341228.8 | 5465466.44 | 0 | 9937655.64 | 15282892.8 | 22515111.54 | 17975543.04 | 411998.4 | 19377469.5 | 0 | 435458.4 | 19945340.16 | 220963222.2 | 5506275.18 | 0 | 0 | 124862.4 | 4391712 | 8438613.12 | 0 | 0 | 0 | 0 |  | 1059400794.65 | 690046073.282 | 1749446867.932 | 108144030.752 | 64666908 | 54327233.8 | 242750560.44 | 752097166.62 | 264347817.94 | 947973.51 | 162531708.3 | 71531205.77 | 20058048 | 8044214.8 | 0
Yesterday Day Peak | 0 | 0 | 230 | 0 | 260 | 72 | 0 | 398 | 186 |  | 0 | 215 | 122 | 51 | 0 | 55 | 264 | 0 | 0 | 62 | 50 | 17 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 25 | 21 | 33 | 8 | 16 | 0 | 80 | 70 | 105 | 0 | 17 | 0 | 0 | 0 | 0 |  | 12 | 25 | 13 | 33 | 7 | 26 | 15 | 9 | 0 | 0 | 0 | 345 | 325 | 205 | 16 | 50 | 39 | 48 | 0 | 43 | 0 | 15 | 8 | 19 | 10 | 14 | 20 | 134 | 65 | 0 | 0 | 0 | 43 | 41 | 31 | 28 | 0 | 0 | 60 | 78 | 0 | 0 | 0 | 20 | 10 | 300 | 10 | 11 | 185 | 192 | 225 | 80 | 91 | 81 | 149 | 20 | 32 | 27 | 122 | 400 | 91 | 50 | 51 | 3 | 52 | 17 | 110 | 17 | 96 | 38 | 395 | 54 | 5 | 72 | 89 | 0 | 17 | 9 | 38 | 18 | 0 | 0 | 0 |  | 892 | 0 | 250 | 0 | 0 | 218 | 0 | 0 | 0 | 0 | 0 | 83 | 19 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 8 | 0 | 22 | 0 | 10 | 80 | 0 | 249 | 0 | 0 | 193 | 0 | 0 | 204 | 0 | 50 | 199 | 0 | 417 | 37 | 50 | 50 | 0 | 54 | 0 | 4 | 75 | 820 | 218 | 0 | 0 | 1 | 24 | 0 | 0 | 0 | 107 | 23 |  | 11806 | DayPeak
Yesterday Evening Peak | 0 | 0 | 230 | 0 | 240 | 77 | 0 | 351 | 166 | 0 | 0 | 200 | 115 | 75 | 0 | 55 | 224 | 0 | 0 | 80 | 92 | 116 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 24 | 33 | 12 | 16 | 0 | 74 | 70 | 105 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 12 | 24 | 47 | 78 | 94 | 38 | 15 | 23 | 0 | 0 | 0 | 280 | 280 | 209 | 8 | 0 | 45 | 56 | 0 | 51 | 0 | 30 | 34 | 19 | 10 | 29 | 21 | 94 | 93 | 0 | 0 | 0 | 43 | 41 | 47 | 37 | 0 | 0 | 62 | 81 | 0 | 0 | 0 | 25 | 10 | 260 | 24 | 8 | 150 | 255 | 226 | 90 | 95 | 90 | 149 | 0 | 90 | 150 | 142 | 401 | 107 | 85 | 105 | 0 | 160 | 36 | 110 | 17 | 106 | 90 | 401 | 74 | 0 | 162 | 107 | 0 | 17 | 0 | 96 | 18 | 0 | 0 | 0 |  | 891 | 0 | 230 | 0 | 0 | 227 | 0 | 0 | 45 | 65 | 0 | 86 | 28 | 32 | 0 | 0 | 0 | 32 | 0 | 81 | 0 | 0 | 32 | 8 | 33 | 22 | 0 | 10 | 82 | 0 | 250 | 0 | 0 | 192 | 0 | 0 | 217 | 0 | 60 | 178 | 0 | 428 | 75 | 80 | 94 | 15 | 91 | 0 | 0 | 95 | 1080 | 220 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 0 |  | 13417 | EvPeak
Forecast for Evening | 0 | 0 | 230 | 0 | 260 | 90 | 0 | 360 | 170 | 0 | 0 | 200 | 120 | 75 | 0 | 55 | 300 | 0 | 0 | 80 | 92 | 115 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 26 | 33 | 21 | 32 | 0 | 80 | 70 | 105 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 12 | 26 | 47 | 80 | 94 | 38 | 15 | 20 | 0 | 0 | 0 | 280 | 280 | 210 | 8 | 0 | 45 | 55 | 0 | 51 | 0 | 35 | 34 | 19 | 10 | 33 | 21 | 166 | 100 | 0 | 0 | 0 | 43 | 41 | 47 | 44 | 0 | 0 | 64 | 81 | 0 | 0 | 0 | 25 | 10 | 300 | 24 | 11 | 190 | 285 | 220 | 90 | 95 | 90 | 149 | 0 | 90 | 200 | 145 | 400 | 108 | 85 | 105 | 0 | 160 | 36 | 110 | 52 | 105 | 90 | 400 | 93 | 0 | 162 | 107 | 0 | 17 |  | 96 | 18 |  |  |  |  | 908 | 0 | 250 | 0 | 0 | 225 | 0 | 0 | 50 | 60 | 0 | 85 | 30 | 32 | 0 | 0 | 0 | 32 | 25 | 80 | 0 | 0 | 32 | 8 | 33 | 22 | 0 | 10 | 80 | 0 | 250 | 0 | 0 | 194 | 0 | 0 | 220 | 0 | 94 | 190 | 0 | 414 | 75 | 165 | 94 | 15 | 92 | 0 | 0 | 95 | 1110 | 220 |  | 17 |  |  | 90
Forecast for Day | 0 | 0 | 230 | 0 | 260 | 90 | 0 | 400 | 200 | 0 | 0 | 200 | 120 | 50 | 0 | 55 | 280 | 0 | 0 | 62 | 50 | 17 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 25 | 26 | 33 | 21 | 16 | 0 | 80 | 70 | 105 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 12 | 26 | 17 | 33 | 11 | 25 | 15 | 10 | 0 | 0 | 0 | 330 | 330 | 205 | 8 | 0 | 43 | 55 | 0 | 51 | 0 | 25 | 8 | 19 | 10 | 33 | 21 | 143 | 68 | 0 | 0 | 1.6 | 43 | 41 | 31 | 20 | 0 | 0 | 60 | 81 | 0 | 0 | 0 | 25 | 10 | 300 | 24 | 11 | 100 | 260 | 220 | 90 | 90 | 80 | 149 | 20 | 33 | 17 | 130 | 400 | 90 | 50 | 55 | 5 | 160 | 35 | 110 | 0 | 105 | 38 | 400 | 55 | 50 | 72 | 107 | 0 | 17 | 30 | 40 | 18 |  |  |  |  | 908 | 0 | 250 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 85 | 20 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 8 | 0 | 22 | 0 | 10 | 80 | 0 | 250 | 0 | 0 | 194 | 0 | 0 | 220 | 0 | 20 | 195 | 0 | 414 | 35 | 60 | 50 | 15 | 55 | 0 | 8 | 60 | 1110 | 220 |  | 0 | 6 | 100 | 0 |  |  |  | 12
Generation at 08:00(Today) | 0 | 0 | 235 | 0 | 260 | 84 | 0 | 363 | 174 | 0 | 0 | 215 | 122 | 41 | 0 | 55 | 170 | 0 | 0 | 40 | 40 | 17 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 16 | 25 | 28 | 33 | 15 | 16 | 0 | 83 | 70 | 105 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 12 | 24 | 13 | 33 | 12 | 24 | 13 | 13 | 0 | 0 | 0 | 315 | 310 | 209 | 8 | 0 | 45 | 56 | 0 | 51 | 0 | 21 | 8 | 19 | 10 | 27 | 21 | 114 | 68 | 0 | 0 | 0 | 43 | 41 | 5 | 6 | 0 | 0 | 62 | 81 | 0 | 0 | 0 | 23 | 10 | 310 | 21 | 8 | 0 | 165 | 10 | 0 | 113 | 25 | 117 | 12 | 32 | 17 | 117 | 403 | 0 | 46 | 55 | 2 | 161 | 36 | 55 | 0 | 95 | 38 | 394 | 45 | 5 | 17 | 107 | 0 | 17 | 7 | 35 | 17 | 0 | 0 | 0 | 0 | 891 | 0 | 240 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 85 | 19 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 8 | 81 | 0 | 250 | 0 | 0 | 198 | 0 | 0 | 194 | 0 | 0 | 202 | 0 | 416 | 37 | 0 | 50 | 0 | 56 | 0 | 0 | 55 | 770 | 224 | 0 | 0 | 1 | 24 | 0 | 0 | 0 | 101 | 0 | 0 |  |  |  |  | 83704088 |  | 0
83704088
| Minimum Generation |  | 10580 | 8:00
| Highest Generation |  | 13417 | 19:30
| Day Peak Generation |  | 11806 | 12:00
| Evening Peak Generation |  | 13417 | 19:30
| HVDC Max Flow |  | 893 | 7:00
| HVDC EvPeak Flow |  | 891 | 19:30
| Load factor L.F |  | 89.27% | [161 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2022-09-06
Till now the maximum generation is : - |  |  | 14782 | 21:00 | Hrs on | 2022-04-16
The Summary of Yesterday's |  | 2022-09-05 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 11806 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 10615 | MW
Evening Peak Generation : |  | 13417 | MW Hour : | 19:30 | Available Max Generation : |  | 14114 | MW
E.P. Demand (at gen end) : |  | 13522 | MW Hour : | 19:30 | Max Demand (Evening) : |  | 13400 | MW
Maximum Generation : |  | 13417 | MW Hour : | 19:30 | Reserve(Generation end) |  | 714 | MW
Total Gen. (MKWH) : |  | 287.4694 | System Load Factor : | 89.27% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | 1115 | MW at | 21:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2022-09-06
Actual : | 96.23 | Ft.(MSL) , | Rule curve : | 100.15 | Ft.( MSL )
Gas Consumed : | Total = | 1051.99 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 162471264.552
: |  | Coal : | 264347817.94 | Oil : | 1228910641.13 | Total : | 1655729723.622
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4291.314 |  |  | 0 | -8.719%
Chittagong Area | 0 | 0:00 | 1215.1519 |  |  | 0 | -6.411%
Khulna Area | 0 | 0:00 | 1604.1487 |  |  | 0 | -5.99%
Rajshahi Area | 0 | 0:00 | 1423.8518 |  |  | 0 | -5.395%
Cumilla Area | 0 | 0:00 | 1211.4472 |  |  | 0 | -5.743%
Mymensingh Area | 97 | 2328:00 | 1001.5124 |  |  | 0 | -5.173%
Sylhet Area | 0 | 0:00 | 447.0376 |  |  | 0 | -6.395%
Barisal Area | 0 | 0:00 | 364.2986 |  |  | 0 | -3.855%
Rangpur Area | 0 | 0:00 | 790.3427 |  |  | 0 | -5.235%
Total | 97 |  | 12349.105 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-2
2) Ghorasal-3,
3) Ashuganj-5
4) Baghabari-71,100 MW
5) Raozan unit-1& 2
6) Siddhirganj 210 MW .
7) Sikalbaha 225 MW
8) Shajibazar 330 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Purbasadipur 132/33 kV T-1 & T-2 transformers tripped at 08:05 showing E/F and were switched on at | [5 empty] | About 75 MW power interruption occurred under
08:20(T-1) & 08:25(T-2) respectively. | [5 empty] | Purbasadipur S/S area from 08:05 to 08:20.
b) Sylhet-Chattak 132 kV Ckt-1 tripped at 08:03 from Sylhet end showing Dist. Z1, A-φ and was switched | [5 empty] | About 10 MW power interruption occurred under
on at 09:02. | [5 empty] | Chattak S/S area from 08:03 to 08:16.
c) Rampal 1320 MW Unit-1 was synchronized at 11:24.
d) Tongi 230 kV S/S-Tongi 80 MW P.P. 132 kV Ckt was under shut down from 11:06 to 17:05 due to power plant work.
e) Payra P/S-Payra S/S 400 kV Ckt-1 was under shut down was under shut down from 08:43 to 22:36 for C/M.
f) Payra S/S 400/132 kV ATR-1 transformer was under shut down from 08:43 to 22:38 for C/M.
g) Savar 132/33 kV T-1 & T-2 transformers tripped at 15:18 due to L-43 feeder fault and were switched | [5 empty] | About 90 MW power interruption occurred under
on at 15:26. | [5 empty] | Savar S/S area from 15:18 to 15:26.
h) Jamalpur 132/33 kV T-3 transformer was under shut down from 17:27 to 20:01 for C/M. | [5 empty] | About 10 MW power interruption occurred under
Jamalpur S/S area from 17:27 to 20:01.
i) Jashore-Benapole 132 kV Ckt-2 tripped at 14:08 showing Dist. Z1 and was switched on at 16:22.
j) Chandpur CCPP GT trip at 16:16 due to GBC trip.
k) Rampal 1320 MW unit-1 trip at 18:06.
l) Tangail 132/33 kV T-2 transformer tripped at 18:35 showing E/F and was switched | [5 empty] | About 58 MW power interruption occurred under
on at 21:43. | [5 empty] | Tangail S/S area from 18:35 to 21:43.
m) Bhulta 132/33 kV GT-1 transformer was under shut down from 21:15 to 22:12 for R/H maintenance. | [5 empty] | About 50 MW power interruption occurred under
Bhulta S/S area from 21:15 to 22:12.
n) Rampal ICT-2 was charged at 22:21 from 400 kV side.
o) Rampal 1320 MW Unit-1 was synchronized at 00:19(06/09/2022).
p) Fenchuganj-Sylhet 132 kV Ckt tripped at 00:33(06/09/2022) from both ends showing Dist. Z2, 3-φ at Fenchuganj end | [5 empty] | About 33 MW power interruption occurred under
& Dist. Z2, Z3, 3-φ at Sylhet end and was switched on at 00:43(06/09/2022). | [5 empty] | Beanibazar S/S area from 00:33(06/09/2022) to 00:43.
q) Payra S/S 132 kV Bus-2 was charged at 22:43.
r) Jamalpur 115 MW tripped at 05:19(06/09/2022) due to LT switchgear problem and was synchronized at
07:05(06/09/2022) and again tripped at 07:30(06/09/2022).
| Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2022-09-05 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 230 | 5528000
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 240 | 6079045 | Machine problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 77 | 1947681 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 351 | 8992770 | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 166 | 4104000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 200 | 4438400 | GT-2 S/D due to dirty gas
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 75 | 1298880 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 115 | 2811520 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 0 | 0 | Under maint.
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 55 | 1339932
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 341064
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 80 | 1578355 | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 224 | 5873157 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 92 | 1340640 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 646920
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 116 | 1059840 | Fuel shortage
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 873206
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 859749
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 49 | 1081140 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 816600
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 12 | 306000 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 16 | 475680 | #REF!
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 255 | 5178764 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 226 | 3495906 | Low Demand
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 90 | 1683223 | Engine problem
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 90 | 1640039 | Engine problem
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 3484656
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 85 | 1413600 | Fuel shortage
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 74 | 1362240 | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 1774080
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 93197
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 18 | 419400 | Fuel shortage
| Dhaka area Total |  |  |  | 5847 | 3466 | 72337684
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 105 | 2500000 | Machine problem
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 25 | 549565
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 33615
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 38 | 711360 | Engine problem
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 144 | 3511013 | Low water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | HGPI
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 105 | 1830792
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 24 | 578208 | Fuel shortage
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 47 | 517867 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 78 | 1044840 | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 90 | 1094400 | Engine problem
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 15 | 353856 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 23 | 575040
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 94 | 643200 | Engine problem
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 25680
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 160 | 1909418 | Fuel shortage
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 36 | 782848 | Engine problem
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 110 | 2659625
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 90 | 1169280 | Fuel shortage
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 107 | 2399945 | Engine problem
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Chattogram area Total |  |  |  | 2382 | 1291 | 22890552
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 209 | 4967000 | #REF!
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 280 | 7450800 | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 280 | 7006000 | FGMO
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+136*1 | 284 | 0 | 0 | On test.
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 45 | 1005624
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 56 | 1279680
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 284363 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1182422
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 142 | 3223345 | Engine problem
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 30 | 487296 | Engine problem
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 790950 | Machine problem
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 150 | 1483200
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 461952
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 10 | 236160
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 94 | 2793600
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 29 | 584000 | Engine problem
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 34 | 294744 | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 21 | 496280 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 150 | 2906880 | Low Demand
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 17 | 417240 | Fuel shortage
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 106 | 2380560 | Engine problem
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 420480 | 33 kV feeder problem.
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 96 | 1286400 | Engine problem
| Cumilla Area Total |  |  |  | 3169 | 1844 | 41438976
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 93 | 2219520 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 0 | Gas shortage
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 6250
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 95 | 2114400 | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 107 | 2395200 | Engine problem
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 102830
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 297360 | Engine problem
| Mymensingh Area Total |  |  |  | 614 | 307 | 7135560
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1022000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 41 | 964048 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Gas shortage
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 47 | 840600
| Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 37 | 783288 | Engine problem
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 8 | 229100 | Engine problem
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 62 | 1480800
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1936320
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 0 | 0 | Machine problem
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50MW PP (EPL) |  | NENP | 27*2 | 50 | 25 | 461660 | Gas shortage
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 417528
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 260 | 7224000 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 401 | 9640000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 224820
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 401 | 9542900
| Sylhet Area Total |  |  |  | 2477 | 1440 | 34767064
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 891 | 21555636
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 0 | 0 | Fuel shortage
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 45 | 198240 | Engine problem
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 227 | 4915200
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 65 | 317312 | Engine problem
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 230 | 5160384 | Gas shortage.
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 0 | 0 | Fuel shortage
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 60 | 826560
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 75 | 1137120 | Fuel shortage
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 15 | 28512 | Fuel shortage
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 374400
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 0 | 0 | 0 | On test.
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 0 | 0 | 0 | 552270
| Khulna Area Total |  |  |  | 2384 | 1608 | 35065634
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 32 | 482496 | Line O/L
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 28 | 569850 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 86 | 2031872 | Gas shortage
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1080 | 24524220 | Line O/L
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 5398309
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Line O/L
| Barisal Area Total |  |  |  | 1958 | 1446 | 33006747
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 32 | 198464 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contract Expired
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Fuel shortage
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 296990 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 192 | 4827491 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 217 | 4663855
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 178 | 4711609 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 428 | 10038036
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 33 | 251251 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 504240
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | .
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 10 | 223236
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 8 | 193714 | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 81 | 358448 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 80 | 1073682 | Low Demand
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 94 | 1519488 | Engine problem
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 95 | 1642944 | Engine problem
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 11040
| Rajshahi Area Total |  |  |  | 2129 | 1502 | 30514488
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 82 | 1947054
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 250 | 6062800 | Machine problem
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 91 | 1525785 | Engine problem
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 39408
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 90 | 550464 | Engine problem
| Intraco Solar 30 MW |  | IPP | 0 | 0 | 0 | 187220
| Rangpur Area Total |  |  |  | 720 | 513 | 10312731
| Total |  |  |  | 21680 | 13417 | 287469436
| Eastern Grid Total |  |  |  | 14489 | 8348 | 178569836
| Western Grid Total |  |  |  | 7191 | 5069 | 108899600
| National Grid Total |  |  |  | 21680 | 13417 | 287469436
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2022-09-05
(a) ENTIRE EASTERN GRID : |  | 8759.24 | MW | (b) ENTIRE WESTERN GRID : |  | 4143.65 | MW
i) Dhaka area |  | 4711.34 | MW | i) Khulna area |  | 1551.4 | MW
ii) Chittagong area |  | 1377.9 | MW | ii) Rajshahi area |  | 1325.3 | MW
iii) Comilla area |  | 1268 | MW | iii) Barisal area |  | 392.95 | MW
iv) Mymensingh area |  | 893 | MW | iv) Rangpur area |  | 874 | MW
v) Sylhet area |  | 509 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 12902.89 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
AKS | 0 | 00:00 | Chowmuhani | 216 | 22:00 | Kaptai | 5 | 19:00 | Nawabganj | 36.9 | 19:00 | Siddhirganj | 108 | 22:00
AKSML | 148 | 17:00 | Chuadanga | 104 | 21:00 | Kazla | 90 | 19:30 | Netrakona | 96 | 19:00 | Sirajganj | 88 | 07:00
Aftabnagar | 33 | 11:00 | Coxsbazar | 117 | 22:00 | Keranigonj | 54 | 19:00 | New | 81 | 09:00 | Sonargaon | 80 | 12:00
Agargaon | 96 | 13:00 | Cumilla(N) | 173 | 21:00 | Khagrachori | 26 | 18:30 | Niamatpur | 64 | 06:00 | Sreemongol | 44 | 12:00
Agrabad | 72 | 15:00 | Cumilla(S) | 147 | 23:00 | Khulna | 93 | 19:00 | Noapara | 47 | 01:00 | Srinagar | 46.28 | 21:00
Amnura | 53 | 21:00 | Daudkandi | 144 | 20:00 | Khulshi | 178 | 15:00 | PHP | 11 | 10:00 | Sunamganj | 38 | 22:00
Ashuganj | 66 | 23:00 | Dhaka | 50 | 13:00 | Kishoreganj | 138 | 05:00 | Pabna | 89 | 00:00 | Sylhet | 136 | 00:00
BSRM | 168 | 23:00 | Dhamrai | 114 | 19:00 | Kodda | 322 | 18:30 | Palashbari | 108 | 23:00 | TK | 28.5 | 19:00
Bagerhat | 102 | 19:00 | Dhanmondi | 142 | 13:00 | Kulaura | 44 | 21:00 | Panchagarh | 46 | 08:00 | Tangail | 195 | 22:00
Bakulia | 100 | 19:30 | Dohazari | 90 | 18:30 | Kurigram | 66 | 19:30 | Patuakhali | 133 | 22:00 | Thakurgaon | 66 | 22:00
Banani | 46 | 12:00 | Faridpur | 136 | 20:00 | Kushtia | 134 | 19:00 | Payra | 1.02 | 16:00 | Tongi | 116 | 19:30
Bangabhaban | 20 | 09:00 | Fatullah | 74 | 15:00 | Lalbag | 96 | 13:00 | Purbachal | 20 | 21:00 | Ullon | 40 | 21:00
Barapukuria | 52 | 19:30 | Fenchuganj | 43 | 19:30 | Lalmonirhat | 46 | 19:30 | Purbasadipur | 96 | 05:00 | Uttara | 93 | 21:00
Barguna | 20 | 00:00 | Feni | 99 | 19:00 | Madanganj | 94 | 02:00 | Rahim | 26 | 08:00 | UttaraNew | 18 | 00:00
Barishal | 102 | 00:00 | GPH | 94 | 12:00 | Madaripur | 103 | 21:00 | Rajbari | 60 | 19:30 | Zigatola | 57 | 19:00
Barishal-230 | 80 | 00:00 | Ghorashal | 70 | 18:30 | Madartek | 85 | 00:00 | Rajendrapur | 92 | 05:00
Baroaulia | 65 | 19:30 | Goalpara | 27 | 13:00 | Madunaghat | 54 | 00:00 | Rajshahi | 132 | 22:00
Baroirhat | 54 | 18:30 | Gollamari | 54 | 12:00 | Magura | 58 | 19:00 | Rajshahi-230 | 26 | 02:00
Bashundhara | 161 | 11:00 | Gopalganj | 102.4 | 00:00 | Mahasthangarh | 66 | 19:30 | Ramganj | 88 | 19:00
BashundharaCement | 2 | 15:00 | Gulshan | 130 | 12:00 | Manikganj | 77 | 04:00 | Rampur | 16 | 00:00
Beanibazar | 54 | 18:30 | Halishahar | 88 | 15:00 | Maniknagar | 79 | 13:00 | Rangamati | 14 | 19:00
Benapole | 62 | 22:00 | HaripurSBU | 173 | 10:00 | Matarbari | 39 | 22:00 | Rangpur | 105 | 08:00
Bhaluka | 136 | 04:00 | Hasnabad | 91 | 12:00 | Matuail | 66 | 11:00 | Ruppur | 5 | 09:00
Bhandaria | 50 | 00:00 | Hathazari | 101 | 19:00 | Millgate | 56 | 09:00 | SSM | 3 | 05:00
Bhangura | 30 | 01:00 | Ishurdi | 74 | 19:00 | Mirpur | 127 | 12:00 | Saidpur | 93 | 08:00
Bheramara(GK) | 60 | 19:30 | Jaldhaka | 66 | 19:00 | Mirsorai | N/A | N/A | Satkhira | 95 | 06:00
Bhulta | 234 | 10:00 | Jamalpur | 133 | 22:00 | Mithapukur | 30 | 01:00 | Satmasjid | 101 | 19:00
Bog-Sherpur | 56 | 19:00 | Jashore | 120 | 11:00 | Modern | 0 | 07:00 | Savar | 156 | 09:00
Bogura | 159 | 19:30 | Jhenaidah | 122 | 18:30 | Mogbazar | 142 | 11:00 | Shahjadpur | 85 | 22:00
Borhanuddin | 42 | 00:00 | Joydebpur | 189 | 20:00 | Mongla | 30 | 00:00 | Shahjibazar | 95 | 00:00
Brahmanbaria | 164 | 21:00 | Joypurhat | 55 | 20:00 | Motijheel | 39 | 13:00 | Shahmirpur | 46.5 | 18:30
Cantonment | 143 | 12:00 | Juldah | 21 | 00:00 | Munshiganj | 101 | 23:00 | Shariatpur | 78 | 22:00
Chandpur | 66 | 21:00 | KSRM | 34 | 14:00 | Mymensingh | 215 | 19:00 | Sherpur | 100 | 19:00
Chandraghona | 32 | 19:00 | Kabirpur | 301 | 09:00 | Naogaon | 120 | 21:00 | Shikalbaha | 28 | 19:00
Chapai | 62 | 23:00 | Kachua | 77 | 22:00 | Narail | 40 | 20:00 | Shikalbaha-230 | N/A | N/A
Charsaidpur | 48 | 01:00 | Kallyanpur | 90 | 13:00 | Narinda | 80 | 13:00 | Shitalakhya | 114 | 12:00
Chauddagram | 56 | 19:00 | Kalurghat | 34 | 12:00 | Narshingdi | 180 | 22:00 | Sholosohor | N/A | N/A
Chhatak | 26 | 19:30 | Kamrangirchar | 63 | 13:00 | Natore | 132 | 19:00 | Shyampur | 144 | 01:00
Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
(1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2022-09-05 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Bhulta | 385 | 19:00 | 372 | 10:00 | Kaliakoir | 384 | 03:00 | 375 | 08:00
| Bibiana | 399 | 00:00 | 392 | 05:00 | Payra | 417 | 15:00 | 409 | 21:00
| BIPTC | 400 | 06:00 | 394 | 20:00 | Rahanpur_I | 396 | 05:00 | 380 | 12:00
| Gopalganj_I | 407 | 06:00 | 391 | 22:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 222 | 19:00 | 211 | 12:00 | Hasnabad | 223 | 04:00 | 215 | 10:00
| AKSML | 231 | 19:00 | 214 | 12:00 | Hathazari | 232 | 19:30 | 217 | 11:00
| Aminbazar | 223 | 21:00 | 213 | 12:00 | Ishurdi | 233 | 00:00 | 228 | 12:00
| Ashuganj | 236 | 19:30 | 228 | 12:00 | Jhenaidah | 229 | 17:00 | 222 | 22:00
| Baghabari | 232 | 17:00 | 229 | 11:00 | Kaliakoir | 222 | 03:00 | 214 | 14:00
| Barapukuria | 222 | 17:00 | 214 | 19:00 | Keranigonj | 223 | 19:00 | 212 | 12:00
| Barishal | 245 | 06:00 | 236 | 23:00 | Khulna(S) | 236 | 15:00 | 228 | 22:00
| Bheramara | 230 | 04:00 | 225 | 13:00 | Maniknagar | 224 | 20:00 | 214 | 12:00
| Bhulta | 228 | 06:00 | 218 | 10:00 | Meghnaghat | 228 | 19:30 | 217 | 12:00
| Bibiana | 235 | 06:00 | 230 | 06:00 | Mirsorai | N/A | N/A | N/A | N/A
| BIPTC | 234 | 17:00 | 226 | 12:00 | Rajshahi | 232 | 17:00 | 225 | 12:00
| Bogura | 225 | 05:00 | 220 | 21:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 248 | 03:00 | 243 | 01:00 | Rampura | 225 | 20:00 | 216 | 11:00
| BSRM | 229 | 19:00 | 213 | 12:00 | Shikalbaha | 234 | 19:30 | 217 | 15:00
| Cumilla(N) | 227 | 19:00 | 217 | 12:00 | Shyampur | 224 | 19:00 | 213 | 12:00
| Fenchuganj | 235 | 00:00 | 231 | 12:00 | Siddhirganj | 226 | 05:00 | 218 | 09:00
| Ghorashal | N/A | N/A | N/A | N/A | Sirajgonj | 230 | 06:00 | 227 | 12:00
| GPH | 231 | 19:00 | 214 | 12:00 | Tongi | 225 | 19:30 | 214 | 11:00
| Haripur | 224 | 21:00 | 216 | 10:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 137 | 05:00 | 129 | 13:00 | Lalbag | 139 | 19:00 | 132 | 12:00
| Agargaon | 137 | 03:00 | 129 | 12:00 | Lalmonirhat | 130 | 04:00 | 121 | 13:00
| Agrabad | 134 | 18:30 | 124 | 14:00 | Madanganj | 132 | 18:30 | 125 | 10:00
| AKS | 134 | 18:00 | 123 | 14:00 | Madaripur | 137 | 09:00 | 131 | 22:00
| Aminbazar | 137 | 19:00 | 130 | 10:00 | Madartek | 137 | 19:30 | 128 | 10:00
| Amnura | 133 | 19:30 | 127 | 01:00 | Madunaghat | 135 | 06:00 | 126 | 12:00
| Ashuganj | 135 | 00:00 | 134 | 01:00 | Magura | 138 | 15:00 | 132 | 04:00
| Bagerhat | 135 | 09:00 | 130 | 20:00 | Mahasthangarh | 135 | 17:00 | 129 | 19:00
| Bakulia | 135 | 19:00 | 124 | 13:00 | Manikganj | 136 | 13:00 | 127 | 10:00
| Banani | 133 | 19:00 | 124 | 11:00 | Maniknagar | 134 | 03:00 | 126 | 12:00
| Bangabhaban | 134 | 05:00 | 127 | 10:00 | Matarbari | 125 | 07:00 | 113 | 15:00
| Barapukuria | 135 | 05:00 | 129 | 14:00 | Matuail | 131 | 19:00 | 126 | 10:00
| Barguna | 138 | 02:00 | 130 | 22:00 | Millgate | 134 | 23:00 | 125 | 12:00
| Barishal | 139 | 15:00 | 130 | 18:30 | Mirpur | 136 | 22:00 | 128 | 10:00
| Barishal-230 | 139 | 06:00 | 133 | 00:00 | Mithapukur | 132 | 17:00 | 125 | 19:00
| Baroaulia | 136 | 20:00 | 125 | 13:00 | Modern | 135 | 19:30 | 125 | 10:00
| Baroirhat | 131 | 08:00 | 123 | 12:00 | Mogbazar | 138 | 02:00 | 129 | 10:00
| Bashundhara | 134 | 20:00 | 124 | 11:00 | Mongla | 135 | 15:00 | 128 | 02:00
| BashundharaCement | 132 | 18:30 | 125 | 10:00 | Motijheel | 134 | 05:00 | 127 | 10:00
| Beanibazar | 133 | 09:00 | 125 | 01:00 | Munshiganj | 133 | 18:30 | 127 | 11:00
| Benapole | 134 | 14:00 | 127 | 22:00 | Mymensingh | 135 | 05:00 | 111 | 21:00
| Bhaluka | 133 | 11:00 | 112 | 19:30 | Naogaon | 132 | 17:00 | 125 | 22:00
| Bhandaria | 137 | 08:00 | 129 | 00:00 | Narail | 138 | 15:00 | 130 | 20:00
| Bhangura | 138 | 17:00 | 134 | 13:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bheramara | 136 | 17:00 | 133 | 12:00 | Narshingdi | 126 | 18:30 | 118 | 16:00
| Bheramara(GK) | 137 | 06:00 | 134 | 12:00 | Natore | 135 | 17:00 | 129 | 21:00
| Bhulta | 123 | 22:00 | 115 | 12:00 | Nawabganj | 139 | 05:00 | 132 | 11:00
| Bog-Sherpur | 136 | 17:00 | 132 | 21:00 | Netrakona | 125 | 13:00 | 109 | 21:00
| Bogura | 136 | 06:00 | 132 | 00:00 | New | 134 | 20:00 | 126 | 10:00
| Bogura-230 | 136 | 05:00 | 133 | 12:00 | Niamatpur | 130 | 17:00 | 122 | 12:00
| Brahmanbaria | 131 | 07:00 | 130 | 10:00 | Noapara | 136 | 15:00 | 131 | 21:00
| Cantonment | 136 | 03:00 | 127 | 12:00 | Pabna | 135 | 15:00 | 131 | 03:00
| Chandpur | 137 | 17:00 | 122 | 01:00 | Palashbari | 131 | 17:00 | 124 | 19:00
| Chandraghona | 136 | 18:30 | 134 | 07:00 | Panchagarh | 129 | 02:00 | 114 | 14:00
| Chapai | 133 | 17:00 | 128 | 01:00 | Patuakhali | 137 | 06:00 | 130 | 22:00
| Charsaidpur | 133 | 19:00 | 120 | 02:00 | Payra | 137 | 02:00 | 133 | 22:00
| Chauddagram | 131 | 19:00 | 124 | 12:00 | PHP | 130 | 19:30 | 122 | 16:00
| Chhatak | 132 | 09:00 | 123 | 20:00 | Postogola | 142 | 22:00 | 134 | 12:00
| Chowmuhani | 131 | 18:00 | 122 | 15:00 | Purbachal | 134 | 20:00 | 125 | 11:00
| Chuadanga | 134 | 15:00 | 125 | 21:00 | Purbasadipur | 131 | 06:00 | 118 | 13:00
| Coxsbazar | 124 | 07:00 | 111 | 15:00 | Rahim | 132 | 18:30 | 127 | 10:00
| Cumilla(N) | 134 | 19:00 | 126 | 14:00 | Rajbari | 135 | 15:00 | 129 | 21:00
| Cumilla(S) | 133 | 19:00 | 125 | 16:00 | Rajendrapur | 135 | 06:00 | 128 | 09:00
| Daudkandi | 135 | 18:30 | 124 | 08:00 | Rajshahi | 132 | 00:00 | 128 | 13:00
| Dhaka | 137 | 05:00 | 129 | 10:00 | Rajshahi-230 | 134 | 17:00 | 128 | 12:00
| Dhamrai | 136 | 23:00 | 129 | 12:00 | Ramganj | 131 | 17:00 | 121 | 14:00
| Dhanmondi | 131.5 | 22:00 | 125 | 11:00 | Rampur | 133 | 07:00 | 124 | 12:00
| Dohazari | 132 | 19:00 | 121 | 15:00 | Rampura | 137 | 21:00 | 128 | 10:00
| Faridpur | 135 | 15:00 | 129 | 22:00 | Rangamati | 135 | 22:00 | 127 | 14:00
| Fatullah | 136 | 19:00 | 129 | 12:00 | Rangpur | 129 | 17:00 | 122 | 19:00
| Fenchuganj | 134 | 06:00 | 132 | 01:00 | Ruppur | 136 | 00:00 | 132 | 21:00
| Feni | 131 | 17:00 | 123 | 01:00 | Saidpur | 133 | 08:00 | 122 | 15:00
| Ghorashal | 136 | 00:00 | 136 | 00:00 | Satkhira | 133 | 15:00 | 125 | 22:00
| Goalpara | 138 | 17:00 | 133 | 22:00 | Satmasjid | 137 | 03:00 | 128 | 12:00
| Gollamari | 136 | 15:00 | 132 | 00:00 | Savar | 138 | 19:00 | 129 | 11:00
| Gopalganj | 137 | 15:00 | 132 | 04:00 | Shahjadpur | 139 | 00:00 | 136 | 10:00
| Gopalganj_I | 139 | 15:00 | 133 | 21:00 | Shahjibazar | 135 | 08:00 | 130 | 21:00
| Gulshan | 137 | 20:00 | 128 | 10:00 | Shahmirpur | 135 | 19:00 | 124 | 15:00
| Halishahar | 136 | 19:30 | 124 | 14:00 | Shariatpur | 136 | 15:00 | 127 | 22:00
| Haripur | 132 | 18:30 | 127 | 10:00 | Sherpur | 138 | 05:00 | 115 | 21:00
| HaripurSBU | 132 | 19:00 | 127 | 10:00 | Shikalbaha | 136 | 19:30 | 125 | 12:00
| Hasnabad | 142 | 23:00 | 135 | 12:00 | Shikalbaha-230 | 136 | 19:30 | 126 | 15:00
| Hathazari | 137 | 19:00 | 127 | 12:00 | Shitalakhya | 142 | 22:00 | 132 | 12:00
| Ishurdi | 136 | 15:00 | 133 | 04:00 | Sholosohor | N/A | N/A | N/A | N/A
| Jaldhaka | 133 | 04:00 | 120 | 13:00 | Shyampur | 135 | 19:00 | 129 | 04:00
| Jamalpur | 140 | 13:00 | 119 | 20:00 | Shyampur-230 | 135 | 03:00 | 129 | 12:00
| Jashore | 135 | 15:00 | 129 | 21:00 | Siddhirganj | 132 | 20:00 | 126 | 12:00
| Jhenaidah | 139 | 15:00 | 133 | 21:00 | Sirajganj | 135 | 00:00 | 132 | 13:00
| Jhenaidah-230 | 140 | 15:00 | 134 | 21:00 | Sonargaon | 132 | 00:00 | 128 | 07:00
| Joydebpur | 138 | 19:30 | 127 | 08:00 | Sreemongol | 135 | 06:00 | 132 | 21:00
| Joypurhat | 132 | 00:00 | 125 | 12:00 | Srinagar | 139 | 05:00 | 132 | 11:00
| Juldah | 136 | 19:00 | 125 | 12:00 | SSM | 139 | 19:30 | 128 | 13:00
| Kabirpur | 136 | 00:00 | 121 | 11:00 | Sunamganj | 131 | 08:00 | 121 | 19:00
| Kachua | 133 | 17:00 | 130 | 18:00 | Sylhet | 134 | 09:00 | 127 | 18:30
| Kaliakoir | 138 | 05:00 | 132 | 10:00 | Tangail | 136 | 11:00 | 124 | 20:00
| Kallyanpur | 137 | 19:30 | 128 | 12:00 | Thakurgaon | 128 | 19:30 | 112 | 15:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2022-09-05
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 1530 | 7529 | 4718 | 12247 |  |  |  | QF-LDC-11
0:30 | 1472.5 | 7535.5 | 4592 | 12127.5 | Date: | 2022-09-05
1:00 | 1415 | 7542 | 4466 | 12008
1:30 | 1417.5 | 7502.5 | 4440 | 11942.5
2:00 | 1420 | 7463 | 4414 | 11877
2:30 | 1420 | 7448.5 | 4401 | 11849.5 | [5 empty] | Gen. at Eve. Peak | 13417 | 13417 MW (19:30 )
3:00 | 1420 | 7434 | 4388 | 11822 | [6 empty] | 19:30
3:30 | 1380 | 7404.5 | 4347 | 11751.5 | [5 empty] | Gen. at Day Peak | 11806 | 11806 MW (12:00 )
4:00 | 1340 | 7375 | 4306 | 11681 | [6 empty] | 12:00
4:30 | 1340 | 7324 | 4318 | 11642 | [5 empty] | Highest Generation | 13417
5:00 | 1340 | 7273 | 4330 | 11603 | [6 empty] | 19:30
5:30 | 1340 | 7052 | 4264 | 11316
6:00 | 1340 | 6831 | 4198 | 11029
6:30 | 1280 | 6756 | 4094 | 10850
7:00 | 1220 | 6681 | 3990 | 10671
7:30 | 1232.5 | 6665.5 | 3960 | 10625.5
8:00 | 1245 | 6650 | 3930 | 10580
8:30 | 1392.5 | 6833.5 | 4035 | 10868.5
9:00 | 1540 | 7017 | 4140 | 11157
9:30 | 1542.5 | 7111 | 4156 | 11267
10:00 | 1545 | 7205 | 4172 | 11377
10:30 | 1547.5 | 7291 | 4231.5 | 11522.5
11:00 | 1550 | 7377 | 4291 | 11668
11:30 | 1542.5 | 7397 | 4340 | 11737
12:00 | 1535 | 7417 | 4389 | 11806
12:30 | 1540 | 7299 | 4348 | 11647
13:00 | 1545 | 7181 | 4307 | 11488
13:30 | 1552.5 | 7102.5 | 4272.5 | 11375
14:00 | 1560 | 7024 | 4238 | 11262
14:30 | 1555 | 7091.5 | 4207.5 | 11299
15:00 | 1550 | 7159 | 4177 | 11336
15:30 | 1547.5 | 7098.5 | 4116 | 11214.5
16:00 | 1545 | 7038 | 4055 | 11093
16:30 | 1545 | 7069 | 4014 | 11083
17:00 | 1545 | 7100 | 3973 | 11073
17:30 | 1462.5 | 7202 | 4028.5 | 11230.5
18:00 | 1380 | 7304 | 4084 | 11388
18:30 | 1305 | 7836 | 4458.5 | 12294.5
19:00 | 1230 | 8368 | 4833 | 13201
19:30 | 1295 | 8348 | 5069 | 13417
20:00 | 1125 | 8348 | 4947 | 13295 |  |  |  | Executive Engineer
20:30 | 1120 | 8313 | 4937 | 13250 |  |  |  | Network Operation Division
21:00 | 1115 | 8278 | 4927 | 13205
21:30 | 1125 | 8271.5 | 4926.5 | 13198
22:00 | 1135 | 8265 | 4926 | 13191 |  |  |  |  | Page 6 of 7
22:30 | 1275 | 8212.5 | 4911 | 13123.5
23:00 | 1415 | 8160 | 4896 | 13056
23:30 | 1472.5 | 7844.5 | 4807 | 12651.5
24:00 | 1530 | 7529 | 4718 | 12247
13417 MW (19:30 )
11806 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2022-09-05 |  | Energy |  | 287469436
[13 empty] | 2022-09-05 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 3948 | 891 | 1916 | 795 | 2386 | 1311 | 147 | 445 | 526 | 102 | 0 | 0
0:30 | 4017 | 889 | 1909.5 | 806 | 2271.5 | 1360 | 149.5 | 359.5 | 379.5 | 121 | 0 | 434.0618 | Date: | 2022-09-05
1:00 | 4086 | 887 | 1903 | 817 | 2157 | 1409 | 152 | 274 | 233 | 140 | 0 | 868.1237
1:30 | 4100 | 887.5 | 1906 | 791.5 | 2135 | 1394.5 | 152.5 | 265.5 | 212.5 | 139 | 0 | 790.2506 | [8 empty] | Total Energy | 287.4694 | Total Energy Gen 287.469 MKWHr Energy Not Served 2.492 MKWHr Energy Requirement 289.962 MKWHr
2:00 | 4114 | 888 | 1909 | 766 | 2113 | 1380 | 153 | 257 | 192 | 138 | 0 | 712.3775 | [8 empty] | Energy not Served | 2.4924
2:30 | 4098.5 | 888 | 1912 | 766 | 2106 | 1355 | 153.5 | 275.5 | 208.5 | 137 | 0 | 576.4452 | [8 empty] | Energy Requirement | 289.9618
3:00 | 4083 | 888 | 1915 | 766 | 2099 | 1330 | 154 | 294 | 225 | 136 | 0 | 440.5129
3:30 | 4123 | 890 | 1914 | 616 | 2095.5 | 1320 | 154 | 362 | 280 | 134 | 0 | 263.5705 | [6 empty] | Shortage
4:00 | 4163 | 892 | 1913 | 466 | 2092 | 1310 | 154 | 430 | 335 | 132 | 0 | 86.628
4:30 | 4143.5 | 892 | 1913 | 463.5 | 2070 | 1310 | 153.5 | 436.5 | 340.5 | 131 | 0 | 63.1279
5:00 | 4124 | 892 | 1913 | 461 | 2048 | 1310 | 153 | 443 | 346 | 130 | 0 | 39.6277
5:30 | 4124 | 892 | 1916 | 230.5 | 2029 | 1295 | 152.5 | 441 | 327.5 | 126 | 0.5 | 39.6277
6:00 | 4124 | 892 | 1919 | 0 | 2010 | 1280 | 152 | 439 | 309 | 122 | 1 | 39.6277
6:30 | 4107.5 | 892.5 | 1911 | 0 | 1946.5 | 1279.5 | 151.5 | 362 | 247 | 117 | 10 | 19.8139 |  |  |  |  | Coal
7:00 | 4091 | 893 | 1903 | 0 | 1883 | 1279 | 151 | 285 | 185 | 112 | 19 | 0
7:30 | 4037.5 | 892.5 | 1885 | 0 | 1915 | 1244.5 | 151 | 292.5 | 185 | 115 | 37.5 | 0 |  |  |  | Oil |  |  |  | ,
8:00 | 3984 | 892 | 1867 | 0 | 1947 | 1210 | 151 | 300 | 185 | 118 | 56 | 0
8:30 | 3997 | 892 | 1865 | 160.5 | 1990 | 1215 | 151 | 344 | 202.5 | 121 | 78 | 50
9:00 | 4010 | 892 | 1863 | 321 | 2033 | 1220 | 151 | 388 | 220 | 124 | 100 | 100
9:30 | 4010.5 | 892 | 1862.5 | 359.5 | 2062 | 1190.5 | 151 | 412.5 | 250 | 124 | 142.5 | 50
10:00 | 4011 | 892 | 1862 | 398 | 2091 | 1161 | 151 | 437 | 280 | 124 | 185 | 0
10:30 | 4070.5 | 892 | 1864 | 525.5 | 2091 | 1155.5 | 151 | 437 | 283.5 | 127 | 141 | 0
11:00 | 4130 | 892 | 1866 | 653 | 2091 | 1150 | 151 | 437 | 287 | 130 | 97 | 0
11:30 | 4147.5 | 892 | 1860 | 662 | 2089 | 1203 | 150.5 | 429.5 | 288.5 | 132 | 93 | 61
12:00 | 4165 | 892 | 1854 | 671 | 2087 | 1256 | 150 | 422 | 290 | 134 | 89 | 122
12:30 | 4134 | 892 | 1838 | 563 | 2090 | 1253 | 151 | 428 | 297.5 | 134 | 76 | 61
13:00 | 4103 | 892 | 1822 | 455 | 2093 | 1250 | 152 | 434 | 305 | 134 | 63 | 0
13:30 | 4103 | 892 | 1822 | 455 | 2093 | 1250 | 152 | 434 | 305 | 134 | 63 | 0
14:00 | 4103 | 892 | 1822 | 455 | 2093 | 1250 | 152 | 434 | 305 | 134 | 63 | 0
14:30 | 4012 | 892 | 1834 | 503.5 | 2099 | 1229.5 | 149 | 392 | 294 | 139 | 70.5 | 0
15:00 | 3921 | 892 | 1846 | 552 | 2105 | 1209 | 146 | 350 | 283 | 144 | 78 | 0
15:30 | 3905 | 892 | 1826.5 | 511 | 2119.5 | 1209 | 145 | 332.5 | 285 | 113 | 68.5 | 0
16:00 | 3889 | 892 | 1807 | 470 | 2134 | 1209 | 144 | 315 | 287 | 82 | 59 | 0
16:30 | 3848 | 892 | 1802.5 | 405 | 2235 | 1209 | 144 | 311.5 | 287 | 80 | 40 | 0
17:00 | 3848 | 892 | 1798 | 340 | 2336 | 1209 | 144 | 308 | 287 | 78 | 21 | 0
17:30 | 3826.5 | 892 | 1811 | 232.5 | 2565 | 1209 | 144 | 311.5 | 338.5 | 80 | 12 | 0
18:00 | 3805 | 892 | 1824 | 125 | 2794 | 1209 | 144 | 315 | 390 | 82 | 3 | 0
18:30 | 3867 | 891.5 | 1860.5 | 445 | 3071.5 | 1234.5 | 144 | 374.5 | 517.5 | 88 | 1.5 | 58.9808
19:00 | 3929 | 891 | 1897 | 765 | 3349 | 1260 | 144 | 434 | 645 | 94 | 0 | 117.9616
19:30 | 3943 | 891 | 1854 | 696 | 3434 | 1412 | 144 | 444 | 722 | 94 | 0 | 96.7654
20:00 | 3954 | 893 | 1871 | 530 | 3459 | 1422 | 144 | 444 | 701 | 94 | 0 | 67.275
20:30 | 3949.5 | 893 | 1868 | 500 | 3449.5 | 1426.5 | 146 | 443.5 | 696.5 | 95 | 0 | 33.6375
21:00 | 3945 | 893 | 1865 | 470 | 3440 | 1431 | 148 | 443 | 692 | 96 | 0 | 0
21:30 | 3911.5 | 892.5 | 1878 | 502.5 | 3427 | 1431 | 148 | 443.5 | 684 | 98 | 0 | 0
22:00 | 3878 | 892 | 1891 | 535 | 3414 | 1431 | 148 | 444 | 676 | 100 | 0 | 0
22:30 | 3909 | 891.5 | 1896.5 | 539 | 3365 | 1425.5 | 147.5 | 444.5 | 621.5 | 102 | 0 | 0
23:00 | 3940 | 891 | 1902 | 543 | 3316 | 1420 | 147 | 445 | 567 | 104 | 0 | 0
23:30 | 3944 | 891 | 1909 | 669 | 2851 | 1365.5 | 147 | 445 | 546.5 | 103 | 0 | 0 | Max Temp. in Dhaka |  | 24.7° C | 34° C
24:00 | 3948 | 891 | 1916 | 795 | 2386 | 1311 | 147 | 445 | 526 | 102 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 287.469 MKWHr Energy Not Served 2.492 MKWHr Energy Requirement 289.962 MKWHr
Note on W13: Author:

## Generation
g | 2022-09-05
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 82 | 83 | 84 | 84 | 83 | 82 | 81 | 81 | 81 | 81 | 81 | 80 | 82 | 81 | 76 | 74 | 74 | 74 |  | 74 | 74 | 74 | 78 | 78 | 77 | 77 | 1823013
2 | Karnaphuli Hydro PP Unit-4 & 5 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1688000
3 | Chattogram TPP-1 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 110 | 110 | 110 | 108 | 105 | 105 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2500000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 20 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 17 | 17 | 17 | 17 | 17 | 17 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 549565
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 0 | 0 | 1 | 3 | 8 | 20 |  |  |  | 11 | 1 | 0 | [8 empty] | 33615
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 |  | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 517867
12 | Hathazari 100 MW peaking PP | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 17 | 24 | 24 | 25 | 24 | 578208
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 69 | 69 | 69 | 69 | 69 | 69 | 54 | 51 | 51 | 51 | 51 | 51 | 59 | 69 | 69 | 69 | 95 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 78 | 1830792
| Daudkandi 200 MW PP (B.Trac) | 189 | 130 | 130 | 100 | 100 | 0 |  |  | 70 | 70 | 185 | 185 | 152 | 100 | 190 | 170 | 120 | 0 |  | 191 | 150 | 150 | 120 | 150 | 150 | 190 | 2906880
14 | Titas 50 MW Peaking PP | 31 | 31 | 31 | 31 | 31 | 31 | 0 |  |  |  | 0 | 15 | 19 | 15 | 23 | 22 | 29 | 33 |  | 30 | 30 | 30 | 23 | 23 | 22 | 22 | 487296
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 253 | 253 | 251 | 258 | 262 | 262 | 265 | 257 | 295 | 290 | 275 | 264 | 255 | 250 | 245 | 236 | 242 | 244 |  | 238 | 224 | 224 | 213 | 150 | 150 | 150 | 5873157
18 | Kodda 300 MW PP Unit-2 (Summit) | 213 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 193 | 195 | 195 | 192 | 190 | 190 | 195 | 195 | 195 | 200 |  | 255 | 255 | 278 | 278 | 278 | 278 | 278 | 5178764
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 284363
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4 | 231 | 231 | 231 | 230 | 231 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 229 | 230 | 230 | 230 | 240 | 225 |  | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 5528000
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 260 | 260 | 260 | 260 | 260 | 270 | 260 | 260 | 260 | 260 | 260 | 260 | 240 | 240 | 240 | 240 | 240 | 240 |  | 240 | 240 | 240 | 260 | 260 | 260 | 260 | 6079045
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 45 | 45 | 45 | 45 | 45 | 42 | 41 | 41 | 37 | 40 | 38 | 39 | 41 | 41 | 37 | 38 | 43 | 44 |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 1005624
33 | Ashuganj 225 MW CCPP | 208 | 207 | 210 | 207 | 210 | 210 | 207 | 207 | 209 | 206 | 206 | 205 | 207 | 205 | 196 | 192 | 180 | 197 |  | 204 | 209 | 210 | 207 | 208 | 210 | 208 | 4967000
34 | Ashuganj 450 MW CCPP(South) | 275 | 285 | 265 | 300 | 270 | 265 | 285 | 265 | 300 | 280 | 285 | 325 | 325 | 320 | 300 | 300 | 300 | 270 |  | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 7006000
| Ashuganj 450 MW CCPP(North) | 280 | 290 | 270 | 300 | 280 | 280 | 308 | 355 | 310 | 315 | 315 | 345 | 340 | 335 | 300 | 300 | 300 | 280 |  | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 7450800
| Ashuganj 420 MW CCPP(East) | [25 empty] | 0 | 0
35 | Ashuganj 55 MW PP (Precision) | 51 | 52 | 51 | 52 | 51 | 51 | 51 | 52 | 51 | 52 | 51 | 48 | 50 | 56 | 55 | 55 | 56 | 56 |  | 56 | 56 | 56 | 55 | 56 | 56 | 56 | 1279680
36 | Chandpur 150 MW CCPP | 51 | 50 | 51 | 50 | 50 | 52 | 50 | 50 | 50 | 50 | 50 | 50 | 48 | 50 | 50 | 31 | 0 | [9 empty] | 790950
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 370 | 378 | 378 | 377 | 378 | 381 | 385 | 378 | 397 | 404 | 403 | 398 | 378 | 367 | 362 | 361 | 361 | 361 |  | 365 | 351 | 356 | 338 | 317 | 336 | 343 | 8992770
40 | Meghnaghat 450 MW CCPP(MPL) | 210 | 210 | 210 | 210 | 210 | 225 | 225 | 225 | 225 | 225 | 225 | 215 | 215 | 210 | 210 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4438400
41 | Haripur 360MW CCPP(HPL) | 163 | 163 | 166 | 172 | 174 | 177 | 177 | 175 | 206 | 213 | 203 | 186 | 175 | 168 | 163 | 157 | 166 | 172 |  | 171 | 166 | 160 | 138 | 139 | 151 | 154 | 4104000
42 | RPCL 210MW CCPP | 150 | 146 | 148 | 150 | 149 | 149 | 106 | 69 | 69 | 66 | 66 | 65 | 65 | 66 | 44 | 44 | 44 | 42 |  | 72 | 93 | 107 | 106 | 118 | 141 | 141 | 2219520
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 0 | 4 | 5 | 12 | 41 | 19 | 5 | 4 | 7 | 8 | 4 | 3 | 0 | [8 empty] | 102830
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1022000
45 | Fenchugonj CCPP Phase-2 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 |  | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 964048
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 62 | 63 | 63 | 64 | 64 | 64 | 62 | 62 | 62 | 61 | 60 | 60 | 60 | 61 | 61 | 61 | 61 | 60 |  | 62 | 62 | 61 | 59 | 58 | 64 | 64 | 1480800
48 | Shahjibazar 86MW PP (Shahjibazar) | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 78 | 78 | 78 | 78 | 81 | 81 | 81 | 81 | 81 | 81 |  | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 1936320
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL) | 24 | 24 | 24 | 24 | 24 | 24 | 21 | 15 |  |  | 5 | 20 | 25 | 24 | 23 | 24 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 461660
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 9 | 9 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 224820
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 |  | 8 | 8 | 0 | 8 | 8 | 8 | 8 | 229100
55 | Fenchugonj 51 MW PP (Barakatullah) | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 |  | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 840600
56 | Shahjahanulla 25 MW PP | 24 | 24 | 24 | 24 | 24 | 24 | 7 |  |  | 6 | 3 | 10 |  | 22 | 22 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 417528
57 | Bibiana-II 341 MW CCPP (Summit) | 305 | 300 | 295 | 290 | 280 | 270 | 290 | 300 | 290 | 280 | 290 | 300 | 280 | 290 | 300 | 300 | 300 | 290 |  | 300 | 260 | 270 | 305 | 305 | 285 | 290 | 7224000
| Bibiyana South 400 MW | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 401 | 400 | 401 | 395 | 396 | 398 | 391 | 391 | 401 | 386 |  | 401 | 401 | 401 | 397 | 401 | 401 | 401 | 9542900
58 | Nababganj 55 MW PP (Southern power ) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 17 | 17 | 35 | 35 |  | 55 | 55 | 55 | 35 | 35 | 35 | 35 | 859749
59 | Tangail Palli Power Gen 22 MW | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 297360
60 | Barabkunda 22 MW PP (Regent) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 12 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 | 15 | 15 | 13 | 13 | 13 | 353856
61 | Narshingdi 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 0 |  |  |  | 0 |  | 22 | 22 | 22 | 19 | 19 | 19 | 19 | 341064
62 | Tangail 22 MW PP (Doreen)
63 | Impoprt (Tripura) | 140 | 138 | 136 | 132 | 130 | 122 | 112 | 118 | 124 | 124 | 130 | 134 | 134 | 144 | 144 | 82 | 78 | 82 |  | 94 | 94 | 94 | 96 | 100 | 104 | 102 | 2793600
64 | Malancha, Ctg. EPZ (United) | 38 | 38 | 39 | 39 | 40 | 40 | 31 | 17 | 8 | 8 | 9 | 9 | 13 | 10 | 7 | 10 | 17 | 7 |  | 20 | 23 | 28 | 32 | 35 | 35 | 34 | 575040
65 | Feni 22MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 461952
66 | Feni 11 MW PP (Doreen) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 236160
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 23 | 15 | 15 | 15 | 14 | 14 | 10 | 8 | 8 | 16 | 16 |  | 25 | 29 | 32 | 33 | 33 | 33 | 33 | 584000
68 | Cumilla 25 MW PP (Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 15 | 21 |  | 21 | 21 | 20 | 21 | 21 | 21 | 21 | 496280
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 27 | 27 | 27 | 27 | 27 | 27 | 0 | 0 | 6 | 23 | 23 | 21 | 25 | 0 | 0 | 24 | 24 | 24 |  | 19 | 24 | 24 | 24 | 28 | 28 | 28 | 481140
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 816600
72 | Rupganj 33 MW PP(Summit) | 14 | 14 | 16 | 16 | 16 | 16 | 15 | 8 | 14 | 13 | 13 | 8 | 13 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 13 | 8 | 16 | 16 | 306000
73 | Ghorashal 108MW PP (Regent) | 92 | 92 | 92 | 92 | 92 | 92 | 88 | 86 | 81 | 77 | 75 | 72 | 72 | 77 | 77 | 77 | 75 | 71 |  | 74 | 77 | 81 | 81 | 85 | 88 | 88 | 1947681
| Feni Lanka Power | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 417240
| Chowmuhani 113 MW | 104 | 99 | 99 | 94 | 94 | 95 | 96 | 95 | 95 | 95 | 95 | 96 | 94 | 94 | 95 | 102 | 104 | 104 |  | 105 | 106 | 105 | 105 | 105 | 104 | 96 | 2380560
| Manikgonj 162MW PP(MPGL) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 29 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 80 | 162 |  | 162 | 162 | 162 | 162 | 162 | 162 | 17 | 1774080
77 | Siddhirganj 100 PP(Dutch Bangla) | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 72 |  | 80 | 80 | 80 | 80 | 80 | 80 | 46 | 1578355
78 | Gazipur 52 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 21 |  | 33 | 16 | 18 | 32 | 32 | 32 | 16 | 475680
79 | Kodda 150MW PP | 50 | 50 | 50 | 50 | 50 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 67 |  | 105 | 116 | 116 | 116 | 116 | 50 | 50 | 1059840
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 10 | 8 | 8 |  | 14 | 34 | 33 | 34 | 34 | 8 | 8 | 294744
| Gazipur 100 MW PP | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 49 | 66 | 84 | 84 |  | 85 | 85 | 85 | 85 | 84 | 70 | 50 | 1413600
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 0 | 1 | 2 | 3 | 4 | 3 | 2 | 3 | 3 | 1 | 0 | [9 empty] | 25680
| Jodiac Power | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 17 | 17 | 17 | 17 | 17 | 17 | 25 | 36 | 36 |  | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 782848
| Karnaphuli Power Ltd. | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 78 | 2659625
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP ( Summit) | 112 | 118 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 122 | 122 | 120 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 90 | 95 | 108 | 120 | 2811520
87 | Meghnaghat 100 MW(IEL) | 50 | 50 | 50 | 49 | 51 | 49 | 50 | 50 | 49 | 50 | 50 | 51 | 49 | 49 | 44 | 41 | 41 | 48 |  | 72 | 75 | 74 | 74 | 73 | 74 | 43 | 1298880
| Meghnaghat 104 MW PP (OPCL) | 55 | 55 | 54 | 55 | 55 | 54 | 32 | 17 | 31 | 53 | 55 | 54 | 51 | 51 | 55 | 55 | 58 | 71 |  | 74 | 74 | 73 | 72 | 66 | 72 | 72 | 1362240
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 78 |  | 78 | 78 | 78 | 78 | 78 | 78 | 33 | 1044840
92 | Fenchuganj 44MW (Energyprima) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 6 | 12 | 21 | 27 | 28 | 28 | 30 | 30 | 30 | 32 | 32 |  | 37 | 37 | 40 | 48 | 49 | 49 | 49 | 783288
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 35 | 43 | 43 | 43 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1182422
94 | Gagnagar 102 MW PP (Digital Power) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 40 | 40 | 40 | 40 |  | 92 | 92 | 92 | 92 | 92 | 92 | 40 | 1340640
95 | Patenga 50MW PP (Baraka) | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 27 | 30 | 38 |  | 39 | 38 | 39 | 38 | 39 | 39 | 25 | 711360
96 | Chattogram 108 MW PP (ECPV) | 11 | 11 | 12 | 12 | 11 | 12 | 12 | 12 | 12 | 12 | 12 | 7 | 7 | 11 | 11 | 11 | 11 | 24 |  | 79 | 94 | 94 | 94 | 94 | 46 | 12 | 643200
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1339932
100 | Manikganj 55 MW PP (Northern) | 35 | 35 | 35 | 35 | 35 | 35 | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 16 | 35 | 35 |  | 55 | 55 | 55 | 55 | 35 | 35 | 35 | 873206
101 | Kushiara 163 MW CCPP (KP)
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | [9 empty] | 6250
103 | Kamalaghat 54 MW PP(Banco Energy) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 17 | 646920
104 | Keranigonj 300 MW PP (APR) | 225 | 226 | 225 | 136 | 131 | 0 |  |  | 53 | 148 | 225 | 225 | 123 | 102 | 180 | 170 | 80 | 50 |  | 226 | 226 | 180 | 150 | 185 | 180 | 225 | 3495906
105 | Bramhangoan 100 MW PP (Aggreko) | 80 | 80 | 80 | 80 | 80 | 0 |  |  | 80 | 80 | 80 | 80 | 80 | 40 | 80 | 80 | 90 | 25 |  | 90 | 90 | 90 | 90 | 90 | 85 | 80 | 1683223
106 | Mymensingh 200 MW PP (United) | 95 | 96 | 94 | 94 | 55 | 55 | 38 | 85 | 85 | 94 | 94 | 91 | 92 | 92 | 93 | 102 | 101 | 91 |  | 95 | 95 | 96 | 95 | 96 | 95 | 95 | 2114400
112 | Aurahati 100MW PP (Aggreko) | 80 | 80 | 80 | 80 | 80 | 0 |  |  | 81 | 80 | 80 | 81 | 80 | 30 | 80 | 50 | 50 | 50 |  | 90 | 90 | 90 | 90 | 90 | 90 | 80 | 1640039
114 | Kodda 149 MW PP Unit-1 (Summit) | 149 | 149 | 149 | 149 | 141 | 135 | 122 | 112 | 119 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 |  | 149 | 149 | 149 | 149 | 149 | 134 | 145 | 3484656
115 | Juldah 100 MW PP Unit-3 (Acorn) | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 33 | 1094400
116 | Chandpur 200MW (Desh energy) | 45 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 20 | 27 | 35 | 35 | 35 | 35 | 92 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 68 | 1483200
117 | Ashuganj 150MW PP (Midland) | 132 | 132 | 137 | 135 | 137 | 135 | 133 | 130 | 125 | 125 | 125 | 122 | 125 | 127 | 128 | 128 | 132 | 142 |  | 143 | 142 | 142 | 145 | 145 | 145 | 143 | 3223345
118 | Bibiyana-III 400 MW CCPP | 403 | 402 | 402 | 402 | 402 | 401 | 402 | 403 | 401 | 402 | 402 | 400 | 402 | 402 | 401 | 403 | 402 | 404 |  | 401 | 401 | 400 | 401 | 401 | 402 | 401 | 9640000
| Jamalpur 115 MW PP (United) | 97 | 98 | 98 | 98 | 98 | 98 | 98 | 106 | 106 | 91 | 91 | 91 | 101 | 101 | 105 | 89 | 98 | 107 |  | 108 | 107 | 108 | 108 | 108 | 108 | 108 | 2395200
| Anwara 300 MW PP (United) | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 51 | 52 | 52 | 51 | 52 | 52 | 52 | 52 | 101 |  | 155 | 160 | 161 | 161 | 161 | 161 | 161 | 1909418
| Juldah unit-2 (Acorn) | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 |  | 90 | 90 | 90 | 90 | 90 | 90 | 40 | 1169280
| Anlima Energy Ltd. | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 91 | 90 | 89 | 89 | 89 | 89 | 89 | 95 | 85 |  | 89 | 107 | 107 | 107 | 107 | 107 | 107 | 2399945
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 11 | 12 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 420480
| Spectra Solar Plant Ltd. |  |  |  |  | 0 | 0 | 5 | 9 | 10 | 18 | 18 | 9 |  | 3 | 1 | 0 | 0 | [9 empty] | 93197
| Chandpur 115(Doreen) | 38 | 38 | 37 | 38 | 37 | 37 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 37 | 37 | 49 | 96 |  | 96 | 96 | 96 | 96 | 96 | 96 | 49 | 1286400
| Kanchan Purbachal Power Generation Ltd. | 18 | 18 | 18 | 17 | 18 | 5 | 18 | 17 | 17 | 18 | 17 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 17 | 18 | 419400
Mirsharai 150 MW (Oil)
Mirsharai 150 MW (Gas)
120 | Eastern Zone Total | 7542 | 7463 | 7434 | 7375 | 7273 | 6831 | 6681 | 6650 | 7017 | 7205 | 7377 | 7417 | 7181 | 7024 | 7159 | 7038 | 7100 | 7304 |  | 8368 | 8348 | 8348 | 8278 | 8265 | 8160 | 7529 | 178569836
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
Khulna 115 PP MW (KPCL-2)
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 10 | 10 | 10 | 10 | 10 | 4 | 0 | [10 empty] | 12 |  | 37 | 45 | 35 | 27 | 17 | 17 | 11 | 198240
| Khulna 225 MW CCPP | 224 | 224 | 226 | 224 | 226 | 220 | 155 | 170 | 223 | 222 | 221 | 218 | 219 | 215 | 160 | 120 | 120 | 120 |  | 227 | 227 | 227 | 225 | 226 | 226 | 225 | 4915200
129 | Rupsha 105 MW PP (Orion rupsha) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 37 | 37 | 37 | 37 | 37 | 40 | 56 | 56 | 56 |  | 60 | 75 | 75 | 75 | 75 | 75 | 37 | 1137120
130 | Mongla Orion 100 MW Solar PP |  |  |  |  | 0 | 1 | 8 | 33 | 52 | 85 | 24 | 24 | 21 | 29 | 41 | 32 | 10 | 1 | [8 empty] | 374400
131 | Rampal 1320 MW (BIFPCL) | [11 empty] | 107 | 100 | 100 | 100 | 100 | 100 | 100 | [8 empty] | 552270
132 | United Payra Power Ltd. | [25 empty] | 0 | 0
133 | Bhola Nutan Biddut BD LTD (GAS) | 224 | 224 | 222 | 225 | 227 | 227 | 226 | 226 | 225 | 226 | 224 | 218 | 220 | 220 | 220 | 218 | 222 | 218 |  | 222 | 220 | 220 | 220 | 226 | 227 | 225 | 5398309
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 32 | 32 | 16 | 16 | 16 | 0 |  |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 26 | 32 | 32 | 32 | 32 | 32 | 32 | 482496
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 84 | 84 | 82 | 85 | 86 | 72 | 86 | 86 | 86 | 86 | 84 | 83 | 83 | 83 | 82 | 82 | 84 | 82 |  | 84 | 86 | 85 | 84 | 85 | 86 | 86 | 2031872
140 | Bhola 33 MW PP (Venture) | 34 | 34 | 32 | 32 | 29 | 26 | 21 | 18 | 17 | 16 | 19 | 19 | 11 | 17 | 14 | 17 | 20 | 20 |  | 28 | 28 | 30 | 31 | 32 | 32 | 32 | 569850
141 | Noapara 100 MW PP (Bangla Trac) | 90 | 90 | 91 | 70 | 70 | 0 |  |  | 10 | 10 | 50 | 50 | 10 | 10 | 10 |  |  |  |  | 91 | 60 | 10 | 10 | 10 | 25 | 89 | 826560
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP | [17 empty] | 13 |  | 50 | 65 | 61 | 59 | 59 | 59 | 47 | 317312
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | [19 empty] | 15 | 15 | 15 |  |  |  | 0 | 28512
146 | Bheramara HVDC | 887 | 888 | 888 | 892 | 892 | 892 | 893 | 892 | 892 | 892 | 892 | 892 | 892 | 892 | 892 | 892 | 892 | 892 |  | 891 | 891 | 893 | 893 | 892 | 891 | 891 | 21555636
147 | Bheramara 410 MW CCPP | 185 | 190 | 195 | 200 | 200 | 205 | 205 | 135 | 120 | 120 | 255 | 250 | 245 | 235 | 235 | 230 | 230 | 235 |  | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 5160384
148 | Payra 1320 MW | 1080 | 1050 | 1000 | 980 | 980 | 950 | 950 | 880 | 890 | 830 | 820 | 820 | 820 | 790 | 780 | 780 | 780 | 780 |  | 930 | 1080 | 1090 | 1100 | 1100 | 1090 | 980 | 24524220
149
150 | Barapukuria TPP Unit-1 | 80 | 80 | 80 | 80 | 80 | 80 | 79 | 80 | 80 | 81 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 82 | 82 | 81 | 82 | 81 | 81 | 1947054
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 249 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 249 | 250 | 249 | 249 | 249 | 249 | 249 |  | 250 | 250 | 250 | 250 | 249 | 249 | 250 | 6062800
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [19 empty] | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 198464
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 3 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 11040
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 192 | 193 | 192 | 193 | 192 | 192 | 193 | 198 | 195 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 160 | 169 |  | 193 | 192 | 192 | 193 | 193 | 194 | 194 | 4827491
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
| Sirajgonj 225 MW CCPP Unit-2 (Oil) | 50 | 33 | 68 | 206 | 217 | 219 | 130 | 130 | 165 | 215 | 216 | 204 | 215 | 205 | 190 | 195 | 188 | 195 |  | 207 | 217 | 217 | 218 | 218 | 219 | 220 | 4663855
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 185 | 185 | 186 | 188 | 191 | 195 | 197 | 201 | 197 | 198 | 199 | 199 | 193 | 182 | 180 | 160 | 160 | 160 |  | 172 | 178 | 178 | 179 | 182 | 183 | 187 | 4711609
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 417 | 421 | 426 | 419 | 428 | 429 | 415 | 419 | 424 | 420 | 421 | 417 | 418 | 419 | 422 | 394 | 360 | 415 |  | 430 | 428 | 427 | 421 | 425 | 427 | 424 | 10038036
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 21 | 21 | 21 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 504240
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 223236
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP | 24 | 0 | [7 empty] | 10 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 24 |  | 24 | 32 | 32 | 32 | 32 | 24 | 24 | 296990
168 | Santahar 50 MW Peaking PP | 30 | 30 | 28 | 0 | [15 empty] | 33 | 33 | 33 | 33 | 27 | 27 | 27 | 251251
169 | Natore 52 MW PP (Rajlanka) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 193714
170 | Chapainawabganj 100 MW Peaking PP | [17 empty] | 9 |  | 56 | 81 | 81 | 81 | 81 | 45 | 22 | 358448
171 | Baghabari 200 MW PP (Paramount) | 153 | 160 | 160 | 0 |  |  |  |  | 27 | 10 | 33 | 50 | 10 | 10 | 12 |  |  |  |  | 77 | 80 | 10 | 10 | 10 | 13 | 131 | 1073682
| Bagura 113 MW PP (Confidence)-2 | 50 | 50 | 50 | 50 | 50 | 50 | 35 | 35 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 35 | 35 |  | 71 | 94 | 94 | 94 | 94 | 94 | 50 | 1519488
172 | Confidence Power Bogura Unit-1 113 MW | 55 | 55 | 55 | 55 | 55 | 55 | 35 | 60 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 35 | 35 | 35 |  | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 1642944
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | 56 | 56 | 56 | 56 | 56 | 56 | 35 | 34 | 49 | 56 | 52 | 54 | 57 | 56 | 56 | 56 | 80 | 92 |  | 92 | 91 | 91 | 92 | 92 | 92 | 56 | 1525785
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 0 | 1 | 4 | 4 | 5 | 4 | 5 | 5 | 4 | 3 | 2 | 1 | [8 empty] | 39408
178 | Energypac Power Venture Thakurgaon Ltd. | [15 empty] | 34 | 34 | 34 |  | 90 | 90 | 90 | 90 | 90 | 91 | 0 | 550464
178 | Intraco Solar 30 MW | [5 empty] | 0 | 2 | 7 | 17 | 29 | 19 | 23 | 28 | 15 | 21 | 8 | 5 | 1 | [8 empty] | 187220