## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2022-09-07 | Wednesday
|  | Date (day): | 2022-09-07 |  | Wednesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11944.6 | MW |  |  | (b) At Evening Peak Hour : |  | 13805 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2022-09-06 | 2022-09-07 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 230 | 230 | 230 | 230
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint.
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 250 | 260 | 260 | 260 | 105 |  | Gas shortage
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 76 | 83 | 80 | 83 |  | 25 | Engine problem
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 399 | 375 | 360 | 375 | 37 |  | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 189 | 190 | 190 | 190 | 170 |  | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 205 | 190 | 200 | 200 | 250 |  | Dirty fuel
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 41 | 66 | 50 | 66 | 34 |  | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 110 | 110 | 110 | 110 | 225 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 0 | 0 | 0 | 0 |  | 102 | Under maint
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 40 | 55 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 16 | 16 | 16 | 16 |  | 6 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 40 | 72 | 62 | 72 |  | 28 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 250 | 236 | 240 | 250 | 85 |  | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 40 | 92 | 50 | 92 |  | 10 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 54 | 17 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 17 | 115 | 17 | 115 | 34 |  | Fuel shortage
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 35 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 35 | 35 | 35 |  | 20 | Engine problem
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 49 | 52 | 51 | 52 |  | 28 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 12 | 12 | 10 | 12 |  | 21 | Engine problem
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 18 | 41 | 16 | 41 |  | 11 | Engine problem
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 195 | 278 | 260 | 280 |  | 20 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 220 | 225 | 150 | 225 |  | 75 | Engine problem
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 80 | 90 | 90 | 90 |  | 10 | Engine problem
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 80 | 90 | 80 | 90 |  | 10 | Engine problem
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 128 | 132 | 132 | 132 |  | 17 | Engine problem
36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 47 | 50 | 50 | 55 |  | Fuel shortage
37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 55 | 92 | 55 | 92 | 12 |  | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 72 | 162 | 72 | 162
39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 27 | 0 | 30 | 0
40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 11 | 0 | 11 | 44 |  | Fuel shortage
| Dhaka area Total |  |  |  |  | 6263 | 5847 | 2959 | 3499 | 3036 | 3528 | 1312 | 1073
41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 105 | 105 | 105 | 105 | 75 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 25 | 25 | 25 | 25
43 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 12 | 0 | 20 | 0
44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 19 | 25 | 25 | 25 |  | 25 | Engine problem
45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 151 | 153 | 150 | 153 |  | 77 | Low Water Level
46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | S/D due to HGPI
47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 69 | 105 | 55 | 105
49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 24 | 24 | 24 | 24 | 74 |  | Fuel shortage
50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 11 | 46 | 17 | 46 | 56 |  | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 33 | 78 | 33 | 78 |  | 22 | Engine problem
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 32 | 90 | 33 | 90 |  | 10 | Engine problem
53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 13 | 13 | 13 | 13 |  | 9 | Engine problem
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 10 | 31 | 10 | 20
54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 12 | 84 | 11 | 84 | 24 |  | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 161 | 161 | 160 | 161 | 139 |  | Fuel shortage
57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 17 | 36 | 35 | 36 |  | 18 | Engine prolem
58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 55 | 72 | 60 | 72 |  | 38 | Engine prolem
59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 38 | 100 | 38 | 100
60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 92 | 107 | 107 | 107 |  | 9 | Engine problem
| Mirsharai 150 MW |  | Gas/HSD | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0
| Chattogram area Total |  |  |  |  | 2442 | 2382 | 883 | 1255 | 926 | 1244 | 548 | 583
61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 200 | 206 | 205 | 206 | 15 |  | Gas shortage
63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 340 | 295 | 280 | 295 | 65 |  | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 320 | 295 | 280 | 300 | 60 |  | Gas shortage
| Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+136*1 | 284 | 284 | 0 | 0 | 0 | 0 |  |  | On test.
65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 38 | 45 | 43 | 45
66 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 55 | 51 | 56 | 55 | 55
67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 118 | 130 | 130 | 130 |  | 20 | Engine problem
70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 21 | 34 | 25 | 34 |  | 18 | Engine problem
71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 90 | 50 | 80 |  | 83 | Machine problem
72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 34 | 156 | 17 | 100
73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 19 | 19
74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 10 | 10 | 10 | 10
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 127 | 156 | 143 | 166
75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 16 | 33 | 33 | 33
76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 35 | 8 | 35 | 17 |  | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 21 | 21 | 21 | 21 |  | 4 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 191 | 193 | 100 | 193 |  | 7 | Engine problem
79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 50 | 17 | 50 | 64 |  | Fuel shortage
80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 96 | 115 | 105 | 115
81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 17 |  | 37 | 33 kV feeder fault
82 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 35 | 96 | 34 | 96 | 19 |  | Fuel shortage
| Cumilla Area Total |  |  |  |  | 3193 | 3169 | 1721 | 2111 | 1651 | 2059 | 561 | 169
83 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 64 | 111 | 70 | 110 | 92 |  | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 22 |  | Gas shortage
85 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0 |  | 8 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1 | 0 | 1.6 | 0
87 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 98 | 87 | 80 | 90 | 110 |  | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 107 | 115 | 90 | 115
89 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 8 | 0 | 50 | 0
90 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 12 | 12 |  | 10 | Engine problem
| Mymensingh Area Total |  |  |  |  | 717 | 614 | 290 | 325 | 303.6 | 327 | 114 | 18
91 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 43 | 43 | 43 |  | 27 | Machine problem.
92 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 41 | 41 | 41 | 41 |  | 49 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 | 163 |  | Gas shortage
94 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 5 | 5 | 30 | 30
96 | Fenchuganj 44MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 6 | 6 | 20 | 20 |  | 30
97 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 5 | 6 | 11
98 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 58 | 63 | 60 | 63
99 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 81 | 81 | 81 | 81
100 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
101 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 0 | 0 | 0 |  | 231 | Under Maint.
102 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Gas shortage
103 | Sylhet 50MW PP (EPL) |  | Gas | NENP | 27*2 | 50 | 50 | 23 | 23 | 23 | 23 | 27 |  | Gas shortage
104 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 24 | 24 | 24
105 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 320 | 300 | 300 | 300 | 41 |  | FGMO
106 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 403 | 403 | 400 | 400
107 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 9 | 10 | 10 | 10
108 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 260 | 260 | 400 | 400
| Sylhet Area Total |  |  |  |  | 2522 | 2477 | 1273 | 1264 | 1438 | 1446 | 251 | 767
109 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 891 | 891 | 908 | 908 |  |  | .
110 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 0 | 0 | 0 | 0 | 115 |  | Fuel shortage
111 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 10 | 0 | 40 |  | 14 | Engine problem
112 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 145 | 225 | 225
113 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 60 |  | 49 | Engine problem
114 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 80 | 180 | 200 | 210 |  | Gas shortage
115 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 0 | 0 | 0 | 40 |  | Fuel shortage
116 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 85 | 89 | 20 | 90 |  | 10 | Engine problem
117 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 35 | 70 | 35 | 70 | 35 |  | Fuel shortage
118 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 32 | 15 | 32 | 73 |  | Fuel shortage
119 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 87 | 0 | 100 | 0
| Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 2388 | 2384 | 1098 | 1317 | 1483 | 1625 | 489 | 73
120 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 32 | 32 | 32 |  |  | Line O/L
121 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 23 | 38 | 20 | 38
122 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 0 | 30 | 65 | 65 |  | 129 | Machine problem
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
123 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 60 | 430 | 1110 | 1110 |  |  | Line O/L
124 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 0 | 139 | 220 | 220
125 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 0 | 17 |  |  | Line O/L
| Barisal Area Total |  |  |  |  | 1958 | 1958 | 83 | 669 | 1447 | 1482 | 0 | 129
126 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
127 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 32 | 0 | 32 |  | 20 | Engine problem
128 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 0 |  | 71 | Engine problem
129 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
130 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage
131 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 32 | 16 | 32 |  | 18 | Engine problem
132 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 206 | 206 | 194 | 200 | 10 |  | Gas shortage
133 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 211 | 219 | 220 | 220
134 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 204 | 202 | 195 | 202 | 18 |  | Gas shortage
135 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 414 | 420 | 414 | 414
136 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 26 | 0 | 26 |  | 24 | Engine problem
137 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 21 | 22 | 22 | 22
138 | Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
139 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 10 | 11
140 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 43 | 8 | 8 | 44 |  | Fuel shortage
141 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 80 | 0 | 80 |  | 24 | Engine problem
142 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 165 | 164 | 60 | 164 |  | 36 | Engine problem
143 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 50 | 94 | 50 | 94 |  | 19 | Engine problem
144 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 75 | 75 | 60 | 75 |  | 38 | Engine problem
145 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 2 | 0 | 6 | 0
| Rajshahi Area Total |  |  |  |  | 2199 | 2129 | 1359 | 1626 | 1255 | 1580 | 293 | 250
146 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 81 | 82 | 80 | 82
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
147 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 250 | 250 | 250 | 250 | 24
148 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
149 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
150 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 56 | 92 | 55 | 92 |  | 21 | Engine problem
151 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 3 | 0 | 8 | 0
152 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 34 | 90 | 0 | 90 |  | 25 | Fuel shortage
| Intraco Solar 30 MW |  | Solar | IPP | 0 | 0 | 0 | 22 | 0 | 12 | 0
| Rangpur Area Total |  |  |  |  | 800 | 720 | 446 | 514 | 405 | 514 | 64 | 131
| Total |  |  |  |  | 22482 | 21680 | 10112 | 12580 | 11944.6 | 13805 | 3632 | 3193
A. |  | 2022-09-06 | (Yesterday) |  |  |  |  | Tuesday
1 | Highest Generation : |  |  | 13342 | MW at | 23:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 9749 | MW at | 9:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 13800 | MW
3 | Day peak Generation : |  |  | 10112 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 13294.26 | MW
4 | Evening peak Generation : |  |  | 12580 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 1124 | MW
5 | Total Energy Generation : |  | 277.9213 | MKWHr | By Solar | 0.99482 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Gas : | 133.8349 | MKWHr |  | By Oil: | 91.3571 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 25.6366 | MKWHr |  | By Hydro: | 3.5006 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 3632 | MW | Dhaka | 4705.32 | 4555.32 |  | 150 |  | 18:00 |  | 292.1393
|  |  | For Plants S/D or M/C prob = |  |  | 3193 | MW | Chittagong | 1362.8 | 1312.8 |  | 50 |  | 19:00 |  | 1310
|  |  | Total = |  |  | 6825 | MW | Khulna | 1632.04 | 1372.04 |  | 260 |  | 19:30 |  | 1211
7 | Total Gas Supplied : |  |  | 1014.44 | MMCFD |  |  | Rajshahi | 1335.2 | 1175.2 |  | 160 |  | 20:00 |  | 1138
8 | Fuel Cost : | i) Gas : | Taka | 153633778.824 | ii) Oil : | Taka | 1346424757.03 | Comilla | 1368 | 1216 |  | 152 |  | 21:00 |  | 1124
|  | iii) Coal : |  | 184198812.19 | Total | Taka | 1684257348.044 | Mymensingh | 1079 | 857 |  | 222 |  | 22:00 |  | 548.3371
9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0 | MKWHr. | Sylhet | 554 | 554 |  | 0 |  | 23:00 |  | 237.7664
| ii) During Peak Demand : |  |  | 825 | MW (E to W) at | 21:00 | hrs | Barisal | 384.9 | 384.9 |  | 0 |  | 24:00 |  | 947.3791
| iii) Maximum : |  |  | 825 | MW at | 21:00 | hrs | Rangpur | 873 | 743 |  | 130
10 | Maximum Temperature in Dhaka was |  |  |  | 32.5° C |  |  | Total | 13294.26 | 12170.26 |  | 1124
B. |  | 2022-09-07 | (Today) |  |  |  | Wednesday |  |  | Probable max. temperature in Dhaka |  |  | 35.4° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 13800 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 13805 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 12000 | MW
4 | Reserve(Generation end) |  |  |  | 5 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 287.4617 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 10924 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 19.9055 | MKWHr. | ii) HVDC Flow at Peak Time |  | 891 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.6918 | MKWHr. | iii) Maximum HVDC Flow : |  | 902 | MW at | 24:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 96.23 |  | (b) Today: | 96.27 |  | (c) Rule Curve: |  | 100.38
.

## YesterdayGen
2022-09-06
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 230 | 0 | 260 | 90 | 0 | 347 | 152 |  | 0 | 210 | 115 | 42 | 0 | 55 | 170 | 0 | 0 | 40 | 40 | 50 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 16 | 25 | 28 | 33 | 15 | 16 | 0 | 80 | 70 | 105 | 0 | 25 | 0 | 0 | 0 | 0 |  | 9 | 24 | 13 | 33 | 12 | 25 | 13 | 35 | 0 | 0 | 0 | 280 | 275 | 208 | 8 | 0 | 45 | 56 | 0 | 51 | 0 | 22 | 8 | 19 | 10 | 33 | 21 | 100 | 142 | 0 | 0 | 0 | 43 | 41 | 47 | 0 | 0 | 0 | 63 | 81 | 0 | 0 | 0 | 17 | 10 | 290 | 0 | 8 | 191 | 210 | 225 | 80 | 95 | 80 | 149 | 0 | 33 | 17 | 145 | 401 | 107 | 50 | 69 | 0 | 161 | 36 | 73 | 17 | 95 | 38 | 401 | 55 | 0 | 17 | 107 | 0 | 17 | 0 | 38 | 17 | 0 | 0 | 0 |  | 891 | 0 | 235 | 0 | 0 | 225 | 0 | 0 | 11 | 35 | 0 | 85 | 31 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 8 | 0 | 22 | 0 | 8 | 81 | 0 | 250 | 0 | 0 | 194 | 0 | 0 | 219 | 0 | 90 | 188 | 0 | 425 | 37 | 155 | 50 | 0 | 56 | 0 | 0 | 95 | 950 | 226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102 | 0 |  | 7267 | 4709 | 11976 | 3942 | 891 | 1866 | 821 | 2200 | 1383 | 150 | 444 | 398 | 100 | 0 | 667.2203 | 96.21
2:00 | 0 | 0 | 230 | 0 | 260 | 91 | 0 | 346 | 151 |  | 0 | 210 | 118 | 41 | 0 | 55 | 170 | 0 | 0 | 39 | 40 | 50 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 16 | 25 | 28 | 33 | 15 | 16 | 0 | 80 | 70 | 105 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 24 | 13 | 33 | 12 | 25 | 13 | 38 | 0 | 0 | 0 | 280 | 275 | 210 | 8 | 0 | 45 | 56 | 0 | 51 | 0 | 22 | 8 | 19 | 10 | 33 | 21 | 98 | 140 | 0 | 0 | 0 | 43 | 41 | 47 | 13 | 0 | 0 | 62 | 81 | 0 | 0 | 0 | 23 | 10 | 270 | 24 | 8 | 190 | 195 | 177 | 80 | 95 | 80 | 149 | 0 | 33 | 17 | 143 | 401 | 108 | 50 | 69 | 0 | 161 | 36 | 73 | 16 | 97 | 38 | 400 | 55 | 0 | 17 | 107 | 0 | 17 | 0 | 35 | 17 | 0 | 0 | 0 |  | 891 | 0 | 235 | 0 | 0 | 227 | 0 | 0 | 11 | 28 | 0 | 86 | 30 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 8 | 81 | 0 | 249 | 0 | 0 | 194 | 0 | 0 | 220 | 0 | 89 | 190 | 0 | 427 | 37 | 120 | 50 | 0 | 56 | 0 | 0 | 95 | 950 | 227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102 | 0 |  | 7225 | 4649 | 11874 | 3966 | 891 | 1873 | 736 | 2183 | 1382 | 150 | 447 | 368 | 98 | 0 | 162.1972 | 96.22
3:00 | 0 | 0 | 230 | 0 | 260 | 92 | 0 | 347 | 152 |  | 0 | 210 | 120 | 41 | 0 | 55 | 170 | 0 | 0 | 40 | 40 | 50 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 16 | 25 | 28 | 33 | 15 | 16 | 0 | 81 | 70 | 105 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 24 | 13 | 33 | 12 | 25 | 13 | 39 | 0 | 0 | 0 | 280 | 275 | 209 | 8 | 0 | 45 | 56 | 0 | 51 | 0 | 22 | 8 | 19 | 10 | 33 | 21 | 96 | 149 | 0 | 0 | 0 | 43 | 41 | 47 | 39 | 0 | 0 | 63 | 81 | 0 | 0 | 0 | 23 | 10 | 290 | 24 | 8 | 191 | 194 | 75 | 80 | 95 | 80 | 149 | 0 | 33 | 17 | 143 | 401 | 107 | 50 | 69 | 0 | 161 | 36 | 73 | 16 | 96 | 38 | 400 | 55 | 0 | 17 | 107 | 0 | 17 | 0 | 35 | 17 | 0 | 0 | 0 |  | 891 | 0 | 240 | 0 | 0 | 226 | 0 | 0 | 11 | 28 | 0 | 86 | 29 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 8 | 81 | 0 | 250 | 0 | 0 | 193 | 0 | 0 | 220 | 0 | 89 | 193 | 0 | 425 | 37 | 10 | 50 | 0 | 56 | 0 | 0 | 95 | 920 | 226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101 | 0 |  | 7182 | 4511 | 11693 | 3983 | 891 | 1920 | 525 | 2181 | 1352 | 151 | 446 | 368 | 96 | 0 | 126.2558 | 96.22
4:00 | 0 | 0 | 230 | 0 | 260 | 92 | 0 | 351 | 163 |  | 0 | 215 | 122 | 41 | 0 | 55 | 170 | 0 | 0 | 40 | 40 | 50 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 16 | 25 | 28 | 33 | 16 | 16 | 0 | 81 | 70 | 105 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 24 | 13 | 33 | 12 | 25 | 13 | 39 | 0 | 0 | 0 | 280 | 275 | 210 | 8 | 0 | 45 | 56 | 0 | 51 | 0 | 22 | 8 | 19 | 10 | 33 | 21 | 94 | 149 | 0 | 0 | 0 | 43 | 41 | 47 | 45 | 0 | 0 | 64 | 81 | 0 | 0 | 0 | 23 | 10 | 280 | 24 | 8 | 190 | 195 | 11 | 80 | 95 | 80 | 143 | 0 | 32 | 17 | 138 | 401 | 108 | 50 | 69 | 0 | 161 | 36 | 73 | 16 | 96 | 38 | 400 | 55 | 0 | 17 | 107 | 0 | 17 | 0 | 34 | 17 | 0 | 0 | 0 |  | 892 | 0 | 245 | 0 | 0 | 226 | 0 | 0 | 11 | 28 | 0 | 86 | 28 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 8 | 82 | 0 | 250 | 0 | 0 | 193 | 0 | 0 | 205 | 0 | 80 | 196 | 0 | 429 | 37 | 10 | 50 | 0 | 56 | 0 | 0 | 95 | 900 | 226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107 | 0 |  | 7125 | 4486 | 11611 | 3998 | 892 | 1937 | 451 | 2170 | 1339 | 151 | 431 | 353 | 94 | 0 | 82.0202 | 96.22
5:00 | 0 | 0 | 230 | 0 | 260 | 92 | 0 | 353 | 160 |  | 0 | 215 | 120 | 41 | 0 | 55 | 170 | 0 | 0 | 40 | 40 | 17 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 16 | 25 | 28 | 33 | 17 | 16 | 0 | 82 | 70 | 105 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 24 | 13 | 33 | 12 | 25 | 13 | 39 | 0 | 0 | 0 | 280 | 275 | 210 | 8 | 0 | 45 | 56 | 0 | 51 | 0 | 22 | 8 | 19 | 10 | 33 | 21 | 94 | 149 | 0 | 0 | 0 | 43 | 41 | 47 | 48 | 0 | 0 | 65 | 81 | 0 | 0 | 0 | 23 | 10 | 270 | 24 | 8 | 190 | 195 | 11 | 40 | 95 | 25 | 143 | 0 | 32 | 17 | 138 | 401 | 108 | 50 | 69 | 0 | 161 | 36 | 73 | 16 | 95 | 38 | 401 | 55 | 0 | 17 | 107 | 0 | 17 | 0 | 34 | 17 | 0 | 0 | 0 |  | 891 | 0 | 250 | 0 | 0 | 226 | 0 | 0 | 11 | 28 | 0 | 86 | 27 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 8 | 81 | 0 | 250 | 0 | 0 | 193 | 0 | 0 | 193 | 0 | 50 | 197 | 0 | 431 | 37 | 0 | 50 | 0 | 56 | 0 | 0 | 95 | 870 | 227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 |  | 6990 | 4403 | 11393 | 4009 | 891 | 1927 | 316 | 2169 | 1301 | 152 | 419 | 308 | 94 | 0 | 52.5298 | 96.23
6:00 | 0 | 0 | 230 | 0 | 260 | 92 | 0 | 359 | 166 |  | 0 | 215 | 125 | 41 | 0 | 55 | 170 | 0 | 0 | 40 | 40 | 17 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 16 | 25 | 28 | 33 | 17 | 16 | 0 | 83 | 70 | 105 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 24 | 13 | 33 | 12 | 25 | 13 | 39 | 0 | 0 | 0 | 280 | 275 | 208 | 8 | 0 | 45 | 56 | 0 | 51 | 0 | 21 | 8 | 19 | 10 | 33 | 21 | 88 | 152 | 0 | 0 | 0 | 43 | 41 | 47 | 49 | 0 | 0 | 64 | 81 | 0 | 0 | 0 | 23 | 10 | 265 | 24 | 8 | 50 | 145 | 0 | 0 | 94 | 0 | 138 | 0 | 32 | 17 | 100 | 401 | 0 | 50 | 17 | 0 | 161 | 36 | 58 | 0 | 97 | 38 | 401 | 54 | 0 | 17 | 107 | 0 | 17 | 0 | 34 | 17 | 0 | 0 | 0 |  | 892 | 0 | 250 | 0 | 0 | 188 | 0 | 0 | 4 | 28 | 0 | 87 | 23 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 8 | 82 | 0 | 250 | 0 | 0 | 192 | 0 | 0 | 193 | 0 | 0 | 197 | 0 | 428 | 37 | 0 | 35 | 0 | 56 | 0 | 0 | 35 | 850 | 226 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 100 | 0 |  | 6497 | 4208 | 10705 | 4015 | 892 | 1926 | 50 | 1810 | 1282 | 153 | 381 | 300 | 88 | 1 | 0 | 96.23
7:00 | 0 | 0 | 230 | 0 | 260 | 92 | 0 | 363 | 167 |  | 0 | 215 | 125 | 38 | 0 | 55 | 170 | 0 | 0 | 40 | 40 | 17 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 16 | 25 | 28 | 33 | 15 | 16 | 0 | 82 | 70 | 105 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 24 | 13 | 33 | 12 | 7 | 13 | 35 | 0 | 0 | 0 | 330 | 320 | 205 | 8 | 0 | 45 | 56 | 0 | 51 | 0 | 21 | 8 | 19 | 10 | 33 | 21 | 78 | 103 | 0 | 0 | 0 | 43 | 41 | 47 | 48 | 0 | 0 | 62 | 81 | 0 | 0 | 0 | 23 | 10 | 305 | 16 | 8 | 50 | 145 | 0 | 0 | 95 | 0 | 122 | 6 | 32 | 17 | 107 | 405 | 0 | 46 | 18 | 1 | 161 | 36 | 55 | 0 | 98 | 38 | 392 | 17 | 4 | 17 | 107 | 0 | 17 | 5 | 35 | 17 | 0 | 0 | 0 |  | 892 | 0 | 250 | 0 | 0 | 180 | 0 | 0 | 0 | 20 | 0 | 84 | 21 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 8 | 82 | 0 | 250 | 0 | 0 | 194 | 0 | 0 | 194 | 0 | 0 | 199 | 0 | 419 | 37 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 790 | 222 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 101 | 0 |  | 6498 | 4117 | 10615 | 4046 | 892 | 1947 | 50 | 1718 | 1223 | 152 | 374 | 289 | 78 | 40 | 0 | 96.23
8:00 | 0 | 0 | 235 | 0 | 260 | 84 | 0 | 363 | 174 |  | 0 | 215 | 122 | 41 | 0 | 55 | 170 | 0 | 0 | 40 | 40 | 17 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 16 | 25 | 28 | 33 | 15 | 16 | 0 | 83 | 70 | 105 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 24 | 13 | 33 | 12 | 24 | 13 | 13 | 0 | 0 | 0 | 315 | 310 | 209 | 8 | 0 | 45 | 56 | 0 | 51 | 0 | 21 | 8 | 19 | 10 | 27 | 21 | 114 | 68 | 0 | 0 | 0 | 43 | 41 | 5 | 6 | 0 | 0 | 62 | 81 | 0 | 0 | 0 | 23 | 10 | 310 | 21 | 8 | 0 | 165 | 10 | 0 | 113 | 25 | 117 | 12 | 32 | 17 | 117 | 403 | 0 | 46 | 55 | 2 | 161 | 36 | 55 | 0 | 95 | 38 | 394 | 45 | 5 | 17 | 107 | 0 | 17 | 7 | 35 | 17 | 0 | 0 | 0 |  | 891 | 0 | 240 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 85 | 19 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 8 | 81 | 0 | 250 | 0 | 0 | 198 | 0 | 0 | 194 | 0 | 0 | 202 | 0 | 416 | 37 | 0 | 50 | 0 | 56 | 0 | 0 | 55 | 770 | 224 | 0 | 0 | 1 | 24 | 0 | 0 | 0 | 101 | 0 |  | 6498 | 4138 | 10636 | 3992 | 891 | 1839 | 35 | 1900 | 1202 | 153 | 384 | 269 | 114 | 51 | 0 | 96.24
9:00 | 0 | 0 | 147 | 0 | 260 | 81 | 0 | 392 | 196 |  | 0 | 195 | 125 | 41 | 0 | 55 | 250 | 0 | 0 | 40 | 40 | 17 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 16 | 25 | 28 | 33 | 14 | 16 | 0 | 82 | 70 | 105 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 21 | 13 | 33 | 12 | 25 | 13 | 3 | 0 | 0 | 0 | 315 | 300 | 206 | 8 | 0 | 41 | 55 | 0 | 51 | 0 | 21 | 8 | 19 | 0 | 20 | 21 | 114 | 69 | 0 | 0 | 0 | 43 | 41 | 5 | 6 | 0 | 0 | 61 | 81 | 0 | 0 | 0 | 23 | 9 | 290 | 24 | 8 | 110 | 195 | 100 | 50 | 152 | 25 | 112 | 0 | 32 | 17 | 112 | 387 | 67 | 46 | 69 | 4 | 161 | 36 | 55 | 0 | 97 | 38 | 400 | 55 | 5 | 24 | 107 | 0 | 17 | 10 | 35 | 18 | 0 | 0 | 0 |  | 569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 10 | 80 | 0 | 250 | 0 | 0 | 195 | 0 | 0 | 193 | 0 | 0 | 195 | 0 | 414 | 0 | 0 | 50 | 0 | 56 | 0 | 2 | 55 | 760 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 30 | 0 |  | 6847 | 2902 | 9749 | 3638 | 569 | 1560 | 285 | 2024 | 1120 | 152 | 193 | 265 | 114 | 22 | 50.6866 | 96.24
10:00 | 0 | 0 | 230 | 0 | 260 | 80 | 0 | 406 | 206 |  | 0 | 195 | 125 | 41 | 0 | 55 | 263 | 0 | 0 | 40 | 40 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 35 | 16 | 25 | 24 | 33 | 14 | 16 | 0 | 81 | 70 | 105 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 24 | 13 | 33 | 12 | 2 | 13 | 5 | 0 | 0 | 0 | 300 | 290 | 204 | 8 | 0 | 41 | 51 | 0 | 51 | 0 | 21 | 8 | 19 | 0 | 15 | 21 | 118 | 65 | 0 | 0 | 1 | 43 | 41 | 5 | 6 | 0 | 0 | 61 | 81 | 0 | 0 | 0 | 23 | 9 | 310 | 24 | 8 | 191 | 193 | 222 | 80 | 107 | 80 | 122 | 20 | 32 | 17 | 115 | 402 | 101 | 46 | 69 | 3 | 161 | 17 | 55 | 0 | 94 | 38 | 260 | 55 | 10 | 72 | 107 | 0 | 17 | 7 | 35 | 18 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 10 | 81 | 0 | 250 | 0 | 0 | 204 | 0 | 0 | 203 | 0 | 0 | 193 | 0 | 416 | 0 | 45 | 50 | 0 | 56 | 0 | 2 | 55 | 0 | 0 | 0 | 0 | 1 | 0 | 17 | 0 | 0 | 0 | 19 |  | 7103 | 1639 | 8742 | 3590 | 0 | 1608 | 618 | 1985 | 331 | 151 | 203 | 278 | 118 | 63 | 2202.5643 | 96.24
11:00 | 0 | 0 | 230 | 0 | 250 | 76 | 0 | 405 | 202 |  | 0 | 195 | 118 | 41 | 0 | 55 | 261 | 0 | 0 | 40 | 40 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 35 | 16 | 25 | 24 | 33 | 14 | 16 | 0 | 81 | 70 | 105 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 24 | 13 | 33 | 12 | 18 | 13 | 12 | 0 | 0 | 0 | 345 | 330 | 202 | 8 | 0 | 40 | 52 | 0 | 51 | 0 | 21 | 8 | 19 | 10 | 16 | 21 | 126 | 64 | 0 | 0 | 1 | 43 | 41 | 5 | 6 | 0 | 0 | 60 | 81 | 0 | 0 | 0 | 23 | 9 | 310 | 24 | 8 | 191 | 195 | 224 | 80 | 106 | 80 | 124 | 4 | 32 | 17 | 118 | 404 | 103 | 30 | 69 | 3 | 161 | 17 | 55 | 0 | 94 | 38 | 260 | 54 | 9 | 72 | 107 | 0 | 17 | 13 | 35 | 18 | 0 | 0 | 0 |  | 519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 11 | 81 | 0 | 250 | 0 | 0 | 205 | 0 | 0 | 213 | 0 | 77 | 198 | 0 | 414 | 0 | 161 | 50 | 0 | 56 | 0 | 4 | 55 | 0 | 0 | 0 | 0 | 2 | 84 | 34 | 0 | 0 | 0 | 16 |  | 7182 | 2470 | 9652 | 3677 | 519 | 1602 | 813 | 2009 | 331 | 151 | 213 | 288 | 126 | 136 | 1385.1272 | 96.25
12:00 | 0 | 0 | 230 | 0 | 250 | 76 | 0 | 399 | 189 |  | 0 | 205 | 110 | 41 | 0 | 40 | 250 | 0 | 0 | 40 | 40 | 17 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 16 | 25 | 24 | 33 | 12 | 18 | 0 | 81 | 70 | 105 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 24 | 11 | 33 | 12 | 19 | 13 | 10 | 0 | 0 | 0 | 340 | 320 | 200 | 8 | 0 | 38 | 51 | 0 | 51 | 0 | 21 | 8 | 19 | 10 | 16 | 21 | 127 | 64 | 0 | 0 | 1 | 43 | 41 | 5 | 6 | 0 | 0 | 58 | 81 | 0 | 0 | 0 | 23 | 9 | 320 | 16 | 8 | 191 | 195 | 220 | 80 | 98 | 80 | 128 | 12 | 32 | 34 | 118 | 403 | 107 | 0 | 69 | 4 | 161 | 17 | 55 | 0 | 96 | 38 | 260 | 55 | 8 | 72 | 92 | 0 | 17 | 27 | 35 | 0 | 0 | 0 | 0 |  | 891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 81 | 0 | 250 | 0 | 0 | 206 | 0 | 0 | 211 | 0 | 85 | 204 | 0 | 414 | 35 | 165 | 50 | 0 | 56 | 0 | 3 | 75 | 60 | 0 | 0 | 0 | 2 | 87 | 34 | 0 | 0 | 0 | 22 |  | 7126 | 2986 | 10112 | 3635 | 891 | 1602 | 821 | 2044 | 391 | 151 | 211 | 284 | 127 | 166 | 1234.9105 | 96.25
13:00 | 0 | 0 | 230 | 0 | 250 | 76 | 0 | 394 | 188 |  | 0 | 205 | 110 | 41 | 0 | 40 | 250 | 0 | 0 | 33 | 40 | 17 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 0 | 25 | 24 | 33 | 12 | 24 | 0 | 81 | 70 | 105 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 24 | 11 | 33 | 12 | 24 | 13 | 13 | 0 | 0 | 0 | 320 | 305 | 204 | 8 | 0 | 38 | 54 | 0 | 51 | 0 | 21 | 8 | 19 | 10 | 16 | 21 | 140 | 40 | 0 | 0 | 1 | 43 | 41 | 5 | 6 | 0 | 0 | 60 | 81 | 0 | 0 | 0 | 23 | 10 | 305 | 16 | 8 | 194 | 195 | 221 | 80 | 97 | 80 | 132 | 20 | 32 | 17 | 115 | 401 | 107 | 0 | 69 | 4 | 161 | 17 | 55 | 0 | 94 | 38 | 260 | 55 | 13 | 72 | 107 | 0 | 17 | 25 | 35 | 0 | 0 | 0 | 0 |  | 891 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 11 | 80 | 0 | 250 | 0 | 0 | 205 | 0 | 0 | 213 | 0 | 70 | 205 | 0 | 416 | 53 | 161 | 50 | 0 | 56 | 0 | 3 | 75 | 190 | 0 | 0 | 0 | 2 | 46 | 34 | 0 | 0 | 0 | 21 |  | 7069 | 3083 | 10152 | 3559 | 891 | 1597 | 806 | 2062 | 520 | 151 | 218 | 286 | 140 | 135 | 1150.1256 | 96.25
14:00 | 0 | 0 | 230 | 0 | 250 | 74 | 0 | 250 | 221 |  | 0 | 200 | 115 | 43 | 0 | 40 | 285 | 0 | 0 | 40 | 40 | 17 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 0 | 25 | 24 | 33 | 12 | 24 | 0 | 81 | 70 | 105 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 24 | 11 | 33 | 12 | 16 | 13 | 10 | 0 | 0 | 0 | 325 | 315 | 195 | 8 | 0 | 39 | 54 | 0 | 51 | 0 | 29 | 8 | 19 | 10 | 15 | 21 | 144 | 38 | 0 | 0 | 1 | 43 | 41 | 5 | 6 | 0 | 0 | 64 | 81 | 0 | 0 | 0 | 23 | 10 | 300 | 24 | 8 | 195 | 195 | 225 | 80 | 97 | 80 | 131 | 18 | 32 | 17 | 110 | 402 | 107 | 17 | 69 | 4 | 161 | 17 | 55 | 0 | 94 | 38 | 260 | 58 | 8 | 75 | 107 | 0 | 17 | 33 | 35 | 0 | 0 | 0 | 0 |  | 891 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 80 | 0 | 250 | 0 | 0 | 206 | 0 | 0 | 213 | 0 | 89 | 206 | 0 | 415 | 53 | 162 | 50 | 0 | 56 | 0 | 6 | 75 | 270 | 0 | 0 | 31 | 2 | 69 | 34 | 0 | 0 | 0 | 11 |  | 7036 | 3257 | 10293 | 3469 | 891 | 1619 | 831 | 2127 | 600 | 151 | 228 | 294 | 144 | 152 | 1112.341 | 96.25
15:00 | 0 | 0 | 230 | 0 | 250 | 74 | 0 | 359 | 194 |  | 0 | 200 | 110 | 40 | 0 | 40 | 255 | 0 | 0 | 40 | 40 | 17 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 0 | 25 | 24 | 33 | 12 | 24 | 0 | 81 | 70 | 105 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 24 | 12 | 33 | 12 | 23 | 13 | 6 | 0 | 0 | 0 | 325 | 320 | 186 | 8 | 0 | 39 | 53 | 0 | 51 | 0 | 34 | 8 | 19 | 10 | 16 | 15 | 92 | 42 | 0 | 0 | 1 | 43 | 41 | 5 | 6 | 0 | 0 | 64 | 81 | 0 | 0 | 0 | 23 | 10 | 310 | 24 | 8 | 195 | 195 | 225 | 80 | 97 | 80 | 132 | 17 | 32 | 17 | 112 | 376 | 107 | 32 | 69 | 2 | 161 | 17 | 55 | 0 | 93 | 38 | 260 | 64 | 18 | 72 | 107 | 0 | 17 | 15 | 34 | 0 | 0 | 0 | 0 |  | 891 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 4 | 0 | 0 | 0 | 27 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 80 | 0 | 250 | 0 | 0 | 205 | 0 | 0 | 211 | 0 | 90 | 205 | 0 | 415 | 53 | 163 | 50 | 15 | 56 | 0 | 5 | 75 | 390 | 0 | 0 | 54 | 1 | 34 | 34 | 0 | 0 | 0 | 15 |  | 7023 | 3480 | 10503 | 3515 | 891 | 1594 | 833 | 2282 | 720 | 151 | 226 | 302 | 92 | 108 | 1103.1253 | 96.26
16:00 | 0 | 0 | 230 | 0 | 250 | 74 | 0 | 381 | 180 |  | 0 | 200 | 110 | 41 | 0 | 40 | 243 | 0 | 0 | 40 | 40 | 17 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 16 | 25 | 24 | 33 | 12 | 24 | 0 | 83 | 70 | 105 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 24 | 12 | 33 | 12 | 25 | 13 | 7 | 0 | 0 | 0 | 310 | 305 | 174 | 8 | 0 | 39 | 52 | 0 | 51 | 0 | 34 | 8 | 19 | 10 | 21 | 21 | 82 | 43 | 0 | 0 | 0 | 43 | 41 | 5 | 6 | 0 | 0 | 64 | 81 | 0 | 0 | 0 | 23 | 10 | 300 | 16 | 5 | 195 | 185 | 221 | 80 | 106 | 80 | 132 | 7 | 32 | 17 | 122 | 403 | 96 | 32 | 69 | 1 | 161 | 27 | 55 | 0 | 94 | 38 | 260 | 54 | 10 | 72 | 107 | 0 | 17 | 4 | 35 | 0 | 0 | 0 | 0 |  | 892 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 14 | 0 | 0 | 0 | 27 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 11 | 80 | 0 | 250 | 0 | 0 | 206 | 0 | 0 | 214 | 0 | 90 | 209 | 0 | 420 | 53 | 157 | 50 | 15 | 56 | 0 | 3 | 75 | 470 | 0 | 0 | 54 | 1 | 41 | 34 | 0 | 0 | 0 | 7 |  | 6971 | 3609 | 10580 | 3532 | 892 | 1574 | 823 | 2285 | 800 | 153 | 264 | 315 | 82 | 74 | 940.0065 | 96.26
17:00 | 0 | 0 | 230 | 0 | 250 | 72 | 0 | 380 | 183 |  | 0 | 200 | 110 | 44 | 0 | 54 | 240 | 0 | 0 | 45 | 40 | 17 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 16 | 25 | 24 | 33 | 12 | 26 | 0 | 83 | 70 | 105 | 0 | 25 | 0 | 0 | 0 | 0 |  | 6 | 24 | 11 | 33 | 12 | 24 | 13 | 12 | 0 | 0 | 0 | 310 | 305 | 167 | 8 | 0 | 43 | 56 | 0 | 51 | 0 | 34 | 8 | 19 | 10 | 21 | 21 | 74 | 41 | 0 | 0 | 0 | 43 | 41 | 5 | 6 | 0 | 0 | 61 | 81 | 0 | 0 | 0 | 23 | 10 | 290 | 24 | 5 | 195 | 195 | 137 | 80 | 107 | 80 | 132 | 1 | 32 | 67 | 128 | 403 | 97 | 47 | 95 | 1 | 161 | 36 | 55 | 0 | 98 | 38 | 261 | 54 | 4 | 80 | 107 | 0 | 17 | 0 | 44 | 0 | 0 | 0 | 0 |  | 892 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 10 | 0 | 0 | 0 | 25 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 0 | 80 | 0 | 250 | 0 | 0 | 206 | 0 | 0 | 216 | 0 | 50 | 210 | 0 | 416 | 53 | 163 | 94 | 15 | 90 | 0 | 2 | 75 | 500 | 7 | 0 | 54 | 0 | 13 | 34 | 0 | 0 | 0 | 3 |  | 7015 | 3648 | 10663 | 3519 | 892 | 1577 | 705 | 2527 | 830 | 153 | 266 | 312 | 74 | 24 | 771.3583 | 96.26
18:00 | 0 | 0 | 230 | 0 | 240 | 72 | 0 | 381 | 180 |  | 0 | 190 | 110 | 55 | 0 | 55 | 244 | 0 | 0 | 63 | 40 | 66 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 16 | 25 | 24 | 33 | 12 | 30 | 0 | 46 | 70 | 105 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 24 | 12 | 78 | 14 | 5 | 13 | 6 | 0 | 0 | 0 | 325 | 335 | 150 | 8 | 0 | 44 | 56 | 0 | 51 | 0 | 35 | 8 | 19 | 10 | 21 | 21 | 90 | 42 | 0 | 0 | 0 | 43 | 41 | 5 | 6 | 0 | 0 | 63 | 81 | 0 | 0 | 0 | 23 | 10 | 310 | 24 | 5 | 195 | 255 | 225 | 85 | 106 | 90 | 132 | 0 | 90 | 150 | 130 | 398 | 97 | 48 | 105 | 0 | 151 | 36 | 55 | 0 | 109 | 38 | 260 | 68 | 0 | 162 | 107 | 0 | 17 | 0 | 75 | 0 | 0 | 0 | 0 |  | 891 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 30 | 3 | 0 | 0 | 26 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 8 | 0 | 22 | 0 | 11 | 81 | 0 | 250 | 0 | 0 | 205 | 0 | 0 | 213 | 0 | 75 | 210 | 0 | 414 | 53 | 165 | 94 | 32 | 92 | 0 | 1 | 75 | 520 | 10 | 0 | 54 | 0 | 1 | 50 | 0 | 0 | 0 | 1 |  | 7630 | 3753 | 11383 | 3550 | 891 | 1580 | 835 | 3028 | 851 | 116 | 263 | 389 | 90 | 3 | 292.1393 | 96.26
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1309.5581 | 0
19:00 | 0 | 0 | 230 | 0 | 245 | 76 | 0 | 384 | 190 |  | 0 | 190 | 110 | 70 | 0 | 55 | 244 | 0 | 0 | 72 | 92 | 98 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 27 | 33 | 12 | 41 | 0 | 46 | 70 | 105 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 24 | 46 | 78 | 48 | 0 | 13 | 0 | 0 | 0 | 0 | 300 | 265 | 167 | 8 | 0 | 44 | 56 | 0 | 51 | 0 | 35 | 16 | 19 | 10 | 25 | 21 | 106 | 86 | 0 | 0 | 0 | 43 | 41 | 8 | 6 | 0 | 0 | 62 | 81 | 0 | 0 | 0 | 23 | 10 | 300 | 24 | 5 | 170 | 278 | 65 | 90 | 96 | 40 | 132 | 0 | 90 | 150 | 125 | 401 | 107 | 47 | 105 | 0 | 161 | 36 | 55 | 15 | 107 | 100 | 259 | 92 | 0 | 162 | 107 | 0 | 17 | 0 | 85 | 0 | 0 | 0 | 0 |  | 891 | 0 | 0 | 0 | 0 | 46 | 0 | 0 | 50 | 0 | 0 | 0 | 36 | 110 | 0 | 0 | 0 | 18 | 0 | 56 | 0 | 0 | 24 | 10 | 28 | 22 | 0 | 11 | 81 | 0 | 250 | 0 | 8 | 205 | 0 | 0 | 213 | 0 | 60 | 202 | 0 | 395 | 70 | 165 | 94 | 0 | 92 | 0 | 0 | 75 | 440 | 35 | 0 | 54 | 0 | 0 | 90 | 0 | 0 | 0 | 0 |  | 7748 | 3831 | 11579 | 3527 | 891 | 1597 | 590 | 3335 | 771 | 116 | 267 | 592 | 106 | 0 | 1310 | 96.27
19:30 | 0 | 0 | 230 | 0 | 255 | 80 | 0 | 385 | 194 |  | 0 | 190 | 110 | 73 | 0 | 55 | 251 | 0 | 0 | 72 | 92 | 98 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 27 | 33 | 12 | 41 | 0 | 46 | 70 | 105 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 24 | 46 | 78 | 76 | 1 | 13 | 19 | 0 | 0 | 0 | 300 | 295 | 180 | 8 | 20 | 45 | 56 | 0 | 51 | 0 | 35 | 43 | 19 | 10 | 25 | 21 | 104 | 107 | 0 | 0 | 0 | 43 | 41 | 8 | 6 | 0 | 0 | 62 | 81 | 0 | 0 | 0 | 23 | 10 | 310 | 24 | 5 | 191 | 278 | 122 | 90 | 97 | 62 | 132 | 0 | 90 | 150 | 130 | 403 | 107 | 47 | 105 | 0 | 161 | 36 | 55 | 20 | 114 | 100 | 260 | 92 | 0 | 162 | 107 | 0 | 17 | 0 | 96 | 0 | 0 | 0 | 0 |  | 891 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 110 | 0 | 0 | 0 | 30 | 0 | 80 | 0 | 0 | 32 | 43 | 26 | 22 | 0 | 11 | 82 | 0 | 250 | 0 | 0 | 205 | 0 | 0 | 220 | 0 | 90 | 202 | 0 | 414 | 70 | 165 | 94 | 0 | 92 | 0 | 0 | 75 | 430 | 35 | 0 | 54 | 0 | 0 | 90 | 0 | 0 | 0 | 0 |  | 8077 | 3909 | 11986 | 3633 | 891 | 1653 | 720 | 3456 | 762 | 116 | 280 | 591 | 104 | 0 | 1211 | 96.26
20:00 | 0 | 0 | 230 | 0 | 260 | 79 | 0 | 385 | 191 |  | 0 | 190 | 110 | 72 | 0 | 55 | 254 | 0 | 0 | 72 | 92 | 98 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 27 | 33 | 12 | 41 | 0 | 46 | 70 | 105 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 24 | 46 | 78 | 79 | 25 | 13 | 25 | 0 | 0 | 0 | 290 | 285 | 189 | 8 | 20 | 45 | 56 | 0 | 51 | 0 | 34 | 43 | 19 | 10 | 33 | 21 | 106 | 106 | 0 | 0 | 0 | 43 | 41 | 5 | 6 | 0 | 0 | 63 | 81 | 0 | 0 | 0 | 23 | 10 | 290 | 24 | 5 | 191 | 278 | 187 | 90 | 97 | 90 | 132 | 0 | 90 | 158 | 127 | 403 | 107 | 47 | 105 | 0 | 161 | 36 | 65 | 34 | 113 | 100 | 260 | 92 | 0 | 162 | 107 | 0 | 17 | 0 | 97 | 0 | 0 | 0 | 0 |  | 891 | 0 | 65 | 0 | 0 | 77 | 0 | 0 | 0 | 0 | 0 | 15 | 36 | 32 | 0 | 0 | 0 | 32 | 0 | 80 | 0 | 0 | 32 | 43 | 26 | 22 | 0 | 11 | 82 | 0 | 250 | 0 | 0 | 206 | 0 | 0 | 219 | 0 | 89 | 202 | 0 | 420 | 70 | 164 | 94 | 0 | 92 | 0 | 0 | 75 | 420 | 50 | 0 | 20 | 0 | 0 | 90 | 0 | 0 | 0 | 0 |  | 8210 | 3905 | 12115 | 3719 | 891 | 1653 | 811 | 3399 | 752 | 116 | 296 | 591 | 106 | 0 | 1138 | 96.27
21:00 | 0 | 0 | 230 | 0 | 260 | 83 | 0 | 375 | 190 |  | 0 | 190 | 110 | 66 | 0 | 55 | 236 | 0 | 0 | 72 | 92 | 115 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 16 | 25 | 27 | 33 | 12 | 41 | 0 | 83 | 70 | 105 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 24 | 46 | 78 | 84 | 25 | 13 | 31 | 0 | 0 | 0 | 295 | 295 | 206 | 8 | 90 | 45 | 56 | 0 | 51 | 0 | 34 | 35 | 19 | 10 | 33 | 21 | 156 | 111 | 0 | 0 | 0 | 43 | 41 | 5 | 6 | 0 | 0 | 63 | 81 | 0 | 0 | 0 | 23 | 10 | 300 | 24 | 5 | 193 | 278 | 225 | 90 | 87 | 90 | 132 | 0 | 90 | 156 | 130 | 403 | 115 | 47 | 105 | 0 | 161 | 36 | 72 | 50 | 115 | 100 | 260 | 92 | 0 | 162 | 107 | 0 | 17 | 0 | 96 | 11 | 0 | 0 | 0 |  | 891 | 0 | 80 | 0 | 0 | 145 | 0 | 0 | 10 | 0 | 0 | 30 | 38 | 32 | 0 | 0 | 0 | 32 | 0 | 80 | 0 | 0 | 32 | 43 | 26 | 22 | 0 | 11 | 82 | 0 | 250 | 0 | 0 | 206 | 0 | 0 | 219 | 0 | 89 | 202 | 0 | 420 | 70 | 164 | 94 | 32 | 92 | 0 | 0 | 75 | 430 | 139 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 0 |  | 8454 | 4126 | 12580 | 3825 | 891 | 1763 | 851 | 3416 | 762 | 153 | 364 | 618 | 156 | 0 | 1124 | 96.27
22:00 | 0 | 0 | 230 | 0 | 260 | 87 | 0 | 359 | 185 |  | 0 | 190 | 110 | 71 | 0 | 55 | 242 | 0 | 0 | 80 | 90 | 115 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 16 | 25 | 27 | 33 | 15 | 41 | 0 | 82 | 70 | 105 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 24 | 46 | 78 | 87 | 25 | 13 | 34 | 0 | 0 | 0 | 270 | 275 | 209 | 8 | 50 | 45 | 56 | 0 | 51 | 0 | 34 | 41 | 19 | 10 | 33 | 21 | 158 | 130 | 0 | 0 | 0 | 43 | 41 | 50 | 49 | 0 | 0 | 59 | 81 | 0 | 0 | 0 | 23 | 10 | 300 | 24 | 5 | 194 | 270 | 225 | 90 | 87 | 90 | 147 | 0 | 90 | 156 | 137 | 403 | 115 | 47 | 105 | 0 | 163 | 36 | 72 | 52 | 115 | 100 | 260 | 91 | 0 | 162 | 107 | 0 | 17 | 0 | 96 | 17 | 0 | 0 | 0 |  | 891 | 0 | 130 | 0 | 0 | 180 | 0 | 0 | 15 | 0 | 0 | 0 | 36 | 32 | 0 | 0 | 0 | 32 | 0 | 80 | 0 | 0 | 32 | 34 | 26 | 22 | 0 | 11 | 82 | 0 | 250 | 0 | 0 | 205 | 0 | 0 | 219 | 0 | 60 | 201 | 0 | 418 | 70 | 157 | 94 | 32 | 92 | 0 | 0 | 75 | 660 | 224 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 0 |  | 8495 | 4450 | 12945 | 3769 | 891 | 1934 | 816 | 3430 | 992 | 152 | 399 | 623 | 158 | 0 | 548.3371 | 96.2
23:00 | 0 | 0 | 230 | 0 | 260 | 92 | 0 | 359 | 189 |  | 0 | 190 | 115 | 73 | 0 | 55 | 248 | 0 | 0 | 80 | 84 | 53 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 19 | 25 | 27 | 33 | 15 | 41 | 0 | 81 | 70 | 105 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 17 | 46 | 78 | 31 | 25 | 13 | 37 | 0 | 0 | 0 | 300 | 320 | 207 | 8 | 51 | 45 | 56 | 0 | 51 | 0 | 35 | 8 | 19 | 10 | 33 | 21 | 172 | 144 | 0 | 0 | 0 | 43 | 41 | 50 | 49 | 0 | 0 | 63 | 81 | 0 | 0 | 0 | 23 | 10 | 290 | 24 | 5 | 194 | 278 | 204 | 85 | 87 | 90 | 149 | 0 | 90 | 156 | 137 | 401 | 115 | 47 | 105 | 0 | 165 | 36 | 72 | 52 | 113 | 100 | 260 | 92 | 0 | 144 | 107 | 0 | 17 | 0 | 96 | 17 | 0 | 0 | 0 |  | 891 | 0 | 180 | 0 | 0 | 210 | 0 | 0 | 16 | 0 | 0 | 65 | 36 | 32 | 0 | 0 | 0 | 32 | 0 | 45 | 0 | 0 | 23 | 34 | 26 | 22 | 0 | 11 | 82 | 0 | 249 | 0 | 0 | 206 | 0 | 0 | 219 | 0 | 60 | 202 | 0 | 418 | 70 | 166 | 94 | 32 | 92 | 0 | 0 | 75 | 1020 | 224 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 0 |  | 8420 | 4922 | 13342 | 3985 | 891 | 1941 | 799 | 3330 | 1351 | 151 | 429 | 512 | 172 | 0 | 237.7664 | 96.21
24:00 | 0 | 0 | 230 | 0 | 260 | 93 | 0 | 367 | 189 |  | 0 | 190 | 122 | 48 | 0 | 55 | 251 | 0 | 0 | 47 | 40 | 48 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 19 | 25 | 27 | 33 | 16 | 16 | 0 | 81 | 70 | 105 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 24 | 46 | 33 | 11 | 25 | 13 | 37 | 0 | 0 | 0 | 270 | 305 | 206 | 8 | 51 | 45 | 57 | 0 | 51 | 0 | 35 | 8 | 19 | 10 | 33 | 21 | 156 | 143 | 0 | 0 | 0 | 43 | 41 | 50 | 49 | 0 | 0 | 63 | 81 | 0 | 0 | 0 | 23 | 10 | 325 | 24 | 5 | 194 | 278 | 225 | 80 | 86 | 81 | 135 | 0 | 32 | 64 | 135 | 402 | 115 | 48 | 77 | 0 | 173 | 36 | 75 | 17 | 114 | 54 | 260 | 57 | 0 | 17 | 107 | 0 | 17 | 0 | 47 | 0 | 0 | 0 | 0 |  | 902 | 0 | 180 | 0 | 0 | 224 | 0 | 0 | 16 | 0 | 0 | 65 | 32 | 32 | 0 | 0 | 0 | 32 | 0 | 30 | 0 | 0 | 16 | 8 | 26 | 22 | 0 | 11 | 81 | 0 | 250 | 0 | 0 | 203 | 0 | 0 | 215 | 0 | 88 | 201 | 0 | 418 | 35 | 166 | 50 | 15 | 56 | 0 | 0 | 75 | 950 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122 | 0 |  | 7721 | 4746 | 12467 | 3947 | 902 | 1982 | 834 | 2380 | 1403 | 151 | 439 | 488 | 156 | 0 | 947.3791 | 96.21
KWH | 0 | 0 | 5500000 | 0 | 6159318 | 1940363 | 0 | 8916990 | 4362000 |  | 0 | 4496100 | 2811520 | 1162560 | 0 | 1267982 | 5408139 | 0 | 0 | 1171200 | 1202256 | 992160 | 0 | 0 | 0 | 0 | 650520 | 871983 | 908152 | 353736 | 600000 | 602460 | 787600 | 329800 | 598560 | 0 | 1816571 | 1684000 | 2500000 | 0 | 598894 | 0 | 0 | 0 | 0 |  | 288480 | 564624 | 504801 | 1035120 | 5702400 | 490080 | 313968 | 556320 | 0 | 0 | 0 | 7663500 | 7242000 | 4792000 | 200727 | 230390 | 1014336 | 1320000 | 0 | 1240989 | 0 | 654040 | 318581 | 447876 | 227160 | 635000 | 494760 | 2691840 | 2188800 | 0 | 0 | 62100 | 1021000 | 960488 | 577200 | 518112 | 0 | 0 | 1493664 | 1932480 | 0 | 0 | 0 | 535380 | 232380 | 7349000 | 523008 | 165246 | 4032960 | 5166218 | 3664055 | 1623779 | 2388000 | 1598818 | 3262180 | 106785 | 1097280 | 1371360 | 3046036 | 9561000 | 2163600 | 1000800 | 1875955 | 30359 | 3871527 | 786131 | 1523012 | 283860 | 2420040 | 1237440 | 7461300 | 1495680 | 101640 | 1765440 | 2570564 | 0 | 444240 | 142525 | 1207680 | 254880 | 0 | 0 | 0 |  | 19905454 | 0 | 2782944 | 0 | 0 | 2927040 | 0 | 0 | 183360 | 211200 | 0 | 898684 | 663718 | 899904 | 0 | 0 | 0 | 178464 | 0 | 358104 | 0 | 0 | 156578 | 257746 | 141079 | 473760 | 0 | 192402 | 1987199 | 0 | 6024600 | 0 | 7000 | 5147664 | 0 | 0 | 5246136 | 0 | 1476480 | 5080282 | 0 | 10061454 | 1050720 | 2760104 | 1648224 | 207792 | 1568774 | 0 | 30974 | 1809504 | 15625200 | 2867891 | 0 | 362400 | 20040 | 500400 | 772608 | 0 | 0 | 1999600 | 0 |  | 181435858 | 96485483 | 277921341 | 91695515 | 19905454 | 42139394 | 15156196 | 64076363 | 25636599 | 3500571 | 8180176 | 3944410 | 2691840 | 994823 | 0
Fuel Cost | 0 | 0 | 8030000 | 0 | 6898436.16 | 2580682.79 | 0 | 9362839.5 | 4710960 |  | 0 | 4900749 | 3120787.2 | 12997420.8 | 0 | 16800761.5 | 6057115.68 | 0 | 0 | 17122944 | 16915741.92 | 16082913.6 | 0 | 0 | 0 | 0 | 8274614.4 | 11771770.5 | 12178318.32 | 265302 | 450000 | 0 | 0 | 0 | 10181505.6 | 0 | 490474.17 | 454680 | 4725000 | 0 | 9791916.9 | 0 | 0 | 0 | 0 |  | 3764664 | 9417928.32 | 8591713.02 | 13984471.2 | 72306432 | 5670225.6 | 398739.36 | 1852545.6 | 0 | 0 | 0 | 8506485 | 7893780 | 5558720 | 258937.83 | 281075.8 | 1146199.68 | 1966800 | 0 | 2072451.63 | 0 | 11295270.8 | 4284914.45 | 613590.12 | 170370 | 1111250 | 371070 | 19327411.2 | 2385792 | 0 | 0 | 989874 | 1398770 | 1267844.16 | 1004328 | 896333.76 | 0 | 0 | 2897708.16 | 4406054.4 | 0 | 0 | 0 | 797716.2 | 460112.4 | 7349000 | 392256 | 125586.96 | 84530841.6 | 70518875.7 | 76798592.8 | 33563511.93 | 32190240 | 33047568.06 | 45181193 | 1248316.65 | 11323929.6 | 18732777.6 | 40420897.72 | 8796120 | 26309376 | 14471568 | 23730830.75 | 0 | 45451726.98 | 8560966.59 | 16189617.56 | 3851980.2 | 31194315.6 | 14577043.2 | 6864396 | 19369056 | 1468698 | 22403433.6 | 29253018.32 | 0 | 5801774.4 | 1703173.75 | 18078969.6 | 3356769.6 | 0 | 0 | 0 |  | 59716362 | 0 | 3116897.28 | 0 | 0 | 48296160 | 0 | 0 | 3302313.6 | 3801600 | 0 | 1006526.08 | 1287612.92 | 9808953.6 | 0 | 0 | 0 | 2992841.28 | 0 | 5600746.56 | 0 | 0 | 2647733.98 | 3513077.98 | 2380002.73 | 980683.2 | 0 | 145648.314 | 11545626.19 | 0 | 31870134 | 0 | 246050 | 5971290.24 | 0 | 0 | 91597534.56 | 0 | 30976550.4 | 5893127.12 | 0 | 9960839.46 | 14121676.8 | 57879380.88 | 19498489.92 | 3002594.4 | 19923429.8 | 0 | 342262.7 | 21967378.56 | 140783052 | 2925248.82 | 0 | 2681760 | 226652.4 | 5869692 | 11844080.64 | 0 | 0 | 0 | 0 |  | 1138370934.5 | 637724010.414 | 1776094944.914 | 102101935.614 | 59716362 | 51531843.21 | 316796445.67 | 823375502.91 | 184198812.19 | 945154.17 | 140139744.56 | 66113063.89 | 19327411.2 | 11848669.5 | 0
Yesterday Day Peak | 0 | 0 | 230 | 0 | 250 | 76 | 0 | 399 | 189 |  | 0 | 205 | 110 | 41 | 0 | 40 | 250 | 0 | 0 | 40 | 40 | 17 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 16 | 25 | 24 | 33 | 12 | 18 | 0 | 81 | 70 | 105 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 24 | 11 | 33 | 12 | 19 | 13 | 10 | 0 | 0 | 0 | 340 | 320 | 200 | 8 | 0 | 38 | 51 | 0 | 51 | 0 | 21 | 8 | 19 | 10 | 16 | 21 | 127 | 64 | 0 | 0 | 1 | 43 | 41 | 5 | 6 | 0 | 0 | 58 | 81 | 0 | 0 | 0 | 23 | 9 | 320 | 16 | 8 | 191 | 195 | 220 | 80 | 98 | 80 | 128 | 12 | 32 | 34 | 118 | 403 | 107 | 0 | 69 | 4 | 161 | 17 | 55 | 0 | 96 | 38 | 260 | 55 | 8 | 72 | 92 | 0 | 17 | 27 | 35 | 0 | 0 | 0 | 0 |  | 891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 81 | 0 | 250 | 0 | 0 | 206 | 0 | 0 | 211 | 0 | 85 | 204 | 0 | 414 | 35 | 165 | 50 | 0 | 56 | 0 | 3 | 75 | 60 | 0 | 0 | 0 | 2 | 87 | 34 | 0 | 0 | 0 | 22 |  | 10112 | DayPeak
Yesterday Evening Peak | 0 | 0 | 230 | 0 | 260 | 83 | 0 | 375 | 190 | 0 | 0 | 190 | 110 | 66 | 0 | 55 | 236 | 0 | 0 | 72 | 92 | 115 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 16 | 25 | 27 | 33 | 12 | 41 | 0 | 83 | 70 | 105 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 12 | 24 | 46 | 78 | 84 | 25 | 13 | 31 | 0 | 0 | 0 | 295 | 295 | 206 | 8 | 90 | 45 | 56 | 0 | 51 | 0 | 34 | 35 | 19 | 10 | 33 | 21 | 156 | 111 | 0 | 0 | 0 | 43 | 41 | 5 | 6 | 0 | 0 | 63 | 81 | 0 | 0 | 0 | 23 | 10 | 300 | 24 | 5 | 193 | 278 | 225 | 90 | 87 | 90 | 132 | 0 | 90 | 156 | 130 | 403 | 115 | 47 | 105 | 0 | 161 | 36 | 72 | 50 | 115 | 100 | 260 | 92 | 0 | 162 | 107 | 0 | 17 | 0 | 96 | 11 | 0 | 0 | 0 |  | 891 | 0 | 80 | 0 | 0 | 145 | 0 | 0 | 10 | 0 | 0 | 30 | 38 | 32 | 0 | 0 | 0 | 32 | 0 | 80 | 0 | 0 | 32 | 43 | 26 | 22 | 0 | 11 | 82 | 0 | 250 | 0 | 0 | 206 | 0 | 0 | 219 | 0 | 89 | 202 | 0 | 420 | 70 | 164 | 94 | 32 | 92 | 0 | 0 | 75 | 430 | 139 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 0 |  | 12580 | EvPeak
Forecast for Evening | 0 | 0 | 230 | 0 | 260 | 83 | 0 | 375 | 190 | 0 | 0 | 200 | 110 | 66 | 0 | 55 | 250 | 0 | 0 | 72 | 92 | 115 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 16 | 25 | 27 | 33 | 12 | 41 | 0 | 83 | 70 | 105 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 12 | 24 | 46 | 78 | 84 | 25 | 13 | 20 | 0 | 0 | 0 | 295 | 300 | 206 | 8 | 80 | 45 | 55 | 0 | 51 | 0 | 34 | 35 | 19 | 10 | 33 | 21 | 166 | 110 | 0 | 0 | 0 | 43 | 41 | 30 | 20 | 0 | 0 | 63 | 81 | 0 | 0 | 0 | 23 | 10 | 300 | 24 | 11 | 193 | 280 | 225 | 90 | 90 | 90 | 132 | 0 | 90 | 100 | 130 | 400 | 115 | 50 | 105 | 0 | 161 | 36 | 72 | 50 | 115 | 100 | 400 | 92 | 0 | 162 | 107 | 0 | 17 |  | 96 | 11 |  |  |  |  | 908 | 0 | 200 | 0 | 0 | 225 | 0 | 0 | 40 | 60 | 0 | 65 | 38 | 32 | 0 | 0 | 0 | 32 | 0 | 80 | 0 | 0 | 32 | 8 | 26 | 22 | 0 | 11 | 82 | 0 | 250 | 0 | 0 | 200 | 0 | 0 | 220 | 0 | 90 | 202 | 0 | 414 | 70 | 164 | 94 | 32 | 92 | 0 | 0 | 75 | 1110 | 220 |  | 17 |  |  | 90
Forecast for Day | 0 | 0 | 230 | 0 | 260 | 80 | 0 | 360 | 190 | 0 | 0 | 200 | 110 | 50 | 0 | 55 | 240 | 0 | 0 | 62 | 50 | 17 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 16 | 25 | 26 | 33 | 10 | 16 | 0 | 80 | 70 | 105 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 12 | 24 | 17 | 33 | 11 | 25 | 13 | 10 | 0 | 0 | 0 | 280 | 280 | 205 | 8 | 50 | 43 | 55 | 0 | 51 | 0 | 25 | 8 | 19 | 10 | 33 | 21 | 143 | 70 | 0 | 0 | 1.6 | 43 | 41 | 30 | 20 | 0 | 0 | 60 | 81 | 0 | 0 | 0 | 23 | 10 | 300 | 24 | 6 | 100 | 260 | 150 | 90 | 80 | 80 | 132 | 20 | 33 | 17 | 130 | 400 | 90 | 50 | 55 | 5 | 160 | 35 | 60 | 17 | 105 | 38 | 400 | 55 | 50 | 72 | 107 | 0 | 17 | 30 | 34 | 0 |  |  |  |  | 908 | 0 | 180 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 65 | 20 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 8 | 0 | 22 | 0 | 10 | 80 | 0 | 250 | 0 | 0 | 194 | 0 | 0 | 220 | 0 | 20 | 195 | 0 | 414 | 35 | 60 | 50 | 15 | 55 | 0 | 8 | 60 | 1110 | 220 |  | 0 | 6 | 100 | 0 |  |  |  | 12
Generation at 08:00(Today) | 0 | 0 | 230 | 0 | 260 | 88 | 0 | 374 | 193 | 0 | 0 | 210 | 132 | 41 | 0 | 55 | 245 | 0 | 0 | 40 | 40 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 16 | 25 | 28 | 25 | 8 | 16 | 0 | 82 | 70 | 105 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 12 | 24 | 11 | 33 | 11 | 25 | 13 | 11 | 0 | 0 | 0 | 280 | 280 | 204 | 8 | 50 | 41 | 56 | 0 | 51 | 0 | 35 | 8 | 19 | 10 | 22 | 21 | 130 | 69 | 0 | 0 | 1 | 43 | 41 | 50 | 48 | 0 | 0 | 62 | 78 | 0 | 0 | 0 | 23 | 10 | 290 | 24 | 5 | 0 | 278 | 10 | 80 | 87 | 50 | 149 | 2 | 32 | 17 | 138 | 404 | 115 | 50 | 69 | 2 | 161 | 36 | 55 | 17 | 98 | 38 | 140 | 55 | 12 | 17 | 107 | 0 | 17 | 8 | 34 | 0 | 0 | 0 | 0 | 0 | 900 | 0 | 185 | 0 | 0 | 226 | 0 | 0 | 0 | 0 | 0 | 65 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 80 | 0 | 250 | 0 | 0 | 194 | 0 | 0 | 194 | 0 | 0 | 203 | 0 | 422 | 35 | 0 | 50 | 15 | 56 | 0 | 2 | 75 | 790 | 223 | 0 | 0 | 1 | 43 | 0 | 0 | 0 | 148 | 0 | 0 |  |  |  |  | 91357145 |  | 0
91357145
| Minimum Generation |  | 9749 | 9:00
| Highest Generation |  | 13342 | 23:00
| Day Peak Generation |  | 10112 | 12:00
| Evening Peak Generation |  | 12580 | 21:00
| HVDC Max Flow |  | 902 | 24:00
| HVDC EvPeak Flow |  | 891 | 21:00
| Load factor L.F |  | 86.79% | [161 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2022-09-07
Till now the maximum generation is : - |  |  | 14782 | 21:00 | Hrs on | 2022-04-16
The Summary of Yesterday's |  | 2022-09-06 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 10112 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 10924 | MW
Evening Peak Generation : |  | 12580 | MW Hour : | 21:00 | Available Max Generation : |  | 13805 | MW
E.P. Demand (at gen end) : |  | 13800 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 13800 | MW
Maximum Generation : |  | 13342 | MW Hour : | 23:00 | Reserve(Generation end) |  | 5 | MW
Total Gen. (MKWH) : |  | 277.9213 | System Load Factor : | 86.79% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | 825 | MW at | 21:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2022-09-07
Actual : | 96.27 | Ft.(MSL) , | Rule curve : | 100.38 | Ft.( MSL )
Gas Consumed : | Total = | 1014.44 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 153633778.824
: |  | Coal : | 184198812.19 | Oil : | 1346424757.03 | Total : | 1684257348.044
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 150 | 3600:00 | 4419.4129 |  |  | 0 | -5.567%
Chittagong Area | 50 | 1200:00 | 1251.4251 |  |  | 0 | -3.327%
Khulna Area | 260 | 6240:00 | 1652.0338 |  |  | 0 | -2.918%
Rajshahi Area | 160 | 3840:00 | 1466.3548 |  |  | 0 | -2.34%
Cumilla Area | 152 | 3648:00 | 1247.6098 |  |  | 0 | -2.678%
Mymensingh Area | 222 | 5328:00 | 1031.4083 |  |  | 0 | -2.125%
Sylhet Area | 0 | 0:00 | 460.382 |  |  | 0 | -3.311%
Barisal Area | 0 | 0:00 | 375.1732 |  |  | 0 | -0.8446%
Rangpur Area | 130 | 3120:00 | 813.935 |  |  | 0 | -2.185%
Total | 1124 |  | 12717.735 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-2
2) Ghorasal-3,
3) Ashuganj-5
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
7) Sikalbaha 225 MW
8) Shajibazar 330 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Agargaon 132/33 kV T-1 transformer was under shut down from 09:12 to 12:06 for C/M.
b) B.Pukuria S/S-B.Pukuria P/S 230 kV Ckt1 was under shut down from 11:26 to 12:40 for C/M.
c) Joypurhat 132/33 kv T-1 & T-2 transformers were shut down from 10:25 to 12:57 for maintenance work.
d) HVDC block-1 tripped at 08:58.Along with all 230 kV Ckts except Ishurdi-Ghorasal 230 kV Ckt-2 and all | [5 empty] | About 1246 MW power interruption occurred under
132 kV Ckts from Ishurdi S/S got tripped. At the same Payra unit-1 & 2 run back operated. | [5 empty] | Khulna, Barishal & Rajshahi(Partially) zones area
HVDC block-1 was de-bloced at 10:06. | [5 empty] | from 08:58 to 09:20.
e) Rajshahi-Natore 132 kV Ckt-1 & 2 tripped at 08:57 showing dist.CAT,PTAW,CD(Ckt-1), dist.Z1(Ckt-2)
at Rajshahi end and from Natore end Ckt-2 tripped showing back up O/C and were switched on 09:20
& 09:40 respectively.
f) Rajshahi-HVDC 230 kV Ckt-1 & 2 were switched on at 09:46.
g) Bheramara-HVDC 230 kV Ckt-1 & 2 were switched on at 09:51.
g) Bheramara-HVDC 230 kV Ckt-1 & 2 were switched on at 09:51.
h) HVDC-Jhenidah 230 kV Ckt-1 & 2 were switched on at 09:56 & 10:32 respectively.
i) Khulna(S)-Rampal 230 kV Ckt-1 & 2 were switched on at 10:20 & 12:00 respectively.
j) Rampal-Gopalganj 400 kV Ckt-1 was switched on at 10:38.
k) Gopalganj-Payra P/S 400 kV Ckt-1 & 2 were switched on at 11:02 & 20:18 respectively.
l) Gopalganj-Madaripur 132 kV Ckt-4 was switched on at 10:30.
m) Payra P/S 400 kv bus coupler was switched on at 11:03.
n) Khulna-225 MW CCPP GT was synchronized at 12:15.
o) Noapara-100 MW was synchronized at 10:26.
p) Payra Unit-1 & 2 were synchronized at 16:06 & 11:16 respectively.
q) Bheramara-410 MW CCPP GT was synchronized at 19:40.
r) Tangail 132/33 kV T-2 transformer tripped at 16:25 by TCS and was switched on at 17:24.
s) Bogura-Mohastanghor 132 kV Ckt-1 & 2 tripped at 15:26 showing dist.Z1 and was switched on at 16:12.
t) Bhola-225 MW CCPP GT-1 was synchronized at 22:30.
u) Rampal Unit-1 was synchronized at 23:43.
v) Tangail-Kaliakoir 132 kV Ckt2 was under shut down from 05:45 to 07:05(7/9/22) for C/M. | [5 empty] | About 100 MW power interruption occurred under
Tangail S/S area from 05:45 to 07:05(7/9/22).
w) Bhulta 132/33 kV T-1 transformer is under shut down since 06:47(7/9/22) for maintenance work.
x) Bibiyana(S)-400 MW CCPP STG was synchronized at 06:13(7/9/22).
y) Ishurdi-HVDC 230 kV Ckt-3 & 4 were switched on at 09:35.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2022-09-06 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 230 | 5500000
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 260 | 6159318 | Machine problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 83 | 1940363 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 375 | 8916990 | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 190 | 4362000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 190 | 4496100 | GT-2 S/D due to dirty gas
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 66 | 1162560 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 110 | 2811520 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 0 | 0 | Under maint.
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 55 | 1267982
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 16 | 353736
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 72 | 1171200 | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 236 | 5408139 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 92 | 1202256 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 650520
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 115 | 992160 | Fuel shortage
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 871983
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 908152 | Fuel shortage
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 52 | 1202460 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 787600
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 12 | 329800 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 41 | 598560 | #REF!
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 278 | 5166218 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 225 | 3664055 | Engine problem
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 90 | 1623779 | Engine problem
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 90 | 1598818 | Engine problem
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 132 | 3262180 | Engine problem
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 47 | 1000800 | Fuel shortage
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 92 | 1495680 | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 1765440
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 142525
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 11 | 254880 | Fuel shortage
| Dhaka area Total |  |  |  | 5847 | 3499 | 71067774
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 105 | 2500000 | Machine problem
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 25 | 598894
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 106785
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 25 | 490080 | Engine problem
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 153 | 3500571 | Low water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | HGPI
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 105 | 1875955
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 24 | 564624 | Fuel shortage
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 46 | 504801 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 78 | 1035120 | Engine problem
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 90 | 1097280 | Engine problem
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 13 | 313968 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 31 | 556320
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 84 | 5702400 | Engine problem
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 30359
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 161 | 3871527 | Fuel shortage
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 36 | 786131 | Engine problem
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 72 | 1523012 | Engine problem
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 1237440 | Engine problem
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 107 | 2570564 | Engine problem
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Chattogram area Total |  |  |  | 2382 | 1255 | 28865831
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 206 | 4792000 | #REF!
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 295 | 7663500 | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 295 | 7242000 | FGMO
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+136*1 | 284 | 0 | 0 | On test.
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 45 | 1014336
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 56 | 1320000
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 200727 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1240989
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 130 | 3046036 | Engine problem
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 34 | 654040 | Engine problem
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 90 | 230390 | Machine problem
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 156 | 1371360
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 447876
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 10 | 227160
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 156 | 2691840
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 635000 | Engine problem
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 35 | 318581 | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 21 | 494760 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 193 | 4032960
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 50 | 283860 | Fuel shortage
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 115 | 2420040
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 444240 | 33 kV feeder problem.
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 96 | 1207680 | Engine problem
| Cumilla Area Total |  |  |  | 3169 | 2111 | 41979375
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 111 | 2188800 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 0 | Gas shortage
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 62100
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 87 | 2388000 | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 115 | 2163600
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 101640
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 288480 | Engine problem
| Mymensingh Area Total |  |  |  | 614 | 325 | 7192620
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1021000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 41 | 960488 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Gas shortage
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 5 | 577200 | Gas shortage
| Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 6 | 518112 | Gas shortage
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 5 | 165246 | Engine problem
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 63 | 1493664
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1932480
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 0 | 0 | Machine problem
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50MW PP (EPL) |  | NENP | 27*2 | 50 | 23 | 535380 | Gas shortage
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 523008
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7349000 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 403 | 9561000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 232380
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 260 | 7461300 | ST under shut down
| Sylhet Area Total |  |  |  | 2477 | 1264 | 32330258
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 891 | 19905454
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 0 | 0 | Fuel shortage
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 10 | 183360 | Engine problem
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 145 | 2927040 | Machine problem
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 211200 | Engine problem
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 80 | 2782944 | Start up process
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 0 | 0 | Fuel shortage
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 89 | 1476480 | Engine problem
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 70 | 1050720 | Fuel shortage
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 32 | 207792 | Fuel shortage
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 500400
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 0 | 0 | 0 | On test.
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 0 | 0 | 0 | 1999600
| Khulna Area Total |  |  |  | 2384 | 1317 | 31244990
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 32 | 899904 | Line O/L
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 38 | 663718 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 30 | 898684 | Gas shortage
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 430 | 15625200
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 139 | 2867891
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 362400 | Line O/L
| Barisal Area Total |  |  |  | 1958 | 669 | 21317797
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 32 | 178464 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contract Expired
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Fuel shortage
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 156578 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 206 | 5147664
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 219 | 5246136
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 202 | 5080282 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 420 | 10061454
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 26 | 141079 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 473760
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | .
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 192402
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 43 | 257746 | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 80 | 358104 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 164 | 2760104 | Engine problem
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 94 | 1648224 | Engine problem
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 75 | 1809504 | Engine problem
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 20040
| Rajshahi Area Total |  |  |  | 2129 | 1626 | 33531541
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 82 | 1987199
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 250 | 6024600 | Machine problem
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 7000
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 92 | 1568774 | Engine problem
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 30974
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 90 | 772608 | Engine problem
| Intraco Solar 30 MW |  | IPP | 0 | 0 | 0 | 0
| Rangpur Area Total |  |  |  | 720 | 514 | 10391155
| Total |  |  |  | 21680 | 12580 | 277921341
| Eastern Grid Total |  |  |  | 14489 | 8454 | 181435858
| Western Grid Total |  |  |  | 7191 | 4126 | 96485483
| National Grid Total |  |  |  | 21680 | 12580 | 277921341
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2022-09-06
(a) ENTIRE EASTERN GRID : |  | 8495.12 | MW | (b) ENTIRE WESTERN GRID : |  | 3675.14 | MW
i) Dhaka area |  | 4555.32 | MW | i) Khulna area |  | 1372.04 | MW
ii) Chittagong area |  | 1312.8 | MW | ii) Rajshahi area |  | 1175.2 | MW
iii) Comilla area |  | 1216 | MW | iii) Barisal area |  | 384.9 | MW
iv) Mymensingh area |  | 857 | MW | iv) Rangpur area |  | 743 | MW
v) Sylhet area |  | 554 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 12170.26 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
AKS | 0 | 00:00 | Chowmuhani | 236 | 22:00 | Kaptai | 5 | 19:30 | Nawabganj | 36.9 | 19:00 | Siddhirganj | 108 | 22:00
AKSML | 139 | 00:00 | Chuadanga | 89 | 02:00 | Kazla | 93 | 19:00 | Netrakona | 96 | 19:00 | Sirajganj | 88 | 07:00
Aftabnagar | 32 | 12:00 | Coxsbazar | 115 | 20:00 | Keranigonj | 52 | 18:30 | New | 81 | 09:00 | Sonargaon | 80 | 12:00
Agargaon | 85 | 11:00 | Cumilla(N) | 172 | 22:00 | Khagrachori | 28 | 18:30 | Niamatpur | 64 | 06:00 | Sreemongol | 44 | 12:00
Agrabad | 78 | 18:30 | Cumilla(S) | 172 | 23:00 | Khulna | 92 | 13:00 | Noapara | 47 | 01:00 | Srinagar | 46.28 | 21:00
Amnura | 52 | 21:00 | Daudkandi | 151 | 21:00 | Khulshi | 180 | 17:00 | PHP | 11 | 10:00 | Sunamganj | 38 | 22:00
Ashuganj | 65 | 00:00 | Dhaka | 44 | 12:00 | Kishoreganj | 132 | 03:00 | Pabna | 89 | 00:00 | Sylhet | 136 | 00:00
BSRM | 170 | 12:00 | Dhamrai | 116 | 22:00 | Kodda | 330 | 09:00 | Palashbari | 108 | 23:00 | TK | 28.5 | 19:00
Bagerhat | 89 | 02:00 | Dhanmondi | 119 | 13:00 | Kulaura | 48 | 21:00 | Panchagarh | 46 | 08:00 | Tangail | 195 | 22:00
Bakulia | 107 | 20:00 | Dohazari | 104 | 20:00 | Kurigram | 64 | 23:00 | Patuakhali | 133 | 22:00 | Thakurgaon | 66 | 22:00
Banani | 43 | 11:00 | Faridpur | 158 | 21:00 | Kushtia | 120 | 00:00 | Payra | 1.02 | 16:00 | Tongi | 116 | 19:30
Bangabhaban | 20 | 09:00 | Fatullah | 73 | 11:00 | Lalbag | 92 | 13:00 | Purbachal | 20 | 21:00 | Ullon | 40 | 21:00
Barapukuria | 57 | 19:00 | Fenchuganj | 49 | 21:00 | Lalmonirhat | 47 | 22:00 | Purbasadipur | 96 | 05:00 | Uttara | 93 | 21:00
Barguna | 22 | 19:30 | Feni | 107 | 19:00 | Madanganj | 95 | 11:00 | Rahim | 26 | 08:00 | UttaraNew | 18 | 00:00
Barishal | 118 | 20:00 | GPH | 84 | 01:00 | Madaripur | 106 | 21:00 | Rajbari | 60 | 19:30 | Zigatola | 57 | 19:00
Barishal-230 | 81 | 23:00 | Ghorashal | 77 | 18:30 | Madartek | 86 | 23:00 | Rajendrapur | 92 | 05:00
Baroaulia | 66 | 21:00 | Goalpara | 28 | 13:00 | Madunaghat | 61 | 20:00 | Rajshahi | 132 | 22:00
Baroirhat | 58 | 18:30 | Gollamari | 56 | 12:00 | Magura | 46 | 02:00 | Rajshahi-230 | 26 | 02:00
Bashundhara | 154 | 11:00 | Gopalganj | 100 | 23:00 | Mahasthangarh | 68 | 00:00 | Ramganj | 88 | 19:00
BashundharaCement | 0 | 00:00 | Gulshan | 122 | 11:00 | Manikganj | 88 | 23:00 | Rampur | 16 | 00:00
Beanibazar | 65 | 21:00 | Halishahar | 82.5 | 15:00 | Maniknagar | 79 | 12:00 | Rangamati | 14 | 19:00
Benapole | 54 | 02:00 | HaripurSBU | 163 | 23:00 | Matarbari | 40 | 20:00 | Rangpur | 105 | 08:00
Bhaluka | 132 | 18:30 | Hasnabad | 98 | 21:00 | Matuail | 64 | 11:00 | Ruppur | 5 | 09:00
Bhandaria | 58 | 19:00 | Hathazari | 101 | 21:00 | Millgate | 60 | 10:00 | SSM | 3 | 05:00
Bhangura | 30 | 19:30 | Ishurdi | 67 | 22:00 | Mirpur | 123 | 18:30 | Saidpur | 93 | 08:00
Bheramara(GK) | 52 | 02:00 | Jaldhaka | 59 | 22:00 | Mirsorai | N/A | N/A | Satkhira | 95 | 06:00
Bhulta | 219 | 23:00 | Jamalpur | 129 | 03:00 | Mithapukur | 32 | 00:00 | Satmasjid | 101 | 19:00
Bog-Sherpur | 54 | 22:00 | Jashore | 108 | 22:00 | Modern | 0 | 00:00 | Savar | 156 | 09:00
Bogura | 147 | 23:00 | Jhenaidah | 102 | 02:00 | Mogbazar | 132 | 12:00 | Shahjadpur | 85 | 22:00
Borhanuddin | 43 | 22:00 | Joydebpur | 190 | 21:00 | Mongla | 28 | 09:00 | Shahjibazar | 95 | 00:00
Brahmanbaria | 144 | 20:00 | Joypurhat | 56 | 23:00 | Motijheel | 38 | 11:00 | Shahmirpur | 46.5 | 18:30
Cantonment | 144 | 18:30 | Juldah | 28 | 07:00 | Munshiganj | 110 | 21:00 | Shariatpur | 78 | 22:00
Chandpur | 70 | 22:00 | KSRM | 27 | 19:00 | Mymensingh | 209 | 22:00 | Sherpur | 100 | 19:00
Chandraghona | 36 | 18:30 | Kabirpur | 292 | 16:00 | Naogaon | 120 | 23:00 | Shikalbaha | 28 | 19:00
Chapai | 62 | 22:00 | Kachua | 76 | 22:00 | Narail | 36 | 02:00 | Shikalbaha-230 | N/A | N/A
Charsaidpur | 45 | 11:00 | Kallyanpur | 92 | 18:30 | Narinda | 75 | 12:00 | Shitalakhya | 114 | 12:00
Chauddagram | 64 | 22:00 | Kalurghat | 34 | 09:00 | Narshingdi | 159 | 22:00 | Sholosohor | N/A | N/A
Chhatak | 31 | 23:00 | Kamrangirchar | 63 | 12:00 | Natore | 128 | 22:00 | Shyampur | 144 | 01:00
Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
(1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2022-09-06 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Bhulta | 389 | 19:00 | 375 | 12:00 | Kaliakoir | 390 | 18:30 | 374 | 08:00
| Bibiana | 403 | 19:00 | 389 | 18:00 | Payra | 420 | 18:30 | 408 | 23:00
| BIPTC | 407 | 09:00 | 393 | 00:00 | Rahanpur_I | 398 | 18:30 | 380 | 03:00
| Gopalganj_I | 426 | 18:30 | 318 | 11:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 224 | 19:00 | 214 | 12:00 | Hasnabad | 226 | 19:30 | 216 | 12:00
| AKSML | 235 | 20:00 | 216 | 08:00 | Hathazari | 236 | 19:00 | 221 | 00:00
| Aminbazar | 224 | 18:00 | 217 | 10:00 | Ishurdi | 233 | 05:00 | 225 | 13:00
| Ashuganj | 239 | 19:00 | 230 | 12:00 | Jhenaidah | 235 | 10:00 | 222 | 09:00
| Baghabari | 235 | 10:00 | 227 | 15:00 | Kaliakoir | 224 | 18:30 | 215 | 08:00
| Barapukuria | 224 | 08:00 | 214 | 22:00 | Keranigonj | 224 | 19:00 | 215 | 12:00
| Barishal | 245 | 07:00 | 190 | 11:00 | Khulna(S) | 237 | 19:30 | 227 | 14:00
| Bheramara | 234 | 10:00 | 221 | 15:00 | Maniknagar | 225 | 19:00 | 217 | 12:00
| Bhulta | 228 | 18:30 | 220 | 12:00 | Meghnaghat | 229 | 19:00 | 220 | 07:00
| Bibiana | 237 | 18:30 | 229 | 11:00 | Mirsorai | N/A | N/A | N/A | N/A
| BIPTC | 235 | 10:00 | 222 | 15:00 | Rajshahi | 235 | 10:00 | 222 | 15:00
| Bogura | 229 | 05:00 | 218 | 22:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 247 | 06:00 | 230 | 19:30 | Rampura | 226 | 18:30 | 217 | 12:00
| BSRM | 233 | 19:00 | 215 | 01:00 | Shikalbaha | 234 | 19:30 | 223 | 01:00
| Cumilla(N) | 229 | 19:00 | 219 | 01:00 | Shyampur | 225 | 19:00 | 216 | 12:00
| Fenchuganj | 236 | 05:00 | 230 | 01:00 | Siddhirganj | 226 | 19:00 | 220 | 12:00
| Ghorashal | N/A | N/A | N/A | N/A | Sirajgonj | 229 | 05:00 | 227 | 02:00
| GPH | 233 | 09:00 | 217 | 01:00 | Tongi | 226 | 22:00 | 218 | 11:00
| Haripur | 224 | 19:00 | 217 | 12:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 137 | 04:00 | 130 | 11:00 | Lalbag | 139 | 02:00 | 134 | 12:00
| Agargaon | 138 | 19:00 | 131 | 12:00 | Lalmonirhat | 132 | 09:00 | 117 | 22:00
| Agrabad | 137 | 19:00 | 126 | 17:00 | Madanganj | 133 | 19:00 | 126 | 12:00
| AKS | 137 | 09:00 | 126 | 00:00 | Madaripur | 137 | 05:00 | 107 | 11:00
| Aminbazar | 137 | 18:00 | 130 | 08:00 | Madartek | 136 | 03:00 | 129 | 12:00
| Amnura | 134 | 10:00 | 126 | 14:00 | Madunaghat | 138 | 09:00 | 129 | 00:00
| Ashuganj | 138 | 19:00 | 134 | 00:00 | Magura | 137 | 00:00 | 126 | 14:00
| Bagerhat | 135 | 00:00 | 120 | 11:00 | Mahasthangarh | 137 | 09:00 | 115 | 16:00
| Bakulia | 139 | 19:00 | 128 | 00:00 | Manikganj | 134 | 10:00 | 128 | 16:00
| Banani | 134 | 04:00 | 128 | 11:00 | Maniknagar | 134 | 21:00 | 128 | 12:00
| Bangabhaban | 133 | 19:00 | 127 | 12:00 | Matarbari | 131 | 09:00 | 107 | 20:00
| Barapukuria | 137 | 08:00 | 127 | 16:00 | Matuail | 132 | 19:00 | 127 | 11:00
| Barguna | 138 | 15:00 | 120 | 13:00 | Millgate | 134 | 19:00 | 128 | 12:00
| Barishal | 139 | 09:00 | 120 | 13:00 | Mirpur | 136 | 17:00 | 129 | 10:00
| Barishal-230 | 139 | 07:00 | 108 | 11:00 | Mithapukur | 136 | 10:00 | 119 | 16:00
| Baroaulia | 138 | 18:30 | 128 | 00:00 | Modern | 137 | 19:00 | 128 | 00:00
| Baroirhat | 135 | 19:00 | 121 | 01:00 | Mogbazar | 137 | 04:00 | 130 | 11:00
| Bashundhara | 133 | 03:00 | 128 | 12:00 | Mongla | 133 | 00:00 | 120 | 11:00
| BashundharaCement | 133 | 19:00 | 126 | 12:00 | Motijheel | 133 | 19:00 | 127 | 12:00
| Beanibazar | 130 | 06:00 | 120 | 21:00 | Munshiganj | 133 | 19:00 | 127 | 11:00
| Benapole | 134 | 00:00 | 121 | 11:00 | Mymensingh | 135 | 09:00 | 114 | 22:00
| Bhaluka | 134 | 11:00 | 115 | 18:30 | Naogaon | 135 | 16:00 | 121 | 22:00
| Bhandaria | 138 | 09:00 | 120 | 15:00 | Narail | 135 | 05:00 | 126 | 14:00
| Bhangura | 139 | 09:00 | 134 | 15:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bheramara | 136 | 10:00 | 127 | 15:00 | Narshingdi | 127 | 18:00 | 121 | 04:00
| Bheramara(GK) | 136 | 06:00 | 128 | 14:00 | Natore | 136 | 09:00 | 128 | 22:00
| Bhulta | 124 | 18:30 | 118 | 08:00 | Nawabganj | 140 | 18:30 | 134 | 08:00
| Bog-Sherpur | 138 | 10:00 | 128 | 22:00 | Netrakona | 127 | 09:00 | 115 | 03:00
| Bogura | 139 | 10:00 | 128 | 22:00 | New | 135 | 19:00 | 129 | 12:00
| Bogura-230 | 139 | 10:00 | 130 | 22:00 | Niamatpur | 133 | 10:00 | 118 | 22:00
| Brahmanbaria | 134 | 09:00 | 129 | 00:00 | Noapara | 136 | 00:00 | 126 | 11:00
| Cantonment | 137 | 19:00 | 130 | 12:00 | Pabna | 135 | 06:00 | 130 | 12:00
| Chandpur | 139 | 19:00 | 119 | 00:00 | Palashbari | 135 | 11:00 | 115 | 16:00
| Chandraghona | 138 | 09:00 | 130 | 00:00 | Panchagarh | 133 | 19:00 | 112 | 23:00
| Chapai | 135 | 10:00 | 125 | 23:00 | Patuakhali | 137 | 19:00 | 128 | 21:00
| Charsaidpur | 133 | 19:00 | 127 | 12:00 | Payra | 138 | 18:00 | 133 | 21:00
| Chauddagram | 135 | 19:00 | 123 | 00:00 | PHP | 133 | 19:00 | 121 | 01:00
| Chhatak | 129 | 07:00 | 118 | 21:00 | Postogola | 144 | 19:00 | 136 | 12:00
| Chowmuhani | 138 | 18:30 | 120 | 01:00 | Purbachal | 135 | 19:00 | 127 | 12:00
| Chuadanga | 134 | 08:00 | 122 | 14:00 | Purbasadipur | 135 | 10:00 | 121 | 17:00
| Coxsbazar | 129 | 09:00 | 108 | 17:00 | Rahim | 133 | 19:00 | 128 | 12:00
| Cumilla(N) | 136 | 19:00 | 126 | 01:00 | Rajbari | 133 | 06:00 | 117 | 15:00
| Cumilla(S) | 137 | 18:30 | 125 | 00:00 | Rajendrapur | 137 | 05:00 | 130 | 08:00
| Daudkandi | 136 | 17:00 | 126 | 07:00 | Rajshahi | 135.7 | 10:00 | 127 | 22:00
| Dhaka | 137 | 14:00 | 129 | 12:00 | Rajshahi-230 | 136 | 10:00 | 127 | 15:00
| Dhamrai | 138 | 19:00 | 131 | 08:00 | Ramganj | 133 | 19:00 | 115 | 01:00
| Dhanmondi | 132.5 | 19:00 | 126.7 | 12:00 | Rampur | 138 | 19:00 | 126 | 03:00
| Dohazari | 138 | 09:00 | 121 | 01:00 | Rampura | 137 | 14:00 | 129 | 12:00
| Faridpur | 135 | 18:00 | 120 | 11:00 | Rangamati | 138 | 19:00 | 129 | 00:00
| Fatullah | 137 | 19:00 | 131 | 07:00 | Rangpur | 135 | 10:00 | 119 | 16:00
| Fenchuganj | 134 | 04:00 | 130 | 01:00 | Ruppur | 136 | 07:00 | 130 | 15:00
| Feni | 135 | 19:00 | 122 | 01:00 | Saidpur | 136 | 18:30 | 120 | 16:00
| Ghorashal | 139 | 18:30 | 135 | 15:00 | Satkhira | 133 | 00:00 | 118 | 11:00
| Goalpara | 137 | 00:00 | 15 | 19:00 | Satmasjid | 138 | 19:00 | 131 | 12:00
| Gollamari | 135 | 00:00 | 123 | 11:00 | Savar | 138 | 19:00 | 129 | 10:00
| Gopalganj | 137 | 18:00 | 117 | 11:00 | Shahjadpur | 142 | 10:00 | 136 | 15:00
| Gopalganj_I | 138 | 18:00 | 103 | 19:00 | Shahjibazar | 135 | 06:00 | 131 | 02:00
| Gulshan | 136 | 14:00 | 129 | 12:00 | Shahmirpur | 134 | 18:30 | 127 | 18:00
| Halishahar | 137 | 09:00 | 128 | 01:00 | Shariatpur | 136 | 07:00 | 109 | 11:00
| Haripur | 133 | 19:00 | 128 | 12:00 | Sherpur | 138 | 09:00 | 120 | 06:00
| HaripurSBU | 134 | 19:00 | 128 | 12:00 | Shikalbaha | 139 | 19:00 | 127 | 18:00
| Hasnabad | 141 | 14:00 | 136 | 08:00 | Shikalbaha-230 | 135 | 18:30 | 128 | 01:00
| Hathazari | 138 | 19:00 | 130 | 00:00 | Shitalakhya | 142 | 21:00 | 134 | 11:00
| Ishurdi | 136 | 07:00 | 130 | 11:00 | Sholosohor | N/A | N/A | N/A | N/A
| Jaldhaka | 134 | 09:00 | 120 | 16:00 | Shyampur | 134 | 13:00 | 130 | 12:00
| Jamalpur | 139 | 19:00 | 124 | 06:00 | Shyampur-230 | 136 | 19:00 | 131 | 07:00
| Jashore | 135 | 00:00 | 121 | 11:00 | Siddhirganj | 133 | 19:00 | 128 | 08:00
| Jhenaidah | 138 | 00:00 | 127 | 14:00 | Sirajganj | 137 | 10:00 | 128 | 22:00
| Jhenaidah-230 | 138 | 00:00 | 127 | 14:00 | Sonargaon | 134 | 19:00 | 129 | 16:00
| Joydebpur | 142 | 18:30 | 130 | 12:00 | Sreemongol | 135 | 09:00 | 132 | 21:00
| Joypurhat | 136 | 10:00 | 119 | 22:00 | Srinagar | 139 | 04:00 | 134 | 07:00
| Juldah | 138 | 19:00 | 125 | 17:00 | SSM | 139 | 19:00 | 132 | 01:00
| Kabirpur | 137 | 18:30 | 124 | 08:00 | Sunamganj | 127 | 04:00 | 115 | 21:00
| Kachua | 137 | 19:00 | 119 | 03:00 | Sylhet | 130 | 04:00 | 123 | 21:00
| Kaliakoir | 139 | 04:00 | 133 | 08:00 | Tangail | 136 | 11:00 | 125 | 18:00
| Kallyanpur | 137 | 21:00 | 131 | 06:00 | Thakurgaon | 135 | 19:00 | 116 | 00:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2022-09-06
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 1375 | 7721 | 4746 | 12467 |  |  |  | QF-LDC-11
0:30 | 1415 | 7494 | 4727.5 | 12221.5 | Date: | 2022-09-06
1:00 | 1455 | 7267 | 4709 | 11976
1:30 | 1452.5 | 7246 | 4679 | 11925
2:00 | 1450 | 7225 | 4649 | 11874
2:30 | 1445 | 7203.5 | 4580 | 11783.5 | [5 empty] | Gen. at Eve. Peak | 12580 | 12580 MW (21:00 )
3:00 | 1440 | 7182 | 4511 | 11693 | [6 empty] | 21:00
3:30 | 1445 | 7153.5 | 4498.5 | 11652 | [5 empty] | Gen. at Day Peak | 10112 | 10112 MW (12:00 )
4:00 | 1450 | 7125 | 4486 | 11611 | [6 empty] | 12:00
4:30 | 1450 | 7057.5 | 4444.5 | 11502 | [5 empty] | Highest Generation | 13342
5:00 | 1450 | 6990 | 4403 | 11393 | [6 empty] | 23:00
5:30 | 1450 | 6743.5 | 4305.5 | 11049
6:00 | 1450 | 6497 | 4208 | 10705
6:30 | 1490 | 6497.5 | 4162.5 | 10660
7:00 | 1530 | 6498 | 4117 | 10615
7:30 | 1540 | 6498 | 4127.5 | 10625.5
8:00 | 1550 | 6498 | 4138 | 10636
8:30 | 1250 | 6672.5 | 3520 | 10192.5
9:00 | 950 | 6847 | 2902 | 9749
9:30 | 985 | 6975 | 2270.5 | 9245.5
10:00 | 1020 | 7103 | 1639 | 8742
10:30 | 1092.5 | 7142.5 | 2054.5 | 9197
11:00 | 1165 | 7182 | 2470 | 9652
11:30 | 1285 | 7154 | 2728 | 9882
12:00 | 1405 | 7126 | 2986 | 10112
12:30 | 1387.5 | 7097.5 | 3034.5 | 10132
13:00 | 1370 | 7069 | 3083 | 10152
13:30 | 1200 | 7052.5 | 3170 | 10222.5
14:00 | 1030 | 7036 | 3257 | 10293
14:30 | 1130 | 7029.5 | 3368.5 | 10398
15:00 | 1230 | 7023 | 3480 | 10503
15:30 | 1317.5 | 6997 | 3544.5 | 10541.5
16:00 | 1405 | 6971 | 3609 | 10580
16:30 | 1350 | 6993 | 3628.5 | 10621.5
17:00 | 1295 | 7015 | 3648 | 10663
17:30 | 1212.5 | 7322.5 | 3700.5 | 11023
18:00 | 1130 | 7630 | 3753 | 11383
18:30 | 985 | 7689 | 3792 | 11481
19:00 | 840 | 7748 | 3831 | 11579
19:30 | 850 | 8077 | 3909 | 11986
20:00 | 880 | 8210 | 3905 | 12115 |  |  |  | Executive Engineer
20:30 | 852.5 | 8332 | 4015.5 | 12347.5 |  |  |  | Network Operation Division
21:00 | 825 | 8454 | 4126 | 12580
21:30 | 1032.5 | 8474.5 | 4288 | 12762.5
22:00 | 1240 | 8495 | 4450 | 12945 |  |  |  |  | Page 6 of 7
22:30 | 1270 | 8457.5 | 4686 | 13143.5
23:00 | 1300 | 8420 | 4922 | 13342
23:30 | 1337.5 | 8070.5 | 4834 | 12904.5
24:00 | 1375 | 7721 | 4746 | 12467
12580 MW (21:00 )
10112 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2022-09-06 |  | Energy |  | 277921341
[13 empty] | 2022-09-06 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 3947 | 902 | 1982 | 834 | 2380 | 1403 | 151 | 439 | 488 | 156 | 0 | 947.3791
0:30 | 3944.5 | 896.5 | 1924 | 827.5 | 2290 | 1393 | 150.5 | 441.5 | 443 | 128 | 0 | 807.2997 | Date: | 2022-09-06
1:00 | 3942 | 891 | 1866 | 821 | 2200 | 1383 | 150 | 444 | 398 | 100 | 0 | 667.2203
1:30 | 3954 | 891 | 1869.5 | 778.5 | 2191.5 | 1382.5 | 150 | 445.5 | 383 | 99 | 0 | 414.7087 | [8 empty] | Total Energy | 277.9213 | Total Energy Gen 277.921 MKWHr Energy Not Served 16.394 MKWHr Energy Requirement 294.315 MKWHr
2:00 | 3966 | 891 | 1873 | 736 | 2183 | 1382 | 150 | 447 | 368 | 98 | 0 | 162.1972 | [8 empty] | Energy not Served | 16.3935
2:30 | 3974.5 | 891 | 1896.5 | 630.5 | 2182 | 1367 | 150.5 | 446.5 | 368 | 97 | 0 | 144.2265 | [8 empty] | Energy Requirement | 294.3149
3:00 | 3983 | 891 | 1920 | 525 | 2181 | 1352 | 151 | 446 | 368 | 96 | 0 | 126.2558
3:30 | 3990.5 | 891.5 | 1928.5 | 488 | 2175.5 | 1345.5 | 151 | 438.5 | 360.5 | 95 | 0 | 104.138 | [6 empty] | Shortage
4:00 | 3998 | 892 | 1937 | 451 | 2170 | 1339 | 151 | 431 | 353 | 94 | 0 | 82.0202
4:30 | 4003.5 | 891.5 | 1932 | 383.5 | 2169.5 | 1320 | 151.5 | 425 | 330.5 | 94 | 0 | 67.275
5:00 | 4009 | 891 | 1927 | 316 | 2169 | 1301 | 152 | 419 | 308 | 94 | 0 | 52.5298
5:30 | 4012 | 891.5 | 1926.5 | 183 | 1989.5 | 1291.5 | 152.5 | 400 | 304 | 91 | 0.5 | 26.2649
6:00 | 4015 | 892 | 1926 | 50 | 1810 | 1282 | 153 | 381 | 300 | 88 | 1 | 0
6:30 | 4030.5 | 892 | 1936.5 | 50 | 1764 | 1252.5 | 152.5 | 377.5 | 294.5 | 83 | 20.5 | 0 |  |  |  |  | Coal
7:00 | 4046 | 892 | 1947 | 50 | 1718 | 1223 | 152 | 374 | 289 | 78 | 40 | 0
7:30 | 4019 | 891.5 | 1893 | 42.5 | 1809 | 1212.5 | 152.5 | 379 | 279 | 96 | 45.5 | 0 |  |  |  | Oil |  |  |  | ,
8:00 | 3992 | 891 | 1839 | 35 | 1900 | 1202 | 153 | 384 | 269 | 114 | 51 | 0
8:30 | 3815 | 730 | 1699.5 | 160 | 1962 | 1161 | 152.5 | 288.5 | 267 | 114 | 36.5 | 11
9:00 | 3638 | 569 | 1560 | 285 | 2024 | 1120 | 152 | 193 | 265 | 114 | 22 | 22
9:30 | 3614 | 284.5 | 1584 | 451.5 | 2004.5 | 725.5 | 151.5 | 198 | 271.5 | 116 | 42.5 | 1112.2821
10:00 | 3590 | 0 | 1608 | 618 | 1985 | 331 | 151 | 203 | 278 | 118 | 63 | 2202.5643
10:30 | 3633.5 | 259.5 | 1605 | 715.5 | 1997 | 331 | 151 | 208 | 283 | 122 | 99.5 | 1793.8457
11:00 | 3677 | 519 | 1602 | 813 | 2009 | 331 | 151 | 213 | 288 | 126 | 136 | 1385.1272
11:30 | 3656 | 705 | 1602 | 817 | 2026.5 | 361 | 151 | 212 | 286 | 126.5 | 151 | 1310.0189
12:00 | 3635 | 891 | 1602 | 821 | 2044 | 391 | 151 | 211 | 284 | 127 | 166 | 1234.9105
12:30 | 3597 | 891 | 1599.5 | 813.5 | 2053 | 455.5 | 151 | 214.5 | 285 | 133.5 | 150.5 | 1192.518
13:00 | 3559 | 891 | 1597 | 806 | 2062 | 520 | 151 | 218 | 286 | 140 | 135 | 1150.1256
13:30 | 3559 | 891 | 1597 | 806 | 2062 | 520 | 151 | 218 | 286 | 140 | 135 | 1131.2333
14:00 | 3559 | 891 | 1597 | 806 | 2062 | 520 | 151 | 218 | 286 | 140 | 135 | 1112.341
14:30 | 3537 | 891 | 1595.5 | 819.5 | 2172 | 620 | 151 | 222 | 294 | 116 | 121.5 | 1107.7332
15:00 | 3515 | 891 | 1594 | 833 | 2282 | 720 | 151 | 226 | 302 | 92 | 108 | 1103.1253
15:30 | 3523.5 | 891.5 | 1584 | 828 | 2283.5 | 760 | 152 | 245 | 308.5 | 87 | 91 | 1021.5659
16:00 | 3532 | 892 | 1574 | 823 | 2285 | 800 | 153 | 264 | 315 | 82 | 74 | 940.0065
16:30 | 3519 | 892 | 1575.5 | 764 | 2406 | 815 | 153 | 265 | 313.5 | 78 | 49 | 855.6824
17:00 | 3519 | 892 | 1577 | 705 | 2527 | 830 | 153 | 266 | 312 | 74 | 24 | 771.3583
17:30 | 3534.5 | 891.5 | 1578.5 | 770 | 2777.5 | 840.5 | 134.5 | 264.5 | 350.5 | 82 | 13.5 | 531.7488
18:00 | 3550 | 891 | 1580 | 835 | 3028 | 851 | 116 | 263 | 389 | 90 | 3 | 292.1393
18:30 | 3538.5 | 891 | 1588.5 | 712.5 | 3181.5 | 811 | 116 | 265 | 490.5 | 98 | 1.5 | 801.0696
19:00 | 3527 | 891 | 1597 | 590 | 3335 | 771 | 116 | 267 | 592 | 106 | 0 | 1310
19:30 | 3633 | 891 | 1653 | 720 | 3456 | 762 | 116 | 280 | 591 | 104 | 0 | 1211
20:00 | 3719 | 891 | 1653 | 811 | 3399 | 752 | 116 | 296 | 591 | 106 | 0 | 1138
20:30 | 3772 | 891 | 1708 | 831 | 3407.5 | 757 | 134.5 | 330 | 604.5 | 131 | 0 | 1131
21:00 | 3825 | 891 | 1763 | 851 | 3416 | 762 | 153 | 364 | 618 | 156 | 0 | 1124
21:30 | 3797 | 891 | 1848.5 | 833.5 | 3423 | 877 | 152.5 | 381.5 | 620.5 | 157 | 0 | 836.1686
22:00 | 3769 | 891 | 1934 | 816 | 3430 | 992 | 152 | 399 | 623 | 158 | 0 | 548.3371
22:30 | 3877 | 891 | 1937.5 | 807.5 | 3380 | 1171.5 | 151.5 | 414 | 567.5 | 165 | 0 | 393.0517
23:00 | 3985 | 891 | 1941 | 799 | 3330 | 1351 | 151 | 429 | 512 | 172 | 0 | 237.7664
23:30 | 3966 | 896.5 | 1961.5 | 816.5 | 2855 | 1377 | 151 | 434 | 500 | 164 | 0 | 592.5727 | Max Temp. in Dhaka |  | 24.7° C | 32.5° C
24:00 | 3947 | 902 | 1982 | 834 | 2380 | 1403 | 151 | 439 | 488 | 156 | 0 | 947.3791
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 277.921 MKWHr Energy Not Served 16.394 MKWHr Energy Requirement 294.315 MKWHr
Note on W13: Author:

## Generation
g | 2022-09-06
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 80 | 80 | 81 | 81 | 82 | 83 | 82 | 83 | 82 | 81 | 81 | 81 | 81 | 81 | 81 | 83 | 83 | 46 |  | 46 | 46 | 46 | 83 | 82 | 81 | 81 | 1816571
2 | Karnaphuli Hydro PP Unit-4 & 5 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1684000
3 | Chattogram TPP-1 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2500000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 598894
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 6 | 12 |  | 20 | 4 | 12 | 20 | 18 | 17 | 7 | 1 | 0 | [8 empty] | 106785
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 11 | 11 | 11 | 12 | 12 | 11 | 12 |  | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 504801
12 | Hathazari 100 MW peaking PP | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 21 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 17 | 24 | 564624
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 69 | 69 | 69 | 69 | 69 | 17 | 18 | 55 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 95 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 77 | 1875955
| Daudkandi 200 MW PP (B.Trac) | 191 | 190 | 191 | 190 | 190 | 50 | 50 |  | 110 | 191 | 191 | 191 | 194 | 195 | 195 | 195 | 195 | 195 |  | 170 | 191 | 191 | 193 | 194 | 194 | 194 | 4032960
14 | Titas 50 MW Peaking PP | 22 | 22 | 22 | 22 | 22 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 29 | 34 | 34 | 34 | 35 |  | 35 | 35 | 34 | 34 | 34 | 35 | 35 | 654040
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 250 | 263 | 261 | 250 | 250 | 285 | 255 | 243 | 240 | 244 |  | 244 | 251 | 254 | 236 | 242 | 248 | 251 | 5408139
18 | Kodda 300 MW PP Unit-2 (Summit) | 210 | 195 | 194 | 195 | 195 | 145 | 145 | 165 | 195 | 193 | 195 | 195 | 195 | 195 | 195 | 185 | 195 | 255 |  | 278 | 278 | 278 | 278 | 270 | 278 | 278 | 5166218
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 200727
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 235 | 147 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 |  | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 5500000
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 240 |  | 245 | 255 | 260 | 260 | 260 | 260 | 260 | 6159318
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 41 | 41 | 40 | 38 | 38 | 39 | 39 | 39 | 43 | 44 |  | 44 | 45 | 45 | 45 | 45 | 45 | 45 | 1014336
33 | Ashuganj 225 MW CCPP | 208 | 210 | 209 | 210 | 210 | 208 | 205 | 209 | 206 | 204 | 202 | 200 | 204 | 195 | 186 | 174 | 167 | 150 |  | 167 | 180 | 189 | 206 | 209 | 207 | 206 | 4792000
34 | Ashuganj 450 MW CCPP(South) | 275 | 275 | 275 | 275 | 275 | 275 | 320 | 310 | 300 | 290 | 330 | 320 | 305 | 315 | 320 | 305 | 305 | 335 |  | 265 | 295 | 285 | 295 | 275 | 320 | 305 | 7242000
| Ashuganj 450 MW CCPP(North) | 280 | 280 | 280 | 280 | 280 | 280 | 330 | 315 | 315 | 300 | 345 | 340 | 320 | 325 | 325 | 310 | 310 | 325 |  | 300 | 300 | 290 | 295 | 270 | 300 | 270 | 7663500
| Ashuganj 420 MW CCPP(East) | [26 empty] | 0
35 | Ashuganj 55 MW PP (Precision) | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 55 | 51 | 52 | 51 | 54 | 54 | 53 | 52 | 56 | 56 |  | 56 | 56 | 56 | 56 | 56 | 56 | 57 | 1320000
36 | Chandpur 150 MW CCPP | [19 empty] | 0 | 20 | 20 | 90 | 50 | 51 | 51 | 230390
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 347 | 346 | 347 | 351 | 353 | 359 | 363 | 363 | 392 | 406 | 405 | 399 | 394 | 250 | 359 | 381 | 380 | 381 |  | 384 | 385 | 385 | 375 | 359 | 359 | 367 | 8916990
40 | Meghnaghat 450 MW CCPP(MPL) | 210 | 210 | 210 | 215 | 215 | 215 | 215 | 215 | 195 | 195 | 195 | 205 | 205 | 200 | 200 | 200 | 200 | 190 |  | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 4496100
41 | Haripur 360MW CCPP(HPL) | 152 | 151 | 152 | 163 | 160 | 166 | 167 | 174 | 196 | 206 | 202 | 189 | 188 | 221 | 194 | 180 | 183 | 180 |  | 190 | 194 | 191 | 190 | 185 | 189 | 189 | 4362000
42 | RPCL 210MW CCPP | 142 | 140 | 149 | 149 | 149 | 152 | 103 | 68 | 69 | 65 | 64 | 64 | 40 | 38 | 42 | 43 | 41 | 42 |  | 86 | 107 | 106 | 111 | 130 | 144 | 143 | 2188800
43 | Sutiakhali 50 MW Solar PP |  |  |  |  | 0 | 0 | 4 | 5 | 5 | 10 | 9 | 8 | 13 | 8 | 18 | 10 | 4 | 0 | [8 empty] | 101640
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1021000
45 | Fenchugonj CCPP Phase-2 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 |  | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 960488
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 63 | 62 | 63 | 64 | 65 | 64 | 62 | 62 | 61 | 61 | 60 | 58 | 60 | 64 | 64 | 64 | 61 | 63 |  | 62 | 62 | 63 | 63 | 59 | 63 | 63 | 1493664
48 | Shahjibazar 86MW PP (Shahjibazar) | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 |  | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 1932480
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL) | 17 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 |  | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 535380
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 9 | 9 | 9 | 9 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 232380
54 | Hobiganj 11MW PP Cofidence-E | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 165246
55 | Fenchugonj 51 MW PP (Barakatullah) | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 8 | 8 | 5 | 5 | 50 | 50 | 50 | 577200
56 | Shahjahanulla 25 MW PP | 0 | 24 | 24 | 24 | 24 | 24 | 16 | 21 | 24 | 24 | 24 | 16 | 16 | 24 | 24 | 16 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 523008
57 | Bibiana-II 341 MW CCPP (Summit) | 290 | 270 | 290 | 280 | 270 | 265 | 305 | 310 | 290 | 310 | 310 | 320 | 305 | 300 | 310 | 300 | 290 | 310 |  | 300 | 310 | 290 | 300 | 300 | 290 | 325 | 7349000
| Bibiyana South 400 MW | 401 | 400 | 400 | 400 | 401 | 401 | 392 | 394 | 400 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 261 | 260 |  | 259 | 260 | 260 | 260 | 260 | 260 | 260 | 7461300
58 | Nababganj 55 MW PP (Southern power ) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 55 | 55 | 55 | 35 | 35 | 35 | 35 | 908152
59 | Tangail Palli Power Gen 22 MW | 9 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 6 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 288480
60 | Barabkunda 22 MW PP (Regent) | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 |  | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 313968
61 | Narshingdi 22 MW PP (Doreen) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  |  | 0 | 16 | 16 | 16 |  | 19 | 19 | 19 | 16 | 16 | 19 | 19 | 353736
62 | Tangail 22 MW PP (Doreen)
63 | Impoprt (Tripura) | 100 | 98 | 96 | 94 | 94 | 88 | 78 | 114 | 114 | 118 | 126 | 127 | 140 | 144 | 92 | 82 | 74 | 90 |  | 106 | 104 | 106 | 156 | 158 | 172 | 156 | 2691840
64 | Malancha, Ctg. EPZ (United) | 35 | 38 | 39 | 39 | 39 | 39 | 35 | 13 | 3 | 5 | 12 | 10 | 13 | 10 | 6 | 7 | 12 | 6 |  | 0 | 19 | 25 | 31 | 34 | 37 | 37 | 556320
65 | Feni 22MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 447876
66 | Feni 11 MW PP (Doreen) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 227160
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 27 | 20 | 15 | 16 | 16 | 16 | 15 | 16 | 21 | 21 | 21 |  | 25 | 25 | 33 | 33 | 33 | 33 | 33 | 635000
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 494760
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 602460
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 787600
72 | Rupganj 33 MW PP(Summit) | 15 | 15 | 15 | 16 | 17 | 17 | 15 | 15 | 14 | 14 | 14 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 15 | 15 | 16 | 329800
73 | Ghorashal 108MW PP (Regent) | 90 | 91 | 92 | 92 | 92 | 92 | 92 | 84 | 81 | 80 | 76 | 76 | 76 | 74 | 74 | 74 | 72 | 72 |  | 76 | 80 | 79 | 83 | 87 | 92 | 93 | 1940363
| Feni Lanka Power | 17 | 16 | 16 | 16 | 16 | 0 | [11 empty] | 0 |  | 15 | 20 | 34 | 50 | 52 | 52 | 17 | 283860
| Chowmuhani 113 MW | 95 | 97 | 96 | 96 | 95 | 97 | 98 | 95 | 97 | 94 | 94 | 96 | 94 | 94 | 93 | 94 | 98 | 109 |  | 107 | 114 | 113 | 115 | 115 | 113 | 114 | 2420040
| Manikgonj 162MW PP(MPGL) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 24 | 72 | 72 | 72 | 72 | 75 | 72 | 72 | 80 | 162 |  | 162 | 162 | 162 | 162 | 162 | 144 | 17 | 1765440
77 | Siddhirganj 100 PP(Dutch Bangla) | 40 | 39 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 33 | 40 | 40 | 40 | 45 | 63 |  | 72 | 72 | 72 | 72 | 80 | 80 | 47 | 1171200
78 | Gazipur 52 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 18 | 24 | 24 | 24 | 24 | 26 | 30 |  | 41 | 41 | 41 | 41 | 41 | 41 | 16 | 598560
79 | Kodda 150MW PP | 50 | 50 | 50 | 50 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 66 |  | 98 | 98 | 98 | 115 | 115 | 53 | 48 | 992160
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 16 | 43 | 43 | 35 | 41 | 8 | 8 | 318581
| Gazipur 100 MW PP | 50 | 50 | 50 | 50 | 50 | 50 | 46 | 46 | 46 | 46 | 30 | 0 |  | 17 | 32 | 32 | 47 | 48 |  | 47 | 47 | 47 | 47 | 47 | 47 | 48 | 1000800
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 2 | 4 | 3 | 3 | 4 | 4 | 4 | 2 | 1 | 1 | 0 | [8 empty] | 30359
| Jodiac Power | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 17 | 17 | 17 | 17 | 17 | 17 | 27 | 36 | 36 |  | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 786131
| Karnaphuli Power Ltd. | 73 | 73 | 73 | 73 | 73 | 58 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 65 | 72 | 72 | 72 | 75 | 1523012
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP ( Summit) | 115 | 118 | 120 | 122 | 120 | 125 | 125 | 122 | 125 | 125 | 118 | 110 | 110 | 115 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 115 | 122 | 2811520
87 | Meghnaghat 100 MW(IEL) | 42 | 41 | 41 | 41 | 41 | 41 | 38 | 41 | 41 | 41 | 41 | 41 | 41 | 43 | 40 | 41 | 44 | 55 |  | 70 | 73 | 72 | 66 | 71 | 73 | 48 | 1162560
| Meghnaghat 104 MW PP (OPCL) | 55 | 55 | 55 | 55 | 55 | 54 | 17 | 45 | 55 | 55 | 54 | 55 | 55 | 58 | 64 | 54 | 54 | 68 |  | 92 | 92 | 92 | 92 | 91 | 92 | 57 | 1495680
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 78 |  | 78 | 78 | 78 | 78 | 78 | 78 | 33 | 1035120
92 | Fenchuganj 44MW (Energyprima) | 0 | 13 | 39 | 45 | 48 | 49 | 48 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 |  | 6 | 6 | 6 | 6 | 49 | 49 | 49 | 518112
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1240989
94 | Gagnagar 102 MW PP (Digital Power) | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 92 | 92 | 92 | 92 | 90 | 84 | 40 | 1202256
95 | Patenga 50MW PP (Baraka) | 25 | 25 | 25 | 25 | 25 | 25 | 7 | 24 | 25 | 2 | 18 | 19 | 24 | 16 | 23 | 25 | 24 | 5 |  | 0 | 1 | 25 | 25 | 25 | 25 | 25 | 490080
96 | Chattogram 108 MW PP (ECPV) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 14 |  | 48 | 76 | 79 | 84 | 87 | 31 | 11 | 5702400
97 | katpotti 52 MW
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 40 | 40 | 40 | 40 | 40 | 54 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1267982
100 | Manikganj 55 MW PP (Northern) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  |  | 35 | 35 | 35 | 35 | 35 | 35 | 55 |  | 55 | 55 | 55 | 55 | 35 | 35 | 35 | 871983
101 | Kushiara 163 MW CCPP (KP)
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | [8 empty] | 62100
103 | Kamalaghat 54 MW PP(Banco Energy) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 35 | 650520
104 | Keranigonj 300 MW PP (APR) | 225 | 177 | 75 | 11 | 11 | 0 |  | 10 | 100 | 222 | 224 | 220 | 221 | 225 | 225 | 221 | 137 | 225 |  | 65 | 122 | 187 | 225 | 225 | 204 | 225 | 3664055
105 | Bramhangoan 100 MW PP (Aggreko) | 80 | 80 | 80 | 80 | 40 | 0 |  |  | 50 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 85 |  | 90 | 90 | 90 | 90 | 90 | 85 | 80 | 1623779
106 | Mymensingh 200 MW PP (United) | 95 | 95 | 95 | 95 | 95 | 94 | 95 | 113 | 152 | 107 | 106 | 98 | 97 | 97 | 97 | 106 | 107 | 106 |  | 96 | 97 | 97 | 87 | 87 | 87 | 86 | 2388000
112 | Aurahati 100MW PP (Aggreko) | 80 | 80 | 80 | 80 | 25 | 0 |  | 25 | 25 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 90 |  | 40 | 62 | 90 | 90 | 90 | 90 | 81 | 1598818
114 | Kodda 149 MW PP Unit-1 (Summit) | 149 | 149 | 149 | 143 | 143 | 138 | 122 | 117 | 112 | 122 | 124 | 128 | 132 | 131 | 132 | 132 | 132 | 132 |  | 132 | 132 | 132 | 132 | 147 | 149 | 135 | 3262180
115 | Juldah 100 MW PP Unit-3 (Acorn) | 33 | 33 | 33 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 32 | 1097280
116 | Chandpur 200MW (Desh energy) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 34 | 17 | 17 | 17 | 17 | 67 | 150 |  | 150 | 150 | 158 | 156 | 156 | 156 | 64 | 1371360
117 | Ashuganj 150MW PP (Midland) | 145 | 143 | 143 | 138 | 138 | 100 | 107 | 117 | 112 | 115 | 118 | 118 | 115 | 110 | 112 | 122 | 128 | 130 |  | 125 | 130 | 127 | 130 | 137 | 137 | 135 | 3046036
118 | Bibiyana-III 400 MW CCPP | 401 | 401 | 401 | 401 | 401 | 401 | 405 | 403 | 387 | 402 | 404 | 403 | 401 | 402 | 376 | 403 | 403 | 398 |  | 401 | 403 | 403 | 403 | 403 | 401 | 402 | 9561000
| Jamalpur 115 MW PP (United) | 107 | 108 | 107 | 108 | 108 | 0 |  |  | 67 | 101 | 103 | 107 | 107 | 107 | 107 | 96 | 97 | 97 |  | 107 | 107 | 107 | 115 | 115 | 115 | 115 | 2163600
| Anwara 300 MW PP (United) | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 151 |  | 161 | 161 | 161 | 161 | 163 | 165 | 173 | 3871527
| Juldah unit-2 (Acorn) | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 |  | 100 | 100 | 100 | 100 | 100 | 100 | 54 | 1237440
| Anlima Energy Ltd. | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 92 | 107 | 107 | 107 | 107 | 107 | 107 |  | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 2570564
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 444240
| Spectra Solar Plant Ltd. | [5 empty] | 0 | 5 | 7 | 10 | 7 | 13 | 27 | 25 | 33 | 15 | 4 | 0 | [9 empty] | 142525
| Chandpur 115(Doreen) | 38 | 35 | 35 | 34 | 34 | 34 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 34 | 35 | 44 | 75 |  | 85 | 96 | 97 | 96 | 96 | 96 | 47 | 1207680
| Kanchan Purbachal Power Generation Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 18 | 18 | 18 | [10 empty] | 0 | 11 | 17 | 17 |  | 254880
Mirsharai 150 MW (Oil)
Mirsharai 150 MW (Gas)
120 | Eastern Zone Total | 7267 | 7225 | 7182 | 7125 | 6990 | 6497 | 6498 | 6498 | 6847 | 7103 | 7182 | 7126 | 7069 | 7036 | 7023 | 6971 | 7015 | 7630 |  | 7748 | 8077 | 8210 | 8454 | 8495 | 8420 | 7721 | 181435858
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
Khulna 115 PP MW (KPCL-2)
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 11 | 11 | 11 | 11 | 11 | 4 | 0 | [6 empty] | 0 | 4 | 14 | 10 | 30 |  | 50 | 0 | 0 | 10 | 15 | 16 | 16 | 183360
| Khulna 225 MW CCPP | 225 | 227 | 226 | 226 | 226 | 188 | 180 | 190 |  |  |  |  | 5 | 15 | 15 | 50 | 50 | 50 |  | 46 | 60 | 77 | 145 | 180 | 210 | 224 | 2927040
129 | Rupsha 105 MW PP (Orion rupsha) | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 |  |  |  | 35 | 53 | 53 | 53 | 53 | 53 | 53 |  | 70 | 70 | 70 | 70 | 70 | 70 | 35 | 1050720
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 1 | 24 | 24 |  |  | 84 | 87 | 46 | 69 | 34 | 41 | 13 | 1 |  | 0 | [6 empty] | 500400
131 | Rampal 1320 MW (BIFPCL) | 102 | 102 | 101 | 107 | 100 | 100 | 101 | 101 | 30 | [16 empty] | 122 | 1999600
132 | United Payra Power Ltd. | [13 empty] | 31 | 54 | 54 | 54 | 54 |  | 54 | 54 | 20 | 0 |  |  |  | 362400
133 | Bhola Nutan Biddut BD LTD (GAS) | 226 | 227 | 226 | 226 | 227 | 226 | 222 | 224 | [7 empty] | 0 | 7 | 10 |  | 35 | 35 | 50 | 139 | 224 | 224 | 225 | 2867891
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  |  |  |  | 16 | 110 | 110 | 110 | 110 |  | 110 | 110 | 32 | 32 | 32 | 32 | 32 | 899904
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 85 | 86 | 86 | 86 | 86 | 87 | 84 | 85 | [12 empty] | 0 | 15 | 30 |  | 65 | 65 | 898684
140 | Bhola 33 MW PP (Venture) | 31 | 30 | 29 | 28 | 27 | 23 | 21 | 19 | 18 | 22 | 23 | 23 | 26 | 25 | 27 | 27 | 25 | 26 |  | 36 | 36 | 36 | 38 | 36 | 36 | 32 | 663718
141 | Noapara 100 MW PP (Bangla Trac) | 90 | 89 | 89 | 80 | 50 | 0 |  |  |  |  | 77 | 85 | 70 | 89 | 90 | 90 | 50 | 75 |  | 60 | 90 | 89 | 89 | 60 | 60 | 88 | 1476480
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP | 35 | 28 | 28 | 28 | 28 | 28 | 20 | [9 empty] | 0 | 3 |  | 0 | [6 empty] | 211200
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | [13 empty] | 0 | 15 | 15 | 15 | 32 |  | 0 |  | 0 | 32 | 32 | 32 | 15 | 207792
146 | Bheramara HVDC | 891 | 891 | 891 | 892 | 891 | 892 | 892 | 891 | 569 | 0 | 519 | 891 | 891 | 891 | 891 | 892 | 892 | 891 |  | 891 | 891 | 891 | 891 | 891 | 891 | 902 | 19905454
147 | Bheramara 410 MW CCPP | 235 | 235 | 240 | 245 | 250 | 250 | 250 | 240 | [12 empty] | 0 | 65 | 80 | 130 | 180 | 180 | 2782944
148 | Payra 1320 MW | 950 | 950 | 920 | 900 | 870 | 850 | 790 | 770 | 760 |  |  | 60 | 190 | 270 | 390 | 470 | 500 | 520 |  | 440 | 430 | 420 | 430 | 660 | 1020 | 950 | 15625200
149
150 | Barapukuria TPP Unit-1 | 81 | 81 | 81 | 82 | 81 | 82 | 82 | 81 | 80 | 81 | 81 | 81 | 80 | 80 | 80 | 80 | 80 | 81 |  | 81 | 82 | 82 | 82 | 82 | 82 | 81 | 1987199
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 250 | 249 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 |  | 250 | 250 | 250 | 250 | 250 | 249 | 250 | 6024600
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [17 empty] | 0 |  | 18 | 30 | 32 | 32 | 32 | 32 | 32 | 178464
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 1 | 1 | 0 | 0 | [8 empty] | 20040
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 194 | 194 | 193 | 193 | 193 | 192 | 194 | 198 | 195 | 204 | 205 | 206 | 205 | 206 | 205 | 206 | 206 | 205 |  | 205 | 205 | 206 | 206 | 205 | 206 | 203 | 5147664
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
| Sirajgonj 225 MW CCPP Unit-2 (Oil) | 219 | 220 | 220 | 205 | 193 | 193 | 194 | 194 | 193 | 203 | 213 | 211 | 213 | 213 | 211 | 214 | 216 | 213 |  | 213 | 220 | 219 | 219 | 219 | 219 | 215 | 5246136
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 188 | 190 | 193 | 196 | 197 | 197 | 199 | 202 | 195 | 193 | 198 | 204 | 205 | 206 | 205 | 209 | 210 | 210 |  | 202 | 202 | 202 | 202 | 201 | 202 | 201 | 5080282
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 425 | 427 | 425 | 429 | 431 | 428 | 419 | 416 | 414 | 416 | 414 | 414 | 416 | 415 | 415 | 420 | 416 | 414 |  | 395 | 414 | 420 | 420 | 418 | 418 | 418 | 10061454
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 0 | 15 | 17 | 21 | 20 | 21 | 21 | 20 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 473760
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 10 | 10 | 11 | 11 | 11 | 11 | 11 | 11 | 0 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 192402
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP | 24 | 0 | [14 empty] | 0 | 6 |  | 24 | 32 | 32 | 32 | 32 | 23 | 16 | 156578
168 | Santahar 50 MW Peaking PP | [17 empty] | 0 |  | 28 | 26 | 26 | 26 | 26 | 26 | 26 | 141079
169 | Natore 52 MW PP (Rajlanka) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | [6 empty] | 0 | 8 | 8 |  | 10 | 43 | 43 | 43 | 34 | 34 | 8 | 257746
170 | Chapainawabganj 100 MW Peaking PP | [17 empty] | 0 |  | 56 | 80 | 80 | 80 | 80 | 45 | 30 | 358104
171 | Baghabari 200 MW PP (Paramount) | 155 | 120 | 10 | 10 | 0 |  |  |  |  | 45 | 161 | 165 | 161 | 162 | 163 | 157 | 163 | 165 |  | 165 | 165 | 164 | 164 | 157 | 166 | 166 | 2760104
| Bagura 113 MW PP (Confidence)-2 | 50 | 50 | 50 | 50 | 50 | 35 | 35 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 94 | 94 |  | 94 | 94 | 94 | 94 | 94 | 94 | 50 | 1648224
172 | Confidence Power Bogura Unit-1 113 MW | 95 | 95 | 95 | 95 | 95 | 35 | 35 | 55 | 55 | 55 | 55 | 75 | 75 | 75 | 75 | 75 | 75 | 75 |  | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 1809504
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP | [17 empty] | 0 |  | 8 | 0 | [5 empty] | 7000
176 | Rangpur 113 MW PP (Confidence) | 56 | 56 | 56 | 56 | 56 | 56 | 34 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 90 | 92 |  | 92 | 92 | 92 | 92 | 92 | 92 | 56 | 1568774
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 0 | 2 | 2 | 4 | 3 | 3 | 6 | 5 | 3 | 2 | 1 |  | 0 | [6 empty] | 30974
178 | Energypac Power Venture Thakurgaon Ltd. | [9 empty] | 17 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 50 |  | 90 | 90 | 90 | 90 | 90 | 90 |  | 772608
178 | Intraco Solar 30 MW | [5 empty] | 0 |  |  |  | 19 | 16 | 22 | 21 | 11 | 15 | 7 | 3 | 1 |  | 0