## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID COMPANY OF BANGLADESH LTD.
SYSTEM OPERATION DATA
Month:July 2022
Sl. | Items | Current Month |  | Previous Month |  | This Month Last Year |  | Max. Till-to-date
|  | 2022-07-01 |  | 2022-06-01 |  | 2021-07-01
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 13765 | 2022-07-17 | 14038 | 2022-06-08 | 13525 | 44392 | 14782 | 2022-04-16
|  |  | 21:00 |  | 23:00 |  | 21:00 |  | 21:00
2 | Minimum Generation (MW) | 7802 | 2022-07-10 | 8231 | 2022-06-17 | 6682 | 2021-07-29 | - | -
|  |  | 6:00 |  | 6:00 |  | 1:00 |  | -
3 | Maximum Evening Peak Generation (MW) | 13765 | 2022-07-17 | 14004 | 2022-06-06 | 13525 | 2021-07-15 | 14782 | 2022-04-16
|  |  | 21:00 |  | 21:00 |  | 21:00 |  | 21:00
4 | Maximum Day Peak Generation (MW) | 12258 | 2022-07-18 | 12226 | 2022-06-08 | 11549 | 2021-07-15 | 12895 | 2022-04-26
|  |  | 10:00 |  | 12:00 |  | 12:00 |  | 12:00
5 | Maximum Evening Peak Demand (MW) Estimated | 15001 | 2022-07-19 | 14038 | 2022-06-08 | 13525 | 2021-07-15 | 14782 | 2022-04-16
|  |  | 21:00 |  | 12:00 |  | 21:00 |  | 12:00
6 | Average Generation (MW) at Evening Peak | 12574.9032 |  | 13051.7667 |  | 11656.2903 |  | 13536.33 | 2022-04-27
7 | Average Generation (MW) at Day Peak | 10718.3548 |  | 11161.4333 |  | 9260.4516 |  | 11233.4 | 2022-04-27
8 | Maximum Power Import from India, BIPTC (MW) | 926 | 2022-07-17 | 933 | 2022-06-07 | 907 | 2021-07-01 | 956 | 27/3/2019
|  |  | 1:30 |  | 2:00 |  | 0:30 |  | 19:00
9 | Maximum Power Import from Tripura, India (MW) | 182 | 2022-07-19 | 188 | 2022-06-08 | 172 | 2021-07-10 | 194 | 12/06/19
|  |  | 23:00 |  | 21:00 |  | 23:00 |  | 19:00
10 | Maximum Load Shed (MW) at Evening Peak | 2385 | 2022-07-19 | - | - | - | - | 1459 | 04/05/2010
|  |  | 21:00 |  | - |  |  |  | 20:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | 11739 | 2022-07-19 | - | - | - | - | 13792 | 2021-04-27
|  | - | 21:00 | - | - | - | - |  | 20:00
12 | Minimum Load Shed (MW) at Evening Peak | 0 | - | - | - | - | -
13 | Generation During Min. Load Shed (MW) at Evening Peak | - | - | - | - | - | -
14 | Maximum Load Shed (MW) at Day Peak | - | - | - | - | - | -
15 | Generation During Max. Load Shed (MW) at Day Peak | - | - | - | - | - | -
16 | Minimum Load Shed (MW) at Day Peak | - | - | - | - | - | -
17 | Generation During Min. Load Shed (MW) at Day Peak | - | - | - | - | - | -
18 | Nos. of Days Load Shed at Evening Peak | - |  | - |  | -
19 | Nos. of Days Load Shed at Day Peak | - |  | - |  | -
20 | Gross Generation of BPDB (MKWH) | 1773.1307 |  | 1590.9771 |  | 1852.5058 |  | 3805.72 | 2019-09-19
21 | Station Use of BPDB (MKWH) | 135.2896 |  | 84.3577 |  | 113.9022
22 | Net Generation of BPDB (MKWH) | 1637.8411 |  | 1506.6194 |  | 1738.6035
23 | Net Generation of IPP (MKWH) | 5534.1867 |  | 5289.635 |  | 4403.448
24 | Net Generation of REB (MKWH) | 130.5165 |  | 122.8415 |  | 129.0256
24 | Net Generation of Rental Power Plant (MKWH) | 382.0653 |  | 624.4748 |  | 427.9978
25 | Total Net Generation (MKHWh) (BPDB, IPP, RPP & REB) | 7684.6096 |  | 7543.5707 |  | 6699.0748 |  | 7842.9924 | April'22
26 | Energy Generation by Gas (MKWH) | 4256.9757 |  | 4234.9012 |  | 4815.0058 |  | 4756.96 | Sep-19
27 | Energy Generation by Diesel (MKWH) | 240.1426 |  | 491.7382 |  | 290.9346 |  | 771.52 | July-18
28 | Energy Generation by Furnace Oil (MKWH) | 2402.1611 |  | 2164.1587 |  | 1187.2509 |  | 2365.7466 | April'22
29 | Energy Generation by Hydro (MKWH) | 88.9738 |  | 52.8346 |  | 61.0975 |  | 151.4 | August-19
30 | Energy Generation by Solar (MKWH) | 38.5148 |  | 25.0967 |  | 16.6657 |  | 40.58 | March-22
31 | Energy Generation by Coal (MKWH) | 793.1312 |  | 659.199 |  | 442.0225 |  | 793.13 | July'22
32 | Enegry Import from India (BIPTC & AC) (MKWH) | 681.8974 |  | 738.4142 |  | 659.2349 |  | 775.9511 | August-20
33 | Monthly Load Factor (%) | 91.9201 |  | 88.6952 |  | 74.2573 |  | 91.59 | July'22

## QF-LDC-22
Page: 1/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month:July 2022
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quantity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 13765 | 2022-07-17 | 21:00
Generation Period
| Dhaka | MW | 4411.49
| Chattogram | MW | 1370
| Cumilla | MW | 1313
| Mymensingh | MW | 989
| Sylhet | MW | 545
a) | Total supply in East zone | MW | 8628.49
| Khulna | MW | 1700.4
| Barisal | MW | 395.88
| Rajshahi | MW | 1536.2
| Rangpur | MW | 950
b) | Total supply in West zone | MW | 4582.48
c) | Total supply in both zone ( a+b) | MW | 13210.97
Ref: | 27.21.0000.603.16.087.20.538 | Date: 21/08/2022
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
Page: 2/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month:July 2022
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Daily Maximum power Export through EWI/ NO-1
| a) Ghorashal end | AMPS
| b) Ishurdi end | MW | 720 | 2022-07-10 | 23:00
18 | Daily Maximum power Import through EWI/ NO-1 |  | 500 | 2022-07-31 | 12:00
| a) Ghorashal end | AMPS
| b) Ishurdi end | MW | 1200 | 2022-07-31 | 12:00
19 | Daily Maximum Energy Export through EWI/NO-1 |  | 266 | 2022-07-10 | 20:00
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
20 | Daily Maximum Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
21 | Total Energy Export through EWI/ NO-1
| a) Ghorashal end | MKWH | 21.52
| b) Ishurdi end | MKWH | 155.25
22 | Total Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | -
| b) Ishurdi end | MKWH | -
23 | Transmission loss of EWI/ NO-1 | % | 3
24 | Daily Maximum power Export through EWI/ NO-2
| a) Ashuganj end | MW | 280 | 2022-07-10 | 20:00
| b)Serajganj end | MW | 670 | 2022-07-31 | 18:00
25 | Daily Maximum power Import through EWI/ NO-2
| a) Ashuganj end | MW | 570 | 2022-07-26 | 9:00
| b)Sirajganj end | MW | 270 | 2022-07-10 | 20:00
26 | Daily Maximum Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 3.02 | 2022-07-10
| b)Sirajganj end | MKWH | 3 | 2022-07-10
27 | Daily Maximum Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | - | -
| b)Sirajganj end | MKWH
28 | Total Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 18.87
| b)Sirajganj end | MKWH | 183.63
29 | Total Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | 176.81
| b)Sirajganj end | MKWH | 19.04
30 | Transmission loss of EWI /NO-2 | % | 3.286%
* Total energy export from Ghorasal end and import from Ishurdi end and the transmission loss of EWI/NO-1 is taken
from the calculation of GMD, PGCB, Ishwardi.
* *Total energy export from Ashuganj end and import from Sirajganj end and the transmission loss of EWI/NO-2 is taken
from the calculation of Sirajganj switching sub station.
* **The energy meter of Ghorasal end is out of order.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-23
QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: July2022
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Kodda | 132/33 kV transformer T-2 | 2022-07-02 12:30 | 2022-07-02 14:15 | 1:45 | E/O | Due to red-hot maint | 30 | 52.5 | Power interruption
Netrakona | 132/33 kV transformer T-2 | 2022-07-02 12:56 | 2022-07-02 14:52 | 1:56 | E/O | Due to red-hot maint | 30 | 58 | Power interruption
| 132/33 kV transformer T-1 | 2022-07-02 14:52 | 2022-07-02 19:00 | 4:08 | T | Tripped showing buchholz . relay | 10 | 41.3333 | Power interruption
| 132/33 kV transformer T-1 | 2022-07-02 14:52 | 2022-07-02 14:57 | 0:05 | E/O | Tripped showing abnormal sound | 0 | 0 | No interruption
| 132/33 kV transformer T-2 | 2022-07-03 16:17 | 2022-07-03 17:28 | 1:11 | E/O | Due to red-hot maint at 33 kV Bus | 0 | 0 | No interruption
Kishoreganj | 132/33 kV transformers T-1 & T-2 | 2022-07-04 13:42 | 2022-07-04 14:44 | 1:02 | T | Due to 33 kV feeder fault | 90 | 93 | Power interruption
| 132/33 kV transformers T-1 & T-2 | 2022-07-05 06:38 | 2022-07-05 06:40 | 0:02 | T | Tripped showing O/C . relay at 33 kV feeder | 55 | 1.8333 | Power interruption
Mymensingh | 132/33 kV transformers T-1 & T-2 | 2022-07-05 07:15 | 2022-07-05 07:25 | 0:10 | T | Due to 33 kV feeder fault | 116 | 19.3333 | Power interruption
| 132/33 kV transformers T-1 & T-2 | 2022-07-07 11:11 | 2022-07-07 11:17 | 0:06 | T | Tripped showing buchholz . relay | 140 | 14 | Power interruption
Netrakona | 132/33 kV transformer T-2 | 2022-07-16 09:50 | 2022-07-16 09:50 | 0:00 | T |  | 0 | 0 | No interruption
Tongi | 132/33 kV transformers T-1 & T-2 | 2022-07-20 11:11 | 2022-07-20 11:17 | 0:06 | T | Tripped showing O/C . relay | 0 | 0 | No interruption
Dhamrai | 132/33 kV transformer T-1 | 2022-07-28 10:13 | 2022-07-28 12:53 | 2:40 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Sherpur | 132/33 kV transformer T-1 | 2022-07-28 11:37 | 2022-07-28 13:56 | 2:19 | T | Tripped showing O/C . relay | 0 | 0 | No interruption
Kishoreganj | 132/33 kV transformer T-3 | 2022-07-29 19:40 | 2022-07-30 11:03 | 15:23 | T | Due to 33 kV feeder fault | 28 | 10.2667 | Power interruption 19:40 to 20:02
Netrakona | 132/33 kV transformer T-2 | 2022-07-30 08:12 | 2022-07-30 08:12 | 0:00 | T | Tripped showing buchholz . relay | 0 | 0 | No interruption
|  |  | Total : | 30:53 |  | Unserved Energy: |  | 290.2667
Dhaka (South) Grid Circle :
Keraniganj | 132/33 kV transformers T-1 & T-2 | 2022-07-15 14:59 | 2022-07-15 15:36 | 0:37 | T | Tripped showing O/C . relay at 33 kV feeder | 38 | 23.4333 | Power interruption
| 132/33 kV transformer T-2 | 2022-07-16 16:08 | 2022-07-16 17:19 | 1:11 | T | Due to 33 kV feeder fault | 0 | 0 | No interruption
Ghorashal | 132 kV Bus-2 | 2022-07-19 00:25 | 2022-07-19 00:40 | 0:15 | T | Due to breaker of Narsinghdi Ckt-2 got locked | 0 | 0 | No interruption
Hasnabad | 33 kV Bus | 2022-07-24 12:05 | 2022-07-24 16:14 | 4:09 | T | Due to 33 kV feeder fault | 23 | 95.45 | Power interruption
| 132/33 kV transformer T-2 | 2022-07-24 17:35 | 2022-07-25 11:12 | 17:37 | T | Tripped showing O/C . relay at 33 kV feeder
Nawabganj | 132/33 kV transformer T-1 | 2022-07-27 06:39 | 2022-07-27 07:31 | 0:52 | E/O | Due to red-hot maint. | 0 | 0 | No interruption
| 132/33 kV transformer T-2 | 2022-07-27 07:39 | 2022-07-27 08:43 | 1:04 | E/O | Due to red-hot maint. | 0 | 0 | No interruption
Rampura | 230 kV Bus-1 | 2022-07-27 11:02 | 2022-07-27 11:40 | 0:38 | T | Tripped showing O/C . relay | 0 | 0 | No interruption
|  |  | Total : | 26:23 |  | Unserved Energy: |  | 118.8833
Chattogram Grid Circle :
Bakulia | 132/33 kV transformer T2 | 2022-07-02 18:14 | 2022-07-02 18:22 | 0:08 | T | Tripped showing O/C. relay | 0 | 0 | No interruption
Dohazari | 132/33 kV transformer T2 | 2022-07-04 06:56 | 2022-07-04 08:32 | 1:36 | E/O | Due to red-hot maint.at 33 kV side | 0 | 0 | No interruption
Cox'sbazar | 132/33 kV transformers T-2 & T3 with 33 kV Bus | 2022-07-05 15:46 | 2022-07-05 15:59 | 0:13 | T | Tripped showing O/C. relay | 40 | 8.6667 | Power interruption
Bakulia | 132/33 kV transformers T-1 & T2 | 2022-07-06 08:46 | 2022-07-06 08:56 | 0:10 | T | Due to 33 kV feeder fault | 44 | 7.3333 | Power interruption
GPH | 230/132 kV transformer T-01 | 2022-07-13 10:54 | 2022-07-13 12:13 | 1:19 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Dohazari | 132/33 kV transformer T-1 with 33 kV Bus | 2022-07-15 07:08 | 2022-07-15 08:12 | 1:04 | E/O | Due to red-hot maint. | 15 | 16 | Power interruption
Halishahar | 132/33 kV transformer T1 | 2022-07-27 03:20 | 2022-07-27 03:46 | 0:26 | T | Tripped showing O/C. relay | 0 | 0 | No interruption
Khulshi | 132/33 kV transformer T2 | 2022-07-27 05:34 | 2022-07-27 06:40 | 1:06 | E/O | Due to red-hot maint. | 0 | 0 | No interruption
PHP | 230/132 kV transformer T-01 | 2022-07-28 11:38 | 2022-07-28 12:50 | 1:12 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Matarbari | 132/33 kV transformer T1 | 2022-07-31 02:30 | 2022-07-31 04:08 | 1:38 | T | Tripped showing E/F. relay | 0 | 0 | No interruption
| 132/33 kV transformers T-1 & T2 | 2022-07-31 04:32 | 2022-07-31 04:52 | 0:20 | T | Due to 33 kV feeder fault | 0 | 0 | No interruption
Khagrachari | 132/33 kV transformer T2 | 2022-07-31 18:09 | 2022-07-31 21:06 | 2:57 | T | Tripped showing winding tem.high | 0 | 0 | No interruption
|  |  | Total : | 12:09 |  | Unserved Energy: |  | 32
Cumilla Grid Circle :
Ashuganj | 230/132 kV transformer OAT12 | 2022-07-02 18:58 | 2022-07-02 19:32 | 0:34 | T | Tripped showing O/C. relay | 0 | 0 | No interruption
| 230/132 kV transformer OAT2 | 2022-07-03 15:40 | 2022-07-03 15:40 | 0:00 | T | Tripped showing O/C. relay | 0 | 0 | No interruption
| 230/132 kV transformer OAT12 | 2022-07-05 00:16 | 2022-07-05 00:43 | 0:27 | T | Tripped showing O/C. relay | 0 | 0 | No interruption
Beanibazar | 132/33 kV transformers T1 | 2022-07-11 14:30 | 2022-07-11 15:05 | 0:35 | T | Due to 33 kV feeder fault | 56 | 32.6667 | Power interruption
| 132/33 kV transformers T2 | 2022-07-11 14:30 | 2022-07-11 15:38 | 1:08 | T
Ashuganj | 132 kV all reactor | 2022-07-14 19:44 | 2022-07-14 21:00 | 1:16 | E/O | Due to thundering | 746 | 944.9333 | Power interruption
Shahjibazar | 132/33 kV transformer T4 | 2022-07-16 08:34 | 2022-07-16 09:13 | 0:39 | T | Due to red-hot maint.at 33 kV feeder fault | 40 | 26 | Power interruption
Chatak | 132/33 kV transformer T2 | 2022-07-16 15:19 | 2022-07-16 16:18 | 0:59 | T | Due to red-hot maint.at 33 kV feeder fault | 4 | 3.9333 | Power interruption
Chowmuhani | 132/33 kV transformer T3 | 2022-07-17 09:50 | 2022-07-17 18:56 | 9:06 | E/O | Due to bursting of Y-phase CB | 0 | 0 | No interruption
Ashuganj | 230/132 kV transformer OAT12 | 2022-07-17 20:36 | 2022-07-17 20:49 | 0:13 | T | Tripped showing O/C. relay | 0 | 0 | No interruption
B.Baria | 132/33 kV transformers T1 & T2 | 2022-07-19 10:10 | 2022-07-19 10:54 | 0:44 | T | Due to 33 kV feeder fault | 10 | 7.3333 | Power interruption
Chaddagram | 132/33 kV transformer T1 | 2022-07-19 13:31 | 2022-07-19 14:46 | 1:15 | E/O | Due to red-hot maint. | 0 | 0 | No interruption
Ramganj | 132/33 kV transformer T1 | 2022-07-21 21:33 | 2022-07-21 22:47 | 1:14 | E/O | Due to red-hot maint. | 40 | 49.3333 | Power interruption
Chatak | 132/33 kV transformer T2 | 2022-07-23 20:24 | 2022-07-24 10:41 | 14:17 | T | Due to 33 kV feeder fault | 0 | 0 | No interruption
Shahjibazar | 132/33 kV transformer T4 | 2022-07-29 09:36 | 2022-07-29 12:15 | 2:39 | E/O | Due to red-hot maint. | 0 | 0 | No interruption
Ashuganj | 230/132 kV transformer OAT12 | 2022-07-31 03:23 | 2022-07-31 03:23 | 0:00 | E/O | Due to Oil leakage | 0 | 0 | No interruption
|  |  | Total : | 35:06 |  |  |  | 1064.2
Khulna Grid Circle :
Barishal | 132/33 kV transformers T4 & T5 | 2022-07-01 00:07 | 2022-07-01 00:20 | 0:13 | T | Tripped showing under frequency | 57 | 12.35 | Power interruption
Barishal(S) | 132/33 kV transformer T1 | 2022-07-02 08:25 | 2022-07-02 10:13 | 1:48 | E/O | Due to red-hot maint | 15 | 27 | Power interruption
Mongla | 132/33 kV transformers T1 & T2 | 2022-07-02 18:59 | 2022-07-02 19:26 | 0:27 | T | Tripped showing O/C relay | 28 | 12.6 | Power interruption
Rajbari | 132/33 kV transformer T1 | 2022-07-04 10:55 | 2022-07-04 12:34 | 1:39 | E/O | Due to red-hot maint | 18 | 29.7 | Power interruption
Barishal(N) | 132/33 kV transformer T4 | 2022-07-07 09:04 | 2022-07-07 15:44 | 6:40 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Narial | 132/33 kV transformer T2 | 2022-07-09 07:33 | 2022-07-09 08:24 | 0:51 | E/O | Due to red-hot maint | 10 | 8.5 | Power interruption
Khulna© | 132/33 kV transformer T-3 | 2022-07-13 07:07 | 2022-07-13 08:30 | 1:23 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Faridpur | 132/33 kV transformer T3 | 2022-07-13 08:55 | 2022-07-13 14:34 | 5:39 | E/O | Due to bursting of 33 kV cable burst | 0 | 0 | No interruption
Payra | 132/33 kV transformer ATR-1 | 2022-07-13 15:26 | 2022-07-13 17:17 | 1:51 | E/O | Due to over fluxing | 0 | 0 | No interruption
Mongla | 132/33 kV transformers T1 & T2 | 2022-07-17 04:18 | 2022-07-17 05:14 | 0:56 | T | Tripped showing O/C relay at 33 kV side | 25 | 23.3333 | Power interruption
Noapara | 132/33 kV transformer T2 | 2022-07-17 06:04 | 2022-07-17 12:20 | 6:16 | T | Tripped showing PRD relay | 0 | 0 | No interruption
| 132/33 kV transformer T2 | 2022-07-20 07:16 | 2022-07-20 07:52 | 0:36 | T | Tripped showing PRD relay | 0 | 0 | No interruption
Magura | 132/33 kV transformer T1 | 2022-07-23 01:32 | 2022-07-23 10:32 | 9:00 | T | Due to winding temp.high | 17 | 153 | Power interruption
| 132/33 kV transformer T2 | 2022-07-23 01:32 | 2022-07-23 01:48 | 0:16 | T |  | 48 | 12.8 | Power interruption
Khulna© | 132/33 kV transformer T-3 | 2022-07-24 06:03 | 2022-07-24 06:31 | 0:28 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Bhandaria | 132/33 kV transformer T2 | 2022-07-26 10:04 | 2022-07-26 10:35 | 0:31 | E/O | Due to red-hot maint | 15 | 7.75 | Power interruption
Barishal(N) | 132/33 kV transformers T1 & T2 | 2022-07-27 16:57 | 2022-07-27 20:12 | 3:15 | E/O | Due to 33 kV feeder fault | 40 | 130 | Power interruption
Bhandaria | 132/33 kV transformers T1 | 2022-07-29 17:28 | 2022-07-29 18:28 | 1:00 | E/O | Due to 33 kV feeder fault | 34 | 34 | Power interruption
| 132/33 kV transformers T2 | 2022-07-29 17:28 | 2022-07-29 21:05 | 3:37 | E/O
Faridpur | 132/33 kV transformers T1 & T2 | 2022-07-31 00:15 | 2022-07-31 00:46 | 0:31 | T | Tripped showing E/F relay | 0 | 0 | No interruption
|  |  | Total : | 46:57 |  | Unserved Energy: |  | 451.0333
HVDC Grid Circle :
Bheramara GK | 230/132 kV transformer T2 | 2022-07-02 13:41 | 2022-07-02 14:54 | 1:13 | T | Tripped showing O/C relay 33 kV side | 0 | 0 | No interruption
Bheramara | 230/132 kV transformer T01 | 2022-07-02 10:42 | 2022-07-02 18:46 | 8:04 | T | Tripped showing PRD relay | 0 | 0 | No interruption
HVDC pole-2 | HVDC pole-2 | 2022-07-06 15:22 | 2022-07-06 15:58 | 0:36 | T | Due to auxiliary problem | 0 | 0 | No interruption
Benapole | 132/33 kV transformer T2 | 2022-07-07 06:44 | 2022-07-07 09:05 | 2:21 | E/O | Due to red-hot maint at 33 kV side | 20 | 47 | Power interruption
Pabna | 132/33 kV transformer T2 | 2022-07-12 12:07 | 2022-07-12 13:10 | 1:03 | E/O | Due to red-hot maint | 30 | 31.5 | Power interruption
Jassore | 132/33 kV transformer T3 | 2022-07-14 09:37 | 2022-07-14 10:33 | 0:56 | T | Due to 33 kV feeder fault | 22 | 20.5333 | Power interruption
| 132/33 kV transformer T3 | 2022-07-14 12:12 | 2022-07-14 12:21 | 0:09 | T | Due to 33 kV feeder fault | 25 | 3.75 | Power interruption
|  |  | Total : | 14:22 |  |  |  | 102.7833
Bogura Grid Circle:
Rangpur | 132/33 kV transformer T3 | 2022-07-03 11:30 | 2022-07-03 11:45 | 0:15 | E/O | Due to red-hot maint at 33 kV Bus | 20 | 5 | Power interruption
| 33 kV Bus-1 | 2022-07-05 07:25 | 2022-07-05 08:35 | 1:10 | E/O | Due to red-hot maint | 20 | 23.3333 | Power interruption
Panchugarh | 132/33 kV transformer T2 | 2022-07-13 10:01 | 2022-07-13 11:25 | 1:24 | E/O | Due to red-hot maint at 33 kV Bus | 10 | 14 | Power interruption
Rangpur | 132/33 kV transformer T3 | 2022-07-13 13:05 | 2022-07-13 13:30 | 0:25 | T | Due to 33 kV CB gas filing | 0 | 0 | No interruption
Mithapukur | 132/33 kV transformer T1 | 2022-07-16 18:43 | 2022-07-16 19:31 | 0:48 | E/O | Due to red-hot maint at 33 kV PBS feeder | 15 | 12 | Power interruption
Bogura | 132/33 kV transformer T1 | 2022-07-17 06:40 | 2022-07-17 08:38 | 1:58 | E/O | Due to red-hot maint at 132 B-phase CT connector | 20 | 39.3333 | Power interruption
Amnura | 132/33 kV transformer T1 | 2022-07-17 23:00 | 2022-07-17 23:50 | 0:50 | T | Tripped showing backup pro. relay | 10 | 8.3333 | Power interruption
Rajshahi | 132/33 kV transformers T2 & T3 | 2022-07-19 10:24 | 2022-07-19 10:38 | 0:14 | T | Due to 33 kV feeder fault | 75 | 17.5 | Power interruption
Bogura | 230/132 kV transformer T01 | 2022-07-21 17:14 | 2022-07-21 17:32 | 0:18 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
| 230/132 kV transformerAT01 | 2022-07-28 11:51 | 2022-07-28 12:20 | 0:29 | E/O | Due to Oil filling | 0 | 0 | No interruption
Naogaon | 132/33 kV transformer T2 with 33 kV Bus | 2022-07-29 10:10 | 2022-07-29 15:05 | 4:55 | E/O | Due to red-hot maint | 15 | 73.75 | Power interruption
Niyamatpur | 132/33 kV transformer T1 | 2022-07-29 20:45 | 2022-07-29 21:58 | 1:13 | E/O | Due to red-hot maint | 15 | 18.25 | Power interruption
| 132/33 kV transformer T1 | 2022-07-29 23:30 | 2022-07-30 01:33 | 2:03 | E/O
Barapukuria | 132/33 kV transformer T3 | 2022-07-30 13:05 | 2022-07-30 15:04 | 1:59 | E/O | Due to red-hot maint at 33 kV side | 0 | 0 | No interruption
Purbasadipur | 132/33 kV transformers T1 & T2 | 2022-07-31 03:50 | 2022-07-31 04:22 | 0:32 | T | Due to 33 kV feeder fault | 0 | 0 | No interruption
Barapukuria | 230/132 kV transformer T06 | 2022-07-31 05:05 | 2022-07-31 05:05 | 0:00 | T | Tripped showing PRD relay | 0 | 0 | No interruption
Natore | 132/33 kV transformer T4 | 2022-07-31 21:05 | 2022-07-31 21:21 | 0:16 | T | Due to 33 kV feeder fault | 8 | 2.1333 | Power interruption
|  |  | Total : | 18:49 |  |  |  | 213.6333
Others :Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 184:39 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-24
Page: 1/2 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month:July2022
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Mirpur | Mirpur-Uttara 132 kV Ckt | 2022-07-04 16:30 | 2022-07-04 18:07 | 1:37 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Tongi | Tongi-kabirpur 132 kV Ckt-2 | 2022-07-05 08:58 | 2022-07-05 09:18 | 0:20 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Mirpur | Mirpur-Aminbazar 132 kV Ckt-1 | 2022-07-06 11:52 | 2022-07-06 12:43 | 0:51 | T | Tripped showing E/F. relay | 30 | 25.5 | Power interruption
Mymensingh | Mymensingh-Kishoreganj 132 kV Ckt-1 | 2022-07-07 11:11 | 2022-07-07 11:16 | 0:05 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
| Mymensingh-RPCL 132 kV Ckt-1 | 2022-07-13 06:51 | 2022-07-13 08:59 | 2:08 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Tangail | Tangail-Kaliakoir 132 kV Ckt-2 | 2022-07-14 19:45 | 2022-07-14 20:10 | 0:25 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
| Tangail-Kaliakoir 132 kV Ckt-1 | 2022-07-14 19:45 | 2022-07-14 20:09 | 0:24 | T | Tripped showing O/C. relay | 0 | 0 | No interruption
Mymensingh | Mymensingh-Jamalpur 132 kV Ckt-1 | 2022-07-15 01:50 | 2022-07-15 01:56 | 0:06 | T | Tripped showing Dist. relay
| Mymensingh-Jamalpur 132 kV Ckt-2 | 2022-07-15 01:50 | 2022-07-15 02:41 | 0:51 | T |  | 125 | 106.25 | Power interruption
| Mymensingh-Bhaluka 132 kV Ckt-1 | 2022-07-29 14:59 | 2022-07-29 15:08 | 0:09 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
|  |  | Total : | 6:56 |  | Unserved Energy: |  | 131.75
Dhaka (South) Grid Circle :
Ullon | Ullon-Haripur 132 kV Ckt | 2022-07-03 10:33 | 2022-07-03 10:45 | 0:12 | T | Tripped showing Dist. relay | 122 | 24.4 | Power interruption
Haripur | Haripur-Ullon 132 kV Ckt | 2022-07-12 05:56 | 2022-07-12 05:56 | 0:00 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Rampura | Rampura-Narsinghdi 132 kV Ckt-2 | 2022-07-12 21:15 | 2022-07-12 21:15 | 0:00 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Keraniganj | Keraniganj-Seenagar 132 kV Ckt-1 & 2 | 2022-07-14 22:24 | 2022-07-14 22:43 | 0:19 | T | Tripped showing Dist. relay | 49 | 15.5167 | Power interruption
Siddhirganj | Siddhirganj-Ullon 132 kV Ckt-1 | 2022-07-16 16:55 | 2022-07-16 16:55 | 0:00 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Haripur | Haripur-Bhulta 132 kV Ckt | 2022-07-17 06:00 | 2022-07-17 08:27 | 2:27 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Matuail 132 kV Ckt | 2022-07-17 21:08 | 2022-07-18 01:48 | 4:40 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Ghorshal | Ghorshal-Narsinghdi 132 kV CKt-2 | 2022-07-19 00:25 | 2022-07-19 00:51 | 0:26 | E/O | Due to breaker of Narsinghdi Ckt-2 got locked | 0 | 0 | No interruption
Rampura | Rampura-Bashundhara 132 kV Ckt-1 | 2022-07-19 11:28 | 2022-07-19 11:54 | 0:26 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Mdanganj | Mdanganj-Haripur 132 kV Ckt | 2022-07-19 19:51 | 2022-07-19 21:41 | 1:50 | E/O | Due to red-hot maint at 33 kV side | 0 | 0 | No interruption
Ghorshal | Ghorshal-Narsinghdi 132 kV CKt | 2022-07-22 12:46 | 2022-07-22 13:31 | 0:45 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Haripur 230 kV Ckt-1 | 2022-07-25 18:17 | 2022-07-25 18:31 | 0:14 | T | Tripped showing E/F. relay | 0 | 0 | No interruption
Ghorashal | Ghorashal(GIS)-Ishurdi 230 kV Ckt-2 | 2022-07-27 09:55 | 2022-07-27 11:32 | 1:37 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
| Ghorashal(GIS)-Ishurdi 230 kV Ckt-1 | 2022-07-27 10:40 | 2022-07-27 11:32 | 0:52 | T |  | 0 | 0 | No interruption
Rampura | Rampura-Bhulta 230 kV Ckt-2 | 2022-07-27 11:02 | 2022-07-27 15:31 | 4:29 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Haripur | Haripur-Madanganj 132 kV Ckt | 2022-07-28 19:35 | 2022-07-28 19:46 | 0:11 | T | Tripped showing E/F. relay | 12 | 2.2 | Power interruption
Siddhirganj | Siddhirganj-Haripur 230 kV Ckt-1 & 2 | 2022-07-30 19:45 | 2022-07-30 20:12 | 0:27 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Fatulla | Fatulla-Haripur 132 kV Ckt | 2022-07-30 19:47 | 2022-07-30 20:42 | 0:55 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Ullon | Ullon-Siddhirganj 132 kV Ckt-1 | 2022-07-30 23:54 | 2022-07-31 01:59 | 2:05 | E/O | Due to red-hot maint | 0 | 0 | No interruption
|  |  | Total : | 21:55 |  | Unserved Energy: |  | 42.1167
Chattogram Grid Circle :
Juldah | Juldah-Halishahar 132 kV Ckt | 2022-07-01 11:10 | 2022-07-01 12:26 | 1:16 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
| Juldah-Sikalbaha 132 kV Ckt | 2022-07-01 11:10 | 2022-07-01 12:32 | 1:22 | T |  | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'sbazar 132 kV Ckt-2 | 2022-07-05 16:37 | 2022-07-05 16:37 | 0:00 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Hathazari | Hathazari-AKSML 230 kV Ckt | 2022-07-08 10:03 | 2022-07-08 10:34 | 0:31 | T | Tripped showing E/F. relay | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'sbazar 132 kV Ckt-2 | 2022-07-23 07:42 | 2022-07-23 10:35 | 2:53 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Bakulia | Bakulia-Sikalbaha 132 kV Ckt-1 & 2 | 2022-07-29 17:10 | 2022-07-29 19:34 | 2:24 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
|  |  | Total : | 8:26 |  | Unserved Energy: |  | 0
Cumilla Grid Circle :
Sylhet | Sylhet-Fenchuganj P.S 132 kV Ckt | 2022-07-04 03:10 | 2022-07-04 03:16 | 0:06 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Sunamganj | Sunamganj-Chattak 132 kV Ckt | 2022-07-31 06:30 | 2022-07-31 07:00 | 0:30 | T | Tripped showing 67N PT fuse fail | 0 | 0 | No interruption
|  |  | Total : | 0:36 |  | Unserved Energy: |  | 0
Khulna Grid Circle :
Barisal | Barisal-Bhandaria 132 kV Ckt | 2022-07-04 11:09 | 2022-07-04 11:14 | 0:05 | T | Tripped showing Dist. relay | 32 | 2.6667 | Power interruption
Rampal | Rampal-Gopalganj 400 kV Ckt-1 | 2022-07-05 15:23 | 2022-07-05 17:40 | 2:17 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Gopalganj(N) | Gopalganj(N)-Payra 400 kV Ckt-1 | 2022-07-15 17:25 | 2022-07-15 19:12 | 1:47 | E/O | Due to heavy flashing of B-phase isolator | 0 | 0 | No interruption
Khulna(S) | Khulna(S)-Rampal 230 kV Ckt-1 | 2022-07-24 10:32 | 2022-07-24 15:59 | 5:27 | E/O | Due to red-hot maint | 0 | 0 | No interruption
|  |  | Total : | 9:36 |  | Unserved Energy: |  | 2.6667
HVDC Grid Circle :
Ishurdi | Ishurdi-Ghorashal 230 kV Ckt-1 | 2022-07-05 10:55 | 2022-07-05 11:05 | 0:10 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
|  |  | Total : | 0:10 |  | Unserved Energy: |  | 0
Bogura Grid Circle:
Bogura confi. | Bogura confi.-Mithapukur 132 kV Ckt-1 | 2022-07-06 11:09 | 2022-07-06 12:27 | 1:18 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Thakurgaon P/S | Thakurgaon P/S-Thakurgaon S/S 132 kV Ckt | 2022-07-20 03:36 | 2022-07-20 03:44 | 0:08 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Sirajganj | Sirajganj-Ashuganj 230 kV Ckt-2 | 2022-07-29 12:44 | 2022-07-29 12:58 | 0:14 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
|  |  | Total : | 1:40 |  | Unserved Energy: |  | 0
Others :Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 49:19 | Hours
T = Tripping | [7 empty] | Executive Engineer
E/O = Emergency Outage | [7 empty] | Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-25
Page: 1/4 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: July 2022
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Kishoreganj | 132/33 kV transformer T-3 | 2022-07-02 07:42 | 2022-07-02 07:42 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV transformer T-3 | 2022-07-04 08:12 | 2022-07-04 17:45 | 9:33 | S/O | Due to D/W work | 0 | 0 | No interruption
Mirpur | 132/33 kV transformer T-1 | 2022-07-04 08:54 | 2022-07-04 08:54 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Kishoreganj | 132/33 kV transformer T-3 | 2022-07-05 08:30 | 2022-07-05 17:36 | 9:06 | S/O | Due to C/M work | 0 | 0 | No interruption
Jamalpur | 132/33 kV transformer T-3 | 2022-07-05 14:15 | 2022-07-05 14:50 | 0:35 | S/O | Due to C/M work | 0 | 0 | No interruption
Agargaon | 230/132 kV transformer T-02 | 2022-07-07 06:51 | 2022-07-07 06:51 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Netrakona | 132/33 kV transformer T-1 | 2022-07-08 09:58 | 2022-07-08 10:40 | 0:42 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-2 | 2022-07-08 09:56 | 2022-07-08 10:03 | 0:07 | S/O | Due to C/M work | 0 | 0 | No interruption
Joydevpur | 132/33 kV transformer T-3 | 2022-07-12 15:24 | 2022-07-12 17:19 | 1:55 | S/O | Due to C/M work | 0 | 0 | No interruption
Savar | 132/33 kV transformer T-3 | 2022-07-13 11:46 | 2022-07-13 13:36 | 1:50 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-2 | 2022-07-14 07:32 | 2022-07-14 09:26 | 1:54 | S/O | Due to C/M work | 0 | 0 | No interruption
Mirpur | 132/33 kV transformer T-2 | 2022-07-14 12:15 | 2022-07-14 15:40 | 3:25 | S/O | Due to D/W work | 0 | 0 | No interruption
Bhaluka | 132/33 kV transformer T-1 | 2022-07-17 07:03 | 2022-07-17 09:27 | 2:24 | S/O | Due to maint.work at 33 kV feeder | 65 | 156 | Power interruption
| 132/33 kV transformer T-2 | 2022-07-17 22:01 | 2022-07-18 00:15 | 2:14 | S/O | Due to PBS work | 60 | 134 | Power interruption
Netrakona | 132/33 kV transformer T-2 |  | 2022-07-17 11:16 |  | S/O | After maint.work | 0 | 0 | No interruption
Tongi | 132/33 kV transformer T-1 | 2022-07-21 10:54 | 2022-07-21 17:32 | 6:38 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV transformer T-1 | 2022-07-20 20:22 | 2022-07-21 10:20 | 13:58 | S/O | Due to maint.work | 0 | 0 | No interruption
Agargaon | 230/132 kV transformer T-01 | 2022-07-24 06:39 | 2022-07-24 06:39 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | 230/132 kV transformer T-02 | 2022-07-25 06:22 | 2022-07-25 06:22 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Tongi | 132/33 kV transformer T-3 | 2022-07-25 13:50 | 2022-07-25 17:53 | 4:03 | S/O | Due to D/W work | 0 | 0 | No interruption
Jamalpur | 132/33 kV transformer T-4 | 2022-07-25 21:37 | 2022-07-25 23:48 | 2:11 | S/O | Due to C/M work | 0 | 0 | No interruption
Kabirpur | 132/33 kV transformer T-3 | 2022-07-27 06:06 | 2022-07-27 07:16 | 1:10 | S/O | Due to C/M work | 0 | 0 | No interruption
Kabirpur | 132/33 kV transformer T-3 | 2022-07-30 08:59 | 2022-07-30 09:49 | 0:50 | S/O | Due to PBS work | 0 | 0 | No interruption
|  |  | Total : | 62:35 |  | Unserved Energy: |  | 290
Dhaka (South) Grid Circle :
Matuail | 132 kV Bus-2 | 2022-07-05 10:35 | 2022-07-05 15:17 | 4:42 | S/O | Due to C/M work | 0 | 0 | No interruption
Sonargaon | 132/33 kV transformer T-1 | 2022-07-09 08:55 | 2022-07-09 09:56 | 1:01 | S/O | Due to C/M work | 15 | 15.25 | Power interruption
Keraniganj | 132/33 kV transformer T-1 | 2022-07-16 07:32 | 2022-07-16 07:32 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-2 | 2022-07-16 09:53 | 2022-07-16 12:45 | 2:52 | S/O | Due to C/M work | 0 | 0 | No interruption
Haripur | 230 kV Bus-1 | 2022-07-26 08:10 | 2022-07-26 17:36 | 9:26 | S/O | Due to C/M work | 0 | 0 | No interruption
Hasnabad | 132/33 kV transformer T-1 | 2022-07-26 08:23 | 2022-07-26 08:23 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 18:01 |  | Unserved Energy: |  | 15.25
Chattogram Grid Circle :
Dohazari | 132/33 kV transformer T-1 with 33 kV Bus | 2022-07-02 11:12 | 2022-07-02 12:58 | 1:46 | S/O | Due to C/M work | 15 | 26.5 | Power interruption
Mirsharai | 132/33 kV transformer T1 | 2022-07-06 10:10 | 2022-07-06 17:14 | 7:04 | S/O | Due to D/W work | 0 | 0 | No interruption
| 230/132/11 kV transformer T2 | 2022-07-07 11:44 | 2022-07-07 12:04 | 0:20 | S/O | Due to D/W work | 0 | 0 | No interruption
Rampur | 132/33 kV transformer T1 | 2022-07-07 13:03 | 2022-07-07 14:52 | 1:49 | S/O | Due to C/M work | 0 | 0 | No interruption
Bhandaria | 132/33 kV transformer T2 | 2022-07-08 08:34 | 2022-07-08 09:57 | 1:23 | S/O | Due to C/M work | 15 | 20.75 | Power interruption
| 132/33 kV transformer T2 | 2022-07-09 10:10 | 2022-07-09 10:10 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Baroierhat | 132/33 kV transformer T1 | 2022-07-09 10:53 | 2022-07-09 12:02 | 1:09 | S/O | Due to C/M work | 20 | 23 | Power interruption
T.K chemical | 132/33 kV transformer T1 |  | 2022-07-14 09:41 |  | S/O | After maint.work | 0 | 0 | No interruption
Sitalakhya | 132/33 kV transformer T1 | 2022-07-19 11:00 | 2022-07-19 11:47 | 0:47 | S/O | Due to C/M work | 0 | 0 | No interruption
Dohazari | 132/33 kV transformer T1 | 2022-07-20 08:15 | 2022-07-20 08:15 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Sikalbaha | 132/33 kV transformer T3 | 2022-07-24 09:38 | 2022-07-24 11:13 | 1:35 | S/O | Due to C/M work | 0 | 0 | No interruption
Hathazari | 132/33 kV transformer T2 | 2022-07-25 07:18 | 2022-07-25 07:18 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Rampur | 132/33 kV transformer T1 | 2022-07-26 10:38 | 2022-07-26 13:58 | 3:20 | S/O | Due to C/M work | 0 | 0 | No interruption
Halishahar | 132/33 kV transformer T1 | 2022-07-30 08:25 | 2022-07-30 11:21 | 2:56 | S/O | Due to D/W work | 0 | 0 | No interruption
Juldah | 132 kV Bus-A | 2022-07-30 10:30 | 2022-07-30 13:46 | 3:16 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 25:25 |  | Unserved Energy : |  | 70.25
Cumilla Grid Circle :
Chandpur | 132/33 kV transformer T5 | 2022-07-02 07:12 | 2022-07-02 10:45 | 3:33 | S/O | Due to C/M work | 25 | 88.75 | Power interruption
Sylhet | 132/33 kV transformerT2 with 33 kV Bus | 2022-07-07 20:28 | 2022-07-07 21:08 | 0:40 | S/O | Due to maint.of 33 kV feeder | 0 | 0 | No interruption
| 132/33 kV transformer T1 with 33 kV Bus | 2022-07-08 01:13 | 2022-07-08 03:26 | 2:13 | S/O | Due to C/M work | 0 | 0 | No interruption
Sunamganj | 132/33 kV transformer T1 |  | 2022-07-14 10:02 |  | S/O | After maint.work | 0 | 0 | No interruption
| 132/33 kV transformer T1 | 2022-07-14 11:30 | 2022-07-14 13:53 | 2:23 | S/O | Due to maint.work | 0 | 0 | No interruption
Beanibazar | 132/33 kV transformer T2 | 2022-07-15 08:23 | 2022-07-15 11:19 | 2:56 | S/O | Due to C/M work | 35 | 102.6667 | Power interruption
Ramganj | 132/33 kV transformer T2 | 2022-07-17 08:01 | 2022-07-17 09:09 | 1:08 | S/O | Due to C/M work | 35 | 39.6667 | Power interruption
Shajibazar | 132/33 kV transformer T4 | 2022-07-18 05:57 | 2022-07-18 09:02 | 3:05 | S/O | Due to C/M work | 0 | 0 | No interruption
Feni | 132/33 kV transformer T1 with 33 kV Bus | 2022-07-28 06:36 | 2022-07-28 06:36 | 0:00 | S/O | Due to C/M work | 5 | 0 | Power interruption
Kachua | 132/33 kV transformer T1 | 2022-07-28 09:26 | 2022-07-28 22:27 | 13:01 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132 kV Bus-1 | 2022-07-28 12:22 | 2022-07-28 14:11 | 1:49 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132 kV Bus-2 | 2022-07-28 14:28 | 2022-07-28 17:14 | 2:46 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer T2 | 2022-07-29 09:27 | 2022-07-29 12:31 | 3:04 | S/O | Due to C/M work | 0 | 0 | No interruption
Cumilla(N) | 132/33 kV transformer T3 | 2022-07-30 06:41 | 2022-07-30 06:41 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 36:38 |  | Unserved Energy : |  | 231.0833
Khulna Grid Circle :
Gallamari | 132/33 kV transformer T2 | 2022-07-02 09:31 | 2022-07-02 18:59 | 9:28 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV transformer T1 | 2022-07-03 06:25 | 2022-07-03 06:25 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Patuakhali | 132/33 kV transformer T2 | 2022-07-04 08:42 | 2022-07-04 09:58 | 1:16 | S/O | Due to C/M work | 0 | 0 | No interruption
Gallamari | 132/33 kV transformer T1 | 2022-07-04 09:25 | 2022-07-04 09:25 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Patuakhali | 132/33 kV transformer T2 | 2022-07-07 07:19 | 2022-07-07 07:19 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Gopalganj | 132/33 kV transformer T2 | 2022-07-07 07:19 | 2022-07-07 07:19 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Bhandaria | 132/33 kV transformer T1 | 2022-07-08 07:25 | 2022-07-08 08:29 | 1:04 | S/O | Due to C/M work | 0 | 0 | No interruption
Barisal(N) | 132/33 kV transformer T-5 | 2022-07-08 09:08 | 2022-07-08 13:09 | 4:01 | S/O | Due to C/M work | 0 | 0 | No interruption
Khulna© | 132/33 kV transformer T-2 | 2022-07-09 12:32 | 2022-07-09 12:58 | 0:26 | S/O | Due to changing of PT | 0 | 0 | No interruption
Bagerhat | 132/33 kV transformers T-1 & T2 | 2022-07-12 07:39 | 2022-07-12 07:52 | 0:13 | S/O | Due to C/M work | 35 | 7.5833 | Power interruption
Satkhira | 132/33 kV transformer T-2 | 2022-07-15 08:18 | 2022-07-15 11:43 | 3:25 | S/O | Due to C/M work | 40 | 136.6667 | Power interruption
Gopalganj | 132/33 kV transformer T1 | 2022-07-18 09:14 | 2022-07-18 17:08 | 7:54 | S/O | Due to C/M work | 0 | 0 | No interruption
Barisal(S) | 132/33 kV transformer T2 | 2022-07-23 09:43 | 2022-07-23 12:52 | 3:09 | S/O | Due to C/M work | 0 | 0 | No interruption
Madaripur | 132/33 kV transformer T1 | 2022-07-25 09:35 | 2022-07-25 12:27 | 2:52 | S/O | Due to C/M work | 0 | 0 | No interruption
Barisal(S) | 132/33 kV transformer T1 | 2022-07-25 06:43 | 2022-07-25 07:35 | 0:52 | S/O | Due to C/M work | 34 | 29.4667 | Power interruption
Noapara | 132/33 kV transformer T1 | 2022-07-28 06:43 | 2022-07-28 07:35 | 0:52 | S/O | Due to C/M work | 0 | 0 | No interruption
Shariatpur | 132/33 kV transformers T-1 & T-2 with 33 kV Bus | 2022-07-28 16:47 | 2022-07-28 17:10 | 0:23 | S/O | Due to 33 kV feeder maint | 40 | 15.3333 | Power interruption
Payra | 400/132 kV transformer ATR1 | 2022-07-30 09:44 | 2022-07-30 09:44 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Matarbari | 132/33 kV transformer T1 | 2022-07-31 09:21 | 2022-07-31 09:41 | 0:20 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 36:15 |  | Unserved Energy : |  | 189.05
HVDC Grid Circle
Bheramara GK | 132/33 kV transformer T2 | 2022-07-01 12:20 | 2022-07-01 12:20 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Shahjadpur | 132/33 kV transformer T3 | 2022-07-09 15:21 | 2022-07-09 15:58 | 0:37 | S/O | Due to C/M work | 15 | 9.25 | Power interruption
HVDC | HVDC 400 kV 10CF25 filter | 2022-07-14 09:10 | 2022-07-14 21:27 | 12:17 | S/O | Due to maint.work | 0 | 0 | No interruption
Bheramara | HVDC 400 kV Bus-2 | 2022-07-25 06:33 | 2022-07-25 09:52 | 3:19 | S/O | Due to C/M work | 0 | 0 | No interruption
Pabna | 132/33 kV transformer T2 | 2022-07-29 06:52 | 2022-07-29 08:24 | 1:32 | S/O | Due to C/M work | 30 | 46 | Power interruption
|  |  | Total : | 17:45 |  | Unserved Energy : |  | 55.25
Bogura Grid Circle:
Niyamatpur | 33 kV Bus-1 & 2 | 2022-07-01 09:15 | 2022-07-01 21:50 | 12:35 | S/O | Due to C/M work | 55 | 692.0833 | Power interruption
Naogaon | 132/33 kV transformer T2 | 2022-07-01 10:31 | 2022-07-01 14:35 | 4:04 | S/O | Due to replacemnet work | 0 | 0 | No interruption
| 132/33 kV transformer T1 | 2022-07-01 14:52 | 2022-07-01 17:55 | 3:03 | S/O | Due to C/M work | 0 | 0 | No interruption
Mithapukur | 132/33 kV transformer T1 | 2022-07-02 11:05 | 2022-07-02 14:07 | 3:02 | S/O | Due to C/M work | 0 | 0 | No interruption
Rangpur | 132/33 kV transformer T1 | 2022-07-04 06:35 | 2022-07-04 06:35 | 0:00 | S/O | Due to isolator problem | 0 | 0 | No interruption
Amnura | 132/33 kV transformer T1 |  | 2022-07-05 20:40 |  | S/O | After maint.work | 0 | 0 | No interruption
Niyamatpur | 132/33 kV transformer T3 | 2022-07-06 13:43 | 2022-07-06 18:50 | 5:07 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformers T1 | 2022-07-07 13:26 | 2022-07-07 15:43 | 2:17 | S/O | Due to C/M work | 40 | 91.3333 | Power interruption
| 132/33 kV transformers T2 | 2022-07-07 13:26 | 2022-07-07 14:52 | 1:26 | S/O | Due to C/M work | 0 | 0 | No interruption
Bogura | 132/33 kV transformer T1 | 2022-07-08 07:06 | 2022-07-08 10:20 | 3:14 | S/O | Due to C/M work | 40 | 129.3333 | Power interruption
Thakurgaon | 33 kV Bus-3 | 2022-07-17 05:55 | 2022-07-17 07:16 | 1:21 | S/O | Due to maint.of isolator | 30 | 40.5 | Power interruption
Amnura | 132/33 kV transformer T1 |  | 2022-07-18 09:52 |  | S/O | After maint.work | 0 | 0 | No interruption
Kurigram | 132/33 kV transformer T1 | 2022-07-19 11:37 | 2022-07-19 13:17 | 1:40 | S/O | Due to C/M work | 0 | 0 | No interruption
Rajshahi | 230/132 kV transformer T01 | 2022-07-21 11:10 | 2022-07-21 11:10 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Saidpur | 132/33 kV transformer T2 | 2022-07-22 07:02 | 2022-07-22 10:50 | 3:48 | S/O | Due to C/M work | 0 | 0 | No interruption
Rajshahi | 132/33 kV transformer T3 with 33 kV Bus | 2022-07-23 06:09 | 2022-07-23 18:16 | 12:07 | S/O | Due to C/M work | 21 | 254.45 | Power interruption
Bogura | 132/33 kV transformer T2 | 2022-07-25 10:05 | 2022-07-25 10:05 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Amnura | 132/33 kV transformer T2 | 2022-07-25 09:28 | 2022-07-25 13:22 | 3:54 | S/O | Due to C/M work | 0 | 0 | No interruption
Sirajganj | 132/33 kV transformer T3 | 2022-07-26 10:30 | 2022-07-26 13:58 | 3:28 | S/O | Due to C/M work | 0 | 0 | No interruption
Rajshahi | 132/33 kV transformer T2 | 2022-07-27 09:20 | 2022-07-27 12:33 | 3:13 | S/O | Due to C/M work | 0 | 0 | No interruption
Bogura | 132/33 kV transformer T2 | 2022-07-28 08:05 | 2022-07-28 10:05 | 2:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Palashbari | 132/33 kV transformer T3 | 2022-07-28 18:03 | 2022-07-28 19:10 | 1:07 | S/O | Due to C/M work | 0 | 0 | No interruption
Rangpur | 33 kV Bus section-2 | 2022-07-30 06:10 | 2022-07-30 09:35 | 3:25 | S/O | Due to replacemnet work | 50 | 170.8333 | Power interruption
Mohastanghor | 132/33 kV transformer T1 | 2022-07-30 12:38 | 2022-07-30 12:38 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 70:51 |  | Unserved Energy : |  | 1378.5333
Others :Nil
|  |  | Total | 0:00 |  | Unserved Energy : |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 267:30 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-26
Page: 1/2 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: July2022
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Savar | Savar-Manikganj 132 kV Ckt-1 | 2022-07-13 07:12 | 2022-07-13 10:31 | 3:19 | S/O | Due to C/M work | 0 | 0 | No interruption
Lalbagh | Lalbagh-Keraniganj 132 kV Ckt | 2022-07-15 09:10 | 2022-07-15 17:11 | 8:01 | S/O | Due to C/M work | 0 | 0 | No interruption
Tongi | Tongi-Kaliakoir 230 kV Ckt | 2022-07-26 14:54 | 2022-07-26 17:18 | 2:24 | S/O | Due to C/M work | 0 | 0 | No interruption
| Tongi-Kaliakoir 230 kV Ckt | 2022-07-27 10:25 | 2022-07-27 17:52 | 7:27 | S/O | Due to D/W work | 0 | 0 | No interruption
| Tongi-Tongi 80MW P/S 230 kV Ckt | 2022-07-28 12:44 | 2022-07-28 18:25 | 5:41 | S/O | Due to project work | 0 | 0 | No interruption
Tangail | Tangail-Kaliakoir 230 kV Ckt | 2022-07-30 11:22 | 2022-07-30 11:22 | 0:00 | S/O | Due to DFDR work | 0 | 0 | No interruption
Tongi | Tongi-Kabirpur 230 kV Ckt | 2022-07-31 10:23 | 2022-07-31 18:43 | 8:20 | S/O | Due to DFDR work | 0 | 0 | No interruption
|  |  | Total : | 35:12 |  | Unserved Energy: |  | 0
Dhaka (South) Grid Circle :
Madanganj | Madanganj-Sikalbaha 132 kV Ckt | 2022-07-01 12:10 | 2022-07-01 12:10 | 0:00 | S/O | Due to reduce load of Haripur-Madanganj Ckt | 0 | 0 | No interruption
Ghporashal GIS | Ghporashal GIS-Ghorashal 230 kV Ckt | 2022-07-03 09:24 | 2022-07-03 09:24 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Rampura | Rampura-Bashundhara 132 kV Ckt-2 | 2022-07-05 10:15 | 2022-07-05 12:45 | 2:30 | S/O | Due to testing purpose | 0 | 0 | No interruption
Munshiganj | Munshiganj-Madnganj 132 kV Ckt-1 | 2022-07-05 11:37 | 2022-07-05 14:38 | 3:01 | S/O | Due to C/M work | 0 | 0 | No interruption
Rampura | Rampura-Bashundhara 132 kV Ckt-1 | 2022-07-05 14:58 | 2022-07-05 16:06 | 1:08 | S/O | Due to C/M work | 0 | 0 | No interruption
Haripur S/S | Haripur S/S-Haripur 412 MW 132 kV Ckt | 2022-07-06 10:13 | 2022-07-06 13:44 | 3:31 | S/O | Due to C/M work | 0 | 0 | No interruption
Bhulta | Bhulta-Haripur 230 kV Ckt-2 | 2022-07-08 05:25 | 2022-07-08 10:50 | 5:25 | S/O | Due to C/M work | 0 | 0 | No interruption
Haripur | Haripur-Bhulta 230 kV ckt-2 | 2022-07-13 08:29 | 2022-07-13 13:27 | 4:58 | S/O | Due to C/M work | 0 | 0 | No interruption
Ghorashal | Ghorashal-Narsinghdi 132 kV Ckt-2 | 2022-07-13 11:40 | 2022-07-13 13:27 | 1:47 | S/O | Due to C/M work | 0 | 0 | No interruption
Haripur P/S | Haripur P/S-Haripur 230 kV Ckt-2 | 2022-07-14 07:08 | 2022-07-14 07:08 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Haripur S/S | Haripur S/S-HPL 230 MW 132 kV Ckt-1 | 2022-07-15 07:10 | 2022-07-15 07:10 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Keraniganj | Keraniganj-Sreenagar 132 kV Ckt-1 | 2022-07-15 11:47 | 2022-07-15 15:53 | 4:06 | S/O | Due to protection test | 0 | 0 | No interruption
| Keraniganj-Sreenagar 132 kV Ckt-2 | 2022-07-15 14:18 | 2022-07-15 15:58 | 1:40 | S/O |  | 0 | 0 | No interruption
| Keraniganj-Sreenagar 132 kV Ckt-2 | 2022-07-17 11:45 | 2022-07-17 14:30 | 2:45 | S/O | Due to protection work | 0 | 0 | No interruption
Sitalakyha | Sitalakyha-Madanganj 132 kV Ckt | 2022-07-21 12:12 | 2022-07-21 12:12 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Ullon 132 kV Ckt-1 | 2022-07-22 09:14 | 2022-07-22 17:52 | 8:38 | S/O | Due to C/M work | 0 | 0 | No interruption
Mdanganj | Mdanganj-Munshiganj 132 kV Ckt-2 | 2022-07-26 11:00 | 2022-07-26 17:20 | 6:20 | S/O | Due to C/M work | 0 | 0 | No interruption
Ghorashal(Gis) | Ghorashal(GIS)-Ishurdi 230 kV Ckt-1 | 2022-07-27 16:17 | 2022-07-27 17:51 | 1:34 | S/O | Due to PBS work | 0 | 0 | No interruption
Rampura | Rampura-Bhulta 230 kV Ckt-2 | 2022-07-28 11:30 | 2022-07-28 14:28 | 2:58 | S/O | Due to protection test | 0 | 0 | No interruption
|  |  | Total : | 50:21 |  | Unserved Energy: |  | 0
Chattogram Grid Circle :
Sikalbaha | Sikalbaha-intermidiate 230 kV Ckt-1 | 2022-07-02 09:47 | 2022-07-02 09:47 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
| Sikalbaha-intermidiate 230 kV Ckt-1 | 2022-07-03 10:12 | 2022-07-03 10:12 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
| Sikalbaha-intermidiate 132 kV Ckt-1 | 2022-07-04 08:54 | 2022-07-04 18:24 | 9:30 | S/O | Due to D/W work | 0 | 0 | No interruption
BSRM | BSRM-Mirsharai 230 kV Ckt | 2022-07-06 10:27 | 2022-07-06 17:03 | 6:36 | S/O | Due to D/W work | 0 | 0 | No interruption
Hathazari | Hathazari-Baroierhat 132 kV Ckt-1 & 2 | 2022-07-17 06:26 | 2022-07-17 06:26 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Rangamati | Rangamati-Chandraghona 132 kV Ckt-2 | 2022-07-26 10:01 | 2022-07-26 13:15 | 3:14 | S/O | Due to C/M work | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'sbazar 132 kV Ckt-1 | 2022-07-28 11:19 | 2022-07-28 11:24 | 0:05 | S/O | Due to protection test | 0 | 0 | No interruption
|  |  | Total : | 19:25 |  | Unserved Energy: |  | 0
Cumilla Grid Circle :
Chowmuhani | Chowmuhani-HPPL 132 kV Ckt | 2022-07-05 10:30 | 2022-07-05 15:46 | 5:16 | S/O | Due to right of way | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Meghnaghat 230 kV Ckt-1 | 2022-07-06 09:36 | 2022-07-06 13:32 | 3:56 | S/O | Due to C/M work | 0 | 0 | No interruption
Mirsoari | Mirsoari-BSRM 230 kV Ckt-2 | 2022-07-07 09:21 | 2022-07-07 13:54 | 4:33 | S/O | Due to D/W work | 0 | 0 | No interruption
B.Baria | B.Baria-Ashuganj 132 kV Ckt-2 | 2022-07-14 10:28 | 2022-07-14 13:55 | 3:27 | S/O | Due to load control | 0 | 0 | No interruption
Chandpur | Chandpur-Chandpur P/S 132 kV Ckt | 2022-07-18 10:02 | 2022-07-18 15:32 | 5:30 | S/O | Due to C/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-B.Baria 132 kV Ckt-2 | 2022-07-23 10:12 | 2022-07-23 11:58 | 1:46 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 24:28 |  | Unserved Energy: |  | 0:00
Page: 2/2 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: July2022
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Cumilla Grid Circle :
Kulaura | Kulaura-Fenchuganj 132 kV Ckt-2 | 2022-07-26 15:53 | 2022-07-26 21:28 | 5:35 | S/O | Due to C/M work | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Kachua 132 kV Ckt | 2022-07-27 09:14 | 2022-07-27 12:44 | 3:30 | S/O | Due to C/M work | 0 | 0 | No interruption
Cumilla(S) | Cumilla(N)-Kachua 132 kV Ckt | 2022-07-27 13:07 | 2022-07-27 16:30 | 3:23 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 12:28 |  | Unserved Energy: |  | 0
Khulna Grid Circle :
Khulna(S) | Khulna(S)-Satkhira 132 kV Ckt-2 | 2022-07-08 07:58 | 2022-07-08 09:43 | 1:45 | S/O | Due to C/M work | 0 | 0 | No interruption
| Khulna(S)-Jhenaidah 230 kV Ckt-1 | 2022-07-17 11:03 | 2022-07-17 12:20 | 1:17 | S/O | Due to tree trimming | 0 | 0 | No interruption
| Khulna(S)-Rampal 230 kV Ckt | 2022-07-21 06:20 | 2022-07-21 06:20 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Gopalganj(N) | Gopalganj(N)-Gopalganj(O) 132 kV Ckt-1 | 2022-07-22 07:24 | 2022-07-22 09:45 | 2:21 | S/O | Due to C/M work | 0 | 0 | No interruption
Rajbari | Rajbari-Faridpur 132 kV Ckt-2 | 2022-07-23 08:10 | 2022-07-23 13:11 | 5:01 | S/O | Due to C/M work | 0 | 0 | No interruption
| Rajbari-Faridpur 132 kV Ckt-1 | 2022-07-23 13:15 | 2022-07-23 16:14 | 2:59 | S/O | Due to C/M work | 0 | 0 | No interruption
Khulna© | Khulna©-Khulna(S) 132 kV Ckt-1 | 2022-07-28 07:21 | 2022-07-28 07:21 | 0:00 | S/O | Due to winding tem.high | 0 | 0 | No interruption
Bagerhat | Bagerhat-Bhandaria 132 kV Ckt |  | 2022-07-28 06:42 |  | S/O | after maint.work | 0 | 0 | No interruption
Khulna(S) | Khulna(S)-Khulna 330 MW P/S 132 kV Ckt | 2022-07-29 11:37 | 2022-07-29 11:37 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Bagerhat | Bagerhat-Bhandaria 132 kV Ckt | 2022-07-29 07:00 | 2022-07-29 07:00 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Rampal | Rampal-Khulna(S) 230 kV Ckt-2 | 2022-07-30 15:36 | 2022-07-30 19:42 | 4:06 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 17:29 |  | Unserved Energy: |  | 0
HVDC Grid Circle :
Ishurdi | Ishurdi-Natore 132 kV Ckt-1 & 2 | 2022-07-15 07:46 | 2022-07-15 10:13 | 2:27 | S/O | Due to maint.work | 0 | 0 | No interruption
Bheramara | Bheramara-Bheramara 400 kV Ckt-3 | 2022-07-18 10:57 | 2022-07-18 20:19 | 9:22 | S/O | Due to C/M work | 0 | 0 | No interruption
| Bheramara-Bheramara 400 kV Ckt-4 | 2022-07-18 10:58 | 2022-07-18 20:30 | 9:32 | S/O | Due to C/M work | 0 | 0 | No interruption
| Bheramara-HVDC 400 kV Ckt-2 | 2022-07-20 08:46 | 2022-07-20 19:16 | 10:30 | S/O | Due to D/W work | 0 | 0 | No interruption
Jhenaidah(N) | Jhenaidah(N)-Chuadanga 132 kV Ckt | 2022-07-23 09:05 | 2022-07-23 15:12 | 6:07 | S/O | Due to C/M work | 0 | 0 | No interruption
| Jhenaidah(N)-Jassore 132 kV Ckt-1 | 2022-07-23 09:25 | 2022-07-23 17:55 | 8:30 | S/O | Due to C/M work | 0 | 0 | No interruption
| Jhenaidah(N)-Jassore 132 kV Ckt-2 | 2022-07-24 15:23 | 2022-07-24 17:04 | 1:41 | S/O | Due to protection work | 0 | 0 | No interruption
Jhenaidah(O) | Jhenaidah(O)-Jhenaidah (N) 132 kV Ckt-1 | 2022-07-25 09:11 | 2022-07-25 16:05 | 6:54 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 55:03 |  | Unserved Energy: |  | 0
Bogura Grid Circle :
Thakurgaon | Thakurgaon-Thakurgaon P/S 132 kV Ckt | 2022-07-01 16:12 | 2022-07-01 16:55 | 0:43 | S/O | Due to C/M work | 0 | 0 | No interruption
Rohanpur | Rohanpur-Jharkhond 400 kV Ckt | 2022-07-18 08:38 |  |  | S/O | Due to project work | 0 | 0 | No interruption
Thakurgaon | Thakurgaon-Thakurgaon P/S 132 kV Ckt | 2022-07-24 03:55 | 2022-07-24 05:45 | 1:50 | S/O | Due to C/M work | 106 | 194.3333 | Power interruption
Sirajganj | Sirajganj-Baghabari 230 kV Ckt-1 | 2022-07-26 15:21 | 2022-07-26 16:07 | 0:46 | S/O | Due to D/W work | 0 | 0 | No interruption
| Sirajganj-Baghabari 230 kV Ckt-2 | 2022-07-26 16:08 | 2022-07-26 16:50 | 0:42 | S/O | Due to C/M work | 0 | 0 | No interruption
| Sirajganj-Baghabari 230 kV Ckt-2 | 2022-07-27 09:20 | 2022-07-27 12:33 | 3:13 | S/O | Due to C/M work | 0 | 0 | No interruption
| Sirajganj-Baghabari 230 kV Ckt-1 | 2022-07-27 13:13 | 2022-07-27 13:45 | 0:32 | S/O | Due to C/M work | 0 | 0 | No interruption
| Sirajganj-Baghabari 230 kV Ckt-2 | 2022-07-27 13:46 | 2022-07-27 14:19 | 0:33 | S/O | Due to C/M work | 0 | 0 | No interruption
C.nawabganj | C.nawabganj-Rohanpur 132 kV Ckt |  | 2022-07-27 15:57 |  |  | new connection | 0 | 0 | No interruption
Naogaon | Naogaon-Santahar P/S 132 kV Ckt | 2022-07-28 11:55 | 2022-07-28 15:05 | 3:10 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 11:29 |  | Unserved Energy: |  | 194.3333
Others :Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 225:55 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance
Executive Engineer
Information Management Division
|  |  |  | 8.3937 |  |  |  | LDC, PGCB, Dhaka.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month:July 2022
| Area | Previous Month (June' 2022) |  |  |  | Current Month (July '2022)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 31 | 2 | 52 | 85 | 22 | 3 | 30 | 55
2 | Dhaka (South) Grid Circle. | 26 | 2 | 15 | 43 | 21 | 8 | 25 | 54
3 | Chattogram Grid Circle. | 25 | 2 | 29 | 56 | 15 | 3 | 22 | 40
4 | Cumilla Grid Circle. | 21 | 16 | 34 | 71 | 15 | 3 | 24 | 42
5 | Khulna Grid Circle. | 9 | 12 | 72 | 93 | 11 | 13 | 30 | 54
6 | HVDC Grid Circle | 12 | 11 | 18 | 41 | 6 | 2 | 13 | 21
7 | Bogura Grid Circle. | 33 | 13 | 41 | 87 | 8 | 12 | 33 | 53
8 | Others | 2 |  |  | 2 | 0 | 0 | 0 | 0
9 | Total | 159 | 58 | 261 | 478 | 98 | 44 | 177 | 319
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month:July 2022
| Area | Previous Month (June' 2022) |  |  |  | Current Month (July '2022)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 916.22 |  | 554.37 | 1470.59 | 422.02 |  | 290 | 712.02
2 | Dhaka (South) Grid Circle. | 281.97 |  | 61.67 | 343.64 | 161 |  | 15.25 | 176.25
3 | Chattogram Grid Circle. | 346.35 | 1.05 | 468.95 | 816.35 | 32 |  | 70.25 | 102.25
4 | Cumilla Grid Circle. | 429.45 | 348.83 | 440.67 | 1218.95 | 119.27 | 944.93 | 231.08 | 1295.28
5 | Khulna Grid Circle. | 25.63 | 127 | 44.43 | 197.06 | 216.75 | 236.95 | 189.05 | 642.75
6 | HVDC Grid Circle | 21.93 | 230.57 | 106 | 358.5 | 24.28 | 78.5 | 55.25 | 158.03
7 | Bogura Grid Circle. | 770.23 | 165.57 | 1282.33 | 2218.13 | 27.96 | 185.67 | 1572.86 | 1786.49
8 | Others | Energy unserved ( MWH ) due to Total: 0; Energy unserved ( MWH ) due to Total: 0
9 | Total | 2791.78 | 873.02 | 2958.42 | 6623.22 | 1003.28 | 1446.05 | 2423.74 | 4873.07
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-29
Page: 1/1 | [9 empty] | QF-LDC-29
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month:March 2022
A) Power Interruption
SL. | Name of | Total Capacity | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of the Sub-Station |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Dhaka (North) | 8801.6 | 8 | 2 | 10 | 3 |  | 7 | 580.27
2 | Dhaka (South) | 5031.6 | 2 | 1 | 3 |  | 1 | 2 | 134.13
3 | Chattogram | 2042 | 3 | 3 | 6 | 2 |  | 4 | 102.25
4 | Khulna | 2434 | 12 | 4 | 16 | 6 | 5 | 5 | 640.08
5 | HVDC | 5954.3 | 4 | 2 | 6 | 1 | 2 | 3 | 158.02
6 | Bogura | 3145.6 | 10 | 6 | 16 | 4 | 2 | 10 | 1592.16
7 | Cumilla | 2981 | 6 | 3 | 9 |  | 4 | 5 | 1295.28
8 | Others | - | - | - | - | - | - | - | 0
| Total | 30390.1 | [6 empty] | 4502.19
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 99.96%
2 | Dhaka (South) | 99.99%
3 | Chattogram | 99.94%
4 | Khulna | 99.82%
5 | HVDC | 99.98%
6 | Bogura | 99.89%
7 | Cumilla | 99.91%
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-30
Page: 1/1 | [10 empty] | QF-LDC-30
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month:July 2022
A) Power Interruption
SL. | Name of | Total length | No. of Section in | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of Transmission line | the Transmission |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | (Ckt-KM) | Line | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 2254.4715 | - | - | 2 |  | 2 |  | 1 |  | 131.75
2 | Dhaka (South) | 990.29 |  |  | 3 | - | 3 | 3 |  |  | 42.12
3 | Chattogram | 917 | - | - | - | - | - | - | - | - | -
4 | Khulna | 1238.4 | - | - | 1 | - | 1 | 1 | - | - | 2.67
5 | HVDC | 1325 | - | - | - | - | - | - | - | - | -
6 | Bogura | 1803.3 | - | - | 1 |  | 1 |  |  | 1 | 194.33
7 | Cumilla | 1648.16 | - | -
8 | Others | - |  |  | - | - | - | - | - | - | -
| Total | 10176.6215 | [8 empty] | 370.87
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 99.98%
2 | Dhaka (South) | 99.92%
3 | Chattogram | 99.95%
4 | Khulna | 99.97%
5 | Bheramara (HVDC) | 99.99% | [7 empty] | Executive Engineer
6 | Bogura | 99.96% | [7 empty] | Information Management Division
7 | Cumilla | 99.93% | [7 empty] | LDC, PGCB, Dhaka.

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month:July 2022
Type of | Power failure due to | [7 empty] | Partial |  | Total Grid failure
fault | Trouble In |  | Trouble In Grid S/S |  | Trouble In |  | Lightning in |  | Grid failure |  |  |  | Remarks
| Generation |  | Equipment |  | Transmission Line |  | Transmission Line/Thunder Storm
Period | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration
| No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min.
2022-07-01 | 16 | - | 13 | 21hr6 min | - | - | - | - | - | - | - | - | -
* Tripping of a generator is accounted in the category "Trouble in Generation ". Not all tripping cause power interruption.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-32
Page: 1/2 |  |  |  |  | QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the Systems
Month:July 2022
| Total Nos.of | Total | Unserved | Total | Remarks
Sub-station | Interruption | Duration of | Load | Unserved
|  | Interruption | (MW) | Energy
|  | Hrs./Mins. |  | (MWH)
Kodda | 1 | 1:45 | 30 | 52.5 | Due to red-hot maint 132/33 kV Transformer T2
Netrakona | 2 | 1:56 | 30 | 58
|  | 4:08 | 10 | 41.3333 | Due to tripping of 132/33 kV transformerT 1
Kishoreganj |  | 1:02 | 90 | 93 | Due to tripping of 33 kV feeder fault
Netrakona |  | 0:02 | 55 | 1.8333 | Due to tripping of 132/33 kV transformersT 1 & T2
Mymensingh | 2 | 0:10 | 116 | 19.3333 | Due to tripping of 33 kV feeder fault
|  | 0:06 | 140 | 14 | Due to tripping of 132/33 kV transformersT 1 & T2
Kishoreganj | 1 | 15:23 | 28 | 10.2667 | Due to tripping of 33 kV feeder fault
Mirpur | 2 | 0:51 | 30 | 25.5 | Due to tripping of Mirpur-Aminbazar 132 kV Ckt-1
Mymensingh |  | 0:51 | 125 | 106.25 | Due to tripping of Mymensingh-Jamalpur 132 kV Ckt-2
Bhaluka | 1 | 2:24 | 65 | 156 | Due to S/D of 132/33 kV transformer T1
Mymensingh | 1 | 2:14 | 60 | 134 | Due to S/D of 132/33 kV transformer T2
Keraniganj | 1 | 0:37 | 38 | 23.4333 | Due to tripping of 132/33 kV transformersT 1 & T2
Hasnabad | 1 | 4:09 | 23 | 95.45 | Due to tripping of 33 kV feeder fault
Ullon | 1 | 0:12 | 122 | 24.4 | Due to tripping of Ullon-Haripur 132 kV Ckt
Keraniganj | 1 | 0:19 | 49 | 15.5167 | Due to tripping of Keraniganj-Seenagar 132 kV Ckt-1 & 2
Haripur | 1 | 0:11 | 12 | 2.2 | Due to tripping of Haripur-Madanganj 132 kV Ckt
Sonargaon | 1 | 1:01 | 15 | 15.25 | Due to S/D of 132/33 kV transformer T-1
Cox'sbazar |  | 0:13 | 40 | 8.6667 | Due to tripping of 132/33 kV transformers T-2 & T3 with 33 kV Bus
Bakulia |  | 0:10 | 44 | 7.3333 | Due to tripping of 132/33 kV transformersT 1 & T2
Dohazari | 2 | 1:04 | 15 | 16 | Due to red-hot maint 132/33 kV Transformer T1 with 33 kV Bus
|  | 1:46 | 15 | 26.5 | Due to S/D of 132/33 kV transformer T-1
Bhandaria | 1 | 1:23 | 15 | 20.75 | Due to S/D of 132/33 kV transformer T-2
Baroierhat |  | 1:09 | 20 | 23 | Due to S/D of 132/33 kV transformer T-1
Beanibazar | 2 | 0:35 | 56 | 32.6667 | Due to 33 kV feeder fault
Ashuganj |  | 1:16 | 746 | 944.9333 | Due to tripping of all transformer
Shahjibazar | 2 | 0:39 | 40 | 26 | Due to red-hot maint 132/33 kV Transformer T4
Chatak |  | 0:59 | 4 | 3.9333 | Due to red-hot maint 132/33 kV Transformer T2
B.Baria | 1 | 0:44 | 10 | 7.3333 | Due to 33 kV feeder fault
Ramganj | 1 | 1:14 | 40 | 49.3333 | Due to red-hot maint 132/33 kV Transformer T4
Chandpur | 1 | 3:33 | 25 | 88.75 | Due to S/D of 132/33 kV transformer T-5
Beanibazar | 2 | 2:56 | 35 | 102.6667 | Due to S/D of 132/33 kV transformer T-2
Ramganj |  | 1:08 | 35 | 39.6667
Barishal |  | 0:13 | 57 | 12.35 | Due to tripping 132/33 kV transformer T4 & T5
Barishal(S) | 1 | 1:48 | 15 | 27 | Due to red-hot maint of 132/33 kV Transformer T1
Mongla |  | 0:27 | 28 | 12.6 | Due to tripping 132/33 kV transformer T1 & T2
Rajbari |  | 1:39 | 18 | 29.7 | Due to red-hot maint 132/33 kV Transformer T1
Narial |  | 0:51 | 10 | 8.5 | Due to red-hot maint of 132/33 kV Transformer T2
Mongla |  | 0:56 | 25 | 23.3333 | Due to tripping 132/33 kV transformer T1 & T2
Magura | 2 | 9:00 | 17 | 153 | Due to tripping 132/33 kV transformer T1
|  | 0:16 | 48 | 12.8 | Due to tripping 132/33 kV transformer T2
Bhandaria |  | 0:31 | 15 | 7.75 | Due to red-hot maint 132/33 kV Transformer T1
Barishal(N) | 2 | 3:15 | 40 | 130 | Due to 33 kV feeder fault
Bhandaria |  | 1:00 | 34 | 34
Barisal | 1 | 0:05 | 32 | 2.6667 | Due to tripping of Barisal-Bhandaria 132 kV Ckt
Bagerhat |  | 0:13 | 35 | 7.5833 | Due to S/D of 132/33 kV transformers T- & T2
Satkhira | 1 | 3:25 | 40 | 136.6667 | Due to S/D of 132/33 kV transformer T2
Barisal(S) | 1 | 0:52 | 34 | 29.4667 | Due to S/D of 132/33 kV transformer T-1
Shariatpur |  | 0:23 | 40 | 15.3333 | Due to S/D of 33 kV feeder
Benapole |  | 2:21 | 20 | 47 | Due to red-hot maint of 132/33 kV Transformer T2
Pabna | 1 | 1:03 | 30 | 31.5
Jassore | 2 | 0:56 | 22 | 20.5333 | Due to 33 kV feeder fault
|  | 0:09 | 25 | 3.75
Shahjadpur | 1 | 0:37 | 15 | 9.25 | Due to S/D of 132/33 kV transformer T-3
Pabna | 1 | 1:32 | 30 | 46 | Due to S/D of 132/33 kV transformer T-2
Rangpur | 1 | 0:15 | 20 | 5 | Due to red-hot maint of 132/33 kV Transformer T3
|  | 1:10 | 20 | 23.3333 | Due to red-hot maint of 33 kV bus-1
Panchugarh | 1 | 1:24 | 10 | 14 | Due to red-hot maint of 132/33 kV Transformer T2
Mithapukur | 1 | 0:48 | 15 | 12 | Due to red-hot maint of 132/33 kV Transformer T1 | 4068.5833
Page: 2/2 |  |  |  |  | QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the Systems
Month:July 2022
| Total Nos.of | Total | Unserved | Total | Remarks
Sub-station | Interruption | Duration of | Load | Unserved
|  | Interruption | (MW) | Energy
|  | Hrs./Mins. |  | (MWH)
Bogura | 1 | 1:58 | 20 | 39.3333 | Due to red-hot maint of 132/33 kV Transformer T1
Amnura | 1 | 0:50 | 10 | 8.3333 | Due to tripping of 132/33 kV transformerT-1
Rajshahi | 1 | 0:14 | 75 | 17.5 | Due to 33 kV feeder fault
Naogaon | 1 | 4:55 | 15 | 73.75 | Due to red-hot maint of 132/33 kV Transformer T2
Niyamatpur | 1 | 1:13 | 15 | 18.25 | Due to red-hot maint of 132/33 kV Transformer T1
Natore | 1 | 0:16 | 8 | 2.1333 | Due to 33 kV feeder fault
Niyamatpur | 2 | 12:35 | 55 | 692.0833 | Due to S/D of 33 kV Bus-1 & 2
|  | 2:17 | 40 | 91.3333 | Due to S/D of 132/33 kV transformer T-1
Bogura | 1 | 3:14 | 40 | 129.3333 | Due to S/D of 132/33 kV transformer T-1
Thakurgaon | 1 | 1:21 | 30 | 40.5 | Due to S/D of 33 kV Bus-3
Rajshahi | 1 | 12:07 | 21 | 254.45 | Due to S/D of 132/33 kV transformer T-3
Rangpur | 1 | 3:25 | 50 | 170.8333 | Due to S/D of 33 kV Bus
Thakurgaon | 1 | 1:50 | 106 | 194.3333 | Due to S/D of Thakurgaon-Thakurgaon P/S 132 kV Ckt
| Total Unserved energy : |  |  | 4873.0833 | MWH
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-33
Page: 1/3 |  |  |  | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month: July '2022
Sl. No | Name of the Sub-station | Date and Time | MW | Remarks
1 | Aftabnagar 132/33kV Grid Sub-Station | 2022-07-02 02:00 | 58
2 | Agargaon 230/132kV Grid Sub-Station | 2022-07-17 13:00 | 98
3 | Agrabad 132/33kV Grid Sub-Station | 2022-07-07 14:00 | 96
4 | AKS 132/33kV Grid Sub-Station | 2022-07-07 13:00 | 23
5 | AKSML 230/33kV Grid Sub-Station | 2022-07-25 23:00 | 155
6 | Amnura 132/33kV Grid Sub-Station | 2022-07-17 22:00 | 73
7 | Ashuganj 230/132/33kV Sub-Station | 2022-07-06 | 48
8 | Bagerhat 132/33kV Grid Sub-Station | 2022-07-17 21:00 | 108
9 | Bakulia 132/33kV Grid Sub-Station | 2022-07-31 20:00 | 138
10 | Banani 132/33kV Grid Sub-Station | 2022-07-03 03:00 | 170
11 | Bangabhaban 132/33kV Grid Sub-Station | 2022-07-17 10:00 | 24
12 | Barapukuria 230/132/33kV Grid Sub-Station | 2022-07-17 22:00 | 59
13 | Barguna 132/33kV Grid Sub-Station | 2022-07-19 22:00 | 22
14 | Barishal 132/33kV Grid Sub-Station | 2022-07-03 22:00 | 121
15 | Barishal 230/132kV Grid Sub-Station | 2022-07-06 19:30 | 86
16 | Baroaulia 132/33kV Grid Sub-Station | 2022-07-05 16:00 | 152
17 | Baroirhat 132/33kV Grid Sub-Station | 2022-07-08 02:00 | 63
18 | Bashundhara 132/33kV Grid Sub-Station | 2022-07-29 17:00 | 170
19 | BashundharaCement 132/33kV Sub-Station | 2022-07-17 01:00 | 61
20 | Beanibazar 132/33kV Grid Sub-Station | 2022-07-10 21:00 | 78
21 | Benapole 132/33kV Grid Sub-Station | 2022-07-11 21:00 | 62
22 | Bhaluka 132/33kV Grid Sub-Station | 2022-07-02 19:00 | 146
23 | Bhandaria 132/33kV Grid Sub-Station | 2022-07-04 23:00 | 62
24 | Bhangura 132/33kV Grid Sub-Station | 2022-07-07 20:00 | 40
25 | Bheramara(GK) 132/33kV Grid Sub-Station | 2022-07-16 21:00 | 67
26 | Bhulta 132/33kV Grid Sub-Station | 2022-07-02 19:30 | 277
27 | Bog-Sherpur 132/33kV Grid Sub-Station | 2022-07-16 20:00 | 70
28 | Bogura 132/33kV Grid Sub-Station | 2022-07-17 21:00 | 180
29 | Borhanuddin 230/33kV Grid Sub-Station | 2022-07-12 22:00 | 46
30 | Brahmanbaria 132/33kV Grid Sub-Station | 2022-07-10 23:00 | 190
31 | BSRM 230/33kV Grid Sub-Station | 2022-07-19 01:00 | 167
32 | Cantonment 132/33kV GIS Grid Sub-Station | 2022-07-18 15:00 | 154
33 | Chandpur 132/33kV Grid Sub-Station | 2022-07-15 21:00 | 78
34 | Chandraghona 132/33kV Grid Sub-Station | 2022-07-10 21:00 | 36
35 | Chapai 132/33kV Grid Sub-Station | 2022-07-18 03:00 | 85
36 | Charsaidpur 132/33kV Sub-Station | 2022-07-29 12:00 | 49
37 | Chauddagram 132/33kV Grid Sub-Station | 2022-07-29 22:00 | 63
38 | Chhatak 132/33kV Grid Sub-Station | 2022-07-10 21:00 | 36
39 | Chowmuhani 132/33kV Grid Sub-Station | 2022-07-10 21:00 | 232
40 | Chuadanga 132/33kV Grid Sub-Station | 2022-07-23 21:00 | 117
41 | Coxsbazar 132/33kV Grid Sub-Station | 2022-07-31 22:00 | 130
42 | Cumilla(N) 230/132/33kV Grid Sub-Station | 2022-07-10 23:00 | 174
43 | Cumilla(S) 132/33kV Grid Sub-Station | 2022-07-19 23:00 | 182
44 | Daudkandi 132/33kV Grid Sub-Station | 2022-07-13 22:00 | 168
45 | Dhaka University 132/33kV Grid Sub-Station | 2022-07-03 11:00 | 44
46 | Dhamrai 132/33kV Grid Sub-Station | 2022-07-03 12:00 | 122
47 | Dhanmondi 132/33kV Grid Sub-Station | 2022-07-04 12:00 | 148
48 | Dohazari 132/33kV Grid Sub-Station | 2022-07-14 | 112
49 | Faridpur 132/33kV Grid Sub-Station | 2022-07-16 22:00 | 159
50 | Fatullah 132/33kV Grid Sub-Station | 2022-07-27 10:00 | 71
51 | Fenchuganj 230/132/33kV Grid Sub-Station | 2022-07-16 19:00 | 52
52 | Feni 132/33kV Grid Sub-Station | 2022-07-10 22:00 | 138
53 | Ghorashal 132/33kV Sub-Station | 2022-07-04 20:00 | 73
Page: 2/3 |  |  |  | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month: July '2022
Sl. No | Name of the Sub-station | Date and Time | MW | Remarks
54 | Goalpara 132/33kV Grid Sub-Station | 2022-07-04 13:00 | 30
56 | Gollamari 132/33kV Grid Sub-Station | 2022-07-05 18:00 | 66
57 | Gopalganj 132/33kV Grid Sub-Station | 2022-07-12 22:00 | 108.6
58 | GPH 230/33kV Grid Sub-Station | 2022-07-15 05:00 | 94
59 | Gulshan 132/33kV Grid Sub-Station | 2022-07-18 12:00 | 132
60 | Halishahar 132/33kV Grid Sub-Station | 2022-07-20 08:00 | 106
61 | HaripurSBU 132/33kV Sub-Station | 2022-07-08 18:00 | 175
62 | Hasnabad 132/33kV Grid Substation | 2022-07-04 23:00 | 122
63 | Hathazari 230/132/33kV Grid Sub-Station | 2022-07-30 19:30 | 107
64 | Ishurdi 132/33kV Grid Sub-Station | 2022-07-21 19:30 | 81
65 | Jaldhaka 132/33kV Grid Sub-Station | 2022-07-15 21:00 | 77
66 | Jamalpur 132/33kV Grid Sub-Station | 2022-07-08 20:00 | 165
67 | Jashore 132/33kV Grid Sub-Station | 2022-07-27 08:00 | 149
68 | Jhenaidah 132/33kV Grid Sub-Station | 2022-07-29 20:00 | 132
69 | Joydebpur 132/33kV Grid Sub-Station | 2022-07-31 21:00 | 202
70 | Joypurhat 132/33kV Grid Sub-Station | 2022-07-18 22:00 | 66
71 | Juldah 132/33kV Grid Sub-Station | 2022-07-07 11:00 | 30
72 | Kabirpur 132/33kV Grid Sub-Station | 2022-07-27 22:00 | 311
73 | Kachua 132/33kV Grid Sub-Station | 2022-07-10 22:00 | 92
74 | Kallyanpur 132/33kV Grid Sub-Station | 2022-07-05 21:00 | 108
75 | Kalurghat 132/33kV Grid Sub-Station | 2022-07-04 16:00 | 33
76 | Kamrangirchar 132/33kV Grid Sub-Station | 2022-07-03 12:00 | 71
77 | Kaptai 132/33kV Sub-Station | 2022-07-11 20:00 | 5
78 | Kazla 132/33kV Grid Sub-Station | 2022-07-05 11:00 | 94
79 | Keranigonj 230/132/33kV Grid Sub-Station | 2022-07-06 13:00 | 64
80 | Khagrachori 132/33kV Grid Sub-Station | 2022-07-07 19:30 | 30
81 | Khulna (C) 132/33kV Grid Sub-Station | 2022-07-05 17:00 | 103
82 | Khulshi 132/33kV Grid Sub-Station | 2022-07-02 14:00 | 203
83 | Kishoreganj 132/33kV Grid Sub-Station | 2022-07-12 23:00 | 168
84 | Kodda 132/33kV Grid Sub-Station | 2022-07-31 18:00 | 330
85 | KSRM 132/33kV Grid Sub-Station | 2022-07-18 23:00 | 45.76
86 | Kulaura 132/33kV Grid Sub-Station | 2022-07-10 22:00 | 54
87 | Kurigram 132/33kV Grid Sub-Station | 2022-07-10 22:00 | 136
88 | Kushtia 132/33kV Grid Sub-Station | 2022-07-16 20:00 | 146
89 | Lalbag 132/33kV Grid Sub-Station | 2022-07-23 13:00 | 106
90 | Lalmonirhat 132/33kV Grid Sub-Station | 2022-07-16 22:00 | 57
91 | Madanganj 132/33kV Grid Sub-Station | 2022-07-28 02:00 | 330
92 | Madaripur 132/33kV Grid Sub-Station | 2022-07-10 23:00 | 122
93 | Madartek 132/33kV Grid Sub-Station | 2022-07-23 23:00 | 90
94 | Madunaghat 132/33kV Grid Sub-Station | 2022-07-30 19:00 | 67
95 | Magura 132/33kV Grid Sub-Station | 2022-07-29 21:00 | 65
96 | Mahasthangarh 132/33kV Grid Sub-Station | 2022-07-12 | 78
97 | Manikganj 132/33kV Grid Sub-Station | 2022-07-05 20:00 | 100
98 | Maniknagar 132/33kV Grid Sub-Station | 2022-07-03 13:00 | 90
99 | Matarbari 132/33kV Sub-Station | 2022-07-22 19:30 | 45
100 | Matuail 132/33kV Grid Sub-Station | 2022-07-26 10:00 | 65
101 | Millgate Tongi 132/33kV Grid Sub-Station | 2022-07-21 12:00 | 77
101 | Mirpur 132/33kV Grid Sub-Station | 2022-07-23 17:00 | 138
102 | Mirsorai 230/33kV Grid Sub-Station | 2022-07-31 21:00 | 2.81
Page: 3/3 |  |  |  | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month: July '2022
Sl. No | Name of the Sub-station | Date and Time | MW | Remarks
103 | Mithapukur 132/33kV Grid Sub-Station | 2022-07-16 10:00 | 46
104 | Modern Steel 132/11kV Grid Sub-Station | 2022-07-01 | 0
105 | Mogbazar 132/33kV Grid Sub-Station | 2022-07-17 16:00 | 137
106 | Mongla 132/33kV Grid Sub-Station | 2022-07-02 12:00 | 44
107 | Motijheel 132/33kV Grid Sub-Station | 2022-07-17 15:00 | 40
108 | Munshiganj 132/33kV Grid Sub-Station | 2022-07-21 | 126
109 | Mymensingh 132/33kV Grid Sub-Station | 2022-07-29 20:00 | 246
110 | Naogaon 132/33kV Grid Sub-Station | 2022-07-07 23:00 | 138
111 | Narail 132/33kV Grid Sub-Station | 2022-07-14 22:00 | 58
112 | Narinda 132/33kV Grid Sub-Station | 2022-07-31 13:00 | 74
113 | Narshingdi 132/33kV Grid Sub-Station | 2022-07-01 23:00 | 189
114 | Natore 132/33kV Grid Sub-Station | 2022-07-18 22:00 | 158
115 | Nawabganj 132/33kV Grid Sub-Station | 2022-07-10 22:00 | 62.4
116 | Netrakona 132/33kV Grid Sub-Station | 2022-07-09 21:00 | 142
117 | New Tongi 132/33kV Grid Sub-Station | 2022-07-02 15:00 | 87.4
118 | Niamatpur 132/33kV Grid Sub-Station | 2022-07-22 20:00 | 107
119 | Noapara 132/33kV Grid Sub-Station | 2022-07-07 21:00 | 55
120 | Pabna 132/33kV Grid Sub-Station | 2022-07-18 20:00 | 116
121 | Palashbari 132/33kV Grid Sub-Station | 2022-07-12 | 136
122 | Panchagarh 132/33kV Grid Sub-Station | 2022-07-16 20:00 | 71
123 | Patuakhali 132/33kV Grid Sub-Station | 2022-07-12 02:00 | 146
124 | Payra 400/132/33kV Grid Sub-Station | 2022-07-31 16:00 | 1.14
125 | PHP 132/33kV Sub-Station | 2022-07-04 10:00 | 11
126 | Postogola 132/33kV Grid Sub-Station | 2022-07-31 | 46
127 | Purbachal 132/33kV Grid Sub-Station | 2022-07-03 23:00 | 20
128 | Purbasadipur 132/33kV Grid Sub-Station | 2022-07-17 19:30 | 131
129 | Rahim Steel 132/33kV Sub-Station | 2022-07-02 14:00 | 117
130 | Rajbari 132/33kV Grid Sub-Station | 2022-07-10 22:00 | 72
131 | Rajendrapur 132/33kV Grid Sub-Station | 2022-07-17 22:00 | 124
132 | Rajshahi 132/33kV Grid Sub-Station | 2022-07-17 21:00 | 173
133 | Rajshahi 230/132/33kV Grid Sub-Station | 2022-07-14 13:00 | 35
134 | Ramganj 132/33kV Grid Sub-Station | 2022-07-14 22:00 | 132
135 | Rampur 230/132/33 kV GIS Grid Sub-Station | 2022-07-31 19:00 | 24
136 | Rangamati 132/33kV Grid Sub-Station | 2022-07-02 19:30 | 14
137 | Rangpur 132/33kV Grid Sub-Station | 2022-07-07 20:00 | 172
138 | Ruppur 132/11kV Grid Sub-Station | 2022-07-26 11:00 | 5.2
139 | Saidpur 132/33kV Grid Sub-Station | 2022-07-16 22:00 | 119
140 | Satkhira 132/33kV Grid Sub-Station | 2022-07-07 22:00 | 128
141 | Satmasjid 132/33kV Grid Sub-Station | 2022-07-30 23:00 | 111
142 | Savar 132/33kV Grid Sub-Station | 2022-07-03 21:00 | 189
143 | Shahjadpur 132/33kV Grid Sub-Station | 2022-07-13 18:30 | 116
144 | Shahjibazar 132/33kV Grid Sub-Station | 2022-07-30 21:00 | 135
145 | Shahmirpur 132/33kV Grid Sub-Station | 2022-07-19 01:00 | 58
146 | Shariatpur 132/33kV Grid Sub-Station | 2022-07-10 23:00 | 90
147 | Sherpur 132/33kV Grid Sub-Station | 2022-07-12 21:00 | 160
148 | Shikalbaha 132/33kV Sub-Station | 2022-07-05 20:00 | 35
149 | Shitalakhya 132/33kV Grid Sub-Station | 2022-07-05 11:00 | 130
150 | Shyampur 132/33kV Grid Sub-Station | 2022-07-28 12:00 | 180
151 | Siddhirganj 132/33kV Grid Sub-Station | 2022-07-23 17:00 | 122
152 | Sirajganj 132/33kV Grid Sub-Station | 2022-07-07 21:00 | 121
153 | Sonargaon 132/33kV Grid Sub-Station | 2022-07-19 | 109
154 | Sreemongol 132/33kV Grid Sub-Station | 2022-07-27 22:00 | 69
155 | Srinagar 132/33kV Grid Sub-Station | 2022-07-10 22:00 | 52.1
156 | SSM 132/33kV Grid Sub-Station | 2022-07-06 | 19
157 | Sunamganj 132/33kV Grid Sub-Station | 2022-07-14 21:00 | 60
158 | Sylhet 132/33kV Grid Sub-Station | 2022-07-14 19:00 | 172
159 | Tangail 132/33kV Grid Sub-Station | 2022-07-07 23:00 | 233
160 | Thakurgaon 132/33kV Grid Sub-Station | 2022-07-07 21:00 | 108
161 | TK chemical 132kV Grid Sub-Station | 2022-07-31 20:00 | 33
162 | Tongi 230/132/33kV Grid Sub-Station | 2022-07-18 15:00 | 137
163 | Ullon 132/33kV Grid Sub-Station | 2022-07-02 07:00 | 73
164 | Uttara 132/33kV Grid Sub-Station | 2022-07-17 16:00 | 100
165 | UttaraNew 132/33kV Grid Sub-Station | 2022-07-28 15:00 | 20
166 | Zigatola 132/33kV Grid Sub-Station | 2022-07-30 23:00 | 63
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID COMPANY OF BANGLADESH LTD. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month:July 2022
Area | MW | Date | Hour | Remarks
Dhaka | 4971.57 | 2022-06-07 | 15:00
Chattogram | 1431.6 | 2022-08-07 | 0:00
Cumilla | 1411.5 | 2022-10-07 | 23:00
Mymensingh | 1152 | 2022-08-07 | 21:00
Sylhet | 608 | 16/07/2022 | 21:00
Khulna | 1735.8 | 2022-07-05 | 21:00
Barishal | 441.77 | 14/07/2022 | 23:00
Rajshahi | 1543.2 | 17/07/2022 | 22:00
Rangpur | 973 | 17/07/2022 | 20:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-35
| Page: 1/3 | [5 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: July '2022
SL. | 400 KV Substation | Rated | Maxm |  | Minm | Date and Time
No. |  | Voltage | Voltage | Date and Time | Voltage |  | Remarks
|  | kV | kV |  | kV
1 | Bhulta 400/230kV Grid Sub-Station | 400 | 408 | 2022-07-10 08:00 | 357 | 2022-07-31 17:00
2 | Bibiana 400/230kV Sub-Station | 400 | 416 | 2022-07-09 19:30 | 392 | 2022-07-27 14:00
3 | BIPTC | 400 | 408 | 2022-07-09 06:00 | 385 | 2022-07-18 13:00
4 | Gopalganj_I 400/132kV Grid Sub-Station | 400 | 422 | 2022-07-10 08:00 | 388 | 2022-07-12 21:00
5 | Kaliakoir 400/230/132kV Grid Sub-Station | 400 | 410 | 2022-07-13 04:00 | 347 | 2022-07-30 17:00
|  | Rated | Maxm |  | Minm | Date and Time
SL. | Substation | Voltage | Voltage | Date and Time | Voltage |  | Remarks
No. | 230 KV Substation | kV | kV |  | kV
1 | Agargaon 230/132kV Grid Sub-Station | 230 | 233 | 2022-07-11 19:30 | 205 | 2022-07-27 10:00
2 | AKSML 230/33kV Grid Sub-Station | 230 | 241 | 2022-07-19 08:00 | 207 | 2022-07-16 12:00
3 | Aminbazar 230/132kV Grid Sub-Station | 230 | 238 | 2022-07-10 19:30 | 206 | 2022-07-23 12:00
4 | Baghabari 230/132kV Grid Sub-Station | 230 | 238 | 2022-07-04 06:00 | 224 | 2022-07-10 20:00
5 | Barapukuria 230/132/33kV Grid Sub-Station | 230 | 230 | 2022-07-03 16:00 | 205 | 2022-07-16 23:00
6 | Barishal 230/132kV Grid Sub-Station | 230 | 248 | 2022-07-21 18:30 | 232 | 2022-07-01 22:00
7 | Bheramara 230/132kV Grid Sub-Station | 230 | 237 | 2022-07-10 07:00 | 221 | 2022-07-15 21:00
8 | Bogura 230/132kV Grid Sub-Station | 230 | 255 | 2022-07-21 23:00 | 210 | 2022-07-18
9 | BSRM 230/33kV Grid Sub-Station | 230 | 236 | 2022-07-02 23:00 | 216 | 2022-07-16 11:00
10 | Cumilla(N) 230/132/33kV Grid Sub-Station | 230 | 233 | 2022-07-09 18:30 | 217 | 2022-07-23 11:00
11 | Fenchuganj 230/132/33kV Grid Sub-Station | 230 | 245 | 2022-07-12 18:30 | 231 | 2022-07-23 09:00
12 | GPH 230/33kV Grid Sub-Station | 230 | 239 | 2022-07-02 23:00 | 212 | 2022-07-16 11:00
13 | Haripur 230/132kV Grid Sub-Station | 230 | 233 | 2022-07-11 18:30 | 209 | 2022-07-23 11:00
14 | Hasnabad 230/132kV Grid Sub-Station | 230 | 233 | 2022-07-15 11:00 | 205 | 2022-07-23 09:00
15 | Hathazari 230/132/33kV Grid Sub-Station | 230 | 240 | 2022-07-05 | 214 | 2022-07-16 12:00
16 | Ishurdi 230/132kV Grid Sub-Station | 230 | 238 | 2022-07-07 18:00 | 224 | 2022-07-09 23:00
17 | Jhenaidah 230/132kV Grid Sub-Station | 230 | 234 | 2022-07-03 20:00 | 212 | 2022-07-09 20:00
18 | Keranigonj 230/132/33kV Grid Sub-Station | 230 | 232 | 2022-07-11 19:30 | 204 | 2022-07-27 10:00
19 | Khulna(S) 230/132kV Grid Sub-Station | 230 | 243 | 2022-07-03 20:00 | 217 | 2022-07-10 19:30
20 | Maniknagar 230/132kV Grid Sub-Station | 230 | 235 | 2022-07-10 08:00 | 208 | 2022-07-31 12:00
21 | Meghnaghat 230/132kV Grid Sub-Station | 230 | 237 | 2022-07-10 08:00 | 212 | 2022-07-23 11:00
22 | Mirsorai 230/33kV Grid Sub-Station | 230 | 234 | 2022-07-31 19:30 | 227 | 2022-07-31 23:00
23 | Rajshahi 230/132/33kV Grid Sub-Station | 230 | 238 | 2022-07-07 18:30 | 217 | 2022-07-14 21:00
24 | Rampura 230/132kV Grid Sub-Station | 230 | 235 | 2022-07-20 01:00 | 210 | 2022-07-25 11:00
25 | Shikalbaha 230/132kV Grid Sub-Station | 230 | 240 | 2022-07-28 22:00 | 214 | 2022-07-16 12:00
26 | Shyampur 230/132kV Grid Sub-Station | 230 | 232 | 2022-07-10 08:00 | 205 | 2022-07-27 10:00
27 | Siddhirganj 230/132kV Grid Sub-Station | 230 | 240 | 2022-07-02 16:00 | 211 | 2022-07-27 12:00
28 | Sirajgonj 230 kV Switching Station | 230 | 239 | 2022-07-05 18:30 | 225 | 2022-07-11 23:00
29 | Tongi 230/132/33kV Grid Sub-Station | 230 | 255 | 2022-07-21 07:00 | 209 | 2022-07-31 17:00
| Page: 2/3 | [5 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: July '2022
|  | Rated | Maxm |  | Minm | Date and Time
SL. | Substation | Voltage | Voltage | Date and Time | Voltage |  | Remarks
No. | 132 KV Substation | kV | kV |  | kV
1 | Aftabnagar 132/33kV Grid Sub-Station | 132 | 139 | 2022-07-30 05:00 | 120 | 2022-07-20 14:00
2 | Agrabad 132/33kV Grid Sub-Station | 132 | 141 | 2022-07-18 21:00 | 123 | 2022-07-16 12:00
3 | AKS 132/33kV Grid Sub-Station | 132 | 140 | 2022-07-04 19:30 | 122 | 2022-07-16 12:00
4 | Amnura 132/33kV Grid Sub-Station | 132 | 138 | 2022-07-07 18:00 | 119 | 2022-07-18 07:00
5 | Ashuganj 230/132/33kV Sub-Station | 132 | 138 | 2022-07-01 18:30 | 129 | 2022-07-15 20:00
6 | Bagerhat 132/33kV Grid Sub-Station | 132 | 137 | 2022-07-03 13:00 | 117 | 2022-07-10 21:00
7 | Bakulia 132/33kV Grid Sub-Station | 132 | 142 | 2022-07-19 19:30 | 123 | 2022-07-16 11:00
8 | Banani 132/33kV Grid Sub-Station | 132 | 141 | 2022-07-10 08:00 | 120 | 2022-07-31 17:00
9 | Bangabhaban 132/33kV Grid Sub-Station | 132 | 135 | 2022-07-29 19:30 | 123 | 2022-07-27 10:00
10 | Barguna 132/33kV Grid Sub-Station | 132 | 140 | 2022-07-11 18:00 | 126 | 2022-07-12 23:00
11 | Barishal 132/33kV Grid Sub-Station | 132 | 141 | 2022-07-24 18:00 | 123 | 2022-07-13 14:00
12 | Baroaulia 132/33kV Grid Sub-Station | 132 | 143 | 2022-07-04 19:00 | 125 | 2022-07-16 11:00
13 | Baroirhat 132/33kV Grid Sub-Station | 132 | 138 | 2022-07-31 19:30 | 114 | 2022-07-17 11:00
14 | Bashundhara 132/33kV Grid Sub-Station | 132 | 140 | 2022-07-10 07:00 | 120 | 2022-07-31 17:00
15 | BashundharaCement 132/33kV Sub-Station | 132 | 139 | 2022-07-08 08:00 | 117 | 2022-07-28 01:00
16 | Beanibazar 132/33kV Grid Sub-Station | 132 | 134 | 2022-07-11 01:00 | 122 | 2022-07-10 21:00
17 | Benapole 132/33kV Grid Sub-Station | 132 | 140 | 2022-07-10 08:00 | 121 | 2022-07-10 19:30
18 | Bhaluka 132/33kV Grid Sub-Station | 132 | 135 | 2022-07-11 18:30 | 113 | 2022-07-06 03:00
19 | Bhandaria 132/33kV Grid Sub-Station | 132 | 140 | 2022-07-23 12:00 | 121 | 2022-07-08 23:00
20 | Bhangura 132/33kV Grid Sub-Station | 132 | 140 | 2022-07-07 18:30 | 130 | 2022-07-14
21 | Bheramara(GK) 132/33kV Grid Sub-Station | 132 | 140 | 2022-07-08 18:00 | 131 | 2022-07-07 21:00
22 | Bhulta 132/33kV Grid Sub-Station | 132 | 133 | 2022-07-09 19:30 | 114 | 2022-07-23 09:00
23 | Bog-Sherpur 132/33kV Grid Sub-Station | 132 | 139 | 2022-07-24 17:00 | 122 | 2022-07-15
24 | Bogura 132/33kV Grid Sub-Station | 132 | 140 | 2022-07-21 16:00 | 122 | 2022-07-15
25 | Brahmanbaria 132/33kV Grid Sub-Station | 132 | 138 | 2022-07-20 14:00 | 113 | 2022-07-14 13:00
26 | Cantonment 132/33kV GIS Grid Sub-Station | 132 | 138 | 2022-07-10 08:00 | 122 | 2022-07-03 11:00
27 | Chandpur 132/33kV Grid Sub-Station | 132 | 140 | 2022-07-02 18:00 | 119 | 2022-07-12 02:00
28 | Chandraghona 132/33kV Grid Sub-Station | 132 | 141 | 2022-07-04 19:00 | 124 | 2022-07-16 11:00
29 | Chapai 132/33kV Grid Sub-Station | 132 | 137 | 2022-07-01 18:00 | 119 | 2022-07-18 07:00
30 | Charsaidpur 132/33kV Sub-Station | 132 | 140 | 2022-07-11 18:30 | 123 | 2022-07-23 09:00
31 | Chauddagram 132/33kV Grid Sub-Station | 132 | 138 | 2022-07-31 19:00 | 119 | 2022-07-16
32 | Chhatak 132/33kV Grid Sub-Station | 132 | 135 | 2022-07-06 02:00 | 119 | 2022-07-17 02:00
33 | Chowmuhani 132/33kV Grid Sub-Station | 132 | 137 | 2022-07-26 18:30 | 113 | 2022-07-13 13:00
34 | Chuadanga 132/33kV Grid Sub-Station | 132 | 140 | 2022-07-21 16:00 | 114 | 2022-07-10 21:00
35 | Coxsbazar 132/33kV Grid Sub-Station | 132 | 134 | 2022-07-04 19:30 | 113 | 2022-07-05 20:00
36 | Cumilla(S) 132/33kV Grid Sub-Station | 132 | 137 | 2022-07-07 18:00 | 124 | 2022-07-16
37 | Daudkandi 132/33kV Grid Sub-Station | 132 | 137 | 2022-07-18 21:00 | 121 | 2022-07-19 19:00
38 | Dhaka University 132/33kV Grid Sub-Station | 132 | 139 | 2022-07-10 08:00 | 123 | 2022-07-03 11:00
39 | Dhamrai 132/33kV Grid Sub-Station | 132 | 137 | 2022-07-10 08:00 | 121 | 2022-07-02 12:00
40 | Dhanmondi 132/33kV Grid Sub-Station | 132 | 139 | 2022-07-12 19:00 | 122.5 | 2022-07-31 12:00
41 | Dohazari 132/33kV Grid Sub-Station | 132 | 141 | 2022-07-18 23:00 | 122 | 2022-07-16 11:00
42 | Faridpur 132/33kV Grid Sub-Station | 132 | 137 | 2022-07-10 08:00 | 124 | 2022-07-12 23:00
43 | Fatullah 132/33kV Grid Sub-Station | 132 | 140 | 2022-07-08 13:00 | 123 | 2022-07-25 11:00
44 | Feni 132/33kV Grid Sub-Station | 132 | 139 | 2022-07-26 19:30 | 118 | 2022-07-17 11:00
45 | Ghorashal 132/33kV Sub-Station | 132 | 143 | 2022-07-18 21:00 | 122 | 2022-07-23 11:00
46 | Goalpara 132/33kV Grid Sub-Station | 132 | 140 | 2022-07-12 18:30 | 121 | 2022-07-10 19:30
47 | Gollamari 132/33kV Grid Sub-Station | 132 | 140 | 2022-07-13 18:30 | 122 | 2022-07-12 21:00
48 | Gopalganj 132/33kV Grid Sub-Station | 132 | 143 | 2022-07-26 18:30 | 122 | 2022-07-12 21:00
49 | Gulshan 132/33kV Grid Sub-Station | 132 | 138 | 2022-07-10 07:00 | 122 | 2022-07-03 11:00
50 | Halishahar 132/33kV Grid Sub-Station | 132 | 141 | 2022-07-18 21:00 | 124 | 2022-07-16 11:00
51 | HaripurSBU 132/33kV Sub-Station | 132 | 139 | 2022-07-06 | 124 | 2022-07-25 11:00
52 | Hasnabad 132/33kV Grid Substation | 132 | 140 | 2022-07-08 06:00 | 125 | 2022-07-23 09:00
53 | Ishurdi 132/33kV Grid Sub-Station | 132 | 139 | 2022-07-10 08:00 | 130 | 2022-07-10 21:00
54 | Jaldhaka 132/33kV Grid Sub-Station | 132 | 136 | 2022-07-31 04:00 | 113 | 2022-07-06 03:00
55 | Jamalpur 132/33kV Grid Sub-Station | 132 | 140 | 2022-07-22 13:00 | 113 | 2022-07-09 01:00
56 | Jashore 132/33kV Grid Sub-Station | 132 | 139 | 2022-07-11 18:00 | 121 | 2022-07-10 21:00
57 | Jhenaidah 132/33kV Grid Sub-Station | 132 | 143 | 2022-07-21 16:00 | 125 | 2022-07-10 21:00
58 | Joydebpur 132/33kV Grid Sub-Station | 132 | 145 | 2022-07-08 19:00 | 132 | 2022-07-31 14:00
59 | Joypurhat 132/33kV Grid Sub-Station | 132 | 140 | 2022-07-31 20:00 | 113 | 2022-07-11 22:00
60 | Juldah 132/33kV Grid Sub-Station | 132 | 142 | 2022-07-04 23:00 | 124 | 2022-07-16 11:00
61 | Kabirpur 132/33kV Grid Sub-Station | 132 | 141 | 2022-07-07 18:00 | 116 | 2022-07-31 17:00
| Page: 3/3 | [5 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: July '2022
Rated
SL. | Substation | Voltage | Voltage | Date and Time | Voltage | Date and Time | Remarks
No. | 132 KV Substation | kV | kV |  | kV
62 | Kachua 132/33kV Grid Sub-Station | 132 | 139 | 2022-07-20 18:00 | 120 | 2022-07-12 02:00
63 | Kallyanpur 132/33kV Grid Sub-Station | 132 | 138 | 2022-07-11 19:30 | 121 | 2022-07-23 09:00
64 | Kalurghat 132/33kV Grid Sub-Station | 132 | 141 | 2022-07-19 19:30 | 125 | 2022-07-16 12:00
65 | Kamrangirchar 132/33kV Grid Sub-Station | 132 | 141 | 2022-07-11 19:30 | 124 | 2022-07-23 09:00
66 | Kaptai 132/33kV Sub-Station | 132 | 140 | 2022-07-27 19:30 | 126 | 2022-07-16 13:00
67 | Kazla 132/33kV Grid Sub-Station | 132 | 136 | 2022-07-02 04:00 | 121 | 2022-07-19 13:00
68 | Khagrachori 132/33kV Grid Sub-Station | 132 | 139 | 2022-07-04 19:30 | 124 | 2022-07-16 11:00
69 | Khulna (C) 132/33kV Grid Sub-Station | 132 | 139 | 2022-07-10 08:00 | 122 | 2022-07-10 19:30
70 | Khulshi 132/33kV Grid Sub-Station | 132 | 140 | 2022-07-19 07:00 | 122 | 2022-07-16 11:00
71 | Kishoreganj 132/33kV Grid Sub-Station | 132 | 135 | 2022-07-04 20:00 | 115 | 2022-07-15 20:00
72 | Kodda 132/33kV Grid Sub-Station | 132 | 145 | 2022-07-13 18:30 | 122 | 2022-07-15 09:00
73 | KSRM 132/33kV Grid Sub-Station | 132 | 141 | 2022-07-05 | 124 | 2022-07-16 11:00
74 | Kulaura 132/33kV Grid Sub-Station | 132 | 137 | 2022-07-01 05:00 | 130 | 2022-07-07 21:00
75 | Kurigram 132/33kV Grid Sub-Station | 132 | 136 | 2022-07-31 05:00 | 113 | 2022-07-10 03:00
76 | Kushtia 132/33kV Grid Sub-Station | 132 | 139 | 2022-07-13 18:30 | 128 | 2022-07-07 21:00
77 | Lalbag 132/33kV Grid Sub-Station | 132 | 141 | 2022-07-10 08:00 | 125 | 2022-07-23 09:00
78 | Lalmonirhat 132/33kV Grid Sub-Station | 132 | 138 | 2022-07-02 17:00 | 113 | 2022-07-06 02:00
79 | Madanganj 132/33kV Grid Sub-Station | 132 | 139 | 2022-07-11 20:00 | 122 | 2022-07-23 09:00
80 | Madaripur 132/33kV Grid Sub-Station | 132 | 142 | 2022-07-26 18:30 | 125 | 2022-07-12 22:00
81 | Madartek 132/33kV Grid Sub-Station | 132 | 139 | 2022-07-10 08:00 | 122 | 2022-07-03 11:00
82 | Madunaghat 132/33kV Grid Sub-Station | 132 | 141 | 2022-07-27 18:00 | 125 | 2022-07-16 11:00
83 | Magura 132/33kV Grid Sub-Station | 132 | 142 | 2022-07-21 16:00 | 123 | 2022-07-14 22:00
84 | Mahasthangarh 132/33kV Grid Sub-Station | 132 | 138 | 2022-07-24 18:00 | 118 | 2022-07-15
85 | Manikganj 132/33kV Grid Sub-Station | 132 | 138 | 2022-07-02 06:00 | 124 | 2022-07-30 10:00
86 | Maniknagar 132/33kV Grid Sub-Station | 132 | 136 | 2022-07-01 05:00 | 120 | 2022-07-23 10:00
87 | Matarbari 132/33kV Sub-Station | 132 | 136 | 2022-07-05 09:00 | 113 | 2022-07-05 23:00
88 | Matuail 132/33kV Grid Sub-Station | 132 | 138.2 | 2022-07-11 20:00 | 122 | 2022-07-27 10:00
89 | Millgate Tongi 132/33kV Grid Sub-Station | 132 | 140 | 2022-07-10 07:00 | 121 | 2022-07-31 17:00
90 | Mirpur 132/33kV Grid Sub-Station | 132 | 137 | 2022-07-11 19:00 | 117 | 2022-07-23 09:00
91 | Mithapukur 132/33kV Grid Sub-Station | 132 | 137 | 2022-07-19 17:00 | 114 | 2022-07-18 03:00
92 | Modern Steel 132/11kV Grid Sub-Station | 132 | 141 | 2022-07-05 | 124 | 2022-07-16 11:00
93 | Mogbazar 132/33kV Grid Sub-Station | 132 | 139 | 2022-07-29 08:00 | 122 | 2022-07-19 12:00
94 | Mongla 132/33kV Grid Sub-Station | 132 | 136 | 2022-07-01 18:00 | 117 | 2022-07-10 19:30
95 | Motijheel 132/33kV Grid Sub-Station | 132 | 137 | 2022-07-02 06:00 | 121 | 2022-07-23 10:00
96 | Munshiganj 132/33kV Grid Sub-Station | 132 | 140 | 2022-07-11 19:30 | 123 | 2022-07-04 15:00
97 | Mymensingh 132/33kV Grid Sub-Station | 132 | 135 | 2022-07-08 18:00 | 113 | 2022-07-15 20:00
98 | Naogaon 132/33kV Grid Sub-Station | 132 | 137 | 2022-07-31 19:30 | 113 | 2022-07-10 22:00
99 | Narail 132/33kV Grid Sub-Station | 132 | 140 | 2022-07-21 16:00 | 123 | 2022-07-07 21:00
100 | Narshingdi 132/33kV Grid Sub-Station | 132 | 141 | 2022-07-09 18:30 | 119 | 2022-07-06 11:00
101 | Natore 132/33kV Grid Sub-Station | 132 | 137 | 2022-07-07 18:00 | 120 | 2022-07-20 06:00
102 | Nawabganj 132/33kV Grid Sub-Station | 132 | 141 | 2022-07-11 19:30 | 122 | 2022-07-23 09:00
103 | Netrakona 132/33kV Grid Sub-Station | 132 | 134 | 2022-07-08 18:00 | 113 | 2022-07-08 04:00
104 | New Tongi 132/33kV Grid Sub-Station | 132 | 140 | 2022-07-09 18:00 | 121 | 2022-07-23 09:00
105 | Niamatpur 132/33kV Grid Sub-Station | 132 | 137 | 2022-07-31 19:30 | 113 | 2022-07-06 05:00
106 | Noapara 132/33kV Grid Sub-Station | 132 | 139 | 2022-07-03 19:30 | 122 | 2022-07-10 19:30
107 | Pabna 132/33kV Grid Sub-Station | 132 | 138 | 2022-07-10 08:00 | 127 | 2022-07-10 21:00
108 | Palashbari 132/33kV Grid Sub-Station | 132 | 135 | 2022-07-21 16:00 | 113 | 2022-07-14
109 | Panchagarh 132/33kV Grid Sub-Station | 132 | 142 | 2022-07-19 17:00 | 113 | 2022-07-01 02:00
110 | Patuakhali 132/33kV Grid Sub-Station | 132 | 142 | 2022-07-11 18:00 | 127 | 2022-07-14 22:00
111 | PHP 132/33kV Sub-Station | 132 | 137 | 2022-07-23 19:30 | 114 | 2022-07-17 11:00
112 | Postogola 132/33kV Grid Sub-Station | 132 | 142 | 2022-07-29 19:30 | 126 | 2022-07-27 09:00
113 | Purbachal 132/33kV Grid Sub-Station | 132 | 140 | 2022-07-11 05:00 | 119 | 2022-07-31 17:00
114 | Purbasadipur 132/33kV Grid Sub-Station | 132 | 138 | 2022-07-24 02:00 | 113 | 2022-07-08 23:00
115 | Rahim Steel 132/33kV Sub-Station | 132 | 138 | 2022-07-02 18:00 | 124 | 2022-07-23 11:00
116 | Rajbari 132/33kV Grid Sub-Station | 132 | 138 | 2022-07-10 08:00 | 123 | 2022-07-12 21:00
117 | Rajendrapur 132/33kV Grid Sub-Station | 132 | 139 | 2022-07-07 18:30 | 123 | 2022-07-15 05:00
118 | Rajshahi 132/33kV Grid Sub-Station | 132 | 137 | 2022-07-01 13:00 | 122 | 2022-07-14 13:00
119 | Ramganj 132/33kV Grid Sub-Station | 132 | 138 | 2022-07-21 20:00 | 113 | 2022-07-11 03:00
120 | Rangamati 132/33kV Grid Sub-Station | 132 | 140 | 2022-07-05 | 125 | 2022-07-16 11:00
121 | Rangpur 132/33kV Grid Sub-Station | 132 | 136 | 2022-07-19 17:00 | 114 | 2022-07-08 23:00
122 | Ruppur 132/11kV Grid Sub-Station | 132 | 139 | 2022-07-10 07:00 | 130 | 2022-07-08 22:00
123 | Saidpur 132/33kV Grid Sub-Station | 132 | 137 | 2022-07-04 18:00 | 113 | 2022-07-14 08:00
124 | Satkhira 132/33kV Grid Sub-Station | 132 | 137 | 2022-07-12 18:30 | 114 | 2022-07-10 19:30
125 | Satmasjid 132/33kV Grid Sub-Station | 132 | 139 | 2022-07-11 19:30 | 124 | 2022-07-03 10:00
126 | Savar 132/33kV Grid Sub-Station | 132 | 138 | 2022-07-11 19:30 | 116 | 2022-07-23 09:00
127 | Shahjadpur 132/33kV Grid Sub-Station | 132 | 143 | 2022-07-19 18:00 | 133 | 2022-07-11 22:00
128 | Shahjibazar 132/33kV Grid Sub-Station | 132 | 137 | 2022-07-10 08:00 | 126 | 2022-07-14 11:00
129 | Shahmirpur 132/33kV Grid Sub-Station | 132 | 141 | 2022-07-05 | 123 | 2022-07-16 11:00
130 | Shariatpur 132/33kV Grid Sub-Station | 132 | 139 | 2022-07-10 09:00 | 123 | 2022-07-12 21:00
131 | Sherpur 132/33kV Grid Sub-Station | 132 | 140 | 2022-07-27 16:00 | 113 | 2022-07-10 03:00
132 | Shikalbaha 132/33kV Sub-Station | 132 | 143 | 2022-07-18 21:00 | 125 | 2022-07-16 11:00
133 | Shitalakhya 132/33kV Grid Sub-Station | 132 | 143 | 2022-07-29 19:30 | 122 | 2022-07-23 09:00
134 | Shyampur 132/33kV Grid Sub-Station | 132 | 137 | 2022-07-10 09:00 | 123 | 2022-07-31 12:00
135 | Siddhirganj 132/33kV Grid Sub-Station | 132 | 138 | 2022-07-09 18:30 | 124 | 2022-07-23 11:00
136 | Sirajganj 132/33kV Grid Sub-Station | 132 | 138 | 2022-07-10 09:00 | 125 | 2022-07-10 21:00
137 | Sonargaon 132/33kV Grid Sub-Station | 132 | 139 | 2022-07-11 20:00 | 118 | 2022-07-19 21:00
138 | Sreemongol 132/33kV Grid Sub-Station | 132 | 138 | 2022-07-01 06:00 | 130 | 2022-07-22 15:00
139 | Srinagar 132/33kV Grid Sub-Station | 132 | 140 | 2022-07-09 18:30 | 123 | 2022-07-23 09:00
140 | SSM 132/33kV Grid Sub-Station | 132 | 145 | 2022-07-04 19:00 | 128 | 2022-07-16 10:00
141 | Sunamganj 132/33kV Grid Sub-Station | 132 | 134 | 2022-07-23 20:00 | 119 | 2022-07-10 19:30
142 | Sylhet 132/33kV Grid Sub-Station | 132 | 136 | 2022-07-06 02:00 | 126 | 2022-07-07 21:00
143 | Tangail 132/33kV Grid Sub-Station | 132 | 138 | 2022-07-01 17:00 | 120 | 2022-07-14 20:00
144 | Thakurgaon 132/33kV Grid Sub-Station | 132 | 140 | 2022-07-19 17:00 | 113 | 2022-07-02 02:00
145 | TK chemical 132kV Grid Sub-Station | 132 | 142 | 2022-07-18 21:00 | 126 | 2022-07-16 11:00
146 | Ullon 132/33kV Grid Sub-Station | 132 | 139 | 2022-07-29 19:30 | 122 | 2022-07-03 11:00
147 | Uttara 132/33kV Grid Sub-Station | 132 | 136 | 2022-07-08 06:00 | 118 | 2022-07-23 09:00
148 | UttaraNew 132/33kV Grid Sub-Station | 132 | 141 | 2022-07-10 07:00 | 121 | 2022-07-03 10:00
149 | Zigatola 132/33kV Grid Sub-Station | 132 | 141 | 2022-07-10 07:00 | 122 | 2022-07-23 10:00

## QF-LDC-36
Page: 1/2 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
Month: July 2022
Name of the | Auto transformer |  | Recorded maximum load
sub-station | Name | Capacity ( MVA ) | MW | Amps ( 230kV side ) | Date | Time | Remarks
| TR1 | 225 | 72 | 217
Hasnabad | TR2 | 225 | 72 | 217 | 30.07.2022 | 12:00
| TR3 | 225 | 72 | 217
| TR1 | 225 | 185 | 540
Tongi | TR2 | 225 | 185 | 540 | 18.07.2022 | 15:00
| TR3 | 225 | 185 | 540
Haripur | TR1 | 225 | 126 | 400
| TR2 | 225 | 126 | 400 | 06.07.2022 | 12:00
| TR3 | 225 | 126 | 400
| TR1 | 225 | 197 | 527
Rampura | TR2 | 225 | 197 | 527 | 18.07.2022 | 15:00
| TR3 | 225 | 197 | 527
Keraniganj | ATR1 | 300 | 118 | 351
| ATR2 | 300 | 118 | 351 | 27.07.2022 | 19:00
| ATR3 | 300 | 118 | 351
| TR1 | 225 | 142 | 404
Aminbazar | TR2 | 225 | 142 | 404 | 30.06.2022 | 12:00
| TR3 | 225 | 150 | 422
Agargaon | TR1 | 300 | 150 | 493
| TR2 | 300 | 150 | 493 | 17.07.2022 | 16:00
Maniknagar | TR1 | 300 | 147 | 450 | 03.07.2022 | 12:00
| TR2 | 300 | 147 | 450
Cumilla (N) | TR1 | 225 | 200 | 588 | 15.07.22 | 1:00
| TR2 | 225 | 196 | 572
Fenchuganj | AT2 | 300 | 239 | 677 | 10.07.22 | 19:30
| MT1 | 150 | 90 | 260
Hathazari | MT2 | 150 | 90 | 260
| MT3 | 150 | 90 | 260 | 18.07.22 | 19:00
| MT4 | 150 | 90 | 260
| TR1 | 225 | 96 | 253
Ishurdi | TR2 | 225 | 96 | 253 | 10.07.22 | 21:00
| TR3 | 225 | 96 | 253
Khulna(S) | TR1 | 225 | 108 | 281
| TR2 | 225 | 108 | 281 | 12.07.22 | 24:00
| TR3 | 300 | 137 | 362
Bogura | TR1 | 225 | 124 | 407
| TR2 | 225 | 124 | 407 | 18.07.22 | 1:00
| TR3 | 225 | 189 | 534
Baghabari | TR1 | 300 | 198 | 555 | 09.07.22 | 23:00
| TR2 | 225 | 148 | 415
Rajshahi | ATR-01 | 300 | 171 | 446
| ATR-02 | 300 | 171 | 446 | 15.07.22 | 8:00
Barapukuria | TR1 | 225 | 117 | 820 |  |  | Due to unavailability of 230 kV side meters
| TR2 | 225 | 166 | 800 | 16.07.22 | 19:30 | 132 kV current is being provided
| TR6 | 300 | 214 | 1031
Bheramara | Transformer-1 | 225 | 72 | 241
| Transformer-2 | 225 | 72 | 241 | 15.07.2022 | 19:30
Shyampur | ATR-01 | 300 | 118 | 333
| ATR-02 | 300 | 118 | 333 | 06.07.2022 | 12:00
Kaliakoir | TR1 | 300 | 125 | 370 | 03.07.2022 | 12:30
Sikalbaha | ATR-1 | 300 | 211 | 545
| ATR-2 | 300 | 211 | 545 | 29.07.2022 | 22:00
Jhenaidah | T1(230/132 kV) | 300 | 186 | 569 | 16.07.2022 | 20:00
| T2(230/132 kV) | 300 | 186 | 569
Page: 2/2 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 400/230 & 400/132 kV Transformer
Month:July 2022
Name of the | Transformer |  | Recorded maximum load |  |  |  | Remarks
sub-station | Name | Capacity ( MVA ) | MW | Amps (400 kV side) | Date | Time
Kaliakoir | TR1(400/230 kV) | 520 | 217.2 | 338 | 19.07.2022 | 13:00
| TR2(400/230 kV) | 520 | 218.9 | 338
| TR1(400/132 kV) | 325 | 306.8 | 513 | 01.07.2022 | 12:00
| TR2(400/132 kV) | 325 | 308.2 | 513
Bibiyana | ICT1(400/230 kV) | 520 | 197 | 297 | 18.07.2022 | 6:00
| ICT2(400/230kV) | 520 | 192 | 290
Bhulta | ATR1(400/230 kV) | 520 | 463 | 710 | 08.07.2022 | 16:00
| ATR2(400/230kV) | 520 | 463 | 710
Ashuganj(N) | GSUT1(400/230 kV) | 567 | 376 | 622 | 26.07.2022 | 9:47
Gopalganj | ATR1(400/138 kV) | 325 | 286 | 430 | 18.07.2022 | 23:00
| ATR2(400/138kV) | 325 | 286 | 430
Payra | GSUT1 | 270 | 626 | 901 | 03.07.2022 | 21:26
| GSUT2 | 270 | 578 | 847 | 19.07.2022 | 19:27
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.
423

## QF-LDC-37
Page: 1/2 |  |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [9 empty] | QF-LDC-37
Information Management Division, LDC, Dhaka.
Report on load shedding
Month:July 2022 | [6 empty] | (For Evening Peak)
| Peak Hour |  | Total load shed
Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur
2022-07-01 | 13119 | 13119 | 0 | - | - | - | - | - | - | - | - | - | - | -
2022-07-02 | 13107 | 13607 | 500 | - | - | - | - | - | - | - | - | - | - | -
2022-07-03 | 12115 | 13615 | 1500 | - | - | - | - | - | - | - | - | - | - | -
2022-07-04 | 12236 | 13636 | 1400 | - | - | - | - | - | - | - | - | - | - | -
2022-07-05 | 13228 | 13678 | 450 | - | - | - | - | - | - | - | - | - | - | -
2022-07-06 | 13614 | 13864 | 250 | - | - | - | - | - | - | - | - | - | - | -
2022-07-07 | 13619 | 13619 | 0 | - | - | - | - | - | - | - | - | - | - | -
2022-07-08 | 12785 | 12785 | 0 | - | - | - | - | - | - | - | - | - | - | -
2022-07-09 | 11760 | 11760 | 0 | - | - | - | - | - | - | - | - | - | - | -
2022-07-10 | 12102 | 12102 | 0 | - | - | - | - | - | - | - | - | - | - | -
2022-07-11 | 11800 | 11800 | 0 | - | - | - | - | - | - | - | - | - | - | -
2022-07-12 | 12181 | 12181 | 0 | - | - | - | - | - | - | - | - | - | - | -
2022-07-13 | 12068 | 12068 | 0 | - | - | - | - | - | - | - | - | - | - | -
2022-07-14 | 12300 | 12300 | 0 | - | - | - | - | - | - | - | - | - | - | -
2022-07-15 | 12626 | 12626 | 0 | - | - | - | - | - | - | - | - | - | - | -
2022-07-16 | 13538 | 13538 | 0 | - | - | - | - | - | - | - | - | - | - | -
2022-07-17 | 13765 | 13765 | 0 | - | - | - | - | - | - | - | - | - | - | -
2022-07-18 | 13221 | 14006 | 785 | - | - | - | - | - | - | - | - | - | - | -
2022-07-19 | 11739 | 14124 | 2385 | - | - | - | - | - | - | - | - | - | - | -
2022-07-20 | 12494 | 13664 | 1170 | - | - | - | - | - | - | - | - | - | - | -
2022-07-21 | 12239 | 13797 | 1558 | - | - | - | - | - | - | - | - | - | - | -
2022-07-22 | 12794 | 13206 | 412 | - | - | - | - | - | - | - | - | - | - | -
2022-07-23 | 12131 | 13914 | 1783 | - | - | - | - | - | - | - | - | - | - | -
2022-07-24 | 11737 | 12579 | 842 | - | - | - | - | - | - | - | - | - | - | -
2022-07-25 | 11689 | 13266 | 1577 | - | - | - | - | - | - | - | - | - | - | -
2022-07-26 | 12042 | 13420.9458 | 1378.9458 | - | - | - | - | - | - | - | - | - | - | -
2022-07-27 | 12572 | 13704 | 1132 | - | - | - | - | - | - | - | - | - | - | -
2022-07-28 | 12784 | 13720 | 936 | - | - | - | - | - | - | - | - | - | - | -
2022-07-29 | 12961 | 13089 | 128 | -
2022-07-30 | 12836 | 13817 | 981 | -
2022-07-31 | 12620 | 13707 | 1087 | - | - | - | - | - | - | - | - | - | - | -
| Max. L/S | - | - | -
Day Peak | Min. L/S | - | - | -
| No. of Days | - | - | -
| Max. L/S | 2385 | - | -
Full Day | Min. L/S | 0 | - | -
| No. of Days | 19
| Average L/S | 653.3853

## QF-LDC-38
Page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month:July 2022
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 13765 | 2022-07-17 | 21:00
2 | Maximum Day Peak Genaration | MW | 12258 | 2022-07-18 | 10:00
3 | Maximum Evening Peak Demand | MW | 15001 | 2022-07-19 | 21:00
4 | Minimum Generation | MW | 7802 | 2022-07-10 | 6:00
5 | Average of the daily evening peak Genaration | MW | 12574.9032
6 | Average of the daily day peak Genaration | MW | 10718.3548
7 | Maximum load shed | MW | 2385 | - | -
8 | Minimum load shed | MW | 0 | - | -
9 | Total nos. of load shed days | Day | 19
10 | Average load shed ( Avg. of the 31 days in the month) | MW/Day | 653.3853
11 | Total Generation | MkWh | 8501.7966
12 | Total Generation by BPDB | MkWh | 1773.1307 | % of total Gen. | 20.86%
13 | Total Generation by IPP | MkWh | 2908.5257 | '' | 34.21%
14 | A) Total Generation by Generation Companies | MkWh | 2625.661 | '' | 30.88%
| B) Total Generation by REB | MkWh | 130.5165 | " | 1.535%
| C) Total Generation by RENTAL | MkWh | 382.0653 | " | 4.494%
| D) Total Imported from India (BIPTC) | MkWh | 592.0356 | " | 6.964%
| E) Total Imported from Tripura, India (A.C) | MkWh | 89.8618 | " | 1.057%
15 | Fuel wise Generation.
| A) Gas | MkWh | 4256.9757 | % of total Gen. | 50.07%
| B) Oil | MkWh | 2642.3038 | '' | 31.08%
| C) Hydro | MkWh | 88.9738 | '' | 1.047%
| D) Solar | MkWh | 38.5148 | '' | 0.453%
| E) Coal | MkWh | 793.1312 | '' | 9.329%
| F) BIPTC (Import from India) | MkWh | 592.0356 | '' | 6.964%
| G) A.C (Import from Tripura, India) | MkWh | 89.8618 | '' | 1.057%
16 | Maximun of the daily total Generation . | MkWh | 300.468 | 2022-07-17
17 | Monthly Load factor | % | 91.9201
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 46383.7052
| A) Gas | M.Taka | 4869.3901
| B) Liquid fuel | M.Taka | 33312.4907
| C) Coal | M.Taka | 5774.5897
| D) BIPTC (Import from India) | M.Taka | 1782.0272
| E) Tripura(Import from India) | M.Taka | 645.2074
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 1964.0267 | 2022-07-11
| A) Gas | M.Taka | 194.4746 | 2022-07-09
| B) Liquid fuel | M.Taka | 1649.7827 | 2022-07-11
| C) Coal | M.Taka | 256.1833 | 2022-07-24
| D) BIPTC (Import from India) | M.Taka | 64.5891 | 2022-07-09
20 | Average fuel cost of per unit Generation
| A) Including Hydro & Solar | Taka/kWhR | 6.008
| B) Excluding Hydro & Solar | Taka/kWhR | 6.0988
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 88.83 | 31/07/2022 | 06:00
b) | Actual | FT (MSL) | 91.98 | 31/07/2022 | 06:00
22 | Peak Genaration of July 2021 | MW | 13525 | 2021-07-15 | 21:00
23 | Peak Demand of July 2021 | MW | 13525 | 2021-07-15 | 21:00
24 | Maximum peak Generation recorded upto 31/07/2022 | MW | 14782 | 16/04/2022 | 21:00
25 | Maximum peak Demand recorded upto 31/07/2022 | MW | 14782 | 16/04/2022 | 21:00
26 | Maximum load shed recorded upto 31/07/2022 | MW | 1459 | 04/05/2010 | 20:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## FGMO
Power Grid Company Of Bangladesh Ltd.
NLDC, Aftabnagar, Dhaka.
Monthly status of Free Governor Mode of Operation (FGMO) Power Plants [July-2022]
SL | Plant Name | Owner | Installed capacity | FGMO Status
|  |  | (MW) | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
1 | Bibiana-II 341 MW CCPP (Summit) | IPP | 341 | √ | √ | √ | √ | √ | √ | √ | √ | √ | [6 empty] | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
2 | Shahjibazar GTPP Unit 8 & 9 | BPDB | 70
3 | Sirajgonj 400 MW CCPP Unit-4 | IPP | 414 | √
4 | Sirajgonj 225MW CCPP Unit-3 | NWPGCL | 220
5 | Sirajgonj 225MW CCPP Unit-2 | NWPGCL | 220
6 | Meghnaghat CCPP(Summit) | IPP | 335
7 | Ashuganj 450 MW CCPP(North) | APSCL | 360 | √ | [13 empty] | √ | √ | √
8 | Ashuganj 225 MW CCPP | APSCL | 221 | √
9 | Bheramara 410 MW CCPP | NWPGCL | 410
10 | Haripur 412 MW CCPP | EGCB | 412
11 | Fenchugonj CCPP Phase-1 | BPDB | 97
12 | Chandpur 150 MW CCPP | BPDB | 163
13 | Siddhirganj 2x120 MW GTPP | EGCB | 210
14 | Shikalbaha 225 MW CCPP | BPDB | 225
15 | Shikalbaha Peaking GT | BPDB | 150
16 | Shahjibazar 330 MW CCPP | BPDB | 330
17 | Ashuganj 450 MW CCPP(South) | APSCL | 360 | √ | [13 empty] | √ | √ | √
18 | Fenchugonj CCPP Phase-2 | BPDB | 104
19 | Bhola 225 MW CCPP | BPDB | 194
20 | Ghorasal 365 MW CCPP Unit-7 | BPDB | 365
21 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | 210
22 | Siddhirganj 335 MW CCPP | EGCB | 335
23 | Bibiyana-III 400 MW CCPP | BPDB | 400
24 | Sylhet 225 MW CCPP | BPDB | 231
25 | RPCL 210 MW CCPP | IPP | 210
26 | Khulna 225 MW CCPP | NWPGCL | 230
27 | a) Baghabari 71 MW GTPP | BPDB | 71
| b) Baghabari 100 MW GTPP | BPDB | 100
28 | Karnaphuli Hydro PP Unit: 1 | BPDB | 40
| Karnaphuli Hydro PP Unit: 2 | BPDB | 40
| Karnaphuli Hydro PP Unit: 3 | BPDB | 50
| Karnaphuli Hydro PP Unit: 4 | BPDB | 50
| Karnaphuli Hydro PP Unit: 5 | BPDB | 50
29 | a) Ghorasal Repowered CCPP Unit-3 | BPDB | 416
| b) Ghorasal Repowered CCPP Unit-4 | BPDB | 410
30 | Bibiyana South 400 MW CCPP | BPDB | 383
31 | Barapukuria 275 MW TPP Unit-3 | BPDB | 274
32 | Shajibazar 100 MW PP | BPDB | 100
33 | Payra 1320 MW Unit-1 | BCPCL | 622
34 | Kushiara 163 MW CCPP (KP) | IPP | 163
35 | Haripur 360MW CCPP(HPL) | IPP | 360
36 | Meghnaghat 450 MW CCPP(MPL) | IPP | 450
due to gas shortage