## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2022-09-14 | Wednesday
|  | Date (day): | 2022-09-14 |  | Wednesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11880.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14186 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2022-09-13 | 2022-09-14 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 200 | 220 | 200 | 220
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint.
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 290 | 262 | 270 | 270 | 95 |  | Machine problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 80 | 76 | 50 | 76 |  | 32 | Engine problem
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 379 | 371 | 335 | 370 | 42 |  | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 193 | 212 | 170 | 212 | 148 |  | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 175 | 175 | 175 | 175 | 275 |  | Dirty fuel
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 8 | 55 | 8 | 55 | 45 |  | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 126 | 125 | 100 | 125 | 210 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 0 | 0 | 0 | 0 |  | 102 | Under maint
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 30 | 55 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 7 | 48 | 8 | 60 |  | 40 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 253 | 250 | 225 | 250 | 85 |  | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 8 | 50 | 8 | 65 |  | 37 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 35 | 17 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 105 | 16 | 105 | 44 |  | Fuel shortage
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 55 | 17 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 35 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 41 | 47 | 50 | 50 |  | 30 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 7 | 6 | 8 | 8 |  | 25 | Engine problem
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 8 | 49 | 25 | 50
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 145 | 253 | 260 | 260 |  | 40 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 150 | 225 |  | 75 | Engine problem
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 0 | 0 | 80 | 90 |  | 10 | Engine problem
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 80 | 90 |  | 10 | Engine problem
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 50 | 144 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 86 | 105 | 85 | 105
37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 0 | 75 | 17 | 55 | 49 |  | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 72 | 162 | 72 | 162
39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 1 | 0 | 30 | 0
40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 55 | 0 | 55
| Dhaka area Total |  |  |  |  | 6263 | 5847 | 2266 | 3100 | 2750 | 3556 | 1254 | 1091
41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 110 | 110 | 110 | 110 | 70 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 17 | 25 | 25 | 25
43 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 11 | 0 | 20 | 0
44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 6 | 32 | 25 | 32 |  | 18 | Engine problem
45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 148 | 149 | 146 | 149 |  | 81 | Low Water Level
46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | S/D due to HGPI
47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 17 | 80 | 70 | 105
49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 17 | 0 | 17 | 81 |  | Fuel shortage
50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 0 | 51 | 51 |  | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 33 | 66 | 33 | 66 |  | 34 | Engine problem
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 33 | 90 | 33 | 90 |  | 10 | Engine problem
53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 15 | 15 | 13 | 15 |  | 7 | Engine problem
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 11 | 18 | 10 | 18
54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 2 | 0 | 6 | 102 |  | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 2 | 0 | 5 | 0
56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 155 | 269 | 214 | 280 |  | 20 | Engine prolem
57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 17 | 36 | 36 | 36 |  | 18 | Engine prolem
58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 68 | 105 | 105 | 105
59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 38 | 64 | 38 | 90 |  | 10 | Engine problem
60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 107 | 107 | 107 | 107 |  | 9 | Engine problem
| Mirsharai 150 MW |  | Gas/HSD | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0
| Chattogram area Total |  |  |  |  | 2442 | 2382 | 788 | 1236 | 990 | 1302 | 484 | 582
61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 177 | 181 | 172 | 181 | 40 |  | Gas shortage
63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 360 | 300 | 300 | 300 | 60 |  | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 335 | 265 | 260 | 300 | 60 |  | Gas shortage
| Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+136*1 | 284 | 284 | 0 | 0 | 0 | 0 |  |  | On test.
65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 41 | 45 | 45 | 45
66 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 55 | 53 | 56 | 55 | 55
67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 80 | 135 | 135 | 135 |  | 15 | Engine problem
70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 35 |  | 17 | Engine problem
71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 83 | 80 | 80 | 80 |  | 83 | Machine problem
72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 60 | 17 | 60 | 140 |  | Fuel shortage
73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 16 | 19 | 19 | 19
74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 10 | 10 | 10
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 100 | 124 | 143 | 165
75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 14 | 24 | 33 | 33
76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 23 | 8 | 35 | 17 |  | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 12 | 21 | 21 | 21 |  | 4 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 150 | 190 |  | 10 | Engine problem
79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 114 | 17 | 114
80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 108 | 113 | 97 | 113
81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 17 |  | 37 | 33 kV feeder fault
82 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 35 | 108 | 35 | 115
| Cumilla Area Total |  |  |  |  | 3193 | 3169 | 1498 | 1754 | 1673 | 2082 | 638 | 166
83 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 44 | 74 | 70 | 80 | 122 |  | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 22 |  | Gas shortage
85 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0 |  |  | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 0 | 0 | 1.6 | 0
87 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 45 | 150 | 87 | 150 | 50 |  | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 75 | 99 | 100 | 100 |  | 15 | Engine problem
89 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 1 | 0 | 50 | 0
90 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 12 | 12 |  | 10 | Engine problem
| Mymensingh Area Total |  |  |  |  | 717 | 614 | 177 | 335 | 320.6 | 342 | 144 | 25
91 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 43 | 43 | 43 |  | 27 | Machine problem.
92 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 41 | 41 | 41 | 41 |  | 49 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 | 163 |  | Gas shortage
94 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 0 | 0 | 5 | 5 | 46 |  | Gas shortage
96 | Fenchuganj 44MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 0 | 0 | 5 | 5 | 45 |  | Gas shortage
97 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 11 |  | Gas shortage
98 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 28 | 30 | 30 | 30 |  | 33 | GT-8 Under maint.
99 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 20 | 81 | 81 | 81
100 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
101 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 220 | 219 | 220 | 220
102 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 19 | 18 | 18 | 18
103 | Sylhet 50MW PP (EPL) |  | Gas | NENP | 27*2 | 50 | 50 | 0 | 0 | 6 | 6 | 44 |  | Gas shortage
104 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 0 | 0 | 8 | 8 | 17 |  | Gas shortage
105 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 305 | 255 | 280 | 280 | 61 |  | FGMO
106 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 374 | 400 | 400 | 400
107 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
108 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 386 | 380 | 400 | 400
| Sylhet Area Total |  |  |  |  | 2522 | 2477 | 1446 | 1477 | 1547 | 1547 | 387 | 539
109 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 903 | 903 | 920 | 920 |  |  | .
110 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 0 | 0 | 0 | 0 | 115 |  | Fuel shortage
111 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 50
112 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 120 | 120 | 130 | 225
113 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 68 |  | 41 | Engine problem
114 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 230 | 300 | 230 | 300 | 110 |  | Gas shortage
115 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 0 | 0 | 0 | 40 |  | Fuel shortage
116 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 90 | 90 |  | 10 | Engine problem
117 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 2 | 53 | 35 | 70 | 35 |  | Fuel shortage
118 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 15 | 50 | 15 | 50 | 55 |  | Fuel shortage
119 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 6 | 0 | 100 | 0
| Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 2388 | 2384 | 1276 | 1426 | 1520 | 1773 | 371 | 51
120 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 5 | 16 | 16 | 48 |  |  | Line O/L
121 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 12 | 18 | 20 | 20
122 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 65 | 56 | 65 | 65 |  | 129 | Machine problem
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
123 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 650 | 710 | 1110 | 1110 |  |  | Line O/L
124 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 171 | 174 | 220 | 220
125 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 0 | 17 |  |  | Line O/L
| Barisal Area Total |  |  |  |  | 1958 | 1958 | 903 | 974 | 1431 | 1480 | 0 | 129
126 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
127 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 32 | 0 | 32 |  | 20 | Engine problem
128 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 0 |  | 71 | Engine problem
129 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
130 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 8 | 42 | 42 | 42 |  | 8 | Engine problem
131 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 9 | 8 | 0 | 50 |  | Fuel shortage
132 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 160 | 150 | 170 | 180 | 30 |  | Gas shortage
133 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 190 | 110 | 220 | 220
134 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 150 | 150 | 180 | 180 | 40 |  | Gas shortage
135 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 368 | 258 | 414 | 414
136 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 33 | 0 | 33 |  | 17 | Engine problem
137 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 18 | 22 | 22
138 | Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
139 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
140 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 35 | 8 | 40 | 12 |  | Fuel shortage
141 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 82 | 0 | 82 |  | 22 | Engine problem
142 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 60 | 164 |  | 36 | Engine problem
143 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 86 | 50 | 86 |  | 27 | Engine problem
144 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 50 | 55 | 90 |  | 23 | Engine problem
145 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 0 | 0 | 6 | 0
| Rajshahi Area Total |  |  |  |  | 2199 | 2129 | 903 | 1066 | 1246 | 1596 | 303 | 224
146 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 80 | 78 | 78 | 78
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
147 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 249 | 250 | 250 | 250 | 24
148 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
149 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
150 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 60 | 55 | 90 |  | 23 | Engine problem
151 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 4 | 0 | 8 | 0
152 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 34 | 34 | 0 | 90 |  | 25 | Fuel shortage
| Intraco Solar 30 MW |  | Solar | IPP | 0 | 0 | 0 | 17 | 0 | 12 | 0
| Rangpur Area Total |  |  |  |  | 800 | 720 | 384 | 422 | 403 | 508 | 64 | 133
| Total |  |  |  |  | 22482 | 21680 | 9641 | 11790 | 11880.6 | 14186 | 3645 | 2940
A. |  | 2022-09-13 | (Yesterday) |  |  |  |  | Tuesday
1 | Highest Generation : |  |  | 11790 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
2 | Minimum Generation : |  |  | 9163 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 11790 | MW
3 | Day peak Generation : |  |  | 9641 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 11493.57 | MW
4 | Evening peak Generation : |  |  | 11790 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 251.0882 | MKWHr | By Solar | 0.42398 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Gas : | 138.96 | MKWHr |  | By Oil: | 56.4667 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 27.3798 | MKWHr |  | By Hydro: | 3.5117 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 3645 | MW | Dhaka | 4352.1 | 4352.1 |  | 0 |  | 18:00 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 2940 | MW | Chittagong | 1311.3 | 1311.3 |  | 0 |  | 19:00 |  | 0
|  |  | Total = |  |  | 6585 | MW | Khulna | 1303 | 1303 |  | 0 |  | 19:30 |  | 0
7 | Total Gas Supplied : |  |  | 1046.46 | MMCFD |  |  | Rajshahi | 1094.5 | 1094.5 |  | 0 |  | 20:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 156654299.948 | ii) Oil : | Taka | 767778158.14 | Comilla | 1010 | 1010 |  | 0 |  | 21:00 |  | 0
|  | iii) Coal : |  | 217989482.29 | Total | Taka | 1142421940.378 | Mymensingh | 937 | 937 |  | 0 |  | 22:00 |  | 0
9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0 | MKWHr. | Sylhet | 483 | 483 |  | 0 |  | 23:00 |  | 0
| ii) During Peak Demand : |  |  | 1030 | MW (E to W) at | 19:00 | hrs | Barisal | 268.67 | 268.67 |  | 0 |  | 24:00 |  | 0
| iii) Maximum : |  |  | 1030 | MW at | 19:00 | hrs | Rangpur | 734 | 734 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 26.5° C |  |  | Total | 11493.57 | 11493.57 |  | 0
B. |  | 2022-09-14 | (Today) |  |  |  | Wednesday |  |  | Probable max. temperature in Dhaka |  |  | 31.9 ° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 12500 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 14186 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 9700 | MW
4 | Reserve(Generation end) |  |  |  | 1686 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 266.2088 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 8905 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.7847 | MKWHr. | ii) HVDC Flow at Peak Time |  | 903 | MW at | 19:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.5613 | MKWHr. | iii) Maximum HVDC Flow : |  | 904 | MW at | 19:30 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 96.21 |  | (b) Today: | 96.32 |  | (c) Rule Curve: |  | 101.99
.

## YesterdayGen
2022-09-13
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 220 | 0 | 250 | 92 | 0 | 342 | 152 |  | 0 | 175 | 118 | 7 | 0 | 55 | 230 | 0 | 0 | 8 | 8 | 40 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 25 | 25 | 33 | 8 | 49 | 0 | 79 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 24 | 17 | 33 | 5 | 26 | 12 | 30 | 0 | 0 | 0 | 375 | 310 | 209 | 55 | 83 | 45 | 56 | 0 | 51 | 0 | 35 | 0 | 19 | 6 | 33 | 21 | 114 | 136 | 0 | 0 | 0 | 43 | 41 | 0 | 0 | 0 | 0 | 28 | 60 | 0 | 220 | 19 | 0 | 10 | 280 | 8 | 0 | 0 | 250 | 19 | 0 | 97 | 0 | 149 | 0 | 33 | 17 | 138 | 401 | 108 | 102 | 62 | 0 | 212 | 36 | 105 | 17 | 110 | 38 | 400 | 17 | 0 | 17 | 107 | 0 | 17 | 0 | 34 | 0 | 0 | 0 | 0 |  | 898 | 0 | 260 | 0 | 0 | 130 | 0 | 0 | 5 | 0 | 0 | 62 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 8 | 0 | 22 | 0 | 8 | 81 | 0 | 250 | 0 | 0 | 197 | 0 | 0 | 190 | 0 | 0 | 175 | 0 | 414 | 17 | 0 | 94 | 50 | 56 | 0 | 0 | 0 | 920 | 224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 7132 | 4139 | 11271 | 4376 | 898 | 1759 | 19 | 2264 | 1251 | 149 | 320 | 311 | 114 | 0 | 61.7455 | 96.21
2:00 | 0 | 0 | 230 | 0 | 250 | 92 | 0 | 346 | 153 |  | 0 | 175 | 125 | 8 | 0 | 55 | 231 | 0 | 0 | 8 | 8 | 48 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 25 | 26 | 33 | 8 | 49 | 0 | 78 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 0 | 17 | 33 | 5 | 26 | 12 | 30 | 0 | 0 | 0 | 380 | 310 | 164 | 55 | 83 | 45 | 56 | 0 | 51 | 0 | 35 | 0 | 19 | 10 | 33 | 21 | 114 | 136 | 0 | 0 | 0 | 43 | 41 | 0 | 0 | 0 | 0 | 25 | 60 | 0 | 220 | 19 | 0 | 10 | 270 | 8 | 0 | 0 | 228 | 0 | 0 | 98 | 0 | 130 | 0 | 33 | 17 | 100 | 401 | 108 | 102 | 34 | 0 | 214 | 36 | 68 | 17 | 65 | 38 | 400 | 17 | 0 | 17 | 68 | 0 | 17 | 0 | 35 | 0 | 0 | 0 | 0 |  | 898 | 0 | 260 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 65 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 8 | 0 | 22 | 0 | 8 | 75 | 0 | 250 | 0 | 0 | 197 | 0 | 0 | 190 | 0 | 0 | 179 | 0 | 414 | 17 | 0 | 50 | 50 | 56 | 0 | 0 | 0 | 880 | 224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6848 | 4019 | 10867 | 4360 | 898 | 1759 | 0 | 1963 | 1205 | 148 | 320 | 290 | 114 | 0 | 67.275 | 96.21
3:00 | 0 | 0 | 224 | 0 | 250 | 92 | 0 | 348 | 153 |  | 0 | 175 | 123 | 7 | 0 | 55 | 231 | 0 | 0 | 8 | 8 | 50 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 25 | 26 | 33 | 8 | 49 | 0 | 78 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 0 | 17 | 33 | 6 | 26 | 12 | 30 | 0 | 0 | 0 | 310 | 275 | 176 | 8 | 83 | 45 | 56 | 0 | 51 | 0 | 35 | 0 | 19 | 10 | 33 | 21 | 110 | 137 | 0 | 0 | 0 | 43 | 41 | 0 | 0 | 0 | 0 | 25 | 20 | 0 | 220 | 18 | 0 | 10 | 280 | 0 | 0 | 0 | 195 | 0 | 0 | 98 | 0 | 80 | 0 | 33 | 17 | 100 | 401 | 108 | 102 | 34 | 0 | 214 | 36 | 68 | 17 | 65 | 38 | 400 | 17 | 0 | 17 | 34 | 0 | 17 | 0 | 35 | 0 | 0 | 0 | 0 |  | 898 | 0 | 260 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 65 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 8 | 0 | 22 | 0 | 8 | 79 | 0 | 250 | 0 | 0 | 196 | 0 | 0 | 190 | 0 | 0 | 181 | 0 | 415 | 17 | 0 | 50 | 15 | 56 | 0 | 0 | 0 | 860 | 224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6545 | 3969 | 10514 | 4256 | 898 | 1680 | 0 | 1811 | 1189 | 148 | 320 | 292 | 110 | 0 | 70.0397 | 96.21
4:00 | 0 | 0 | 220 | 0 | 250 | 92 | 0 | 348 | 153 |  | 0 | 175 | 123 | 8 | 0 | 55 | 234 | 0 | 0 | 8 | 8 | 50 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 25 | 26 | 33 | 8 | 49 | 0 | 77 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 0 | 17 | 33 | 5 | 26 | 12 | 30 | 0 | 0 | 0 | 310 | 260 | 182 | 8 | 83 | 45 | 56 | 0 | 51 | 0 | 35 | 0 | 19 | 10 | 33 | 21 | 108 | 154 | 0 | 0 | 0 | 43 | 41 | 0 | 0 | 0 | 0 | 25 | 20 | 0 | 220 | 17 | 0 | 10 | 260 | 0 | 0 | 0 | 195 | 0 | 0 | 97 | 0 | 80 | 0 | 33 | 17 | 100 | 330 | 108 | 102 | 34 | 0 | 214 | 36 | 68 | 17 | 65 | 38 | 400 | 17 | 0 | 17 | 34 | 0 | 17 | 0 | 35 | 0 | 0 | 0 | 0 |  | 898 | 0 | 265 | 0 | 0 | 126 | 0 | 0 | 0 | 0 | 0 | 65 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 8 | 0 | 22 | 0 | 8 | 79 | 0 | 250 | 0 | 0 | 196 | 0 | 0 | 190 | 0 | 0 | 183 | 0 | 414 | 17 | 0 | 35 | 15 | 55 | 0 | 0 | 0 | 830 | 181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6456 | 3881 | 10337 | 4198 | 898 | 1615 | 0 | 1794 | 1159 | 147 | 316 | 292 | 108 | 0 | 46.0787 | 96.21
5:00 | 0 | 0 | 230 | 0 | 250 | 92 | 0 | 348 | 153 |  | 0 | 175 | 125 | 7 | 0 | 55 | 241 | 0 | 0 | 8 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 25 | 26 | 33 | 8 | 49 | 0 | 76 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 0 | 13 | 33 | 6 | 26 | 12 | 30 | 0 | 0 | 0 | 310 | 260 | 190 | 8 | 83 | 45 | 56 | 0 | 51 | 0 | 35 | 0 | 19 | 10 | 33 | 21 | 100 | 153 | 0 | 0 | 0 | 43 | 41 | 0 | 0 | 0 | 0 | 25 | 20 | 0 | 220 | 18 | 0 | 10 | 265 | 0 | 0 | 0 | 95 | 0 | 0 | 98 | 0 | 80 | 0 | 33 | 17 | 40 | 369 | 108 | 102 | 34 | 0 | 214 | 36 | 68 | 7 | 65 | 38 | 400 | 17 | 0 | 17 | 34 | 0 | 17 | 0 | 35 | 0 | 0 | 0 | 0 |  | 899 | 0 | 270 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 64 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 8 | 0 | 22 | 0 | 8 | 79 | 0 | 250 | 0 | 0 | 160 | 0 | 0 | 190 | 0 | 0 | 150 | 0 | 416 | 17 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 830 | 184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6311 | 3726 | 10037 | 4197 | 899 | 1627 | 0 | 1535 | 1159 | 146 | 310 | 254 | 100 | 0 | 37.7846 | 96.21
6:00 | 0 | 0 | 200 | 0 | 250 | 92 | 0 | 350 | 153 |  | 0 | 175 | 125 | 8 | 0 | 30 | 240 | 0 | 0 | 8 | 8 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 35 | 22 | 25 | 27 | 33 | 8 | 24 | 0 | 76 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 0 | 0 | 33 | 5 | 26 | 12 | 22 | 0 | 0 | 0 | 310 | 260 | 171 | 8 | 83 | 45 | 56 | 0 | 51 | 0 | 35 | 0 | 19 | 10 | 33 | 21 | 96 | 142 | 0 | 0 | 0 | 43 | 41 | 0 | 0 | 0 | 0 | 30 | 20 | 0 | 220 | 18 | 0 | 10 | 270 | 0 | 0 | 0 | 45 | 0 | 0 | 97 | 0 | 73 | 0 | 33 | 17 | 40 | 370 | 108 | 70 | 34 | 0 | 214 | 36 | 68 | 0 | 65 | 38 | 340 | 0 | 0 | 17 | 34 | 0 | 17 | 0 | 35 | 0 | 0 | 0 | 0 |  | 899 | 0 | 270 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 55 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 8 | 0 | 22 | 0 | 8 | 80 | 0 | 250 | 0 | 0 | 160 | 0 | 0 | 190 | 0 | 0 | 150 | 0 | 356 | 17 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 750 | 169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5981 | 3560 | 9541 | 4076 | 899 | 1546 | 0 | 1336 | 1080 | 146 | 310 | 242 | 96 | 0 | 0 | 96.21
7:00 | 0 | 0 | 200 | 0 | 270 | 42 | 0 | 333 | 153 |  | 0 | 175 | 118 | 7 | 0 | 30 | 243 | 0 | 0 | 8 | 8 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 35 | 22 | 25 | 20 | 33 | 8 | 24 | 0 | 76 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 0 | 0 | 33 | 6 | 26 | 9 | 28 | 0 | 0 | 0 | 310 | 260 | 172 | 8 | 84 | 45 | 56 | 0 | 10 | 0 | 30 | 0 | 0 | 0 | 31 | 21 | 84 | 107 | 0 | 0 | 0 | 43 | 41 | 0 | 0 | 0 | 0 | 30 | 20 | 0 | 220 | 18 | 0 | 10 | 275 | 0 | 0 | 0 | 45 | 0 | 0 | 97 | 0 | 63 | 2 | 33 | 17 | 10 | 370 | 108 | 35 | 17 | 1 | 214 | 36 | 17 | 0 | 26 | 38 | 340 | 0 | 5 | 17 | 34 | 0 | 17 | 1 | 35 | 0 | 0 | 0 | 0 |  | 899 | 0 | 280 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 8 | 0 | 22 | 0 | 8 | 80 | 0 | 250 | 0 | 0 | 160 | 0 | 0 | 190 | 0 | 0 | 150 | 0 | 340 | 17 | 0 | 0 | 15 | 0 | 0 | 1 | 0 | 750 | 174 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 3 |  | 5636 | 3577 | 9213 | 4028 | 899 | 1443 | 0 | 1154 | 1080 | 146 | 310 | 237 | 84 | 22 | 0 | 96.21
8:00 | 0 | 0 | 200 | 0 | 300 | 42 | 0 | 323 | 153 |  | 0 | 175 | 118 | 8 | 0 | 30 | 240 | 0 | 0 | 8 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 35 | 22 | 25 | 25 | 25 | 8 | 24 | 0 | 76 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 0 | 0 | 33 | 6 | 26 | 9 | 16 | 0 | 0 | 0 | 310 | 260 | 172 | 8 | 85 | 45 | 56 | 0 | 10 | 0 | 35 | 0 | 0 | 0 | 22 | 18 | 88 | 66 | 0 | 0 | 1 | 43 | 41 | 0 | 0 | 0 | 0 | 30 | 20 | 0 | 220 | 18 | 0 | 10 | 290 | 0 | 0 | 0 | 62 | 0 | 0 | 97 | 0 | 68 | 6 | 33 | 17 | 10 | 402 | 108 | 35 | 17 | 2 | 214 | 36 | 17 | 0 | 26 | 38 | 340 | 0 | 14 | 17 | 34 | 0 | 17 | 1 | 34 | 0 | 0 | 0 | 0 |  | 898 | 0 | 230 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 8 | 0 | 22 | 0 | 8 | 78 | 0 | 250 | 0 | 0 | 160 | 0 | 0 | 190 | 0 | 0 | 150 | 0 | 343 | 17 | 0 | 0 | 15 | 0 | 0 | 2 | 0 | 710 | 170 | 0 | 0 | 1 | 9 | 0 | 0 | 0 | 0 | 9 |  | 5678 | 3485 | 9163 | 3972 | 898 | 1439 | 0 | 1176 | 1038 | 146 | 310 | 241 | 88 | 45 | 0 | 96.21
9:00 | 0 | 0 | 200 | 0 | 300 | 64 | 0 | 333 | 143 |  | 0 | 175 | 120 | 8 | 0 | 30 | 235 | 0 | 0 | 7 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 35 | 22 | 25 | 22 | 25 | 7 | 24 | 0 | 78 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 0 | 0 | 33 | 6 | 26 | 10 | 12 | 0 | 0 | 0 | 310 | 290 | 198 | 8 | 83 | 42 | 55 | 0 | 10 | 0 | 35 | 0 | 0 | 0 | 16 | 16 | 96 | 68 | 0 | 0 | 1 | 43 | 41 | 0 | 0 | 0 | 0 | 25 | 20 | 0 | 220 | 19 | 0 | 10 | 310 | 0 | 0 | 0 | 95 | 0 | 0 | 97 | 0 | 104 | 5 | 33 | 17 | 25 | 402 | 107 | 34 | 17 | 2 | 214 | 36 | 17 | 0 | 34 | 38 | 400 | 0 | 9 | 72 | 35 | 0 | 17 | 0 | 35 | 0 | 0 | 0 | 0 |  | 902 | 0 | 230 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 8 | 78 | 0 | 249 | 0 | 0 | 160 | 0 | 0 | 190 | 0 | 0 | 150 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 710 | 171 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 |  | 5959 | 3428 | 9387 | 4075 | 902 | 1470 | 0 | 1266 | 1037 | 148 | 310 | 241 | 96 | 32 | 0 | 96.21
10:00 | 0 | 0 | 185 | 0 | 300 | 75 | 0 | 337 | 178 |  | 0 | 175 | 118 | 7 | 0 | 30 | 240 | 0 | 0 | 7 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 35 | 0 | 25 | 22 | 25 | 7 | 24 | 0 | 76 | 70 | 110 | 0 | 21 | 0 | 0 | 0 | 0 |  | 12 | 0 | 0 | 33 | 6 | 6 | 12 | 13 | 0 | 0 | 0 | 310 | 265 | 177 | 8 | 82 | 42 | 56 | 0 | 35 | 0 | 0 | 0 | 9 | 10 | 16 | 12 | 102 | 68 | 0 | 0 | 0 | 43 | 41 | 0 | 0 | 0 | 0 | 25 | 20 | 0 | 220 | 19 | 0 | 10 | 270 | 0 | 0 | 0 | 110 | 0 | 0 | 97 | 0 | 101 | 10 | 33 | 17 | 40 | 402 | 107 | 78 | 17 | 2 | 213 | 22 | 57 | 0 | 85 | 38 | 380 | 0 | 38 | 72 | 97 | 0 | 17 | 1 | 35 | 0 | 0 | 0 | 0 |  | 902 | 0 | 230 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 5 | 80 | 0 | 249 | 0 | 0 | 160 | 0 | 0 | 190 | 0 | 0 | 150 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 620 | 155 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 5 |  | 6099 | 3280 | 9379 | 3994 | 902 | 1444 | 0 | 1442 | 949 | 146 | 310 | 206 | 102 | 74 | 0 | 96.21
11:00 | 0 | 0 | 200 | 0 | 300 | 80 | 0 | 375 | 195 |  | 0 | 175 | 125 | 8 | 0 | 30 | 255 | 0 | 0 | 7 | 8 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 35 | 0 | 25 | 22 | 25 | 7 | 8 | 0 | 78 | 70 | 110 | 0 | 17 | 0 | 0 | 0 | 0 |  | 12 | 0 | 0 | 33 | 6 | 6 | 15 | 9 | 0 | 0 | 0 | 295 | 280 | 185 | 8 | 84 | 42 | 54 | 0 | 51 | 0 | 0 | 0 | 16 | 10 | 15 | 12 | 100 | 68 | 0 | 0 | 0 | 43 | 41 | 0 | 0 | 0 | 0 | 28 | 20 | 0 | 220 | 19 | 0 | 10 | 270 | 0 | 0 | 0 | 145 | 0 | 0 | 65 | 0 | 56 | 5 | 33 | 0 | 75 | 351 | 75 | 86 | 17 | 3 | 155 | 17 | 68 | 0 | 98 | 38 | 397 | 0 | 0 | 72 | 107 | 0 | 17 | 2 | 35 | 0 | 0 | 0 | 0 |  | 902 | 0 | 230 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 5 | 80 | 0 | 249 | 0 | 0 | 160 | 0 | 0 | 190 | 0 | 0 | 150 | 0 | 306 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 620 | 170 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 13 |  | 6041 | 3308 | 9349 | 4050 | 902 | 1492 | 0 | 1346 | 949 | 148 | 310 | 190 | 100 | 52 | 0 | 96.22
12:00 | 0 | 0 | 200 | 0 | 290 | 80 | 0 | 379 | 193 |  | 0 | 175 | 126 | 8 | 0 | 30 | 253 | 0 | 0 | 7 | 8 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 35 | 22 | 25 | 16 | 33 | 7 | 8 | 0 | 78 | 70 | 110 | 0 | 17 | 0 | 0 | 0 | 0 |  | 12 | 0 | 0 | 33 | 0 | 6 | 15 | 11 | 0 | 0 | 0 | 360 | 335 | 177 | 8 | 83 | 41 | 53 | 0 | 51 | 0 | 0 | 0 | 16 | 8 | 14 | 12 | 100 | 44 | 0 | 0 | 0 | 43 | 41 | 0 | 0 | 0 | 0 | 28 | 20 | 0 | 220 | 19 | 0 | 10 | 305 | 0 | 0 | 0 | 145 | 0 | 0 | 45 | 0 | 50 | 11 | 33 | 0 | 80 | 374 | 75 | 86 | 17 | 2 | 155 | 17 | 68 | 0 | 108 | 38 | 386 | 0 | 1 | 72 | 107 | 0 | 17 | 1 | 35 | 0 | 0 | 0 | 0 |  | 903 | 0 | 230 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 12 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 22 | 0 | 5 | 80 | 0 | 249 | 0 | 0 | 160 | 0 | 0 | 190 | 0 | 0 | 150 | 0 | 368 | 2 | 0 | 0 | 15 | 0 | 0 | 4 | 0 | 650 | 171 | 0 | 0 | 0 | 6 | 34 | 0 | 0 | 0 | 17 |  | 6175 | 3466 | 9641 | 4161 | 903 | 1605 | 0 | 1393 | 979 | 148 | 310 | 190 | 100 | 42 | 0 | 96.22
13:00 | 0 | 0 | 207 | 0 | 270 | 75 | 0 | 374 | 188 |  | 0 | 175 | 125 | 8 | 0 | 38 | 248 | 0 | 0 | 7 | 8 | 32 | 0 | 0 | 0 | 0 | 17 | 17 | 35 | 22 | 25 | 16 | 33 | 7 | 17 | 0 | 79 | 70 | 110 | 0 | 12 | 0 | 0 | 0 | 0 |  | 12 | 0 | 0 | 33 | 0 | 10 | 15 | 15 | 0 | 0 | 0 | 310 | 265 | 166 | 8 | 83 | 44 | 54 | 0 | 51 | 0 | 0 | 0 | 16 | 8 | 14 | 12 | 100 | 45 | 0 | 0 | 0 | 43 | 41 | 0 | 0 | 0 | 0 | 30 | 20 | 0 | 220 | 19 | 0 | 10 | 300 | 0 | 0 | 0 | 180 | 0 | 0 | 53 | 0 | 61 | 9 | 33 | 7 | 98 | 376 | 97 | 86 | 52 | 0 | 212 | 17 | 97 | 14 | 107 | 38 | 370 | 0 | 4 | 72 | 107 | 0 | 17 | 2 | 35 | 0 | 0 | 0 | 0 |  | 902 | 0 | 250 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 60 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 22 | 0 | 5 | 81 | 0 | 250 | 0 | 0 | 160 | 0 | 0 | 190 | 0 | 0 | 150 | 0 | 372 | 17 | 0 | 0 | 15 | 0 | 0 | 3 | 0 | 670 | 194 | 0 | 0 | 0 | 9 | 34 | 0 | 0 | 0 | 3 |  | 6303 | 3548 | 9851 | 4014 | 902 | 1626 | 0 | 1687 | 1001 | 149 | 310 | 222 | 100 | 30 | 0 | 96.22
14:00 | 0 | 0 | 200 | 0 | 220 | 56 | 0 | 345 | 214 |  | 0 | 175 | 123 | 7 | 0 | 55 | 263 | 0 | 0 | 10 | 8 | 16 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 22 | 25 | 16 | 33 | 6 | 8 | 0 | 79 | 70 | 110 | 0 | 1 | 0 | 0 | 0 | 0 |  | 12 | 0 | 0 | 33 | 0 | 19 | 15 | 13 | 0 | 0 | 0 | 310 | 265 | 175 | 8 | 83 | 41 | 56 | 0 | 51 | 0 | 0 | 4 | 16 | 8 | 14 | 12 | 110 | 43 | 0 | 0 | 0 | 43 | 41 | 0 | 0 | 0 | 0 | 30 | 20 | 0 | 206 | 19 | 0 | 10 | 250 | 0 | 0 | 0 | 245 | 0 | 0 | 65 | 0 | 117 | 9 | 33 | 17 | 112 | 329 | 97 | 86 | 51 | 0 | 213 | 17 | 105 | 17 | 104 | 38 | 345 | 17 | 9 | 72 | 107 | 0 | 17 | 4 | 35 | 0 | 0 | 0 | 0 |  | 902 | 0 | 210 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 12 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 22 | 0 | 5 | 80 | 0 | 250 | 0 | 0 | 155 | 0 | 0 | 198 | 0 | 0 | 130 | 0 | 305 | 17 | 0 | 0 | 15 | 0 | 0 | 3 | 0 | 600 | 183 | 0 | 0 | 0 | 6 | 34 | 0 | 0 | 0 | 1 |  | 6335 | 3337 | 9672 | 3800 | 902 | 1498 | 0 | 1917 | 930 | 149 | 318 | 214 | 110 | 32 | 0 | 96.22
15:00 | 0 | 0 | 200 | 0 | 220 | 56 | 0 | 322 | 220 |  | 0 | 175 | 125 | 8 | 0 | 55 | 275 | 0 | 0 | 8 | 8 | 16 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 22 | 25 | 20 | 33 | 6 | 8 | 0 | 79 | 70 | 110 | 0 | 8 | 0 | 0 | 0 | 0 |  | 12 | 0 | 0 | 33 | 0 | 19 | 15 | 10 | 0 | 0 | 0 | 310 | 265 | 175 | 8 | 82 | 41 | 56 | 0 | 51 | 0 | 0 | 8 | 19 | 8 | 17 | 14 | 100 | 41 | 0 | 0 | 0 | 43 | 41 | 0 | 0 | 0 | 0 | 31 | 20 | 0 | 205 | 18 | 0 | 10 | 285 | 0 | 0 | 0 | 220 | 0 | 0 | 65 | 0 | 116 | 3 | 33 | 17 | 118 | 398 | 107 | 86 | 51 | 0 | 214 | 17 | 105 | 17 | 65 | 38 | 400 | 17 | 4 | 72 | 107 | 0 | 17 | 3 | 35 | 0 | 0 | 0 | 9 |  | 903 | 0 | 210 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 14 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 22 | 0 | 5 | 81 | 0 | 250 | 0 | 0 | 150 | 0 | 0 | 160 | 0 | 0 | 130 | 0 | 256 | 17 | 0 | 0 | 15 | 0 | 0 | 1 | 0 | 600 | 164 | 0 | 0 | 0 | 26 | 34 | 0 | 0 | 0 | 2 |  | 6445 | 3249 | 9694 | 3925 | 903 | 1472 | 0 | 1879 | 931 | 149 | 280 | 176 | 100 | 39 | 0 | 96.22
16:00 | 0 | 0 | 200 | 0 | 220 | 56 | 0 | 322 | 224 |  | 0 | 175 | 125 | 7 | 0 | 55 | 270 | 0 | 0 | 8 | 8 | 16 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 22 | 25 | 20 | 33 | 6 | 8 | 0 | 79 | 70 | 110 | 0 | 17 | 0 | 0 | 0 | 0 |  | 12 | 0 | 0 | 33 | 0 | 19 | 15 | 10 | 0 | 0 | 0 | 310 | 275 | 171 | 8 | 83 | 44 | 56 | 0 | 51 | 0 | 0 | 8 | 19 | 8 | 20 | 14 | 110 | 41 | 0 | 0 | 0 | 43 | 41 | 0 | 0 | 0 | 0 | 31 | 20 | 0 | 205 | 18 | 0 | 10 | 290 | 0 | 0 | 0 | 220 | 0 | 0 | 45 | 0 | 116 | 1 | 33 | 17 | 120 | 401 | 85 | 86 | 51 | 1 | 214 | 36 | 105 | 34 | 65 | 38 | 400 | 17 | 7 | 72 | 107 | 0 | 17 | 3 | 34 | 0 | 0 | 0 | 0 |  | 903 | 0 | 210 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 80 | 0 | 249 | 0 | 0 | 150 | 0 | 0 | 130 | 0 | 0 | 130 | 0 | 258 | 17 | 0 | 0 | 15 | 0 | 0 | 1 | 0 | 600 | 163 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 5 |  | 6471 | 3147 | 9618 | 3922 | 903 | 1480 | 0 | 1824 | 929 | 149 | 250 | 146 | 110 | 35 | 0 | 96.23
17:00 | 0 | 0 | 200 | 0 | 220 | 53 | 0 | 332 | 216 |  | 0 | 175 | 130 | 8 | 0 | 55 | 268 | 0 | 0 | 8 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 25 | 20 | 33 | 6 | 8 | 0 | 79 | 70 | 110 | 0 | 18 | 0 | 0 | 0 | 0 |  | 12 | 0 | 0 | 33 | 0 | 19 | 15 | 15 | 0 | 0 | 0 | 310 | 265 | 174 | 8 | 80 | 44 | 56 | 0 | 51 | 0 | 0 | 8 | 19 | 8 | 16 | 19 | 110 | 43 | 0 | 0 | 0 | 43 | 41 | 0 | 0 | 0 | 0 | 28 | 20 | 0 | 206 | 18 | 0 | 10 | 305 | 0 | 0 | 0 | 220 | 0 | 0 | 45 | 0 | 116 | 0 | 33 | 17 | 120 | 400 | 85 | 86 | 51 | 0 | 213 | 36 | 105 | 34 | 65 | 38 | 400 | 17 | 4 | 80 | 107 | 0 | 17 | 2 | 35 | 41 | 0 | 0 | 0 |  | 903 | 0 | 210 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 80 | 0 | 249 | 0 | 0 | 150 | 0 | 0 | 142 | 0 | 0 | 130 | 0 | 265 | 17 | 0 | 0 | 15 | 0 | 0 | 1 | 0 | 600 | 160 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 3 |  | 6510 | 3149 | 9659 | 3920 | 903 | 1496 | 0 | 1857 | 929 | 149 | 262 | 158 | 110 | 17 | 0 | 96.24
18:00 | 0 | 0 | 200 | 0 | 240 | 65 | 0 | 358 | 210 |  | 0 | 175 | 130 | 28 | 0 | 55 | 258 | 0 | 0 | 14 | 8 | 48 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 22 | 25 | 22 | 33 | 6 | 20 | 0 | 79 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 4 | 51 | 55 | 0 | 19 | 15 | 8 | 0 | 0 | 0 | 300 | 265 | 169 | 8 | 80 | 44 | 56 | 0 | 51 | 0 | 0 | 8 | 19 | 8 | 16 | 19 | 122 | 43 | 0 | 0 | 0 | 43 | 41 | 0 | 0 | 0 | 0 | 30 | 20 | 0 | 219 | 18 | 0 | 10 | 290 | 0 | 0 | 0 | 223 | 0 | 0 | 100 | 0 | 117 | 0 | 90 | 19 | 120 | 400 | 95 | 105 | 51 | 0 | 214 | 36 | 105 | 34 | 71 | 38 | 400 | 17 | 0 | 162 | 107 | 0 | 17 | 0 | 45 | 55 | 0 | 0 | 0 |  | 903 | 0 | 190 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 5 | 79 | 0 | 249 | 0 | 0 | 150 | 0 | 0 | 147 | 0 | 0 | 130 | 0 | 309 | 17 | 0 | 8 | 50 | 0 | 0 | 0 | 0 | 600 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6990 | 3279 | 10269 | 3943 | 903 | 1589 | 0 | 2265 | 928 | 149 | 267 | 250 | 122 | 0 | 0 | 96.25
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 220 | 0 | 262 | 76 | 0 | 371 | 212 |  | 0 | 175 | 125 | 55 | 0 | 55 | 250 | 0 | 0 | 48 | 50 | 105 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 22 | 33 | 6 | 49 | 0 | 79 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 17 | 51 | 66 | 2 | 32 | 15 | 18 | 0 | 0 | 0 | 300 | 265 | 181 | 8 | 80 | 45 | 56 | 0 | 51 | 0 | 0 | 23 | 19 | 10 | 24 | 21 | 124 | 74 | 0 | 0 | 0 | 43 | 41 | 0 | 0 | 0 | 0 | 30 | 81 | 0 | 219 | 18 | 0 | 10 | 255 | 0 | 0 | 0 | 253 | 0 | 0 | 150 | 0 | 144 | 0 | 90 | 60 | 135 | 400 | 99 | 105 | 80 | 0 | 269 | 36 | 105 | 114 | 113 | 64 | 380 | 75 | 0 | 162 | 107 | 0 | 17 | 0 | 108 | 55 | 0 | 0 | 0 |  | 903 | 0 | 300 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 56 | 18 | 16 | 0 | 0 | 0 | 32 | 0 | 82 | 0 | 42 | 9 | 35 | 33 | 18 | 0 | 11 | 78 | 0 | 250 | 0 | 0 | 150 | 0 | 0 | 110 | 0 | 0 | 150 | 0 | 258 | 53 | 0 | 86 | 50 | 60 | 0 | 0 | 50 | 710 | 174 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 |  | 7902 | 3888 | 11790 | 4153 | 903 | 1535 | 0 | 3329 | 1038 | 149 | 230 | 439 | 124 | 0 | 0 | 96.28
19:30 | 0 | 0 | 220 | 0 | 270 | 76 | 0 | 371 | 209 |  | 0 | 175 | 125 | 59 | 0 | 55 | 250 | 0 | 0 | 64 | 65 | 113 | 0 | 0 | 0 | 0 | 35 | 35 | 55 | 22 | 25 | 22 | 33 | 6 | 49 | 0 | 79 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 16 | 35 | 20 | 0 | 22 | 15 | 21 | 0 | 0 | 0 | 300 | 265 | 185 | 8 | 80 | 45 | 56 | 0 | 51 | 0 | 0 | 1 | 19 | 10 | 30 | 21 | 120 | 100 | 0 | 0 | 0 | 43 | 41 | 3 | 0 | 0 | 0 | 30 | 81 | 0 | 219 | 18 | 0 | 10 | 265 | 5 | 0 | 0 | 253 | 0 | 0 | 150 | 0 | 149 | 0 | 90 | 68 | 144 | 400 | 99 | 105 | 87 | 0 | 268 | 36 | 68 | 17 | 117 | 90 | 350 | 43 | 0 | 162 | 107 | 0 | 17 | 0 | 115 | 55 | 0 | 0 | 0 |  | 904 | 0 | 300 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 60 | 21 | 16 | 0 | 0 | 0 | 32 | 0 | 82 | 0 | 42 | 0 | 35 | 33 | 18 | 0 | 11 | 76 | 0 | 249 | 0 | 0 | 150 | 0 | 0 | 80 | 0 | 0 | 150 | 0 | 258 | 53 | 0 | 70 | 50 | 70 | 0 | 0 | 35 | 750 | 174 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 |  | 7755 | 3899 | 11654 | 4176 | 904 | 1551 | 0 | 3168 | 1075 | 149 | 200 | 391 | 120 | 0 | 0 | 0
20:00 | 0 | 0 | 220 | 0 | 270 | 78 | 0 | 368 | 185 |  | 0 | 175 | 125 | 58 | 0 | 55 | 243 | 0 | 0 | 64 | 65 | 113 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 22 | 25 | 22 | 33 | 6 | 49 | 0 | 79 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 16 | 17 | 20 | 0 | 19 | 15 | 23 | 0 | 0 | 0 | 300 | 265 | 183 | 8 | 80 | 45 | 56 | 0 | 51 | 0 | 0 | 0 | 19 | 10 | 30 | 21 | 128 | 105 | 0 | 0 | 0 | 43 | 41 | 5 | 0 | 0 | 0 | 50 | 81 | 0 | 219 | 18 | 6 | 10 | 270 | 8 | 0 | 0 | 260 | 0 | 0 | 150 | 0 | 149 | 0 | 90 | 17 | 142 | 400 | 99 | 105 | 71 | 0 | 268 | 36 | 34 | 17 | 116 | 90 | 400 | 0 | 0 | 162 | 107 | 0 | 17 | 0 | 115 | 55 | 0 | 0 | 0 |  | 903 | 0 | 345 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 61 | 22 | 16 | 0 | 0 | 0 | 0 | 0 | 82 | 0 | 42 | 0 | 35 | 0 | 18 | 0 | 11 | 78 | 0 | 249 | 0 | 0 | 150 | 0 | 0 | 80 | 0 | 0 | 150 | 0 | 422 | 56 | 0 | 70 | 50 | 70 | 0 | 0 | 0 | 750 | 223 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 0 | 0 |  | 7643 | 4075 | 11718 | 4288 | 903 | 1758 | 0 | 2987 | 1077 | 149 | 200 | 308 | 128 | 0 | 0 | 96.27
21:00 | 0 | 0 | 220 | 0 | 270 | 82 | 0 | 356 | 172 |  | 0 | 175 | 125 | 46 | 0 | 55 | 228 | 0 | 0 | 64 | 65 | 48 | 0 | 0 | 0 | 0 | 54 | 0 | 35 | 22 | 25 | 23 | 33 | 6 | 49 | 0 | 79 | 70 | 110 | 0 | 8 | 0 | 0 | 0 | 0 |  | 12 | 0 | 17 | 20 | 0 | 0 | 15 | 24 | 0 | 0 | 0 | 300 | 280 | 190 | 8 | 83 | 45 | 57 | 0 | 51 | 0 | 5 | 0 | 19 | 10 | 33 | 21 | 126 | 117 | 0 | 0 | 0 | 43 | 41 | 5 | 5 | 0 | 0 | 63 | 50 | 0 | 219 | 18 | 6 | 10 | 280 | 8 | 0 | 0 | 248 | 0 | 0 | 150 | 0 | 149 | 0 | 90 | 17 | 100 | 401 | 99 | 105 | 17 | 0 | 268 | 36 | 17 | 17 | 75 | 90 | 400 | 0 | 0 | 162 | 107 | 0 | 17 | 0 | 115 | 55 | 0 | 0 | 0 |  | 904 | 0 | 350 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 21 | 16 | 0 | 0 | 0 | 0 | 0 | 82 | 0 | 42 | 0 | 8 | 0 | 18 | 0 | 11 | 82 | 0 | 250 | 0 | 0 | 164 | 0 | 0 | 80 | 0 | 0 | 161 | 0 | 425 | 56 | 0 | 35 | 50 | 49 | 0 | 0 | 0 | 790 | 225 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 |  | 7336 | 4038 | 11374 | 4350 | 904 | 1739 | 0 | 2632 | 1122 | 149 | 200 | 232 | 126 | 0 | 0 | 96.28
22:00 | 0 | 0 | 220 | 0 | 270 | 82 | 0 | 336 | 171 |  | 0 | 175 | 115 | 17 | 0 | 55 | 225 | 0 | 0 | 65 | 65 | 50 | 0 | 0 | 0 | 0 | 54 | 0 | 35 | 22 | 25 | 23 | 33 | 6 | 49 | 0 | 79 | 70 | 110 | 0 | 8 | 0 | 0 | 0 | 0 |  | 12 | 0 | 17 | 20 | 0 | 0 | 15 | 27 | 0 | 0 | 0 | 300 | 265 | 195 | 8 | 83 | 45 | 57 | 0 | 51 | 0 | 0 | 0 | 19 | 10 | 33 | 21 | 126 | 131 | 0 | 0 | 0 | 43 | 41 | 5 | 5 | 0 | 0 | 64 | 50 | 0 | 219 | 18 | 6 | 10 | 270 | 8 | 0 | 0 | 218 | 0 | 0 | 153 | 0 | 149 | 0 | 90 | 17 | 100 | 401 | 99 | 105 | 17 | 0 | 285 | 36 | 17 | 17 | 75 | 90 | 400 | 0 | 0 | 162 | 107 | 0 | 17 | 0 | 115 | 55 | 0 | 0 | 0 |  | 904 | 0 | 340 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 56 | 21 | 16 | 0 | 0 | 0 | 0 | 0 | 83 | 0 | 42 | 0 | 8 | 0 | 22 | 0 | 11 | 81 | 0 | 250 | 0 | 0 | 204 | 0 | 0 | 42 | 0 | 0 | 192 | 0 | 400 | 56 | 0 | 35 | 50 | 49 | 0 | 0 | 0 | 810 | 226 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 |  | 7259 | 4052 | 11311 | 4384 | 904 | 1701 | 0 | 2594 | 1141 | 149 | 162 | 192 | 126 | 0 | 0 | 96.29
23:00 | 0 | 0 | 220 | 0 | 270 | 86 | 0 | 340 | 172 |  | 0 | 175 | 118 | 16 | 0 | 55 | 227 | 0 | 0 | 65 | 65 | 50 | 0 | 0 | 0 | 0 | 54 | 0 | 35 | 22 | 25 | 23 | 33 | 6 | 49 | 0 | 77 | 70 | 110 | 0 | 8 | 0 | 0 | 0 | 0 |  | 12 | 0 | 17 | 20 | 0 | 0 | 15 | 30 | 0 | 0 | 0 | 320 | 265 | 196 | 8 | 82 | 45 | 56 | 0 | 51 | 0 | 0 | 0 | 19 | 10 | 33 | 21 | 122 | 132 | 0 | 0 | 0 | 43 | 41 | 5 | 5 | 0 | 0 | 64 | 50 | 0 | 220 | 18 | 6 | 10 | 260 | 8 | 0 | 0 | 145 | 0 | 0 | 154 | 0 | 149 | 0 | 90 | 17 | 100 | 401 | 99 | 103 | 17 | 0 | 285 | 36 | 17 | 17 | 75 | 90 | 400 | 0 | 0 | 162 | 107 | 0 | 17 | 0 | 115 | 55 | 0 | 0 | 0 |  | 903 | 0 | 325 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 22 | 16 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 42 | 0 | 8 | 0 | 22 | 0 | 11 | 81 | 0 | 250 | 0 | 0 | 205 | 0 | 0 | 22 | 0 | 0 | 210 | 0 | 325 | 56 | 0 | 35 | 50 | 34 | 0 | 0 | 0 | 770 | 226 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 |  | 7206 | 3877 | 11083 | 4425 | 903 | 1627 | 0 | 2504 | 1101 | 147 | 142 | 134 | 122 | 0 | 0 | 96.3
24:00 | 0 | 0 | 220 | 0 | 270 | 86 | 0 | 347 | 171 |  | 0 | 175 | 118 | 9 | 0 | 55 | 232 | 0 | 0 | 18 | 8 | 50 | 0 | 0 | 0 | 0 | 17 | 0 | 35 | 22 | 25 | 23 | 33 | 6 | 32 | 0 | 77 | 70 | 110 | 0 | 12 | 0 | 0 | 0 | 0 |  | 12 | 0 | 17 | 33 | 0 | 0 | 15 | 25 | 0 | 0 | 0 | 290 | 265 | 184 | 8 | 83 | 45 | 54 | 0 | 51 | 0 | 0 | 0 | 19 | 10 | 33 | 21 | 114 | 132 | 0 | 0 | 0 | 43 | 41 | 5 | 5 | 0 | 0 | 61 | 50 | 0 | 220 | 18 | 6 | 10 | 300 | 8 | 0 | 0 | 145 | 0 | 0 | 106 | 0 | 149 | 0 | 33 | 17 | 100 | 401 | 99 | 103 | 17 | 0 | 211 | 36 | 29 | 17 | 94 | 71 | 400 | 0 | 0 | 30 | 107 | 0 | 17 | 0 | 57 | 0 | 0 | 0 | 0 |  | 903 | 0 | 315 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 21 | 16 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 42 | 0 | 8 | 0 | 22 | 0 | 11 | 80 | 0 | 250 | 0 | 0 | 205 | 0 | 0 | 53 | 0 | 0 | 203 | 0 | 422 | 17 | 0 | 56 | 15 | 34 | 0 | 0 | 0 | 830 | 222 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 |  | 6638 | 3967 | 10605 | 4376 | 903 | 1751 | 0 | 1891 | 1160 | 147 | 173 | 143 | 114 | 0 | 0 | 96.31
KWH | 0 | 0 | 5102000 | 0 | 6248927 | 1731272 | 0 | 8458240 | 4308000 |  | 0 | 4013400 | 2939316 | 373440 | 0 | 1157002 | 5867721 | 0 | 0 | 475200 | 471312 | 804960 | 0 | 0 | 0 | 0 | 660240 | 475332 | 910388 | 456372 | 600000 | 525600 | 784200 | 157900 | 780480 | 0 | 1815736 | 1696000 | 2600000 | 0 | 468529 | 0 | 0 | 0 | 0 |  | 298560 | 59568 | 266936 | 802440 | 68160 | 440160 | 314976 | 496320 | 0 | 0 | 0 | 7715600 | 6759000 | 4408000 | 317818 | 1978650 | 1035360 | 1332960 | 0 | 1107128 | 0 | 347464 | 79886 | 359712 | 200340 | 602100 | 448840 | 2561280 | 2137920 | 0 | 0 | 2850 | 1019000 | 965448 | 24000 | 26424 | 0 | 0 | 807264 | 950400 | 0 | 5133090 | 445000 | 25000 | 241380 | 6909500 | 57168 | 0 | 0 | 4315636 | 25527 | 16553 | 2371200 | 9521 | 2605536 | 55080 | 1119360 | 474240 | 2363563 | 9309000 | 2374800 | 2086800 | 959309 | 16080 | 5341855 | 788548 | 1696974 | 403560 | 1974840 | 1147200 | 9182300 | 246720 | 105410 | 1771200 | 2049927 | 0 | 443520 | 20062 | 1276800 | 382680 | 0 | 0 | 15054 |  | 21784727 | 0 | 6618528 | 0 | 0 | 3064320 | 0 | 0 | 7200 | 0 | 0 | 1469000 | 389200 | 171168 | 0 | 0 | 0 | 53488 | 0 | 358408 | 0 | 518166 | 15840 | 186240 | 53323 | 474240 | 0 | 151344 | 1906909 | 0 | 6075400 | 0 | 0 | 4472527 | 0 | 0 | 3922864 | 0 | 0 | 4246700 | 0 | 8394582 | 565920 | 0 | 695232 | 639792 | 530256 | 0 | 19646 | 80928 | 19397500 | 4626136 | 0 | 0 | 3720 | 139680 | 417600 | 0 | 0 | 0 | 61450 |  | 159576124 | 91512034 | 251088158 | 100652881 | 21784727 | 38307076 | 51601 | 47460699 | 27379809 | 3511736 | 6987184 | 1967187 | 2561280 | 423978 | 0
Fuel Cost | 0 | 0 | 7448920 | 0 | 6998798.24 | 2302591.76 | 0 | 8881152 | 4652640 |  | 0 | 4374606 | 3262640.76 | 4175059.2 | 0 | 15330276.5 | 6571847.52 | 0 | 0 | 6947424 | 6631359.84 | 13048401.6 | 0 | 0 | 0 | 0 | 8398252.8 | 6416982 | 12208303.08 | 342279 | 450000 | 0 | 0 | 0 | 13275964.8 | 0 | 490248.72 | 457920 | 4914000 | 0 | 7660449.15 | 0 | 0 | 0 | 0 |  | 3896208 | 993594.24 | 4543250.72 | 10840964.4 | 864268.8 | 5092651.2 | 400019.52 | 1652745.6 | 0 | 0 | 0 | 8564316 | 7367310 | 5113280 | 409985.22 | 2413953 | 1169956.8 | 1986110.4 | 0 | 1848903.76 | 0 | 6000703.28 | 1074466.7 | 492805.44 | 150255 | 1053675 | 336630 | 18389990.4 | 2330332.8 | 0 | 0 | 45429 | 1396030 | 1274391.36 | 41760 | 45713.52 | 0 | 0 | 1566092.16 | 2166912 | 0 | 5184420.9 | 956750 | 37250 | 477932.4 | 6909500 | 42876 | 0 | 0 | 58908431.4 | 535045.92 | 342150.51 | 31963776 | 196799.07 | 36086673.6 | 643885.2 | 11551795.2 | 6478118.4 | 31364481.01 | 8564280 | 28877568 | 30175128 | 12135258.85 | 0 | 62713377.7 | 8587287.72 | 18038833.62 | 5476309.2 | 25455687.6 | 13514016 | 8447716 | 3195024 | 1523174.5 | 22476528 | 23328169.26 | 0 | 5792371.2 | 239740.9 | 19113696 | 5039895.6 | 0 | 0 | 0 |  | 65354181 | 0 | 7412751.36 | 0 | 0 | 50561280 | 0 | 0 | 129672 | 0 | 0 | 1645280 | 755048 | 1865731.2 | 0 | 0 | 0 | 896993.76 | 0 | 5605501.12 | 0 | 8580828.96 | 267854.4 | 2538451.2 | 899559.01 | 981676.8 | 0 | 114567.408 | 11079141.29 | 0 | 32138866 | 0 | 0 | 5188131.32 | 0 | 0 | 68493205.44 | 0 | 0 | 4926172 | 0 | 8310636.18 | 7605964.8 | 0 | 8224594.56 | 9244994.4 | 6734251.2 | 0 | 217088.3 | 982465.92 | 174771475 | 4718658.72 | 0 | 0 | 42073.2 | 1638446.4 | 6401808 | 0 | 0 | 0 | 0 |  | 733136769.05 | 498327348.948 | 1231464117.998 | 111718988.828 | 65354181 | 44935311.12 | 1073995.5 | 615264147.07 | 217989482.29 | 948168.72 | 119054485.44 | 32385530.13 | 18389990.4 | 4349837.5 | 0
Yesterday Day Peak | 0 | 0 | 200 | 0 | 290 | 80 | 0 | 379 | 193 |  | 0 | 175 | 126 | 8 | 0 | 30 | 253 | 0 | 0 | 7 | 8 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 35 | 22 | 25 | 16 | 33 | 7 | 8 | 0 | 78 | 70 | 110 | 0 | 17 | 0 | 0 | 0 | 0 |  | 12 | 0 | 0 | 33 | 0 | 6 | 15 | 11 | 0 | 0 | 0 | 360 | 335 | 177 | 8 | 83 | 41 | 53 | 0 | 51 | 0 | 0 | 0 | 16 | 8 | 14 | 12 | 100 | 44 | 0 | 0 | 0 | 43 | 41 | 0 | 0 | 0 | 0 | 28 | 20 | 0 | 220 | 19 | 0 | 10 | 305 | 0 | 0 | 0 | 145 | 0 | 0 | 45 | 0 | 50 | 11 | 33 | 0 | 80 | 374 | 75 | 86 | 17 | 2 | 155 | 17 | 68 | 0 | 108 | 38 | 386 | 0 | 1 | 72 | 107 | 0 | 17 | 1 | 35 | 0 | 0 | 0 | 0 |  | 903 | 0 | 230 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 12 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 22 | 0 | 5 | 80 | 0 | 249 | 0 | 0 | 160 | 0 | 0 | 190 | 0 | 0 | 150 | 0 | 368 | 2 | 0 | 0 | 15 | 0 | 0 | 4 | 0 | 650 | 171 | 0 | 0 | 0 | 6 | 34 | 0 | 0 | 0 | 17 |  | 9641 | DayPeak
Yesterday Evening Peak | 0 | 0 | 220 | 0 | 262 | 76 | 0 | 371 | 212 | 0 | 0 | 175 | 125 | 55 | 0 | 55 | 250 | 0 | 0 | 48 | 50 | 105 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 22 | 33 | 6 | 49 | 0 | 79 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 12 | 17 | 51 | 66 | 2 | 32 | 15 | 18 | 0 | 0 | 0 | 300 | 265 | 181 | 8 | 80 | 45 | 56 | 0 | 51 | 0 | 0 | 23 | 19 | 10 | 24 | 21 | 124 | 74 | 0 | 0 | 0 | 43 | 41 | 0 | 0 | 0 | 0 | 30 | 81 | 0 | 219 | 18 | 0 | 10 | 255 | 0 | 0 | 0 | 253 | 0 | 0 | 150 | 0 | 144 | 0 | 90 | 60 | 135 | 400 | 99 | 105 | 80 | 0 | 269 | 36 | 105 | 114 | 113 | 64 | 380 | 75 | 0 | 162 | 107 | 0 | 17 | 0 | 108 | 55 | 0 | 0 | 0 |  | 903 | 0 | 300 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 56 | 18 | 16 | 0 | 0 | 0 | 32 | 0 | 82 | 0 | 42 | 9 | 35 | 33 | 18 | 0 | 11 | 78 | 0 | 250 | 0 | 0 | 150 | 0 | 0 | 110 | 0 | 0 | 150 | 0 | 258 | 53 | 0 | 86 | 50 | 60 | 0 | 0 | 50 | 710 | 174 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 |  | 11790 | EvPeak
Forecast for Evening | 0 | 0 | 220 | 0 | 270 | 76 | 0 | 370 | 212 | 0 | 0 | 175 | 125 | 55 | 0 | 55 | 250 | 0 | 0 | 60 | 65 | 105 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 25 | 33 | 8 | 50 | 0 | 79 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 12 | 17 | 51 | 66 | 6 | 32 | 15 | 18 | 0 | 0 | 0 | 300 | 300 | 181 | 8 | 80 | 45 | 55 | 0 | 51 | 0 | 35 | 35 | 19 | 10 | 33 | 21 | 165 | 80 | 0 | 0 | 0 | 43 | 41 | 5 | 5 | 0 | 0 | 30 | 81 | 0 | 220 | 18 | 6 | 10 | 280 | 8 | 0 | 190 | 260 | 225 | 90 | 150 | 90 | 149 | 0 | 90 | 60 | 135 | 400 | 100 | 105 | 105 | 0 | 280 | 36 | 105 | 114 | 113 | 90 | 400 | 55 | 0 | 162 | 107 | 0 | 17 |  | 115 | 55 |  |  |  |  | 920 | 0 | 300 | 0 | 0 | 225 | 0 | 0 | 50 | 68 | 0 | 65 | 20 | 48 | 0 | 0 | 0 | 32 | 0 | 82 | 0 | 42 | 0 | 40 | 33 | 22 | 0 | 11 | 78 | 0 | 250 | 0 | 0 | 180 | 0 | 0 | 220 | 0 | 90 | 180 | 0 | 414 | 70 | 164 | 86 | 50 | 90 | 0 | 0 | 90 | 1110 | 220 |  | 17 |  |  | 90
Forecast for Day | 0 | 0 | 200 | 0 | 270 | 50 | 0 | 335 | 170 | 0 | 0 | 175 | 100 | 8 | 0 | 55 | 225 | 0 | 0 | 8 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 17 | 35 | 22 | 25 | 25 | 33 | 8 | 25 | 0 | 76 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 33 | 0 | 25 | 13 | 10 | 0 | 0 | 0 | 300 | 260 | 172 | 8 | 80 | 45 | 55 | 0 | 51 | 0 | 0 | 8 | 19 | 10 | 33 | 21 | 143 | 70 | 0 | 0 | 1.6 | 43 | 41 | 5 | 5 | 0 | 0 | 30 | 81 | 0 | 220 | 18 | 6 | 10 | 280 | 8 | 0 | 150 | 260 | 150 | 80 | 87 | 80 | 149 | 20 | 33 | 17 | 135 | 400 | 100 | 85 | 70 | 5 | 214 | 36 | 105 | 17 | 97 | 38 | 400 | 17 | 50 | 72 | 107 | 0 | 17 | 30 | 35 | 0 |  |  |  |  | 920 | 0 | 230 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 65 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 8 | 8 | 0 | 22 | 0 | 11 | 78 | 0 | 250 | 0 | 0 | 170 | 0 | 0 | 220 | 0 | 90 | 180 | 0 | 414 | 35 | 60 | 50 | 15 | 55 | 0 | 8 | 55 | 1110 | 220 |  | 0 | 6 | 100 | 0 |  |  |  | 12
Generation at 08:00(Today) | 0 | 0 | 182 | 0 | 300 | 88 | 0 | 369 | 170 | 0 | 0 | 180 | 130 | 8 | 0 | 30 | 240 | 0 | 0 | 8 | 8 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 24 | 33 | 8 | 0 | 0 | 76 | 70 | 110 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 15 | 16 | 0 | 0 | 0 | 380 | 300 | 172 | 8 | 82 | 45 | 56 | 0 | 51 | 0 | 0 | 0 | 19 | 5 | 25 | 16 | 100 | 71 | 0 | 0 | 0 | 43 | 41 | 5 | 5 | 0 | 0 | 34 | 25 | 0 | 219 | 18 | 6 | 10 | 290 | 8 | 0 | 0 | 30 | 0 | 0 | 85 | 0 | 50 | 0 | 33 | 0 | 6 | 376 | 85 | 40 | 5 | 0 | 214 | 36 | 17 | 0 | 25 | 38 | 350 | 0 | 8 | 17 | 49 | 0 | 17 | 3 | 35 | 0 | 0 | 0 | 0 | 0 | 903 | 0 | 230 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 22 | 0 | 8 | 78 | 0 | 250 | 0 | 0 | 180 | 0 | 0 | 130 | 0 | 0 | 184 | 0 | 308 | 17 | 0 | 0 | 15 | 0 | 0 | 1 | 0 | 660 | 226 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 1 | 0 |  |  |  |  | 56466671 |  | 0
56466671
| Minimum Generation |  | 9163 | 8:00
| Highest Generation |  | 11790 | 19:00
| Day Peak Generation |  | 9641 | 12:00
| Evening Peak Generation |  | 11790 | 19:00
| HVDC Max Flow |  | 904 | 19:30
| HVDC EvPeak Flow |  | 903 | 19:00
| Load factor L.F |  | 88.74% | [161 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2022-09-14
Till now the maximum generation is : - |  |  | 14782 | 21:00 | Hrs on | 2022-04-16
The Summary of Yesterday's |  | 2022-09-13 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 9641 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 8905 | MW
Evening Peak Generation : |  | 11790 | MW Hour : | 19:00 | Available Max Generation : |  | 14186 | MW
E.P. Demand (at gen end) : |  | 11790 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 12500 | MW
Maximum Generation : |  | 11790 | MW Hour : | 19:00 | Reserve(Generation end) |  | 1686 | MW
Total Gen. (MKWH) : |  | 251.0882 | System Load Factor : | 88.74% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | 1030 | MW at | 19:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2022-09-14
Actual : | 96.32 | Ft.(MSL) , | Rule curve : | 101.99 | Ft.( MSL )
Gas Consumed : | Total = | 1046.46 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 156654299.948
: |  | Coal : | 217989482.29 | Oil : | 767778158.14 | Total : | 1142421940.378
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4546.7658 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1288.0197 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1700.079 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1508.3935 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1284.0532 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 1060.8198 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 474.1403 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 386.5074 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 837.5864 |  |  | 0 | 0%
Total | 0 |  | 13086.365 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-2
2) Ghorasal-3,
3) Ashuganj-5
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
7) Sikalbaha 225 MW
8) Shajibazar 330 MW
9) Shahjibazar GT8
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Shahjibazar 132/33 kV T-6 transformer was shut down at 09:35 for C/M.
b) Bogura 230/132 kV T-1 transformer tripped at 10:04 showing lockout relay and was switched on at 13:05.
c) Rangpur 132/33 kV bus-1 was under shut down from 08:36 to 18:15 for D/W.
d) Sonargaon 132/33 kV T-2 transformer was shut down at 10:09 due to red hot maintenance at 33 kV
bushing and was switched on at 11:43.
e) Agargaon-Bhasantek 132 kV Ckt-2 was under shut down from 12:51 to 14:28 for D/W.
f) Agargaon-Aminbazar 230 kV Ckt-1 was under shut down from 13:14 to 14:02 for C/M.
g) Sirajganj #2 CCPP ST tripped at 18:39 due to drum level high and was synchronized at 23:48.
h) Shahjibazar 132/33 kV t-2 transformer was under shut down from 12:57 to 13:25 for power supply
centrifuging machine.
i) Jashore 132/33 kV T-2 transformer was shut down at 10:48 for D/W. | [5 empty] | About 24 MW power interruption occurred under
Jashore S/S area from 10:48 to 10:54.
j) Chuadanga 132/33 kV T-1 & T-2 transformers were shut at 13:45 & 16:14 for D/W and were switched
on at 15:55 & 17:05 respectively.
k) Bottail 132/33 kV T-2 transformer was shut down at 15:39 due to red hot maintenance at 33 kV Y-phase | [5 empty] | About 30 MW power interruption occurred under
CT connector and was switched on at 17:05. | [5 empty] | Bottail S/S area from 15:39 to 17:05.
l) Dhamrai 132/33 kV T-1 transformer was under shut down from 17:22 to 19:28 for C/M. | [5 empty] | About 20 MW power interruption occurred under
Dhamrai S/S area from 17:22 to 19:28.
m) Shahjibazar GT-8 was shut down at 05:23(14/9/22) for maintenance work.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2022-09-13 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 220 | 5102000
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 262 | 6248927 | Machine problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 76 | 1731272 | Machine problem
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 371 | 8458240 | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 212 | 4308000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 175 | 4013400 | GT-2 S/D due to dirty gas
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 55 | 373440 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 125 | 2939316 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 0 | 0 | Under maint.
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 55 | 1157002
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 456372
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 48 | 475200 | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 250 | 5867721 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 50 | 471312 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 35 | 660240 | Fuel shortage
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 105 | 804960 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 475332
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 910388
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 47 | 1125600 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 784200
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 6 | 157900 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 49 | 780480 | #REF!
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 253 | 4315636 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 25527 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 0 | 16553 | Reserve
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 9521 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 144 | 2605536
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 2086800
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 75 | 246720 | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 1771200
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 20062
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 55 | 382680
| Dhaka area Total |  |  |  | 5847 | 3100 | 58781537
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 110 | 2600000 | Machine problem
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 25 | 468529
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 55080
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 32 | 440160 | Engine problem
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 149 | 3511736 | Low water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | HGPI
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 80 | 959309 | Low demand
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 17 | 59568 | Fuel shortage
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 266936 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 66 | 802440 | Engine problem
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 90 | 1119360 | Engine problem
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 15 | 314976 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 18 | 496320
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 2 | 68160 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 16080
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 269 | 5341855 | Fuel shortage
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 36 | 788548 | Engine problem
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 105 | 1696974 | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 64 | 1147200
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 107 | 2049927 | Engine problem
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Chattogram area Total |  |  |  | 2382 | 1236 | 22203158
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 181 | 4408000 | #REF!
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 300 | 7715600 | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 265 | 6759000 | FGMO
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+136*1 | 284 | 0 | 0 | On test.
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 45 | 1035360 | Engine problem
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 56 | 1332960
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 317818 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1107128
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 135 | 2363563 | Engine problem
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 347464 | Reserve
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 80 | 1978650 | Machine problem
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 60 | 474240 | Fuel shortage
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 359712
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 10 | 200340
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 124 | 2561280
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 24 | 602100 | Engine problem
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 23 | 79886 | Engine problem
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 21 | 448840 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 403560
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 113 | 1974840
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 443520 | 33 kV feeder problem.
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 108 | 1276800 | Engine problem
| Cumilla Area Total |  |  |  | 3169 | 1754 | 36190661
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 74 | 2137920 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 0 | Gas shortage
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 2850
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 150 | 2371200 | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 99 | 2374800 | Engine problem
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 105410
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 298560 | Engine problem
| Mymensingh Area Total |  |  |  | 614 | 335 | 7290740
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1019000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 41 | 965448 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Gas shortage
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 0 | 24000 | Gas shortage
| Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 0 | 26424 | Gas shortage
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 0 | 0 | Gas shortage
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 807264 | Gas shortage
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 950400
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 219 | 5133090
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 445000
| Sylhet 50MW PP (EPL) |  | NENP | 27*2 | 50 | 0 | 25000 | Gas shortage
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 0 | 57168 | Gas shortage
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 255 | 6909500 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 400 | 9309000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 241380
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 380 | 9182300
| Sylhet Area Total |  |  |  | 2477 | 1477 | 35094974
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 903 | 21784727
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 0 | 0 | Fuel shortage
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 7200 | Reserve
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 120 | 3064320 | Low demand
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 300 | 6618528 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 0 | 0 | Fuel shortage
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 53 | 565920 | Fuel shortage
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 50 | 639792 | Low demand
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 139680
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 0 | 0 | 0 | On test.
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 0 | 0 | 0 | 0 | On test.
| Khulna Area Total |  |  |  | 2384 | 1426 | 32820167
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 16 | 171168 | Line O/L
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 18 | 389200 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 56 | 1469000 | Gas shortage
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 710 | 19397500 | Line O/L
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 174 | 4626136 | Frequency Control
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Reserve
| Barisal Area Total |  |  |  | 1958 | 974 | 26053004
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 32 | 53488 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contract Expired
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 42 | 518166 | Engine problem
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 9 | 15840 | Low demand
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 150 | 4472527 | Frequency Control
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 110 | 3922864
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 150 | 4246700 | Frequency Control
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 258 | 8394582 | Frequency Control
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 33 | 53323 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 18 | 474240
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | .
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 151344
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 35 | 186240 | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 82 | 358408 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Reserve
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 86 | 695232 | Engine problem
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 50 | 80928 | Low demand
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 3720
| Rajshahi Area Total |  |  |  | 2129 | 1066 | 23627602
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 78 | 1906909
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 250 | 6075400
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 60 | 530256 | Low demand
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 19646
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 34 | 417600 | Low demand
| Intraco Solar 30 MW |  | IPP | 0 | 0 | 0 | 61450
| Rangpur Area Total |  |  |  | 720 | 422 | 9011261
| Total |  |  |  | 21680 | 11790 | 251073104
| Eastern Grid Total |  |  |  | 14489 | 7902 | 159561070
| Western Grid Total |  |  |  | 7191 | 3888 | 91512034
| National Grid Total |  |  |  | 21680 | 11790 | 251073104
*Data collected from respective power station over telephone.
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2022-09-13
(a) ENTIRE EASTERN GRID : |  | 8093.4 | MW | (b) ENTIRE WESTERN GRID : |  | 3400.17 | MW
i) Dhaka area |  | 4352.1 | MW | i) Khulna area |  | 1303 | MW
ii) Chittagong area |  | 1311.3 | MW | ii) Rajshahi area |  | 1094.5 | MW
iii) Comilla area |  | 1010 | MW | iii) Barisal area |  | 268.67 | MW
iv) Mymensingh area |  | 937 | MW | iv) Rangpur area |  | 734 | MW
v) Sylhet area |  | 483 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 11493.57 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
AKS | 0 | 00:00 | Chowmuhani | 158 | 21:00 | Kaptai | 5 | 18:30 | Nawabganj | 32.1 | 00:00 | Sholosohor | N/A | N/A
AKSML | 159 | 07:00 | Chuadanga | 88 | 19:00 | Kazla | 86 | 13:00 | Netrakona | 106 | 19:30 | Shyampur | 132 | 12:00
Aftabnagar | 28 | 13:00 | Coxsbazar | 104 | 19:30 | Keranigonj | 58 | 02:00 | New | 78 | 08:00 | Siddhirganj | 102 | 10:00
Agargaon | 74 | 10:00 | Cumilla(N) | 167 | 00:00 | Khagrachori | 28 | 18:30 | Niamatpur | 54 | 22:00 | Sirajganj | 88 | 19:30
Agrabad | 70 | 13:00 | Cumilla(S) | 130 | 18:30 | Khulna | 78 | 19:00 | Noapara | 38 | 19:00 | Sonargaon | 97 | 00:00
Amnura | 52 | 19:00 | Daudkandi | 114 | 19:00 | Khulshi | 174 | 18:30 | PHP | 3 | 13:00 | Sreemongol | 55 | 19:30
Ashuganj | 61 | 00:00 | Dhaka | 40 | 13:00 | Kishoreganj | 136 | 00:00 | Pabna | 91 | 18:30 | Srinagar | 33.82 | 00:00
BSRM | 161 | 12:00 | Dhamrai | 92 | 09:00 | Kodda | 295 | 19:00 | Palashbari | 104 | 00:00 | Sunamganj | 43 | 00:00
Bagerhat | 79 | 21:00 | Dhanmondi | 99 | 13:00 | Kulaura | 42 | 21:00 | Panchagarh | 55 | 20:00 | Sylhet | 136 | 0.041667
Bakulia | 111 | 18:30 | Dohazari | 82 | 19:00 | Kurigram | 53 | 19:00 | Patuakhali | 86 | 00:00 | TK | 25.5 | 18:30
Banani | 48 | 10:00 | Faridpur | 121 | 00:00 | Kushtia | 114 | 19:00 | Payra | 0.7 | 19:30 | Tangail | 176 | 00:00
Bangabhaban | 18 | 10:00 | Fatullah | 67 | 10:00 | Lalbag | 86 | 18:30 | Purbachal | 37 | 13:00 | Thakurgaon | 72 | 18:30
Barapukuria | 46 | 19:00 | Fenchuganj | 44 | 18:30 | Lalmonirhat | 40 | 18:30 | Purbasadipur | 14 | 00:00 | Tongi | 112 | 12:00
Barguna | 12 | 21:00 | Feni | 92 | 18:30 | Madanganj | 87 | 00:00 | Rahim | 98 | 19:00 | Ullon | 34 | 00:00
Barishal | 92 | 13:00 | GPH | 94 | 18:00 | Madaripur | 74 | 00:00 | Rajbari | 1.8 | 18:30 | Uttara | 74 | 13:00
Barishal-230 | 48 | 00:00 | Ghorashal | 70 | 00:00 | Madartek | 70 | 00:00 | Rajendrapur | 28 | 12:00 | UttaraNew | 36 | 00:00
Baroaulia | 58 | 00:00 | Goalpara | 24 | 12:00 | Madunaghat | 53 | 18:30 | Rajshahi | 54 | 19:00 | Zigatola | 55 | 13:00
Baroirhat | 46 | 20:00 | Gollamari | 40 | 01:00 | Magura | 48 | 19:00 | Rajshahi-230 | 96 | 00:00
Bashundhara | 138 | 13:00 | Gopalganj | 78.8 | 18:30 | Mahasthangarh | 70 | 00:00 | Ramganj | 127 | 00:00
BashundharaCement | 1 | 18:30 | Gulshan | 84 | 13:00 | Manikganj | 72 | 00:00 | Rampur | 26 | 00:00
Beanibazar | 58 | 00:00 | Halishahar | 77 | 12:00 | Maniknagar | 68 | 13:00 | Rangamati | 80 | 00:00
Benapole | 44 | 18:30 | HaripurSBU | 157 | 23:00 | Matarbari | 34 | 18:30 | Rangpur | 16 | 19:00
Bhaluka | 128 | 01:00 | Hasnabad | 81 | 00:00 | Matuail | 62 | 10:00 | Ruppur | 12 | 19:00
Bhandaria | 42 | 18:30 | Hathazari | 79 | 18:30 | Millgate | 52 | 09:00 | SSM | 126 | 19:30
Bhangura | 26 | 00:00 | Ishurdi | 63 | 19:00 | Mirpur | 106 | 19:00 | Saidpur | 3.8 | 16:00
Bheramara(GK) | 47 | 00:00 | Jaldhaka | 50 | 18:30 | Mirsorai | 3.27 | 19:30 | Satkhira | 18 | 10:00
Bhulta | 260 | 00:00 | Jamalpur | 131 | 02:00 | Mithapukur | 26 | 18:30 | Satmasjid | 88 | 19:00
Bog-Sherpur | 48 | 00:00 | Jashore | 112 | 19:00 | Modern | 0 | 00:00 | Savar | 92 | 19:00
Bogura | 130 | 00:00 | Jhenaidah | 101 | 18:30 | Mogbazar | 105 | 11:00 | Shahjadpur | 77 | 19:00
Borhanuddin | 29 | 22:00 | Joydebpur | 173 | 20:00 | Mongla | 22 | 10:00 | Shahjibazar | 170 | 11:00
Brahmanbaria | 140 | 01:00 | Joypurhat | 34 | 19:30 | Motijheel | 32 | 13:00 | Shahmirpur | 77 | 00:00
Cantonment | 122 | 19:00 | Juldah | 25 | 10:00 | Munshiganj | 81 | 00:00 | Shariatpur | 113 | 19:00
Chandpur | 54.5 | 22:00 | KSRM | 37.5 | 01:00 | Mymensingh | 202 | 01:00 | Sherpur | 46 | 00:00
Chandraghona | 30 | 19:00 | Kabirpur | 259 | 18:30 | Naogaon | 100 | 19:00 | Shikalbaha | 56 | 22:00
Chapai | 55 | 22:00 | Kachua | 56 | 18:30 | Narail | 34 | 18:30 | Shikalbaha-230 | 116 | 01:00
Charsaidpur | 42 | 05:00 | Kallyanpur | 82 | 18:30 | Narinda | 66 | 12:00 | Shitalakhya | 28 | 01:00
Chauddagram | 45 | 00:00 | Kalurghat | 7 | 10:00 | Narshingdi | 164 | 00:00 | Sholosohor | N/A | N/A
Chhatak | 26 | 00:00 | Kamrangirchar | 57 | 13:00 | Natore | 116 | 20:00 | Shyampur | 109 | 10:00
Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
(1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2022-09-13 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Bhulta | 385 | 18:30 | 364 | 12:00 | Kaliakoir | 386 | 19:00 | 283 | 20:00
| Bibiana | 400 | 22:00 | 390 | 00:00 | Payra | 421 | 08:00 | 415 | 00:00
| BIPTC | 404 | 04:00 | 398 | 18:30 | Rahanpur_I | 411 | 10:00 | 381 | 00:00
| Gopalganj_I | 423 | 15:00 | 409 | 01:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 222 | 19:00 | 209 | 12:00 | Hasnabad | 223 | 18:30 | 210 | 12:00
| AKSML | 228 | 00:00 | 208 | 12:00 | Hathazari | 233 | 18:00 | 219 | 12:00
| Aminbazar | 222 | 18:00 | 221 | 00:00 | Ishurdi | 233 | 10:00 | 227 | 00:00
| Ashuganj | 238 | 19:00 | 225 | 12:00 | Jhenaidah | 232 | 17:00 | 224 | 00:00
| Baghabari | 232 | 13:00 | 228 | 00:00 | Kaliakoir | 223 | 18:30 | 211 | 12:00
| Barapukuria | 222 | 13:00 | 216 | 21:00 | Keranigonj | 222 | 19:00 | 209 | 12:00
| Barishal | 247 | 06:00 | 240 | 00:00 | Khulna(S) | 239 | 17:00 | 231 | 00:00
| Bheramara | 230 | 18:30 | 223 | 00:00 | Maniknagar | 223 | 18:30 | 212 | 12:00
| Bhulta | 227 | 18:00 | 214 | 12:00 | Meghnaghat | 228 | 18:00 | 219 | 12:00
| Bibiana | 236 | 19:00 | 226 | 12:00 | Mirsorai | 228 | 19:00 | 213 | 12:00
| BIPTC | 233 | 10:00 | 225 | 00:00 | Rajshahi | 234 | 10:00 | 224 | 00:00
| Bogura | 227 | 19:00 | 221 | 01:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 250 | 06:00 | 243 | 22:00 | Rampura | 225 | 19:00 | 222 | 23:00
| BSRM | 229 | 19:30 | 214 | 12:00 | Shikalbaha | 230 | 18:30 | 219 | 12:00
| Cumilla(N) | 228 | 19:00 | 215 | 12:00 | Shyampur | 223 | 19:00 | 210 | 12:00
| Fenchuganj | 236 | 04:00 | 231 | 11:00 | Siddhirganj | 226 | 13:00 | 222 | 18:30
| Ghorashal | N/A | N/A | N/A | N/A | Sirajgonj | 258 | 22:00 | 229 | 09:00
| GPH | 230 | 19:00 | 215 | 12:00 | Tongi | 225 | 00:00 | 214 | 07:00
| Haripur | 222 | 18:30 | 214 | 12:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 137 | 18:00 | 128 | 12:00 | Lalbag | 137 | 19:00 | 125 | 03:00
| Agargaon | 137 | 04:00 | 129 | 12:00 | Lalmonirhat | 129 | 14:00 | 123 | 18:00
| Agrabad | 137 | 18:30 | 127 | 03:00 | Madanganj | 132 | 18:00 | 123 | 12:00
| AKS | 135 | 00:00 | 129 | 10:00 | Madaripur | 138 | 06:00 | 133 | 00:00
| Aminbazar | 137 | 18:00 | 131 | 09:00 | Madartek | 137 | 04:00 | 127 | 12:00
| Amnura | 137 | 19:30 | 126 | 00:00 | Madunaghat | 139 | 18:00 | 130 | 12:00
| Ashuganj | 136 | 18:00 | 133 | 12:00 | Magura | 140 | 10:00 | 133 | 00:00
| Bagerhat | 137 | 16:00 | 131 | 00:00 | Mahasthangarh | 134 | 10:00 | 129 | 00:00
| Bakulia | 139 | 19:00 | 129 | 12:00 | Manikganj | 134 | 05:00 | 125 | 12:00
| Banani | 134 | 06:00 | 124 | 12:00 | Maniknagar | 133 | 19:30 | 125 | 12:00
| Bangabhaban | 132 | 18:30 | 125 | 12:00 | Matarbari | 128 | 17:00 | 120 | 21:00
| Barapukuria | 136 | 13:00 | 131 | 00:00 | Matuail | 131 | 18:00 | 123 | 12:00
| Barguna | 138 | 06:00 | 127 | 21:00 | Millgate | 133 | 01:00 | 125 | 12:00
| Barishal | 140 | 06:00 | 126 | 11:00 | Mirpur | 136 | 18:00 | 126 | 12:00
| Barishal-230 | 140 | 06:00 | 135 | 00:00 | Mithapukur | 132 | 14:00 | 125 | 01:00
| Baroaulia | 137 | 19:00 | 130 | 12:00 | Modern | 134 | 00:00 | 130 | 11:00
| Baroirhat | 136 | 19:00 | 125 | 09:00 | Mogbazar | 136 | 00:00 | 130 | 09:00
| Bashundhara | 133 | 03:00 | 125 | 12:00 | Mongla | 136 | 08:00 | 131 | 00:00
| BashundharaCement | 132 | 18:00 | 123 | 12:00 | Motijheel | 132 | 18:30 | 125 | 12:00
| Beanibazar | 131 | 16:00 | 125 | 00:00 | Munshiganj | 133 | 18:30 | 123 | 12:00
| Benapole | 136 | 08:00 | 130 | 00:00 | Mymensingh | 135 | 09:00 | 113 | 19:30
| Bhaluka | 133 | 22:00 | 119 | 16:00 | Naogaon | 134 | 18:00 | 127 | 01:00
| Bhandaria | 142 | 11:00 | 134 | 00:00 | Narail | 138 | 10:00 | 130 | 01:00
| Bhangura | 138 | 18:30 | 134 | 00:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bheramara | 136 | 10:00 | 132 | 00:00 | Narshingdi | 129 | 14:00 | 120 | 12:00
| Bheramara(GK) | 137 | 06:00 | 134 | 00:00 | Natore | 135 | 18:30 | 130 | 00:00
| Bhulta | 124 | 18:00 | 114 | 11:00 | Nawabganj | 138 | 19:00 | 128 | 12:00
| Bog-Sherpur | 137 | 18:30 | 131 | 21:00 | Netrakona | 124 | 10:00 | 114 | 19:30
| Bogura | 137 | 18:30 | 130 | 02:00 | New | 134 | 19:00 | 125 | 12:00
| Bogura-230 | 138 | 19:00 | 133 | 01:00 | Niamatpur | 135 | 07:00 | 125 | 21:00
| Brahmanbaria | 132 | 18:00 | 128 | 12:00 | Noapara | 137 | 06:00 | 132 | 00:00
| Cantonment | 136 | 04:00 | 127 | 12:00 | Pabna | 135 | 08:00 | 131 | 00:00
| Chandpur | 137 | 18:30 | 126 | 02:00 | Palashbari | 131 | 13:00 | 126 | 00:00
| Chandraghona | 138 | 19:00 | 134 | 23:00 | Panchagarh | 131 | 14:00 | 117 | 18:00
| Chapai | 135 | 18:30 | 129 | 00:00 | Patuakhali | 136 | 09:00 | 127 | 21:00
| Charsaidpur | 133 | 18:30 | 124 | 12:00 | Payra | 138 | 06:00 | 133 | 21:00
| Chauddagram | 137 | 19:00 | 125 | 09:00 | PHP | 137 | 19:00 | 125 | 09:00
| Chhatak | 130 | 08:00 | 129 | 10:00 | Postogola | 141 | 19:00 | 131 | 12:00
| Chowmuhani | 134 | 18:30 | 125 | 02:00 | Purbachal | 134 | 03:00 | 125 | 13:00
| Chuadanga | 138 | 10:00 | 128 | 00:00 | Purbasadipur | 132 | 14:00 | 122 | 18:00
| Coxsbazar | 127 | 17:00 | 120 | 12:00 | Rahim | 132 | 18:30 | 124 | 12:00
| Cumilla(N) | 136 | 19:00 | 126 | 12:00 | Rajbari | 135 | 08:00 | 128 | 00:00
| Cumilla(S) | 135 | 05:00 | 126 | 12:00 | Rajendrapur | 134 | 14:00 | 125 | 13:00
| Daudkandi | 133 | 13:00 | 122 | 12:00 | Rajshahi | 135 | 18:30 | 129 | 00:00
| Dhaka | 138 | 19:00 | 128 | 12:00 | Rajshahi-230 | 135 | 19:00 | 128 | 00:00
| Dhamrai | 138 | 19:30 | 129 | 12:00 | Ramganj | 137 | 19:00 | 125 | 09:00
| Dhanmondi | 131.2 | 19:00 | 123.5 | 12:00 | Rampur | 136 | 19:00 | 129 | 12:00
| Dohazari | 136 | 18:00 | 127 | 12:00 | Rampura | 137 | 03:00 | 127 | 12:00
| Faridpur | 135 | 08:00 | 128 | 00:00 | Rangamati | 136 | 18:00 | 130 | 12:00
| Fatullah | 134 | 19:00 | 125 | 12:00 | Rangpur | 130 | 15:00 | 123 | 06:00
| Fenchuganj | 133 | 06:00 | 131 | 02:00 | Ruppur | 136 | 00:00 | 133 | 23:00
| Feni | 135 | 18:30 | 127 | 09:00 | Saidpur | 132 | 14:00 | 123 | 21:00
| Ghorashal | 137 | 22:00 | 132 | 12:00 | Satkhira | 136 | 06:00 | 131 | 20:00
| Goalpara | 138 | 06:00 | 135 | 00:00 | Satmasjid | 137 | 04:00 | 128 | 12:00
| Gollamari | 137 | 06:00 | 131 | 15:00 | Savar | 138 | 19:00 | 127 | 12:00
| Gopalganj | 137 | 06:00 | 133 | 03:00 | Shahjadpur | 139 | 05:00 | 136 | 01:00
| Gopalganj_I | 139 | 10:00 | 132 | 01:00 | Shahjibazar | 134 | 07:00 | 129 | 12:00
| Gulshan | 137 | 19:00 | 127 | 12:00 | Shahmirpur | 139 | 18:00 | 131 | 23:00
| Halishahar | 137 | 18:00 | 129 | 12:00 | Shariatpur | 138 | 10:00 | 131 | 00:00
| Haripur | 132 | 18:30 | 124 | 12:00 | Sherpur | 137 | 08:00 | 126 | 16:00
| HaripurSBU | 131 | 19:00 | 124 | 12:00 | Shikalbaha | 140 | 19:00 | 131 | 09:00
| Hasnabad | 141 | 19:30 | 134 | 10:00 | Shikalbaha-230 | 138 | 18:30 | 132 | 12:00
| Hathazari | 137 | 18:00 | 129 | 12:00 | Shitalakhya | 140 | 19:00 | 129 | 12:00
| Ishurdi | 136 | 10:00 | 133 | 21:00 | Sholosohor | N/A | N/A | N/A | N/A
| Jaldhaka | 132 | 14:00 | 123 | 19:00 | Shyampur | 134 | 22:00 | 132 | 00:00
| Jamalpur | 140 | 10:00 | 128 | 16:00 | Shyampur-230 | 133 | 19:00 | 126 | 12:00
| Jashore | 137 | 17:00 | 130 | 00:00 | Siddhirganj | 131 | 18:00 | 124 | 12:00
| Jhenaidah | 140 | 06:00 | 134 | 00:00 | Sirajganj | 136 | 18:00 | 132 | 9:00
| Jhenaidah-230 | 140 | 10:00 | 134 | 00:00 | Sonargaon | 132 | 05:00 | 123 | 12:00
| Joydebpur | 139 | 18:30 | 130 | 09:00 | Sreemongol | 134 | 08:00 | 131 | 12:00
| Joypurhat | 134 | 14:00 | 127 | 21:00 | Srinagar | 137 | 04:00 | 129 | 12:00
| Juldah | 139 | 18:00 | 131 | 12:00 | SSM | 140 | 07:00 | 132 | 11:00
| Kabirpur | 137 | 23:00 | 121 | 12:00 | Sunamganj | 129 | 10:00 | 123 | 00:00
| Kachua | 138 | 19:00 | 126 | 00:00 | Sylhet | N/A | N/A | N/A | N/A
| Kaliakoir | 137 | 05:00 | 131 | 12:00 | Tangail | 136 | 05:00 | 126 | 16:00
| Kallyanpur | 136 | 18:00 | 127 | 12:00 | Thakurgaon | 130 | 12:00 | 119 | 00:00
Page 7 of 7

## L-Curve
Date | 2022-09-13
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 1545 | 6638 | 3967 | 10605 |  |  |  | QF-LDC-11
0:30 | 1495 | 6885 | 4053 | 10938 | Date: | 2022-09-13
1:00 | 1445 | 7132 | 4139 | 11271
1:30 | 1445 | 6990 | 4079 | 11069
2:00 | 1445 | 6848 | 4019 | 10867
2:30 | 1445 | 6696.5 | 3994 | 10690.5 | [5 empty] | Gen. at Eve. Peak | 11790 | 11790 MW (19:00 )
3:00 | 1445 | 6545 | 3969 | 10514 | [6 empty] | 19:00
3:30 | 1495 | 6500.5 | 3925 | 10425.5 | [5 empty] | Gen. at Day Peak | 9641 | 9641 MW (12:00 )
4:00 | 1545 | 6456 | 3881 | 10337 | [6 empty] | 12:00
4:30 | 1545 | 6383.5 | 3803.5 | 10187 | [5 empty] | Highest Generation | 11790
5:00 | 1545 | 6311 | 3726 | 10037 | [6 empty] | 19:00
5:30 | 1545 | 6146 | 3643 | 9789
6:00 | 1545 | 5981 | 3560 | 9541
6:30 | 1540 | 5808.5 | 3568.5 | 9377
7:00 | 1535 | 5636 | 3577 | 9213
7:30 | 1535 | 5657 | 3531 | 9188
8:00 | 1535 | 5678 | 3485 | 9163
8:30 | 1535 | 5818.5 | 3456.5 | 9275
9:00 | 1535 | 5959 | 3428 | 9387
9:30 | 1532.5 | 6029 | 3354 | 9383
10:00 | 1530 | 6099 | 3280 | 9379
10:30 | 1530 | 6070 | 3294 | 9364
11:00 | 1530 | 6041 | 3308 | 9349
11:30 | 1530 | 6108 | 3387 | 9495
12:00 | 1530 | 6175 | 3466 | 9641
12:30 | 1530 | 6239 | 3507 | 9746
13:00 | 1530 | 6303 | 3548 | 9851
13:30 | 1527.5 | 6319 | 3442.5 | 9761.5
14:00 | 1525 | 6335 | 3337 | 9672
14:30 | 1515 | 6390 | 3293 | 9683
15:00 | 1505 | 6445 | 3249 | 9694
15:30 | 1512.5 | 6458 | 3198 | 9656
16:00 | 1520 | 6471 | 3147 | 9618
16:30 | 1490 | 6490.5 | 3148 | 9638.5
17:00 | 1460 | 6510 | 3149 | 9659
17:30 | 1307.5 | 6750 | 3214 | 9964
18:00 | 1155 | 6990 | 3279 | 10269
18:30 | 1092.5 | 7446 | 3583.5 | 11029.5
19:00 | 1030 | 7902 | 3888 | 11790
19:30 | 1030 | 7755 | 3899 | 11654
20:00 | 1065 | 7643 | 4075 | 11718 |  |  |  | Executive Engineer
20:30 | 1207.5 | 7489.5 | 4056.5 | 11546 |  |  |  | Network Operation Division
21:00 | 1350 | 7336 | 4038 | 11374
21:30 | 1320 | 7297.5 | 4045 | 11342.5
22:00 | 1290 | 7259 | 4052 | 11311 |  |  |  |  | Page 6 of 7
22:30 | 1407.5 | 7232.5 | 3964.5 | 11197
23:00 | 1525 | 7206 | 3877 | 11083
23:30 | 1535 | 6922 | 3922 | 10844
24:00 | 1545 | 6638 | 3967 | 10605
11790 MW (19:00 )
9641 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2022-09-13 |  | Energy |  | 251088158
[13 empty] | 2022-09-13 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 4376 | 903 | 1751 | 0 | 1891 | 1160 | 147 | 173 | 143 | 114 | 0 | 135
0:30 | 4376 | 900.5 | 1755 | 9.5 | 2077.5 | 1205.5 | 148 | 246.5 | 227 | 114 | 0 | 100 | Date: | 2022-09-13
1:00 | 4376 | 898 | 1759 | 19 | 2264 | 1251 | 149 | 320 | 311 | 114 | 0 | 62
1:30 | 4368 | 898 | 1759 | 9.5 | 2113.5 | 1228 | 148.5 | 320 | 300.5 | 114 | 0 | 64 | [8 empty] | Total Energy | 251.0882 | Total Energy Gen 251.088 MKWHr Energy Not Served 2.081 MKWHr Energy Requirement 253.170 MKWHr
2:00 | 4360 | 898 | 1759 | 0 | 1963 | 1205 | 148 | 320 | 290 | 114 | 0 | 67 | [8 empty] | Energy not Served | 2.0814
2:30 | 4308 | 898 | 1719.5 | 0 | 1887 | 1197 | 148 | 320 | 291 | 112 | 0 | 50 | [8 empty] | Energy Requirement | 253.1696
3:00 | 4256 | 898 | 1680 | 0 | 1811 | 1189 | 148 | 320 | 292 | 110 | 0 | 70
3:30 | 4227 | 898 | 1647.5 | 0 | 1802.5 | 1174 | 147.5 | 318 | 292 | 109 | 0 | 55 | [6 empty] | Shortage
4:00 | 4198 | 898 | 1615 | 0 | 1794 | 1159 | 147 | 316 | 292 | 108 | 0 | 46
4:30 | 4197.5 | 898.5 | 1621 | 0 | 1664.5 | 1159 | 146.5 | 313 | 273 | 104 | 0 | 30
5:00 | 4197 | 899 | 1627 | 0 | 1535 | 1159 | 146 | 310 | 254 | 100 | 0 | 38
5:30 | 4136.5 | 899 | 1586.5 | 0 | 1435.5 | 1119.5 | 146 | 310 | 248 | 98 | 0
6:00 | 4076 | 899 | 1546 | 0 | 1336 | 1080 | 146 | 310 | 242 | 96 | 0
6:30 | 4052 | 899 | 1494.5 | 0 | 1245 | 1080 | 146 | 310 | 239.5 | 90 | 11 | [5 empty] | Coal
7:00 | 4028 | 899 | 1443 | 0 | 1154 | 1080 | 146 | 310 | 237 | 84 | 22
7:30 | 4000 | 898.5 | 1441 | 0 | 1165 | 1059 | 146 | 310 | 239 | 86 | 33.5 |  |  |  |  | Oil |  |  |  | ,
8:00 | 3972 | 898 | 1439 | 0 | 1176 | 1038 | 146 | 310 | 241 | 88 | 45
8:30 | 4023.5 | 900 | 1454.5 | 0 | 1221 | 1037.5 | 147 | 310 | 241 | 92 | 38.5
9:00 | 4075 | 902 | 1470 | 0 | 1266 | 1037 | 148 | 310 | 241 | 96 | 32
9:30 | 4034.5 | 902 | 1457 | 0 | 1354 | 993 | 147 | 310 | 223.5 | 99 | 53
10:00 | 3994 | 902 | 1444 | 0 | 1442 | 949 | 146 | 310 | 206 | 102 | 74
10:30 | 4022 | 902 | 1468 | 0 | 1394 | 949 | 147 | 310 | 198 | 101 | 63
11:00 | 4050 | 902 | 1492 | 0 | 1346 | 949 | 148 | 310 | 190 | 100 | 52
11:30 | 4105.5 | 902.5 | 1548.5 | 0 | 1369.5 | 964 | 148 | 310 | 190 | 100 | 47
12:00 | 4161 | 903 | 1605 | 0 | 1393 | 979 | 148 | 310 | 190 | 100 | 42
12:30 | 4087.5 | 902.5 | 1615.5 | 0 | 1540 | 990 | 148.5 | 310 | 206 | 100 | 36
13:00 | 4014 | 902 | 1626 | 0 | 1687 | 1001 | 149 | 310 | 222 | 100 | 30
13:30 | 4014 | 902 | 1626 | 0 | 1687 | 1001 | 149 | 310 | 222 | 100 | 30
14:00 | 4014 | 902 | 1626 | 0 | 1687 | 1001 | 149 | 310 | 222 | 100 | 30
14:30 | 3969.5 | 902.5 | 1549 | 0 | 1783 | 966 | 149 | 295 | 199 | 100 | 34.5
15:00 | 3925 | 903 | 1472 | 0 | 1879 | 931 | 149 | 280 | 176 | 100 | 39
15:30 | 3923.5 | 903 | 1476 | 0 | 1851.5 | 930 | 149 | 265 | 161 | 105 | 37
16:00 | 3922 | 903 | 1480 | 0 | 1824 | 929 | 149 | 250 | 146 | 110 | 35
16:30 | 3920 | 903 | 1488 | 0 | 1840.5 | 929 | 149 | 256 | 152 | 110 | 26
17:00 | 3920 | 903 | 1496 | 0 | 1857 | 929 | 149 | 262 | 158 | 110 | 17
17:30 | 3931.5 | 903 | 1542.5 | 0 | 2061 | 928.5 | 149 | 264.5 | 204 | 116 | 8.5
18:00 | 3943 | 903 | 1589 | 0 | 2265 | 928 | 149 | 267 | 250 | 122 | 0
18:30 | 4048 | 903 | 1562 | 0 | 2797 | 983 | 149 | 248.5 | 344.5 | 123 | 0
19:00 | 4153 | 903 | 1535 | 0 | 3329 | 1038 | 149 | 230 | 439 | 124 | 0
19:30 | 4176 | 904 | 1551 | 0 | 3168 | 1075 | 149 | 200 | 391 | 120 | 0
20:00 | 4288 | 903 | 1758 | 0 | 2987 | 1077 | 149 | 200 | 308 | 128 | 0
20:30 | 4319 | 903.5 | 1748.5 | 0 | 2809.5 | 1099.5 | 149 | 200 | 270 | 127 | 0
21:00 | 4350 | 904 | 1739 | 0 | 2632 | 1122 | 149 | 200 | 232 | 126 | 0
21:30 | 4367 | 904 | 1720 | 0 | 2613 | 1131.5 | 149 | 181 | 212 | 126 | 0
22:00 | 4384 | 904 | 1701 | 0 | 2594 | 1141 | 149 | 162 | 192 | 126 | 0
22:30 | 4404.5 | 903.5 | 1664 | 0 | 2549 | 1121 | 148 | 152 | 163 | 124 | 0
23:00 | 4425 | 903 | 1627 | 0 | 2504 | 1101 | 147 | 142 | 134 | 122 | 0
23:30 | 4400.5 | 903 | 1689 | 0 | 2197.5 | 1130.5 | 147 | 157.5 | 138.5 | 118 | 0 |  | Max Temp. in Dhaka |  | 24.7° C | 26.5° C
24:00 | 4376 | 903 | 1751 | 0 | 1891 | 1160 | 147 | 173 | 143 | 114 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 251.088 MKWHr Energy Not Served 2.081 MKWHr Energy Requirement 253.170 MKWHr
Note on W13: Author:

## Generation
g | 2022-09-13
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 79 | 78 | 78 | 77 | 76 | 76 | 76 | 76 | 78 | 76 | 78 | 78 | 79 | 79 | 79 | 79 | 79 | 79 |  | 79 | 79 | 79 | 79 | 79 | 77 | 77 | 1815736
2 | Karnaphuli Hydro PP Unit-4 & 5 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1696000
3 | Chattogram TPP-1 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2600000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 21 | 17 | 17 | 12 | 1 | 8 | 17 | 18 | 25 |  | 25 | 25 | 25 | 8 | 8 | 8 | 12 | 468529
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 2 | 6 | 5 | 10 | 5 | 11 | 9 | 9 | 3 | 1 | 0 | [9 empty] | 55080
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 17 | 17 | 17 | 17 | 13 | 0 | [10 empty] | 0 | 51 |  | 51 | 35 | 17 | 17 | 17 | 17 | 17 | 266936
12 | Hathazari 100 MW peaking PP | 24 | 0 | [14 empty] | 0 | 4 |  | 17 | 16 | 16 | 0 |  |  |  | 59568
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 62 | 34 | 34 | 34 | 34 | 34 | 17 | 17 | 17 | 17 | 17 | 17 | 52 | 51 | 51 | 51 | 51 | 51 |  | 80 | 87 | 71 | 17 | 17 | 17 | 17 | 959309
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP | 35 | 35 | 35 | 35 | 35 | 35 | 30 | 35 | 35 | [13 empty] | 5 |  |  | 0 | 347464
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 230 | 231 | 231 | 234 | 241 | 240 | 243 | 240 | 235 | 240 | 255 | 253 | 248 | 263 | 275 | 270 | 268 | 258 |  | 250 | 250 | 243 | 228 | 225 | 227 | 232 | 5867721
18 | Kodda 300 MW PP Unit-2 (Summit) | 250 | 228 | 195 | 195 | 95 | 45 | 45 | 62 | 95 | 110 | 145 | 145 | 180 | 245 | 220 | 220 | 220 | 223 |  | 253 | 253 | 260 | 248 | 218 | 145 | 145 | 4315636
19 | Ashuganj 195MW PP (APSCL-United) | 55 | 55 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 317818
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4 | 220 | 230 | 224 | 220 | 230 | 200 | 200 | 200 | 200 | 185 | 200 | 200 | 207 | 200 | 200 | 200 | 200 | 200 |  | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 5102000
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 250 | 250 | 250 | 250 | 250 | 250 | 270 | 300 | 300 | 300 | 300 | 290 | 270 | 220 | 220 | 220 | 220 | 240 |  | 262 | 270 | 270 | 270 | 270 | 270 | 270 | 6248927
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 42 | 42 | 42 | 41 | 44 | 41 | 41 | 44 | 44 | 44 |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 1035360
33 | Ashuganj 225 MW CCPP | 209 | 164 | 176 | 182 | 190 | 171 | 172 | 172 | 198 | 177 | 185 | 177 | 166 | 175 | 175 | 171 | 174 | 169 |  | 181 | 185 | 183 | 190 | 195 | 196 | 184 | 4408000
34 | Ashuganj 450 MW CCPP(South) | 310 | 310 | 275 | 260 | 260 | 260 | 260 | 260 | 290 | 265 | 280 | 335 | 265 | 265 | 265 | 275 | 265 | 265 |  | 265 | 265 | 265 | 280 | 265 | 265 | 265 | 6759000
| Ashuganj 450 MW CCPP(North) | 375 | 380 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 295 | 360 | 310 | 310 | 310 | 310 | 310 | 300 |  | 300 | 300 | 300 | 300 | 300 | 320 | 290 | 7715600
| Ashuganj 420 MW CCPP(East) | [25 empty] | 0 | 0
35 | Ashuganj 55 MW PP (Precision) | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 55 | 56 | 54 | 53 | 54 | 56 | 56 | 56 | 56 | 56 |  | 56 | 56 | 56 | 57 | 57 | 56 | 54 | 1332960
36 | Chandpur 150 MW CCPP | 83 | 83 | 83 | 83 | 83 | 83 | 84 | 85 | 83 | 82 | 84 | 83 | 83 | 83 | 82 | 83 | 80 | 80 |  | 80 | 80 | 80 | 83 | 83 | 82 | 83 | 1978650
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 342 | 346 | 348 | 348 | 348 | 350 | 333 | 323 | 333 | 337 | 375 | 379 | 374 | 345 | 322 | 322 | 332 | 358 |  | 371 | 371 | 368 | 356 | 336 | 340 | 347 | 8458240
40 | Meghnaghat 450 MW CCPP(MPL) | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 |  | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 4013400
41 | Haripur 360MW CCPP(HPL) | 152 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 143 | 178 | 195 | 193 | 188 | 214 | 220 | 224 | 216 | 210 |  | 212 | 209 | 185 | 172 | 171 | 172 | 171 | 4308000
42 | RPCL 210MW CCPP | 136 | 136 | 137 | 154 | 153 | 142 | 107 | 66 | 68 | 68 | 68 | 44 | 45 | 43 | 41 | 41 | 43 | 43 |  | 74 | 100 | 105 | 117 | 131 | 132 | 132 | 2137920
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 0 | 5 | 14 | 9 | 38 | 0 | 1 | 4 | 9 | 4 | 7 | 4 | 0 | [8 empty] | 105410
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1019000
45 | Fenchugonj CCPP Phase-2 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 |  | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 965448
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 28 | 25 | 25 | 25 | 25 | 30 | 30 | 30 | 25 | 25 | 28 | 28 | 30 | 30 | 31 | 31 | 28 | 30 |  | 30 | 30 | 50 | 63 | 64 | 64 | 61 | 807264
48 | Shahjibazar 86MW PP (Shahjibazar) | 60 | 60 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 81 | 81 | 81 | 50 | 50 | 50 | 50 | 950400
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 206 | 205 | 205 | 206 | 219 |  | 219 | 219 | 219 | 219 | 219 | 220 | 220 | 5133090
51 | Sylhet 20 MW GTPP | 19 | 19 | 18 | 17 | 18 | 18 | 18 | 18 | 19 | 19 | 19 | 19 | 19 | 19 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 445000
52 | Sylhet 50MW PP (EPL) | [21 empty] | 6 | 6 | 6 | 6 | 6 | 25000
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 241380
54 | Hobiganj 11MW PP Cofidence-E
55 | Fenchugonj 51 MW PP (Barakatullah) | [20 empty] | 3 | 5 | 5 | 5 | 5 | 5 | 24000
56 | Shahjahanulla 25 MW PP | 8 | 8 | 0 | [13 empty] | 0 | 0 |  | 0 | 5 | 8 | 8 | 8 | 8 | 8 | 57168
57 | Bibiana-II 341 MW CCPP (Summit) | 280 | 270 | 280 | 260 | 265 | 270 | 275 | 290 | 310 | 270 | 270 | 305 | 300 | 250 | 285 | 290 | 305 | 290 |  | 255 | 265 | 270 | 280 | 270 | 260 | 300 | 6909500
| Bibiyana South 400 MW | 400 | 400 | 400 | 400 | 400 | 340 | 340 | 340 | 400 | 380 | 397 | 386 | 370 | 345 | 400 | 400 | 400 | 400 |  | 380 | 350 | 400 | 400 | 400 | 400 | 400 | 9182300
58 | Nababganj 55 MW PP (Southern power ) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 55 | 55 | 55 | 35 | 35 | 35 | 35 | 910388
59 | Tangail Palli Power Gen 22 MW | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 298560
60 | Barabkunda 22 MW PP (Regent) | 12 | 12 | 12 | 12 | 12 | 12 | 9 | 9 | 10 | 12 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 314976
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 0 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 456372
62 | Tangail 22 MW PP (Doreen)
63 | Impoprt (Tripura) | 114 | 114 | 110 | 108 | 100 | 96 | 84 | 88 | 96 | 102 | 100 | 100 | 100 | 110 | 100 | 110 | 110 | 122 |  | 124 | 120 | 128 | 126 | 126 | 122 | 114 | 2561280
64 | Malancha, Ctg. EPZ (United) | 30 | 30 | 30 | 30 | 30 | 22 | 28 | 16 | 12 | 13 | 9 | 11 | 15 | 13 | 10 | 10 | 15 | 8 |  | 18 | 21 | 23 | 24 | 27 | 30 | 25 | 496320
65 | Feni 22MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 0 |  | 0 | 9 | 16 | 16 | 16 | 16 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 359712
66 | Feni 11 MW PP (Doreen) | 6 | 10 | 10 | 10 | 10 | 10 | 0 |  | 0 | 10 | 10 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 200340
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 31 | 22 | 16 | 16 | 15 | 14 | 14 | 14 | 17 | 20 | 16 | 16 |  | 24 | 30 | 30 | 33 | 33 | 33 | 33 | 602100
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 18 | 16 | 12 | 12 | 12 | 12 | 12 | 14 | 14 | 19 | 19 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 448840
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 25 | 26 | 26 | 26 | 26 | 27 | 20 | 25 | 22 | 22 | 22 | 16 | 16 | 16 | 20 | 20 | 20 | 22 |  | 22 | 22 | 22 | 23 | 23 | 23 | 23 | 525600
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 25 | 25 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 784200
72 | Rupganj 33 MW PP(Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 7 | 7 | 7 | 7 | 7 | 6 | 6 | 6 | 6 | 6 |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 157900
73 | Ghorashal 108MW PP (Regent) | 92 | 92 | 92 | 92 | 92 | 92 | 42 | 42 | 64 | 75 | 80 | 80 | 75 | 56 | 56 | 56 | 53 | 65 |  | 76 | 76 | 78 | 82 | 82 | 86 | 86 | 1731272
| Feni Lanka Power | 17 | 17 | 17 | 17 | 7 | 0 | [6 empty] | 14 | 17 | 17 | 34 | 34 | 34 |  | 114 | 17 | 17 | 17 | 17 | 17 | 17 | 403560
| Chowmuhani 113 MW | 110 | 65 | 65 | 65 | 65 | 65 | 26 | 26 | 34 | 85 | 98 | 108 | 107 | 104 | 65 | 65 | 65 | 71 |  | 113 | 117 | 116 | 75 | 75 | 75 | 94 | 1974840
| Manikgonj 162MW PP(MPGL) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 80 | 162 |  | 162 | 162 | 162 | 162 | 162 | 162 | 30 | 1771200
77 | Siddhirganj 100 PP(Dutch Bangla) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 7 | 7 | 7 | 7 | 7 | 10 | 8 | 8 | 8 | 14 |  | 48 | 64 | 64 | 64 | 65 | 65 | 18 | 475200
78 | Gazipur 52 MW PP | 49 | 49 | 49 | 49 | 49 | 24 | 24 | 24 | 24 | 24 | 8 | 8 | 17 | 8 | 8 | 8 | 8 | 20 |  | 49 | 49 | 49 | 49 | 49 | 49 | 32 | 780480
79 | Kodda 150MW PP | 40 | 48 | 50 | 50 | 16 | 17 | 17 | 16 | 16 | 16 |  |  | 32 | 16 | 16 | 16 | 16 | 48 |  | 105 | 113 | 113 | 48 | 50 | 50 | 50 | 804960
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | [13 empty] | 4 | 8 | 8 | 8 | 8 |  | 23 | 1 | 0 |  |  |  |  | 79886
| Gazipur 100 MW PP | 102 | 102 | 102 | 102 | 102 | 70 | 35 | 35 | 34 | 78 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 105 |  | 105 | 105 | 105 | 105 | 105 | 103 | 103 | 2086800
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 2 | 2 | 2 | 3 | 2 | 0 | 0 | 0 | 1 | 0 | [9 empty] | 16080
| Jodiac Power | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 22 | 17 | 17 | 17 | 17 | 17 | 36 | 36 | 36 |  | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 788548
| Karnaphuli Power Ltd. | 105 | 68 | 68 | 68 | 68 | 68 | 17 | 17 | 17 | 57 | 68 | 68 | 97 | 105 | 105 | 105 | 105 | 105 |  | 105 | 68 | 34 | 17 | 17 | 17 | 29 | 1696974
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP ( Summit) | 118 | 125 | 123 | 123 | 125 | 125 | 118 | 118 | 120 | 118 | 125 | 126 | 125 | 123 | 125 | 125 | 130 | 130 |  | 125 | 125 | 125 | 125 | 115 | 118 | 118 | 2939316
87 | Meghnaghat 100 MW(IEL) | 7 | 8 | 7 | 8 | 7 | 8 | 7 | 8 | 8 | 7 | 8 | 8 | 8 | 7 | 8 | 7 | 8 | 28 |  | 55 | 59 | 58 | 46 | 17 | 16 | 9 | 373440
| Meghnaghat 104 MW PP (OPCL) | 17 | 17 | 17 | 17 | 17 | 0 | [7 empty] | 17 | 17 | 17 | 17 | 17 |  | 75 | 43 | 0 |  |  |  | 0 | 246720
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 55 |  | 66 | 20 | 20 | 20 | 20 | 20 | 33 | 802440
92 | Fenchuganj 44MW (Energyprima) | [22 empty] | 5 | 5 | 5 | 5 | 26424
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 10 | 10 | 10 | 35 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1107128
94 | Gagnagar 102 MW PP (Digital Power) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 50 | 65 | 65 | 65 | 65 | 65 | 8 | 471312
95 | Patenga 50MW PP (Baraka) | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 6 | 6 | 6 | 10 | 19 | 19 | 19 | 19 | 19 |  | 32 | 22 | 19 | 0 |  |  | 0 | 440160
96 | Chattogram 108 MW PP (ECPV) | 5 | 5 | 6 | 5 | 6 | 5 | 6 | 6 | 6 | 6 | 6 | 0 |  |  |  |  | 0 | 0 |  | 2 | 0 |  |  |  |  | 0 | 68160
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 55 | 55 | 55 | 55 | 55 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 38 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1157002
100 | Manikganj 55 MW PP (Northern) | 35 | 35 | 35 | 35 | 35 | 0 | [6 empty] | 17 | 35 | 35 | 35 | 35 | 55 |  | 55 | 35 | 0 |  |  |  | 0 | 475332
101 | Kushiara 163 MW CCPP (KP)
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 2850
103 | Kamalaghat 54 MW PP(Banco Energy) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 35 | 35 | 17 | 35 |  | 35 | 35 | 54 | 54 | 54 | 54 | 17 | 660240
104 | Keranigonj 300 MW PP (APR) | 19 | 0 | [23 empty] | 0 | 25527
105 | Bramhangoan 100 MW PP (Aggreko) | [25 empty] | 0 | 16553
106 | Mymensingh 200 MW PP (United) | 97 | 98 | 98 | 97 | 98 | 97 | 97 | 97 | 97 | 97 | 65 | 45 | 53 | 65 | 65 | 45 | 45 | 100 |  | 150 | 150 | 150 | 150 | 153 | 154 | 106 | 2371200
112 | Aurahati 100MW PP (Aggreko) | [25 empty] | 0 | 9521
114 | Kodda 149 MW PP Unit-1 (Summit) | 149 | 130 | 80 | 80 | 80 | 73 | 63 | 68 | 104 | 101 | 56 | 50 | 61 | 117 | 116 | 116 | 116 | 117 |  | 144 | 149 | 149 | 149 | 149 | 149 | 149 | 2605536
115 | Juldah 100 MW PP Unit-3 (Acorn) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 33 | 1119360
116 | Chandpur 200MW (Desh energy) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  |  | 7 | 17 | 17 | 17 | 17 | 19 |  | 60 | 68 | 17 | 17 | 17 | 17 | 17 | 474240
117 | Ashuganj 150MW PP (Midland) | 138 | 100 | 100 | 100 | 40 | 40 | 10 | 10 | 25 | 40 | 75 | 80 | 98 | 112 | 118 | 120 | 120 | 120 |  | 135 | 144 | 142 | 100 | 100 | 100 | 100 | 2363563
118 | Bibiyana-III 400 MW CCPP | 401 | 401 | 401 | 330 | 369 | 370 | 370 | 402 | 402 | 402 | 351 | 374 | 376 | 329 | 398 | 401 | 400 | 400 |  | 400 | 400 | 400 | 401 | 401 | 401 | 401 | 9309000
| Jamalpur 115 MW PP (United) | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 107 | 107 | 75 | 75 | 97 | 97 | 107 | 85 | 85 | 95 |  | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 2374800
| Anwara 300 MW PP (United) | 212 | 214 | 214 | 214 | 214 | 214 | 214 | 214 | 214 | 213 | 155 | 155 | 212 | 213 | 214 | 214 | 213 | 214 |  | 269 | 268 | 268 | 268 | 285 | 285 | 211 | 5341855
| Juldah unit-2 (Acorn) | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 |  | 64 | 90 | 90 | 90 | 90 | 90 | 71 | 1147200
| Anlima Energy Ltd. | 107 | 68 | 34 | 34 | 34 | 34 | 34 | 34 | 35 | 97 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 |  | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 2049927
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 443520
| Spectra Solar Plant Ltd. | [5 empty] | 0 | 1 | 1 | 0 | 1 | 2 | 1 | 2 | 4 | 3 | 3 | 2 | 0 | [8 empty] | 20062
| Chandpur 115(Doreen) | 34 | 35 | 35 | 35 | 35 | 35 | 35 | 34 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 34 | 35 | 45 |  | 108 | 115 | 115 | 115 | 115 | 115 | 57 | 1276800
| Kanchan Purbachal Power Generation Ltd. | [16 empty] | 41 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 0 | 382680
Mirsharai 150 MW (Oil)
| Mirsharai 150 MW (Gas) | [13 empty] | 0 | 9 | 0 | [10 empty] | 15054
120 | Eastern Zone Total | 7132 | 6848 | 6545 | 6456 | 6311 | 5981 | 5636 | 5678 | 5959 | 6099 | 6041 | 6175 | 6303 | 6335 | 6445 | 6471 | 6510 | 6990 |  | 7902 | 7755 | 7643 | 7336 | 7259 | 7206 | 6638 | 159576124
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
Khulna 115 PP MW (KPCL-2)
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 5 | 0 | [17 empty] | 0 | [6 empty] | 7200
| Khulna 225 MW CCPP | 130 | 130 | 130 | 126 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 3064320
129 | Rupsha 105 MW PP (Orion rupsha) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  |  |  | 2 | 17 | 17 | 17 | 17 | 17 | 17 |  | 53 | 53 | 56 | 56 | 56 | 56 | 17 | 565920
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 0 | 9 | 9 | 6 | 15 | 26 | 6 | 9 | 6 | 26 | 17 | 7 | 0 | [8 empty] | 139680
131 | Rampal 1320 MW (BIFPCL)
132 | United Payra Power Ltd. | [25 empty] | 0 | 0
133 | Bhola Nutan Biddut BD LTD (GAS) | 224 | 224 | 224 | 181 | 184 | 169 | 174 | 170 | 171 | 155 | 170 | 171 | 194 | 183 | 164 | 163 | 160 | 220 |  | 174 | 174 | 223 | 225 | 226 | 226 | 222 | 4626136
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 16 | 0 | [9 empty] | 5 | 16 | 16 | 16 | 0 |  | 0 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 171168
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 62 | 65 | 65 | 65 | 64 | 55 | 65 | 65 | 65 | 65 | 65 | 65 | 60 | 65 | 65 | 65 | 65 | 65 |  | 56 | 60 | 61 | 65 | 56 | 65 | 65 | 1469000
140 | Bhola 33 MW PP (Venture) | 20 | 22 | 21 | 20 | 20 | 17 | 12 | 6 | 10 | 10 | 11 | 12 | 17 | 12 | 14 | 12 | 12 | 16 |  | 18 | 21 | 22 | 21 | 21 | 22 | 21 | 389200
141 | Noapara 100 MW PP (Bangla Trac) | [25 empty] | 0 | 0
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | 50 | 50 | 15 | 15 | 15 | 15 | 15 | 15 |  |  |  | 15 | 15 | 15 | 15 | 15 | 15 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 15 | 639792
146 | Bheramara HVDC | 898 | 898 | 898 | 898 | 899 | 899 | 899 | 898 | 902 | 902 | 902 | 903 | 902 | 902 | 903 | 903 | 903 | 903 |  | 903 | 904 | 903 | 904 | 904 | 903 | 903 | 21784727
147 | Bheramara 410 MW CCPP | 260 | 260 | 260 | 265 | 270 | 270 | 280 | 230 | 230 | 230 | 230 | 230 | 250 | 210 | 210 | 210 | 210 | 190 |  | 300 | 300 | 345 | 350 | 340 | 325 | 315 | 6618528
148 | Payra 1320 MW | 920 | 880 | 860 | 830 | 830 | 750 | 750 | 710 | 710 | 620 | 620 | 650 | 670 | 600 | 600 | 600 | 600 | 600 |  | 710 | 750 | 750 | 790 | 810 | 770 | 830 | 19397500
149
150 | Barapukuria TPP Unit-1 | 81 | 75 | 79 | 79 | 79 | 80 | 80 | 78 | 78 | 80 | 80 | 80 | 81 | 80 | 81 | 80 | 80 | 79 |  | 78 | 76 | 78 | 82 | 81 | 81 | 80 | 1906909
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 249 | 249 | 249 | 249 | 250 | 250 | 250 | 249 | 249 | 249 |  | 250 | 249 | 249 | 250 | 250 | 250 | 250 | 6075400
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [17 empty] | 0 |  | 32 | 32 | 0 |  |  |  |  | 53488
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 3720
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 197 | 197 | 196 | 196 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 155 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 164 | 204 | 205 | 205 | 4472527
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
| Sirajgonj 225 MW CCPP Unit-2 (Oil) | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 198 | 160 | 130 | 142 | 147 |  | 110 | 80 | 80 | 80 | 42 | 22 | 53 | 3922864
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 175 | 179 | 181 | 183 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 130 | 130 | 130 | 130 | 130 |  | 150 | 150 | 150 | 161 | 192 | 210 | 203 | 4246700
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 414 | 414 | 415 | 414 | 416 | 356 | 340 | 343 | 340 | 300 | 306 | 368 | 372 | 305 | 256 | 258 | 265 | 309 |  | 258 | 258 | 422 | 425 | 400 | 325 | 422 | 8394582
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 8 | 22 | 22 | 22 | 22 | 22 | 20 | 21 |  | 18 | 18 | 18 | 18 | 22 | 22 | 22 | 474240
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 5 | 5 | 5 | 5 | 5 | 0 |  | 5 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 151344
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | 42 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  |  |  | 8 | 8 | 8 | 8 | 0 |  | 0 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 518166
167 | Katakhali 50 MW Peaking PP | [17 empty] | 0 |  | 9 | 0 | [5 empty] | 15840
168 | Santahar 50 MW Peaking PP | [17 empty] | 0 |  | 33 | 33 | 0 |  |  |  |  | 53323
169 | Natore 52 MW PP (Rajlanka) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | [8 empty] | 0 |  | 35 | 35 | 35 | 8 | 8 | 8 | 8 | 186240
170 | Chapainawabganj 100 MW Peaking PP | [17 empty] | 0 |  | 82 | 82 | 82 | 82 | 83 | 45 | 23 | 358408
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 94 | 50 | 50 | 35 | 0 | [12 empty] | 8 |  | 86 | 70 | 70 | 35 | 35 | 35 | 56 | 695232
172 | Confidence Power Bogura Unit-1 113 MW | [17 empty] | 0 |  | 50 | 35 | 0 |  |  |  | 0 | 80928
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | 56 | 56 | 56 | 55 | 0 | [12 empty] | 0 |  | 60 | 70 | 70 | 49 | 49 | 34 | 34 | 530256
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1 | 2 | 3 | 3 | 3 | 4 | 3 | 3 | 1 | 1 | 1 | 0 | [8 empty] | 19646
178 | Energypac Power Venture Thakurgaon Ltd. | [11 empty] | 34 | 34 | 34 | 34 | 0 |  | 0 |  | 34 | 60 | 72 | 34 | 34 | 34 | 34 | 417600
178 | Intraco Solar 30 MW | [5 empty] | 0 | 3 | 9 | 6 | 5 | 13 | 17 | 3 | 1 | 2 | 5 | 3 | 0 | [8 empty] | 61450