## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on forecasted generation & Demand of national grid on | [6 empty] | 2019-05-27 | Monday
|  | Date (day): | 2019-05-27 |  | Monday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 14827 | MW |  |  | (b) At Evening Peak Hour : |  | 14962 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2019-05-26 | 2019-05-27 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | Gas | PDB | 2*55 | 110 | 85 | 35 | 35 | 35 | 35 |  |  | ST-1 under maint.
| Ghorasal GT: Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 113 | 94 | 100 | 100 |  |  | On test.
| Ghorasal GT: Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 100 | 100 | 100 | 80 |  | Gas shortage
| Ghorasal ST: Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 110 | 110 | 110 | 110 | 80 |  | Gas shoetage
2 | Ghorasal ST: Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 360 | 320 | 360 | 360
3 | Ghorashal 78MW (MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 71 | 40 | 40 | 40 |  |  | Gas Shortage
4 | Ghorashal (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 102 | 22 | 50 | 55 |  |  | Gas Shortage
5 | Haripur GT: Unit-1, 2 |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 | 40 |  | Gas shortage
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 352 | 327 | 412 | 412 |  |  | FGMO
7 | Haripur NEPC 110MW |  | HFO | IPP | 8*15 | 110 | 110 | 0 | 98 | 110 | 110
8 | Haripur Power CCPP 360MW |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 345 | 349 | 360 | 360
9 | Meghnaghat CCPP 450MW |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 400 | 450 | 450
10 | Meghnaghat (IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 90 | 100 | 100
11 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 265 | 253 | 335 | 335 |  |  | FGMO
12 | Madanganj 102MW |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 72 | 100 | 100
13 | Madanganj-55 MW |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 55 | 55 | 55
14 | Keraniganj (Powerpac) 100MW |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 82 | 100 | 100
15 | Narshingdi (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 19 | 19 | 19
16 | Siddhirgonj ST 210MW |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 115 |  | Gas shortage
17 | Siddhirgonj GT Unit-1& 2 |  | Gas | EGCB | 2*105 | 210 | 210 | 175 | 87 | 110 | 110 | 100 |  | Gas shortage
| Siddhirganj Desh |  | HSD | QRPP | 96*1.2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
18 | Siddhirganj (Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 70 | 100 | 100
19 | Siddhirganj CCPP-335 MW |  | Gas | EGCB | 1*217 | 217 | 217 | 0 | 0 | 0 | 0 | 37 |  | Gas shortage
0 | Pagla (DPA ) |  | HSD | QRPP | 100*0.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
20 | Gagnagar (Orion) |  | HFO | IPP | 12*8.924 | 102 | 102 | 24 | 100 | 102 | 102
21 | Katpotti 51 MW |  | HFO | IPP | 7*7.9 | 51 | 51 | 16 | 45 | 47 | 47
22 | Banco Energy 54MW |  | HFO | IPP | 3*18 | 54 | 54 | 35 | 35 | 35 | 35 |  |  | Engine problem
23 | Kodda 149MW |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 149 | 149 | 149
24 | Northern 55 MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 37 | 56 | 55 | 55
25 | Southern 55MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 55 | 55 | 55
26 | Bosila 108MW |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 54 | 65 | 65 |  | 43 | Engine problem
27 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 54 | 56 | 58 | 58 |  | 22 | Engine problem
28 | Summit Maona |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
29 | Summit Rupganj |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 17 | 33 | 33
30 | Gazipur (RPCL) |  | HFO | IPP | 6*8.9 | 52 | 52 | 50 | 48 | 48 | 48 |  |  | Engine problem
31 | Tongi GT |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 40 | 0 | 105 |  | Gas shortage
32 | Summit Gazipur -2 |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 200 | 300 | 300
33 | APR Energy , Keranigonj |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 300 | 300
34 | Bramhangoan 100 MW (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 100 | 100
35 | Aggreko Aurahati 100MW |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 100 | 100
36 | Summit Gazipur-1 150MW |  | HFO | IPP | 149 | 149 | 149 | 50 | 149 | 149 | 149
| Gazipur 100 MW |  | HFO | RPCL | 100 MW | 0 | 0 | 108 | 108 | 100 | 100
| Dhaka area Total |  |  |  |  | 5934 | 5698 | 2954 | 3728 | 4815 | 4780 | 557 | 65
37 | Chattogram ST-1 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 90 | 105 | 110 | 110 | 70 |  | Gas shortage
| Chittgong ST-2 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
38 | Raozan 25 MW (RPCL) |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 25 | 25 | 25
39 | Teknaf Solartech 20MW |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 14.89 | 0 | 20 | 0
40 | Patenga 50MW |  | HFO | IPP | 8*6.98 | 50 | 50 | 8 | 46 | 45 | 45
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 30 | 38 | 36 | 36 |  | 194 | Low water lavel
42 | Sikalbaha ST 60MW |  | Gas | PDB | 1*60 | 60 | 40 | 0 | 0 | 0 | 0 |  | 40 | Under S/D
43 | Sikalbaha 225MW |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 230 | 211 | 225 | 225
44 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 147 | 110 | 145 | 145
45 | Sikalbaha (Energis) |  | HFO | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 51 | 16 | 16 | 33 | 33 |  | 18 | Engine problem
| Baraka Sikalbaha PL |  | HFO | IPP | 105 MW | 0 | 0 | 18 | 106 | 109 | 109
46 | Hathazari peaking |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 74 | 76 | 83
47 | Dohazari Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 85 | 85 | 85
48 | Juldah (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 10 | 65 | 100 | 100
49 | Juldah 100 MW Unit-3 |  | HFO | IPP | 0 | 100 | 100 | 90 | 100 | 100 | 100
50 | Barabkunda (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 14 | 16 | 16 | 16 |  |  | Engine problem
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 33 | 15 | 20
51 | Chattogram ECPV 108 MW |  | HFO | IPP | 16*7 | 108 | 108 | 2 | 65 | 100 | 100 |  |  | Engine problem
| Kaptai Solar |  | Solar | PDB | 7.4 MW | 0 | 0 | 3.56 | 0 | 2 | 0
| Anwara United |  | HFO | United Group | 300 MW | 0 | 0 | 133 | 100 | 140 | 150 |  |  | on test
| Chattogram area Total |  |  |  |  | 1761 | 1681 | 808.45 | 1195 | 1382 | 1382 | 250 | 252
52 | Ashuganj ST: Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
| Ashuganj ST: Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
| Ashuganj ST: Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 80 | 80 | 80 | 80 |  |  | Gas shortage
53 | Ashuganj CCPP 225 MW |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 183 | 183 | 221 | 221
54 | Ashuganj CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 360 | 300 | 360 | 360
55 | Ashuganj CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 353 | 300 | 360 | 360
56 | Ashuganj Engines TSK |  | Gas | APSCL | 14*3.968 | 53 | 45 | 27 | 33 | 37 | 37 |  | 8 | Engine problem
57 | Ashuganj (Precision) 55MW |  | Gas | RPP | 15*4 | 55 | 55 | 10 | 30 | 30 | 30 | 25 |  | Gas Shortage
58 | Ashuganj (United) 53MW |  | Gas | QRPP | 14*4 | 53 | 53 | 5 | 5 | 5 | 5 | 48 |  | Gas Shortage
59 | Ashuganj 195MW Modular |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
60 | Ashuganj (Midland) 51MW |  | Gas | IPP | 6*9.34 | 51 | 51 | 35 | 35 | 35 | 35 |  | 16 | Engine problem
61 | Midland 150MW |  | HFO | IPP | 23*7.015 | 150 | 150 | 1 | 148 | 150 | 150
62 | B.Baria (Aggreko) 85MW |  | Gas | QRPP | 86*1.10 | 85 | 85 | 0 | 0 | 0 | 0 |  |  | Contract expired
63 | Daudkandi Peaking 52MW |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
64 | Chandpur CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 100 | 100 | 100 | 100
65 | Chandpur Desh 200MW |  | HFO | IPP | 0 | 200 | 200 | 4 | 200 | 200 | 200
66 | Feni (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 22 | 22 | 22
67 | Feni, Mohipal (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 8 | 8
** | Tripura |  |  | Imported power | 0 | 160 | 160 | 142 | 176 | 151 | 187
68 | Jangalia (Summit) 33MW |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
69 | Lakdhanvi 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 52 | 52 | 52
70 | Summit Cumilla 25MW |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 20 | 20
71 | Daudkandi bangla trak |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 200 | 200
| Cumilla Area Total |  |  |  |  | 2951 | 2891 | 1388 | 1733 | 2072 | 2158 | 524 | 24
72 | Mymensingh RPCL 210MW |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 149 | 150 | 153 | 153 | 49 |  | Gas shortage
73 | Tangail (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 20 | 20
74 | Jamalpur 95MW |  | HFO | IPP | 12*8.924 | 95 | 95 | 40 | 93 | 95 | 95
75 | Sarishabari (Solar) |  | Solar | IPP | 1*3 | 3 | 3 | 1.8 | 0 | 2 | 0
76 | United Mymensingh PPL |  | HFO | IPP | 200 | 200 | 200 | 0 | 160 | 200 | 200
77 | United Jamalpur PPL |  | HFO | IPP | 115 MW | 115 | 115 | 96 | 98 | 98 | 98 |  | 17 | Engine problem
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 306.8 | 521 | 568 | 566 | 49 | 0
78 | Fenchugonj CCPP-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 56 | 58 | 57 | 58
79 | Fenchugonj CCPP-2 |  | Gas | PDB | !F71 | 104 | 90 | 50 | 58 | 58 | 58
80 | Kushiara 163 MW CCPP GT |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
81 | Shajibazar 330 MW |  | Gas | PDB | 3*110 | 330 | 330 | 301 | 275 | 330 | 330 |  |  | FGMO
82 | Fenchugonj (Barakatullah) 51MW |  | Gas | RPP | 19*2.90 | 51 | 51 | 45 | 53 | 50 | 50
83 | Fenchuganj (EPL) 44MW |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 47 | 47 | 44 | 44
84 | Hobiganj 11MW |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 10 | 11 | 11 | 11
85 | Shahjibazar GT: Unit- 8, 9 |  | Gas | PDB | 2*35 | 70 | 66 | 61 | 40 | 66 | 66 |  |  | FGMO
86 | Shahjibazar 86MW |  | Gas | RPP | 32*2.90 | 86 | 86 | 78 | 83 | 86 | 86
87 | Shahjibazar (EPL) 50MW |  | Gas | RPP | 27*2.0 | 50 | 50 | 43 | 46 | 44 | 44
88 | Sylhet GT 150 MW |  | Gas | PDB | 1*142 | 142 | 142 | 0 | 110 | 130 | 130
89 | Sylhet GT 20 MW |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 19 | 19 | 19
90 | Sylhet (EPL) 50MW |  | Gas | RPP | 27*2 | 50 | 50 | 40 | 47 | 42 | 42 |  | 8 | Engine problem
91 | Shahjahanulla 25 MW |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 24 | 25 | 25
92 | Summit Bibiana- 2 |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 275 | 240 | 341 | 341 |  |  | FGMO
| Bibiyana-3 285 MW |  | Gas | PDB | 285 MW | 0 | 0 | 298 | 220 | 300 | 300 |  |  | On test
93 | Sylhet (Desh) 10MW |  | Gas | RPP | 6*1.95 | 10 | 10 | 9 | 10 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1594 | 1549 | 1510 | 1504 | 1776 | 1777 | 0 | 8
94 | Bheramara GT-1,2,3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 32
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 938 | 941 | 941 | 944
| Khulna (KPCL-1 & 3) |  | HFO | IPP | 19*6.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
95 | Khulna (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 115 | 115 | 115
96 | Faridpur Peaking |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 32 | 35 | 35
97 | Khulna CCPP 225MW |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 120 | 224 | 225 | 225 |  |  | Reserve
98 | Gopalganj Peaking |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 55 | 50 | 80
99 | Bheramara 360 MW |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 |  | 410 | Under maint. |  | 28/05/2019
100 | Noapara (KZA) 40MW |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 40 | 40 | 40
0 | Khulna (Aggreeco) 55MW |  | HSD | QRPP | 71*0.85 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
101 | Bangla Trak Noapara |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 94 | 100 | 100
102 | Labon Chora 105 MW |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 105 | 105 | 105
103 | Madhumati Power Plant |  | HFO | IPP | 100 MW | 105 | 105 | 0 | 89 | 102 | 102 |  |  | On Test
| Khulna Area Total |  |  |  |  | 2328 | 2314 | 1058 | 1695 | 1713 | 1778 | 0 | 410
104 | Summit Barisal 110 MW |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 110 | 110 | 110
105 | Barisal GT: Unit-1, 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 20
106 | Bhola (Venture) 33MW |  | Gas | RPP | 1*34.50 | 33 | 33 | 27 | 39 | 33 | 33
107 | Bhola CCPP 194MW |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 174 | 173 | 174 | 174
108 | Bhola Aggreko 95MW |  | Gas | QRPP | 96*1.10 | 95 | 95 | 91 | 97 | 95 | 95
| Barisal Area Total |  |  |  |  | 472 | 462 | 292 | 419 | 412 | 432 | 0 | 0
109 | Baghabari GT 71MW |  | Gas | PDB | 1*71 | 71 | 71 | 55 | 60 | 60 | 60
| Baghabari GT 100MW |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
110 | Baghabari Peaking 50MW |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 50 | 50
111 | Bera Peaking |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 32 | 35 | 35
112 | Amnura 50MW |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 50 | 50 | 50
113 | Katakhali (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 43 | 50 | 50
114 | Katakhali Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 44 | 45 | 45
115 | Sirajgonj Unit-1 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 196 | 195 | 200 | 200 |  |  | FGMO
116 | Sirajgonj Unit-2 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 198 | 30 | 200 | 200 |  |  | FGMO
117 | Sirajgonj Unit-3 225MW |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 200 | 184 | 220 | 220 |  |  | FGMO
118 | Sirajgonj Unit-4 414 MW(Gas) |  | Gas | SNWPGCL | 1*282+1*132 | 414 | 414 | 418 | 414 | 414 | 414
119 | Santahar Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 35 | 35 | 35
120 | Bogra (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
121 | Bogra (EPL) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 16 | 16 | 16 | 16
122 | Ullapara (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
123 | Rajlanka 52 MW |  | HFO | IPP | 52 | 52 | 52 | 0 | 52 | 52 | 52
124 | Chapainawabganj-100 MW |  | HFO | PDB | 104 | 104 | 104 | 24 | 95 | 95 | 95
125 | Paramount Baghabari |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
126 | Confidence CPBL-2 |  | HFO | IPP | 113 MW | 113 | 113 | 11 | 90 | 100 | 100
| Rajshahi Area Total |  |  |  |  | 2080 | 2070 | 1145 | 1423 | 1855 | 1855 | 0 | 100
127 | Barapukuria Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under overhauling
| Barapukuria Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
128 | Barapukuria Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 149 | 149 | 199 | 199 | 75
129 | Rangpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 17 | 17 | 17
130 | Saidpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 15 | 18 | 18
| Rangpur Area Total |  |  |  |  | 564 | 484 | 149 | 181 | 234 | 234 | 75 | 170
| Total |  |  |  |  | 18329 | 17786 | 9611.25 | 12399 | 14827 | 14962 | 1455 | 1029
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 9136.0749 | 11786 | 14093.961 | 14222.2866
A. |  | 2019-05-26 | (Yesterday) |  |  |  |  | Sunday
1 | Highest Generation : |  |  | 12399 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 7300.38 | MW at | 6:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 12399 | MW
3 | Day peak Generation : |  |  | 9611.25 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 11786 | MW
4 | Evening peak Generation : |  |  | 12399 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 236.6477 | MKWHr | By Solar | 0.13045 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas: | 155.9456 | MKWHr |  | By Oil: | 50.1043 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal: | 3.6642 | MKWHr |  | By Hydro: | 0.78066 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1455 | MW | Dhaka | 4346 | 4346 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1029 | MW | Chittagong | 1192 | 1192 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 2484 | MW | Khulna | 1508 | 1508 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1395.4 | MMCFD |  |  | Rajshahi | 1262 | 1262 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 105953474.144 | ii) Oil : | Taka | 360230146.67 | Comilla | 1171 | 1171 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 14143812 | Total | Taka | 480327432.814 | Mymensingh | 908 | 908 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0.899 | MKWHr. | Sylhet | 449 | 449 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -260 | MW (E to W) at | 21:00 | hrs | Barisal | 310 | 310 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -440 | MW at | 20:00 | hrs | Rangpur | 640 | 640 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 35.1° C |  |  | Total | 11786 | 11786 |  | 0
B. |  | 2019-05-27 | (Today) |  |  |  | Monday |  |  | Probable max. temperature in Dhaka |  |  | 36.6° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 12700 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 14962 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 10500 | MW
4 | Reserve(Generation end) |  |  |  | 2262 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 242.3926 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 8914.5 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 22.5578 | MKWHr. | ii) HVDC Flow at Peak Time |  | 941 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.4646 | MKWHr. | iii) Maximum HVDC Flow : |  | 942 | MW at | 2:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 72.89 |  | (b) Today: | 73.38 |  | (c) Rule Curve: |  | 77
.
** Wapda control unable to give gas reading.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2019-05-26
Plant Name | Ghorasal ST: Unit-1,2 | Ghorasal GT: Unit-3 | Ghorasal GT: Unit-4 | Ghorasal ST: Unit-5 | Ghorasal ST: Unit-7 | Ghorashal (Regent) | Ghorashal 78MW (MAX) | Haripur 412 MW CCPP | Haripur Power CCPP 360MW | Haripur NEPC 110MW | Haripur GT: Unit-1, 2 | Meghnaghat CCPP 450MW | Meghnaghat CCPP(Summit) | Meghnaghat (IEL) | Madanganj 102MW | Madanganj-55 MW | Siddhirganj CCPP-335 MW | Siddhirgonj ST 210MW | Siddhirgonj GT Unit-1& 2 | Siddhirganj Desh | Siddhirganj (Dutch Bangla) | Gagnagar (Orion) | Kodda 149MW | Keraniganj (Powerpac) 100MW | Bosila 108MW | Pagla (DPA ) | Katpotti 51 MW | Banco Energy 54MW | Northern 55 MW | Southern 55MW | Narshingdi (Doreen) | Summit Ashulia | Summit Madhabdi | Summit Maona | Summit Rupganj | Gazipur (RPCL) | Tongi GT | Kaptai Unit-1, 2 & 3 | Kaptai Unit-4 & 5 | Chattogram ST-1 (Raozan) | Chittgong ST-2 (Raozan) | Raozan 25 MW (RPCL) | Sikalbaha 225MW (Gas) | Sikalbaha 225MW (Oil) | Sikalbaha GT 150MW (Gas) | Sikalbaha GT 150MW (Oil) | Sikalbaha ST 60MW | Sikalbaha (Energis) | Hathazari peaking | Dohazari Peaking | Juldah (Acorn) | Chattogram ECPV 108 MW | Patenga 50MW | Barabkunda (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj ST: Unit- 3 | Ashuganj ST: Unit- 4 | Ashuganj ST: Unit- 5 | Ashuganj CCPP(North) | Ashuganj CCPP(South) | Ashuganj CCPP 225 MW | Ashuganj 195MW Modular | Chandpur CCPP | Ashuganj Engines TSK | Ashuganj (Precision) 55MW | Ashuganj (United) 53MW | Ashuganj (Midland) 51MW | B.Baria (Aggreko) 85MW | Daudkandi Peaking 52MW | Lakdhanvi 52 MW | Feni (Doreen) 22MW | Feni, Mohipal (Doreen) | Jangalia (Summit) 33MW | Summit Cumilla 25MW | Tripura | Mymensingh RPCL 210MW | Jamalpur 95MW | Tangail (Doreen) 22MW | Sarishabari (Solar) | Fenchugonj CCPP-1 | Fenchugonj CCPP-2 | Fenchugonj (Barakatullah) 51MW | Fenchuganj (EPL) 44MW | Kushiara 163 MW CCPP GT | Shajibazar 330 MW | Shahjibazar GT: Unit- 8, 9 | Shahjibazar 86MW | Shahjibazar (EPL) 50MW | Sylhet GT 150 MW | Sylhet GT 20 MW | Sylhet (EPL) 50MW | Sylhet (Desh) 10MW | Summit Bibiana- 2 | Shahjahanulla 25 MW | Hobiganj 11MW | Daudkandi bangla trak | Summit Gazipur -2 | APR Energy , Keranigonj | Bramhangoan 100 MW (Aggreko) | United Mymensingh PPL | Aggreko Aurahati 100MW | Summit Gazipur-1 150MW | Teknaf Solartech 20MW | Juldah 100 MW Unit-3 | Chandpur Desh 200MW | Midland 150MW | Bibiyana-3 285 MW | United Jamalpur PPL | Gazipur 100 MW | Baraka Sikalbaha PL | Kaptai Solar | Anwara United | EasternBlank | Bheramara (HVDC ) | Bheramara GT-1,2,3 | Bheramara 360 MW | Khulna (KPCL-1 & 3) | Khulna (KPCL-2) | Khulna CCPP 225MW | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur Peaking | Gopalganj Peaking | Noapara (KZA) 40MW | Bhola CCPP 194MW | Bhola (Venture) 33MW | Summit Barisal 110 MW | Barisal GT: Unit-1, 2 | Baghabari GT 100MW | Baghabari GT 71MW | Baghabari Peaking 50MW | Bera Peaking | Chapainawabganj-100 MW | Amnura 50MW | Katakhali (Northern) | Katakhali Peaking | Rajlanka 52 MW | Santahar Peaking | Bogra (GBB) | Bogra (EPL) | Ullapara (Summit) | Barapukuria Unit-1 | Barapukuria Unit-2 | Barapukuria Unit-3 | Rangpur GT | Saidpur GT | Sirajgonj Unit-1 225MW (Gas) | Sirajgonj Unit-1 225MW (Oil) | Sirajgonj Unit-2 225MW (Gas) | Sirajgonj Unit-2 225MW (Oil) | Bhola Aggreko 95MW | Bangla Trak Noapara | Sirajgonj Unit-3 225 MW(Gas) | Sirajgonj Unit-3 225 MW(Oil) | Sirajgonj Unit-4 414 MW(Gas) | Labon Chora 105 MW | Paramount Baghabari | Confidence CPBL-2 | Madhumati Power Plant | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 35 | 134 | 0 | 110 | 320 | 111 | 50 | 326 | 335 | 0 | 0 | 340 | 260 | 0 | 0 | 0 | 0 | 0 | 127 | 0 | 0 | 0 | 16 | 0 | 24 | 0 | 48 | 17 | 18 | 17 | 19 | 25 | 32 | 33 | 33 | 25 | 0 | 37 | 0 | 110 | 0 | 25 | 231 | 0 | 130 | 0 | 0 | 16 | 0 | 17 | 10 | 19 | 47 | 14 | 38 | 0 | 0 | 80 | 300 | 280 | 183 | 8 | 100 | 30 | 25 | 5 | 35 | 0 | 0 | 0 | 22 | 8 | 33 | 20 | 134 | 152 | 16 | 20 | 0 | 56 | 50 | 47 | 47 | 130 | 304 | 55 | 82 | 46 | 0 | 19 | 45 | 10 | 260 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 50 | 6 | 200 | 99 | 108 | 18 | 0 | 153 |  | 941 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 27 | 174 | 38 | 16 | 0 | 0 | 60 | 0 | 0 | 55 | 24 | 0 | 0 | 8 | 0 | 22 | 16 | 8 | 0 | 0 | 149 | 0 | 0 | 180 | 0 | 177 | 0 | 95 | 0 | 186 | 0 | 300 | 27 | 0 | 53 | 58 |  | 6520 | 2734 | 9254 | 4411 | 941 | 2085 | 1289 | 149 | 37 | 208 | 134 | 0 | 0 | 72.74
2:00 | 35 | 133 | 0 | 110 | 320 | 111 | 50 | 326 | 333 | 0 | 0 | 340 | 260 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 17 | 18 | 17 | 19 | 25 | 32 | 33 | 33 | 25 | 0 | 37 | 0 | 110 | 0 | 8 | 231 | 0 | 130 | 0 | 0 | 16 | 0 | 0 | 10 | 12 | 47 | 14 | 38 | 0 | 0 | 80 | 300 | 280 | 183 | 8 | 100 | 30 | 25 | 5 | 35 | 0 | 0 | 0 | 22 | 8 | 33 | 20 | 132 | 152 | 8 | 20 | 0 | 56 | 50 | 47 | 47 | 100 | 304 | 64 | 82 | 46 | 0 | 19 | 45 | 10 | 280 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 17 | 6 | 200 | 99 | 108 | 18 | 0 | 143 |  | 942 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 8 | 174 | 39 | 16 | 0 | 0 | 60 | 0 | 0 | 55 | 24 | 0 | 0 | 8 | 0 | 22 | 16 | 8 | 0 | 0 | 149 | 0 | 0 | 181 | 0 | 179 | 0 | 96 | 0 | 187 | 0 | 301 | 17 | 0 | 35 | 36 |  | 6355 | 2673 | 9028 | 4426 | 942 | 2076 | 1091 | 149 | 37 | 175 | 132 | 0 | 0 | 72.77
3:00 | 35 | 134 | 0 | 110 | 330 | 111 | 50 | 345 | 304 | 0 | 0 | 340 | 290 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 17 | 18 | 17 | 19 | 25 | 25 | 33 | 33 | 25 | 0 | 37 | 0 | 110 | 0 | 8 | 231 | 0 | 130 | 0 | 0 | 16 | 0 | 0 | 10 | 12 | 47 | 14 | 40 | 0 | 0 | 80 | 300 | 280 | 196 | 8 | 100 | 30 | 25 | 5 | 7 | 0 | 0 | 0 | 22 | 8 | 33 | 20 | 136 | 152 | 8 | 20 | 0 | 56 | 50 | 47 | 47 | 100 | 306 | 65 | 82 | 46 | 0 | 19 | 45 | 10 | 285 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 17 | 6 | 200 | 70 | 72 | 18 | 0 | 142 |  | 941 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 8 | 174 | 38 | 0 | 0 | 0 | 60 | 0 | 0 | 55 | 24 | 0 | 0 | 8 | 0 | 22 | 16 | 8 | 0 | 0 | 149 | 0 | 0 | 194 | 0 | 191 | 0 | 96 | 0 | 200 | 0 | 302 | 17 | 0 | 35 | 36 |  | 6282 | 2694 | 8976 | 4503 | 941 | 2026 | 1009 | 149 | 37 | 175 | 136 | 0 | 0 | 72.8
4:00 | 35 | 134 | 0 | 110 | 330 | 111 | 50 | 337 | 295 | 0 | 0 | 340 | 257 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 17 | 18 | 17 | 19 | 25 | 25 | 33 | 33 | 0 | 0 | 38 | 0 | 110 | 0 | 8 | 228 | 0 | 130 | 0 | 0 | 16 | 0 | 0 | 10 | 12 | 37 | 14 | 40 | 0 | 0 | 80 | 300 | 280 | 184 | 8 | 100 | 30 | 25 | 5 | 7 | 0 | 0 | 0 | 22 | 8 | 33 | 20 | 128 | 155 | 8 | 20 | 0 | 56 | 50 | 47 | 10 | 100 | 308 | 50 | 40 | 46 | 0 | 19 | 10 | 10 | 270 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 17 | 6 | 173 | 50 | 55 | 18 | 0 | 142 |  | 937 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 174 | 19 | 0 | 0 | 0 | 60 | 0 | 0 | 55 | 12 | 0 | 0 | 8 | 0 | 22 | 16 | 8 | 0 | 0 | 149 | 0 | 0 | 190 | 0 | 187 | 0 | 96 | 0 | 196 | 0 | 297 | 0 | 0 | 35 | 36 |  | 5957 | 2617 | 8574 | 4431 | 937 | 1864 | 852 | 149 | 38 | 175 | 128 | 0 | 0 | 72.83
5:00 | 35 | 64 | 0 | 110 | 280 | 22 | 50 | 327 | 275 | 0 | 0 | 310 | 235 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 17 | 18 | 17 | 19 | 25 | 28 | 33 | 33 | 0 | 0 | 38 | 0 | 110 | 0 | 0 | 229 | 0 | 130 | 0 | 0 | 16 | 0 | 0 | 10 | 12 | 26 | 14 | 40 | 0 | 0 | 80 | 300 | 280 | 183 | 8 | 100 | 26 | 25 | 5 | 7 | 0 | 0 | 0 | 22 | 8 | 33 | 15 | 114 | 154 | 8 | 20 | 0 | 56 | 50 | 11 | 10 | 100 | 309 | 54 | 10 | 10 | 0 | 19 | 10 | 10 | 240 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 17 | 6 | 151 | 50 | 54 | 18 | 0 | 152 |  | 936 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 174 | 34 | 0 | 0 | 0 | 60 | 0 | 0 | 55 | 12 | 0 | 0 | 8 | 0 | 22 | 16 | 8 | 0 | 0 | 149 | 0 | 0 | 181 | 0 | 176 | 0 | 33 | 0 | 187 | 0 | 250 | 0 | 0 | 0 | 36 |  | 5405 | 2457 | 7862 | 4182 | 936 | 1498 | 770 | 149 | 38 | 175 | 114 | 0 | 0 | 72.86
6:00 | 35 | 63 | 0 | 110 | 280 | 22 | 50 | 326 | 276 | 0 | 0 | 310 | 265 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 17 | 18 | 17 | 19 | 25 | 28 | 33 | 33 | 0 | 0 | 37 | 0 | 110 | 0 | 0 | 227 | 0 | 85 | 0 | 0 | 16 | 0 | 0 | 10 | 4 | 11 | 14 | 28 | 0 | 0 | 80 | 250 | 250 | 183 | 8 | 50 | 10 | 25 | 5 | 7 | 0 | 0 | 0 | 22 | 8 | 8 | 15 | 110 | 154 | 8 | 20 | 0 | 56 | 50 | 11 | 10 | 100 | 309 | 40 | 10 | 10 | 0 | 0 | 10 | 0 | 235 | 24 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.38 | 10 | 0 | 0 | 120 | 16 | 36 | 18 | 0 | 151 |  | 936 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 174 | 27 | 0 | 0 | 0 | 60 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 | 16 | 8 | 0 | 0 | 149 | 0 | 0 | 180 | 0 | 145 | 0 | 12 | 0 | 186 | 0 | 243 | 0 | 0 | 0 | 0 |  | 4997.38 | 2303 | 7300.38 | 3870 | 936 | 1437 | 615 | 149 | 37 | 145 | 110 | 1.38 | 0 | 72.89
7:00 | 35 | 63 | 0 | 110 | 280 | 22 | 50 | 326 | 277 | 0 | 0 | 310 | 290 | 0 | 0 | 0 | 0 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 17 | 18 | 17 | 19 | 25 | 31 | 33 | 33 | 0 | 0 | 37 | 0 | 110 | 0 | 0 | 225 | 0 | 85 | 0 | 0 | 16 | 0 | 0 | 10 | 0 | 6 | 14 | 15 | 0 | 0 | 80 | 250 | 250 | 196 | 8 | 50 | 10 | 10 | 5 | 7 | 0 | 0 | 0 | 22 | 8 | 8 | 15 | 108 | 152 | 8 | 20 | 0.3 | 56 | 50 | 11 | 10 | 100 | 308 | 50 | 10 | 10 | 0 | 0 | 12 | 0 | 260 | 24 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.17 | 10 | 0 | 0 | 120 | 16 | 36 | 18 | 0.97 | 151 |  | 936 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 175 | 26 | 0 | 0 | 0 | 60 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 | 16 | 11 | 0 | 0 | 149 | 0 | 0 | 180 | 0 | 145 | 0 | 12 | 0 | 187 | 0 | 257 | 0 | 0 | 0 | 0 |  | 5043.44 | 2321 | 7364.44 | 3902 | 936 | 1450 | 631 | 149 | 37 | 145 | 108 | 6.44 | 0 | 72.9
8:00 | 35 | 63 | 0 | 110 | 280 | 22 | 50 | 344 | 274 | 0 | 0 | 310 | 290 | 0 | 0 | 0 | 0 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 17 | 18 | 17 | 19 | 25 | 31 | 33 | 33 | 10 | 0 | 37 | 0 | 110 | 0 | 0 | 219 | 0 | 85 | 0 | 0 | 16 | 0 | 0 | 10 | 0 | 6 | 14 | 2 | 0 | 0 | 80 | 250 | 250 | 206 | 8 | 50 | 10 | 10 | 5 | 7 | 0 | 0 | 0 | 22 | 8 | 8 | 12 | 118 | 152 | 25 | 20 | 0.96 | 56 | 50 | 11 | 10 | 100 | 312 | 63 | 10 | 10 | 0 | 0 | 12 | 0 | 280 | 24 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.66 | 10 | 0 | 0 | 122 | 53 | 70 | 18 | 2.8 | 154 |  | 937 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 175 | 25 | 0 | 0 | 0 | 60 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 149 | 0 | 0 | 197 | 0 | 168 | 0 | 12 | 0 | 203 | 0 | 250 | 0 | 0 | 0 | 0 |  | 5205.42 | 2367 | 7572.42 | 3996 | 937 | 1444 | 732 | 149 | 37 | 144 | 118 | 15.42 | 0 | 72.9
9:00 | 35 | 94 | 0 | 110 | 330 | 75 | 55 | 362 | 323 | 0 | 0 | 340 | 278 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 18 | 17 | 18 | 17 | 19 | 25 | 27 | 33 | 33 | 25 | 0 | 35 | 0 | 110 | 0 | 0 | 223 | 0 | 140 | 0 | 0 | 16 | 0 | 0 | 10 | 0 | 6 | 14 | 2 | 0 | 0 | 80 | 280 | 280 | 196 | 8 | 50 | 23 | 10 | 5 | 7 | 0 | 0 | 0 | 22 | 8 | 8 | 15 | 124 | 149 | 40 | 20 | 0.1 | 56 | 50 | 27 | 22 | 130 | 306 | 63 | 10 | 44 | 0 | 0 | 44 | 0 | 285 | 24 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 179 | 98 | 108 | 18 | 3.83 | 154 |  | 938 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 175 | 25 | 0 | 0 | 0 | 60 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 5 | 0 | 0 | 149 | 0 | 0 | 203 | 0 | 185 | 0 | 15 | 0 | 211 | 0 | 360 | 0 | 0 | 0 | 0 |  | 5878.93 | 2506 | 8384.93 | 4331 | 938 | 1823 | 837 | 149 | 35 | 144 | 124 | 3.93 | 0 | 72.9
10:00 | 35 | 94 | 70 | 110 | 360 | 108 | 72 | 333 | 323 | 0 | 0 | 380 | 260 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 19 | 17 | 28 | 17 | 19 | 25 | 29 | 33 | 33 | 36 | 0 | 35 | 0 | 105 | 0 | 0 | 230 | 0 | 140 | 0 | 0 | 16 | 0 | 0 | 10 | 0 | 6 | 14 | 2 | 0 | 0 | 80 | 320 | 280 | 184 | 8 | 100 | 27 | 10 | 5 | 25 | 0 | 0 | 0 | 22 | 8 | 33 | 15 | 134 | 149 | 40 | 20 | 1.3 | 56 | 50 | 45 | 47 | 130 | 307 | 60 | 55 | 45 | 0 | 18 | 39 | 9 | 280 | 16 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 40 | 0 | 0 | 218 | 98 | 108 | 18 | 5.109 | 154 |  | 938 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 174 | 25 | 0 | 0 | 0 | 60 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 5 | 0 | 0 | 149 | 0 | 0 | 190 | 0 | 198 | 0 | 51 | 0 | 199 | 0 | 421 | 0 | 0 | 0 | 0 |  | 6390.409 | 2590 | 8980.409 | 4549 | 938 | 2116 | 909 | 149 | 35 | 144 | 134 | 6.409 | 0 | 72.9
11:00 | 35 | 94 | 100 | 100 | 360 | 107 | 71 | 341 | 345 | 0 | 0 | 420 | 278 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 20 | 17 | 37 | 17 | 19 | 25 | 29 | 33 | 33 | 50 | 0 | 30 | 0 | 90 | 0 | 0 | 230 | 0 | 145 | 0 | 0 | 16 | 0 | 0 | 10 | 0 | 6 | 14 | 2 | 0 | 0 | 80 | 360 | 280 | 192 | 8 | 100 | 27 | 10 | 5 | 35 | 0 | 0 | 0 | 19 | 8 | 33 | 18 | 140 | 149 | 40 | 20 | 1.34 | 56 | 50 | 45 | 46 | 130 | 236 | 61 | 50 | 45 | 0 | 18 | 43 | 9 | 285 | 16 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 11.41 | 70 | 0 | 0 | 219 | 97 | 108 | 18 | 3.75 | 133 |  | 938 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 175 | 25 | 0 | 0 | 0 | 60 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 22 | 12 | 5 | 0 | 0 | 149 | 0 | 0 | 194 | 0 | 197 | 0 | 55 | 0 | 198 | 0 | 412 | 0 | 0 | 0 | 0 |  | 6553.5 | 2586 | 9139.5 | 4549 | 938 | 2182 | 991 | 149 | 30 | 144 | 140 | 16.5 | 0 | 72.91
12:00 | 35 | 113 | 100 | 110 | 360 | 102 | 71 | 352 | 345 | 0 | 0 | 450 | 265 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 16 | 35 | 37 | 17 | 19 | 25 | 29 | 33 | 33 | 50 | 0 | 30 | 0 | 90 | 0 | 0 | 230 | 0 | 147 | 0 | 0 | 16 | 0 | 0 | 10 | 2 | 8 | 14 | 2 | 0 | 0 | 80 | 360 | 353 | 183 | 8 | 100 | 27 | 10 | 5 | 35 | 0 | 0 | 0 | 19 | 8 | 33 | 20 | 142 | 149 | 40 | 20 | 1.8 | 56 | 50 | 45 | 47 | 163 | 301 | 61 | 78 | 43 | 0 | 18 | 40 | 9 | 275 | 16 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 14.89 | 90 | 4 | 1 | 298 | 96 | 108 | 18 | 3.56 | 133 |  | 938 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 174 | 27 | 0 | 0 | 0 | 55 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 22 | 16 | 5 | 0 | 0 | 149 | 0 | 0 | 196 | 0 | 198 | 0 | 91 | 0 | 200 | 0 | 418 | 0 | 0 | 11 | 0 |  | 6967.25 | 2644 | 9611.25 | 4855 | 938 | 2302 | 1031 | 149 | 30 | 144 | 142 | 20.25 | 0 | 72.92
13:00 | 35 | 113 | 100 | 110 | 280 | 55 | 70 | 327 | 341 | 0 | 0 | 450 | 278 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 24 | 0 | 0 | 56 | 0 | 37 | 35 | 37 | 17 | 19 | 25 | 31 | 33 | 33 | 49 | 0 | 35 | 0 | 90 | 0 | 8 | 228 | 0 | 145 | 0 | 0 | 16 | 0 | 0 | 10 | 40 | 34 | 16 | 8 | 0 | 0 | 80 | 300 | 300 | 184 | 8 | 100 | 27 | 10 | 5 | 35 | 0 | 0 | 16 | 19 | 8 | 33 | 20 | 156 | 147 | 75 | 20 | 0.9 | 56 | 50 | 47 | 47 | 100 | 296 | 52 | 77 | 44 | 0 | 18 | 40 | 9 | 240 | 16 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 103 | 10.74 | 100 | 50 | 50 | 292 | 97 | 108 | 36 | 5.54 | 134 |  | 938 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 174 | 29 | 0 | 0 | 0 | 55 | 0 | 0 | 24 | 0 | 0 | 0 | 8 | 0 | 22 | 15 | 5 | 0 | 0 | 149 | 0 | 0 | 181 | 0 | 185 | 0 | 91 | 0 | 187 | 0 | 414 | 17 | 0 | 54 | 54 |  | 6997.18 | 2722 | 9719.18 | 4580 | 938 | 2157 | 1543 | 149 | 35 | 144 | 156 | 17.18 | 0 | 72.94
14:00 | 35 | 94 | 100 | 110 | 320 | 52 | 70 | 340 | 340 | 0 | 0 | 450 | 277 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 24 | 0 | 0 | 55 | 0 | 48 | 35 | 37 | 17 | 19 | 25 | 31 | 33 | 33 | 49 | 0 | 35 | 0 | 90 | 0 | 25 | 223 | 0 | 145 | 0 | 0 | 16 | 0 | 0 | 10 | 58 | 46 | 16 | 8 | 0 | 0 | 80 | 360 | 340 | 186 | 8 | 100 | 27 | 10 | 5 | 35 | 0 | 0 | 25 | 21 | 8 | 33 | 18 | 158 | 147 | 95 | 20 | 1.7 | 55 | 50 | 47 | 47 | 130 | 286 | 59 | 75 | 44 | 88 | 18 | 43 | 9 | 260 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 149 | 16.3 | 100 | 52 | 61 | 292 | 95 | 108 | 38 | 4.1 | 150 |  | 940 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 174 | 28 | 0 | 0 | 0 | 55 | 0 | 0 | 24 | 0 | 0 | 0 | 8 | 0 | 22 | 16 | 5 | 0 | 0 | 149 | 0 | 0 | 191 | 0 | 194 | 0 | 92 | 0 | 196 | 0 | 402 | 61 | 0 | 72 | 53 |  | 7427.1 | 2802 | 10229.1 | 4824 | 940 | 2193 | 1764 | 149 | 35 | 144 | 158 | 22.1 | 0 | 72.96
15:00 | 35 | 94 | 100 | 110 | 320 | 22 | 50 | 327 | 341 | 0 | 0 | 450 | 253 | 0 | 0 | 0 | 0 | 0 | 177 | 0 | 0 | 24 | 0 | 0 | 53 | 0 | 48 | 35 | 56 | 35 | 19 | 25 | 31 | 33 | 16 | 48 | 0 | 35 | 0 | 100 | 0 | 25 | 230 | 0 | 110 | 0 | 0 | 16 | 0 | 0 | 30 | 33 | 46 | 16 | 3 | 0 | 0 | 80 | 360 | 355 | 184 | 8 | 100 | 30 | 10 | 5 | 35 | 0 | 0 | 43 | 21 | 8 | 33 | 20 | 166 | 145 | 94 | 20 | 0.7 | 56 | 50 | 50 | 47 | 163 | 289 | 61 | 77 | 44 | 83 | 19 | 41 | 9 | 265 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 149 | 12.4 | 100 | 148 | 137 | 295 | 96 | 108 | 83 | 3.8 | 133 |  | 941 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 174 | 32 | 0 | 0 | 0 | 55 | 0 | 0 | 60 | 0 | 0 | 0 | 8 | 0 | 21 | 16 | 8 | 0 | 0 | 149 | 0 | 0 | 182 | 0 | 186 | 0 | 92 | 0 | 188 | 0 | 411 | 105 | 0 | 82 | 70 |  | 7609.9 | 2900 | 10509.9 | 4772 | 941 | 2192 | 2058 | 149 | 35 | 180 | 166 | 16.9 | 0 | 72.99
16:00 | 35 | 94 | 100 | 110 | 320 | 23 | 50 | 327 | 341 | 0 | 0 | 450 | 257 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 0 | 24 | 0 | 0 | 53 | 0 | 48 | 17 | 56 | 35 | 19 | 25 | 31 | 33 | 16 | 48 | 0 | 35 | 0 | 100 | 0 | 25 | 230 | 0 | 110 | 0 | 0 | 16 | 0 | 0 | 40 | 33 | 46 | 15 | 7 | 0 | 0 | 80 | 360 | 350 | 184 | 8 | 100 | 30 | 10 | 5 | 35 | 0 | 0 | 52 | 21 | 8 | 33 | 20 | 162 | 147 | 94 | 20 | 1 | 56 | 50 | 53 | 47 | 163 | 292 | 61 | 77 | 44 | 83 | 19 | 46 | 10 | 260 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 118 | 8.9 | 100 | 140 | 80 | 298 | 87 | 108 | 103 | 2.4 | 133 |  | 940 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 2 | 0 | 173 | 32 | 0 | 0 | 0 | 55 | 0 | 0 | 60 | 0 | 0 | 0 | 8 | 0 | 21 | 16 | 8 | 0 | 0 | 150 | 0 | 0 | 181 | 0 | 179 | 0 | 90 | 0 | 187 | 0 | 360 | 58 | 0 | 90 | 69 |  | 7530.3 | 2799 | 10329.3 | 4762 | 940 | 2148 | 1938 | 150 | 35 | 182 | 162 | 12.3 | 0 | 73.02
17:00 | 35 | 94 | 100 | 110 | 320 | 22 | 50 | 328 | 344 | 0 | 0 | 400 | 235 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 40 | 0 | 13 | 53 | 0 | 48 | 17 | 56 | 55 | 19 | 25 | 31 | 33 | 16 | 48 | 0 | 35 | 0 | 100 | 0 | 25 | 226 | 0 | 110 | 0 | 0 | 16 | 0 | 0 | 40 | 31 | 46 | 15 | 3 | 0 | 0 | 80 | 360 | 360 | 184 | 8 | 100 | 30 | 10 | 5 | 35 | 0 | 0 | 52 | 21 | 8 | 33 | 20 | 156 | 147 | 93 | 20 | 0.5 | 56 | 50 | 53 | 47 | 163 | 290 | 63 | 78 | 46 | 85 | 19 | 43 | 10 | 270 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 3.8 | 100 | 140 | 80 | 298 | 96 | 108 | 110 | 0.9 | 133 |  | 940 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 4 | 25 | 0 | 173 | 31 | 0 | 0 | 0 | 55 | 0 | 0 | 60 | 0 | 0 | 0 | 8 | 0 | 21 | 16 | 8 | 0 | 0 | 149 | 0 | 0 | 181 | 0 | 181 | 0 | 93 | 0 | 187 | 0 | 360 | 53 | 0 | 108 | 36 |  | 7476.2 | 2809 | 10285.2 | 4743 | 940 | 2108 | 1940 | 149 | 35 | 209 | 156 | 5.2 | 0 | 73.05
18:00 | 35 | 94 | 100 | 110 | 300 | 22 | 40 | 327 | 322 | 13 | 0 | 360 | 250 | 1 | 3 | 8 | 0 | 0 | 145 | 0 | 3 | 74 | 16 | 76 | 51 | 0 | 48 | 17 | 56 | 55 | 19 | 25 | 31 | 33 | 25 | 48 | 0 | 35 | 0 | 105 | 0 | 25 | 209 | 0 | 110 | 0 | 0 | 16 | 0 | 0 | 40 | 31 | 46 | 15 | 4 | 0 | 0 | 80 | 320 | 320 | 184 | 8 | 100 | 30 | 10 | 5 | 35 | 0 | 0 | 52 | 21 | 8 | 33 | 20 | 152 | 148 | 60 | 20 | 0.1 | 60 | 50 | 22 | 20 | 100 | 276 | 50 | 40 | 46 | 83 | 19 | 30 | 10 | 250 | 24 | 11 | 0 | 3 | 0 | 0 | 5 | 0 | 100 | 0 | 100 | 140 | 80 | 220 | 96 | 108 | 107 | 0.1 | 133 |  | 941 | 0 | 0 | 0 | 16 | 120 | 0 | 0 | 20 | 50 | 0 | 174 | 32 | 16 | 0 | 0 | 55 | 0 | 0 | 60 | 0 | 8 | 0 | 8 | 0 | 22 | 16 | 8 | 0 | 0 | 149 | 0 | 0 | 174 | 0 | 173 | 0 | 49 | 0 | 176 | 0 | 330 | 53 | 0 | 96 | 34 |  | 7132.2 | 2780 | 9912.2 | 4520 | 941 | 1773 | 2076 | 149 | 35 | 266 | 152 | 0.2 | 0 | 73.08
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 35 | 94 | 100 | 110 | 260 | 22 | 40 | 327 | 283 | 40 | 0 | 330 | 283 | 20 | 18 | 36 | 0 | 0 | 60 | 0 | 20 | 84 | 70 | 87 | 55 | 0 | 48 | 35 | 56 | 55 | 19 | 25 | 10 | 33 | 25 | 48 | 0 | 35 | 0 | 105 | 0 | 25 | 228 | 0 | 80 | 0 | 0 | 16 | 42 | 70 | 40 | 43 | 46 | 16 | 32 | 0 | 0 | 80 | 280 | 280 | 193 | 8 | 100 | 30 | 10 | 5 | 35 | 0 | 36 | 52 | 0 | 8 | 33 | 20 | 170 | 147 | 72 | 20 | 0 | 60 | 50 | 25 | 33 | 100 | 277 | 65 | 10 | 46 | 97 | 19 | 49 | 10 | 250 | 24 | 11 | 0 | 68 | 0 | 0 | 48 | 0 | 100 | 0 | 100 | 156 | 88 | 220 | 96 | 108 | 107 | 0 | 133 |  | 941 | 0 | 0 | 0 | 115 | 145 | 0 | 0 | 35 | 70 | 40 | 174 | 38 | 64 | 0 | 0 | 55 | 50 | 34 | 90 | 50 | 18 | 43 | 42 | 35 | 22 | 16 | 11 | 0 | 0 | 149 | 0 | 17 | 159 | 0 | 144 | 0 | 66 | 0 | 151 | 0 | 250 | 105 | 0 | 100 | 51 |  | 7435 | 3280 | 10715 | 4235 | 941 | 1680 | 2768 | 149 | 35 | 737 | 170 | 0 | 0 | 73.1
19:30 | 35 | 94 | 100 | 110 | 320 | 22 | 40 | 330 | 353 | 70 | 0 | 430 | 234 | 90 | 40 | 55 | 0 | 0 | 95 | 0 | 50 | 100 | 98 | 87 | 55 | 0 | 48 | 35 | 56 | 55 | 19 | 25 | 18 | 33 | 25 | 48 | 0 | 38 | 0 | 105 | 0 | 25 | 211 | 0 | 145 | 0 | 0 | 16 | 74 | 85 | 60 | 60 | 46 | 16 | 30 | 0 | 0 | 80 | 300 | 320 | 191 | 8 | 100 | 30 | 10 | 5 | 35 | 0 | 50 | 52 | 0 | 8 | 33 | 20 | 172 | 150 | 94 | 20 | 0 | 60 | 58 | 51 | 47 | 130 | 270 | 63 | 82 | 46 | 110 | 19 | 50 | 10 | 260 | 24 | 11 | 0 | 190 | 0 | 0 | 130 | 0 | 108 | 0 | 100 | 200 | 147 | 270 | 96 | 108 | 107 | 0 | 100 |  | 940 | 0 | 0 | 0 | 115 | 160 | 0 | 0 | 35 | 70 | 40 | 173 | 40 | 110 | 0 | 0 | 55 | 50 | 33 | 95 | 50 | 24 | 44 | 52 | 35 | 22 | 16 | 11 | 0 | 0 | 149 | 0 | 14 | 186 | 0 | 0 | 0 | 96 | 10 | 197 | 0 | 330 | 105 | 0 | 108 | 78 |  | 8606 | 3443 | 12049 | 4440 | 940 | 2113 | 3354 | 149 | 38 | 843 | 172 | 0 | 0 | 0
20:00 | 35 | 94 | 100 | 110 | 320 | 22 | 40 | 345 | 349 | 83 | 0 | 400 | 235 | 80 | 48 | 55 | 0 | 0 | 87 | 0 | 68 | 101 | 149 | 89 | 55 | 0 | 47 | 35 | 56 | 55 | 19 | 25 | 28 | 33 | 25 | 48 | 0 | 38 | 0 | 105 | 0 | 25 | 211 | 0 | 110 | 0 | 0 | 16 | 74 | 85 | 66 | 63 | 46 | 16 | 24 | 0 | 0 | 80 | 300 | 320 | 184 | 8 | 100 | 30 | 10 | 5 | 35 | 0 | 50 | 52 | 12 | 8 | 33 | 20 | 174 | 150 | 94 | 20 | 0 | 58 | 58 | 53 | 47 | 130 | 275 | 60 | 84 | 46 | 110 | 19 | 47 | 10 | 260 | 24 | 11 | 0 | 194 | 0 | 0 | 132 | 0 | 110 | 0 | 100 | 200 | 147 | 220 | 96 | 108 | 107 | 0 | 100 |  | 941 | 0 | 0 | 0 | 115 | 185 | 0 | 0 | 32 | 60 | 40 | 174 | 39 | 110 | 0 | 0 | 60 | 50 | 32 | 92 | 50 | 43 | 47 | 52 | 35 | 22 | 16 | 11 | 0 | 0 | 149 | 16 | 15 | 183 | 0 | 0 | 0 | 96 | 37 | 189 | 0 | 300 | 105 | 0 | 100 | 89 |  | 8606 | 3485 | 12091 | 4372 | 941 | 2043 | 3452 | 149 | 38 | 922 | 174 | 0 | 0 | 73.12
21:00 | 35 | 94 | 100 | 110 | 320 | 22 | 40 | 327 | 349 | 98 | 0 | 400 | 253 | 90 | 72 | 55 | 0 | 0 | 87 | 0 | 70 | 100 | 149 | 82 | 54 | 0 | 45 | 35 | 56 | 55 | 19 | 25 | 31 | 33 | 17 | 48 | 0 | 38 | 0 | 105 | 0 | 25 | 211 | 0 | 110 | 0 | 0 | 16 | 74 | 85 | 65 | 65 | 46 | 16 | 33 | 0 | 0 | 80 | 300 | 300 | 183 | 8 | 100 | 33 | 30 | 5 | 35 | 0 | 0 | 52 | 22 | 8 | 33 | 20 | 176 | 150 | 93 | 20 | 0 | 58 | 58 | 53 | 47 | 163 | 275 | 40 | 83 | 46 | 110 | 19 | 47 | 10 | 240 | 24 | 11 | 0 | 200 | 0 | 0 | 160 | 0 | 149 | 0 | 100 | 200 | 148 | 220 | 98 | 108 | 106 | 0 | 100 |  | 941 | 0 | 0 | 0 | 115 | 224 | 0 | 0 | 32 | 55 | 40 | 173 | 39 | 110 | 0 | 0 | 60 | 50 | 32 | 95 | 50 | 43 | 44 | 52 | 35 | 22 | 16 | 11 | 0 | 0 | 149 | 17 | 15 | 195 | 0 | 30 | 0 | 97 | 94 | 184 | 0 | 414 | 105 | 0 | 90 | 89 |  | 8681 | 3718 | 12399 | 4357 | 941 | 2199 | 3632 | 149 | 38 | 907 | 176 | 0 | 0 | 73.14
22:00 | 35 | 94 | 100 | 110 | 320 | 22 | 40 | 328 | 354 | 55 | 0 | 400 | 260 | 92 | 15 | 55 | 0 | 0 | 95 | 0 | 7 | 100 | 149 | 30 | 62 | 0 | 48 | 35 | 56 | 55 | 19 | 25 | 31 | 33 | 25 | 48 | 0 | 38 | 0 | 105 | 0 | 26 | 230 | 0 | 90 | 0 | 0 | 16 | 74 | 85 | 65 | 65 | 46 | 16 | 33 | 0 | 0 | 80 | 300 | 300 | 183 | 8 | 100 | 33 | 30 | 5 | 35 | 0 | 0 | 52 | 22 | 8 | 33 | 20 | 170 | 149 | 93 | 20 | 0 | 58 | 58 | 47 | 47 | 130 | 250 | 64 | 84 | 46 | 110 | 19 | 45 | 10 | 265 | 24 | 11 | 0 | 109 | 0 | 0 | 160 | 0 | 149 | 0 | 100 | 200 | 148 | 221 | 98 | 108 | 109 | 0 | 110 |  | 940 | 0 | 0 | 0 | 115 | 225 | 0 | 0 | 32 | 48 | 40 | 174 | 39 | 110 | 0 | 0 | 60 | 50 | 33 | 92 | 50 | 43 | 44 | 52 | 35 | 22 | 16 | 11 | 0 | 0 | 149 | 17 | 15 | 214 | 0 | 141 | 0 | 98 | 94 | 218 | 0 | 414 | 105 | 0 | 108 | 89 |  | 8408 | 3893 | 12301 | 4537 | 940 | 2190 | 3378 | 149 | 38 | 899 | 170 | 0 | 0 | 73.16
23:00 | 35 | 96 | 100 | 110 | 320 | 22 | 40 | 330 | 312 | 0 | 0 | 370 | 306 | 100 | 0 | 55 | 0 | 0 | 96 | 0 | 0 | 100 | 149 | 0 | 63 | 0 | 48 | 35 | 56 | 55 | 19 | 25 | 32 | 33 | 25 | 48 | 40 | 37 | 0 | 105 | 0 | 25 | 215 | 0 | 110 | 0 | 0 | 16 | 0 | 66 | 65 | 60 | 47 | 16 | 37 | 0 | 0 | 80 | 300 | 300 | 200 | 8 | 100 | 33 | 30 | 5 | 35 | 0 | 0 | 52 | 22 | 8 | 33 | 20 | 160 | 150 | 94 | 20 | 0 | 58 | 58 | 50 | 47 | 130 | 252 | 63 | 84 | 46 | 127 | 19 | 46 | 10 | 270 | 24 | 11 | 0 | 0 | 0 | 0 | 160 | 0 | 149 | 0 | 100 | 200 | 148 | 239 | 99 | 108 | 109 | 0 | 130 |  | 941 | 0 | 0 | 0 | 115 | 225 | 0 | 0 | 32 | 36 | 40 | 174 | 38 | 110 | 0 | 0 | 60 | 50 | 33 | 92 | 50 | 43 | 43 | 52 | 34 | 22 | 16 | 11 | 0 | 0 | 149 | 17 | 15 | 214 | 0 | 213 | 0 | 96 | 70 | 218 | 0 | 407 | 105 | 0 | 108 | 88 |  | 8206 | 3917 | 12123 | 4714 | 941 | 2121 | 3209 | 149 | 37 | 792 | 160 | 0 | 0 | 73.18
24:00 | 35 | 94 | 100 | 110 | 320 | 22 | 40 | 340 | 312 | 0 | 0 | 400 | 290 | 100 | 0 | 0 | 0 | 0 | 97 | 0 | 0 | 100 | 149 | 0 | 63 | 0 | 47 | 35 | 56 | 55 | 19 | 25 | 32 | 33 | 25 | 48 | 40 | 37 | 0 | 105 | 0 | 25 | 203 | 0 | 90 | 0 | 0 | 16 | 0 | 51 | 65 | 63 | 47 | 15 | 36 | 0 | 0 | 80 | 300 | 300 | 193 | 8 | 100 | 33 | 30 | 5 | 35 | 0 | 0 | 52 | 0 | 8 | 33 | 20 | 182 | 149 | 94 | 20 | 0 | 57 | 58 | 50 | 47 | 130 | 249 | 63 | 81 | 46 | 116 | 19 | 46 | 10 | 280 | 24 | 11 | 0 | 0 | 0 | 0 | 160 | 0 | 149 | 0 | 100 | 200 | 150 | 250 | 98 | 108 | 109 | 0 | 132 |  | 940 | 0 | 0 | 0 | 115 | 225 | 0 | 0 | 32 | 31 | 40 | 174 | 38 | 110 | 0 | 0 | 60 | 50 | 33 | 92 | 50 | 43 | 0 | 51 | 34 | 22 | 16 | 11 | 0 | 0 | 149 | 17 | 16 | 214 | 0 | 211 | 0 | 95 | 70 | 218 | 0 | 417 | 105 | 0 | 108 | 89 |  | 8125 | 3876 | 12001 | 4654 | 940 | 2166 | 3143 | 149 | 37 | 730 | 182 | 0 | 0 | 73.2
KWH | 736000 | 2473800 | 1377000 | 2835000 | 7652063 | 1280681 | 1299872 | 8147190 | 7615000 | 276200 | 0 | 8838750 | 6571142 | 490560 | 180696 | 306733 | 0 | 0 | 3077000 | 0 | 189120 | 862416 | 750720 | 403285 | 680640 | 0 | 852528 | 598320 | 874451 | 722000 | 434160 | 600000 | 676080 | 789100 | 687100 | 849648 | 65678 | 780660 | 0 | 2500000 | 0 | 351178 | 5322241 | 0 | 2793076 | 0 | 0 | 389760 | 241352 | 449454 | 641760 | 690240 | 788640 | 350112 | 459840 | 0 | 0 | 1923456 | 7759000 | 7277000 | 4587000 | 200727 | 2182060 | 610848 | 442560 | 120000 | 591226 | 0 | 87624 | 563155 | 442404 | 194400 | 702800 | 431510 | 3464640 | 3522600 | 1328640 | 448812 | 12350 | 1357000 | 1218240 | 944400 | 877000 | 3254040 | 6541000 | 1311000 | 1498560 | 938520 | 1056550 | 372000 | 899760 | 195660 | 6536500 | 509712 | 231984 | 0 | 674950 | 0 | 0 | 871200 | 0 | 1673280 | 84105 | 1790400 | 2053000 | 1420145 | 5256000 | 2040000 | 2264976 | 1390030 | 33996 | 3291920 |  | 22557818 | 0 | 0 | 0 | 642240 | 3471360 | 0 | 0 | 199680 | 342784 | 262125 | 4291060 | 752744 | 632640 | 0 | 0 | 1392000 | 278520 | 156360 | 1248208 | 384020 | 211581 | 202248 | 372000 | 191636 | 510480 | 370116 | 199152 | 0 | 0 | 3664200 | 69000 | 84000 | 4815836 | 0 | 4214591 | 0 | 1739361 | 382080 | 4850445 | 0 | 8365730 | 1043520 | 0 | 1269696 | 1050480 |  | 166429986 | 70217711 | 236647697 | 108214060 | 22557818 | 47731527 | 42331395 | 3664200 | 780660 | 7772946 | 3464640 | 130451 | 0
Fuel Cost | 632960 | 2127468 | 1184220 | 2438100 | 4897320.32 | 1037351.61 | 1221879.68 | 4969785.9 | 4645150 | 2654282 | 0 | 5921962.5 | 99815646.98 | 3080716.8 | 1207049.28 | 1874138.63 | 0 | 0 | 3415470 | 0 | 1182000 | 5683321.44 | 7259462.4 | 2568925.45 | 4077033.6 | 0 | 5686361.76 | 4266021.6 | 5465318.75 | 4526940 | 325620 | 450000 | 0 | 0 | 0 | 8037670.08 | 75529.7 | 0 | 0 | 2750000 | 0 | 3325655.66 | 3512679.06 | 0 | 3212037.4 | 0 | 0 | 3425990.4 | 2599361.04 | 4373187.42 | 3972494.4 | 4458950.4 | 5157705.6 | 297595.2 | 0 | 0 | 0 | 1750344.96 | 4810580 | 5021130 | 3210900 | 138501.63 | 2094777.6 | 409268.16 | 380601.6 | 110400 | 484805.32 | 0 | 949844.16 | 4178610.1 | 340651.08 | 145800 | 541156 | 323632.5 | 23698137.6 | 2641950 | 12210201.6 | 345585.24 | 0 | 1411280 | 1266969.6 | 906624 | 789300 | 2538151.2 | 4578700 | 1494540 | 1603459.2 | 1032372 | 1204467 | 476160 | 836776.8 | 181963.8 | 4183360 | 382284 | 176307.84 | 0 | 4900137 | 0 | 0 | 6229080 | 0 | 0 | 0 | 0 | 19175020 | 13264154.3 | 4572720 | 0 | 0 | 0 | 0 | 0 |  | 115044871.8 | 0 | 0 | 0 | 5324169.6 | 55819468.8 | 0 | 0 | 2248396.8 | 4037995.52 | 2065545 | 2960831.4 | 745216.56 | 4681536 | 0 | 0 | 1461600 | 3189054 | 1676179.2 | 11183943.68 | 3321773 | 1883070.9 | 2153941.2 | 3690240 | 2255555.72 | 561528 | 347909.04 | 150758.064 | 0 | 0 | 14143812 | 2223870 | 2248680 | 3274768.48 | 0 | 2950213.7 | 0 | 0 | 6621446.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 362804067.35 | 256266374.864 | 619070442.214 | 78286161.204 | 115044871.8 | 27667312.94 | 258011206.73 | 14143812 | 0 | 102218939.94 | 23698137.6 | 0 | 0
Yesterday Day Peak | 35 | 113 | 100 | 110 | 360 | 102 | 71 | 352 | 345 | 0 | 0 | 450 | 265 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 16 | 35 | 37 | 17 | 19 | 25 | 29 | 33 | 33 | 50 | 0 | 30 | 0 | 90 | 0 | 0 | 230 | 0 | 147 | 0 | 0 | 16 | 0 | 0 | 10 | 2 | 8 | 14 | 2 | 0 | 0 | 80 | 360 | 353 | 183 | 8 | 100 | 27 | 10 | 5 | 35 | 0 | 0 | 0 | 19 | 8 | 33 | 20 | 142 | 149 | 40 | 20 | 1.8 | 56 | 50 | 45 | 47 | 163 | 301 | 61 | 78 | 43 | 0 | 18 | 40 | 9 | 275 | 16 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 14.89 | 90 | 4 | 1 | 298 | 96 | 108 | 18 | 3.56 | 133 |  | 938 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 174 | 27 | 0 | 0 | 0 | 55 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 22 | 16 | 5 | 0 | 0 | 149 | 0 | 0 | 196 | 0 | 198 | 0 | 91 | 0 | 200 | 0 | 418 | 0 | 0 | 11 | 0 |  | 9611.25 | DayPeak
Yesterday Evening Peak | 35 | 94 | 100 | 110 | 320 | 22 | 40 | 327 | 349 | 98 | 0 | 400 | 253 | 90 | 72 | 55 | 0 | 0 | 87 | 0 | 70 | 100 | 149 | 82 | 54 | 0 | 45 | 35 | 56 | 55 | 19 | 25 | 31 | 33 | 17 | 48 | 0 | 38 | 0 | 105 | 0 | 25 | 211 | 0 | 110 | 0 | 0 | 16 | 74 | 85 | 65 | 65 | 46 | 16 | 33 | 0 | 0 | 80 | 300 | 300 | 183 | 8 | 100 | 33 | 30 | 5 | 35 | 0 | 0 | 52 | 22 | 8 | 33 | 20 | 176 | 150 | 93 | 20 | 0 | 58 | 58 | 53 | 47 | 163 | 275 | 40 | 83 | 46 | 110 | 19 | 47 | 10 | 240 | 24 | 11 | 0 | 200 | 0 | 0 | 160 | 0 | 149 | 0 | 100 | 200 | 148 | 220 | 98 | 108 | 106 | 0 | 100 |  | 941 | 0 | 0 | 0 | 115 | 224 | 0 | 0 | 32 | 55 | 40 | 173 | 39 | 110 | 0 | 0 | 60 | 50 | 32 | 95 | 50 | 43 | 44 | 52 | 35 | 22 | 16 | 11 | 0 | 0 | 149 | 17 | 15 | 195 | 0 | 30 | 0 | 97 | 94 | 184 | 0 | 414 | 105 | 0 | 90 | 89 |  | 12399 | EvPeak
Forecast for Evening | 35 | 100 | 100 | 110 | 360 | 55 | 40 | 412 | 360 | 110 | 0 | 450 | 335 | 100 | 100 | 55 | 0 | 0 | 110 | 0 | 100 | 102 | 149 | 100 | 65 | 0 | 47 | 35 | 55 | 55 | 19 | 25 | 33 | 33 | 33 | 48 | 0 | 36 | 0 | 110 | 0 | 25 | 225 | 0 | 145 | 0 | 0 | 33 | 83 | 85 | 100 | 100 | 45 | 16 | 20 | 0 | 0 | 80 | 360 | 360 | 221 | 8 | 100 | 37 | 30 | 5 | 35 | 0 | 50 | 52 | 22 | 8 | 33 | 20 | 187 | 153 | 95 | 20 | 0 | 58 | 58 | 50 | 44 | 163 | 330 | 66 | 86 | 44 | 130 | 19 | 42 | 10 | 341 | 25 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 300 | 98 | 100 | 109 |  | 150 |  | 944 | 32 | 0 | 0 | 115 | 225 | 0 | 0 | 35 | 80 | 40 | 174 | 33 | 110 | 20 | 0 | 60 | 50 | 35 | 95 | 50 | 50 | 45 | 52 | 35 | 22 | 16 | 11 | 0 | 0 | 199 | 17 | 18 | 200 | 0 | 200 | 0 | 95 | 100 | 220 | 0 | 414 | 105 | 200 | 100 | 102
Forecast for Day | 35 | 100 | 100 | 110 | 360 | 50 | 40 | 412 | 360 | 110 | 0 | 450 | 335 | 100 | 100 | 55 | 0 | 0 | 110 | 0 | 100 | 102 | 149 | 100 | 65 | 0 | 47 | 35 | 55 | 55 | 19 | 25 | 33 | 33 | 33 | 48 | 40 | 36 | 0 | 110 | 0 | 25 | 225 | 0 | 145 | 0 | 0 | 33 | 76 | 85 | 100 | 100 | 45 | 16 | 15 | 0 | 0 | 80 | 360 | 360 | 221 | 8 | 100 | 37 | 30 | 5 | 35 | 0 | 0 | 52 | 22 | 8 | 33 | 20 | 151 | 153 | 95 | 20 | 2 | 57 | 58 | 50 | 44 | 163 | 330 | 66 | 86 | 44 | 130 | 19 | 42 | 10 | 341 | 25 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 20 | 100 | 200 | 150 | 300 | 98 | 100 | 109 | 2 | 140 |  | 941 | 0 | 0 | 0 | 115 | 225 | 0 | 0 | 35 | 50 | 40 | 174 | 33 | 110 | 0 | 0 | 60 | 50 | 35 | 95 | 50 | 50 | 45 | 52 | 35 | 22 | 16 | 11 | 0 | 0 | 199 | 17 | 18 | 200 | 0 | 200 | 0 | 95 | 100 | 220 | 0 | 414 | 105 | 0 | 100 | 102
Generation at 08:00(Today) | 35 | 94 | 100 | 110 | 280 | 22 | 40 | 335 | 312 | 0 | 0 | 370 | 286 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 7 | 16 | 0 | 8 | 0 | 47 | 17 | 18 | 17 | 19 | 25 | 31 | 33 | 25 | 48 | 40 | 35 | 0 | 105 | 0 | 8 | 231 | 0 | 130 | 0 | 0 | 16 | 0 | 0 | 10 | 12 | 18 | 13 | 5 | 0 | 0 | 80 | 300 | 300 | 190 | 8 | 100 | 30 | 30 | 5 | 35 | 0 | 0 | 8 | 22 | 8 | 31 | 0 | 138 | 150 | 45 | 20 | 0.2 | 57 | 58 | 11 | 10 | 130 | 250 | 64 | 82 | 45 | 67 | 19 | 12 | 10 | 275 | 16 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 9 | 85 | 52 | 10 | 250 | 98 | 91 | 18 | 2.9 | 137 | 0 | 937 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 173 | 30 | 0 | 0 | 0 | 55 | 0 | 0 | 40 | 12 | 0 | 0 | 8 | 0 | 22 | 16 | 8 | 0 | 0 | 149 | 0 | 0 | 192 | 0 | 201 | 0 | 97 | 0 | 198 | 0 | 300 | 0 | 0 | 35 | 53 | 0
199
| Minimum Generation |  | 7300.38 | 6:00
| Highest Generation |  | 12399 | 21:00
| Day Peak Generation |  | 9611.25 | 12:00
| Evening Peak Generation |  | 12399 | 21:00
| HVDC Max Flow |  | 942 | 2:00
| HVDC EvPeak Flow |  | 941 | 21:00
| Load factor L.F |  | 79.53%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2019-05-27
Till now the maximum generation is : - |  |  | 12539 MW | 21:00 | Hrs on | 2019-05-21
The Summary of Yesterday's |  | 2019-05-26 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 9611.25 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 8914.5 | MW
Evening Peak Generation : |  | 12399 | MW Hour : | 21:00 | Available Max Generation : |  | 14962 | MW
E.P. Demand (at gen end) : |  | 12399 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 12700 | MW
Maximum Generation : |  | 12399 | MW Hour : | 21:00 | Reserve(Generation end) |  | 2262 | MW
Total Gen. (MKWH) : |  | 236.6477 | System Load Factor : | 79.53% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -440 | MW at | 20:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2019-05-27
Actual : | 73.38 | Ft.(MSL) , | Rule curve : | 77 | Ft.( MSL )
Gas Consumed : | Total = | 1395.4 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 105953474.144
|  | Coal : | 14143812 | Oil : | 360230146.67 | Total : | 480327432.814
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4487.9874 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1530.0795 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1371.5981 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1239.6023 |  |  | 0 | 0%
Comilla Area | 0 | 0:00 | 1120.0741 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 903.87 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 500.3612 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 232.5889 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 697.1335 |  |  | 0 | 0%
Total | 0 |  | 12083.2951 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1 ,2 | 7) Baghabari 100 MW
2) Khulna ST 110 MW
3) Sikalbaha ST 60 MW
4) Bheramara 410 MW.
5) Siddhirganj ST
6) Ashuganj #3
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Rampura-Ullon 132 kV Ckt-1 tripped at 10:26 from Rampura end showing E/F and was
switched on at 10:31.
b) Sonargaon 132/33 kV T2 transformer was under shut down from 11:15 to 11:40 for 33 kV incomer
breaker maintenance.
c) Ghorasal Unit-4 GT was synchronized at 09:56.
d) Madaripur-Gopalganj 132 kV Ckt tripped at 11:16 from Gopalganj end showing E/F and was |  |  |  |  | About 45 MW Power interruption occurred under Gopalganj S/S area
switched on at 11:35. |  |  |  |  | from 11:16 to 11:35.
e) Madaripur-Faridpur 132 kV Ckt-2 tripped at 11:16 from both ends showing Dist Z2 3-phase at
Madaripur end & E/F, O/C C-phase at Faridpur end and was switched on at 11:53.
f) Faridpur-Madaripur 132 kV Ckt-1 tripped at 11:16 from Faridpur end showing Dist C-phase and was
switched on at 12:01.
g) Bhandaria 132/33 kV T1 & T3 transformers tripped at 11:17 from 33 kV sides operating SPS and |  |  |  |  | About 25 MW Power interruption occurred under Bhandaria S/S area
were switched on at 11:20. |  |  |  |  | from 11:17 to 11:20.
h) Sylhet 150 MW GT was synchronized at 13:01.
i) Madaripur 132/33 kV T1 transformer was switched on at 14:56.
j) Hasnabad 230/132 kV T2 transformer was under shut down from 17:14 to 18:06 due to high
temperature at Y-phase LT bushing.
k) Tongi 132/33 kV T1 transformer was under shut down from 17:38 to 18:44 due to red hot at Y-phase
CB to CT loop.
l) Sirajganj Unit-2 tripped at 19:14 due to gas booster problem and GT & ST were synchronized
at 20:22 & 21:14 respectively.
m) Kishoreganj 132/33 kV T1 & T2 transformers tripped at 19:32 showing O/C & E/F and were |  |  |  |  | About 119 MW Power interruption occurred under Kishoreganj S/S area
switched on at 19:46. |  |  |  |  | from 19:32 to 19:46.
n) Barisal(S) 132/33 kV T1 transformer was under shut down from 06:07 to 08:42(27/05/2019) for C/M. |  |  |  |  | About 15 MW Power interruption occurred under Barisal(S) S/S area
from 06:07 to 08:42(27/05/2019).

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2019-05-26 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | PDB | 2*55 | 85 | 35 | 736000 | #1 Under maint.
| Ghorasal GT: Unit-3 |  | PDB | 1*210 | 170 | 94 | 2473800 | Gas shortage
| Ghorasal GT: Unit-4 |  | PDB | 1*210 | 180 | 100 | 1377000
| Ghorasal ST: Unit-5 |  | PDB | 1*210 | 190 | 110 | 2835000 | Gas shortage
2 | Ghorasal ST: Unit-7 |  | PDB | 1*243+1*122 | 365 | 320 | 7652063 | Frequency control
3 | Ghorashal 78MW (MAX) |  | QRPP | 2*40 | 78 | 40 | 1299872 | Low demand
4 | Ghorashal (Regent) |  | IPP | 34*3.35 | 108 | 22 | 1280681 | Gas shortage
5 | Haripur GT: Unit-1, 2 |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Gas shortage
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 327 | 8147190 | Frequency control
7 | Haripur NEPC 110MW |  | IPP | 8*15 | 110 | 98 | 276200 | Engine problem
8 | Haripur Power CCPP 360MW |  | IPP | 1*235+1*125 | 360 | 349 | 7615000
9 | Meghnaghat CCPP 450MW |  | IPP | 2*150+1*150 | 450 | 400 | 8838750 | Frequency control
10 | Meghnaghat (IEL) |  | QRPP | 12*8.9 | 100 | 90 | 490560 | Engine problem
11 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 253 | 6571142 | Low demand
12 | Madanganj 102MW |  | QRPP | 6*17 | 100 | 72 | 180696 | Low demand
13 | Madanganj-55 MW |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 306733
14 | Keraniganj (Powerpac) 100MW |  | QRPP | 8*13.45 | 100 | 82 | 403285 | Engine problem
15 | Narshingdi (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 434160 | Engine problem
16 | Siddhirgonj ST 210MW |  | PDB | 1*210 | 115 | 0 | 0 | Gas shortage
17 | Siddhirgonj GT Unit-1& 2 |  | EGCB | 2*105 | 210 | 87 | 3077000 | Low demand
| Siddhirganj Desh |  | QRPP | 96*1.2 | 0 | 0 | 0 | Contract Expired
18 | Siddhirganj (Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 70 | 189120 | Low demand
19 | Siddhirganj CCPP-335 MW |  | EGCB | 1*217 | 217 | 0 | 0 | Gas shortage
0 | Pagla (DPA ) |  | QRPP | 100*0.5 | 0 | 0 | 0 | Contract Expired
20 | Gagnagar (Orion) |  | IPP | 12*8.924 | 102 | 100 | 862416
21 | Katpotti 51 MW |  | IPP | 7*7.9 | 51 | 45 | 852528 | Engine problem
22 | Banco Energy 54MW |  | IPP | 3*18 | 54 | 35 | 598320 | Engine problem
23 | Kodda 149MW |  | BPDB-RPCL | 9*17.06 | 149 | 149 | 750720
24 | Northern 55 MW |  | IPP | 3*19.3 | 55 | 56 | 874451
25 | Southern 55MW |  | IPP | 3*19.3 | 55 | 55 | 722000
26 | Bosila 108MW |  | IPP | 12*8.775+1*3.5 | 108 | 54 | 680640 | Engine problem
27 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 56 | 1276080 | Engine problem
28 | Summit Maona |  | SIPP,REB | 4*8.73 | 33 | 33 | 789100
29 | Summit Rupganj |  | SIPP,REB | 4*8.73 | 33 | 17 | 687100 | Engine problem
30 | Gazipur (RPCL) |  | IPP | 6*8.9 | 52 | 48 | 849648
31 | Tongi GT |  | PDB | 1* 105 | 105 | 0 | 65678 | Gas shortage
32 | Summit Gazipur -2 |  | IPP | 18*17.076 | 300 | 200 | 674950 | Low demand
33 | APR Energy , Keranigonj |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
34 | Bramhangoan 100 MW (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
35 | Aggreko Aurahati 100MW |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
36 | Summit Gazipur-1 150MW |  | IPP | 149 | 149 | 149 | 1673280
| Gazipur 100 MW |  | RPCL | 100 MW | 0 | 108 | 2264976 | on test
| Dhaka area Total |  |  |  | 5698 | 3728 | 67806139
37 | Chattogram ST-1 (Raozan) |  | PDB | 1*210 | 180 | 105 | 2500000 | Gas shortage
| Chittgong ST-2 (Raozan) |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
38 | Raozan 25 MW (RPCL) |  | IPP | 3*8.9 | 25 | 25 | 351178
39 | Teknaf Solartech 20MW |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 84105
40 | Patenga 50MW |  | IPP | 8*6.98 | 50 | 46 | 788640
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 38 | 780660 | Low water level
42 | Sikalbaha ST 60MW |  | PDB | 1*60 | 40 | 0 | 0 | Under maint.
43 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 211 | 5322241 | FGMO
44 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 110 | 2793076 | FGMO
45 | Sikalbaha (Energis) |  | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 16 | 389760 | Engine problem
| Baraka Sikalbaha PL |  | IPP | 105 MW | 0 | 106 | 1390030
46 | Hathazari peaking |  | PDB | 11*8.9 | 98 | 74 | 241352
47 | Dohazari Peaking |  | PDB | 6*17 | 102 | 85 | 449454
48 | Juldah (Acorn) |  | QRPP | 8*13.45 | 100 | 65 | 641760
49 | Juldah 100 MW Unit-3 |  | IPP | 0 | 100 | 100 | 1790400
50 | Barabkunda (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 16 | 350112 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 33 | 459840
51 | Chattogram ECPV 108 MW |  | IPP | 16*7 | 108 | 65 | 690240 | Line over load
| Kaptai Solar |  | PDB | 7.4 MW | 0 | 0 | 33996 | on test
| Anwara United |  | United Group | 300 MW | 0 | 100 | 3291920 | on test
| Chattogram area Total |  |  |  | 1681 | 1195 | 22348764
52 | Ashuganj ST: Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage
| Ashuganj ST: Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj ST: Unit- 5 |  | APSCL | 1*150 | 134 | 80 | 1923456 | Gas shortage
53 | Ashuganj CCPP 225 MW |  | APSCL | 1*142+1*75 | 221 | 183 | 4587000 | FGMO
54 | Ashuganj CCPP(North) |  | APSCL | 1*360 | 360 | 300 | 7759000 | Frequency control
55 | Ashuganj CCPP(South) |  | APSCL | 1*360 | 360 | 300 | 7277000 | Frequency control
56 | Ashuganj Engines TSK |  | APSCL | 14*3.968 | 45 | 33 | 610848 | Engine problem
57 | Ashuganj (Precision) 55MW |  | RPP | 15*4 | 55 | 30 | 442560 | Gas shortage
58 | Ashuganj (United) 53MW |  | QRPP | 14*4 | 53 | 5 | 120000 | Gas shortage
59 | Ashuganj 195MW Modular |  | IPP | 20*9.73+1*16 | 195 | 8 | 200727 | Gas shortage
60 | Ashuganj (Midland) 51MW |  | IPP | 6*9.34 | 51 | 35 | 591226 | Engine problem
61 | Midland 150MW |  | IPP | 23*7.015 | 150 | 148 | 1420145
62 | B.Baria (Aggreko) 85MW |  | QRPP | 86*1.10 | 85 | 0 | 0 | Contract Expired
63 | Daudkandi Peaking 52MW |  | PDB | 6*8.92 | 52 | 0 | 87624
64 | Chandpur CCPP |  | PDB | 1*106+1*57 | 163 | 100 | 2182060
65 | Chandpur Desh 200MW |  | IPP | 0 | 200 | 200 | 2053000
66 | Feni (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 22 | 442404
67 | Feni, Mohipal (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 194400 | Engine problem
** | Tripura |  | Imported power | 0 | 160 | 176 | 3464640
68 | Jangalia (Summit) 33MW |  | SIPP, PDB | 4*8.73 | 33 | 33 | 702800
69 | Lakdhanvi 52 MW |  | IPP | 6*8.92 | 52 | 52 | 563155
70 | Summit Cumilla 25MW |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 20 | 431510 | Engine problem
71 | Daudkandi bangla trak |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Cumilla Area Total |  |  |  | 2891 | 1733 | 35053555
72 | Mymensingh RPCL 210MW |  | IPP | 4*35+1*70 | 202 | 150 | 3522600 | GT-3 Under maint
73 | Tangail (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 20 | 448812
74 | Jamalpur 95MW |  | IPP | 12*8.924 | 95 | 93 | 1328640
75 | Sarishabari (Solar) |  | IPP | 1*3 | 3 | 0 | 12350
76 | United Mymensingh PPL |  | IPP | 200 | 200 | 160 | 871200 | Low demand
77 | United Jamalpur PPL |  | IPP | 115 MW | 115 | 98 | 2040000 | Low demand
| Mymensingh Area Total |  |  |  | 637 | 521 | 8223602
78 | Fenchugonj CCPP-1 |  | PDB | 2*32+1*33 | 70 | 58 | 1357000
79 | Fenchugonj CCPP-2 |  | PDB | 2*35+1*35 | 90 | 58 | 1218240
80 | Kushiara 163 MW CCPP GT |  | IPP | 1*109+1*54 | 163 | 163 | 3254040
81 | Shajibazar 330 MW |  | PDB | 3*110 | 330 | 275 | 6541000
82 | Fenchugonj (Barakatullah) 51MW |  | RPP | 19*2.90 | 51 | 53 | 944400
83 | Fenchuganj (EPL) 44MW |  | RPP | 12*3.3+5*2 | 44 | 47 | 877000
84 | Hobiganj 11MW |  | SIPP, REB | 4*2.90 | 11 | 11 | 231984
85 | Shahjibazar GT: Unit- 8, 9 |  | PDB | 2*35 | 66 | 40 | 1311000 | FGMO
86 | Shahjibazar 86MW |  | RPP | 32*2.90 | 86 | 83 | 1498560
87 | Shahjibazar (EPL) 50MW |  | RPP | 27*2.0 | 50 | 46 | 938520
88 | Sylhet GT 150 MW |  | PDB | 1*142 | 142 | 110 | 1056550 | Frequency control
89 | Sylhet GT 20 MW |  | PDB | 1*20 | 20 | 19 | 372000
90 | Sylhet (EPL) 50MW |  | RPP | 27*2 | 50 | 47 | 899760
91 | Shahjahanulla 25 MW |  | SIPP, REB | 3*9.34 | 25 | 24 | 509712
92 | Summit Bibiana- 2 |  | IPP | 1*222+1*119 | 341 | 240 | 6536500 | FGMO
| Bibiyana-3 285 MW |  | PDB | 285 MW | 0 | 220 | 5256000 | On test
93 | Sylhet (Desh) 10MW |  | RPP | 6*1.95 | 10 | 10 | 195660
| Sylhet Area Total |  |  |  | 1549 | 1504 | 32997926
94 | Bheramara GT-1,2,3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 941 | 22557818
| Khulna (KPCL-1 & 3) |  | IPP | 19*6.5 | 0 | 0 | 0 | Contract Expired
95 | Khulna (KPCL-2) |  | QRPP | 7*17 | 115 | 115 | 642240
96 | Faridpur Peaking |  | PDB | 8*6.89 | 54 | 32 | 199680
97 | Khulna CCPP 225MW |  | NWPGCL | 1*150+1*75 | 230 | 224 | 3471360
98 | Gopalganj Peaking |  | PDB | 16*6.98 | 109 | 55 | 342784
99 | Bheramara 360 MW |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Under maint.
100 | Noapara (KZA) 40MW |  | QRPP | 5*8.5 | 40 | 40 | 262125
0 | Khulna (Aggreeco) 55MW |  | QRPP | 71*0.85 | 0 | 0 | 0 | Contract Expired
101 | Bangla Trak Noapara |  | IPP | 70*1.4 | 100 | 94 | 382080
102 | Labon Chora 105 MW |  | IPP | 6*18.445 | 105 | 105 | 1043520
103 | Madhumati Power Plant |  | IPP | 100 MW | 105 | 89 | 1050480 | Engine problem
| Khulna Area Total |  |  |  | 2314 | 1695 | 29952087
104 | Summit Barisal 110 MW |  | IPP | 7*17.076 | 110 | 110 | 632640
105 | Barisal GT: Unit-1, 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
106 | Bhola (Venture) 33MW |  | RPP | 1*34.50 | 33 | 39 | 752744
107 | Bhola CCPP 194MW |  | PDB | 2*63+1*68 | 194 | 173 | 4291060 | FGMO
108 | Bhola Aggreko 95MW |  | QRPP | 96*1.10 | 95 | 97 | 1739361
| Barisal Area Total |  |  |  | 462 | 419 | 7415805
109 | Baghabari GT 71MW |  | PDB | 1*71 | 71 | 60 | 1392000
| Baghabari GT 100MW |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
110 | Baghabari Peaking 50MW |  | PDB | 6*8.9 | 52 | 50 | 278520
111 | Bera Peaking |  | PDB | 9*8.29 | 71 | 32 | 156360
112 | Amnura 50MW |  | QRPP | 7*7.79 | 50 | 50 | 384020
113 | Katakhali (Northern) |  | QRPP | 6*8.9 | 50 | 43 | 211581 | Engine problem
114 | Katakhali Peaking |  | PDB | 6*8.7 | 50 | 44 | 202248
115 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 195 | 4815836 | FGMO
116 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 30 | 4214591 | Synchonized at 20:22
117 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 184 | 4850445 | FGMO
118 | Sirajgonj Unit-4 414 MW(Gas) |  | SNWPGCL | 1*282+1*132 | 414 | 414 | 8365730
119 | Santahar Peaking |  | PDB | 6*8.7 | 50 | 35 | 191636
120 | Bogra (GBB) |  | RPP | 6*4 | 22 | 22 | 510480
121 | Bogra (EPL) |  | RPP | 5*3.3+5*2 | 10 | 16 | 370116
122 | Ullapara (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 199152
123 | Rajlanka 52 MW |  | IPP | 6*8.92 | 52 | 52 | 372000
124 | Chapainawabganj-100 MW |  | PDB | 12*8.924 | 104 | 95 | 1248208
125 | Paramount Baghabari |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
126 | Confidence CPBL-2 |  | IPP | 113 MW | 113 | 90 | 1269696
| Rajshahi Area Total |  |  |  | 2070 | 1423 | 29032619
107 | Barapukuria Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under overhauling
| Barapukuria Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
108 | Barapukuria Unit-3 |  | PDB | 1*275 | 274 | 149 | 3664200
129 | Rangpur GT |  | PDB | 1*20 | 20 | 17 | 69000
130 | Saidpur GT |  | PDB | 1*20 | 20 | 15 | 84000
| Rangpur Area Total |  |  |  | 484 | 181 | 3817200
| Total |  |  |  | 17786 | 12399 | 236647697
| Eastern Grid Total |  |  |  | 12456 | 8681 | 166429986
| Western Grid Total |  |  |  | 5330 | 3718 | 70217711
| National Grid Total |  |  |  | 17786 | 12399 | 236647697
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date: | 2019-05-26
| (a) ENTIRE EASTERN GRID : |  | 8066 | MW | (b) ENTIRE WESTERN GRID : |  | 3720 | MW
| i) Dhaka area |  | 4346 | MW | i) Khulna area |  | 1508 | MW
| ii) Chittagong area |  | 1192 | MW | ii) Rajshahi area |  | 1262 | MW
| iii) Comilla area |  | 1171 | MW | iii) Barisal area |  | 310 | MW
| iv) Mymensingh area |  | 908 | MW | iv) Rangpur area |  | 640 | MW
| v) Sylhet area |  | 449 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 11786 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
SL NO | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
1 | Siddhirganj | 124 | 2100 | Jamalpur | 128 | 2200 | Jessore | 121 | 2100
2 | Munsiganj | 123 | 2300 | Sherpur | 98 | 2300 | Jhenida | 119 | 2200
3 | Sonargaon | 68 | 2100 | Srimongal | 33 | 2100 | Bottail | 130 | 1930
4 | Shyampur | 192 | 2400 | Shahjibazar | 121 | 2200 | G.K Project | 58 | 2200
5 | Bhulta | 212 | 2300 | Fenchuganj | 43 | 1900 | Faridpur | 180 | 2200
6 | Madanganj | 58 | 2300 | Kulawara | 37 | 2100 | Madaripur | 123 | 2100
7 | Shitalakhya | 111 | 1600 | Sylhet | 131 | 2100 | Gopalganj | 99 | 2200
8 | Rahim steel | 13 | 1100 | Chatak | 32 | 2100 | Bagerhat | 90 | 1900
9 | Matuail | 96 | 2400 | Sunamganj | 35 | 2100 | Mongla | 40 | 1200
10 | Ghorasal | 85 | 2100 | Biani Bazar | 43 | 2100 | Satkhira | 104 | 2200
11 | Narsingdi | 136 | 2100 | Comilla (S) | 182 | 2400 | Gallamari | 53 | 2300
12 | Haripur (SBU) | 107 | 1100 | Comilla(N) | 149 | 2000 | Magura | 56 | 2000
13 | Ullon | 93 | 1930 | Chandpur | 108 | 2000 | Chuadanga | 90 | 2000
14 | Hasnabad | 230 | 1930 | Feni | 144 | 2100 | Barisal | 104 | 1930
15 | Magbazar | 125 | 1930 | Chowmuhani | 186 | 2100 | Patuakhali | 116 | 2100
16 | Maniknagar | 112 | 1300 | Ashuganj | 49 | 2100 | Bhandaria | 108 | 1930
17 | Bangabhaban | 34 | 1100 | Daudkandi | 144 | 2200 | Barisal (N) | 44 | 2100
18 | Narinda | 98 | 1300 | B.Baria | 149 | 2100 | Sariatpur | 39 | 2100
19 | Dhanmondi | 184 | 1300 | Ramganj | 96 | 2100 | Benapol | 44 | 2100
20 | Lalbag | 82 | 1700 | Madunaghat | 62 | 2100 | Ishurdi | 67 | 1930
21 | Madartek | 62 | 2000 | Hathazari | 101 | 2100 | Ruppur Paromanobik | 1 | 100
22 | Mirpur | 116 | 1930 | Khulshi | 224 | 2400 | Natore | 136 | 2000
23 | Kalyanpur | 123 | 1930 | Halishahar | 144 | 1400 | Bogra | 239 | 1930
24 | Gulshan | 158 | 1200 | Baraulia | 161 | 2400 | Noagaon | 122 | 2000
25 | Uttara | 88 | 1930 | Sikalbaha | 41 | 2100 | Rajshahi | 161 | 1900
26 | Uttara New | 19 | 1200 | Dohazari | 90 | 1900 | C.Nawabganj | 78 | 2000
27 | Kamrangirchar | 73 | 1930 | Cox'sbazar | 93 | 2000 | Amnura | 36 | 1930
28 | Savar | 148 | 1600 | Chandraghona | 28 | 1900 | Pabna | 123 | 2000
29 | Bhasantec | 176 | 1930 | Kaptai | 4 | 1930 | Shahjadpur | 81 | 2000
30 | Agargaon | 58 | 1900 | A. Khaer Stl. | 0 | 0 | Serajganj | 109 | 2000
31 | Satmosjid | 117 | 1930 | Bakulia | 108 | 2100 | Niyamatpur | 64 | 2000
32 | Tongi | 153 | 2100 | Julda | 21 | 2400 | Joypurhat | 51 | 1930
33 | Kabirpur | 205 | 1000 | TK chemical | 4 | 1300 | Mohastangor | 24 | 1930
34 | Basundhara | 138 | 2100 | Modern Steel | 14 | 200 | Rangpur | 133 | 2000
35 | Manikganj | 102 | 2200 | Shahmirpur | 30 | 1500 | Lalmonirhat | 91 | 1900
36 | Joydevpur | 238 | 2000 | Khagrachhari | 18 | 1830 | Saidpur | 103 | 1930
37 | New Tongi | 106 | 1400 | Matarbari | 29 | 2200 | Purbasadipur | 100 | 2000
38 | Korda | 263 | 1200 | Baroiar Hat | 30 | 2200 | Thakurgaon | 70 | 2000
39 | Dhamrai | 59 | 2000 | Rangamati | 12 | 1900 | Palashbari | 110 | 1930
40 | Valuka | 102 | 1930 | Abul Khair 230 | 123 | 2400 | Barapukuria | 51 | 1930
41 | Tangail | 196 | 2300 | BSRM | 139 | 100 | Panchagar | 42 | 2000
42 | Mymensing | 219 | 2200 | Goalpara | 30 | 2000 | Joldhaka | 17 | 2000
43 | Kishorganj | 130 | 1930 | Central (S) | 99 | 2000
44 | Netrokona | 93 | 2100 | Noapara | 108 | 2100
| Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  | (24) Director,System Planning,PDB.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2019-05-26
| Sub-Station | Max Voltage | Hour | Min | Hour |  | Sub-Station | Maxm | Hour
|  |  |  | Voltage |  |  |  | Voltage
SL NO | 400 KV | KV |  | KV |  | SL NO |  | KV
1 | Bibiyana | 387 | 24:00 | 373 | 15:00 | 4 | Kaliakoir | 368 | 5:00
2 | Bheramara | 396 | 6:00 | 387 | 23:00 | 5 | Bhulta | 383 | 4:00
3 | Ashuganj(N) | 388 | 4:00 | 373 | 11:00
SL NO | 230 KV | KV |  | KV |  | SL NO | 230 KV | KV
1 | Ghorasal | 230 | 1:00 | 225 | 15:00 | 15 | Hathazari | 218 | 6:00
2 | Ishurdi | 236 | 18:30 | 226 | 12:00 | 16 | Megnaghat | 222 | 19:30
3 | Ashuganj | 238 | 13:00 | 230 | 9:00 | 17 | Fenchuganj | 236 | 5:00
4 | Serajganj | 234 | 5:00 | 225 | 19:30 | 18 | Siddhirganj | 222 | 5:00
5 | Baghabari | 231 | 6:00 | 222 | 22:00 | 19 | Maniknagar | 220 | 5:00
6 | Barapukuria | 235 | 6:00 | 217 | 21:00 | 20 | Old Airport | 219 | 5:00
7 | Bogra | 229 | 5:00 | 211 | 20:00 | 21 | Barisal | 235 | 19:00
8 | Khulna South | 230 | 6:00 | 217 | 12:00 | 22 | AKSML | 217 | 6:00
9 | Rampura | 223 | 3:00 | 211 | 12:00 | 23 | BSRM | 218 | 5:00
10 | Haripur | 219 | 4:00 | 212 | 16:00 | 24 | Bibiyana | 230 | 1:00
11 | Hasnabad | 218 | 5:00 | 210 | 9:00 | 25 | Bhulta | 223 | 5:00
12 | Aminbazar | 219 | 5:00 | 209 | 12:00 | 26 | Ashuganj (S) | 233 | 5:00
13 | Tongi | 219 | 20:00 | 208 | 11:00 | 27 | Kaliakoir | 223 | 5:00
14 | Comilla (N) | 226 | 5:00 | 219 | 11:00
SL NO | 132 kV | KV |  | KV |  | SL NO | 132 kV | KV
1 | Siddhirganj | 132 | 2000 | 126 | 1200 | 65 | Hathazari | 129 | 100
2 | Munsiganj | 134 | 1900 | 124 | 1100 | 66 | Khulshi | 127 | 500
3 | Megnaghat | 131 | 500 | 124 | 1200 | 67 | Halishahar | 131 | 500
4 | Shyampur | 131 | 1900 | 123 | 1200 | 68 | Baraulia | 128 | 400
5 | Bhulta | 126 | 1830 | 120 | 700 | 69 | Sikalbaha | 130 | 100
6 | Madanganj | 131 | 1830 | 121 | 1100 | 70 | Dohazari | 127 | 500
7 | Shitalakhya | 137 | 1900 | 123 | 1500 | 71 | Cox'sbazar | 123 | 900
8 | Rahim steal | 132 | 1930 | 126 | 1100 | 72 | Chandraghona | 129 | 300
9 | Matuail | 132 | 1900 | 124 | 1100 | 73 | Kaptai | 130 | 700
10 | Ghorasal | 136 | 2000 | 132 | 1500 | 74 | A. Khaer Stl. | 128 | 100
11 | Narsinghdi | 130 | 500 | 122 | 2100 | 75 | Bakulia | 128 | 100
12 | Haripur (SBU) | 132 | 400 | 126 | 1100 | 76 | Julda | 130 | 2000
13 | Ullon | 133 | 100 | 124 | 1200 | 77 | TK Chemical | 130 | 100
14 | Hasnabad | 130 | 100 | 124 | 1200 | 78 | Modern Steel | 128 | 100
15 | Magbazar | 134 | 500 | 124 | 1500 | 79 | Shahmirpur | 130 | 1830
16 | Maniknagar | 134 | 500 | 126 | 1200 | 80 | Khagrachhari | 128 | 100
17 | Bangabhaban | 134 | 500 | 126 | 1200 | 81 | Matarbari | 125 | 600
18 | Narinda | 134 | 500 | 126 | 1200 | 82 | Baroiar Hat | 126 | 700
19 | Dhanmondi | 133 | 100 | 124 | 1200 | 83 | Rangamati | 129 | 600
20 | Lalbag | 132 | 1900 | 121 | 1200 | 84 | Goalpara | 138 | 1830
21 | Madartek | 135 | 600 | 124 | 1200 | 85 | Central s/s | 136 | 600
22 | Mirpur | 131 | 800 | 122 | 1500 | 86 | Noapara | 131 | 600
23 | Kalyanpur | 133 | 500 | 124 | 1200 | 87 | Jessore | 130 | 600
24 | Gulshan | 133 | 400 | 124 | 1600 | 88 | Jhenida | 128 | 600
25 | Uttara | 129 | 400 | 120 | 1100 | 89 | Bottail | 135 | 600
26 | Uttara New | 130 | 100 | 122 | 1200 | 90 | G.K.Project | 142 | 500
27 | Kamrangirchar | 131 | 600 | 122 | 1200 | 91 | Faridpur | 131 | 1830
28 | Savar | 130 | 400 | 121 | 1000 | 92 | Madaripur | 134 | 1800
29 | Bhasantec | 135 | 600 | 124 | 1100 | 93 | Gopalganj | 140 | 1800
30 | Agargaon | 136 | 500 | 126 | 1600 | 94 | Bagerhat | 130 | 1830
31 | Satmosjid | 136 | 500 | 126 | 1100 | 95 | Mongla | 132 | 1830
32 | Tongi | 134 | 2100 | 127 | 1100 | 96 | Satkhira | 134 | 600
33 | Kabirpur | 130 | 1900 | 124 | 1400 | 97 | Gallamari | 136 | 500
34 | Basundhara | 130 | 100 | 120 | 1300 | 98 | Magura | 130 | 500
35 | Manikganj | 137 | 2400 | 126 | 800 | 99 | Chuadanga | 127 | 600
36 | Joydevpur | 137 | 2000 | 127 | 1700 | 100 | Barisal | 132 | 1830
37 | New Tongi | 133 | 2000 | 125 | 900 | 101 | Patuakhali | 133 | 1700
38 | Kodda | 136 | 2100 | 120 | 900 | 102 | Bhandaria | 135 | 1800
39 | Dhamrai | 132 | 600 | 125 | 1300 | 103 | Barisal (N) | 137 | 2000
40 | Valuka | 130 | 700 | 120 | 1930 | 104 | Sariatpur | 132 | 1800
41 | Tangail | 132 | 500 | 123 | 1500 | 105 | Benapol | 129 | 500
42 | Mymensing | 131 | 800 | 117 | 2200 | 106 | Ishurdi | 140 | 1600
43 | Kishorganj | 130 | 700 | 122 | 2100 | 107 | Ruppur Paromanobik | 139 | 500
44 | Netrokona | 132 | 800 | 119 | 2100 | 108 | Natore | 135 | 700
45 | Jamalpur | 138 | 1930 | 123 | 300 | 109 | Bogra | 136 | 500
46 | Sherpur | 136 | 1930 | 123 | 300 | 110 | Noagaon | 133 | 600
47 | Srimongal | 135 | 100 | 131 | 2200 | 111 | Rajshahi | 133 | 500
48 | Shahjibazar | 134 | 500 | 130 | 1900 | 112 | C.Nawabganj | 132 | 1830
49 | Fenchuganj | 134 | 400 | 131 | 1300 | 113 | Amnura | 134 | 500
50 | Khulawara | 133 | 400 | 130 | 2200 | 114 | Pabna | 138 | 600
51 | Sylhet | 133 | 1700 | 129 | 900 | 115 | Shahjadpur | 141 | 500
52 | Chatak | 133 | 1800 | 129 | 700 | 116 | Serajganj | 136 | 600
53 | Sunamganj | 132 | 1700 | 127 | 1200 | 117 | Niyamatpur | 131 | 600
54 | Biani Bazar | 132 | 1600 | 128 | 2200 | 118 | Joypurhat | 133 | 500
55 | Comilla(s) | 128 | 500 | 122 | 1000 | 119 | Mohastangor | 134 | 500
56 | Comilla(n) | 132 | 700 | 127 | 1100 | 120 | Rangpur | 130 | 500
57 | Chandpur | 127 | 700 | 124 | 1100 | 121 | Lalmonirhat | 130 | 400
58 | Feni | 126 | 800 | 120 | 2400 | 122 | Saidpur | 131 | 500
59 | Chowmuhani | 124 | 700 | 115 | 1000 | 123 | Purbasadipur | 130 | 500
60 | Ashuganj | 136 | 800 | 132 | 1900 | 124 | Thakurgaon | 124 | 600
61 | Daudkandi | 129 | 700 | 122 | 1100 | 125 | Palashbari | 133 | 500
62 | B.Baria | 132 | 600 | 126 | 2200 | 126 | Barapukuria | 135 | 600

## L-Curve
Date | 2019-05-26
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 30 | 8125 | 3876 | 12001 |  |  |  | QF-LDC-12
0:30 | 75 | 7322.5 | 3305 | 10627.5 | Date: | 2019-05-26
1:00 | 120 | 6520 | 2734 | 9254
1:30 | 140 | 6437.5 | 2703.5 | 9141
2:00 | 160 | 6355 | 2673 | 9028
2:30 | 160 | 6318.5 | 2683.5 | 9002 | [5 empty] | Gen. at Eve. Peak | 12399 | 12399 MW (21:00 )
3:00 | 160 | 6282 | 2694 | 8976 | [6 empty] | 21:00
3:30 | 90 | 6119.5 | 2655.5 | 8775 | [5 empty] | Gen. at Day Peak | 9611.25 | 9611.25 MW (12:00 )
4:00 | 20 | 5957 | 2617 | 8574 | [6 empty] | 12:00
4:30 | 95 | 5681 | 2537 | 8218 | [5 empty] | Highest Generation | 12399
5:00 | 170 | 5405 | 2457 | 7862 | [6 empty] | 21:00
5:30 | 210 | 5201.19 | 2380 | 7581.19
6:00 | 250 | 4997.38 | 2303 | 7300.38
6:30 | 275 | 5020.41 | 2312 | 7332.41
7:00 | 300 | 5043.44 | 2321 | 7364.44
7:30 | 310 | 5124.43 | 2344 | 7468.43
8:00 | 320 | 5205.42 | 2367 | 7572.42
8:30 | 350 | 5542.175 | 2436.5 | 7978.675
9:00 | 380 | 5878.93 | 2506 | 8384.93
9:30 | 365 | 6134.6695 | 2548 | 8682.6695
10:00 | 350 | 6390.409 | 2590 | 8980.409
10:30 | 290 | 6471.9545 | 2588 | 9059.9545
11:00 | 230 | 6553.5 | 2586 | 9139.5
11:30 | 185 | 6760.375 | 2615 | 9375.375
12:00 | 140 | 6967.25 | 2644 | 9611.25
12:30 | 100 | 6982.215 | 2683 | 9665.215
13:00 | 60 | 6997.18 | 2722 | 9719.18
13:30 | 105 | 7212.14 | 2762 | 9974.14
14:00 | 150 | 7427.1 | 2802 | 10229.1
14:30 | 155 | 7518.5 | 2851 | 10369.5
15:00 | 160 | 7609.9 | 2900 | 10509.9
15:30 | 195 | 7570.1 | 2849.5 | 10419.6
16:00 | 230 | 7530.3 | 2799 | 10329.3
16:30 | 170 | 7503.25 | 2804 | 10307.25
17:00 | 110 | 7476.2 | 2809 | 10285.2
17:30 | 160 | 7304.2 | 2794.5 | 10098.7
18:00 | 210 | 7132.2 | 2780 | 9912.2
18:30 | 260 | 7283.6 | 3030 | 10313.6
19:00 | 310 | 7435 | 3280 | 10715
19:30 | 420 | 8606 | 3443 | 12049
20:00 | 440 | 8606 | 3485 | 12091 |  |  |  | Executive Engineer
20:30 | 350 | 8643.5 | 3601.5 | 12245 |  |  |  | Network Operation Division
21:00 | 260 | 8681 | 3718 | 12399
21:30 | 175 | 8544.5 | 3805.5 | 12350
22:00 | 90 | 8408 | 3893 | 12301 |  |  |  |  | Page 6 of 7
22:30 | 60 | 8307 | 3905 | 12212
23:00 | 30 | 8206 | 3917 | 12123
23:30 | 30 | 8165.5 | 3896.5 | 12062
24:00 | 30 | 8125 | 3876 | 12001
12399 MW (21:00 )
9611.25 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2019-05-26 |  | Energy | 236647697
[10 empty] | 2019-05-26 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 4654 | 940 | 2166 | 3143 | 149 | 37 | 730 | 0 | 182
0:30 | 4532.5 | 940.5 | 2125.5 | 2216 | 149 | 37 | 469 | 0 | 158 | Date: | 2019-05-26
1:00 | 4411 | 941 | 2085 | 1289 | 149 | 37 | 208 | 0 | 134
1:30 | 4418.5 | 941.5 | 2080.5 | 1190 | 149 | 37 | 191.5 | 0 | 133 | [7 empty] | Total Energy | 236.6477 | Total Energy Gen 236.648 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 236.648 MKWHr
2:00 | 4426 | 942 | 2076 | 1091 | 149 | 37 | 175 | 0 | 132 | [7 empty] | Energy not Served | 0
2:30 | 4464.5 | 941.5 | 2051 | 1050 | 149 | 37 | 175 | 0 | 134 | [7 empty] | Energy Requirement | 236.6477
3:00 | 4503 | 941 | 2026 | 1009 | 149 | 37 | 175 | 0 | 136
3:30 | 4467 | 939 | 1945 | 930.5 | 149 | 37.5 | 175 | 0 | 132 | [6 empty] | Shortage
4:00 | 4431 | 937 | 1864 | 852 | 149 | 38 | 175 | 0 | 128
4:30 | 4306.5 | 936.5 | 1681 | 811 | 149 | 38 | 175 | 0 | 121
5:00 | 4182 | 936 | 1498 | 770 | 149 | 38 | 175 | 0 | 114
5:30 | 4026 | 936 | 1467.5 | 692.5 | 149 | 37.5 | 160 | 0 | 112
6:00 | 3870 | 936 | 1437 | 615 | 149 | 37 | 145 | 0 | 110
6:30 | 3886 | 936 | 1443.5 | 623 | 149 | 37 | 145 | 0 | 109 |  |  |  |  | Coal
7:00 | 3902 | 936 | 1450 | 631 | 149 | 37 | 145 | 0 | 108
7:30 | 3949 | 936.5 | 1447 | 681.5 | 149 | 37 | 144.5 | 0 | 113 |  |  |  | Oil |  |  |  | ,
8:00 | 3996 | 937 | 1444 | 732 | 149 | 37 | 144 | 0 | 118
8:30 | 4163.5 | 937.5 | 1633.5 | 784.5 | 149 | 36 | 144 | 0 | 121
9:00 | 4331 | 938 | 1823 | 837 | 149 | 35 | 144 | 0 | 124
9:30 | 4440 | 938 | 1969.5 | 873 | 149 | 35 | 144 | 0 | 129
10:00 | 4549 | 938 | 2116 | 909 | 149 | 35 | 144 | 0 | 134
10:30 | 4549 | 938 | 2149 | 950 | 149 | 32.5 | 144 | 0 | 137
11:00 | 4549 | 938 | 2182 | 991 | 149 | 30 | 144 | 0 | 140
11:30 | 4702 | 938 | 2242 | 1011 | 149 | 30 | 144 | 0 | 141
12:00 | 4855 | 938 | 2302 | 1031 | 149 | 30 | 144 | 0 | 142
12:30 | 4717.5 | 938 | 2229.5 | 1287 | 149 | 32.5 | 144 | 0 | 149
13:00 | 4580 | 938 | 2157 | 1543 | 149 | 35 | 144 | 0 | 156
13:30 | 4580 | 938 | 2157 | 1543 | 149 | 35 | 144 | 0 | 156
14:00 | 4580 | 938 | 2157 | 1543 | 149 | 35 | 144 | 0 | 156
14:30 | 4676 | 939.5 | 2174.5 | 1800.5 | 149 | 35 | 162 | 0 | 161
15:00 | 4772 | 941 | 2192 | 2058 | 149 | 35 | 180 | 0 | 166
15:30 | 4767 | 940.5 | 2170 | 1998 | 149.5 | 35 | 181 | 0 | 164
16:00 | 4762 | 940 | 2148 | 1938 | 150 | 35 | 182 | 0 | 162
16:30 | 4752.5 | 940 | 2128 | 1939 | 149.5 | 35 | 195.5 | 0 | 159
17:00 | 4743 | 940 | 2108 | 1940 | 149 | 35 | 209 | 0 | 156
17:30 | 4631.5 | 940.5 | 1940.5 | 2008 | 149 | 35 | 237.5 | 0 | 154
18:00 | 4520 | 941 | 1773 | 2076 | 149 | 35 | 266 | 0 | 152
18:30 | 4377.5 | 941 | 1726.5 | 2422 | 149 | 35 | 501.5 | 0 | 161
19:00 | 4235 | 941 | 1680 | 2768 | 149 | 35 | 737 | 0 | 170
19:30 | 4440 | 940 | 2113 | 3354 | 149 | 38 | 843 | 0 | 172
20:00 | 4372 | 941 | 2043 | 3452 | 149 | 38 | 922 | 0 | 174
20:30 | 4364.5 | 941 | 2121 | 3542 | 149 | 38 | 914.5 | 0 | 175
21:00 | 4357 | 941 | 2199 | 3632 | 149 | 38 | 907 | 0 | 176
21:30 | 4447 | 940.5 | 2194.5 | 3505 | 149 | 38 | 903 | 0 | 173
22:00 | 4537 | 940 | 2190 | 3378 | 149 | 38 | 899 | 0 | 170
22:30 | 4625.5 | 940.5 | 2155.5 | 3293.5 | 149 | 37.5 | 845.5 | 0 | 165
23:00 | 4714 | 941 | 2121 | 3209 | 149 | 37 | 792 | 0 | 160
23:30 | 4684 | 940.5 | 2143.5 | 3176 | 149 | 37 | 761 | 0 | 171 | Max Temp. in Dhaka |  | 35.1° C
24:00 | 4654 | 940 | 2166 | 3143 | 149 | 37 | 730 | 0 | 182
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 236.648 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 236.648 MKWHr
Note on W13: Author:

## Generation
2019-05-26
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Kaptai Unit-1, 2 & 3 | 37 | 37 | 37 | 38 | 38 | 37 | 37 | 37 | 35 | 35 | 30 | 30 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 38 | 38 | 38 | 38 | 37 | 37 | 780660
2 | Kaptai Unit-4 & 5
3 | Chattogram ST-1 (Raozan) | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 105 | 90 | 90 | 90 | 90 | 100 | 100 | 100 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2500000
4 | Chittgong ST-2 (Raozan)
5 | Raozan 25 MW (RPCL) | 25 | 8 | 8 | 8 | 0 | [6 empty] | 0 | 8 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 26 | 25 | 25 | 351178
| Teknaf Solartech 20MW |  |  |  |  | 0 | 1.38 | 5.17 | 11.66 | 0 | 0 | 11.41 | 14.89 | 10.74 | 16.3 | 12.4 | 8.9 | 3.8 | 0 | [8 empty] | 84105
6 | Sikalbaha 225MW (Gas) | 231 | 231 | 231 | 228 | 229 | 227 | 225 | 219 | 223 | 230 | 230 | 230 | 228 | 223 | 230 | 230 | 226 | 209 |  | 228 | 211 | 211 | 211 | 230 | 215 | 203 | 5322241
7 | Sikalbaha 225MW (Oil)
8 | Sikalbaha ST 60MW
9 | Sikalbaha GT 150MW (Gas) | 130 | 130 | 130 | 130 | 130 | 85 | 85 | 85 | 140 | 140 | 145 | 147 | 145 | 145 | 110 | 110 | 110 | 110 |  | 80 | 145 | 110 | 110 | 90 | 110 | 90 | 2793076
10 | Sikalbaha GT 150MW (Oil)
| Dohazari Peaking | 17 | 0 | [15 empty] | 0 |  | 70 | 85 | 85 | 85 | 85 | 66 | 51 | 449454
12 | Hathazari peaking | [17 empty] | 0 |  | 42 | 74 | 74 | 74 | 74 | 0 | 0 | 241352
| Baraka Sikalbaha PL | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 36 | 38 | 83 | 103 | 110 | 107 |  | 107 | 107 | 107 | 106 | 109 | 109 | 109 | 1390030
Daudkandi bangla trak
14 | Daudkandi Peaking 52MW | [17 empty] | 0 |  | 36 | 50 | 50 | 0 | 0 |  |  | 87624
15 | Siddhirgonj ST 210MW
16 | Siddhirgonj GT Unit-1& 2 | 127 | 130 | 130 | 130 | 75 | 75 | 78 | 78 | 120 | 120 | 120 | 175 | 180 | 180 | 177 | 175 | 145 | 145 |  | 60 | 95 | 87 | 87 | 95 | 96 | 97 | 3077000
17 | Siddhirganj CCPP-335 MW
18 | Summit Gazipur -2 | [16 empty] | 0 | 3 |  | 68 | 190 | 194 | 200 | 109 | 0 | 0 | 674950
19 | Ashuganj 195MW Modular | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 200727
20 | Ghorasal ST: Unit-1,2 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 736000
21 | Ghorasal GT: Unit-3 | 134 | 133 | 134 | 134 | 64 | 63 | 63 | 63 | 94 | 94 | 94 | 113 | 113 | 94 | 94 | 94 | 94 | 94 |  | 94 | 94 | 94 | 94 | 94 | 96 | 94 | 2473800
22 | Ghorasal GT: Unit-4 | [9 empty] | 70 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1377000
23 | Ghorasal ST: Unit-5 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 100 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2835000
24
25 | Ghorasal ST: Unit-7 | 320 | 320 | 330 | 330 | 280 | 280 | 280 | 280 | 330 | 360 | 360 | 360 | 280 | 320 | 320 | 320 | 320 | 300 |  | 260 | 320 | 320 | 320 | 320 | 320 | 320 | 7652063
26
28 | Ashuganj ST: Unit- 3
29 | Ashuganj ST: Unit- 4
30 | Ashuganj ST: Unit- 5 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1923456
32 | Ashuganj Engines TSK | 30 | 30 | 30 | 30 | 26 | 10 | 10 | 10 | 23 | 27 | 27 | 27 | 27 | 27 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 33 | 33 | 33 | 33 | 610848
33 | Ashuganj CCPP 225 MW | 183 | 183 | 196 | 184 | 183 | 183 | 196 | 206 | 196 | 184 | 192 | 183 | 184 | 186 | 184 | 184 | 184 | 184 |  | 193 | 191 | 184 | 183 | 183 | 200 | 193 | 4587000
34 | Ashuganj CCPP(South) | 280 | 280 | 280 | 280 | 280 | 250 | 250 | 250 | 280 | 280 | 280 | 353 | 300 | 340 | 355 | 350 | 360 | 320 |  | 280 | 320 | 320 | 300 | 300 | 300 | 300 | 7277000
| Ashuganj CCPP(North) | 300 | 300 | 300 | 300 | 300 | 250 | 250 | 250 | 280 | 320 | 360 | 360 | 300 | 360 | 360 | 360 | 360 | 320 |  | 280 | 300 | 300 | 300 | 300 | 300 | 300 | 7759000
35 | Ashuganj (Precision) 55MW | 25 | 25 | 25 | 25 | 25 | 25 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 30 | 30 | 30 | 30 | 442560
36 | Chandpur CCPP | 100 | 100 | 100 | 100 | 100 | 50 | 50 | 50 | 50 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2182060
37 | Tongi GT | [24 empty] | 40 | 40 | 65678
38 | Haripur GT: Unit-1, 2
39 | Haripur 412 MW CCPP | 326 | 326 | 345 | 337 | 327 | 326 | 326 | 344 | 362 | 333 | 341 | 352 | 327 | 340 | 327 | 327 | 328 | 327 |  | 327 | 330 | 345 | 327 | 328 | 330 | 340 | 8147190
40 | Meghnaghat CCPP 450MW | 340 | 340 | 340 | 340 | 310 | 310 | 310 | 310 | 340 | 380 | 420 | 450 | 450 | 450 | 450 | 450 | 400 | 360 |  | 330 | 430 | 400 | 400 | 400 | 370 | 400 | 8838750
41 | Haripur Power CCPP 360MW | 335 | 333 | 304 | 295 | 275 | 276 | 277 | 274 | 323 | 323 | 345 | 345 | 341 | 340 | 341 | 341 | 344 | 322 |  | 283 | 353 | 349 | 349 | 354 | 312 | 312 | 7615000
42 | Mymensingh RPCL 210MW | 152 | 152 | 152 | 155 | 154 | 154 | 152 | 152 | 149 | 149 | 149 | 149 | 147 | 147 | 145 | 147 | 147 | 148 |  | 147 | 150 | 150 | 150 | 149 | 150 | 149 | 3522600
43 | Haripur NEPC 110MW | [16 empty] | 0 | 13 |  | 40 | 70 | 83 | 98 | 55 | 0 | 0 | 276200
44 | Fenchugonj CCPP-1 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 55 | 56 | 56 | 56 | 60 |  | 60 | 60 | 58 | 58 | 58 | 58 | 57 | 1357000
45 | Fenchugonj CCPP-2 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 58 | 58 | 58 | 58 | 58 | 58 | 1218240
46 | Shajibazar 330 MW | 304 | 304 | 306 | 308 | 309 | 309 | 308 | 312 | 306 | 307 | 236 | 301 | 296 | 286 | 289 | 292 | 290 | 276 |  | 277 | 270 | 275 | 275 | 250 | 252 | 249 | 6541000
47 | Shahjibazar GT: Unit- 8, 9 | 55 | 64 | 65 | 50 | 54 | 40 | 50 | 63 | 63 | 60 | 61 | 61 | 52 | 59 | 61 | 61 | 63 | 50 |  | 65 | 63 | 60 | 40 | 64 | 63 | 63 | 1311000
48 | Shahjibazar 86MW | 82 | 82 | 82 | 40 | 10 | 10 | 10 | 10 | 10 | 55 | 50 | 78 | 77 | 75 | 77 | 77 | 78 | 40 |  | 10 | 82 | 84 | 83 | 84 | 84 | 81 | 1498560
49 | Shahjibazar (EPL) 50MW | 46 | 46 | 46 | 46 | 10 | 10 | 10 | 10 | 44 | 45 | 45 | 43 | 44 | 44 | 44 | 44 | 46 | 46 |  | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 938520
50 | Sylhet GT 150 MW | [13 empty] | 88 | 83 | 83 | 85 | 83 |  | 97 | 110 | 110 | 110 | 110 | 127 | 116 | 1056550
51 | Sylhet GT 20 MW | 19 | 19 | 19 | 19 | 19 | 0 |  |  |  | 18 | 18 | 18 | 18 | 18 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 372000
52 | Sylhet (EPL) 50MW | 45 | 45 | 45 | 10 | 10 | 10 | 12 | 12 | 44 | 39 | 43 | 40 | 40 | 43 | 41 | 46 | 43 | 30 |  | 49 | 50 | 47 | 47 | 45 | 46 | 46 | 899760
53 | Sylhet (Desh) 10MW | 10 | 10 | 10 | 10 | 10 | 0 |  |  | 0 | 9 | 9 | 9 | 9 | 9 | 9 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 195660
54 | Hobiganj 11MW | 11 | 11 | 11 | 11 | 0 | 5 | 8 | 8 | 8 | 10 | 10 | 10 | 10 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 231984
55 | Fenchugonj (Barakatullah) 51MW | 47 | 47 | 47 | 47 | 11 | 11 | 11 | 11 | 27 | 45 | 45 | 45 | 47 | 47 | 50 | 53 | 53 | 22 |  | 25 | 51 | 53 | 53 | 47 | 50 | 50 | 944400
56 | Shahjahanulla 25 MW | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 509712
57 | Summit Bibiana- 2 | 260 | 280 | 285 | 270 | 240 | 235 | 260 | 280 | 285 | 280 | 285 | 275 | 240 | 260 | 265 | 260 | 270 | 250 |  | 250 | 260 | 260 | 240 | 265 | 270 | 280 | 6536500
58 | Southern 55MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 35 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 722000
59 | Sikalbaha (Energis) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 389760
60 | Barabkunda (Regent) | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 16 | 16 | 16 | 15 | 15 | 15 |  | 16 | 16 | 16 | 16 | 16 | 16 | 15 | 350112
61 | Narshingdi (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 434160
62 | Tangail (Doreen) 22MW | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 448812
63 | Tripura | 134 | 132 | 136 | 128 | 114 | 110 | 108 | 118 | 124 | 134 | 140 | 142 | 156 | 158 | 166 | 162 | 156 | 152 |  | 170 | 172 | 174 | 176 | 170 | 160 | 182 | 3464640
64 | Malancha, Ctg. EPZ (United) | 38 | 38 | 40 | 40 | 40 | 28 | 15 | 2 | 2 | 2 | 2 | 2 | 8 | 8 | 3 | 7 | 3 | 4 |  | 32 | 30 | 24 | 33 | 33 | 37 | 36 | 459840
65 | Feni (Doreen) 22MW | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 19 | 19 | 21 | 21 | 21 | 21 | 21 |  | 0 | 0 | 12 | 22 | 22 | 22 | 0 | 442404
66 | Feni, Mohipal (Doreen) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 194400
67 | Jangalia (Summit) 33MW | 33 | 33 | 33 | 33 | 33 | 8 | 8 | 8 | 8 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 702800
68 | Summit Cumilla 25MW | 20 | 20 | 20 | 20 | 15 | 15 | 15 | 12 | 15 | 15 | 18 | 20 | 20 | 18 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 431510
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 32 | 32 | 25 | 25 | 28 | 28 | 31 | 31 | 27 | 29 | 29 | 29 | 31 | 31 | 31 | 31 | 31 | 31 |  | 10 | 18 | 28 | 31 | 31 | 32 | 32 | 676080
71 | Summit Maona | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 789100
72 | Summit Rupganj | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 16 | 16 | 16 | 25 |  | 25 | 25 | 25 | 17 | 25 | 25 | 25 | 687100
73 | Ghorashal (Regent) | 111 | 111 | 111 | 111 | 22 | 22 | 22 | 22 | 75 | 108 | 107 | 102 | 55 | 52 | 22 | 23 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 1280681
76 | Siddhirganj Desh
77 | Siddhirganj (Dutch Bangla) | [16 empty] | 0 | 3 |  | 20 | 50 | 68 | 70 | 7 | 0 |  | 189120
78 | Gazipur (RPCL) | 25 | 25 | 25 | 0 |  |  |  | 10 | 25 | 36 | 50 | 50 | 49 | 49 | 48 | 48 | 48 | 48 |  | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 849648
79 | Kodda 149MW | 16 | 0 | [14 empty] | 0 | 16 |  | 70 | 98 | 149 | 149 | 149 | 149 | 149 | 750720
80 | Jamalpur 95MW | 16 | 8 | 8 | 8 | 8 | 8 | 8 | 25 | 40 | 40 | 40 | 40 | 75 | 95 | 94 | 94 | 93 | 60 |  | 72 | 94 | 94 | 93 | 93 | 94 | 94 | 1328640
81 | Lakdhanvi 52 MW | [11 empty] | 0 | 16 | 25 | 43 | 52 | 52 | 52 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 563155
| Gazipur 100 MW | 108 | 108 | 72 | 55 | 54 | 36 | 36 | 70 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 |  | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 2264976
| Kaptai Solar | [5 empty] | 0 | 0.97 | 2.8 | 3.83 | 5.109 | 3.75 | 3.56 | 5.54 | 4.1 | 3.8 | 2.4 | 0.9 | 0.1 | [8 empty] | 33996
82 | Madanganj 102MW | [16 empty] | 0 | 3 |  | 18 | 40 | 48 | 72 | 15 | 0 | 0 | 180696
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj (Powerpac) 100MW | [15 empty] | 0 | 13 | 76 |  | 87 | 87 | 89 | 82 | 30 | 0 |  | 403285
86 | Meghnaghat CCPP(Summit) | 260 | 260 | 290 | 257 | 235 | 265 | 290 | 290 | 278 | 260 | 278 | 265 | 278 | 277 | 253 | 257 | 235 | 250 |  | 283 | 234 | 235 | 253 | 260 | 306 | 290 | 6571142
87 | Meghnaghat (IEL) | [16 empty] | 0 | 1 |  | 20 | 90 | 80 | 90 | 92 | 100 | 100 | 490560
88 | Ghorashal 78MW (MAX) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 55 | 72 | 71 | 71 | 70 | 70 | 50 | 50 | 50 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 1299872
90 | Ashuganj (United) 53MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 120000
91 | Juldah (Acorn) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 30 | 40 | 40 | 40 |  | 40 | 60 | 66 | 65 | 65 | 65 | 65 | 641760
92 | Fenchuganj (EPL) 44MW | 47 | 47 | 47 | 10 | 10 | 10 | 10 | 10 | 22 | 47 | 46 | 47 | 47 | 47 | 47 | 47 | 47 | 20 |  | 33 | 47 | 47 | 47 | 47 | 47 | 47 | 877000
93 | Ashuganj (Midland) 51MW | 35 | 35 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 25 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 591226
94 | Gagnagar (Orion) | [8 empty] | 4 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 40 | 74 |  | 84 | 100 | 101 | 100 | 100 | 100 | 100 | 862416
95 | Patenga 50MW | 47 | 47 | 47 | 37 | 26 | 11 | 6 | 6 | 6 | 6 | 6 | 8 | 34 | 46 | 46 | 46 | 46 | 46 |  | 46 | 46 | 46 | 46 | 46 | 47 | 47 | 788640
96 | Chattogram ECPV 108 MW | 19 | 12 | 12 | 12 | 12 | 4 | 0 |  |  |  |  | 2 | 40 | 58 | 33 | 33 | 31 | 31 |  | 43 | 60 | 63 | 65 | 65 | 60 | 63 | 690240
97 | Katpotti 51 MW | 48 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 19 | 20 | 16 | 37 | 48 | 48 | 48 | 48 | 48 |  | 48 | 48 | 47 | 45 | 48 | 48 | 47 | 852528
98 | Bosila 108MW | 24 | 0 | [9 empty] | 0 | 56 | 55 | 53 | 53 | 53 | 51 |  | 55 | 55 | 55 | 54 | 62 | 63 | 63 | 680640
99 | Madanganj-55 MW | [16 empty] | 0 | 8 |  | 36 | 55 | 55 | 55 | 55 | 55 | 0 | 306733
100 | Northern 55 MW | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 28 | 37 | 37 | 37 | 37 | 56 | 56 | 56 | 56 |  | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 874451
101 | Kushiara 163 MW CCPP GT | 130 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 130 | 130 | 130 | 163 | 100 | 130 | 163 | 163 | 163 | 100 |  | 100 | 130 | 130 | 163 | 130 | 130 | 130 | 3254040
102 | Sarishabari (Solar) | [5 empty] | 0 | 0.3 | 0.96 | 0.1 | 1.3 | 1.34 | 1.8 | 0.9 | 1.7 | 0.7 | 1 | 0.5 | 0.1 | [8 empty] | 12350
103 | Banco Energy 54MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 35 | 35 | 35 | 17 | 17 | 17 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 598320
104 | APR Energy , Keranigonj
105 | Bramhangoan 100 MW (Aggreko)
106 | United Mymensingh PPL | [16 empty] | 0 | 5 |  | 48 | 130 | 132 | 160 | 160 | 160 | 160 | 871200
112 | Aggreko Aurahati 100MW
114 | Summit Gazipur-1 150MW | [9 empty] | 18 | 50 | 50 | 103 | 149 | 149 | 118 | 100 | 100 |  | 100 | 108 | 110 | 149 | 149 | 149 | 149 | 1673280
115 | Juldah 100 MW Unit-3 | 100 | 100 | 70 | 55 | 40 | 10 | 10 | 10 | 10 | 40 | 70 | 90 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1790400
116 | Chandpur Desh 200MW | 50 | 17 | 17 | 17 | 17 | 0 | [5 empty] | 4 | 50 | 52 | 148 | 140 | 140 | 140 |  | 156 | 200 | 200 | 200 | 200 | 200 | 200 | 2053000
117 | Midland 150MW | 6 | 6 | 6 | 6 | 6 | 0 | [5 empty] | 1 | 50 | 61 | 137 | 80 | 80 | 80 |  | 88 | 147 | 147 | 148 | 148 | 148 | 150 | 1420145
118 | Bibiyana-3 285 MW | 200 | 200 | 200 | 173 | 151 | 120 | 120 | 122 | 179 | 218 | 219 | 298 | 292 | 292 | 295 | 298 | 298 | 220 |  | 220 | 270 | 220 | 220 | 221 | 239 | 250 | 5256000
| United Jamalpur PPL | 99 | 99 | 70 | 50 | 50 | 16 | 16 | 53 | 98 | 98 | 97 | 96 | 97 | 95 | 96 | 87 | 96 | 96 |  | 96 | 96 | 96 | 98 | 98 | 99 | 98 | 2040000
| Anwara United | 153 | 143 | 142 | 142 | 152 | 151 | 151 | 154 | 154 | 154 | 133 | 133 | 134 | 150 | 133 | 133 | 133 | 133 |  | 133 | 100 | 100 | 100 | 110 | 130 | 132 | 3291920
120 | Eastern Zone Total | 6520 | 6355 | 6282 | 5957 | 5405 | 4997.38 | 5043.44 | 5205.42 | 5878.93 | 6390.409 | 6553.5 | 6967.25 | 6997.18 | 7427.1 | 7609.9 | 7530.3 | 7476.2 | 7132.2 |  | 7435 | 8606 | 8606 | 8681 | 8408 | 8206 | 8125 | 166429986
121
122
123 | Khulna 60MW
124 | Khulna (KPCL-1 & 3)
125 | Khulna (KPCL-2) | [16 empty] | 0 | 16 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 642240
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur Peaking | [15 empty] | 0 | 4 | 20 |  | 35 | 35 | 32 | 32 | 32 | 32 | 32 | 199680
| Khulna CCPP 225MW | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 145 | 160 | 185 | 224 | 225 | 225 | 225 | 3471360
129 | Labon Chora 105 MW | 27 | 17 | 17 | 0 | [8 empty] | 17 | 61 | 105 | 58 | 53 | 53 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 1043520
130
131
132
133
| Summit Barisal 110 MW | 16 | 16 | 0 | [13 empty] | 0 | 16 |  | 64 | 110 | 110 | 110 | 110 | 110 | 110 | 632640
136 | Barisal GT: Unit-1, 2
137 | Bhola Aggreko 95MW | 95 | 96 | 96 | 96 | 33 | 12 | 12 | 12 | 15 | 51 | 55 | 91 | 91 | 92 | 92 | 90 | 93 | 49 |  | 66 | 96 | 96 | 97 | 98 | 96 | 95 | 1739361
| Bhola CCPP 194MW | 174 | 174 | 174 | 174 | 174 | 174 | 175 | 175 | 175 | 174 | 175 | 174 | 174 | 174 | 174 | 173 | 173 | 174 |  | 174 | 173 | 174 | 173 | 174 | 174 | 174 | 4291060
140 | Bhola (Venture) 33MW | 38 | 39 | 38 | 19 | 34 | 27 | 26 | 25 | 25 | 25 | 25 | 27 | 29 | 28 | 32 | 32 | 31 | 32 |  | 38 | 40 | 39 | 39 | 39 | 38 | 38 | 752744
141 | Bangla Trak Noapara | [19 empty] | 0 | 10 | 37 | 94 | 94 | 70 | 70 | 382080
142 | Noapara (KZA) 40MW | 27 | 8 | 8 | 0 | [13 empty] | 0 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 262125
143 | Gopalganj Peaking | [14 empty] | 0 | 2 | 25 | 50 |  | 70 | 70 | 60 | 55 | 48 | 36 | 31 | 342784
144 | Bheramara GT-1,2,3
145 | Madhumati Power Plant | 58 | 36 | 36 | 36 | 36 | 0 | [5 empty] | 0 | 54 | 53 | 70 | 69 | 36 | 34 |  | 51 | 78 | 89 | 89 | 89 | 88 | 89 | 1050480
146 | Bheramara HVDC | 941 | 942 | 941 | 937 | 936 | 936 | 936 | 937 | 938 | 938 | 938 | 938 | 938 | 940 | 941 | 940 | 940 | 941 |  | 941 | 940 | 941 | 941 | 940 | 941 | 940 | 22557818
147 | Bheramara 360 MW
148
149
150 | Barapukuria Unit-1
151 | Barapukuria Unit-2
152 | Barapukuria Unit-3 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 150 | 149 | 149 |  | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 3664200
153 | Baghabari GT 71MW | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 60 | 60 | 60 | 60 | 60 | 1392000
156 | Baghabari GT 100MW
| Baghabari Peaking 50MW | [17 empty] | 0 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 278520
157 | Sirajgonj Unit-1 225MW (Gas) | 180 | 181 | 194 | 190 | 181 | 180 | 180 | 197 | 203 | 190 | 194 | 196 | 181 | 191 | 182 | 181 | 181 | 174 |  | 159 | 186 | 183 | 195 | 214 | 214 | 214 | 4815836
158 | Sirajgonj Unit-1 225MW (Oil)
| Sirajgonj Unit-2 225MW (Gas) | 177 | 179 | 191 | 187 | 176 | 145 | 145 | 168 | 185 | 198 | 197 | 198 | 185 | 194 | 186 | 179 | 181 | 173 |  | 144 | 0 | 0 | 30 | 141 | 213 | 211 | 4214591
Sirajgonj Unit-2 225MW (Oil)
159 | Sirajgonj Unit-3 225 MW(Gas) | 186 | 187 | 200 | 196 | 187 | 186 | 187 | 203 | 211 | 199 | 198 | 200 | 187 | 196 | 188 | 187 | 187 | 176 |  | 151 | 197 | 189 | 184 | 218 | 218 | 218 | 4850445
Sirajgonj Unit-3 225 MW(Oil)
160 | Sirajgonj Unit-4 414 MW(Gas) | 300 | 301 | 302 | 297 | 250 | 243 | 257 | 250 | 360 | 421 | 412 | 418 | 414 | 402 | 411 | 360 | 360 | 330 |  | 250 | 330 | 300 | 414 | 414 | 407 | 417 | 8365730
161 | Bera Peaking | [17 empty] | 0 |  | 34 | 33 | 32 | 32 | 33 | 33 | 33 | 156360
162 | Bogra (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 21 | 21 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 510480
163 | Bogra (EPL) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 14 | 14 | 14 | 12 | 16 | 15 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 370116
164 | Ullapara (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 8 | 8 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 199152
165 | Amnura 50MW | 24 | 24 | 24 | 12 | 12 | 0 | [11 empty] | 0 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 384020
166 | Katakhali (Northern) | [16 empty] | 0 | 8 |  | 18 | 24 | 43 | 43 | 43 | 43 | 43 | 211581
167 | Katakhali Peaking | [17 empty] | 0 |  | 43 | 44 | 47 | 44 | 44 | 43 | 0 | 202248
168 | Santahar Peaking | [17 empty] | 0 |  | 35 | 35 | 35 | 35 | 35 | 34 | 34 | 191636
169 | Rajlanka 52 MW | 8 | 8 | 8 | 8 | 8 | 0 | [6 empty] | 8 | 8 | 8 | 8 | 8 | 8 |  | 42 | 52 | 52 | 52 | 52 | 52 | 51 | 372000
170 | Chapainawabganj-100 MW | 55 | 55 | 55 | 55 | 55 | 25 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 60 | 60 | 60 | 60 |  | 90 | 95 | 92 | 95 | 92 | 92 | 92 | 1248208
171 | Paramount Baghabari
172 | Confidence CPBL-2 | 53 | 35 | 35 | 35 | 0 | [6 empty] | 11 | 54 | 72 | 82 | 90 | 108 | 96 |  | 100 | 108 | 100 | 90 | 108 | 108 | 108 | 1269696
173 | Rangpur GT | [20 empty] | 0 | 16 | 17 | 17 | 17 | 17 | 69000
175 | Saidpur GT | [17 empty] | 0 |  | 17 | 14 | 15 | 15 | 15 | 15 | 16 | 84000
176
177
178
178 | Western Zone Total | 2734 | 2673 | 2694 | 2617 | 2457 | 2303 | 2321 | 2367 | 2506 | 2590 | 2586 | 2644 | 2722 | 2802 | 2900 | 2799 | 2809 | 2780 | 0 | 3280 | 3443 | 3485 | 3718 | 3893 | 3917 | 3876 | 70217711