## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2022-09-20 | Tuesday
|  | Date (day): | 2022-09-20 |  | Tuesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11930.6 | MW |  |  | (b) At Evening Peak Hour : |  | 13785 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2022-09-19 | 2022-09-20 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 200 | 230 | 230 | 230
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint.
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Machine problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 100 | 100 | 90 | 100 |  | 8 | Engine problem
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 406 | 407 | 390 | 400 | 12 |  | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 273 | 252 | 250 | 250 | 110 |  | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 210 | 225 | 225 | 225 |  | Dirty fuel
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 41 | 80 | 40 | 80 | 20 |  | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 130 | 145 | 140 | 140 | 195 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 0 | 0 | 0 | 0 |  | 102 | Under maint
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 19 | 19 | 19
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 47 | 88 | 45 | 90 |  | 10 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 |  | 335 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 40 | 92 | 40 | 92 |  | 10 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 54 | 17 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 16 | 78 | 16 | 130 | 19 |  | Fuel shortage
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 35 | 35 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 55 | 35 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 46 | 45 | 50 | 50 |  | 30 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 15 | 14 | 24 | 24 |  | 9 | Engine problem
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 41 | 48 | 32 | 49
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 273 | 273 | 275 | 275 |  | 25 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 223 | 183 | 120 | 180 |  | 120 | Engine problem
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 75 | 90 | 75 | 90 |  | 10 | Engine problem
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 75 | 90 | 75 | 90 |  | 10 | Engine problem
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 133 | 149 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 90 | 105 | 105 | 105
37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 55 | 94 | 50 | 90 | 14 |  | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 72 | 144 | 72 | 162
39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 34 | 0 | 30 | 0
40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 55 | 0 | 55
| Dhaka area Total |  |  |  |  | 6263 | 5847 | 2769 | 3223 | 2717 | 3327 | 856 | 1724
41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 110 | 110 | 110 | 110 | 70 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 16 | 25 | 25 | 25
43 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 14 | 0 | 20 | 0
44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 38 | 39 | 40 | 40 |  | 10 | Engine problem
45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 151 | 151 | 151 | 151 |  | 79 | Low Water Level
46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | S/D due to HGPI
47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 102 | 105 | 105 | 105
49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 22 | 31 | 20 | 25 | 73 |  | Fuel shortage
50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 17 | 51 | 17 | 51 | 51 |  | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 33 | 78 | 33 | 80 |  | 20 | Engine problem
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 33 | 90 | 33 | 90 |  | 10 | Engine problem
53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 15 | 15 | 15 | 15 |  | 7 | Engine problem
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 10 | 28 | 5 | 20
54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 3 | 0 | 5 | 0
56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 248 | 275 | 250 | 275 |  |  | Engine problem
57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 27 | 36 | 36 | 36 |  | 18 | Engine prolem
58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 84 | 105 | 88 | 105 |  |  | Engine problem
59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 38 | 90 | 38 | 100
60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 107 | 107 | 107 | 107 |  | 9 | Engine problem
| Mirsharai 150 MW |  | Gas/HSD | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0
| Chattogram area Total |  |  |  |  | 2442 | 2382 | 1068 | 1336 | 1098 | 1335 | 482 | 528
61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 200 | 191 | 180 | 185 | 36 |  | Gas shortage
63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 300 | 280 | 280 | 280 | 80 |  | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 250 | 250 | 250 | 250 | 110 |  | Gas shortage
| Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+136*1 | 284 | 284 | 0 | 0 | 0 | 0 |  |  | On test.
65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 36 | 42 | 40 | 40
66 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 55 | 20 | 30 | 20 | 30 |  |  | Gas shortage
67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 132 | 140 | 135 | 140 |  | 10 | Engine problem
70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 27 | 29 | 29 |  | 23 | Engine problem
71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 83 | 83 | 83 | 83 |  | 80 | Machine problem
72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 200 | 200 | 120 | 200
73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 19 | 19
74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 7 | 10 | 10
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 72 | 126 | 143 | 165
75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 14 | 32 | 33 | 33
76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 43 | 8 | 43 | 9 |  | Engine problem
77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 21 | 21 | 21 | 21 |  | 4 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 188 | 190 | 150 | 190 |  | 10 | Engine problem
79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 34 | 17 | 34
80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 98 | 115 | 97 | 113
81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 17 |  | 37 | 33 kV feeder fault
82 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 34 | 115 | 35 | 115
| Cumilla Area Total |  |  |  |  | 3193 | 3169 | 1776 | 2021 | 1746 | 2056 | 556 | 164
83 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 65 | 99 | 70 | 100 | 102 |  | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 14 | 13 | 14 | 14 | 22 |  | Gas shortage
85 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0 |  |  | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
87 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 141 | 151 | 150 | 150 | 50 |  | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 87 | 96 | 97 | 105 |  | 10 | Engine problem
89 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 46 | 0 | 50 | 0
90 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 12 | 12 |  | 10 | Engine problem
| Mymensingh Area Total |  |  |  |  | 717 | 614 | 367 | 371 | 394.6 | 381 | 124 | 20
91 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 42 | 43 | 43 | 43 |  | 27 | Machine problem.
92 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 41 | 41 | 41 | 41 |  | 49 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 | 163 |  | Gas shortage
94 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Gas shortage
96 | Fenchuganj 44MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Gas shortage
97 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 11 |  | Gas shortage
98 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 55 | 63 | 60 | 60
99 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 0 | 78 | 10 | 78
100 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
101 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 220 | 220 | 220 | 220
102 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18
103 | Sylhet 50MW PP (EPL) |  | Gas | NENP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Gas shortage
104 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 0 | 8 | 0 | 0 | 25 |  | Gas shortage
105 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 280 | 265 | 280 | 61 |  | FGMO
106 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 405 | 402 | 400 | 400
107 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 8 | 10 | 10 | 10
108 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 384 | 400 | 400 | 400
| Sylhet Area Total |  |  |  |  | 2522 | 2477 | 1473 | 1563 | 1467 | 1550 | 411 | 506
109 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 885 | 891 | 918 | 918 |  |  | .
110 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 16 | 32 | 16 | 32 | 83 |  | Fuel shortage
111 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 32 | 0 | 35
112 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 180 | 227 | 150 | 225
113 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 40 | 0 | 40 |  | 69 | Engine problem
114 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 215 | 225 | 230 | 230 | 180 |  | Gas shortage
115 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 0 | 0 | 0 | 40 |  | Fuel shortage
116 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 10 | 94 | 50 | 95 |  | 5
117 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 17 | 55 | 17 | 55 | 50 |  | Fuel shortage
118 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 15 | 67 | 15 | 60 | 45 |  | Fuel shortage
119 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 97 | 0 | 100 | 0
| Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 2388 | 2384 | 1435 | 1663 | 1496 | 1690 | 414 | 74
120 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 16 | 32 | 0 | 32 |  |  | Line O/L
121 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 19 | 28 | 16 | 25
122 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 83 | 86 | 85 | 85 |  | 109 | Machine problem
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
123 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 890 | 1080 | 1110 | 1110 |  |  | Line O/L
124 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 214 | 224 | 220 | 220
125 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 17 | 17 |  |  | Line O/L
| Barisal Area Total |  |  |  |  | 1958 | 1958 | 1222 | 1450 | 1448 | 1489 | 0 | 109
126 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
127 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 24 | 0 | 32 |  | 20 | Engine problem
128 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 0 |  | 71 | Engine problem
129 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
130 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 42 | 34 | 42 |  | 8 | Engine problem
131 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 32 | 16 | 32 | 50 |  | Fuel shortage
132 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 187 | 180 | 180 | 180 | 30 |  | Gas shortage
133 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 165 | 216 | 150 | 210
134 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 158 | 154 | 150 | 150 | 70 |  | Gas shortage
135 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 340 | 334 | 260 | 300 |  |  | Gas shortage
136 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 26 | 0 | 26 |  | 24 | Engine problem
137 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 17 | 18 | 18 | 18
138 | Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
139 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 11 | 11 | 11
140 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 8 | 8 | 8 | 44 |  | Fuel shortage
141 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 80 | 0 | 81 |  | 23 | Engine problem
142 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 20 | 90 | 100 | 170 |  | 30 | Engine problem
143 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 108 | 113 | 113 | 113
144 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 76 | 95 | 50 | 95 |  | 18 | Engine problem
145 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 3 | 0 | 6 | 0
| Rajshahi Area Total |  |  |  |  | 2199 | 2129 | 1074 | 1423 | 1096 | 1468 | 365 | 194
146 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 76 | 78 | 78 | 78
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
147 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 250 | 250 | 250 | 250 | 24
148 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
149 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
150 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 73 | 71 | 50 | 71 |  | 35 | Engine problem
151 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5 | 0 | 8 | 0
152 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 94 | 94 | 70 | 90 |  | 25 | Fuel shortage
| Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 30 | 0 | 12 | 0
| Rangpur Area Total |  |  |  |  | 830 | 750 | 528 | 493 | 468 | 489 | 64 | 145
| Total |  |  |  |  | 22512 | 21710 | 11712 | 13543 | 11930.6 | 13785 | 3272 | 3464
A. |  | 2022-09-19 | (Yesterday) |  |  |  |  | Monday
1 | Highest Generation : |  |  | 13543 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 10447 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 13964 | MW
3 | Day peak Generation : |  |  | 11712 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 13436.56 | MW
4 | Evening peak Generation : |  |  | 13543 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 388 | MW
5 | Total Energy Generation : |  | 290.3383 | MKWHr | By Solar | 1.4039 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Gas : | 129.7806 | MKWHr |  | By Oil: | 98.7622 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 32.5784 | MKWHr |  | By Hydro: | 3.6574 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 3272 | MW | Dhaka | 4828.51 | 4799.51 |  | 29 |  | 18:00 |  | 236
|  |  | For Plants S/D or M/C prob = |  |  | 3464 | MW | Chittagong | 1266.05 | 1266.05 |  | 0 |  | 19:00 |  | 970
|  |  | Total = |  |  | 6736 | MW | Khulna | 1594.6 | 1594.6 |  | 0 |  | 19:30 |  | 959
7 | Total Gas Supplied : |  |  | 1009.47 | MMCFD |  |  | Rajshahi | 1387.4 | 1387.4 |  | 0 |  | 20:00 |  | 505
8 | Fuel Cost : | i) Gas : | Taka | 146077969.212 | ii) Oil : | Taka | 1436083230.96 | Comilla | 1319 | 1268 |  | 51 |  | 21:00 |  | 388
|  | iii) Coal : |  | 265112664.58 | Total | Taka | 1847273864.752 | Mymensingh | 1136 | 923 |  | 213 |  | 22:00 |  | 276.4725
9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0 | MKWHr. | Sylhet | 634 | 539 |  | 95 |  | 23:00 |  | 365.8653
| ii) During Peak Demand : |  |  | 1215 | MW (E to W) at | 21:00 | hrs | Barisal | 368 | 368 |  | 0 |  | 24:00 |  | 978.7127
| iii) Maximum : |  |  | 1080 | MW at | 6:00 | hrs | Rangpur | 903 | 903 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 34.3° C |  |  | Total | 13436.56 | 13048.56 |  | 388
B. |  | 2022-09-20 | (Today) |  |  |  | Tuesday |  |  | Probable max. temperature in Dhaka |  |  | 33.8 ° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 14000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 198 | MW
2 | Maximum Generation (Generation end) |  |  |  | 13785 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 12000 | MW
4 | Reserve(Generation end) |  |  |  | - | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 300.1356 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 10459 | MW at | 8:00 | 55 | 0 | 30 | 25 | 20 | 40 | 8 | 0 | 20
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.5091 | MKWHr. | ii) HVDC Flow at Peak Time |  | 891 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.6467 | MKWHr. | iii) Maximum HVDC Flow : |  | 900 | MW at | 23:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 96.72 |  | (b) Today: | 96.99 |  | (c) Rule Curve: |  | 103.37
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2022-09-19
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 220 | 0 | 280 | 11 | 0 | 314 | 130 |  | 0 | 175 | 122 | 42 | 0 | 55 | 0 | 0 | 0 | 47 | 40 | 82 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 25 | 21 | 33 | 16 | 49 | 0 | 80 | 70 | 110 | 0 | 18 | 0 | 0 | 0 | 0 |  | 12 | 22 | 17 | 33 | 0 | 38 | 15 | 35 | 0 | 0 | 0 | 280 | 240 | 181 | 8 | 83 | 43 | 30 | 0 | 51 | 0 | 29 | 8 | 19 | 10 | 33 | 21 | 144 | 143 | 0 | 13 | 0 | 43 | 41 | 0 | 0 | 0 | 0 | 58 | 20 | 0 | 213 | 18 | 0 | 10 | 300 | 8 | 0 | 190 | 273 | 221 | 75 | 153 | 75 | 149 | 0 | 33 | 200 | 143 | 401 | 95 | 105 | 23 | 0 | 240 | 36 | 55 | 17 | 102 | 49 | 400 | 54 | 0 | 17 | 86 | 0 | 17 | 0 | 35 | 0 | 0 | 0 | 0 |  | 893 | 0 | 225 | 0 | 15 | 226 | 0 | 0 | 5 | 20 | 0 | 86 | 29 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 18 | 0 | 0 | 78 | 0 | 250 | 0 | 0 | 184 | 0 | 0 | 219 | 0 | 95 | 158 | 0 | 340 | 17 | 170 | 113 | 0 | 78 | 0 | 0 | 95 | 1045 | 224 | 0 | 0 | 0 | 0 | 94 | 0 | 0 | 0 | 0 |  | 7509 | 4717 | 12226 | 3954 | 893 | 1503 | 826 | 2763 | 1373 | 150 | 445 | 394 | 144 | 0 | 837 | 96.7
2:00 | 0 | 0 | 220 | 0 | 280 | 11 | 0 | 314 | 133 |  | 0 | 175 | 128 | 41 | 0 | 55 | 0 | 0 | 0 | 47 | 40 | 82 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 0 | 25 | 21 | 33 | 16 | 49 | 0 | 80 | 70 | 110 | 0 | 17 | 0 | 0 | 0 | 0 |  | 12 | 22 | 17 | 33 | 0 | 39 | 15 | 35 | 0 | 0 | 0 | 280 | 240 | 183 | 8 | 83 | 43 | 30 | 0 | 51 | 0 | 28 | 8 | 19 | 10 | 33 | 21 | 136 | 140 | 0 | 13 | 0 | 43 | 41 | 0 | 0 | 0 | 0 | 58 | 20 | 0 | 220 | 18 | 0 | 10 | 290 | 8 | 0 | 189 | 273 | 221 | 75 | 153 | 75 | 149 | 0 | 33 | 200 | 142 | 402 | 96 | 105 | 70 | 0 | 249 | 36 | 102 | 17 | 101 | 38 | 400 | 54 | 0 | 17 | 90 | 0 | 17 | 0 | 35 | 0 | 0 | 0 | 0 |  | 894 | 0 | 230 | 0 | 15 | 225 | 0 | 0 | 5 | 0 | 0 | 86 | 27 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 18 | 0 | 8 | 77 | 0 | 251 | 0 | 0 | 184 | 0 | 0 | 219 | 0 | 95 | 159 | 0 | 344 | 17 | 170 | 113 | 0 | 78 | 0 | 0 | 95 | 1010 | 224 | 0 | 0 | 0 | 0 | 94 | 0 | 0 | 0 | 0 |  | 7580 | 4678 | 12258 | 3956 | 894 | 1504 | 825 | 2857 | 1338 | 150 | 444 | 373 | 136 | 0 | 452 | 96.7
3:00 | 0 | 0 | 220 | 0 | 0 | 43 | 0 | 314 | 131 |  | 0 | 180 | 125 | 41 | 0 | 55 | 0 | 0 | 0 | 47 | 40 | 82 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 0 | 25 | 21 | 33 | 16 | 49 | 0 | 80 | 70 | 110 | 0 | 17 | 0 | 0 | 0 | 0 |  | 12 | 22 | 17 | 33 | 0 | 39 | 15 | 35 | 0 | 0 | 0 | 280 | 240 | 190 | 8 | 83 | 43 | 30 | 0 | 51 | 0 | 28 | 8 | 19 | 10 | 33 | 21 | 132 | 132 | 0 | 13 | 0 | 43 | 41 | 0 | 0 | 0 | 0 | 57 | 20 | 0 | 220 | 18 | 0 | 10 | 290 | 8 | 0 | 189 | 273 | 120 | 75 | 153 | 75 | 149 | 0 | 33 | 200 | 143 | 401 | 96 | 105 | 87 | 0 | 249 | 36 | 105 | 17 | 101 | 38 | 400 | 54 | 0 | 17 | 90 | 0 | 17 | 0 | 35 | 0 | 0 | 0 | 0 |  | 894 | 0 | 230 | 0 | 15 | 225 | 0 | 0 | 5 | 0 | 0 | 86 | 26 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 18 | 0 | 8 | 77 | 0 | 250 | 0 | 0 | 185 | 0 | 0 | 219 | 0 | 95 | 160 | 0 | 350 | 17 | 170 | 113 | 0 | 78 | 0 | 0 | 95 | 990 | 224 | 0 | 0 | 0 | 0 | 94 | 0 | 0 | 0 | 0 |  | 7245 | 4664 | 11909 | 3675 | 894 | 1541 | 724 | 2878 | 1317 | 150 | 444 | 373 | 132 | 0 | 175 | 96.71
4:00 | 0 | 0 | 220 | 0 | 0 | 67 | 0 | 333 | 140 |  | 0 | 180 | 133 | 41 | 0 | 55 | 0 | 0 | 0 | 47 | 40 | 82 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 25 | 23 | 33 | 16 | 49 | 0 | 81 | 70 | 110 | 0 | 17 | 0 | 0 | 0 | 0 |  | 12 | 22 | 17 | 33 | 0 | 39 | 15 | 35 | 0 | 0 | 0 | 280 | 240 | 196 | 8 | 83 | 43 | 30 | 0 | 51 | 0 | 28 | 8 | 19 | 10 | 33 | 21 | 128 | 135 | 0 | 13 | 0 | 43 | 41 | 0 | 0 | 0 | 0 | 57 | 10 | 0 | 220 | 18 | 0 | 10 | 290 | 8 | 0 | 189 | 273 | 120 | 75 | 153 | 75 | 149 | 0 | 33 | 200 | 140 | 401 | 97 | 105 | 87 | 0 | 249 | 36 | 105 | 17 | 100 | 38 | 400 | 54 | 0 | 17 | 90 | 0 | 17 | 0 | 35 | 0 | 0 | 0 | 0 |  | 885 | 0 | 230 | 0 | 15 | 226 | 0 | 0 | 5 | 0 | 0 | 86 | 25 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 18 | 0 | 8 | 76 | 0 | 250 | 0 | 0 | 185 | 0 | 0 | 218 | 0 | 20 | 160 | 0 | 361 | 17 | 100 | 113 | 0 | 78 | 0 | 0 | 95 | 950 | 224 | 0 | 0 | 0 | 0 | 94 | 0 | 0 | 0 | 0 |  | 7319 | 4479 | 11798 | 3724 | 885 | 1582 | 579 | 2875 | 1276 | 151 | 444 | 372 | 128 | 0 | 0 | 96.71
5:00 | 0 | 0 | 218 | 0 | 0 | 82 | 0 | 352 | 151 |  | 0 | 185 | 132 | 42 | 0 | 55 | 0 | 0 | 0 | 47 | 40 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 25 | 26 | 33 | 16 | 49 | 0 | 81 | 70 | 110 | 0 | 17 | 0 | 0 | 0 | 0 |  | 12 | 22 | 17 | 33 | 0 | 39 | 15 | 35 | 0 | 0 | 0 | 280 | 240 | 188 | 8 | 83 | 43 | 30 | 0 | 51 | 0 | 28 | 8 | 16 | 10 | 33 | 21 | 130 | 138 | 0 | 13 | 0 | 43 | 41 | 0 | 0 | 0 | 0 | 58 | 10 | 0 | 220 | 18 | 0 | 10 | 280 | 0 | 0 | 80 | 273 | 82 | 75 | 142 | 75 | 135 | 0 | 33 | 200 | 138 | 401 | 97 | 105 | 105 | 0 | 249 | 36 | 100 | 17 | 99 | 38 | 400 | 54 | 0 | 17 | 90 | 0 | 17 | 0 | 35 | 0 | 0 | 0 | 0 |  | 885 | 0 | 230 | 0 | 15 | 226 | 0 | 0 | 2 | 0 | 0 | 86 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 18 | 0 | 8 | 76 | 0 | 250 | 0 | 0 | 185 | 0 | 0 | 215 | 0 | 20 | 161 | 0 | 367 | 17 | 30 | 113 | 0 | 78 | 0 | 0 | 95 | 920 | 225 | 0 | 0 | 0 | 0 | 94 | 0 | 0 | 0 | 0 |  | 7119 | 4364 | 11483 | 3730 | 885 | 1608 | 362 | 2845 | 1246 | 151 | 441 | 300 | 130 | 0 | 0 | 96.72
6:00 | 0 | 0 | 220 | 0 | 0 | 92 | 0 | 356 | 160 |  | 0 | 190 | 132 | 42 | 0 | 55 | 0 | 0 | 0 | 47 | 40 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 25 | 26 | 33 | 16 | 49 | 0 | 81 | 70 | 110 | 0 | 17 | 0 | 0 | 0 | 0 |  | 8 | 22 | 17 | 33 | 0 | 39 | 15 | 35 | 0 | 0 | 0 | 280 | 240 | 187 | 8 | 83 | 43 | 30 | 0 | 51 | 0 | 28 | 8 | 16 | 10 | 33 | 21 | 124 | 123 | 0 | 14 | 0 | 43 | 41 | 0 | 0 | 0 | 0 | 62 | 10 | 0 | 220 | 18 | 0 | 10 | 290 | 5 | 0 | 0 | 258 | 11 | 25 | 142 | 0 | 134 | 1 | 33 | 200 | 138 | 400 | 97 | 105 | 105 | 0 | 249 | 36 | 97 | 17 | 97 | 38 | 400 | 54 | 0 | 17 | 97 | 0 | 17 | 0 | 35 | 0 | 0 | 0 | 0 |  | 885 | 0 | 235 | 0 | 15 | 208 | 0 | 0 | 0 | 0 | 0 | 82 | 19 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 18 | 0 | 8 | 76 | 0 | 250 | 0 | 0 | 184 | 0 | 0 | 130 | 0 | 0 | 162 | 0 | 374 | 17 | 0 | 113 | 0 | 78 | 0 | 0 | 95 | 870 | 225 | 0 | 0 | 0 | 1 | 94 | 0 | 0 | 0 | 0 |  | 6853 | 4163 | 11016 | 3730 | 885 | 1644 | 36 | 2827 | 1196 | 151 | 338 | 213 | 124 | 2 | 0 | 96.72
7:00 | 0 | 0 | 220 | 0 | 0 | 87 | 0 | 345 | 150 |  | 0 | 190 | 132 | 41 | 0 | 45 | 0 | 0 | 0 | 47 | 40 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 25 | 25 | 33 | 16 | 49 | 0 | 81 | 70 | 110 | 0 | 17 | 0 | 0 | 0 | 0 |  | 6 | 22 | 17 | 33 | 0 | 6 | 15 | 33 | 0 | 0 | 0 | 280 | 240 | 188 | 8 | 83 | 43 | 30 | 0 | 51 | 0 | 0 | 8 | 0 | 10 | 33 | 21 | 118 | 96 | 0 | 14 | 0 | 43 | 41 | 0 | 0 | 0 | 0 | 62 | 10 | 0 | 220 | 18 | 0 | 10 | 280 | 8 | 0 | 0 | 266 | 0 | 0 | 144 | 0 | 79 | 2 | 33 | 100 | 137 | 402 | 97 | 105 | 98 | 1 | 249 | 36 | 94 | 17 | 98 | 38 | 397 | 32 | 7 | 17 | 105 | 0 | 17 | 7 | 34 | 0 | 0 | 0 | 0 |  | 885 | 0 | 240 | 0 | 15 | 130 | 0 | 0 | 0 | 0 | 0 | 84 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 18 | 0 | 8 | 75 | 0 | 250 | 0 | 0 | 184 | 0 | 0 | 130 | 0 | 0 | 163 | 0 | 370 | 17 | 0 | 113 | 0 | 34 | 0 | 1 | 35 | 870 | 225 | 0 | 0 | 0 | 12 | 56 | 0 | 0 | 0 | 2 |  | 6504 | 3943 | 10447 | 3686 | 885 | 1612 | 0 | 2453 | 1195 | 151 | 260 | 185 | 118 | 32 | 0 | 96.73
8:00 | 0 | 0 | 220 | 0 | 0 | 91 | 0 | 332 | 140 |  | 0 | 190 | 138 | 42 | 0 | 55 | 0 | 0 | 0 | 47 | 40 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 25 | 25 | 33 | 24 | 49 | 0 | 81 | 70 | 110 | 0 | 17 | 0 | 0 | 0 | 0 |  | 6 | 22 | 17 | 33 | 0 | 6 | 15 | 12 | 0 | 0 | 0 | 280 | 240 | 182 | 8 | 83 | 43 | 30 | 0 | 51 | 0 | 0 | 8 | 16 | 10 | 17 | 21 | 104 | 71 | 0 | 14 | 0 | 43 | 41 | 0 | 0 | 0 | 0 | 64 | 10 | 0 | 220 | 18 | 0 | 10 | 300 | 8 | 0 | 0 | 275 | 0 | 0 | 144 | 0 | 72 | 5 | 33 | 108 | 138 | 402 | 97 | 105 | 87 | 2 | 231 | 36 | 88 | 17 | 98 | 38 | 400 | 17 | 25 | 17 | 107 | 0 | 17 | 17 | 35 | 0 | 0 | 0 | 0 |  | 885 | 0 | 240 | 0 | 15 | 170 | 0 | 0 | 0 | 0 | 0 | 85 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 18 | 0 | 8 | 75 | 0 | 250 | 0 | 0 | 186 | 0 | 0 | 130 | 0 | 0 | 163 | 0 | 367 | 17 | 0 | 113 | 15 | 34 | 0 | 2 | 35 | 870 | 224 | 0 | 0 | 1 | 14 | 56 | 0 | 0 | 0 | 4 |  | 6465 | 4001 | 10466 | 3658 | 885 | 1605 | 0 | 2443 | 1195 | 151 | 300 | 185 | 104 | 70 | 0 | 96.74
9:00 | 0 | 0 | 200 | 0 | 0 | 91 | 0 | 321 | 151 |  | 0 | 190 | 125 | 41 | 0 | 55 | 0 | 0 | 0 | 47 | 40 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 25 | 25 | 33 | 24 | 49 | 0 | 81 | 70 | 110 | 0 | 17 | 0 | 0 | 0 | 0 |  | 6 | 22 | 17 | 33 | 0 | 31 | 15 | 7 | 0 | 0 | 0 | 300 | 240 | 183 | 8 | 83 | 40 | 30 | 0 | 51 | 0 | 0 | 8 | 19 | 10 | 16 | 21 | 108 | 71 | 0 | 14 | 1 | 43 | 41 | 0 | 0 | 0 | 0 | 57 | 10 | 0 | 220 | 18 | 0 | 10 | 320 | 8 | 0 | 50 | 275 | 158 | 75 | 132 | 75 | 123 | 5 | 33 | 187 | 135 | 402 | 96 | 105 | 102 | 3 | 248 | 22 | 88 | 17 | 98 | 38 | 396 | 17 | 18 | 23 | 107 | 0 | 17 | 13 | 35 | 0 | 0 | 0 | 0 |  | 885 | 0 | 235 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 85 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 18 | 0 | 8 | 75 | 0 | 251 | 0 | 0 | 186 | 0 | 0 | 130 | 0 | 0 | 160 | 0 | 352 | 17 | 0 | 113 | 15 | 45 | 0 | 3 | 90 | 870 | 182 | 0 | 0 | 2 | 35 | 74 | 0 | 0 | 0 | 5 |  | 6971 | 4031 | 11002 | 3628 | 885 | 1562 | 358 | 2674 | 1196 | 151 | 300 | 185 | 108 | 85 | 35 | 96.75
10:00 | 0 | 0 | 200 | 0 | 0 | 91 | 0 | 394 | 267 |  | 0 | 210 | 138 | 40 | 0 | 55 | 0 | 0 | 0 | 47 | 40 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 25 | 23 | 33 | 15 | 41 | 0 | 81 | 70 | 110 | 0 | 16 | 0 | 0 | 0 | 0 |  | 7 | 22 | 17 | 33 | 0 | 38 | 15 | 9 | 0 | 0 | 0 | 300 | 250 | 199 | 8 | 83 | 40 | 20 | 0 | 51 | 0 | 0 | 8 | 19 | 10 | 16 | 21 | 70 | 67 | 0 | 14 | 1 | 43 | 41 | 0 | 0 | 0 | 0 | 57 | 0 | 0 | 220 | 18 | 0 | 10 | 300 | 0 | 0 | 100 | 274 | 200 | 75 | 125 | 75 | 133 | 20 | 33 | 200 | 135 | 405 | 96 | 105 | 98 | 4 | 248 | 17 | 72 | 17 | 98 | 38 | 400 | 30 | 56 | 72 | 107 | 0 | 17 | 17 | 35 | 0 | 0 | 0 | 0 |  | 885 | 0 | 225 | 0 | 16 | 150 | 0 | 0 | 0 | 0 | 0 | 85 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 18 | 0 | 8 | 75 | 0 | 250 | 0 | 0 | 188 | 0 | 0 | 130 | 0 | 0 | 159 | 0 | 350 | 17 | 0 | 70 | 15 | 70 | 0 | 4 | 70 | 870 | 183 | 0 | 0 | 1 | 85 | 74 | 0 | 0 | 0 | 9 |  | 7327 | 4033 | 11360 | 3702 | 885 | 1673 | 450 | 2702 | 1195 | 151 | 280 | 185 | 70 | 197 | 53 | 96.76
11:00 | 0 | 0 | 200 | 0 | 0 | 99 | 0 | 404 | 273 |  | 0 | 225 | 132 | 43 | 0 | 55 | 0 | 0 | 0 | 47 | 40 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 0 | 19 | 25 | 22 | 33 | 15 | 41 | 0 | 76 | 70 | 110 | 0 | 16 | 0 | 0 | 0 | 0 |  | 12 | 22 | 17 | 33 | 0 | 38 | 15 | 5 | 0 | 0 | 0 | 300 | 250 | 200 | 8 | 83 | 40 | 20 | 0 | 51 | 0 | 0 | 8 | 19 | 10 | 16 | 21 | 74 | 66 | 0 | 14 | 1 | 43 | 41 | 0 | 0 | 0 | 0 | 57 | 0 | 0 | 220 | 18 | 0 | 0 | 315 | 0 | 0 | 185 | 273 | 223 | 75 | 123 | 75 | 133 | 13 | 33 | 200 | 132 | 405 | 87 | 90 | 87 | 2 | 248 | 21 | 69 | 17 | 94 | 38 | 400 | 44 | 40 | 72 | 107 | 0 | 17 | 35 | 34 | 0 | 0 | 0 | 0 |  | 886 | 0 | 215 | 0 | 16 | 160 | 0 | 0 | 0 | 0 | 0 | 83 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 8 | 75 | 0 | 250 | 0 | 0 | 188 | 0 | 0 | 133 | 0 | 4 | 157 | 0 | 330 | 17 | 0 | 74 | 15 | 70 | 0 | 4 | 90 | 890 | 216 | 0 | 0 | 3 | 54 | 74 | 0 | 0 | 0 | 18 |  | 7402 | 4066 | 11468 | 3697 | 886 | 1710 | 562 | 2660 | 1215 | 146 | 293 | 188 | 74 | 170 | 246 | 96.76
12:00 | 0 | 0 | 200 | 0 | 0 | 100 | 0 | 406 | 273 |  | 0 | 225 | 130 | 41 | 0 | 55 | 0 | 0 | 0 | 47 | 40 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 0 | 19 | 25 | 21 | 33 | 15 | 41 | 0 | 81 | 70 | 110 | 0 | 16 | 0 | 0 | 0 | 0 |  | 12 | 22 | 17 | 33 | 0 | 38 | 15 | 10 | 0 | 0 | 0 | 300 | 250 | 200 | 8 | 83 | 36 | 20 | 0 | 51 | 0 | 0 | 8 | 19 | 8 | 14 | 21 | 72 | 65 | 0 | 14 | 2 | 42 | 41 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 220 | 18 | 0 | 8 | 300 | 0 | 0 | 188 | 273 | 223 | 75 | 141 | 75 | 133 | 14 | 33 | 200 | 132 | 405 | 87 | 90 | 102 | 3 | 248 | 27 | 84 | 17 | 98 | 38 | 384 | 55 | 46 | 72 | 107 | 0 | 17 | 34 | 34 | 0 | 0 | 0 | 0 |  | 885 | 0 | 215 | 0 | 16 | 180 | 0 | 0 | 0 | 0 | 0 | 83 | 19 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 76 | 0 | 250 | 0 | 0 | 187 | 0 | 0 | 165 | 0 | 10 | 158 | 0 | 340 | 17 | 20 | 108 | 15 | 73 | 0 | 5 | 76 | 890 | 214 | 0 | 0 | 3 | 97 | 94 | 0 | 0 | 0 | 30 |  | 7453 | 4259 | 11712 | 3662 | 885 | 1715 | 591 | 2786 | 1216 | 151 | 345 | 220 | 72 | 234 | 347 | 96.78
13:00 | 0 | 0 | 200 | 0 | 0 | 100 | 0 | 400 | 273 |  | 0 | 225 | 135 | 41 | 0 | 55 | 0 | 0 | 0 | 47 | 40 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 0 | 19 | 25 | 20 | 33 | 15 | 41 | 0 | 81 | 70 | 110 | 0 | 17 | 0 | 0 | 0 | 0 |  | 12 | 22 | 16 | 33 | 0 | 32 | 15 | 13 | 0 | 0 | 0 | 300 | 250 | 187 | 8 | 82 | 42 | 25 | 0 | 51 | 0 | 20 | 8 | 19 | 10 | 14 | 21 | 82 | 41 | 0 | 14 | 2 | 42 | 41 | 0 | 0 | 0 | 0 | 57 | 0 | 0 | 220 | 18 | 0 | 10 | 320 | 0 | 0 | 187 | 274 | 226 | 75 | 139 | 75 | 133 | 0 | 33 | 200 | 133 | 397 | 86 | 105 | 105 | 5 | 248 | 24 | 91 | 17 | 95 | 38 | 384 | 55 | 43 | 72 | 107 | 0 | 17 | 35 | 34 | 0 | 0 | 0 | 0 |  | 884 | 0 | 220 | 0 | 16 | 217 | 0 | 0 | 0 | 0 | 0 | 81 | 19 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 8 | 76 | 0 | 250 | 0 | 0 | 187 | 0 | 0 | 180 | 0 | 10 | 156 | 0 | 323 | 17 | 10 | 113 | 15 | 73 | 0 | 4 | 95 | 920 | 216 | 0 | 0 | 4 | 79 | 94 | 0 | 0 | 0 | 23 |  | 7475 | 4323 | 11798 | 3628 | 884 | 1735 | 583 | 2823 | 1246 | 151 | 397 | 254 | 82 | 195 | 326 | 96.8
14:00 | 0 | 0 | 220 | 0 | 0 | 100 | 0 | 408 | 263 |  | 0 | 210 | 135 | 42 | 0 | 55 | 0 | 0 | 0 | 47 | 40 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 12 | 19 | 25 | 20 | 33 | 15 | 41 | 0 | 81 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 22 | 15 | 33 | 0 | 33 | 15 | 10 | 0 | 0 | 0 | 300 | 250 | 189 | 8 | 82 | 38 | 20 | 0 | 51 | 0 | 30 | 8 | 19 | 10 | 14 | 21 | 82 | 41 | 0 | 14 | 2 | 43 | 41 | 0 | 0 | 0 | 0 | 56 | 0 | 0 | 220 | 18 | 0 | 10 | 300 | 0 | 0 | 189 | 273 | 226 | 75 | 140 | 75 | 133 | 0 | 33 | 200 | 132 | 405 | 86 | 105 | 105 | 2 | 249 | 22 | 94 | 17 | 96 | 38 | 381 | 55 | 32 | 72 | 107 | 0 | 17 | 11 | 35 | 0 | 0 | 0 | 0 |  | 889 | 0 | 220 | 0 | 16 | 217 | 0 | 0 | 0 | 0 | 0 | 82 | 22 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 16 | 0 | 8 | 76 | 0 | 250 | 0 | 0 | 187 | 0 | 0 | 180 | 0 | 10 | 155 | 0 | 330 | 17 | 10 | 113 | 15 | 72 | 0 | 5 | 95 | 920 | 217 | 0 | 0 | 4 | 43 | 94 | 0 | 0 | 0 | 25 |  | 7451 | 4312 | 11763 | 3659 | 889 | 1692 | 585 | 2855 | 1246 | 151 | 397 | 263 | 82 | 124 | 334 | 96.82
15:00 | 0 | 0 | 200 | 0 | 0 | 100 | 0 | 406 | 253 |  | 0 | 210 | 145 | 42 | 0 | 55 | 0 | 0 | 0 | 47 | 40 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 19 | 25 | 20 | 33 | 15 | 40 | 0 | 82 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 23 | 16 | 33 | 0 | 33 | 12 | 7 | 0 | 0 | 0 | 300 | 250 | 186 | 8 | 82 | 41 | 20 | 0 | 51 | 0 | 27 | 8 | 19 | 10 | 17 | 21 | 90 | 39 | 0 | 14 | 2 | 42 | 41 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 220 | 18 | 0 | 10 | 310 | 0 | 0 | 188 | 275 | 226 | 75 | 139 | 75 | 134 | 5 | 33 | 200 | 133 | 395 | 84 | 90 | 105 | 2 | 249 | 17 | 105 | 17 | 95 | 38 | 382 | 50 | 41 | 72 | 107 | 0 | 17 | 26 | 35 | 0 | 0 | 0 | 0 |  | 891 | 0 | 215 | 0 | 16 | 217 | 0 | 0 | 0 | 0 | 0 | 84 | 20 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 17 | 0 | 8 | 76 | 0 | 250 | 0 | 0 | 183 | 0 | 0 | 191 | 0 | 60 | 155 | 0 | 318 | 20 | 38 | 113 | 15 | 71 | 0 | 4 | 95 | 930 | 220 | 0 | 0 | 1 | 21 | 93 | 0 | 0 | 0 | 12 |  | 7445 | 4374 | 11819 | 3613 | 891 | 1689 | 662 | 2862 | 1256 | 152 | 408 | 273 | 90 | 114 | 433 | 96.84
16:00 | 0 | 0 | 200 | 0 | 0 | 100 | 0 | 407 | 253 |  | 0 | 210 | 145 | 41 | 0 | 55 | 0 | 0 | 0 | 47 | 40 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 19 | 25 | 20 | 33 | 14 | 40 | 0 | 81 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 23 | 17 | 33 | 0 | 34 | 15 | 6 | 0 | 0 | 0 | 280 | 250 | 186 | 8 | 83 | 40 | 20 | 0 | 51 | 0 | 27 | 8 | 19 | 10 | 22 | 21 | 80 | 35 | 0 | 11 | 1 | 43 | 41 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 220 | 18 | 0 | 10 | 300 | 0 | 0 | 187 | 275 | 225 | 75 | 139 | 75 | 134 | 0 | 33 | 200 | 132 | 404 | 83 | 105 | 105 | 0 | 249 | 36 | 105 | 17 | 101 | 38 | 385 | 50 | 25 | 72 | 107 | 0 | 17 | 16 | 35 | 0 | 0 | 0 | 0 |  | 891 | 0 | 215 | 0 | 21 | 214 | 0 | 0 | 0 | 0 | 0 | 84 | 19 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 17 | 0 | 11 | 76 | 0 | 250 | 0 | 0 | 180 | 0 | 0 | 212 | 0 | 0 | 154 | 0 | 317 | 35 | 0 | 113 | 15 | 71 | 0 | 3 | 95 | 910 | 216 | 0 | 0 | 0 | 27 | 94 | 0 | 0 | 0 | 5 |  | 7421 | 4302 | 11723 | 3607 | 891 | 1672 | 562 | 2938 | 1236 | 151 | 426 | 295 | 80 | 77 | 377 | 96.86
17:00 | 0 | 0 | 193 | 0 | 0 | 100 | 0 | 408 | 253 |  | 0 | 210 | 145 | 38 | 0 | 55 | 0 | 0 | 0 | 50 | 40 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 19 | 25 | 20 | 33 | 14 | 48 | 0 | 81 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 23 | 17 | 33 | 0 | 37 | 15 | 13 | 0 | 0 | 0 | 280 | 250 | 196 | 8 | 82 | 37 | 20 | 0 | 51 | 0 | 27 | 8 | 19 | 10 | 27 | 21 | 74 | 60 | 0 | 14 | 0 | 43 | 41 | 0 | 0 | 0 | 0 | 58 | 0 | 0 | 220 | 18 | 0 | 10 | 290 | 0 | 0 | 100 | 273 | 84 | 75 | 141 | 75 | 147 | 2 | 33 | 200 | 130 | 404 | 94 | 105 | 105 | 1 | 249 | 36 | 105 | 34 | 112 | 38 | 390 | 55 | 8 | 76 | 107 | 0 | 17 | 6 | 72 | 27 | 0 | 0 | 0 |  | 891 | 0 | 220 | 0 | 16 | 180 | 0 | 0 | 0 | 15 | 0 | 72 | 17 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 8 | 0 | 17 | 0 | 11 | 75 | 0 | 249 | 0 | 0 | 180 | 0 | 0 | 180 | 0 | 0 | 154 | 0 | 322 | 35 | 0 | 50 | 15 | 70 | 0 | 1 | 35 | 890 | 185 | 0 | 0 | 0 | 15 | 34 | 0 | 0 | 0 | 1 |  | 7337 | 3995 | 11332 | 3644 | 891 | 1641 | 334 | 2891 | 1214 | 151 | 360 | 278 | 74 | 34 | 244 | 96.87
18:00 | 0 | 0 | 200 | 0 | 0 | 100 | 0 | 409 | 254 |  | 0 | 210 | 145 | 47 | 0 | 55 | 0 | 0 | 0 | 77 | 40 | 64 | 0 | 0 | 0 | 0 | 54 | 35 | 17 | 19 | 25 | 20 | 33 | 14 | 48 | 0 | 82 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 23 | 39 | 67 | 0 | 39 | 15 | 8 | 0 | 0 | 0 | 280 | 250 | 199 | 8 | 84 | 42 | 20 | 0 | 51 | 0 | 27 | 8 | 19 | 7 | 25 | 21 | 122 | 47 | 0 | 14 | 0 | 43 | 41 | 0 | 0 | 0 | 0 | 61 | 78 | 0 | 220 | 18 | 0 | 10 | 260 | 8 | 0 | 10 | 273 | 13 | 25 | 150 | 25 | 149 | 0 | 90 | 200 | 132 | 403 | 94 | 105 | 105 | 0 | 255 | 36 | 105 | 34 | 113 | 38 | 360 | 69 | 0 | 141 | 107 | 0 | 17 | 0 | 109 | 55 | 0 | 0 | 0 |  | 892 | 0 | 215 | 0 | 27 | 180 | 0 | 0 | 33 | 40 | 0 | 87 | 18 | 32 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 42 | 9 | 8 | 15 | 18 | 0 | 11 | 78 | 0 | 250 | 0 | 0 | 180 | 0 | 0 | 180 | 0 | 0 | 154 | 0 | 321 | 35 | 0 | 50 | 67 | 71 | 0 | 0 | 35 | 850 | 183 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 |  | 7532 | 4131 | 11663 | 3634 | 892 | 1684 | 73 | 3302 | 1178 | 152 | 360 | 446 | 122 | 0 | 236 | 96.88
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 230 | 0 | 0 | 100 | 0 | 405 | 251 |  | 0 | 210 | 145 | 79 | 0 | 55 | 0 | 0 | 0 | 88 | 92 | 115 | 0 | 0 | 0 | 0 | 54 | 35 | 17 | 19 | 25 | 20 | 33 | 14 | 48 | 0 | 82 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 23 | 51 | 78 | 0 | 39 | 15 | 18 | 0 | 0 | 0 | 280 | 250 | 198 | 8 | 82 | 42 | 20 | 0 | 51 | 0 | 29 | 15 | 19 | 7 | 31 | 18 | 132 | 82 | 0 | 14 | 0 | 43 | 41 | 0 | 0 | 0 | 0 | 63 | 78 | 0 | 220 | 18 | 0 | 10 | 280 | 8 | 0 | 50 | 273 | 108 | 90 | 152 | 90 | 149 | 0 | 90 | 200 | 140 | 403 | 96 | 105 | 105 | 0 | 274 | 36 | 105 | 34 | 114 | 78 | 400 | 94 | 0 | 144 | 107 | 0 | 17 | 0 | 115 | 55 | 0 | 0 | 0 |  | 891 | 0 | 215 | 0 | 32 | 226 | 0 | 0 | 44 | 50 | 0 | 85 | 26 | 32 | 0 | 0 | 0 | 24 | 0 | 80 | 0 | 42 | 25 | 8 | 26 | 18 | 0 | 11 | 79 | 0 | 250 | 0 | 0 | 180 | 0 | 0 | 208 | 0 | 20 | 154 | 0 | 327 | 55 | 50 | 72 | 67 | 71 | 0 | 0 | 80 | 970 | 183 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 0 |  | 8221 | 4691 | 12912 | 3735 | 891 | 1725 | 408 | 3669 | 1299 | 152 | 434 | 675 | 132 | 0 | 970 | 96.93
19:30 | 0 | 0 | 230 | 0 | 0 | 100 | 0 | 409 | 251 |  | 0 | 210 | 145 | 83 | 0 | 55 | 0 | 0 | 0 | 88 | 92 | 115 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 20 | 33 | 14 | 48 | 0 | 81 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 26 | 51 | 78 | 0 | 39 | 15 | 25 | 0 | 0 | 0 | 280 | 250 | 199 | 8 | 83 | 42 | 20 | 0 | 51 | 0 | 28 | 43 | 19 | 7 | 32 | 21 | 126 | 98 | 0 | 14 | 0 | 43 | 41 | 0 | 0 | 0 | 0 | 59 | 78 | 0 | 220 | 18 | 0 | 10 | 315 | 8 | 0 | 60 | 273 | 111 | 90 | 152 | 88 | 149 | 0 | 90 | 200 | 143 | 404 | 96 | 105 | 105 | 0 | 270 | 36 | 105 | 34 | 115 | 90 | 390 | 94 | 0 | 144 | 107 | 0 | 17 | 0 | 115 | 55 | 0 | 0 | 0 |  | 891 | 0 | 220 | 0 | 32 | 225 | 0 | 0 | 37 | 45 | 0 | 85 | 25 | 32 | 0 | 0 | 0 | 24 | 0 | 80 | 0 | 42 | 32 | 8 | 26 | 18 | 0 | 11 | 78 | 0 | 250 | 0 | 0 | 180 | 0 | 0 | 215 | 0 | 20 | 154 | 0 | 328 | 56 | 50 | 113 | 67 | 71 | 0 | 0 | 95 | 1020 | 220 | 0 | 0 | 0 | 0 | 94 | 0 | 0 | 0 | 0 |  | 8364 | 4844 | 13208 | 3753 | 891 | 1804 | 419 | 3812 | 1348 | 151 | 440 | 679 | 126 | 0 | 959 | 0
20:00 | 0 | 0 | 230 | 0 | 0 | 100 | 0 | 407 | 251 |  | 0 | 210 | 145 | 83 | 0 | 55 | 0 | 0 | 0 | 88 | 92 | 115 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 20 | 33 | 14 | 48 | 0 | 81 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 31 | 51 | 78 | 0 | 40 | 15 | 30 | 0 | 0 | 0 | 280 | 250 | 194 | 8 | 82 | 42 | 20 | 0 | 51 | 0 | 28 | 43 | 19 | 7 | 32 | 21 | 126 | 99 | 0 | 13 | 0 | 43 | 41 | 0 | 0 | 0 | 0 | 61 | 78 | 0 | 220 | 18 | 0 | 10 | 280 | 8 | 0 | 189 | 273 | 177 | 90 | 151 | 90 | 149 | 0 | 90 | 200 | 140 | 378 | 96 | 105 | 105 | 0 | 275 | 36 | 105 | 34 | 115 | 90 | 400 | 94 | 0 | 144 | 107 | 0 | 17 | 0 | 115 | 55 | 0 | 0 | 0 |  | 891 | 0 | 220 | 0 | 32 | 227 | 0 | 0 | 37 | 45 | 0 | 86 | 27 | 32 | 0 | 0 | 0 | 24 | 0 | 80 | 0 | 42 | 32 | 8 | 26 | 18 | 0 | 11 | 78 | 0 | 250 | 0 | 0 | 180 | 0 | 0 | 214 | 0 | 94 | 154 | 0 | 333 | 56 | 63 | 113 | 67 | 71 | 0 | 0 | 95 | 1040 | 224 | 0 | 0 | 0 | 0 | 94 | 0 | 0 | 0 | 0 |  | 8516 | 4964 | 13480 | 3732 | 891 | 1785 | 703 | 3814 | 1368 | 151 | 441 | 683 | 126 | 0 | 505 | 96.91
21:00 | 0 | 0 | 230 | 0 | 0 | 100 | 0 | 407 | 252 |  | 0 | 210 | 145 | 80 | 0 | 55 | 0 | 0 | 0 | 88 | 92 | 78 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 19 | 25 | 20 | 33 | 14 | 48 | 0 | 81 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 31 | 51 | 78 | 0 | 39 | 15 | 28 | 0 | 0 | 0 | 280 | 250 | 191 | 8 | 83 | 42 | 30 | 0 | 51 | 0 | 27 | 43 | 19 | 7 | 32 | 21 | 126 | 99 | 0 | 13 | 0 | 43 | 41 | 0 | 0 | 0 | 0 | 63 | 78 | 0 | 220 | 18 | 0 | 10 | 280 | 8 | 0 | 190 | 273 | 183 | 90 | 151 | 90 | 149 | 0 | 90 | 200 | 140 | 402 | 96 | 105 | 105 | 0 | 275 | 36 | 105 | 34 | 115 | 90 | 400 | 94 | 0 | 144 | 107 | 0 | 17 | 0 | 115 | 55 | 0 | 0 | 0 |  | 891 | 0 | 225 | 0 | 32 | 227 | 0 | 0 | 32 | 40 | 0 | 86 | 28 | 32 | 0 | 0 | 0 | 24 | 0 | 80 | 0 | 42 | 32 | 8 | 26 | 18 | 0 | 11 | 78 | 0 | 250 | 0 | 0 | 180 | 0 | 0 | 216 | 0 | 94 | 154 | 0 | 334 | 55 | 90 | 113 | 67 | 71 | 0 | 0 | 95 | 1080 | 224 | 0 | 0 | 0 | 0 | 94 | 0 | 0 | 0 | 0 |  | 8514 | 5029 | 13543 | 3761 | 891 | 1796 | 737 | 3809 | 1408 | 151 | 443 | 637 | 126 | 0 | 388 | 96.93
22:00 | 0 | 0 | 230 | 0 | 0 | 100 | 0 | 408 | 252 |  | 0 | 210 | 145 | 83 | 0 | 55 | 0 | 0 | 0 | 88 | 92 | 78 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 19 | 25 | 20 | 33 | 14 | 48 | 0 | 81 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 31 | 51 | 78 | 0 | 40 | 15 | 31 | 0 | 0 | 0 | 280 | 250 | 196 | 8 | 83 | 42 | 30 | 0 | 51 | 0 | 27 | 36 | 19 | 7 | 32 | 21 | 136 | 128 | 0 | 13 | 0 | 43 | 41 | 0 | 0 | 0 | 0 | 60 | 78 | 0 | 220 | 18 | 0 | 10 | 290 | 8 | 0 | 170 | 273 | 143 | 90 | 150 | 90 | 149 | 0 | 90 | 200 | 140 | 402 | 96 | 105 | 105 | 0 | 264 | 36 | 105 | 34 | 115 | 90 | 400 | 94 | 0 | 144 | 107 | 0 | 17 | 0 | 115 | 55 | 0 | 0 | 0 |  | 892 | 0 | 225 | 0 | 32 | 225 | 0 | 0 | 32 | 38 | 0 | 85 | 29 | 32 | 0 | 0 | 0 | 24 | 0 | 80 | 0 | 42 | 32 | 8 | 26 | 18 | 0 | 11 | 78 | 0 | 250 | 0 | 0 | 180 | 0 | 0 | 215 | 0 | 94 | 154 | 0 | 340 | 55 | 60 | 113 | 67 | 71 | 0 | 0 | 95 | 1050 | 224 | 0 | 0 | 0 | 0 | 94 | 0 | 0 | 0 | 0 |  | 8494 | 4971 | 13465 | 3792 | 892 | 1816 | 647 | 3794 | 1378 | 151 | 440 | 634 | 136 | 0 | 276.4725 | 96.95
23:00 | 0 | 0 | 230 | 0 | 0 | 100 | 0 | 408 | 252 |  | 0 | 210 | 145 | 79 | 0 | 45 | 0 | 0 | 0 | 89 | 92 | 48 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 19 | 25 | 20 | 33 | 14 | 48 | 0 | 81 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 31 | 51 | 78 | 0 | 40 | 15 | 32 | 0 | 0 | 0 | 280 | 250 | 187 | 8 | 82 | 42 | 40 | 0 | 51 | 0 | 27 | 8 | 19 | 7 | 32 | 21 | 142 | 133 | 0 | 13 | 0 | 43 | 41 | 0 | 0 | 0 | 0 | 60 | 78 | 0 | 220 | 18 | 0 | 10 | 295 | 8 | 0 | 140 | 273 | 219 | 90 | 151 | 90 | 149 | 0 | 90 | 200 | 140 | 404 | 95 | 105 | 105 | 0 | 249 | 36 | 105 | 34 | 115 | 90 | 400 | 94 | 0 | 144 | 107 | 0 | 17 | 0 | 115 | 55 | 0 | 0 | 0 |  | 900 | 0 | 225 | 0 | 16 | 225 | 0 | 0 | 16 | 38 | 0 | 85 | 28 | 32 | 0 | 0 | 0 | 24 | 0 | 80 | 0 | 42 | 24 | 8 | 26 | 18 | 0 | 11 | 77 | 0 | 250 | 0 | 0 | 181 | 0 | 0 | 216 | 0 | 94 | 154 | 0 | 343 | 55 | 60 | 113 | 67 | 71 | 0 | 0 | 95 | 1040 | 224 | 0 | 0 | 0 | 0 | 94 | 0 | 0 | 0 | 0 |  | 8473 | 4932 | 13405 | 3790 | 900 | 1834 | 693 | 3722 | 1367 | 151 | 441 | 581 | 142 | 0 | 365.8653 | 96.97
24:00 | 0 | 0 | 230 | 0 | 0 | 100 | 0 | 407 | 257 |  | 0 | 225 | 145 | 47 | 0 | 50 | 0 | 0 | 0 | 59 | 40 | 48 | 0 | 0 | 0 | 0 | 17 | 35 | 55 | 19 | 25 | 21 | 33 | 16 | 41 | 0 | 82 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 31 | 51 | 33 | 0 | 40 | 15 | 32 | 0 | 0 | 0 | 280 | 250 | 187 | 8 | 83 | 42 | 40 | 0 | 51 | 0 | 29 | 8 | 19 | 7 | 33 | 21 | 126 | 134 | 0 | 13 | 0 | 43 | 41 | 0 | 0 | 0 | 0 | 62 | 10 | 0 | 220 | 18 | 0 | 10 | 290 | 8 | 0 | 30 | 273 | 20 | 75 | 152 | 75 | 135 | 0 | 33 | 200 | 138 | 402 | 95 | 105 | 105 | 0 | 250 | 36 | 105 | 17 | 64 | 52 | 400 | 94 | 0 | 17 | 107 | 0 | 17 | 0 | 55 | 0 | 0 | 0 | 0 |  | 900 | 0 | 230 | 0 | 16 | 228 | 0 | 0 | 10 | 25 | 0 | 85 | 22 | 32 | 0 | 0 | 0 | 24 | 0 | 30 | 0 | 42 | 24 | 8 | 26 | 18 | 0 | 11 | 76 | 0 | 250 | 0 | 0 | 180 | 0 | 0 | 215 | 0 | 94 | 154 | 0 | 343 | 17 | 100 | 113 | 15 | 71 | 0 | 0 | 95 | 1010 | 224 | 0 | 0 | 0 | 0 | 94 | 0 | 0 | 0 | 0 |  | 7456 | 4782 | 12238 | 3799 | 900 | 1775 | 394 | 3015 | 1336 | 152 | 443 | 513 | 126 | 0 | 978.7127 | 96.99
KWH | 0 | 0 | 5193000 | 0 | 0 | 1940363 | 0 | 9189380 | 5116000 |  | 0 | 4608000 | 3295942 | 1206720 | 0 | 1314099 | 0 | 0 | 0 | 1378560 | 1201968 | 1007520 | 0 | 0 | 0 | 0 | 653760 | 895320 | 718347 | 404712 | 600000 | 506880 | 794880 | 388500 | 1109760 | 0 | 1965376 | 1692000 | 2600000 | 0 | 505755 | 0 | 0 | 0 | 0 |  | 269280 | 569280 | 618026 | 1029720 | 0 | 854400 | 349728 | 507360 | 0 | 0 | 0 | 7431200 | 6087000 | 4609000 | 217454 | 1987010 | 988560 | 672960 | 0 | 1196574 | 0 | 497512 | 317626 | 417780 | 211500 | 627900 | 497300 | 2646720 | 2061120 | 0 | 296496 | 8900 | 1021000 | 957552 | 0 | 0 | 0 | 0 | 1407072 | 712320 | 0 | 5258110 | 423000 | 0 | 234000 | 7236500 | 120072 | 0 | 3176448 | 6561273 | 3664768 | 1651875 | 3420000 | 1611679 | 3293424 | 75060 | 1090560 | 4590720 | 3295272 | 9611000 | 2212800 | 2329200 | 2335127 | 26281 | 5986691 | 803925 | 2324244 | 532380 | 2446080 | 1183680 | 9222000 | 1421760 | 342440 | 1654560 | 2481491 | 0 | 443880 | 222042 | 1379520 | 370440 | 0 | 0 | 0 |  | 21509090 | 0 | 5534784 | 0 | 421440 | 4970880 | 0 | 0 | 204480 | 289024 | 0 | 2040653 | 532354 | 550752 | 0 | 0 | 0 | 135296 | 0 | 404224 | 0 | 332382 | 143733 | 141010 | 163990 | 419520 | 0 | 188766 | 1826618 | 0 | 6068200 | 0 | 0 | 4633391 | 0 | 0 | 4678182 | 0 | 985920 | 4023518 | 0 | 8211418 | 690720 | 1432649 | 2534304 | 605088 | 1679856 | 0 | 35040 | 1993920 | 24683600 | 5196955 | 0 | 0 | 25500 | 527760 | 1994880 | 0 | 0 | 0 | 140900 |  | 180387494 | 109950797 | 290338291 | 89682864 | 21509090 | 40097720 | 12523339 | 72556694 | 32578418 | 3657376 | 9649062 | 4033085 | 2646720 | 1403923 | 0
Fuel Cost | 0 | 0 | 7581780 | 0 | 0 | 2580682.79 | 0 | 9648849 | 5525280 |  | 0 | 5022720 | 3658495.62 | 13491129.6 | 0 | 17411811.75 | 0 | 0 | 0 | 20154547.2 | 16911689.76 | 16331899.2 | 0 | 0 | 0 | 0 | 8315827.2 | 12086820 | 9633033.27 | 303534 | 450000 | 0 | 0 | 0 | 18877017.6 | 0 | 530651.52 | 456840 | 4914000 | 0 | 8269094.25 | 0 | 0 | 0 | 0 |  | 3514104 | 9495590.4 | 10518802.52 | 13911517.2 | 0 | 9885408 | 444154.56 | 1689508.8 | 0 | 0 | 0 | 8248632 | 6634830 | 5346440 | 280515.66 | 2424152.2 | 1117072.8 | 1002710.4 | 0 | 1998278.58 | 0 | 8592032.24 | 4272069.7 | 572358.6 | 158625 | 1098825 | 372975 | 19003449.6 | 2246620.8 | 0 | 403234.56 | 141866 | 1398770 | 1263968.64 | 0 | 0 | 0 | 0 | 2729719.68 | 1624089.6 | 0 | 5310691.1 | 909450 | 0 | 463320 | 7236500 | 90054 | 0 | 66578350.08 | 89561376.45 | 76813537.28 | 34144256.25 | 46101600 | 33313404.93 | 45613922.4 | 877451.4 | 11254579.2 | 62709235.2 | 43728259.44 | 8842120 | 26907648 | 33680232 | 29539356.55 | 0 | 70283752.34 | 8754743.25 | 24706713.72 | 7224396.6 | 31529971.2 | 13943750.4 | 8484240 | 18411792 | 4948258 | 20996366.4 | 28239367.58 | 0 | 5797072.8 | 2653401.9 | 20651414.4 | 4878694.8 | 0 | 0 | 0 |  | 64527270 | 0 | 6198958.08 | 0 | 4387190.4 | 82019520 | 0 | 0 | 3682684.8 | 5202432 | 0 | 2285531.36 | 1032766.76 | 6003196.8 | 0 | 0 | 0 | 2268913.92 | 0 | 6322063.36 | 0 | 5504245.92 | 2430525.03 | 1921966.3 | 2766511.3 | 868406.4 | 0 | 142895.862 | 10612650.58 | 0 | 32100778 | 0 | 0 | 5374733.56 | 0 | 0 | 81681057.72 | 0 | 20684601.6 | 4667280.88 | 0 | 8129303.82 | 9283276.8 | 30042649.53 | 29980816.32 | 8743521.6 | 21334171.2 | 0 | 387192 | 24206188.8 | 222399236 | 5300894.1 | 0 | 0 | 288405 | 6190624.8 | 30581510.4 | 0 | 0 | 0 | 0 |  | 1197725303.97 | 749553971.002 | 1947279274.972 | 99664496.682 | 64527270 | 46413472.53 | 261576799.67 | 943194398.8 | 265112664.58 | 987491.52 | 163700577.72 | 67611454.77 | 19003449.6 | 15487199.1 | 0
Yesterday Day Peak | 0 | 0 | 200 | 0 | 0 | 100 | 0 | 406 | 273 |  | 0 | 225 | 130 | 41 | 0 | 55 | 0 | 0 | 0 | 47 | 40 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 0 | 19 | 25 | 21 | 33 | 15 | 41 | 0 | 81 | 70 | 110 | 0 | 16 | 0 | 0 | 0 | 0 |  | 12 | 22 | 17 | 33 | 0 | 38 | 15 | 10 | 0 | 0 | 0 | 300 | 250 | 200 | 8 | 83 | 36 | 20 | 0 | 51 | 0 | 0 | 8 | 19 | 8 | 14 | 21 | 72 | 65 | 0 | 14 | 2 | 42 | 41 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 220 | 18 | 0 | 8 | 300 | 0 | 0 | 188 | 273 | 223 | 75 | 141 | 75 | 133 | 14 | 33 | 200 | 132 | 405 | 87 | 90 | 102 | 3 | 248 | 27 | 84 | 17 | 98 | 38 | 384 | 55 | 46 | 72 | 107 | 0 | 17 | 34 | 34 | 0 | 0 | 0 | 0 |  | 885 | 0 | 215 | 0 | 16 | 180 | 0 | 0 | 0 | 0 | 0 | 83 | 19 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 76 | 0 | 250 | 0 | 0 | 187 | 0 | 0 | 165 | 0 | 10 | 158 | 0 | 340 | 17 | 20 | 108 | 15 | 73 | 0 | 5 | 76 | 890 | 214 | 0 | 0 | 3 | 97 | 94 | 0 | 0 | 0 | 30 |  | 11712 | DayPeak
Yesterday Evening Peak | 0 | 0 | 230 | 0 | 0 | 100 | 0 | 407 | 252 | 0 | 0 | 210 | 145 | 80 | 0 | 55 | 0 | 0 | 0 | 88 | 92 | 78 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 19 | 25 | 20 | 33 | 14 | 48 | 0 | 81 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 12 | 31 | 51 | 78 | 0 | 39 | 15 | 28 | 0 | 0 | 0 | 280 | 250 | 191 | 8 | 83 | 42 | 30 | 0 | 51 | 0 | 27 | 43 | 19 | 7 | 32 | 21 | 126 | 99 | 0 | 13 | 0 | 43 | 41 | 0 | 0 | 0 | 0 | 63 | 78 | 0 | 220 | 18 | 0 | 10 | 280 | 8 | 0 | 190 | 273 | 183 | 90 | 151 | 90 | 149 | 0 | 90 | 200 | 140 | 402 | 96 | 105 | 105 | 0 | 275 | 36 | 105 | 34 | 115 | 90 | 400 | 94 | 0 | 144 | 107 | 0 | 17 | 0 | 115 | 55 | 0 | 0 | 0 |  | 891 | 0 | 225 | 0 | 32 | 227 | 0 | 0 | 32 | 40 | 0 | 86 | 28 | 32 | 0 | 0 | 0 | 24 | 0 | 80 | 0 | 42 | 32 | 8 | 26 | 18 | 0 | 11 | 78 | 0 | 250 | 0 | 0 | 180 | 0 | 0 | 216 | 0 | 94 | 154 | 0 | 334 | 55 | 90 | 113 | 67 | 71 | 0 | 0 | 95 | 1080 | 224 | 0 | 0 | 0 | 0 | 94 | 0 | 0 | 0 | 0 |  | 13543 | EvPeak
Forecast for Evening | 0 | 0 | 230 | 0 | 0 | 100 | 0 | 400 | 250 | 0 | 0 | 225 | 140 | 80 | 0 | 55 | 0 | 0 | 0 | 90 | 92 | 130 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 25 | 33 | 24 | 49 | 0 | 81 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 12 | 25 | 51 | 80 | 0 | 40 | 15 | 20 | 0 | 0 | 0 | 280 | 250 | 185 | 8 | 83 | 40 | 30 | 0 | 51 | 0 | 29 | 43 | 19 | 10 | 33 | 21 | 165 | 100 | 0 | 14 | 0 | 43 | 41 | 0 | 0 | 0 | 0 | 60 | 78 | 0 | 220 | 18 | 0 | 10 | 280 | 0 | 0 | 190 | 275 | 180 | 90 | 150 | 90 | 149 | 0 | 90 | 200 | 140 | 400 | 105 | 105 | 105 | 0 | 275 | 36 | 105 | 34 | 113 | 100 | 400 | 90 | 0 | 162 | 107 | 0 | 17 |  | 115 | 55 |  |  |  |  | 918 | 0 | 230 | 0 | 32 | 225 | 0 | 0 | 35 | 40 | 0 | 85 | 25 | 32 | 0 | 0 | 0 | 32 | 0 | 81 | 0 | 42 | 32 | 8 | 26 | 18 | 0 | 11 | 78 | 0 | 250 | 0 | 0 | 180 | 0 | 0 | 210 | 0 | 95 | 150 | 0 | 300 | 55 | 170 | 113 | 60 | 71 | 0 | 0 | 95 | 1110 | 220 |  | 17 |  |  | 90
Forecast for Day | 0 | 0 | 230 | 0 | 0 | 90 | 0 | 390 | 250 | 0 | 0 | 225 | 140 | 40 | 0 | 55 | 0 | 0 | 0 | 45 | 40 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 25 | 25 | 33 | 24 | 32 | 0 | 81 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 12 | 20 | 17 | 33 | 0 | 40 | 15 | 5 | 0 | 0 | 0 | 280 | 250 | 180 | 8 | 83 | 40 | 20 | 0 | 51 | 0 | 29 | 8 | 19 | 10 | 33 | 21 | 143 | 70 | 0 | 14 | 1.6 | 43 | 41 | 0 | 0 | 0 | 0 | 60 | 10 | 0 | 220 | 18 | 0 | 10 | 265 | 0 | 0 | 150 | 275 | 120 | 75 | 150 | 75 | 149 | 20 | 33 | 120 | 135 | 400 | 97 | 105 | 105 | 5 | 250 | 36 | 88 | 17 | 97 | 38 | 400 | 50 | 50 | 72 | 107 | 0 | 17 | 30 | 35 | 0 |  |  |  |  | 918 | 0 | 230 | 0 | 16 | 150 | 0 | 0 | 0 | 0 | 0 | 85 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 16 | 8 | 0 | 18 | 0 | 11 | 78 | 0 | 250 | 0 | 0 | 180 | 0 | 0 | 150 | 0 | 50 | 150 | 0 | 260 | 17 | 100 | 113 | 15 | 50 | 0 | 8 | 50 | 1110 | 220 |  | 17 | 6 | 100 | 70 |  |  |  | 12
Generation at 08:00(Today) | 0 | 0 | 230 | 0 | 0 | 94 | 0 | 396 | 307 | 0 | 0 | 225 | 143 | 43 | 0 | 55 | 0 | 0 | 0 | 46 | 40 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 25 | 27 | 0 | 15 | 32 | 0 | 81 | 70 | 110 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 12 | 23 | 17 | 33 | 0 | 40 | 15 | 12 | 0 | 0 | 0 | 280 | 250 | 193 | 8 | 83 | 43 | 40 | 0 | 51 | 0 | 29 | 8 | 19 | 7 | 25 | 9 | 118 | 70 | 0 | 14 | 1 | 43 | 41 | 0 | 0 | 0 | 0 | 61 | 10 | 0 | 220 | 18 | 0 | 10 | 265 | 0 | 0 | 0 | 273 | 0 | 0 | 154 | 0 | 149 | 10 | 33 | 165 | 137 | 353 | 97 | 0 | 68 | 2 | 249 | 36 | 88 | 17 | 48 | 38 | 350 | 17 | 16 | 17 | 107 | 0 | 17 | 12 | 35 | 0 | 0 | 0 | 0 | 0 | 901 | 0 | 235 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 0 | 85 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 8 | 0 | 18 | 0 | 11 | 80 | 0 | 250 | 0 | 0 | 188 | 0 | 0 | 130 | 0 | 0 | 162 | 0 | 262 | 17 | 0 | 50 | 15 | 0 | 0 | 2 | 50 | 880 | 183 | 0 | 0 | 2 | 34 | 75 | 0 | 0 | 0 | 9 | 0 |  |  |  |  | 98762180 |  | 0
98762180
| Minimum Generation |  | 10447 | 7:00
| Highest Generation |  | 13543 | 21:00
| Day Peak Generation |  | 11712 | 12:00
| Evening Peak Generation |  | 13543 | 21:00
| HVDC Max Flow |  | 900 | 23:00
| HVDC EvPeak Flow |  | 891 | 21:00
| Load factor L.F |  | 89.33% | [161 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2022-09-20
Till now the maximum generation is : - |  |  | 14782 | 21:00 | Hrs on | 2022-04-16
The Summary of Yesterday's |  | 2022-09-19 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 11712 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 10459 | MW
Evening Peak Generation : |  | 13543 | MW Hour : | 21:00 | Available Max Generation : |  | 13785 | MW
E.P. Demand (at gen end) : |  | 13964 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 14000 | MW
Maximum Generation : |  | 13543 | MW Hour : | 21:00 | Reserve(Generation end) |  | - | MW
Total Gen. (MKWH) : |  | 290.3383 | System Load Factor : | 89.33% | Load Shed : |  | 198 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | 1080 | MW at | 6:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2022-09-20
Actual : | 96.99 | Ft.(MSL) , | Rule curve : | 103.37 | Ft.( MSL )
Gas Consumed : | Total = | 1009.47 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 146077969.212
: |  | Coal : | 265112664.58 | Oil : | 1436083230.96 | Total : | 1847273864.752
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 29 | 696:00 | 4482.7268 |  |  | 55 | 1.227%
Chittagong Area | 0 | 0:00 | 1269.8786 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1676.1342 |  |  | 30 | 1.79%
Rajshahi Area | 0 | 0:00 | 1487.1485 |  |  | 25 | 1.681%
Cumilla Area | 51 | 1224:00 | 1265.9679 |  |  | 20 | 1.58%
Mymensingh Area | 213 | 5112:00 | 1045.8787 |  |  | 40 | 3.825%
Sylhet Area | 95 | 2280:00 | 467.4623 |  |  | 8 | 1.711%
Barisal Area | 0 | 0:00 | 381.0636 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 825.7894 |  |  | 20 | 2.422%
Total | 388 |  | 12902.05 |  |  | 198
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-2
2) Ghorasal-3,
3) Ashuganj-5
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
7) Sikalbaha 225 MW
8) Shajibazar 330 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Bheramara HVDC-Jhenaidah 230 kV Ckt-2 tripped at 08:46 showing Dist. C-phase ,auto reclose at
Jhenaidah end and was switched on at 09:28.
b) Hasnabad 132/33 kV T-2 transformer along with 33 kV Bus was under shut down from 10:33 to 12:32
for D/W.
c) Haripur 230 kV 808 Breaker was under shut down from 10:32 to 12:32 for C/M.
d) Haripur 230 kV 818 Breaker was under shut down from 10:32 to 11:27 for C/M.
e) Chandpur 132/33 kV T-5 transformer was under shut down from 09:41 to 17:53 due to R/H
maintenance at 33 kV end.
f) Bhandaria 132/33 kV T-2 transformer was under shut down from 14:18 to 14:38 for C/M.
g) Agargaon 230/132 kV T-2 transformer was shut down 05:30(20-09-2022) for D/W.
h) Purbasadipur 132/33 kV T-3 transformer was shut down 07:06(20-09-2022) for C/M. | [5 empty] | About 30 MW power interruption occurred under
Purbasadipur S/S area from 07:06(20-09-22) to till.
| Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2022-09-19 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 230 | 5193000
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Machine problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 100 | 1940363 | Engine problem
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 407 | 9189380
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 252 | 5116000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 210 | 4608000 | GT-2 S/D due to dirty gas
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 80 | 1206720 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 145 | 3295942 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 0 | 0 | Under maint.
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 55 | 1314099
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 404712
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 88 | 1378560 | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 92 | 1201968 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 653760
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 78 | 1007520 | Engine problem
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 35 | 895320 | Engine problem
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 718347
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 45 | 1106880 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 794880
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 14 | 388500 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 48 | 1109760 | #REF!
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 273 | 6561273 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 183 | 3664768 | High voltage
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 90 | 1651875 | Engine problem
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 90 | 1611679 | Engine problem
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 3293424
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 2329200
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 94 | 1421760 | Engine problem
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 144 | 1654560 | Fuel shortage
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 222042
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 55 | 370440
| Dhaka area Total |  |  |  | 5847 | 3223 | 64304732
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 110 | 2600000 | Machine problem
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 25 | 505755
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 75060
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 39 | 854400 | Engine problem
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 151 | 3657376 | Low water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | HGPI
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 105 | 2335127
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 31 | 569280 | Fuel shortage
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 618026 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 78 | 1029720 | Engine problem
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 90 | 1090560 | Engine problem
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 15 | 349728 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 28 | 507360
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 26281
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 275 | 5986691 | Engine problem
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 36 | 803925 | Engine problem
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 105 | 2324244
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 90 | 1183680
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 107 | 2481491 | Engine problem
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Chattogram area Total |  |  |  | 2382 | 1336 | 26998704
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 191 | 4609000 | #REF!
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 280 | 7431200 | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 250 | 6087000 | Gas shortage
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+136*1 | 284 | 0 | 0 | On test.
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 42 | 988560 | Engine problem
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 30 | 672960 | Gas shortage
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 217454 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1196574
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 140 | 3295272 | Engine problem
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 27 | 497512 | Engine problem
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 83 | 1987010 | Machine problem
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 200 | 4590720
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 417780
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 7 | 211500
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 126 | 2646720
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 32 | 627900
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 43 | 317626 | Engine problem
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 21 | 497300 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 190 | 3176448 | Engine problem
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 34 | 532380 | Fuel shortage
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 115 | 2446080
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 443880 | 33 kV feeder problem.
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 115 | 1379520
| Cumilla Area Total |  |  |  | 3169 | 2021 | 44270396
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 99 | 2061120 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 13 | 296496 | Gas shortage
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 8900
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 151 | 3420000 | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 96 | 2212800 | Engine problem
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 342440
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 269280 | Engine problem
| Mymensingh Area Total |  |  |  | 614 | 371 | 8611036
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1021000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 41 | 957552 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Gas shortage
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 0 | 0 | Gas shortage
| Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 0 | 0 | Gas shortage
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 0 | 0 | Gas shortage
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 63 | 1407072
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 78 | 712320 | Engine problem
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 220 | 5258110
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 423000
| Sylhet 50MW PP (EPL) |  | NENP | 27*2 | 50 | 0 | 0 | Gas shortage
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 8 | 120072 | Gas shortage
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 280 | 7236500 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 402 | 9611000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 234000
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 400 | 9222000
| Sylhet Area Total |  |  |  | 2477 | 1563 | 36202626
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 891 | 21509090
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 32 | 421440 | Fuel shortage
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 32 | 204480 | Engine problem
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 227 | 4970880
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 40 | 289024 | Engine problem
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 225 | 5534784 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 0 | 0 | Fuel shortage
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 94 | 985920 | Engine problem
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 55 | 690720 | Fuel shortage
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 67 | 605088 | Fuel shortage
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 527760
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 0 | 0 | 0 | On test.
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 0 | 0 | 0 | 0 | On test.
| Khulna Area Total |  |  |  | 2384 | 1663 | 35739186
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 32 | 550752 | Line O/L
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 28 | 532354 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 86 | 2040653 | Gas shortage
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1080 | 24683600 | Line O/L
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 224 | 5196955
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Line O/L
| Barisal Area Total |  |  |  | 1958 | 1450 | 33004314
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 24 | 135296 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under maint.
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contract Expired
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 42 | 332382 | Engine problem
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 143733 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 180 | 4633391 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 216 | 4678182
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 154 | 4023518 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 334 | 8211418 | Gas shortage
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 26 | 163990 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 18 | 419520
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | .
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 188766
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 8 | 141010 | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 80 | 404224 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 90 | 1432649 | Line O/L
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 2534304
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 95 | 1993920 | Engine problem
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 25500
| Rajshahi Area Total |  |  |  | 2129 | 1423 | 29461803
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 78 | 1826618
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 250 | 6068200 | Coal shortage
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 71 | 1679856 | Engine problem
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 35040
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 94 | 1994880 | Engine problem
| Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 140900
| Rangpur Area Total |  |  |  | 750 | 493 | 11745494
| Total |  |  |  | 21710 | 13543 | 290338291
| Eastern Grid Total |  |  |  | 14489 | 8514 | 180387494
| Western Grid Total |  |  |  | 7221 | 5029 | 109950797
| National Grid Total |  |  |  | 21710 | 13543 | 290338291
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2022-09-19
(a) ENTIRE EASTERN GRID : |  | 8795.56 | MW | (b) ENTIRE WESTERN GRID : |  | 4253 | MW
i) Dhaka area |  | 4799.51 | MW | i) Khulna area |  | 1594.6 | MW
ii) Chittagong area |  | 1266.05 | MW | ii) Rajshahi area |  | 1387.4 | MW
iii) Comilla area |  | 1268 | MW | iii) Barisal area |  | 368 | MW
iv) Mymensingh area |  | 923 | MW | iv) Rangpur area |  | 903 | MW
v) Sylhet area |  | 539 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 13048.56 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
AKS | 0 | 00:00 | Chowmuhani | 208 | 21:00 | Kaptai | 5 | 18:30 | Nawabganj | 36.9 | 19:00 | Siddhirganj | 108 | 22:00
AKSML | 13 | 00:00 | Chuadanga | 105 | 21:00 | Kazla | 95 | 10:00 | Netrakona | 96 | 19:00 | Sirajganj | 88 | 07:00
Aftabnagar | 32 | 13:00 | Coxsbazar | 106 | 19:00 | Keranigonj | 99 | 16:00 | New | 81 | 09:00 | Sonargaon | 80 | 12:00
Agargaon | 85 | 13:00 | Cumilla(N) | 176 | 21:00 | Khagrachori | 32 | 18:30 | Niamatpur | 64 | 06:00 | Sreemongol | 44 | 12:00
Agrabad | 90 | 15:00 | Cumilla(S) | 152 | 00:00 | Khulna | 94 | 19:30 | Noapara | 47 | 01:00 | Srinagar | 46.28 | 21:00
Amnura | 61 | 22:00 | Daudkandi | 150 | 00:00 | Khulshi | 182 | 13:00 | PHP | 11 | 10:00 | Sunamganj | 38 | 22:00
Ashuganj | 69 | 23:00 | Dhaka | 46 | 13:00 | Kishoreganj | 122 | 06:00 | Pabna | 89 | 00:00 | Sylhet | 136 | 00:00
BSRM | 160 | 14:00 | Dhamrai | 112 | 10:00 | Kodda | 293 | 09:00 | Palashbari | 108 | 23:00 | TK | 28.5 | 19:00
Bagerhat | 95 | 21:00 | Dhanmondi | 137 | 13:00 | Kulaura | 52 | 22:00 | Panchagarh | 46 | 08:00 | Tangail | 195 | 22:00
Bakulia | 125 | 19:00 | Dohazari | 88 | 19:00 | Kurigram | 67 | 21:00 | Patuakhali | 133 | 22:00 | Thakurgaon | 66 | 22:00
Banani | 43 | 13:00 | Faridpur | 146 | 20:00 | Kushtia | 138 | 19:30 | Payra | 1.02 | 16:00 | Tongi | 116 | 19:30
Bangabhaban | 20 | 10:00 | Fatullah | 73 | 15:00 | Lalbag | 95 | 13:00 | Purbachal | 20 | 21:00 | Ullon | 40 | 21:00
Barapukuria | 56 | 18:30 | Fenchuganj | 52 | 22:00 | Lalmonirhat | 49 | 03:00 | Purbasadipur | 96 | 05:00 | Uttara | 93 | 21:00
Barguna | 18 | 00:00 | Feni | 114 | 20:00 | Madanganj | 100 | 14:00 | Rahim | 26 | 08:00 | UttaraNew | 18 | 00:00
Barishal | 106 | 18:30 | GPH | 88 | 06:00 | Madaripur | 100 | 22:00 | Rajbari | 60 | 19:30 | Zigatola | 57 | 19:00
Barishal-230 | 60 | 22:00 | Ghorashal | 75 | 21:00 | Madartek | 82 | 23:00 | Rajendrapur | 92 | 05:00
Baroaulia | 58 | 14:00 | Goalpara | 27 | 00:00 | Madunaghat | 61 | 18:30 | Rajshahi | 132 | 22:00
Baroirhat | 55 | 20:00 | Gollamari | 50 | 13:00 | Magura | 64 | 20:00 | Rajshahi-230 | 26 | 02:00
Bashundhara | 181 | 18:30 | Gopalganj | 96.4 | 18:30 | Mahasthangarh | 78 | 03:00 | Ramganj | 88 | 19:00
BashundharaCement | 0 | 00:00 | Gulshan | 124 | 13:00 | Manikganj | 93 | 19:00 | Rampur | 16 | 00:00
Beanibazar | 67 | 22:00 | Halishahar | 91 | 12:00 | Maniknagar | 79 | 13:00 | Rangamati | 14 | 19:00
Benapole | 54 | 20:00 | HaripurSBU | 155 | 19:30 | Matarbari | 43 | 18:30 | Rangpur | 105 | 08:00
Bhaluka | 134 | 15:00 | Hasnabad | 93 | 23:00 | Matuail | 66 | 10:00 | Ruppur | 5 | 09:00
Bhandaria | 50 | 18:30 | Hathazari | 95 | 20:00 | Millgate | 56 | 10:00 | SSM | 3 | 05:00
Bhangura | 35 | 20:00 | Ishurdi | 73 | 20:00 | Mirpur | 131 | 19:30 | Saidpur | 93 | 08:00
Bheramara(GK) | 62 | 20:00 | Jaldhaka | 65 | 21:00 | Mirsorai | N/A | N/A | Satkhira | 95 | 06:00
Bhulta | 265 | 23:00 | Jamalpur | 130 | 04:00 | Mithapukur | 34 | 19:30 | Satmasjid | 101 | 19:00
Bog-Sherpur | 62 | 19:30 | Jashore | 142 | 18:30 | Modern | 0 | 00:00 | Savar | 156 | 09:00
Bogura | 165 | 21:00 | Jhenaidah | 122 | 20:00 | Mogbazar | 139 | 11:00 | Shahjadpur | 85 | 22:00
Borhanuddin | 38 | 23:00 | Joydebpur | 193 | 20:00 | Mongla | 20 | 00:00 | Shahjibazar | 95 | 00:00
Brahmanbaria | 180 | 20:00 | Joypurhat | 60 | 20:00 | Motijheel | 37 | 13:00 | Shahmirpur | 46.5 | 18:30
Cantonment | 140 | 13:00 | Juldah | 27 | 11:00 | Munshiganj | 98 | 22:00 | Shariatpur | 78 | 22:00
Chandpur | 69 | 23:00 | KSRM | 31 | 17:00 | Mymensingh | 238 | 00:00 | Sherpur | 100 | 19:00
Chandraghona | 36 | 18:00 | Kabirpur | 296 | 21:00 | Naogaon | 126 | 20:00 | Shikalbaha | 28 | 19:00
Chapai | 67 | 22:00 | Kachua | 75 | 22:00 | Narail | 45 | 20:00 | Shikalbaha-230 | N/A | N/A
Charsaidpur | 30 | 10:00 | Kallyanpur | 96 | 18:30 | Narinda | 76 | 13:00 | Shitalakhya | 114 | 12:00
Chauddagram | 44 | 22:00 | Kalurghat | 7 | 09:00 | Narshingdi | 190 | 23:00 | Sholosohor | N/A | N/A
Chhatak | 34 | 22:00 | Kamrangirchar | 61 | 13:00 | Natore | 137 | 22:00 | Shyampur | 144 | 01:00
Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
(1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2022-09-19 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Bhulta | 385 | 05:00 | 364 | 12:00 | Kaliakoir | 387 | 05:00 | 367 | 16:00
| Bibiana | 396 | 06:00 | 387 | 16:00 | Payra | 418 | 06:00 | 401 | 21:00
| BIPTC | 400 | 06:00 | 395 | 19:00 | Rahanpur_I | 397 | 18:30 | 378 | 13:00
| Gopalganj_I | 416 | 06:00 | 401 | 21:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 222 | 05:00 | 211 | 12:00 | Hasnabad | 224 | 03:00 | 214 | 15:00
| AKSML | 235 | 06:00 | 219 | 00:00 | Hathazari | 238 | 21:00 | 226 | 01:00
| Aminbazar | 224 | 04:00 | 213 | 15:00 | Ishurdi | 234 | 06:00 | 226 | 21:00
| Ashuganj | 236 | 06:00 | 226 | 12:00 | Jhenaidah | 230 | 06:00 | 221 | 20:00
| Baghabari | 231 | 06:00 | 228 | 11:00 | Kaliakoir | 222 | 04:00 | 212 | 12:00
| Barapukuria | 222 | 09:00 | 211 | 21:00 | Keranigonj | 223 | 05:00 | 212 | 12:00
| Barishal | 246 | 17:00 | 237 | 23:00 | Khulna(S) | 237 | 06:00 | 228 | 21:00
| Bheramara | 231 | 06:00 | 226 | 02:00 | Maniknagar | 224 | 05:00 | 221 | 16:00
| Bhulta | 227 | 04:00 | 214 | 12:00 | Meghnaghat | 229 | 22:00 | 220 | 12:00
| Bibiana | 234 | 05:00 | 229 | 09:00 | Mirsorai | N/A | N/A | N/A | N/A
| BIPTC | 233 | 06:00 | 224 | 21:00 | Rajshahi | 231 | 06:00 | 224 | 01:00
| Bogura | 227 | 06:00 | 217 | 22:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 249 | 08:00 | 242 | 21:00 | Rampura | 224 | 05:00 | 213 | 12:00
| BSRM | 234 | 06:00 | 223 | 12:00 | Shikalbaha | 239 | 18:30 | 224 | 00:00
| Cumilla(N) | 227 | 06:00 | 220 | 15:00 | Shyampur | 224 | 05:00 | 213 | 12:00
| Fenchuganj | 236 | 05:00 | 230 | 12:00 | Siddhirganj | 227 | 05:00 | 215 | 12:00
| Ghorashal | N/A | N/A | N/A | N/A | Sirajgonj | 232 | 06:00 | 223 | 05:00
| GPH | 232 | 06:00 | 220 | 19:00 | Tongi | 224 | 04:00 | 205 | 15:00
| Haripur | 224 | 05:00 | 214 | 10:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 138 | 04:00 | 127 | 12:00 | Lalbag | 138 | 22:00 | 131 | 12:00
| Agargaon | 137 | 01:00 | 130 | 09:00 | Lalmonirhat | 130 | 09:00 | 119 | 22:00
| Agrabad | 137 | 20:00 | 130 | 12:00 | Madanganj | 132 | 18:30 | 125 | 12:00
| AKS | 137 | 05:00 | 129 | 12:00 | Madaripur | 137 | 06:00 | 129 | 21:00
| Aminbazar | 137 | 04:00 | 130 | 11:00 | Madartek | 138 | 05:00 | 127 | 12:00
| Amnura | 134 | 19:00 | 125 | 01:00 | Madunaghat | 138 | 20:00 | 132 | 10:00
| Ashuganj | 136 | 00:00 | 132 | 11:00 | Magura | 136 | 08:00 | 128 | 20:00
| Bagerhat | 135 | 10:00 | 128 | 22:00 | Mahasthangarh | 135 | 06:00 | 124 | 22:00
| Bakulia | 137 | 18:30 | 129 | 00:00 | Manikganj | 135 | 18:30 | 126 | 15:00
| Banani | 134 | 05:00 | 123 | 16:00 | Maniknagar | 134 | 04:00 | 124 | 12:00
| Bangabhaban | 133 | 03:00 | 124 | 12:00 | Matarbari | 129 | 16:00 | 112 | 01:00
| Barapukuria | 136 | 09:00 | 127 | 21:00 | Matuail | 131 | 03:00 | 124 | 12:00
| Barguna | 137 | 17:00 | 128 | 21:00 | Millgate | 134 | 04:00 | 124 | 12:00
| Barishal | 139 | 05:00 | 127 | 22:00 | Mirpur | 136 | 04:00 | 128 | 12:00
| Barishal-230 | 139 | 06:00 | 132 | 21:00 | Mithapukur | 134 | 09:00 | 121 | 22:00
| Baroaulia | 140 | 05:00 | 133 | 10:00 | Modern | 137 | 20:00 | 131 | 10:00
| Baroirhat | 134 | 06:00 | 128 | 13:00 | Mogbazar | 140 | 06:00 | 125 | 18:30
| Bashundhara | 135 | 06:00 | 124 | 12:00 | Mongla | 136 | 18:30 | 129 | 02:00
| BashundharaCement | 132 | 18:30 | 125 | 12:00 | Motijheel | 133 | 03:00 | 124 | 12:00
| Beanibazar | 128 | 06:00 | 124 | 19:30 | Munshiganj | 133 | 18:30 | 125 | 12:00
| Benapole | 136 | 17:00 | 129 | 20:00 | Mymensingh | 130 | 06:00 | 120 | 03:00
| Bhaluka | 130 | 07:00 | 113 | 13:00 | Naogaon | 133 | 06:00 | 121 | 22:00
| Bhandaria | 138 | 06:00 | 129 | 21:00 | Narail | 135 | 06:00 | 126 | 20:00
| Bhangura | 137 | 06:00 | 132 | 21:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bheramara | 136 | 06:00 | 131 | 21:00 | Narshingdi | 128 | 18:00 | 118 | 16:00
| Bheramara(GK) | 136 | 17:00 | 133 | 01:00 | Natore | 134 | 06:00 | 127 | 22:00
| Bhulta | 123 | 18:30 | 117 | 09:00 | Nawabganj | 138 | 03:00 | 130 | 11:00
| Bog-Sherpur | 136 | 06:00 | 128 | 21:00 | Netrakona | 128 | 18:30 | 113 | 21:00
| Bogura | 137 | 06:00 | 128 | 22:00 | New | 134 | 03:00 | 125 | 15:00
| Bogura-230 | 138 | 06:00 | 130 | 21:00 | Niamatpur | 132 | 05:00 | 118 | 22:00
| Brahmanbaria | 131 | 05:00 | 127 | 10:00 | Noapara | 137 | 17:00 | 132 | 19:30
| Cantonment | 137 | 03:00 | 128 | 12:00 | Pabna | 135 | 06:00 | 129 | 21:00
| Chandpur | 139 | 17:00 | 135 | 14:00 | Palashbari | 133 | 09:00 | 119 | 22:00
| Chandraghona | 137 | 07:00 | 133 | 01:00 | Panchagarh | 131 | 00:00 | 118 | 21:00
| Chapai | 133 | 19:00 | 127 | 01:00 | Patuakhali | 136 | 17:00 | 129 | 22:00
| Charsaidpur | 133 | 18:30 | 125 | 12:00 | Payra | 137 | 17:00 | 133 | 22:00
| Chauddagram | 134 | 06:00 | 129 | 15:00 | PHP | 135 | 18:30 | 129 | 15:00
| Chhatak | 129 | 06:00 | 124 | 22:00 | Postogola | 142 | 05:00 | 134 | 12:00
| Chowmuhani | 134 | 08:00 | 127 | 23:00 | Purbachal | 134 | 04:00 | 124 | 12:00
| Chuadanga | 136 | 07:00 | 122 | 21:00 | Purbasadipur | 132 | 10:00 | 118 | 18:00
| Coxsbazar | 126 | 17:00 | 114 | 01:00 | Rahim | 132 | 18:30 | 126 | 10:00
| Cumilla(N) | 135 | 19:00 | 130 | 10:00 | Rajbari | 132 | 06:00 | 124 | 21:00
| Cumilla(S) | 135 | 04:00 | 128 | 18:00 | Rajendrapur | 137 | 06:00 | 128 | 17:00
| Daudkandi | 135 | 20:00 | 127 | 10:00 | Rajshahi | 133 | 17:00 | 126 | 23:00
| Dhaka | 138 | 03:00 | 127 | 12:00 | Rajshahi-230 | 131 | 06:00 | 127 | 01:00
| Dhamrai | 136 | 05:00 | 130 | 09:00 | Ramganj | 135 | 07:00 | 130 | 23:00
| Dhanmondi | 132 | 05:00 | 124.4 | 12:00 | Rampur | 137 | 21:00 | 130 | 01:00
| Dohazari | 135 | 18:30 | 125 | 01:00 | Rampura | 137 | 04:00 | 127 | 12:00
| Faridpur | 132 | 06:00 | 126 | 21:00 | Rangamati | 137 | 21:00 | 132 | 01:00
| Fatullah | 135 | 05:00 | 129 | 12:00 | Rangpur | 131 | 10:00 | 117 | 21:00
| Fenchuganj | 133 | 00:00 | 130 | 16:00 | Ruppur | 135 | 09:00 | 131 | 20:00
| Feni | 135 | 06:00 | 130 | 01:00 | Saidpur | 133 | 00:00 | 119 | 22:00
| Ghorashal | 136 | 19:30 | 130 | 15:00 | Satkhira | 135 | 17:00 | 127 | 20:00
| Goalpara | 138 | 17:00 | 132 | 04:00 | Satmasjid | 138 | 05:00 | 129 | 09:00
| Gollamari | 136 | 17:00 | 132 | 01:00 | Savar | 138 | 18:30 | 128 | 08:00
| Gopalganj | 137 | 18:00 | 130 | 02:00 | Shahjadpur | 139 | 10:00 | 135 | 21:00
| Gopalganj_I | 136 | 06:00 | 131 | 01:00 | Shahjibazar | 133 | 18:30 | 130 | 01:00
| Gulshan | 138 | 06:00 | 126 | 12:00 | Shahmirpur | 138 | 20:00 | 131 | 10:00
| Halishahar | 138 | 20:00 | 131 | 10:00 | Shariatpur | 136 | 07:00 | 126 | 21:00
| Haripur | 132 | 18:30 | 126 | 10:00 | Sherpur | 134 | 06:00 | 121 | 21:00
| HaripurSBU | 132 | 06:00 | 126 | 13:00 | Shikalbaha | 139 | 18:30 | 130 | 00:00
| Hasnabad | 141 | 05:00 | 134 | 12:00 | Shikalbaha-230 | 138 | 19:30 | 131 | 01:00
| Hathazari | 140 | 16:00 | 132 | 01:00 | Shitalakhya | 141 | 05:00 | 132 | 12:00
| Ishurdi | 136 | 06:00 | 131 | 21:00 | Sholosohor | N/A | N/A | N/A | N/A
| Jaldhaka | 132 | 06:00 | 118 | 22:00 | Shyampur | 133 | 01:00 | 127 | 12:00
| Jamalpur | 136 | 06:00 | 124 | 21:00 | Shyampur-230 | 135 | 03:00 | 129 | 12:00
| Jashore | 136 | 17:00 | 129 | 21:00 | Siddhirganj | 132 | 06:00 | 125 | 10:00
| Jhenaidah | 138 | 17:00 | 130 | 21:00 | Sirajganj | 135 | 04:00 | 128 | 22:00
| Jhenaidah-230 | 138 | 06:00 | 131 | 20:00 | Sonargaon | 133 | 20:00 | 125 | 10:00
| Joydebpur | 136 | 01:00 | 125 | 15:00 | Sreemongol | 133 | 07:00 | 130 | 10:00
| Joypurhat | 133 | 06:00 | 121 | 22:00 | Srinagar | 138 | 03:00 | 131 | 12:00
| Juldah | 139 | 19:00 | 131 | 10:00 | SSM | 141 | 05:00 | 135 | 11:00
| Kabirpur | 137 | 18:30 | 121 | 10:00 | Sunamganj | 128 | 06:00 | 119 | 22:00
| Kachua | 136 | 00:00 | 133 | 13:00 | Sylhet | 131 | 05:00 | 128 | 19:30
| Kaliakoir | 138 | 05:00 | 130 | 15:00 | Tangail | 136 | 06:00 | 123 | 13:00
| Kallyanpur | 136 | 21:00 | 120 | 12:00 | Thakurgaon | 132 | 06:00 | 118 | 22:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2022-09-19
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 1555 | 7456 | 4782 | 12238 |  |  |  | QF-LDC-11
0:30 | 1535 | 7482.5 | 4749.5 | 12232 | Date: | 2022-09-19
1:00 | 1515 | 7509 | 4717 | 12226
1:30 | 1512.5 | 7544.5 | 4697.5 | 12242
2:00 | 1510 | 7580 | 4678 | 12258
2:30 | 1507.5 | 7412.5 | 4671 | 12083.5 | [5 empty] | Gen. at Eve. Peak | 13543 | 13543 MW (21:00 )
3:00 | 1505 | 7245 | 4664 | 11909 | [6 empty] | 21:00
3:30 | 1462.5 | 7282 | 4571.5 | 11853.5 | [5 empty] | Gen. at Day Peak | 11712 | 11712 MW (12:00 )
4:00 | 1420 | 7319 | 4479 | 11798 | [6 empty] | 12:00
4:30 | 1317.5 | 7219 | 4421.5 | 11640.5 | [5 empty] | Highest Generation | 13543
5:00 | 1215 | 7119 | 4364 | 11483 | [6 empty] | 21:00
5:30 | 1147.5 | 6986 | 4263.5 | 11249.5
6:00 | 1080 | 6853 | 4163 | 11016
6:30 | 1190 | 6678.5 | 4053 | 10731.5
7:00 | 1300 | 6504 | 3943 | 10447
7:30 | 1340 | 6484.5 | 3972 | 10456.5
8:00 | 1380 | 6465 | 4001 | 10466
8:30 | 1455 | 6718 | 4016 | 10734
9:00 | 1530 | 6971 | 4031 | 11002
9:30 | 1527.5 | 7149 | 4032 | 11181
10:00 | 1525 | 7327 | 4033 | 11360
10:30 | 1530 | 7364.5 | 4049.5 | 11414
11:00 | 1535 | 7402 | 4066 | 11468
11:30 | 1532.5 | 7427.5 | 4162.5 | 11590
12:00 | 1530 | 7453 | 4259 | 11712
12:30 | 1530 | 7464 | 4291 | 11755
13:00 | 1530 | 7475 | 4323 | 11798
13:30 | 1530 | 7463 | 4317.5 | 11780.5
14:00 | 1530 | 7451 | 4312 | 11763
14:30 | 1530 | 7448 | 4343 | 11791
15:00 | 1530 | 7445 | 4374 | 11819
15:30 | 1530 | 7433 | 4338 | 11771
16:00 | 1530 | 7421 | 4302 | 11723
16:30 | 1530 | 7379 | 4148.5 | 11527.5
17:00 | 1530 | 7337 | 3995 | 11332
17:30 | 1472.5 | 7434.5 | 4063 | 11497.5
18:00 | 1415 | 7532 | 4131 | 11663
18:30 | 1392.5 | 7876.5 | 4411 | 12287.5
19:00 | 1370 | 8221 | 4691 | 12912
19:30 | 1290 | 8364 | 4844 | 13208
20:00 | 1245 | 8516 | 4964 | 13480 |  |  |  | Executive Engineer
20:30 | 1230 | 8515 | 4996.5 | 13511.5 |  |  |  | Network Operation Division
21:00 | 1215 | 8514 | 5029 | 13543
21:30 | 1182.5 | 8504 | 5000 | 13504
22:00 | 1150 | 8494 | 4971 | 13465 |  |  |  |  | Page 6 of 7
22:30 | 1170 | 8483.5 | 4951.5 | 13435
23:00 | 1190 | 8473 | 4932 | 13405
23:30 | 1372.5 | 7964.5 | 4857 | 12821.5
24:00 | 1555 | 7456 | 4782 | 12238
13543 MW (21:00 )
11712 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2022-09-19 |  | Energy |  | 290338291
[13 empty] | 2022-09-19 |  |  |  |  | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 3799 | 900 | 1775 | 394 | 3015 | 1336 | 152 | 443 | 513 | 126 | 0 | 978.7127
0:30 | 3876.5 | 896.5 | 1639 | 610 | 2889 | 1354.5 | 151 | 444 | 453.5 | 135 | 0 | 907.8563 | Date: | 2022-09-19
1:00 | 3954 | 893 | 1503 | 826 | 2763 | 1373 | 150 | 445 | 394 | 144 | 0 | 837
1:30 | 3955 | 893.5 | 1503.5 | 825.5 | 2810 | 1355.5 | 150 | 444.5 | 383.5 | 140 | 0 | 644.5 | [7 empty] | Total Energy | 290.3383 | Total Energy Gen 180.187 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 180.187 MKWHr
2:00 | 3956 | 894 | 1504 | 825 | 2857 | 1338 | 150 | 444 | 373 | 136 | 0 | 452 | [7 empty] | Energy not Served | 7.5866
2:30 | 3815.5 | 894 | 1522.5 | 774.5 | 2867.5 | 1327.5 | 150 | 444 | 373 | 134 | 0 | 313.5 | [7 empty] | Energy Requirement | 297.9249
3:00 | 3675 | 894 | 1541 | 724 | 2878 | 1317 | 150 | 444 | 373 | 132 | 0 | 175
3:30 | 3699.5 | 889.5 | 1561.5 | 651.5 | 2876.5 | 1296.5 | 150.5 | 444 | 372.5 | 130 | 0 | 87.5 | [5 empty] | Shortage
4:00 | 3724 | 885 | 1582 | 579 | 2875 | 1276 | 151 | 444 | 372 | 128 | 0 | 0
4:30 | 3727 | 885 | 1595 | 470.5 | 2860 | 1261 | 151 | 442.5 | 336 | 129 | 0 | 0
5:00 | 3730 | 885 | 1608 | 362 | 2845 | 1246 | 151 | 441 | 300 | 130 | 0 | 0
5:30 | 3730 | 885 | 1626 | 199 | 2836 | 1221 | 151 | 389.5 | 256.5 | 127 | 1 | 0
6:00 | 3730 | 885 | 1644 | 36 | 2827 | 1196 | 151 | 338 | 213 | 124 | 2 | 0
6:30 | 3708 | 885 | 1628 | 18 | 2640 | 1195.5 | 151 | 299 | 199 | 121 | 17 | 0 |  |  |  | Coal
7:00 | 3686 | 885 | 1612 | 0 | 2453 | 1195 | 151 | 260 | 185 | 118 | 32 | 0
7:30 | 3672 | 885 | 1608.5 | 0 | 2448 | 1195 | 151 | 280 | 185 | 111 | 51 | 0 |  |  | Oil |  |  |  | ,
8:00 | 3658 | 885 | 1605 | 0 | 2443 | 1195 | 151 | 300 | 185 | 104 | 70 | 0
8:30 | 3643 | 885 | 1583.5 | 179 | 2558.5 | 1195.5 | 151 | 300 | 185 | 106 | 77.5 | 17.5
9:00 | 3628 | 885 | 1562 | 358 | 2674 | 1196 | 151 | 300 | 185 | 108 | 85 | 35
9:30 | 3665 | 885 | 1617.5 | 404 | 2688 | 1195.5 | 151 | 290 | 185 | 89 | 141 | 44
10:00 | 3702 | 885 | 1673 | 450 | 2702 | 1195 | 151 | 280 | 185 | 70 | 197 | 53
10:30 | 3699.5 | 885.5 | 1691.5 | 506 | 2681 | 1205 | 148.5 | 286.5 | 186.5 | 72 | 183.5 | 149.5
11:00 | 3697 | 886 | 1710 | 562 | 2660 | 1215 | 146 | 293 | 188 | 74 | 170 | 246
11:30 | 3679.5 | 885.5 | 1712.5 | 576.5 | 2723 | 1215.5 | 148.5 | 319 | 204 | 73 | 202 | 296.5
12:00 | 3662 | 885 | 1715 | 591 | 2786 | 1216 | 151 | 345 | 220 | 72 | 234 | 347
12:30 | 3645 | 884.5 | 1725 | 587 | 2804.5 | 1231 | 151 | 371 | 237 | 77 | 214.5 | 336.5
13:00 | 3628 | 884 | 1735 | 583 | 2823 | 1246 | 151 | 397 | 254 | 82 | 195 | 326
13:30 | 3628 | 884 | 1735 | 583 | 2823 | 1246 | 151 | 397 | 254 | 82 | 195 | 330
14:00 | 3628 | 884 | 1735 | 583 | 2823 | 1246 | 151 | 397 | 254 | 82 | 195 | 334
14:30 | 3620.5 | 887.5 | 1712 | 622.5 | 2842.5 | 1251 | 151.5 | 402.5 | 263.5 | 86 | 154.5 | 383.5
15:00 | 3613 | 891 | 1689 | 662 | 2862 | 1256 | 152 | 408 | 273 | 90 | 114 | 433
15:30 | 3610 | 891 | 1680.5 | 612 | 2900 | 1246 | 151.5 | 417 | 284 | 85 | 95.5 | 405
16:00 | 3607 | 891 | 1672 | 562 | 2938 | 1236 | 151 | 426 | 295 | 80 | 77 | 377
16:30 | 3644 | 891 | 1656.5 | 448 | 2914.5 | 1225 | 151 | 393 | 286.5 | 77 | 55.5 | 310.5
17:00 | 3644 | 891 | 1641 | 334 | 2891 | 1214 | 151 | 360 | 278 | 74 | 34 | 244
17:30 | 3639 | 891.5 | 1662.5 | 203.5 | 3096.5 | 1196 | 151.5 | 360 | 362 | 98 | 17 | 240
18:00 | 3634 | 892 | 1684 | 73 | 3302 | 1178 | 152 | 360 | 446 | 122 | 0 | 236
18:30 | 3684.5 | 891.5 | 1704.5 | 240.5 | 3485.5 | 1238.5 | 152 | 397 | 560.5 | 127 | 0 | 603
19:00 | 3735 | 891 | 1725 | 408 | 3669 | 1299 | 152 | 434 | 675 | 132 | 0 | 970
19:30 | 3753 | 891 | 1804 | 419 | 3812 | 1348 | 151 | 440 | 679 | 126 | 0 | 959
20:00 | 3732 | 891 | 1785 | 703 | 3814 | 1368 | 151 | 441 | 683 | 126 | 0 | 505
20:30 | 3746.5 | 891 | 1790.5 | 720 | 3811.5 | 1388 | 151 | 442 | 660 | 126 | 0 | 446.5
21:00 | 3761 | 891 | 1796 | 737 | 3809 | 1408 | 151 | 443 | 637 | 126 | 0 | 388
21:30 | 3776.5 | 891.5 | 1806 | 692 | 3801.5 | 1393 | 151 | 441.5 | 635.5 | 131 | 0 | 194
22:00 | 3792 | 892 | 1816 | 647 | 3794 | 1378 | 151 | 440 | 634 | 136 | 0 | 0
22:30 | 3791 | 896 | 1825 | 670 | 3758 | 1372.5 | 151 | 440.5 | 607.5 | 139 | 0 | 182.9326
23:00 | 3790 | 900 | 1834 | 693 | 3722 | 1367 | 151 | 441 | 581 | 142 | 0 | 365.8653
23:30 | 3794.5 | 900 | 1804.5 | 543.5 | 3368.5 | 1351.5 | 151.5 | 442 | 547 | 134 | 0 | 672.289 | Max Temp. in Dhaka |  | 34.3° C
24:00 | 3799 | 900 | 1775 | 394 | 3015 | 1336 | 152 | 443 | 513 | 126 | 0 | 978.7127
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 180.187 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 180.187 MKWHr
Shortage
Note on W13: Author:

## Generation
g | 2022-09-19
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 80 | 80 | 80 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 76 | 81 | 81 | 81 | 82 | 81 | 81 | 82 |  | 82 | 81 | 81 | 81 | 81 | 81 | 82 | 1965376
2 | Karnaphuli Hydro PP Unit-4 & 5 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1692000
3 | Chattogram TPP-1 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2600000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 18 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 16 | 16 | 16 | 17 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 505755
| Teknaf 20MW PP (Solartech) | [5 empty] | 1 | 2 | 5 | 5 | 20 | 13 | 14 |  | 0 | 5 | 0 | 2 | 0 | [8 empty] | 75060
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 16 | 15 | 16 | 17 | 17 | 39 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 618026
12 | Hathazari 100 MW peaking PP | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 23 | 23 | 23 | 23 |  | 23 | 26 | 31 | 31 | 31 | 31 | 31 | 569280
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 23 | 70 | 87 | 87 | 105 | 105 | 98 | 87 | 102 | 98 | 87 | 102 | 105 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2335127
| Daudkandi 200 MW PP (B.Trac) | 190 | 189 | 189 | 189 | 80 |  |  |  | 50 | 100 | 185 | 188 | 187 | 189 | 188 | 187 | 100 | 10 |  | 50 | 60 | 189 | 190 | 170 | 140 | 30 | 3176448
14 | Titas 50 MW Peaking PP | 29 | 28 | 28 | 28 | 28 | 28 | [6 empty] | 20 | 30 | 27 | 27 | 27 | 27 |  | 29 | 28 | 28 | 27 | 27 | 27 | 29 | 497512
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 273 | 273 | 273 | 273 | 273 | 258 | 266 | 275 | 275 | 274 | 273 | 273 | 274 | 273 | 275 | 275 | 273 | 273 |  | 273 | 273 | 273 | 273 | 273 | 273 | 273 | 6561273
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 217454
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4 | 220 | 220 | 220 | 220 | 218 | 220 | 220 | 220 | 200 | 200 | 200 | 200 | 200 | 220 | 200 | 200 | 193 | 200 |  | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 5193000
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 280 | 280
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 40 | 40 | 40 | 36 | 42 | 38 | 41 | 40 | 37 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 988560
33 | Ashuganj 225 MW CCPP | 181 | 183 | 190 | 196 | 188 | 187 | 188 | 182 | 183 | 199 | 200 | 200 | 187 | 189 | 186 | 186 | 196 | 199 |  | 198 | 199 | 194 | 191 | 196 | 187 | 187 | 4609000
34 | Ashuganj 450 MW CCPP(South) | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 |  | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 6087000
| Ashuganj 450 MW CCPP(North) | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 280 | 280 | 280 |  | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 7431200
Ashuganj 420 MW CCPP(East)
35 | Ashuganj 55 MW PP (Precision) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 20 | 20 | 20 | 25 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 30 | 30 | 40 | 40 | 672960
36 | Chandpur 150 MW CCPP | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 82 | 82 | 82 | 83 | 82 | 84 |  | 82 | 83 | 82 | 83 | 83 | 82 | 83 | 1987010
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 314 | 314 | 314 | 333 | 352 | 356 | 345 | 332 | 321 | 394 | 404 | 406 | 400 | 408 | 406 | 407 | 408 | 409 |  | 405 | 409 | 407 | 407 | 408 | 408 | 407 | 9189380
40 | Meghnaghat 450 MW CCPP(MPL) | 175 | 175 | 180 | 180 | 185 | 190 | 190 | 190 | 190 | 210 | 225 | 225 | 225 | 210 | 210 | 210 | 210 | 210 |  | 210 | 210 | 210 | 210 | 210 | 210 | 225 | 4608000
41 | Haripur 360MW CCPP(HPL) | 130 | 133 | 131 | 140 | 151 | 160 | 150 | 140 | 151 | 267 | 273 | 273 | 273 | 263 | 253 | 253 | 253 | 254 |  | 251 | 251 | 251 | 252 | 252 | 252 | 257 | 5116000
42 | RPCL 210MW CCPP | 143 | 140 | 132 | 135 | 138 | 123 | 96 | 71 | 71 | 67 | 66 | 65 | 41 | 41 | 39 | 35 | 60 | 47 |  | 82 | 98 | 99 | 99 | 128 | 133 | 134 | 2061120
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 0 | 7 | 25 | 18 | 56 | 40 | 46 | 43 | 32 | 41 | 25 | 8 | 0 | [8 empty] | 342440
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 42 | 42 | 43 | 42 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1021000
45 | Fenchugonj CCPP Phase-2 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 |  | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 957552
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 58 | 58 | 57 | 57 | 58 | 62 | 62 | 64 | 57 | 57 | 57 | 55 | 57 | 56 | 51 | 52 | 58 | 61 |  | 63 | 59 | 61 | 63 | 60 | 60 | 62 | 1407072
48 | Shahjibazar 86MW PP (Shahjibazar) | 20 | 20 | 20 | 10 | 10 | 10 | 10 | 10 | 10 | [8 empty] | 78 |  | 78 | 78 | 78 | 78 | 78 | 78 | 10 | 712320
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 213 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 |  | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 5258110
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 423000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 8 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 234000
54 | Hobiganj 11MW PP Cofidence-E | [26 empty] | 0
55 | Fenchugonj 51 MW PP (Barakatullah) | [26 empty] | 0
56 | Shahjahanulla 25 MW PP | 8 | 8 | 8 | 8 |  | 5 | 8 | 8 | 8 | [8 empty] | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 120072
57 | Bibiana-II 341 MW CCPP (Summit) | 300 | 290 | 290 | 290 | 280 | 290 | 280 | 300 | 320 | 300 | 315 | 300 | 320 | 300 | 310 | 300 | 290 | 260 |  | 280 | 315 | 280 | 280 | 290 | 295 | 290 | 7236500
| Bibiyana South 400 MW | 400 | 400 | 400 | 400 | 400 | 400 | 397 | 400 | 396 | 400 | 400 | 384 | 384 | 381 | 382 | 385 | 390 | 360 |  | 400 | 390 | 400 | 400 | 400 | 400 | 400 | 9222000
58 | Nababganj 55 MW PP (Southern power ) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  |  |  | 12 | 17 | 17 | 17 | 17 |  | 17 | 35 | 35 | 55 | 55 | 55 | 55 | 718347
59 | Tangail Palli Power Gen 22 MW | 12 | 12 | 12 | 12 | 12 | 8 | 6 | 6 | 6 | 7 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 269280
60 | Barabkunda 22 MW PP (Regent) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 12 | 15 | 15 | 15 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 349728
61 | Narshingdi 22 MW PP (Doreen) | 19 |  |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 404712
62 | Tangail 22 MW PP (Doreen) | 13 | 13 | 13 | 13 | 13 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 11 | 14 | 14 |  | 14 | 14 | 13 | 13 | 13 | 13 | 13 | 296496
63 | Impoprt (Tripura) | 144 | 136 | 132 | 128 | 130 | 124 | 118 | 104 | 108 | 70 | 74 | 72 | 82 | 82 | 90 | 80 | 74 | 122 |  | 132 | 126 | 126 | 126 | 136 | 142 | 126 | 2646720
64 | Malancha, Ctg. EPZ (United) | 35 | 35 | 35 | 35 | 35 | 35 | 33 | 12 | 7 | 9 | 5 | 10 | 13 | 10 | 7 | 6 | 13 | 8 |  | 18 | 25 | 30 | 28 | 31 | 32 | 32 | 507360
65 | Feni 22MW PP (Doreen) | 19 | 19 | 19 | 19 | 16 | 16 |  | 16 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 417780
66 | Feni 11 MW PP (Doreen) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 8 | 10 | 10 | 10 | 10 | 10 | 7 |  | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 211500
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 17 | 16 | 16 | 16 | 14 | 14 | 14 | 17 | 22 | 27 | 25 |  | 31 | 32 | 32 | 32 | 32 | 32 | 33 | 627900
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 18 | 21 | 21 | 21 | 21 | 21 | 21 | 497300
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 21 | 21 | 21 | 23 | 26 | 26 | 25 | 25 | 25 | 23 | 22 | 21 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 21 | 506880
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 794880
72 | Rupganj 33 MW PP(Summit) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 24 | 24 | 15 | 15 | 15 | 15 | 15 | 15 | 14 | 14 | 14 |  | 14 | 14 | 14 | 14 | 14 | 14 | 16 | 388500
73 | Ghorashal 108MW PP (Regent) | 11 | 11 | 43 | 67 | 82 | 92 | 87 | 91 | 91 | 91 | 99 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1940363
| Feni Lanka Power | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 34 | 34 |  | 34 | 34 | 34 | 34 | 34 | 34 | 17 | 532380
| Chowmuhani 113 MW | 102 | 101 | 101 | 100 | 99 | 97 | 98 | 98 | 98 | 98 | 94 | 98 | 95 | 96 | 95 | 101 | 112 | 113 |  | 114 | 115 | 115 | 115 | 115 | 115 | 64 | 2446080
| Manikgonj 162MW PP(MPGL) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 23 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 76 | 141 |  | 144 | 144 | 144 | 144 | 144 | 144 | 17 | 1654560
77 | Siddhirganj 100 PP(Dutch Bangla) | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 50 | 77 |  | 88 | 88 | 88 | 88 | 88 | 89 | 59 | 1378560
78 | Gazipur 52 MW PP | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 41 | 41 | 41 | 41 | 41 | 40 | 40 | 48 | 48 |  | 48 | 48 | 48 | 48 | 48 | 48 | 41 | 1109760
79 | Kodda 150MW PP | 82 | 82 | 82 | 82 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 64 |  | 115 | 115 | 115 | 78 | 78 | 48 | 48 | 1007520
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 15 | 43 | 43 | 43 | 36 | 8 | 8 | 317626
| Gazipur 100 MW PP | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 90 | 90 | 105 | 105 | 90 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2329200
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 2 | 3 | 4 | 2 | 3 | 5 | 2 | 2 | 0 | 1 | 0 | [8 empty] | 26281
| Jodiac Power | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 22 | 17 | 21 | 27 | 24 | 22 | 17 | 36 | 36 | 36 |  | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 803925
| Karnaphuli Power Ltd. | 55 | 102 | 105 | 105 | 100 | 97 | 94 | 88 | 88 | 72 | 69 | 84 | 91 | 94 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2324244
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP ( Summit) | 122 | 128 | 125 | 133 | 132 | 132 | 132 | 138 | 125 | 138 | 132 | 130 | 135 | 135 | 145 | 145 | 145 | 145 |  | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 3295942
87 | Meghnaghat 100 MW(IEL) | 42 | 41 | 41 | 41 | 42 | 42 | 41 | 42 | 41 | 40 | 43 | 41 | 41 | 42 | 42 | 41 | 38 | 47 |  | 79 | 83 | 83 | 80 | 83 | 79 | 47 | 1206720
| Meghnaghat 104 MW PP (OPCL) | 54 | 54 | 54 | 54 | 54 | 54 | 32 | 17 | 17 | 30 | 44 | 55 | 55 | 55 | 50 | 50 | 55 | 69 |  | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 1421760
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 67 |  | 78 | 78 | 78 | 78 | 78 | 78 | 33 | 1029720
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1196574
94 | Gagnagar 102 MW PP (Digital Power) | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 92 | 92 | 92 | 92 | 92 | 92 | 40 | 1201968
95 | Patenga 50MW PP (Baraka) | 38 | 39 | 39 | 39 | 39 | 39 | 6 | 6 | 31 | 38 | 38 | 38 | 32 | 33 | 33 | 34 | 37 | 39 |  | 39 | 39 | 40 | 39 | 40 | 40 | 40 | 854400
96 | Chattogram 108 MW PP (ECPV) | [20 empty] | 0 | [5 empty] | 0
97 | katpotti 52 MW
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 55 | 55 | 55 | 55 | 55 | 55 | 45 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 45 | 50 | 1314099
100 | Manikganj 55 MW PP (Northern) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 55 | 55 | 35 | 35 | 35 | 35 | 895320
101 | Kushiara 163 MW CCPP (KP)
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 1 | 0 | [9 empty] | 8900
103 | Kamalaghat 54 MW PP(Banco Energy) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 17 | 653760
104 | Keranigonj 300 MW PP (APR) | 221 | 221 | 120 | 120 | 82 | 11 |  |  | 158 | 200 | 223 | 223 | 226 | 226 | 226 | 225 | 84 | 13 |  | 108 | 111 | 177 | 183 | 143 | 219 | 20 | 3664768
105 | Bramhangoan 100 MW PP (Aggreko) | 75 | 75 | 75 | 75 | 75 | 25 |  |  | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 25 |  | 90 | 90 | 90 | 90 | 90 | 90 | 75 | 1651875
106 | Mymensingh 200 MW PP (United) | 153 | 153 | 153 | 153 | 142 | 142 | 144 | 144 | 132 | 125 | 123 | 141 | 139 | 140 | 139 | 139 | 141 | 150 |  | 152 | 152 | 151 | 151 | 150 | 151 | 152 | 3420000
112 | Aurahati 100MW PP (Aggreko) | 75 | 75 | 75 | 75 | 75 |  |  |  | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 25 |  | 90 | 88 | 90 | 90 | 90 | 90 | 75 | 1611679
114 | Kodda 149 MW PP Unit-1 (Summit) | 149 | 149 | 149 | 149 | 135 | 134 | 79 | 72 | 123 | 133 | 133 | 133 | 133 | 133 | 134 | 134 | 147 | 149 |  | 149 | 149 | 149 | 149 | 149 | 149 | 135 | 3293424
115 | Juldah 100 MW PP Unit-3 (Acorn) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 33 | 1090560
116 | Chandpur 200MW (Desh energy) | 200 | 200 | 200 | 200 | 200 | 200 | 100 | 108 | 187 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4590720
117 | Ashuganj 150MW PP (Midland) | 143 | 142 | 143 | 140 | 138 | 138 | 137 | 138 | 135 | 135 | 132 | 132 | 133 | 132 | 133 | 132 | 130 | 132 |  | 140 | 143 | 140 | 140 | 140 | 140 | 138 | 3295272
118 | Bibiyana-III 400 MW CCPP | 401 | 402 | 401 | 401 | 401 | 400 | 402 | 402 | 402 | 405 | 405 | 405 | 397 | 405 | 395 | 404 | 404 | 403 |  | 403 | 404 | 378 | 402 | 402 | 404 | 402 | 9611000
| Jamalpur 115 MW PP (United) | 95 | 96 | 96 | 97 | 97 | 97 | 97 | 97 | 96 | 96 | 87 | 87 | 86 | 86 | 84 | 83 | 94 | 94 |  | 96 | 96 | 96 | 96 | 96 | 95 | 95 | 2212800
| Anwara 300 MW PP (United) | 240 | 249 | 249 | 249 | 249 | 249 | 249 | 231 | 248 | 248 | 248 | 248 | 248 | 249 | 249 | 249 | 249 | 255 |  | 274 | 270 | 275 | 275 | 264 | 249 | 250 | 5986691
| Juldah unit-2 (Acorn) | 49 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 |  | 78 | 90 | 90 | 90 | 90 | 90 | 52 | 1183680
| Anlima Energy Ltd. | 86 | 90 | 90 | 90 | 90 | 97 | 105 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 |  | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 2481491
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 443880
| Spectra Solar Plant Ltd. | [5 empty] | 0 | 7 | 17 | 13 | 17 | 35 | 34 | 35 | 11 | 26 | 16 | 6 | 0 | [8 empty] | 222042
| Chandpur 115(Doreen) | 35 | 35 | 35 | 35 | 35 | 35 | 34 | 35 | 35 | 35 | 34 | 34 | 34 | 35 | 35 | 35 | 72 | 109 |  | 115 | 115 | 115 | 115 | 115 | 115 | 55 | 1379520
| Kanchan Purbachal Power Generation Ltd. | [16 empty] | 27 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 0 | 370440
Mirsharai 150 MW (Oil)
Mirsharai 150 MW (Gas)
120 | Eastern Zone Total | 7509 | 7580 | 7245 | 7319 | 7119 | 6853 | 6504 | 6465 | 6971 | 7327 | 7402 | 7453 | 7475 | 7451 | 7445 | 7421 | 7337 | 7532 |  | 8221 | 8364 | 8516 | 8514 | 8494 | 8473 | 7456 | 180387494
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 16 | 16 | 16 | 16 | 16 | 16 | 21 | 16 | 27 |  | 32 | 32 | 32 | 32 | 32 | 16 | 16 | 421440
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 5 | 5 | 5 | 5 | 2 | [12 empty] | 33 |  | 44 | 37 | 37 | 32 | 32 | 16 | 10 | 204480
| Khulna 225 MW CCPP | 226 | 225 | 225 | 226 | 226 | 208 | 130 | 170 | 170 | 150 | 160 | 180 | 217 | 217 | 217 | 214 | 180 | 180 |  | 226 | 225 | 227 | 227 | 225 | 225 | 228 | 4970880
129 | Rupsha 105 MW PP (Orion rupsha) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 20 | 35 | 35 | 35 |  | 55 | 56 | 56 | 55 | 55 | 55 | 17 | 690720
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 1 | 12 | 14 | 35 | 85 | 54 | 97 | 79 | 43 | 21 | 27 | 15 | 0 | [8 empty] | 527760
131 | Rampal 1320 MW (BIFPCL)
132 | United Payra Power Ltd. | [26 empty] | 0
133 | Bhola Nutan Biddut BD LTD (GAS) | 224 | 224 | 224 | 224 | 225 | 225 | 225 | 224 | 182 | 183 | 216 | 214 | 216 | 217 | 220 | 216 | 185 | 183 |  | 183 | 220 | 224 | 224 | 224 | 224 | 224 | 5196955
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 32 | 32 | 32 | 32 | 16 | 16 | [5 empty] | 16 | 16 | 16 | 32 | 32 | 32 | 32 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 550752
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 86 | 86 | 86 | 86 | 86 | 82 | 84 | 85 | 85 | 85 | 83 | 83 | 81 | 82 | 84 | 84 | 72 | 87 |  | 85 | 85 | 86 | 86 | 85 | 85 | 85 | 2040653
140 | Bhola 33 MW PP (Venture) | 29 | 27 | 26 | 25 | 24 | 19 | 18 | 16 | 17 | 18 | 18 | 19 | 19 | 22 | 20 | 19 | 17 | 18 |  | 26 | 25 | 27 | 28 | 29 | 28 | 22 | 532354
141 | Noapara 100 MW PP (Bangla Trac) | 95 | 95 | 95 | 20 | 20 | [5 empty] | 4 | 10 | 10 | 10 | 60 |  |  |  |  | 20 | 20 | 94 | 94 | 94 | 94 | 94 | 985920
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP | 20 | [15 empty] | 15 | 40 |  | 50 | 45 | 45 | 40 | 38 | 38 | 25 | 289024
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | [7 empty] | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 67 |  | 67 | 67 | 67 | 67 | 67 | 67 | 15 | 605088
146 | Bheramara HVDC | 893 | 894 | 894 | 885 | 885 | 885 | 885 | 885 | 885 | 885 | 886 | 885 | 884 | 889 | 891 | 891 | 891 | 892 |  | 891 | 891 | 891 | 891 | 892 | 900 | 900 | 21509090
147 | Bheramara 410 MW CCPP | 225 | 230 | 230 | 230 | 230 | 235 | 240 | 240 | 235 | 225 | 215 | 215 | 220 | 220 | 215 | 215 | 220 | 215 |  | 215 | 220 | 220 | 225 | 225 | 225 | 230 | 5534784
148 | Payra 1320 MW | 1045 | 1010 | 990 | 950 | 920 | 870 | 870 | 870 | 870 | 870 | 890 | 890 | 920 | 920 | 930 | 910 | 890 | 850 |  | 970 | 1020 | 1040 | 1080 | 1050 | 1040 | 1010 | 24683600
149
150 | Barapukuria TPP Unit-1 | 78 | 77 | 77 | 76 | 76 | 76 | 75 | 75 | 75 | 75 | 75 | 76 | 76 | 76 | 76 | 76 | 75 | 78 |  | 79 | 78 | 78 | 78 | 78 | 77 | 76 | 1826618
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 250 | 251 | 250 | 250 | 250 | 250 | 250 | 250 | 251 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 249 | 250 |  | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 6068200
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [17 empty] | 16 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 135296
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 1 | 2 | 1 | 3 | 3 | 4 | 4 | 1 | 0 | 0 | [9 empty] | 25500
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 184 | 184 | 185 | 185 | 185 | 184 | 184 | 186 | 186 | 188 | 188 | 187 | 187 | 187 | 183 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 181 | 180 | 4633391
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
| Sirajgonj 225 MW CCPP Unit-2 (Oil) | 219 | 219 | 219 | 218 | 215 | 130 | 130 | 130 | 130 | 130 | 133 | 165 | 180 | 180 | 191 | 212 | 180 | 180 |  | 208 | 215 | 214 | 216 | 215 | 216 | 215 | 4678182
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 158 | 159 | 160 | 160 | 161 | 162 | 163 | 163 | 160 | 159 | 157 | 158 | 156 | 155 | 155 | 154 | 154 | 154 |  | 154 | 154 | 154 | 154 | 154 | 154 | 154 | 4023518
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 340 | 344 | 350 | 361 | 367 | 374 | 370 | 367 | 352 | 350 | 330 | 340 | 323 | 330 | 318 | 317 | 322 | 321 |  | 327 | 328 | 333 | 334 | 340 | 343 | 343 | 8211418
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 17 | 17 | 16 | 17 | 17 | 17 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 419520
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 0 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 188766
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | [13 empty] | 8 | 8 | 25 | 25 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 332382
167 | Katakhali 50 MW Peaking PP | [17 empty] | 9 |  | 25 | 32 | 32 | 32 | 32 | 24 | 24 | 143733
168 | Santahar 50 MW Peaking PP | [17 empty] | 15 |  | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 163990
169 | Natore 52 MW PP (Rajlanka) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | [6 empty] | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 141010
170 | Chapainawabganj 100 MW Peaking PP | [19 empty] | 80 | 80 | 80 | 80 | 80 | 80 | 30 | 404224
171 | Baghabari 200 MW PP (Paramount) | 170 | 170 | 170 | 100 | 30 | [6 empty] | 20 | 10 | 10 | 38 |  |  |  |  | 50 | 50 | 63 | 90 | 60 | 60 | 100 | 1432649
| Bagura 113 MW PP (Confidence)-2 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 70 | 74 | 108 | 113 | 113 | 113 | 113 | 50 | 50 |  | 72 | 113 | 113 | 113 | 113 | 113 | 113 | 2534304
172 | Confidence Power Bogura Unit-1 113 MW | 95 | 95 | 95 | 95 | 95 | 95 | 35 | 35 | 90 | 70 | 90 | 76 | 95 | 95 | 95 | 95 | 35 | 35 |  | 80 | 95 | 95 | 95 | 95 | 95 | 95 | 1993920
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | 78 | 78 | 78 | 78 | 78 | 78 | 34 | 34 | 45 | 70 | 70 | 73 | 73 | 72 | 71 | 71 | 70 | 71 |  | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 1679856
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1 | 2 | 3 | 4 | 4 | 5 | 4 | 5 | 4 | 3 | 1 | 0 | [8 empty] | 35040
178 | Energypac Power Venture Thakurgaon Ltd. | 94 | 94 | 94 | 94 | 94 | 94 | 56 | 56 | 74 | 74 | 74 | 94 | 94 | 94 | 93 | 94 | 34 | 34 |  | 90 | 94 | 94 | 94 | 94 | 94 | 94 | 1994880
178 | Intraco Solar 30 MW | [5 empty] | 0 | 2 | 4 | 5 | 9 | 18 | 30 | 23 | 25 | 12 | 5 | 1 | 0 | [8 empty] | 140900