## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2022-10-23 | Sunday
|  | Date (day): | 2022-10-23 |  | Sunday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 9965.6 | MW |  |  | (b) At Evening Peak Hour : |  | 12380 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2022-10-22 | 2022-10-23 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 170 | 100 | 100 |  |  | Line O/L
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Machine problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 79 | 80 | 80 | 80 |  | 28 | Engine problem
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 417 | 411 | 400 | 412
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 294 | 257 | 250 | 250 | 110 |  | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 225 | 225 | 225 |  | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 67 | 83 | 67 | 83 |  | 17 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 |  | 335 | Under maint
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 0 | 0 | 0 | 0 |  | 102 | Under maint
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 0 | 19 | 19 |  | 3 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 41 | 87 | 63 | 87 |  | 13 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 161 | 170 | 160 | 170 |  | 165 | ST under maint
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 75 | 92 | 74 | 92 |  | 10 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 54 | 17 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 16 | 132 | 16 | 132 |  | 17 | Engine problem
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 35 | 35 | 35 | 20 |  | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 35 | 35 | 35 | 20 |  | Fuel shortage
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 42 | 39 | 40 | 45 |  | 35 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 0 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 7 | 13 | 12 | 13 |  | 20 | Engine problem
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 41 | 41 | 41 | 41 |  | 11 | Engine problem
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 163 | 260 | 160 | 260 |  | 40 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 106 | 0 | 150 | 150 |  | Fuel conservation
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 0 | 50 | 0 | 50 | 50 |  | Fuel conservation
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 50 | 0 | 50 | 50 |  | Fuel conservation
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 126 | 144 | 80 | 118 |  | 31 | Engine problem
36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 88 | 88 | 88 | 88 |  | 17 | Engine problem
37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 74 | 84 | 74 | 84 | 20 |  | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 35 | 162 | 35 | 162
39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 34 | 0 | 30 | 0
40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 54 | 54 | 54 | 54
| Dhaka area Total |  |  |  |  | 6263 | 5847 | 2480 | 3190 | 2423 | 3157 | 906 | 1709
41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 0 | 25 | 25 | 25
43 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 18 | 0 | 20 | 0
44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 25 | 44 | 32 | 44 |  | 6 | Engine problem
45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 156 | 155 | 155 | 155 | 75 |  | Low Water Level
46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 150 | 151 | 150 | 150 |  | 75 | ST under maint
47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 51 | 105 | 51 | 105
49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 30 | 36 | 30 | 36 | 62 |  | Fuel shortage
50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 16 | 51 | 17 | 51 | 51 |  | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 33 | 56 | 33 | 56 | 44 |  | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 25 | 76 | 25 | 76 |  | 24 | Engine problem
53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 16 | 16 | 16 | 16 |  | 6 | Engine problem
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 30 | 10 | 20
54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 141 | 300 | 140 | 300
57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 54 | 54 | 54 | 54
58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 71 | 105 | 61 | 105
59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 100 | 25 | 100
60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 107 | 107 | 107 | 107 |  | 9 | Engine problem
| Mirsharai 150 MW |  | Gas/HSD | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0
| Chattogram area Total |  |  |  |  | 2442 | 2382 | 924 | 1411 | 956 | 1400 | 700 | 270
61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 148 | 47 | 120 | 135 |  | 75 | ST Under maint.
63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint.
64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 200 | 305 | 260 | 305 | 55 |  | Gas shortage
| Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+136*1 | 284 | 284 | 432 | 318 | 300 | 318 |  |  | On test.
65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 10 | 50 | 48 | 50
66 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 55 | 5 | 47 | 5 | 47 | 8 |  | Gas shortage
67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 73 | 8 | 8 | 187 |  | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 71 | 73 | 70 | 73 | 77 |  | Fuel shortage
70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 44 | 44 | 44 | 44 |  | 8 | Engine problem
71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 50 | 50 | 50 | 113 |  | Gas shortage.
72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 17 | 51 | 17 | 51 | 149 |  | Fuel shortage
73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 22 | 22 | 22
74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 9 | 11 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 162 | 158 | 143 | 166
75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 8 | 25 | 25 | 25 |  | 8 | Engine problem
76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 34 | 8 | 34 | 18 |  | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 15 | 12 | 12 | 15 |  | 10 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 100 | 0 | 100 | 100 |  | Fuel conservation
79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 111 | 17 | 111
80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 0 | 0 | 113 |  | Fuel shortage
81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 35 | 35 | 35 | 35 |  | 19 | Engine problem
82 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 52 | 115 | 53 | 115
| Cumilla Area Total |  |  |  |  | 3193 | 3169 | 1361 | 1732 | 1299 | 1766 | 954 | 480
83 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 31 | 74 | 70 | 80 | 122 |  | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 16 | 18 | 18 | 18 |  | 4 | Engine problem
85 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0
86 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
87 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 57 | 88 | 48 | 88 | 112 |  | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 78 | 97 | 90 | 97 |  | 18 | Engine problem
89 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 54 | 0 | 50 | 0
90 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 12 | 12 |  | 10 | Engine problem
| Mymensingh Area Total |  |  |  |  | 717 | 614 | 250 | 289 | 289.6 | 295 | 122 | 32
91 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 30 | 30 | 30 | 30 |  | 40 | Machine problem.
92 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 41 | 41 | 41 | 41 |  | 49 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 | 163 |  | Gas shortage
94 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Gas shortage
96 | Fenchuganj 44MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Gas shortage
97 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 11 |  | Gas shortage
98 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 58 | 61 | 60 | 61
99 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 0 | 81 | 0 | 81
100 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
101 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 140 | 140 | 140 | 140 |  | 91 | ST Under maint.
102 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18
103 | Sylhet 50MW PP (EPL) |  | Gas | NENP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Gas shortage
104 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 0 | 0 | 0 | 0 | 25 |  | Gas shortage
105 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 280 | 341 | 300 | 341 |  |  | FGMO
106 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 409 | 408 | 400 | 400
107 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
108 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 396 | 380 | 380 | 380
| Sylhet Area Total |  |  |  |  | 2522 | 2477 | 1382 | 1510 | 1379 | 1502 | 350 | 610
109 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 919 | 917 | 937 | 937
110 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 0 | 16 | 0 | 16 | 99 |  | Fuel shortage
111 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 28 | 0 | 30 | 24 |  | Fuel shortage
112 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
113 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 65 | 0 | 65 | 44 |  | Fuel shortage
114 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 200 | 225 | 190 | 225 | 185 |  | Gas shortage
115 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 8 | 0 | 8 | 32 |  | Fuel shortage
116 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 0 | 50 | 50 |  | Fuel conservation
117 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 28 | 75 | 50 | 75 |  | 30 | Engine problem
118 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 15 | 105 | 67 | 105
119 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 84 | 0 | 100 | 0
| Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 0 | 0 | 0 | 0 | 304 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 2388 | 2384 | 1246 | 1743 | 1344 | 1511 | 680 | 30
120 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 32 | 0 | 32 |  |  | Line O/L
121 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 19 | 31 | 16 | 31 |  | 9 | Engine problem
122 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 62 | 50 | 60 | 66 |  | 128 | Machine problem
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
123 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 810 | 810 | 1000 | 1000 |  |  | Line O/L
124 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 212 | 205 | 200 | 205
125 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 0 | 0 |  |  | Line O/L
| Barisal Area Total |  |  |  |  | 1958 | 1958 | 1103 | 1128 | 1276 | 1334 | 0 | 137
126 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
127 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 32 | 0 | 32 |  | 20 | Engine problem
128 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 0 |  | 71 | Engine problem
129 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
130 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 16 | 42 | 16 | 42 |  | 8 | Engine problem
131 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 32 | 0 | 32 | 18 |  | Fuel shortage
132 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 171 | 0 | 0 | 0 | 210 |  | Gas shortage
133 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Fuel shortage
134 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 143 | 143 | 140 | 143 | 77 |  | Gas shortage
135 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 280 | 374 | 320 | 374 | 40 |  | Gas shortage
136 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 32 | 0 | 32 |  | 18 | Engine problem
137 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 18 | 22 | 20 | 22
138 | Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
139 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
140 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 8 | 0 | 8 | 44 |  | Fuel shortage
141 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 86 | 0 | 86 |  | 18 | Engine problem
142 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 0 | 100 | 100 |  | Fuel conservation
143 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 69 | 113 | 113 | 113
144 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 90 | 113 | 113 | 113
145 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
| Rajshahi Area Total |  |  |  |  | 2199 | 2129 | 803 | 1008 | 739 | 1108 | 880 | 135
146 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 78 | 81 | 80 | 81
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
147 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 |  | 274 | Under maint
148 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
149 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
150 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 52 | 113 | 90 | 113
151 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 0 | 0 | 8 | 0
152 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 36 | 113 | 70 | 113
| Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 35 | 0 | 12 | 0
| Rangpur Area Total |  |  |  |  | 830 | 750 | 201 | 307 | 260 | 307 | 40 | 359
| Total |  |  |  |  | 22512 | 21710 | 9750 | 12318 | 9965.6 | 12380 | 4632 | 3762
[6 empty] | 41757 | 41467 | 17969 | 23006 | 23006 | 17969
A. |  | 2022-10-22 | (Yesterday) |  |  |  |  | Saturday
1 | Highest Generation : |  |  | 12318 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 9281 | MW at | 9:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 12952 | MW
3 | Day peak Generation : |  |  | 9750 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 12372.96 | MW
4 | Evening peak Generation : |  |  | 12318 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 584 | MW
5 | Total Energy Generation : |  | 250.6362 | MKWHr | By Solar | 1.6784 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Gas : | 128.0792 | MKWHr |  | By Oil: | 66.2744 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 25.0874 | MKWHr |  | By Hydro: | 3.7394 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 4632 | MW | Dhaka | 4665.6 | 4505.6 |  | 160 |  | 18:00 |  | 1300.3423
|  |  | For Plants S/D or M/C prob = |  |  | 3762 | MW | Chittagong | 1214.3 | 1214.3 |  | 0 |  | 19:00 |  | 1196
|  |  | Total = |  |  | 8394 | MW | Khulna | 1480.6 | 1480.6 |  | 0 |  | 19:30 |  | 1162.1061
7 | Total Gas Supplied : |  |  | 973.92 | MMCFD |  |  | Rajshahi | 1212.6 | 1212.6 |  | 0 |  | 20:00 |  | 854.3
8 | Fuel Cost : | i) Gas : | Taka | 134111225.468 | ii) Oil : | Taka | 893521634.55 | Comilla | 1249 | 1128 |  | 121 |  | 21:00 |  | 584.2786
|  | iii) Coal : |  | 201935663.42 | Total | Taka | 1229568523.438 | Mymensingh | 1005 | 805 |  | 200 |  | 22:00 |  | 568.6118
9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0 | MKWHr. | Sylhet | 522 | 419 |  | 103 |  | 23:00 |  | 740.9463
| ii) During Peak Demand : |  |  | 1062 | MW (E to W) at | 21:00 | hrs | Barisal | 378.86 | 378.86 |  | 0 |  | 24:00 |  | 1626
| iii) Maximum : |  |  | 496 | MW at | 18:00 | hrs | Rangpur | 645 | 645 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 34.8° C |  |  | Total | 12372.96 | 11788.96 |  | 584
B. |  | 2022-10-23 | (Today) |  |  |  | Sunday |  |  | Probable max. temperature in Dhaka |  |  | 31.8° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 13500 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 1032 | MW
2 | Maximum Generation (Generation end) |  |  |  | 12380 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 11500 | MW
4 | Reserve(Generation end) |  |  |  | - | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 274.6866 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 9259 | MW at | 8:00 | 400 | 165 | 0 | 0 | 160 | 180 | 50 | 0 | 77
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 22.2255 | MKWHr. | ii) HVDC Flow at Peak Time |  | 917 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.552 | MKWHr. | iii) Maximum HVDC Flow : |  | 921 | MW at | 3:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 97.41 |  | (b) Today: | 97.21 |  | (c) Rule Curve: |  | 108
.

## YesterdayGen
2022-10-22
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 100 | 175 | 0 | 84 | 0 | 392 | 250 |  | 0 | 225 | 0 | 58 | 0 | 55 | 159 | 0 | 0 | 58 | 58 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 21 | 28 | 33 | 16 | 41 | 0 | 84 | 70 | 0 | 0 | 25 | 151 | 0 | 0 | 0 |  | 12 | 30 | 17 | 33 | 0 | 33 | 16 | 40 | 0 | 0 | 0 | 0 | 345 | 208 | 8 | 50 | 48 | 51 | 0 | 51 | 0 | 45 | 43 | 22 | 11 | 25 | 15 | 128 | 108 | 0 | 19 | 0 | 30 | 41 | 0 | 0 | 0 | 0 | 63 | 0 | 0 | 140 | 19 | 0 | 10 | 320 | 0 | 5 | 0 | 97 | 0 | 0 | 48 | 0 | 100 | 0 | 25 | 24 | 65 | 408 | 89 | 88 | 68 | 0 | 106 | 54 | 51 | 111 | 0 | 25 | 400 | 55 | 0 | 35 | 107 | 0 | 35 | 0 | 54 | 54 | 202 | 0 | 0 |  | 920 | 0 | 210 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 42 | 0 | 0 | 0 | 22 | 0 | 11 | 82 | 0 | 0 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 146 | 0 | 302 | 72 | 0 | 113 | 105 | 107 | 0 | 0 | 113 | 890 | 221 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 |  | 6492 | 3734 | 10226 | 3906 | 920 | 1609 | 0 | 2397 | 972 | 154 | 0 | 140 | 128 | 0 | 676.4361 | 97.26
2:00 | 0 | 0 | 100 | 175 | 0 | 84 | 0 | 392 | 257 |  | 0 | 225 | 0 | 59 | 0 | 55 | 155 | 0 | 0 | 58 | 58 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 21 | 28 | 33 | 16 | 41 | 0 | 84 | 70 | 0 | 0 | 25 | 151 | 0 | 0 | 0 |  | 12 | 30 | 17 | 33 | 0 | 33 | 16 | 40 | 0 | 0 | 0 | 0 | 310 | 191 | 8 | 50 | 48 | 51 | 0 | 51 | 0 | 46 | 43 | 22 | 11 | 25 | 15 | 142 | 108 | 0 | 19 | 0 | 30 | 41 | 0 | 0 | 0 | 0 | 63 | 0 | 0 | 140 | 18 | 0 | 10 | 300 | 0 | 0 | 0 | 97 | 0 | 0 | 48 | 0 | 90 | 0 | 25 | 17 | 65 | 406 | 89 | 88 | 68 | 0 | 106 | 41 | 51 | 111 | 2 | 25 | 400 | 54 | 0 | 35 | 107 | 0 | 35 | 0 | 49 | 54 | 202 | 0 | 0 |  | 919 | 0 | 210 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 21 | 0 | 11 | 82 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 305 | 72 | 0 | 70 | 105 | 70 | 0 | 0 | 70 | 870 | 221 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 |  | 6397 | 3558 | 9955 | 3840 | 919 | 1598 | 0 | 2241 | 952 | 154 | 0 | 109 | 142 | 0 | 658.9261 | 97.25
3:00 | 0 | 0 | 100 | 175 | 0 | 84 | 0 | 393 | 260 |  | 0 | 225 | 0 | 59 | 0 | 55 | 160 | 0 | 0 | 57 | 58 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 20 | 28 | 33 | 16 | 41 | 0 | 83 | 70 | 0 | 0 | 25 | 151 | 0 | 0 | 0 |  | 12 | 30 | 17 | 33 | 0 | 33 | 16 | 40 | 0 | 0 | 0 | 0 | 310 | 182 | 8 | 51 | 48 | 51 | 0 | 51 | 0 | 46 | 43 | 22 | 11 | 25 | 15 | 142 | 108 | 0 | 19 | 0 | 30 | 41 | 0 | 0 | 0 | 0 | 63 | 0 | 0 | 140 | 19 | 0 | 10 | 290 | 0 | 0 | 0 | 97 | 0 | 0 | 48 | 0 | 88 | 0 | 25 | 17 | 56 | 407 | 89 | 88 | 68 | 0 | 106 | 54 | 51 | 111 | 0 | 25 | 400 | 54 | 0 | 35 | 107 | 0 | 35 | 0 | 54 | 54 | 202 | 0 | 0 |  | 921 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 22 | 0 | 8 | 82 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 146 | 0 | 313 | 72 | 0 | 35 | 67 | 34 | 0 | 0 | 35 | 840 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6392 | 3313 | 9705 | 3837 | 921 | 1597 | 0 | 2024 | 922 | 153 | 0 | 109 | 142 | 0 | 608.2395 | 97.24
4:00 | 0 | 0 | 100 | 175 | 0 | 84 | 0 | 396 | 264 |  | 0 | 225 | 0 | 58 | 0 | 55 | 167 | 0 | 0 | 57 | 58 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 20 | 28 | 33 | 16 | 41 | 0 | 83 | 70 | 0 | 0 | 25 | 150 | 0 | 0 | 0 |  | 12 | 30 | 17 | 33 | 0 | 33 | 16 | 42 | 0 | 0 | 0 | 0 | 310 | 176 | 8 | 50 | 48 | 51 | 0 | 51 | 0 | 46 | 40 | 22 | 11 | 25 | 15 | 140 | 110 | 0 | 19 | 0 | 30 | 41 | 0 | 0 | 0 | 0 | 63 | 0 | 0 | 140 | 19 | 0 | 10 | 280 | 0 | 0 | 0 | 97 | 0 | 0 | 48 | 0 | 90 | 0 | 25 | 17 | 61 | 407 | 89 | 88 | 68 | 0 | 106 | 54 | 51 | 17 | 0 | 25 | 400 | 54 | 0 | 35 | 107 | 0 | 35 | 0 | 54 | 54 | 202 | 0 | 0 |  | 920 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 22 | 0 | 8 | 83 | 0 | 0 | 0 | 0 | 182 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 312 | 17 | 0 | 35 | 50 | 34 | 0 | 0 | 35 | 840 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6299 | 3239 | 9538 | 3840 | 920 | 1592 | 0 | 1861 | 923 | 153 | 0 | 109 | 140 | 0 | 479 | 97.23
5:00 | 0 | 0 | 100 | 175 | 0 | 84 | 0 | 397 | 264 |  | 0 | 225 | 0 | 59 | 0 | 55 | 172 | 0 | 0 | 57 | 58 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 21 | 26 | 33 | 16 | 41 | 0 | 83 | 70 | 0 | 0 | 25 | 150 | 0 | 0 | 0 |  | 12 | 30 | 17 | 33 | 0 | 33 | 16 | 42 | 0 | 0 | 0 | 0 | 325 | 165 | 8 | 50 | 48 | 51 | 0 | 51 | 0 | 46 | 34 | 22 | 11 | 25 | 15 | 134 | 109 | 0 | 19 | 0 | 30 | 41 | 0 | 0 | 0 | 0 | 63 | 0 | 0 | 140 | 19 | 0 | 10 | 295 | 0 | 0 | 0 | 97 | 0 | 0 | 48 | 0 | 90 | 0 | 25 | 17 | 68 | 353 | 89 | 88 | 68 | 0 | 106 | 54 | 51 | 17 | 0 | 25 | 350 | 54 | 0 | 35 | 107 | 0 | 35 | 0 | 53 | 42 | 202 | 0 | 0 |  | 920 | 0 | 215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 22 | 0 | 8 | 83 | 0 | 0 | 0 | 0 | 182 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 316 | 17 | 0 | 35 | 50 | 34 | 0 | 0 | 35 | 800 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6201 | 3173 | 9374 | 3754 | 920 | 1571 | 0 | 1850 | 883 | 153 | 0 | 109 | 134 | 0 | 0 | 97.22
6:00 | 0 | 0 | 100 | 175 | 0 | 84 | 0 | 398 | 264 |  | 0 | 225 | 0 | 59 | 0 | 55 | 176 | 0 | 0 | 54 | 58 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 19 | 28 | 33 | 16 | 41 | 0 | 84 | 70 | 0 | 0 | 25 | 140 | 0 | 0 | 0 |  | 9 | 30 | 17 | 33 | 0 | 33 | 16 | 42 | 0 | 0 | 0 | 0 | 310 | 165 | 8 | 50 | 49 | 51 | 0 | 51 | 0 | 46 | 34 | 22 | 11 | 25 | 15 | 130 | 109 | 0 | 19 | 0 | 30 | 41 | 0 | 0 | 0 | 0 | 63 | 0 | 0 | 140 | 19 | 0 | 10 | 300 | 0 | 0 | 0 | 97 | 0 | 0 | 48 | 0 | 88 | 0 | 25 | 17 | 70 | 352 | 89 | 88 | 68 | 0 | 106 | 54 | 51 | 17 | 0 | 25 | 330 | 54 | 0 | 35 | 107 | 0 | 35 | 0 | 54 | 54 | 204 | 0 | 0 |  | 920 | 0 | 215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 22 | 0 | 8 | 82 | 0 | 0 | 0 | 0 | 182 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 317 | 17 | 0 | 35 | 32 | 34 | 0 | 0 | 35 | 800 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6172 | 3147 | 9319 | 3716 | 920 | 1577 | 0 | 1831 | 882 | 154 | 0 | 109 | 130 | 0 | 0 | 97.41
7:00 | 0 | 0 | 100 | 175 | 0 | 84 | 0 | 398 | 264 |  | 0 | 225 | 0 | 59 | 0 | 55 | 177 | 0 | 0 | 0 | 58 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 19 | 28 | 33 | 16 | 41 | 0 | 85 | 70 | 0 | 0 | 25 | 150 | 0 | 0 | 0 |  | 12 | 30 | 17 | 33 | 0 | 33 | 16 | 41 | 0 | 0 | 0 | 0 | 330 | 157 | 8 | 50 | 49 | 51 | 0 | 51 | 0 | 46 | 34 | 22 | 11 | 25 | 15 | 116 | 70 | 0 | 19 | 0 | 30 | 41 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 140 | 19 | 0 | 10 | 320 | 0 | 0 | 0 | 95 | 0 | 0 | 48 | 0 | 89 | 5 | 25 | 17 | 70 | 408 | 89 | 88 | 68 | 1 | 106 | 54 | 51 | 17 | 3 | 25 | 400 | 73 | 7 | 35 | 107 | 0 | 35 | 6 | 54 | 54 | 203 | 0 | 0 |  | 921 | 0 | 215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 22 | 0 | 8 | 82 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 317 | 17 | 0 | 35 | 32 | 34 | 0 | 1 | 35 | 750 | 180 | 0 | 0 | 1 | 13 | 0 | 0 | 0 | 0 | 5 |  | 6278 | 3119 | 9397 | 3832 | 921 | 1592 | 0 | 1801 | 832 | 155 | 0 | 109 | 116 | 39 | 0 | 97.4
8:00 | 0 | 0 | 100 | 175 | 0 | 84 | 0 | 400 | 288 |  | 0 | 225 | 0 | 63 | 0 | 55 | 181 | 0 | 0 | 0 | 58 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 21 | 28 | 33 | 14 | 41 | 0 | 86 | 70 | 0 | 0 | 0 | 152 | 0 | 0 | 0 |  | 12 | 30 | 17 | 33 | 0 | 33 | 16 | 19 | 0 | 0 | 0 | 0 | 310 | 179 | 8 | 50 | 48 | 20 | 0 | 51 | 0 | 47 | 34 | 22 | 11 | 14 | 15 | 128 | 70 | 0 | 19 | 1 | 30 | 41 | 0 | 0 | 0 | 0 | 64 | 0 | 0 | 140 | 18 | 0 | 10 | 300 | 0 | 0 | 0 | 97 | 0 | 0 | 48 | 0 | 89 | 11 | 25 | 17 | 70 | 409 | 89 | 88 | 68 | 2 | 106 | 54 | 51 | 17 | 0 | 25 | 400 | 73 | 14 | 35 | 107 | 0 | 35 | 16 | 53 | 54 | 203 | 0 | 0 |  | 921 | 0 | 215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 21 | 0 | 8 | 81 | 0 | 0 | 0 | 0 | 183 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 306 | 17 | 0 | 39 | 32 | 34 | 0 | 1 | 70 | 770 | 183 | 0 | 0 | 3 | 39 | 0 | 0 | 0 | 0 | 16 |  | 6242 | 3113 | 9355 | 3736 | 921 | 1533 | 0 | 1817 | 851 | 156 | 0 | 110 | 128 | 103 | 282.0019 | 97.39
9:00 | 0 | 0 | 100 | 175 | 0 | 84 | 0 | 418 | 288 |  | 0 | 225 | 0 | 68 | 0 | 55 | 160 | 0 | 0 | 0 | 75 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 21 | 28 | 33 | 14 | 41 | 0 | 86 | 70 | 0 | 0 | 0 | 151 | 0 | 0 | 0 |  | 12 | 30 | 17 | 33 | 0 | 26 | 16 | 10 | 0 | 0 | 0 | 0 | 260 | 160 | 8 | 50 | 45 | 20 | 0 | 51 | 0 | 47 | 8 | 19 | 8 | 14 | 15 | 136 | 21 | 0 | 19 | 2 | 30 | 41 | 0 | 0 | 0 | 0 | 64 | 0 | 0 | 140 | 18 | 0 | 10 | 275 | 0 | 0 | 0 | 97 | 0 | 0 | 48 | 0 | 91 | 7 | 25 | 17 | 68 | 389 | 89 | 88 | 54 | 3 | 140 | 54 | 53 | 17 | 0 | 25 | 350 | 74 | 40 | 35 | 107 | 0 | 35 | 24 | 54 | 54 | 393 | 0 | 0 |  | 921 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 20 | 0 | 8 | 82 | 0 | 0 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 146 | 0 | 257 | 17 | 0 | 35 | 15 | 34 | 0 | 4 | 35 | 770 | 183 | 0 | 0 | 4 | 61 | 0 | 0 | 0 | 0 | 25 |  | 6250 | 3031 | 9281 | 3716 | 921 | 1446 | 0 | 1774 | 852 | 156 | 0 | 110 | 136 | 170 | 447.8854 | 97.38
10:00 | 0 | 0 | 100 | 175 | 0 | 79 | 0 | 419 | 302 |  | 0 | 225 | 0 | 67 | 0 | 55 | 158 | 0 | 0 | 0 | 75 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 21 | 26 | 33 | 14 | 41 | 0 | 86 | 70 | 0 | 0 | 0 | 150 | 0 | 0 | 0 |  | 12 | 30 | 16 | 33 | 0 | 25 | 16 | 0 | 0 | 0 | 0 | 0 | 200 | 149 | 8 | 50 | 46 | 10 | 0 | 51 | 0 | 46 | 8 | 19 | 8 | 14 | 15 | 140 | 16 | 0 | 18 | 2 | 30 | 41 | 0 | 0 | 0 | 0 | 59 | 0 | 0 | 140 | 18 | 0 | 10 | 280 | 0 | 0 | 0 | 145 | 0 | 0 | 48 | 0 | 123 | 18 | 25 | 17 | 65 | 408 | 87 | 88 | 51 | 4 | 140 | 54 | 68 | 17 | 0 | 25 | 350 | 74 | 49 | 35 | 107 | 0 | 35 | 30 | 54 | 54 | 424 | 0 | 0 |  | 920 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 8 | 80 | 0 | 0 | 0 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 146 | 0 | 259 | 17 | 0 | 35 | 0 | 34 | 0 | 6 | 0 | 770 | 183 | 0 | 0 | 5 | 78 | 0 | 0 | 0 | 0 | 31 |  | 6323 | 2985 | 9308 | 3666 | 920 | 1444 | 0 | 1801 | 850 | 156 | 0 | 108 | 140 | 223 | 471.8464 | 97.37
11:00 | 0 | 0 | 100 | 180 | 0 | 79 | 0 | 420 | 302 |  | 0 | 225 | 0 | 68 | 0 | 55 | 160 | 0 | 0 | 7 | 75 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 19 | 25 | 33 | 12 | 41 | 0 | 86 | 70 | 0 | 0 | 0 | 150 | 0 | 0 | 0 |  | 12 | 30 | 16 | 33 | 0 | 25 | 16 | 2 | 0 | 0 | 0 | 0 | 200 | 130 | 8 | 52 | 46 | 5 | 0 | 51 | 0 | 45 | 8 | 19 | 8 | 8 | 15 | 150 | 25 | 0 | 16 | 2 | 30 | 41 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 140 | 18 | 0 | 10 | 280 | 0 | 0 | 0 | 163 | 0 | 0 | 59 | 0 | 125 | 20 | 25 | 17 | 68 | 410 | 77 | 88 | 51 | 4 | 141 | 54 | 70 | 17 | 0 | 25 | 400 | 74 | 43 | 35 | 107 | 0 | 35 | 33 | 38 | 54 | 428 | 0 | 0 |  | 921 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 300 | 17 | 0 | 35 | 0 | 34 | 0 | 6 | 0 | 750 | 215 | 0 | 0 | 5 | 86 | 0 | 0 | 0 | 0 | 35 |  | 6371 | 3054 | 9425 | 3692 | 921 | 1515 | 0 | 1820 | 830 | 156 | 0 | 107 | 150 | 234 | 943.6928 | #REF!
12:00 | 0 | 0 | 100 | 180 | 0 | 79 | 0 | 417 | 294 |  | 0 | 225 | 0 | 67 | 0 | 55 | 161 | 0 | 0 | 41 | 75 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 18 | 24 | 0 | 7 | 41 | 0 | 86 | 70 | 0 | 0 | 0 | 150 | 0 | 0 | 0 |  | 12 | 30 | 16 | 33 | 0 | 25 | 16 | 2 | 0 | 0 | 0 | 0 | 200 | 148 | 8 | 50 | 10 | 5 | 0 | 51 | 0 | 44 | 8 | 19 | 9 | 8 | 15 | 162 | 31 | 0 | 16 | 2 | 30 | 41 | 0 | 0 | 0 | 0 | 58 | 0 | 0 | 140 | 18 | 0 | 10 | 280 | 0 | 0 | 0 | 163 | 0 | 0 | 57 | 0 | 126 | 18 | 25 | 17 | 71 | 409 | 78 | 88 | 51 | 4 | 141 | 54 | 71 | 17 | 0 | 25 | 396 | 74 | 54 | 35 | 107 | 0 | 35 | 34 | 52 | 54 | 432 | 0 | 0 |  | 919 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 18 | 0 | 11 | 78 | 0 | 0 | 0 | 0 | 171 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 280 | 28 | 0 | 69 | 15 | 52 | 0 | 0 | 90 | 810 | 212 | 0 | 0 | 5 | 84 | 36 | 0 | 0 | 0 | 35 |  | 6397 | 3353 | 9750 | 3709 | 919 | 1483 | 0 | 2091 | 888 | 156 | 0 | 106 | 162 | 236 | 1062 | 97.35
13:00 | 0 | 0 | 93 | 180 | 0 | 76 | 0 | 411 | 285 |  | 0 | 225 | 0 | 67 | 0 | 55 | 160 | 0 | 0 | 60 | 75 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 18 | 6 | 0 | 13 | 41 | 0 | 86 | 70 | 0 | 0 | 0 | 148 | 0 | 0 | 0 |  | 12 | 30 | 16 | 33 | 0 | 25 | 16 | 2 | 0 | 0 | 0 | 0 | 200 | 163 | 8 | 50 | 10 | 5 | 0 | 51 | 0 | 43 | 8 | 21 | 11 | 8 | 15 | 164 | 31 | 0 | 16 | 2 | 30 | 41 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 140 | 18 | 0 | 10 | 341 | 0 | 0 | 0 | 160 | 0 | 0 | 48 | 0 | 125 | 20 | 25 | 17 | 67 | 380 | 78 | 88 | 51 | 4 | 141 | 54 | 71 | 17 | 8 | 24 | 392 | 74 | 51 | 35 | 107 | 0 | 35 | 31 | 53 | 54 | 431 | 0 | 0 |  | 920 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 18 | 0 | 11 | 78 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 257 | 54 | 0 | 113 | 15 | 56 | 0 | 7 | 113 | 830 | 213 | 0 | 0 | 5 | 83 | 98 | 0 | 0 | 0 | 34 |  | 6412 | 3521 | 9933 | 3648 | 920 | 1509 | 0 | 2286 | 908 | 156 | 0 | 105 | 164 | 237 | 1163 | 97.34
14:00 | 0 | 0 | 100 | 180 | 0 | 73 | 0 | 413 | 283 |  | 0 | 225 | 0 | 67 | 0 | 55 | 160 | 0 | 0 | 70 | 75 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 18 | 23 | 33 | 13 | 41 | 0 | 86 | 70 | 0 | 0 | 0 | 146 | 0 | 0 | 0 |  | 12 | 30 | 15 | 33 | 0 | 25 | 16 | 2 | 0 | 0 | 0 | 0 | 200 | 174 | 8 | 50 | 10 | 5 | 0 | 51 | 0 | 43 | 13 | 21 | 11 | 8 | 15 | 160 | 31 | 0 | 16 | 2 | 30 | 41 | 0 | 0 | 0 | 0 | 58 | 0 | 0 | 140 | 18 | 0 | 10 | 341 | 0 | 0 | 0 | 165 | 0 | 0 | 58 | 0 | 131 | 17 | 25 | 17 | 67 | 355 | 78 | 88 | 51 | 3 | 141 | 54 | 71 | 17 | 0 | 25 | 378 | 74 | 45 | 75 | 107 | 0 | 35 | 27 | 54 | 54 | 414 | 0 | 0 |  | 921 | 0 | 190 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 21 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 42 | 0 | 0 | 0 | 18 | 0 | 11 | 78 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 139 | 0 | 267 | 55 | 0 | 113 | 50 | 107 | 0 | 7 | 113 | 860 | 212 | 0 | 0 | 4 | 67 | 113 | 0 | 0 | 0 | 29 |  | 6468 | 3659 | 10127 | 3653 | 921 | 1516 | 0 | 2474 | 938 | 156 | 0 | 108 | 160 | 201 | 1151 | 97.36
15:00 | 0 | 0 | 100 | 180 | 0 | 73 | 0 | 412 | 273 |  | 0 | 225 | 0 | 67 | 0 | 55 | 150 | 0 | 0 | 70 | 75 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 18 | 23 | 33 | 13 | 41 | 0 | 83 | 70 | 0 | 0 | 0 | 148 | 0 | 0 | 0 |  | 12 | 28 | 15 | 33 | 0 | 25 | 16 | 2 | 0 | 0 | 0 | 0 | 200 | 180 | 8 | 50 | 10 | 5 | 0 | 51 | 0 | 35 | 16 | 21 | 11 | 10 | 15 | 164 | 30 | 0 | 16 | 2 | 30 | 41 | 0 | 0 | 0 | 0 | 56 | 0 | 0 | 140 | 18 | 0 | 10 | 341 | 0 | 0 | 0 | 155 | 0 | 0 | 58 | 0 | 134 | 8 | 25 | 17 | 68 | 355 | 78 | 88 | 51 | 2 | 141 | 54 | 70 | 17 | 0 | 25 | 391 | 74 | 33 | 0 | 107 | 0 | 35 | 19 | 54 | 54 | 430 | 0 | 0 |  | 917 | 0 | 190 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 21 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 42 | 0 | 0 | 0 | 19 | 0 | 11 | 77 | 0 | 0 | 0 | 0 | 148 | 0 | 0 | 0 | 0 | 0 | 138 | 0 | 266 | 54 | 0 | 113 | 50 | 107 | 0 | 5 | 113 | 890 | 213 | 0 | 0 | 3 | 48 | 113 | 0 | 0 | 0 | 21 |  | 6365 | 3643 | 10008 | 3667 | 917 | 1507 | 0 | 2394 | 967 | 153 | 0 | 98 | 164 | 141 | 1363 | 97.36
16:00 | 0 | 0 | 100 | 180 | 0 | 70 | 0 | 418 | 272 |  | 0 | 225 | 0 | 65 | 0 | 55 | 140 | 0 | 0 | 70 | 75 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 18 | 23 | 33 | 13 | 41 | 0 | 83 | 70 | 0 | 0 | 2 | 150 | 0 | 0 | 0 |  | 12 | 34 | 15 | 33 | 0 | 25 | 16 | 2 | 0 | 0 | 0 | 0 | 260 | 176 | 8 | 51 | 10 | 5 | 0 | 51 | 0 | 38 | 15 | 21 | 11 | 16 | 15 | 168 | 30 | 0 | 16 | 1 | 30 | 41 | 0 | 0 | 0 | 0 | 62 | 0 | 0 | 140 | 18 | 0 | 10 | 325 | 0 | 0 | 0 | 155 | 0 | 0 | 57 | 0 | 134 | 3 | 11 | 22 | 68 | 412 | 78 | 88 | 51 | 1 | 141 | 54 | 76 | 17 | 0 | 25 | 370 | 74 | 18 | 65 | 107 | 0 | 35 | 10 | 53 | 42 | 327 | 0 | 0 |  | 917 | 0 | 190 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 56 | 19 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 34 | 0 | 0 | 0 | 19 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 142 | 0 | 0 | 0 | 0 | 0 | 138 | 0 | 278 | 54 | 0 | 113 | 50 | 103 | 0 | 3 | 50 | 880 | 215 | 0 | 0 | 2 | 23 | 95 | 0 | 0 | 0 | 10 |  | 6374 | 3502 | 9876 | 3653 | 917 | 1499 | 0 | 2348 | 960 | 153 | 0 | 107 | 168 | 71 | 1438.5786 | 97.35
17:00 | 0 | 0 | 100 | 180 | 0 | 70 | 0 | 407 | 252 |  | 0 | 225 | 0 | 67 | 0 | 55 | 169 | 0 | 0 | 78 | 75 | 16 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 19 | 18 | 23 | 33 | 13 | 36 | 0 | 84 | 70 | 0 | 0 | 17 | 150 | 0 | 0 | 0 |  | 12 | 34 | 15 | 33 | 0 | 40 | 16 | 2 | 0 | 0 | 0 | 0 | 320 | 0 | 8 | 49 | 10 | 5 | 0 | 51 | 0 | 38 | 16 | 20 | 11 | 0 | 0 | 156 | 30 | 0 | 16 | 0 | 30 | 41 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 140 | 18 | 0 | 10 | 341 | 0 | 0 | 0 | 155 | 0 | 0 | 58 | 0 | 134 | 0 | 25 | 28 | 67 | 366 | 78 | 88 | 70 | 0 | 141 | 54 | 105 | 110 | 0 | 25 | 400 | 74 | 2 | 109 | 107 | 0 | 35 | 1 | 72 | 42 | 309 | 0 | 0 |  | 918 | 0 | 195 | 0 | 16 | 0 | 0 | 0 | 6 | 10 | 0 | 64 | 21 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 42 | 0 | 0 | 0 | 20 | 0 | 11 | 79 | 0 | 0 | 0 | 0 | 138 | 0 | 0 | 0 | 0 | 0 | 138 | 0 | 279 | 54 | 0 | 50 | 50 | 106 | 0 | 1 | 50 | 730 | 213 | 0 | 0 | 0 | 4 | 36 | 0 | 0 | 155 | 2 |  | 6439 | 3392 | 9831 | 3494 | 918 | 1497 | 0 | 2515 | 964 | 154 | 0 | 123 | 156 | 10 | 1480.0495 | 97.34
18:00 | 0 | 0 | 100 | 180 | 0 | 70 | 0 | 408 | 253 |  | 0 | 225 | 0 | 70 | 0 | 55 | 184 | 0 | 0 | 85 | 83 | 132 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 19 | 18 | 23 | 33 | 13 | 38 | 0 | 84 | 70 | 0 | 0 | 17 | 151 | 0 | 0 | 0 |  | 12 | 34 | 51 | 56 | 0 | 43 | 16 | 4 | 0 | 0 | 0 | 0 | 305 | 0 | 45 | 49 | 48 | 20 | 0 | 51 | 0 | 43 | 20 | 20 | 11 | 22 | 12 | 172 | 33 | 0 | 16 | 0 | 30 | 41 | 0 | 0 | 0 | 0 | 63 | 81 | 0 | 140 | 18 | 0 | 10 | 341 | 0 | 0 | 50 | 215 | 24 | 50 | 86 | 51 | 134 | 0 | 25 | 51 | 68 | 400 | 97 | 88 | 105 | 0 | 276 | 54 | 105 | 111 | 5 | 42 | 360 | 74 | 0 | 149 | 107 | 0 | 35 | 0 | 115 | 54 | 321 | 0 | 0 |  | 917 | 0 | 200 | 0 | 16 | 0 | 0 | 0 | 36 | 45 | 8 | 50 | 29 | 16 | 0 | 0 | 0 | 32 | 4 | 85 | 0 | 42 | 0 | 8 | 15 | 20 | 0 | 11 | 79 | 0 | 0 | 0 | 0 | 138 | 0 | 0 | 0 | 0 | 30 | 138 | 0 | 272 | 71 | 3 | 80 | 105 | 109 | 0 | 0 | 113 | 720 | 202 | 0 | 0 | 0 | 0 | 113 | 0 | 0 | 188 | 0 |  | 7494 | 3895 | 11389 | 3571 | 917 | 1623 | 208 | 3280 | 987 | 154 | 0 | 477 | 172 | 0 | 1300.3423 | 97.33
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1196.2043 | 0
19:00 | 0 | 0 | 100 | 180 | 0 | 70 | 0 | 411 | 253 |  | 0 | 225 | 0 | 75 | 0 | 55 | 171 | 0 | 0 | 87 | 83 | 132 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 19 | 18 | 23 | 33 | 13 | 41 | 0 | 85 | 70 | 0 | 0 | 18 | 151 | 0 | 0 | 0 |  | 12 | 36 | 51 | 56 | 0 | 44 | 16 | 10 | 0 | 0 | 0 | 0 | 305 | 0 | 45 | 49 | 50 | 47 | 0 | 51 | 0 | 44 | 31 | 21 | 11 | 25 | 12 | 154 | 33 | 0 | 16 | 0 | 30 | 41 | 0 | 0 | 0 | 0 | 61 | 81 | 0 | 140 | 18 | 0 | 10 | 341 | 0 | 0 | 50 | 270 | 60 | 25 | 87 | 25 | 135 | 0 | 76 | 51 | 71 | 409 | 97 | 88 | 105 | 0 | 284 | 54 | 105 | 111 | 0 | 100 | 398 | 74 | 0 | 162 | 107 | 0 | 35 | 0 | 115 | 54 | 318 | 0 | 0 |  | 917 | 0 | 200 | 0 | 9 | 0 | 0 | 0 | 30 | 75 | 8 | 54 | 32 | 32 | 0 | 0 | 0 | 32 | 8 | 85 | 0 | 42 | 32 | 8 | 32 | 22 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 138 | 0 | 297 | 75 | 0 | 113 | 105 | 113 | 0 | 0 | 113 | 760 | 205 | 0 | 0 | 0 | 0 | 113 | 0 | 0 | 277 | 0 |  | 7764 | 4038 | 11802 | 3495 | 917 | 1689 | 160 | 3558 | 1117 | 155 | 0 | 557 | 154 | 0 | 1196 | 97.3
19:30 | 0 | 0 | 140 | 180 | 0 | 79 | 0 | 411 | 253 |  | 0 | 225 | 0 | 84 | 0 | 55 | 180 | 0 | 0 | 87 | 83 | 132 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 0 | 18 | 24 | 33 | 13 | 41 | 0 | 85 | 70 | 0 | 0 | 25 | 152 | 0 | 0 | 0 |  | 12 | 36 | 51 | 56 | 0 | 44 | 16 | 14 | 0 | 0 | 0 | 0 | 305 | 29 | 51 | 50 | 50 | 47 | 0 | 51 | 0 | 44 | 34 | 21 | 11 | 25 | 12 | 172 | 47 | 0 | 18 | 0 | 30 | 41 | 0 | 0 | 0 | 0 | 63 | 81 | 0 | 140 | 18 | 0 | 10 | 341 | 0 | 0 | 50 | 260 | 106 | 25 | 87 | 25 | 135 | 0 | 76 | 51 | 72 | 409 | 97 | 88 | 105 | 0 | 284 | 54 | 105 | 111 | 0 | 100 | 400 | 74 | 0 | 162 | 107 | 0 | 35 | 0 | 115 | 54 | 318 | 0 | 0 |  | 917 | 0 | 200 | 0 | 16 | 0 | 0 | 0 | 28 | 60 | 8 | 63 | 32 | 32 | 0 | 0 | 0 | 32 | 8 | 86 | 0 | 42 | 32 | 8 | 32 | 22 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 137 | 0 | 330 | 75 | 0 | 113 | 105 | 113 | 0 | 0 | 113 | 770 | 223 | 0 | 0 | 0 | 0 | 113 | 0 | 0 | 285 | 0 |  | 7939 | 4086 | 12025 | 3565 | 917 | 1759 | 206 | 3575 | 1135 | 155 | 0 | 541 | 172 | 0 | 1162.1061 | 0
20:00 | 0 | 0 | 170 | 180 | 0 | 80 | 0 | 410 | 253 |  | 0 | 225 | 0 | 81 | 0 | 55 | 175 | 0 | 0 | 87 | 92 | 132 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 0 | 18 | 24 | 33 | 13 | 41 | 0 | 85 | 70 | 0 | 0 | 25 | 151 | 0 | 0 | 0 |  | 12 | 36 | 51 | 56 | 0 | 44 | 16 | 21 | 0 | 0 | 0 | 0 | 305 | 33 | 73 | 49 | 50 | 47 | 0 | 51 | 0 | 44 | 33 | 21 | 11 | 25 | 12 | 162 | 57 | 0 | 18 | 0 | 30 | 41 | 0 | 0 | 0 | 0 | 62 | 81 | 0 | 140 | 18 | 0 | 10 | 341 | 0 | 0 | 50 | 258 | 107 | 25 | 87 | 25 | 135 | 0 | 76 | 51 | 72 | 409 | 97 | 88 | 105 | 0 | 300 | 54 | 105 | 111 | 0 | 100 | 400 | 74 | 0 | 162 | 107 | 0 | 35 | 0 | 115 | 54 | 318 | 0 | 0 |  | 918 | 0 | 215 | 0 | 16 | 0 | 0 | 0 | 28 | 62 | 8 | 65 | 34 | 32 | 0 | 0 | 0 | 32 | 0 | 86 | 0 | 42 | 32 | 8 | 32 | 22 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 137 | 0 | 351 | 75 | 0 | 113 | 105 | 113 | 0 | 0 | 113 | 790 | 222 | 0 | 0 | 0 | 0 | 113 | 0 | 0 | 304 | 0 |  | 8014 | 4159 | 12173 | 3617 | 918 | 1811 | 207 | 3594 | 1174 | 155 | 0 | 535 | 162 | 0 | 854.3 | 97.31
21:00 | 0 | 0 | 170 | 180 | 0 | 80 | 0 | 411 | 257 |  | 0 | 225 | 0 | 83 | 0 | 55 | 170 | 0 | 0 | 87 | 92 | 132 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 0 | 15 | 24 | 33 | 13 | 41 | 0 | 85 | 70 | 0 | 0 | 25 | 151 | 0 | 0 | 0 |  | 12 | 36 | 51 | 56 | 0 | 44 | 16 | 30 | 0 | 0 | 0 | 0 | 305 | 47 | 73 | 50 | 50 | 47 | 0 | 51 | 0 | 44 | 34 | 22 | 11 | 25 | 12 | 158 | 74 | 0 | 18 | 0 | 30 | 41 | 0 | 0 | 0 | 0 | 61 | 81 | 0 | 140 | 18 | 0 | 10 | 341 | 0 | 0 | 100 | 260 | 106 | 50 | 88 | 50 | 144 | 0 | 76 | 51 | 73 | 408 | 97 | 88 | 105 | 0 | 300 | 54 | 105 | 111 | 0 | 100 | 380 | 84 | 0 | 162 | 107 | 0 | 35 | 0 | 115 | 54 | 318 | 0 | 0 |  | 917 | 0 | 225 | 0 | 16 | 0 | 0 | 0 | 28 | 65 | 8 | 50 | 31 | 32 | 0 | 0 | 0 | 32 | 0 | 86 | 0 | 42 | 32 | 8 | 32 | 22 | 0 | 11 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 374 | 75 | 0 | 113 | 105 | 113 | 0 | 0 | 113 | 810 | 205 | 0 | 0 | 0 | 0 | 113 | 0 | 0 | 304 | 0 |  | 8132 | 4186 | 12318 | 3622 | 917 | 1827 | 306 | 3600 | 1195 | 155 | 0 | 538 | 158 | 0 | 584.2786 | 97.3
22:00 | 0 | 0 | 170 | 180 | 0 | 83 | 0 | 411 | 260 |  | 0 | 225 | 0 | 83 | 0 | 55 | 175 | 0 | 0 | 87 | 92 | 16 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 0 | 14 | 24 | 33 | 13 | 41 | 0 | 85 | 70 | 0 | 0 | 25 | 151 | 0 | 0 | 0 |  | 12 | 36 | 51 | 56 | 0 | 44 | 16 | 35 | 0 | 0 | 0 | 0 | 305 | 52 | 8 | 51 | 50 | 47 | 0 | 51 | 0 | 44 | 38 | 22 | 11 | 25 | 12 | 160 | 101 | 0 | 18 | 0 | 30 | 41 | 0 | 0 | 0 | 0 | 57 | 81 | 0 | 140 | 18 | 0 | 10 | 300 | 0 | 0 | 100 | 248 | 150 | 50 | 88 | 50 | 149 | 0 | 76 | 51 | 67 | 409 | 97 | 88 | 105 | 0 | 141 | 54 | 105 | 111 | 0 | 100 | 400 | 93 | 0 | 162 | 107 | 0 | 35 | 0 | 115 | 54 | 318 | 0 | 0 |  | 917 | 0 | 235 | 0 | 16 | 0 | 0 | 0 | 22 | 64 | 8 | 65 | 32 | 32 | 0 | 0 | 0 | 32 | 0 | 86 | 0 | 42 | 32 | 8 | 32 | 22 | 0 | 11 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 400 | 75 | 0 | 113 | 105 | 113 | 0 | 0 | 113 | 770 | 222 | 0 | 0 | 0 | 0 | 113 | 0 | 0 | 304 | 0 |  | 7862 | 4214 | 12076 | 3707 | 917 | 1776 | 350 | 3441 | 1155 | 155 | 0 | 415 | 160 | 0 | 568.6118 | 97.29
23:00 | 0 | 0 | 170 | 180 | 0 | 84 | 0 | 412 | 260 |  | 0 | 225 | 0 | 84 | 0 | 55 | 176 | 0 | 0 | 87 | 92 | 16 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 0 | 21 | 18 | 33 | 14 | 41 | 0 | 85 | 70 | 0 | 0 | 25 | 150 | 0 | 0 | 0 |  | 12 | 12 | 51 | 56 | 0 | 44 | 16 | 37 | 0 | 0 | 0 | 0 | 240 | 56 | 8 | 0 | 50 | 45 | 0 | 51 | 0 | 44 | 43 | 22 | 11 | 25 | 12 | 164 | 108 | 0 | 18 | 0 | 30 | 41 | 0 | 0 | 0 | 0 | 57 | 81 | 0 | 140 | 18 | 0 | 10 | 305 | 0 | 0 | 100 | 245 | 154 | 50 | 88 | 50 | 149 | 0 | 76 | 51 | 73 | 410 | 87 | 88 | 105 | 0 | 141 | 54 | 105 | 111 | 4 | 100 | 390 | 92 | 0 | 108 | 107 | 0 | 35 | 0 | 115 | 54 | 318 | 0 | 0 |  | 917 | 0 | 240 | 0 | 16 | 0 | 0 | 0 | 0 | 64 | 0 | 65 | 31 | 32 | 0 | 0 | 0 | 32 | 0 | 63 | 0 | 42 | 0 | 0 | 32 | 22 | 0 | 11 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 0 | 416 | 75 | 0 | 113 | 67 | 113 | 0 | 0 | 113 | 760 | 222 | 0 | 0 | 0 | 0 | 113 | 0 | 0 | 236 | 0 |  | 7689 | 4028 | 11717 | 3604 | 917 | 1797 | 354 | 3335 | 1077 | 155 | 0 | 314 | 164 | 0 | 740.9463 | 97.28
24:00 | 0 | 0 | 170 | 180 | 0 | 84 | 0 | 411 | 260 |  | 0 | 225 | 0 | 57 | 0 | 50 | 163 | 0 | 0 | 60 | 58 | 16 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 19 | 21 | 19 | 33 | 14 | 41 | 0 | 84 | 70 | 0 | 0 | 25 | 151 | 0 | 0 | 0 |  | 12 | 30 | 51 | 33 | 0 | 32 | 0 | 37 | 0 | 0 | 0 | 0 | 240 | 95 | 8 | 20 | 50 | 10 | 0 | 0 | 0 | 0 | 38 | 22 | 11 | 25 | 15 | 166 | 104 | 0 | 18 | 0 | 30 | 41 | 0 | 0 | 0 | 0 | 57 | 81 | 0 | 140 | 18 | 0 | 10 | 290 | 0 | 0 | 0 | 148 | 0 | 0 | 53 | 0 | 149 | 0 | 76 | 23 | 80 | 409 | 48 | 88 | 68 | 0 | 141 | 54 | 64 | 111 | 0 | 31 | 400 | 92 | 0 | 35 | 107 | 0 | 35 | 0 | 68 | 54 | 318 | 0 | 0 |  | 918 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 0 | 65 | 31 | 16 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 34 | 0 | 0 | 32 | 22 | 0 | 11 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 157 | 0 | 404 | 74 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 730 | 221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 303 | 0 |  | 6652 | 3784 | 10436 | 3667 | 918 | 1683 | 0 | 2499 | 1116 | 154 | 0 | 233 | 166 | 0 | 1626 | 97.27
KWH | 0 | 0 | 2727000 | 4315500 | 0 | 1868227 | 0 | 9910270 | 6410000 |  | 0 | 5127000 | 0 | 1619520 | 0 | 1332382 | 4083965 | 0 | 0 | 1318080 | 1719792 | 833280 | 0 | 0 | 0 | 0 | 662760 | 887434 | 895924 | 358092 | 505000 | 577080 | 737600 | 326800 | 990240 | 0 | 2031436 | 1708000 | 0 | 0 | 379202 | 3606934 | 0 | 0 | 0 |  | 294240 | 741984 | 635517 | 913560 | 0 | 797760 | 366240 | 509760 | 0 | 0 | 0 | 0 | 6847000 | 3109000 | 401454 | 1141730 | 932616 | 762240 | 0 | 1136830 | 0 | 1048528 | 680064 | 484848 | 240840 | 465000 | 338150 | 3552000 | 1444800 | 0 | 415908 | 15150 | 715000 | 960240 | 0 | 0 | 0 | 0 | 1435488 | 580800 | 0 | 3348610 | 432000 | 0 | 239760 | 7545500 | 0 | 6048 | 383040 | 3796255 | 600515 | 263847 | 1447200 | 264433 | 2878992 | 117450 | 863040 | 660480 | 1647636 | 9468000 | 2049600 | 2112000 | 1778109 | 27598 | 3658255 | 1347289 | 1780610 | 1430700 | 54600 | 1013760 | 9123200 | 1723200 | 366420 | 1869120 | 2578091 | 0 | 885960 | 230364 | 1685760 | 1266480 | 7759300 | 0 | 0 |  | 22225454 | 0 | 5169600 | 0 | 192000 | 0 | 0 | 0 | 135360 | 402304 | 45000 | 1450648 | 566136 | 203808 | 0 | 0 | 0 | 198484 | 27513 | 538784 | 0 | 656799 | 122595 | 47731 | 181273 | 479760 | 0 | 235854 | 1926982 | 0 | 0 | 0 | 0 | 3281900 | 0 | 0 | 0 | 0 | 29760 | 3729036 | 0 | 7401818 | 1202400 | 10538 | 2004672 | 1436688 | 1817683 | 0 | 42455 | 1894656 | 21169800 | 5000618 | 0 | 0 | 40140 | 593280 | 1337088 | 0 | 0 | 1990600 | 245520 |  | 162601487 | 88034737 | 250636224 | 90049297 | 22225454 | 38029903 | 1552133 | 59856620 | 25087382 | 3739436 | 0 | 4865622 | 3552000 | 1678377 | 0
Fuel Cost | 0 | 0 | 3981420 | 6430095 | 0 | 2484741.91 | 0 | 10405783.5 | 6922800 |  | 0 | 5588430 | 0 | 18106233.6 | 0 | 17654061.5 | 4574040.8 | 0 | 0 | 19270329.6 | 24197473.44 | 13507468.8 | 0 | 0 | 0 | 0 | 8430307.2 | 11980359 | 12014340.84 | 268569 | 378750 | 0 | 0 | 0 | 16843982.4 | 0 | 548487.72 | 461160 | 0 | 0 | 6199952.7 | 3751211.36 | 0 | 0 | 0 |  | 3839832 | 12376293.12 | 10816499.34 | 12342195.6 | 0 | 9230083.2 | 465124.8 | 1697500.8 | 0 | 0 | 0 | 0 | 7463230 | 3606440 | 517875.66 | 1392910.6 | 1053856.08 | 1135737.6 | 0 | 1898506.1 | 0 | 18108078.56 | 9146860.8 | 664241.76 | 180630 | 813750 | 253612.5 | 25503360 | 1574832 | 0 | 565634.88 | 241491 | 979550 | 1267516.8 | 0 | 0 | 0 | 0 | 2784846.72 | 1324224 | 0 | 3382096.1 | 928800 | 0 | 474724.8 | 7545500 | 0 | 4596.48 | 8028518.4 | 51818880.75 | 12586794.4 | 5453717.49 | 19508256 | 5465830.11 | 39874039.2 | 1372990.5 | 8906572.8 | 9022156.8 | 21864129.72 | 8710560 | 24923136 | 30539520 | 22493078.85 | 0 | 42947913.7 | 14671977.21 | 18927884.3 | 19414599 | 703794 | 11942092.8 | 8393344 | 22315440 | 5294769 | 23719132.8 | 29338675.58 | 0 | 11570637.6 | 2752849.8 | 25235827.2 | 16679541.6 | 0 | 0 | 0 |  | 66676362 | 0 | 5789952 | 0 | 1998720 | 0 | 0 | 0 | 2437833.6 | 7241472 | 646650 | 1624725.76 | 1098303.84 | 2221507.2 | 0 | 0 | 0 | 3328576.68 | 481202.37 | 8426581.76 | 0 | 10876591.44 | 2073081.45 | 650573.53 | 3058075.51 | 993103.2 | 0 | 178541.478 | 11195765.42 | 0 | 0 | 0 | 0 | 3807004 | 0 | 0 | 0 | 0 | 624364.8 | 4325681.76 | 0 | 7327799.82 | 16160256 | 220981.86 | 23715269.76 | 20760141.6 | 23084574.1 | 0 | 469127.75 | 23001123.84 | 190739898 | 5100630.36 | 0 | 0 | 453983.4 | 6959174.4 | 20497559.04 | 0 | 0 | 0 | 0 |  | 862057089.28 | 478245189.728 | 1340302279.008 | 90001347.378 | 66676362 | 44109878.09 | 32380207.06 | 779286264.3 | 201935663.42 | 1009647.72 | 0 | 81855163.19 | 25503360 | 17544385.85 | 0
Yesterday Day Peak | 0 | 0 | 100 | 180 | 0 | 79 | 0 | 417 | 294 |  | 0 | 225 | 0 | 67 | 0 | 55 | 161 | 0 | 0 | 41 | 75 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 18 | 24 | 0 | 7 | 41 | 0 | 86 | 70 | 0 | 0 | 0 | 150 | 0 | 0 | 0 |  | 12 | 30 | 16 | 33 | 0 | 25 | 16 | 2 | 0 | 0 | 0 | 0 | 200 | 148 | 8 | 50 | 10 | 5 | 0 | 51 | 0 | 44 | 8 | 19 | 9 | 8 | 15 | 162 | 31 | 0 | 16 | 2 | 30 | 41 | 0 | 0 | 0 | 0 | 58 | 0 | 0 | 140 | 18 | 0 | 10 | 280 | 0 | 0 | 0 | 163 | 0 | 0 | 57 | 0 | 126 | 18 | 25 | 17 | 71 | 409 | 78 | 88 | 51 | 4 | 141 | 54 | 71 | 17 | 0 | 25 | 396 | 74 | 54 | 35 | 107 | 0 | 35 | 34 | 52 | 54 | 432 | 0 | 0 |  | 919 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 18 | 0 | 11 | 78 | 0 | 0 | 0 | 0 | 171 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 280 | 28 | 0 | 69 | 15 | 52 | 0 | 0 | 90 | 810 | 212 | 0 | 0 | 5 | 84 | 36 | 0 | 0 | 0 | 35 |  | 9750 | DayPeak
Yesterday Evening Peak | 0 | 0 | 170 | 180 | 0 | 80 | 0 | 411 | 257 | 0 | 0 | 225 | 0 | 83 | 0 | 55 | 170 | 0 | 0 | 87 | 92 | 132 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 0 | 15 | 24 | 33 | 13 | 41 | 0 | 85 | 70 | 0 | 0 | 25 | 151 | 0 | 0 | 0 | 0 | 12 | 36 | 51 | 56 | 0 | 44 | 16 | 30 | 0 | 0 | 0 | 0 | 305 | 47 | 73 | 50 | 50 | 47 | 0 | 51 | 0 | 44 | 34 | 22 | 11 | 25 | 12 | 158 | 74 | 0 | 18 | 0 | 30 | 41 | 0 | 0 | 0 | 0 | 61 | 81 | 0 | 140 | 18 | 0 | 10 | 341 | 0 | 0 | 100 | 260 | 106 | 50 | 88 | 50 | 144 | 0 | 76 | 51 | 73 | 408 | 97 | 88 | 105 | 0 | 300 | 54 | 105 | 111 | 0 | 100 | 380 | 84 | 0 | 162 | 107 | 0 | 35 | 0 | 115 | 54 | 318 | 0 | 0 |  | 917 | 0 | 225 | 0 | 16 | 0 | 0 | 0 | 28 | 65 | 8 | 50 | 31 | 32 | 0 | 0 | 0 | 32 | 0 | 86 | 0 | 42 | 32 | 8 | 32 | 22 | 0 | 11 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 374 | 75 | 0 | 113 | 105 | 113 | 0 | 0 | 113 | 810 | 205 | 0 | 0 | 0 | 0 | 113 | 0 | 0 | 304 | 0 |  | 12318 | EvPeak
Forecast for Evening | 0 | 0 | 100 | 180 | 0 | 80 | 0 | 412 | 250 | 0 | 0 | 225 | 0 | 83 | 0 | 55 | 170 | 0 | 0 | 87 | 92 | 132 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 19 | 20 | 25 | 33 | 13 | 41 | 0 | 85 | 70 | 0 | 0 | 25 | 150 | 0 | 0 | 0 | 0 | 12 | 36 | 51 | 56 | 0 | 44 | 16 | 20 | 0 | 0 | 0 | 0 | 305 | 135 | 8 | 50 | 50 | 47 | 0 | 51 | 0 | 44 | 34 | 22 | 11 | 25 | 15 | 166 | 80 | 0 | 18 | 0 | 30 | 41 | 0 | 0 | 0 | 0 | 61 | 81 | 0 | 140 | 18 | 0 | 10 | 341 | 0 | 0 | 100 | 260 | 150 | 50 | 88 | 50 | 118 | 0 | 76 | 51 | 73 | 400 | 97 | 88 | 105 | 0 | 300 | 54 | 105 | 111 | 0 | 100 | 380 | 84 | 0 | 162 | 107 | 0 | 35 |  | 115 | 54 | 318 |  |  |  | 937 | 0 | 225 | 0 | 16 | 0 | 0 | 0 | 30 | 65 | 8 | 66 | 31 | 32 | 0 | 0 | 0 | 32 | 0 | 86 | 0 | 42 | 32 | 8 | 32 | 22 | 0 | 11 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 143 | 0 | 374 | 75 | 100 | 113 | 105 | 113 | 0 | 0 | 113 | 1000 | 205 |  | 0 |  |  | 113
Forecast for Day | 0 | 0 | 100 | 180 | 0 | 80 | 0 | 400 | 250 | 0 | 0 | 225 | 0 | 67 | 0 | 55 | 160 | 0 | 0 | 63 | 74 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 15 | 25 | 33 | 12 | 41 | 0 | 85 | 70 | 0 | 0 | 25 | 150 | 0 | 0 | 0 | 0 | 12 | 30 | 17 | 33 | 0 | 32 | 16 | 10 | 0 | 0 | 0 | 0 | 260 | 120 | 8 | 50 | 48 | 5 | 0 | 51 | 0 | 44 | 8 | 22 | 11 | 25 | 12 | 143 | 70 | 0 | 18 | 1.6 | 30 | 41 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 140 | 18 | 0 | 10 | 300 | 0 | 0 | 0 | 160 | 0 | 0 | 48 | 0 | 80 | 20 | 25 | 17 | 70 | 400 | 90 | 88 | 51 | 5 | 140 | 54 | 61 | 17 | 0 | 25 | 380 | 74 | 50 | 35 | 107 | 0 | 35 | 30 | 53 | 54 | 300 |  |  |  | 937 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 20 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 320 | 50 | 0 | 113 | 67 | 90 | 0 | 8 | 113 | 1000 | 200 |  | 0 | 6 | 100 | 70 |  |  |  | 12
Generation at 08:00(Today) | 0 | 0 | 170 | 180 | 0 | 79 | 0 | 400 | 282 | 0 | 0 | 225 | 0 | 59 | 0 | 55 | 192 | 0 | 0 | 62 | 58 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 21 | 27 | 33 | 15 | 42 | 0 | 86 | 35 | 0 | 0 | 25 | 25 | 0 | 0 | 0 | 0 | 12 | 29 | 16 | 33 | 0 | 32 | 0 | 13 | 0 | 0 | 0 | 0 | 280 | 112 | 8 | 51 | 46 | 5 | 0 | 0 | 0 | 45 | 34 | 22 | 11 | 16 | 12 | 134 | 71 | 0 | 19 | 1 | 30 | 41 | 0 | 0 | 0 | 0 | 61 | 0 | 0 | 140 | 18 | 0 | 10 | 280 | 0 | 0 | 0 | 95 | 0 | 0 | 49 | 0 | 71 | 1 | 25 | 17 | 55 | 340 | 47 | 88 | 56 | 0 | 106 | 54 | 51 | 17 | 0 | 25 | 350 | 73 | 17 | 35 | 107 | 0 | 35 | 4 | 54 | 54 | 318 | 0 | 0 | 0 | 917 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 22 | 0 | 8 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 0 | 352 | 74 | 0 | 113 | 0 | 75 | 0 | 1 | 100 | 570 | 170 | 0 | 0 | 1 | 7 | 0 | 0 | 0 | 329 | 18 | 0 |  |  |  |  | 66274375 |  | 0
66274375
| Minimum Generation |  | 9281 | 9:00
| Highest Generation |  | 12318 | 21:00
| Day Peak Generation |  | 9750 | 12:00
| Evening Peak Generation |  | 12318 | 21:00
| HVDC Max Flow |  | 921 | 3:00
| HVDC EvPeak Flow |  | 917 | 21:00
| Load factor L.F |  | 84.78% | [161 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2022-10-23
Till now the maximum generation is : - |  |  | 14782 | 21:00 | Hrs on | 2022-04-16
The Summary of Yesterday's |  | 2022-10-22 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 9750 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 9259 | MW
Evening Peak Generation : |  | 12318 | MW Hour : | 21:00 | Available Max Generation : |  | 12380 | MW
E.P. Demand (at gen end) : |  | 12952 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 13500 | MW
Maximum Generation : |  | 12318 | MW Hour : | 21:00 | Reserve(Generation end) |  | - | MW
Total Gen. (MKWH) : |  | 250.6362 | System Load Factor : | 84.78% | Load Shed : |  | 1032 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | 496 | MW at | 18:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2022-10-23
Actual : | 97.21 | Ft.(MSL) , | Rule curve : | 108 | Ft.( MSL )
Gas Consumed : | Total = | 973.92 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 134111225.468
: |  | Coal : | 201935663.42 | Oil : | 893521634.55 | Total : | 1229568523.438
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 160 | 3840:00 | 4258.5905 |  |  | 400 | 9.393%
Chittagong Area | 0 | 0:00 | 1206.3846 |  |  | 165 | 13.68%
Khulna Area | 0 | 0:00 | 1592.3275 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1412.7911 |  |  | 0 | 0%
Cumilla Area | 121 | 2904:00 | 1202.6695 |  |  | 160 | 13.3%
Mymensingh Area | 200 | 4800:00 | 993.5847 |  |  | 180 | 18.12%
Sylhet Area | 103 | 2472:00 | 444.0892 |  |  | 50 | 11.26%
Barisal Area | 0 | 0:00 | 362.0104 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 784.4999 |  |  | 77 | 9.815%
Total | 584 |  | 12256.9475 |  |  | 1032
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 2
2) Ghorasal-3, 7
3) Ashuganj-5
4) Baghabari-71,100 MW
5) Raozan unit-1 & 2
6) Siddhirganj 210 MW .
7) Shajibazar 330 MW
8) Sirajganj-2
9) Ashuganj(N)-360 MW.
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Bhola-225 MW GT & ST tripped at 07:44 due to gas shortage and GT was synchronized at 11:05.
b) Chandraghona-Madunaghat 132 kV Ckt-1 was under shut down from 07:45 to 15:59 for A/M.
c) Sonargaon 132/33 kV T-2 transformer was under shut down from 08:21 to 10:00 for C/M.
d) Ashuganj-Kishorganj 132 kV Ckt-2 was under shut down from 08:39 to 16:40 for A/M.
e) Sherpur 132/33 kV T-3 transformer was under shut down from 08:20 to 16:34 for C/M.
f) Hathazari-Raozan 230 kV Ckt-1 was under shut down from 09:20 to 16:45 for A/M.
g) Cumilla(N)-Daudkandi 132 kV Ckt-2 was under shut down from 08:28 to 17:06 for A/M.
h) Thakurgaon 132/33 kV T-2 transformer was under shut down from 08:17 to 14:14 for A/M.
i) Mymensing-Netrokona 132 kV Ckt-2 was under shut down from 09:12 to 17:36 for A/M.
j) Cumilla(N) 132/33 kV T-5 transformer was under shut down from 09:11 to 10:23 for C/M.
k) Bagerhat 132/33 kV T-2 transformer was under shut down from 09:10 to 16:32 for A/M.
l) Kurigram 132/33 kV T-1 transformer was under shut down from 08:44 to 11:31 for A/M.
m) Kallyanpur 132 kV bus-2 was under shut down from 11:35 to 16:38 for A/M.
n) Kurigram 132/33 kV T-2 transformer was under shut down from 11:34 to 13:40 for A/M.
o) Thakurgaon 132/33 kV T-1 transformer was under shut down from 14:35 to 22:18 for C/M.
p) Rangpur S/S-Rangpur confidence 132 kV Ckt-2 tripped at 12:31 showing dist.Z1 and was switched on at 12:46.
q) Dhamrai 132/33 kV T-1 transformer bus-section was shut down at 15:18 for C/M and was switched on at 17:28. | [5 empty] | About 20 MW power interruption occurred under
Dhamrai S/S area from 15:18 to 17:28.
r) Cumilla(N) 132/33 kV T-3 & T-4 transformers were under shut down from 16:25 to 16:45 for A/M.
s) Niamatpur 132/33 kV T-1 transformer was under shut down from 15:51 to 17:00 for C/M. | [5 empty] | About 20 MW power interruption occurred under
Niamatpur S/S area from 15:51 to 17:00.
t) Ashuganj-225 MW tripped at 16:33 due to gas pressure fall and GT was synchronized at 19:03.
u) Rampal unit-1 was synchronized at 16:05.
v) Sirajganj #1 was shut down at 19:03 for gas shortage.
w) Gopalganj 132/33 kV T-2 transformer is under shut down since 07:30(23/10/22) for A/M.
x) Chandraghona-Madunaghat 132 kV Ckt-1 is under shut down since 07:37(23/10/22) for A/M.
y) Kaptai #5 was shut down at 06:00(23/10/22) for maintenance.
z) Chandpur-150 MW CCPP GT tripped at 22:56 due to axial diffial high and was synchronized at 23:58.
aa) Midland-51 MW was shut down at 23:02 due to gas shortage.
ab) Barabkunda-22 MW was shut down at 23:02 due to gas shortage.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2022-10-22 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 170 | 2727000
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4315500
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 80 | 1868227 | Engine problem
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 411 | 9910270
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 257 | 6410000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 5127000 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 83 | 1619520 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 0 | 0 | Under maint.
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 55 | 1332382
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 358092 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 87 | 1318080 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 170 | 4083965 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 92 | 1719792 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 662760
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 132 | 833280 | Engine problem
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 35 | 887434 | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 895924 | Fuel shortage
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 39 | 1082080 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 737600
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 13 | 326800 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 41 | 990240 | Engine problem
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 260 | 3796255 | Fuel shortage
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 106 | 600515 | Fuel conservation
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 50 | 263847 | Fuel conservation
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 50 | 264433 | Fuel conservation
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 144 | 2878992
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 88 | 2112000 | Engine problem
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 84 | 1723200 | Engine problem
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 1869120
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 230364
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 54 | 1266480
| Dhaka area Total |  |  |  | 5847 | 3190 | 62211152
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Machine problem
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 25 | 379202
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 117450
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 44 | 797760 | Engine problem
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 155 | 3739436 | Low water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 151 | 3606934 | ST Under maint
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 105 | 1778109
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 36 | 741984 | Fuel shortage
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 635517 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 56 | 913560 | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 76 | 863040 | Engine problem
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 16 | 366240 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 30 | 509760
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 27598
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 300 | 3658255
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1347289
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 105 | 1780610
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 1013760 | Engine problem
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 107 | 2578091 | Engine problem
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Chattogram area Total |  |  |  | 2382 | 1411 | 24854595
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 47 | 3109000 | Gas shortage
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 0 | 0 | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 305 | 6847000 | Gas shortage
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+136*1 | 284 | 318 | 7759300 | On test.
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 50 | 932616
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 47 | 762240 | Gas shortage
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 73 | 401454 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1136830
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 73 | 1647636 | Fuel shortage
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 44 | 1048528 | Fuel shortage
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1141730 | Machine problem
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 51 | 660480 | Fuel shortage
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 484848
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 240840
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 158 | 3552000
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 25 | 465000 | Engine problem
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 34 | 680064 | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 12 | 338150 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 100 | 383040 | Fuel conservation
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 111 | 1430700
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 54600 | Fuel shortage
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 35 | 885960 | Engine problem
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 115 | 1685760
| Cumilla Area Total |  |  |  | 3169 | 1732 | 35647776
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 74 | 1444800 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 415908 | Gas shortage
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 15150
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 88 | 1447200 | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 97 | 2049600 | Engine problem
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 366420
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 294240 | Engine problem
| Mymensingh Area Total |  |  |  | 614 | 289 | 6033318
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 30 | 715000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 41 | 960240 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Gas shortage
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 0 | 0 | Gas shortage
| Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 0 | 0 | Gas shortage
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 0 | 6048 | Engine problem
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 61 | 1435488
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 580800
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 140 | 3348610 | ST Under maint
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 432000
| Sylhet 50MW PP (EPL) |  | NENP | 27*2 | 50 | 0 | 0 | Gas shortage
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 0 | 0 | Gas shortage
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 341 | 7545500 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 408 | 9468000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 239760
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 380 | 9123200
| Sylhet Area Total |  |  |  | 2477 | 1510 | 33854646
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Fuel shortage
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 917 | 22225454
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 16 | 192000 | Fuel shortage
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 28 | 135360 | Engine problem
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 65 | 402304 | Engine problem
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 225 | 5169600 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 8 | 45000 | Fuel shortage
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 29760 | Fuel conservation
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 75 | 1202400 | Engine problem
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 105 | 1436688
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 593280
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 0 | 0 | 0 | On test.
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 0 | 0 | 304 | 1990600 | On test.
| Khulna Area Total |  |  |  | 2384 | 1743 | 33422446
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 32 | 203808 | Line O/L
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 31 | 566136 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 50 | 1450648 | Gas shortage
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 810 | 21169800 | Line O/L
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 205 | 5000618
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Line O/L
| Barisal Area Total |  |  |  | 1958 | 1128 | 28391010
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 32 | 198484 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 27513 | Under maint.
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contract Expired
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 42 | 656799 | Engine problem
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 122595 | Fuel shortage
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 3281900 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 143 | 3729036 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 374 | 7401818 | Gas shortage
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 181273 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 479760
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 235854
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 8 | 47731 | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 86 | 538784 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 10538 | Line O/L
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 2004672
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 1894656
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 40140
| Rajshahi Area Total |  |  |  | 2129 | 1008 | 20851553
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 81 | 1926982
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under maint.
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 1817683
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 42455
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 113 | 1337088
| Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 245520
| Rangpur Area Total |  |  |  | 750 | 307 | 5369728
| Total |  |  |  | 21710 | 12318 | 250636224
| Eastern Grid Total |  |  |  | 14489 | 8132 | 162601487
| Western Grid Total |  |  |  | 7221 | 4186 | 88034737
| National Grid Total |  |  |  | 21710 | 12318 | 250636224
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2022-10-22
| (a) ENTIRE EASTERN GRID : |  | 8071.9 | MW | (b) ENTIRE WESTERN GRID : |  | 3717.06 | MW
| i) Dhaka area |  | 4505.6 | MW | i) Khulna area |  | 1480.6 | MW
| ii) Chittagong area |  | 1214.3 | MW | ii) Rajshahi area |  | 1212.6 | MW
| iii) Comilla area |  | 1128 | MW | iii) Barisal area |  | 378.86 | MW
| iv) Mymensingh area |  | 805 | MW | iv) Rangpur area |  | 645 | MW
| v) Sylhet area |  | 419 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 11788.96 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 21 | 10:00 | Chowmuhani | 167 | 22:00 | Kaptai | 5 | 18:00 | Nawabganj | 45.6 | 20:00 | Sholosohor | 35 | 19:00
2 | AKSML | 91 | 17:00 | Chuadanga | 92 | 18:00 | Kazla | 88 | 00:00 | Netrakona | 83 | 02:00 | Shyampur | 176 | 00:00
3 | Aftabnagar | 32.8 | 19:30 | Coxsbazar | 106 | 19:00 | Keranigonj | 64 | 19:00 | New | 72.8 | 09:00 | Siddhirganj | 108 | 21:00
4 | Agargaon | 75 | 19:30 | Cumilla(N) | 119 | 21:00 | Khagrachori | 30 | 21:00 | Niamatpur | 70 | 18:30 | Sirajganj | 94 | 20:00
5 | Agrabad | 68 | 19:30 | Cumilla(S) | 172 | 18:00 | Khulna | 87 | 18:00 | Noapara | 44 | 18:30 | Sonargaon | 95 | 05:00
6 | Amnura | 45 | 18:30 | Daudkandi | 116 | 20:00 | Khulshi | 185 | 20:00 | PHP | 4 | 13:00 | Sreemongol | 46 | 22:00
7 | Ashuganj | 68 | 21:00 | Dhaka | 32 | 11:00 | Kishoreganj | 122 | 00:00 | Pabna | 96 | 20:00 | Srinagar | 42.24 | 21:00
8 | BSRM | 95 | 05:00 | Dhamrai | 104 | 21:00 | Kodda | 229 | 19:30 | Palashbari | 108 | 18:30 | Sunamganj | 33 | 20:00
9 | Bagerhat | 99 | 18:30 | Dhanmondi | 109 | 13:00 | Kulaura | 34 | 20:00 | Panchagarh | 47 | 20:00 | Sylhet | 133 | 18:30
10 | Bakulia | 138 | 19:30 | Dohazari | 102 | 21:00 | Kurigram | 53 | 18:00 | Patuakhali | 120 | 20:00 | TK | 20.8 | 19:00
11 | Banani | 34 | 13:00 | Faridpur | 140 | 18:30 | Kushtia | 126 | 18:30 | Payra | 1.07 | 18:00 | Tangail | 158 | 22:00
12 | Bangabhaban | 6 | 12:00 | Fatullah | 70 | 10:00 | Lalbag | 85 | 20:00 | Postogola | 43 | 19:30 | Thakurgaon | 62 | 18:00
13 | Barapukuria | 51 | 18:00 | Fenchuganj | 32 | 05:00 | Lalmonirhat | 36 | 18:00 | Purbachal | 17 | 20:00 | Tongi | 106 | 21:00
14 | Barguna | 18 | 19:30 | Feni | 92 | 21:00 | Madanganj | 90 | 07:00 | Purbasadipur | 95 | 19:30 | Ullon | 43 | 19:30
15 | Barishal | 101 | 18:00 | GPH | 91 | 20:00 | Madaripur | 96 | 21:00 | Rahanpur_I | 16 | 19:00 | Uttara | 83 | 18:30
16 | Barishal-230 | 76 | 19:00 | Ghorashal | 55 | 20:00 | Madartek | 84 | 19:30 | Rahim | 38 | 16:00 | UttaraNew | 23 | 18:30
17 | Baroaulia | 68 | 18:00 | Goalpara | 24 | 18:30 | Madunaghat | 65 | 21:00 | Rajbari | 60 | 18:00 | Zigatola | 57 | 19:00
18 | Baroirhat | 57 | 21:00 | Gollamari | 46 | 13:00 | Magura | 56 | 18:00 | Rajendrapur | 122 | 21:00
19 | Bashundhara | 150 | 20:00 | Gopalganj | 97 | 18:30 | Mahasthangarh | 56 | 18:00 | Rajshahi | 126 | 19:00
20 | BashundharaCement | 12 | 15:00 | Gulshan | 90 | 11:00 | Manikganj | 92 | 21:00 | Rajshahi-230 | 27 | 20:00
21 | Beanibazar | 47 | 21:00 | Halishahar | 89.5 | 08:00 | Maniknagar | 63 | 19:30 | Ramganj | 100 | 19:30
22 | Benapole | 52 | 18:00 | HaripurSBU | 145 | 22:00 | Matarbari | 42 | 22:00 | Rampur | 40 | 21:00
23 | Bhaluka | 102 | 13:00 | Hasnabad | 88 | 21:00 | Matuail | 66 | 09:00 | Rangamati | 12 | 20:00
24 | Bhandaria | 46 | 19:00 | Hathazari | 63 | 14:00 | Millgate | 66 | 10:00 | Rangpur | 115 | 18:30
25 | Bhangura | 31 | 19:00 | Ishurdi | 69 | 18:30 | Mirpur | 119 | 20:00 | Ruppur | 3.2 | 12:00
26 | Bheramara(GK) | 55 | 18:30 | Jaldhaka | 48 | 18:30 | Mirsorai | 3 | 15:00 | SSM | 2 | 01:00
27 | Bhulta | 243 | 21:00 | Jamalpur | 113 | 07:00 | Mithapukur | 28 | 18:00 | Saidpur | 95 | 18:00
28 | Bog-Sherpur | 52 | 12:00 | Jashore | 129 | 19:00 | Modern | 0 | 00:00 | Satkhira | 112 | 18:30
29 | Bogura | 145 | 20:00 | Jhenaidah | 114 | 18:00 | Mogbazar | 112 | 19:30 | Satmasjid | 95 | 19:30
30 | Borhanuddin | 44 | 20:00 | Joydebpur | 143 | 18:30 | Mongla | 30 | 12:00 | Savar | 138 | 21:00
31 | Brahmanbaria | 148 | 22:00 | Joypurhat | 53 | 20:00 | Motijheel | 33 | 19:00 | Shahjadpur | 91 | 20:00
32 | Cantonment | 144 | 20:00 | Juldah | 27 | 23:00 | Munshiganj | 103 | 23:00 | Shahjibazar | 95 | 21:00
33 | Chandpur | 58 | 21:00 | KSRM | 40 | 16:00 | Mymensingh | 197 | 22:00 | Shahmirpur | 39 | 16:00
34 | Chandraghona | 36 | 18:30 | Kabirpur | 304 | 18:00 | Naogaon | 106 | 20:00 | Shariatpur | 70 | 19:30
35 | Chapai | 63 | 18:30 | Kachua | 60 | 21:00 | Narail | 45 | 18:30 | Sherpur | 96 | 21:00
36 | Charsaidpur | 48.15 | 00:00 | Kallyanpur | 93 | 19:30 | Narinda | 63 | 19:30 | Shikalbaha | 27 | 18:00
37 | Chauddagram | 50 | 20:00 | Kalurghat | 7 | 10:00 | Narshingdi | 140 | 18:00 | Shikalbaha-230 | N/A | N/A
38 | Chhatak | 19 | 18:00 | Kamrangirchar | 67 | 00:00 | Natore | 118 | 18:30 | Shitalakhya | 98 | 20:00
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2022-10-22 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Bhulta | 383 | 14:00 | 359 | 10:00 | Kaliakoir | 386 | 17:00 | 378 | 00:00
| Bibiana | 398 | 18:00 | 390 | 02:00 | Payra | 422 | 08:00 | 412 | 21:00
| BIPTC | 405 | 06:00 | 397 | 18:30 | Rahanpur_I | 408 | 05:00 | 388 | 15:00
| Gopalganj_I | 422 | 09:00 | 406 | 21:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 223 | 18:00 | 212 | 10:00 | Hasnabad | 224 | 18:00 | 216 | 10:00
| AKSML | 237 | 18:00 | 225 | 10:00 | Hathazari | 237 | 18:00 | 227 | 14:00
| Aminbazar | 224 | 18:00 | 217 | 12:00 | Ishurdi | 234 | 06:00 | 228 | 10:00
| Ashuganj | 237 | 18:00 | 230 | 10:00 | Jhenaidah | 231 | 06:00 | 222 | 14:00
| Baghabari | 231 | 02:00 | 227 | 11:00 | Kaliakoir | 223 | 17:00 | 217 | 10:00
| Barapukuria | 227 | 04:00 | 211 | 11:00 | Keranigonj | 223 | 18:00 | 212 | 10:00
| Barishal | 246 | 08:00 | 238 | 22:00 | Khulna(S) | 237 | 06:00 | 226 | 14:00
| Bheramara | 231 | 06:00 | 225 | 10:00 | Maniknagar | 225 | 18:00 | 217 | 10:00
| Bhulta | 226 | 04:00 | 219 | 10:00 | Meghnaghat | 228 | 04:00 | 222 | 12:00
| Bibiana | 234 | 18:00 | 228 | 15:00 | Mirsorai | 235 | 18:00 | 224 | 10:00
| BIPTC | 234 | 05:00 | 226 | 11:00 | Rajshahi | 233 | 06:00 | 226 | 11:00
| Bogura | 227 | 01:00 | 219 | 18:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 248 | 06:00 | 242 | 22:00 | Rampura | 224 | 18:00 | 216 | 10:00
| BSRM | 235 | 18:00 | 226 | 10:00 | Shikalbaha | 238 | 19:00 | 228 | 12:00
| Cumilla(N) | 229 | 18:00 | 221 | 10:00 | Shyampur | 224 | 18:00 | 214 | 10:00
| Fenchuganj | 235 | 17:00 | 230 | 15:00 | Siddhirganj | 227 | 14:00 | 221 | 17:00
| Ghorashal | N/A | N/A | N/A | N/A | Sirajgonj | 230 | 00:00 | 225 | 20:00
| GPH | 236 | 21:00 | 225 | 10:00 | Tongi | 227 | 18:30 | 219 | 05:00
| Haripur | 224 | 13:00 | 216 | 10:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 133 | 02:00 | 126 | 10:00 | Lalbag | 139 | 18:00 | 132 | 10:00
| Agargaon | 131 | 18:00 | 124 | 10:00 | Lalmonirhat | 134 | 16:00 | 123 | 07:00
| Agrabad | 137 | 00:00 | 130 | 10:00 | Madanganj | 134 | 18:00 | 128 | 10:00
| AKS | 136 | 00:00 | 130 | 11:00 | Madaripur | 138 | 07:00 | 131 | 23:00
| Aminbazar | 139 | 18:00 | 131 | 15:00 | Madartek | 133 | 04:00 | 126 | 10:00
| Amnura | 132 | 00:00 | 125 | 11:00 | Madunaghat | 138 | 00:00 | 132 | 06:00
| Ashuganj | 138 | 06:00 | 134 | 17:00 | Magura | 137 | 05:00 | 129 | 18:00
| Bagerhat | 133 | 06:00 | 126 | 21:00 | Mahasthangarh | 136 | 00:00 | 130 | 11:00
| Bakulia | 138 | 18:00 | 130 | 10:00 | Manikganj | 138 | 09:00 | 130 | 00:00
| Banani | 136 | 03:00 | 129 | 11:00 | Maniknagar | 134 | 06:00 | 128 | 10:00
| Bangabhaban | 135 | 18:00 | 131 | 10:00 | Matarbari | 126 | 00:00 | 114 | 23:00
| Barapukuria | 137 | 00:00 | 129 | 08:00 | Matuail | 132 | 09:00 | 128 | 10:00
| Barguna | 133 | 09:00 | 127 | 01:00 | Millgate | 135 | 03:00 | 128 | 15:00
| Barishal | 140 | 09:00 | 126 | 14:00 | Mirpur | 138 | 18:00 | 131 | 10:00
| Barishal-230 | 140 | 08:00 | 134 | 22:00 | Mithapukur | 137 | 00:00 | 128 | 11:00
| Baroaulia | 139 | 20:00 | 133 | 14:00 | Modern | 137 | 18:30 | 131 | 09:00
| Baroirhat | 137 | 18:00 | 128 | 05:00 | Mogbazar | 135 | 04:00 | 127 | 10:00
| Bashundhara | 135 | 02:00 | 128 | 15:00 | Mongla | 132 | 06:00 | 125 | 20:00
| BashundharaCement | 134 | 18:00 | 128 | 10:00 | Motijheel | 134 | 03:00 | 131 | 10:00
| Beanibazar | 129 | 06:00 | 126 | 22:00 | Munshiganj | 135 | 18:00 | 129 | 10:00
| Benapole | 134 | 05:00 | 126 | 14:00 | Mymensingh | 131 | 06:00 | 112 | 12:00
| Bhaluka | 131 | 08:00 | 112 | 19:00 | Naogaon | 134 | 01:00 | 127 | 11:00
| Bhandaria | 139 | 08:00 | 130 | 20:00 | Narail | 136 | 06:00 | 128 | 14:00
| Bhangura | 138 | 02:00 | 133 | 10:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bheramara | 136 | 05:00 | 133 | 10:00 | Narshingdi | 130 | 02:00 | 125 | 00:00
| Bheramara(GK) | 139 | 05:00 | 133 | 15:00 | Natore | 134 | 00:00 | 129 | 11:00
| Bhulta | 129 | 09:00 | 124 | 07:00 | Nawabganj | 139 | 18:00 | 133 | 15:00
| Bog-Sherpur | 137 | 00:00 | 130 | 11:00 | Netrakona | 127 | 01:00 | 116 | 08:00
| Bogura | 138 | 00:00 | 130 | 11:00 | New | 135 | 02:00 | 129 | 15:00
| Bogura-230 | 138 | 01:00 | 132 | 10:00 | Niamatpur | 133 | 16:00 | 125 | 11:00
| Brahmanbaria | 137 | 22:00 | 128 | 18:00 | Noapara | 135 | 06:00 | 128 | 13:00
| Cantonment | 130 | 18:00 | 122 | 10:00 | Pabna | 136 | 06:00 | 131 | 11:00
| Chandpur | 136 | 18:00 | 128 | 06:00 | Palashbari | 134 | 01:00 | 127 | 07:00
| Chandraghona | 138 | 00:00 | 134 | 20:00 | Panchagarh | 136 | 00:00 | 120 | 07:00
| Chapai | 131 | 19:30 | 126 | 10:00 | Patuakhali | 134 | 09:00 | 128 | 13:00
| Charsaidpur | 135 | 18:00 | 129 | 10:00 | Payra | 136 | 09:00 | 133 | 00:00
| Chauddagram | 135 | 00:00 | 128 | 06:00 | PHP | 136 | 18:00 | 127 | 05:00
| Chhatak | 131 | 09:00 | 125 | 18:30 | Postogola | 137 | 18:00 | 129 | 10:00
| Chowmuhani | 132 | 17:00 | 123 | 00:00 | Purbachal | 137 | 04:00 | 129 | 12:00
| Chuadanga | 135 | 06:00 | 124 | 14:00 | Purbasadipur | 133 | 00:00 | 120 | 07:00
| Coxsbazar | 128 | 13:00 | 112 | 23:00 | Rahim | 134 | 18:00 | 129 | 10:00
| Cumilla(N) | 136 | 18:00 | 130 | 10:00 | Rajbari | 134 | 05:00 | 128 | 20:00
| Cumilla(S) | 136 | 18:00 | 125 | 12:00 | Rajendrapur | 137 | 18:00 | 129 | 22:00
| Daudkandi | 135 | 21:00 | 130 | 05:00 | Rajshahi | 132 | 00:00 | 126 | 11:00
| Dhaka | 133 | 02:00 | 127 | 10:00 | Rajshahi-230 | 131 | 00:00 | 126 | 10:00
| Dhamrai | 138 | 17:00 | 132 | 10:00 | Ramganj | 132 | 17:00 | 125 | 22:00
| Dhanmondi | 132 | 03:00 | 126 | 10:00 | Rampur | 137 | 18:30 | 131 | 16:00
| Dohazari | 135 | 00:00 | 128 | 06:00 | Rampura | 133 | 04:00 | 127 | 10:00
| Faridpur | 134 | 06:00 | 129 | 20:00 | Rangamati | 137 | 00:00 | 133 | 05:00
| Fatullah | 135 | 18:00 | 127 | 10:00 | Rangpur | 133 | 00:00 | 123 | 07:00
| Fenchuganj | 133 | 03:00 | 131 | 15:00 | Ruppur | 136 | 05:00 | 133 | 11:00
| Feni | 137 | 18:00 | 129 | 05:00 | Saidpur | 135 | 01:00 | 123 | 07:00
| Ghorashal | 138 | 07:00 | 135 | 15:00 | Satkhira | 134 | 09:00 | 125 | 20:00
| Goalpara | 136 | 09:00 | 130 | 12:00 | Satmasjid | 130 | 04:00 | 124 | 10:00
| Gollamari | 136 | 06:00 | 131 | 12:00 | Savar | 139 | 18:00 | 128 | 10:00
| Gopalganj | 136 | 00:00 | 131 | 13:00 | Shahjadpur | 141 | 03:00 | 136 | 10:00
| Gopalganj_I | 138 | 09:00 | 132 | 21:00 | Shahjibazar | 134 | 01:00 | 129 | 22:00
| Gulshan | 133 | 05:00 | 126 | 10:00 | Shahmirpur | 138 | 18:00 | 133 | 18:30
| Halishahar | 138 | 18:00 | 130 | 14:00 | Shariatpur | 136 | 09:00 | 129 | 20:00
| Haripur | 134 | 18:00 | 129 | 10:00 | Sherpur | 133 | 08:00 | 119 | 14:00
| HaripurSBU | 133 | 08:00 | 130 | 11:00 | Shikalbaha | 138 | 00:00 | 132 | 05:00
| Hasnabad | 136 | 18:00 | 129 | 10:00 | Shikalbaha-230 | 137 | 18:00 | 132 | 07:00
| Hathazari | 139 | 18:00 | 133 | 06:00 | Shitalakhya | 137 | 18:00 | 129 | 10:00
| Ishurdi | 137 | 06:00 | 132 | 10:00 | Sholosohor | 137 | 18:00 | 130 | 14:00
| Jaldhaka | 133 | 00:00 | 121 | 07:00 | Shyampur | 133 | 18:00 | 128 | 10:00
| Jamalpur | 133 | 06:00 | 119 | 15:00 | Shyampur-230 | 134 | 18:00 | 127 | 10:00
| Jashore | 133 | 02:00 | 126 | 14:00 | Siddhirganj | 133 | 09:00 | 128 | 10:00
| Jhenaidah | 139 | 05:00 | 131 | 18:00 | Sirajganj | 137 | 04:00 | 130 | 11:00
| Jhenaidah-230 | 139 | 06:00 | 131 | 21:00 | Sonargaon | 134 | 22:00 | 129 | 12:00
| Joydebpur | 138 | 05:00 | 133 | 10:00 | Sreemongol | 135 | 09:00 | 131 | 23:00
| Joypurhat | 133 | 02:00 | 126 | 18:00 | Srinagar | 138 | 18:00 | 131 | 10:00
| Juldah | 138 | 19:00 | 132 | 11:00 | SSM | 140 | 13:00 | 135 | 16:00
| Kabirpur | 155 | 14:00 | 125 | 21:00 | Sunamganj | 130 | 09:00 | 124 | 22:00
| Kachua | 136 | 18:00 | 128 | 05:00 | Sylhet | 131 | 09:00 | 129 | 00:00
| Kaliakoir | 139 | 03:00 | 134 | 07:00 | Tangail | 135 | 02:00 | 126 | 18:30
| Kallyanpur | 138 | 18:00 | 130 | 10:00 | Thakurgaon | 137 | 00:00 | 119 | 06:00
| Kalurghat | 137 | 00:00 | 132 | 05:00 | TK | 138 | 18:00 | 132 | 10:00
| Kamrangirchar | 139 | 18:00 | 133 | 01:00 | Tongi | 137 | 00:00 | 130 | 21:00
| Kaptai | 137 | 18:00 | 134 | 13:00 | Ullon | 132 | 06:00 | 126 | 10:00
| Kazla | 135 | 18:00 | 129 | 10:00 | Uttara | 136 | 18:00 | 128 | 10:00
| Keranigonj | 140 | 18:00 | 132 | 10:00 | UttaraNew | 138 | 18:00 | 127 | 18:30
| Khagrachori | 137 | 18:00 | 131 | 00:00 | Zigatola | 138 | 18:00 | 133 | 02:00
| Khulna | 135 | 06:00 | 129 | 20:00
| Khulna(S) | 136 | 06:00 | 130 | 14:00
| Khulshi | 136 | 18:00 | 129 | 10:00
| Kishoreganj | 132 | 01:00 | 118 | 14:00
| Kodda | 140 | 06:00 | 131 | 23:00
| KSRM | 137 | 00:00 | 132 | 05:00
| Kulaura | 132 | 09:00 | 130 | 22:00
| Kurigram | 133 | 00:00 | 121 | 18:00
| Kushtia | 137 | 06:00 | 132 | 14:00
Page 7 of 7

## L-Curve
Date | 2022-10-22
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 1300 | 6652 | 3784 | 10436 |  |  |  | QF-LDC-11
0:30 | 1270 | 6572 | 3759 | 10331 | Date: | 2022-10-22
1:00 | 1240 | 6492 | 3734 | 10226
1:30 | 1255 | 6444.5 | 3646 | 10090.5
2:00 | 1270 | 6397 | 3558 | 9955
2:30 | 1300 | 6394.5 | 3435.5 | 9830 | [5 empty] | Gen. at Eve. Peak | 12318 | 12318 MW (21:00 )
3:00 | 1330 | 6392 | 3313 | 9705 | [6 empty] | 21:00
3:30 | 1305 | 6345.5 | 3276 | 9621.5 | [5 empty] | Gen. at Day Peak | 9750 | 9750 MW (12:00 )
4:00 | 1280 | 6299 | 3239 | 9538 | [6 empty] | 12:00
4:30 | 1275 | 6250 | 3206 | 9456 | [5 empty] | Highest Generation | 12318
5:00 | 1270 | 6201 | 3173 | 9374 | [6 empty] | 21:00
5:30 | 1235 | 6186.5 | 3160 | 9346.5
6:00 | 1200 | 6172 | 3147 | 9319
6:30 | 1015 | 6225 | 3133 | 9358
7:00 | 830 | 6278 | 3119 | 9397
7:30 | 955 | 6260 | 3116 | 9376
8:00 | 1080 | 6242 | 3113 | 9355
8:30 | 1140 | 6246 | 3072 | 9318
9:00 | 1200 | 6250 | 3031 | 9281
9:30 | 1240 | 6286.5 | 3008 | 9294.5
10:00 | 1280 | 6323 | 2985 | 9308
10:30 | 1023 | 6347 | 3019.5 | 9366.5
11:00 | 766 | 6371 | 3054 | 9425
11:30 | 868 | 6384 | 3203.5 | 9587.5
12:00 | 970 | 6397 | 3353 | 9750
12:30 | 937 | 6404.5 | 3437 | 9841.5
13:00 | 904 | 6412 | 3521 | 9933
13:30 | 972 | 6440 | 3590 | 10030
14:00 | 1040 | 6468 | 3659 | 10127
14:30 | 1066 | 6416.5 | 3651 | 10067.5
15:00 | 1092 | 6365 | 3643 | 10008
15:30 | 1066 | 6369.5 | 3572.5 | 9942
16:00 | 1040 | 6374 | 3502 | 9876
16:30 | 1018 | 6406.5 | 3447 | 9853.5
17:00 | 996 | 6439 | 3392 | 9831
17:30 | 746 | 6966.5 | 3643.5 | 10610
18:00 | 496 | 7494 | 3895 | 11389
18:30 | 633 | 7629 | 3966.5 | 11595.5
19:00 | 770 | 7764 | 4038 | 11802
19:30 | 1016 | 7939 | 4086 | 12025
20:00 | 1096 | 8014 | 4159 | 12173 |  |  |  | Executive Engineer
20:30 | 1079 | 8073 | 4172.5 | 12245.5 |  |  |  | Network Operation Division
21:00 | 1062 | 8132 | 4186 | 12318
21:30 | 1186 | 7997 | 4200 | 12197
22:00 | 1310 | 7862 | 4214 | 12076 |  |  |  |  | Page 6 of 7
22:30 | 1325 | 7775.5 | 4121 | 11896.5
23:00 | 1340 | 7689 | 4028 | 11717
23:30 | 1320 | 7170.5 | 3906 | 11076.5
24:00 | 1300 | 6652 | 3784 | 10436
12318 MW (21:00 )
9750 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2022-10-22 |  | Energy |  | 250636224
[13 empty] | 2022-10-22 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 3667 | 918 | 1683 | 0 | 2499 | 1116 | 154 | 0 | 233 | 166 | 0 | 792
0:30 | 3786.5 | 919 | 1646 | 0 | 2448 | 1044 | 154 | 0 | 186.5 | 147 | 0 | 734.218 | Date: | 2022-10-22
1:00 | 3906 | 920 | 1609 | 0 | 2397 | 972 | 154 | 0 | 140 | 128 | 0 | 676.4361
1:30 | 3873 | 919.5 | 1603.5 | 0 | 2319 | 962 | 154 | 0 | 124.5 | 135 | 0 | 667.6811 | [8 empty] | Total Energy | 250.6362 | Total Energy Gen 250.636 MKWHr Energy Not Served 18.501 MKWHr Energy Requirement 269.137 MKWHr
2:00 | 3840 | 919 | 1598 | 0 | 2241 | 952 | 154 | 0 | 109 | 142 | 0 | 658.9261 | [8 empty] | Energy not Served | 18.5008
2:30 | 3838.5 | 920 | 1597.5 | 0 | 2132.5 | 937 | 153.5 | 0 | 109 | 142 | 0 | 633.5828 | [8 empty] | Energy Requirement | 269.137
3:00 | 3837 | 921 | 1597 | 0 | 2024 | 922 | 153 | 0 | 109 | 142 | 0 | 608.2395
3:30 | 3838.5 | 920.5 | 1594.5 | 0 | 1942.5 | 922.5 | 153 | 0 | 109 | 141 | 0 | 543.6198 | [6 empty] | Shortage
4:00 | 3840 | 920 | 1592 | 0 | 1861 | 923 | 153 | 0 | 109 | 140 | 0 | 479
4:30 | 3797 | 920 | 1581.5 | 0 | 1855.5 | 903 | 153 | 0 | 109 | 137 | 0 | 239.5
5:00 | 3754 | 920 | 1571 | 0 | 1850 | 883 | 153 | 0 | 109 | 134 | 0 | 0
5:30 | 3735 | 920 | 1574 | 0 | 1840.5 | 882.5 | 153.5 | 0 | 109 | 132 | 0 | 0
6:00 | 3716 | 920 | 1577 | 0 | 1831 | 882 | 154 | 0 | 109 | 130 | 0 | 0
6:30 | 3774 | 920.5 | 1584.5 | 0 | 1816 | 857 | 154.5 | 0 | 109 | 123 | 19.5 | 0 |  |  |  |  | Coal
7:00 | 3832 | 921 | 1592 | 0 | 1801 | 832 | 155 | 0 | 109 | 116 | 39 | 0
7:30 | 3784 | 921 | 1562.5 | 0 | 1809 | 841.5 | 155.5 | 0 | 109.5 | 122 | 71 | 141.001 |  |  |  | Oil |  |  |  | ,
8:00 | 3736 | 921 | 1533 | 0 | 1817 | 851 | 156 | 0 | 110 | 128 | 103 | 282.0019
8:30 | 3726 | 921 | 1489.5 | 0 | 1795.5 | 851.5 | 156 | 0 | 110 | 132 | 136.5 | 364.9437
9:00 | 3716 | 921 | 1446 | 0 | 1774 | 852 | 156 | 0 | 110 | 136 | 170 | 447.8854
9:30 | 3691 | 920.5 | 1445 | 0 | 1787.5 | 851 | 156 | 0 | 109 | 138 | 196.5 | 459.8659
10:00 | 3666 | 920 | 1444 | 0 | 1801 | 850 | 156 | 0 | 108 | 140 | 223 | 471.8464
10:30 | 3679 | 920.5 | 1479.5 | 0 | 1810.5 | 840 | 156 | 0 | 107.5 | 145 | 228.5 | 707.7696
11:00 | 3692 | 921 | 1515 | 0 | 1820 | 830 | 156 | 0 | 107 | 150 | 234 | 943.6928
11:30 | 3700.5 | 920 | 1499 | 0 | 1955.5 | 859 | 156 | 0 | 106.5 | 156 | 235 | 1002.8464
12:00 | 3709 | 919 | 1483 | 0 | 2091 | 888 | 156 | 0 | 106 | 162 | 236 | 1062
12:30 | 3678.5 | 919.5 | 1496 | 0 | 2188.5 | 898 | 156 | 0 | 105.5 | 163 | 236.5 | 1106.5
13:00 | 3648 | 920 | 1509 | 0 | 2286 | 908 | 156 | 0 | 105 | 164 | 237 | 1151
13:30 | 3648 | 920 | 1509 | 0 | 2286 | 908 | 156 | 0 | 105 | 164 | 237 | 1151
14:00 | 3648 | 920 | 1509 | 0 | 2286 | 908 | 156 | 0 | 105 | 164 | 237 | 1151
14:30 | 3657.5 | 918.5 | 1508 | 0 | 2340 | 937.5 | 154.5 | 0 | 101.5 | 164 | 189 | 1257
15:00 | 3667 | 917 | 1507 | 0 | 2394 | 967 | 153 | 0 | 98 | 164 | 141 | 1363
15:30 | 3660 | 917 | 1503 | 0 | 2371 | 963.5 | 153 | 0 | 102.5 | 166 | 106 | 1400.7893
16:00 | 3653 | 917 | 1499 | 0 | 2348 | 960 | 153 | 0 | 107 | 168 | 71 | 1438.5786
16:30 | 3494 | 917.5 | 1498 | 0 | 2431.5 | 962 | 153.5 | 0 | 115 | 162 | 40.5 | 1459.314
17:00 | 3494 | 918 | 1497 | 0 | 2515 | 964 | 154 | 0 | 123 | 156 | 10 | 1480.0495
17:30 | 3532.5 | 917.5 | 1560 | 104 | 2897.5 | 975.5 | 154 | 0 | 300 | 164 | 5 | 1390.1959
18:00 | 3571 | 917 | 1623 | 208 | 3280 | 987 | 154 | 0 | 477 | 172 | 0 | 1300.3423
18:30 | 3533 | 917 | 1656 | 184 | 3419 | 1052 | 154.5 | 0 | 517 | 163 | 0 | 1248.1712
19:00 | 3495 | 917 | 1689 | 160 | 3558 | 1117 | 155 | 0 | 557 | 154 | 0 | 1196
19:30 | 3565 | 917 | 1759 | 206 | 3575 | 1135 | 155 | 0 | 541 | 172 | 0 | 1025.15
20:00 | 3617 | 918 | 1811 | 207 | 3594 | 1174 | 155 | 0 | 535 | 162 | 0 | 854.3
20:30 | 3619.5 | 917.5 | 1819 | 256.5 | 3597 | 1184.5 | 155 | 0 | 536.5 | 160 | 0 | 719.2893
21:00 | 3622 | 917 | 1827 | 306 | 3600 | 1195 | 155 | 0 | 538 | 158 | 0 | 584.2786
21:30 | 3664.5 | 917 | 1801.5 | 328 | 3520.5 | 1175 | 155 | 0 | 476.5 | 159 | 0 | 576.4452
22:00 | 3707 | 917 | 1776 | 350 | 3441 | 1155 | 155 | 0 | 415 | 160 | 0 | 568.6118
22:30 | 3655.5 | 917 | 1786.5 | 352 | 3388 | 1116 | 155 | 0 | 364.5 | 162 | 0 | 654.779
23:00 | 3604 | 917 | 1797 | 354 | 3335 | 1077 | 155 | 0 | 314 | 164 | 0 | 740.9463
23:30 | 3635.5 | 917.5 | 1740 | 177 | 2917 | 1096.5 | 154.5 | 0 | 273.5 | 165 | 0 | 1183.4732 | Max Temp. in Dhaka |  | 24.7° C | 34.8° C
24:00 | 3667 | 918 | 1683 | 0 | 2499 | 1116 | 154 | 0 | 233 | 166 | 0 | 1626
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 250.636 MKWHr Energy Not Served 18.501 MKWHr Energy Requirement 269.137 MKWHr
Note on W13: Author:

## Generation
g | 2022-10-22
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 84 | 84 | 83 | 83 | 83 | 84 | 85 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 83 | 83 | 84 | 84 |  | 85 | 85 | 85 | 85 | 85 | 85 | 84 | 2031436
2 | Karnaphuli Hydro PP Unit-4 & 5 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1708000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 0 | [7 empty] | 2 | 17 | 17 |  | 18 | 25 | 25 | 25 | 25 | 25 | 25 | 379202
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 5 | 11 | 7 | 18 | 20 | 18 | 20 | 17 | 8 | 3 | [10 empty] | 117450
6 | Sikalbaha 225MW CCPP (Gas) | 151 | 151 | 151 | 150 | 150 | 140 | 150 | 152 | 151 | 150 | 150 | 150 | 148 | 146 | 148 | 150 | 150 | 151 |  | 151 | 152 | 151 | 151 | 151 | 150 | 151 | 3606934
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 16 | 16 | 16 | 16 | 15 | 15 | 15 | 15 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 635517
12 | Hathazari 100 MW peaking PP | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 28 | 34 | 34 | 34 |  | 36 | 36 | 36 | 36 | 36 | 12 | 30 | 741984
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 54 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 70 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 68 | 1778109
| Daudkandi 200 MW PP (B.Trac) | [17 empty] | 50 |  | 50 | 50 | 50 | 100 | 100 | 100 | 0 | 383040
14 | Titas 50 MW Peaking PP | 45 | 46 | 46 | 46 | 46 | 46 | 46 | 47 | 47 | 46 | 45 | 44 | 43 | 43 | 35 | 38 | 38 | 43 |  | 44 | 44 | 44 | 44 | 44 | 44 | 0 | 1048528
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 159 | 155 | 160 | 167 | 172 | 176 | 177 | 181 | 160 | 158 | 160 | 161 | 160 | 160 | 150 | 140 | 169 | 184 |  | 171 | 180 | 175 | 170 | 175 | 176 | 163 | 4083965
18 | Kodda 300 MW PP Unit-2 (Summit) | 97 | 97 | 97 | 97 | 97 | 97 | 95 | 97 | 97 | 145 | 163 | 163 | 160 | 165 | 155 | 155 | 155 | 215 |  | 270 | 260 | 258 | 260 | 248 | 245 | 148 | 3796255
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 45 |  | 45 | 51 | 73 | 73 | 8 | 8 | 8 | 401454
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 93 | 100 | 100 | 100 | 100 | 100 |  | 100 | 140 | 170 | 170 | 170 | 170 | 170 | 2727000
23 | Ghorasal TPP Unit-5 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4315500
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 48 | 48 | 48 | 48 | 48 | 49 | 49 | 48 | 45 | 46 | 46 | 10 | 10 | 10 | 10 | 10 | 10 | 48 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 932616
33 | Ashuganj 225 MW CCPP | 208 | 191 | 182 | 176 | 165 | 165 | 157 | 179 | 160 | 149 | 130 | 148 | 163 | 174 | 180 | 176 |  |  |  |  | 29 | 33 | 47 | 52 | 56 | 95 | 3109000
34 | Ashuganj 450 MW CCPP(South) | 345 | 310 | 310 | 310 | 325 | 310 | 330 | 310 | 260 | 200 | 200 | 200 | 200 | 200 | 200 | 260 | 320 | 305 |  | 305 | 305 | 305 | 305 | 305 | 240 | 240 | 6847000
Ashuganj 450 MW CCPP(North)
| Ashuganj 420 MW CCPP(East) | 202 | 202 | 202 | 202 | 202 | 204 | 203 | 203 | 393 | 424 | 428 | 432 | 431 | 414 | 430 | 327 | 309 | 321 |  | 318 | 318 | 318 | 318 | 318 | 318 | 318 | 7759300
35 | Ashuganj 55 MW PP (Precision) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 20 | 20 | 10 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 20 |  | 47 | 47 | 47 | 47 | 47 | 45 | 10 | 762240
36 | Chandpur 150 MW CCPP | 50 | 50 | 51 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 52 | 50 | 50 | 50 | 50 | 51 | 49 | 49 |  | 49 | 50 | 49 | 50 | 51 | 0 | 20 | 1141730
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 392 | 392 | 393 | 396 | 397 | 398 | 398 | 400 | 418 | 419 | 420 | 417 | 411 | 413 | 412 | 418 | 407 | 408 |  | 411 | 411 | 410 | 411 | 411 | 412 | 411 | 9910270
40 | Meghnaghat 450 MW CCPP(MPL) | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 |  | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 5127000
41 | Haripur 360MW CCPP(HPL) | 250 | 257 | 260 | 264 | 264 | 264 | 264 | 288 | 288 | 302 | 302 | 294 | 285 | 283 | 273 | 272 | 252 | 253 |  | 253 | 253 | 253 | 257 | 260 | 260 | 260 | 6410000
42 | RPCL 210MW CCPP | 108 | 108 | 108 | 110 | 109 | 109 | 70 | 70 | 21 | 16 | 25 | 31 | 31 | 31 | 30 | 30 | 30 | 33 |  | 33 | 47 | 57 | 74 | 101 | 108 | 104 | 1444800
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 0 | 7 | 14 | 40 | 49 | 43 | 54 | 51 | 45 | 33 | 18 | 2 | [9 empty] | 366420
44 | Fenchugonj CCPP Phase-1 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 715000
45 | Fenchugonj CCPP Phase-2 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 |  | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 960240
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 63 | 63 | 63 | 63 | 63 | 63 | 65 | 64 | 64 | 59 | 40 | 58 | 60 | 58 | 56 | 62 | 60 | 63 |  | 61 | 63 | 62 | 61 | 57 | 57 | 57 | 1435488
48 | Shahjibazar 86MW PP (Shahjibazar) | [17 empty] | 81 |  | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 580800
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 |  | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 3348610
51 | Sylhet 20 MW GTPP | 19 | 18 | 19 | 19 | 19 | 19 | 19 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 432000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 239760
54 | Hobiganj 11MW PP Cofidence-E | 5 | [24 empty] | 0 | 6048
55 | Fenchugonj 51 MW PP (Barakatullah) | [25 empty] | 0 | 0
56 | Shahjahanulla 25 MW PP | [25 empty] | 0 | 0
57 | Bibiana-II 341 MW CCPP (Summit) | 320 | 300 | 290 | 280 | 295 | 300 | 320 | 300 | 275 | 280 | 280 | 280 | 341 | 341 | 341 | 325 | 341 | 341 |  | 341 | 341 | 341 | 341 | 300 | 305 | 290 | 7545500
| Bibiyana South 400 MW | 400 | 400 | 400 | 400 | 350 | 330 | 400 | 400 | 350 | 350 | 400 | 396 | 392 | 378 | 391 | 370 | 400 | 360 |  | 398 | 400 | 400 | 380 | 400 | 390 | 400 | 9123200
58 | Nababganj 55 MW PP (Southern power ) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 55 | 55 | 55 | 35 | 35 | 35 | 35 | 895924
59 | Tangail Palli Power Gen 22 MW | 12 | 12 | 12 | 12 | 12 | 9 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 294240
60 | Barabkunda 22 MW PP (Regent) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 0 | 366240
61 | Narshingdi 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 0 |  |  |  |  | 19 | 358092
62 | Tangail 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 18 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 18 | 18 | 18 | 18 | 18 | 18 | 415908
63 | Impoprt (Tripura) | 128 | 142 | 142 | 140 | 134 | 130 | 116 | 128 | 136 | 140 | 150 | 162 | 164 | 160 | 164 | 168 | 156 | 172 |  | 154 | 172 | 162 | 158 | 160 | 164 | 166 | 3552000
64 | Malancha, Ctg. EPZ (United) | 40 | 40 | 40 | 42 | 42 | 42 | 41 | 19 | 10 | 0 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 4 |  | 10 | 14 | 21 | 30 | 35 | 37 | 37 | 509760
65 | Feni 22MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 19 | 19 | 19 | 21 | 21 | 21 | 21 | 20 | 20 |  | 21 | 21 | 21 | 22 | 22 | 22 | 22 | 484848
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 9 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 240840
67 | Jangalia 33MW PP (Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 14 | 14 | 14 | 8 | 8 | 8 | 8 | 10 | 16 |  | 22 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 465000
68 | Cumilla 25 MW PP (Summit) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 0 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 15 | 338150
69 | Summit Ashulia | 21 | 21 | 20 | 20 | 21 | 19 | 19 | 21 | 21 | 21 | 19 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 15 | 14 | 21 | 21 | 505000
70 | Summit Madhabdi | 28 | 28 | 28 | 28 | 26 | 28 | 28 | 28 | 28 | 26 | 25 | 24 | 6 | 23 | 23 | 23 | 23 | 23 |  | 23 | 24 | 24 | 24 | 24 | 18 | 19 | 577080
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 0 |  | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 737600
72 | Rupganj 33 MW PP(Summit) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 14 | 14 | 14 | 12 | 7 | 13 | 13 | 13 | 13 | 13 | 13 |  | 13 | 13 | 13 | 13 | 13 | 14 | 14 | 326800
73 | Ghorashal 108MW PP (Regent) | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 79 | 79 | 79 | 76 | 73 | 73 | 70 | 70 | 70 |  | 70 | 79 | 80 | 80 | 83 | 84 | 84 | 1868227
| Feni Lanka Power | 111 | 111 | 111 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 110 | 111 |  | 111 | 111 | 111 | 111 | 111 | 111 | 111 | 1430700
| Chowmuhani 113 MW | 0 | 2 | 0 |  |  | 0 | 3 | 0 |  |  | 0 | 0 | 8 |  |  |  |  | 5 | [6 empty] | 4 | 0 | 54600
| Manikgonj 162MW PP(MPGL) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 75 |  | 65 | 109 | 149 |  | 162 | 162 | 162 | 162 | 162 | 108 | 35 | 1869120
77 | Siddhirganj 100 PP(Dutch Bangla) | 58 | 58 | 57 | 57 | 57 | 54 | 0 |  |  | 0 | 7 | 41 | 60 | 70 | 70 | 70 | 78 | 85 |  | 87 | 87 | 87 | 87 | 87 | 87 | 60 | 1318080
78 | Gazipur 52 MW PP | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 36 | 38 |  | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 990240
79 | Kodda 150MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 132 |  | 132 | 132 | 132 | 132 | 16 | 16 | 16 | 833280
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 43 | 43 | 43 | 40 | 34 | 34 | 34 | 34 | 8 | 8 | 8 | 8 | 8 | 13 | 16 | 15 | 16 | 20 |  | 31 | 34 | 33 | 34 | 38 | 43 | 38 | 680064
| Gazipur 100 MW PP | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 |  | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 2112000
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 2 | 3 | 4 | 4 | 4 | 4 | 3 | 2 | 1 | 0 | [9 empty] | 27598
| Jodiac Power | 54 | 41 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1347289
| Karnaphuli Power Ltd. | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 53 | 68 | 70 | 71 | 71 | 71 | 70 | 76 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 64 | 1780610
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL) | 58 | 59 | 59 | 58 | 59 | 59 | 59 | 63 | 68 | 67 | 68 | 67 | 67 | 67 | 67 | 65 | 67 | 70 |  | 75 | 84 | 81 | 83 | 83 | 84 | 57 | 1619520
| Meghnaghat 104 MW PP (OPCL) | 55 | 54 | 54 | 54 | 54 | 54 | 73 | 73 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 |  | 74 | 74 | 74 | 84 | 93 | 92 | 92 | 1723200
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 56 |  | 56 | 56 | 56 | 56 | 56 | 56 | 33 | 913560
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 0 | 1136830
94 | Gagnagar 102 MW PP (Digital Power) | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 83 |  | 83 | 83 | 92 | 92 | 92 | 92 | 58 | 1719792
95 | Patenga 50MW PP (Baraka) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 26 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 40 | 43 |  | 44 | 44 | 44 | 44 | 44 | 44 | 32 | 797760
96 | Chattogram 108 MW PP (ECPV) | [21 empty] | 0 |  |  |  | 0 | 0
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 50 | 1332382
100 | Manikganj 55 MW PP (Northern) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 887434
101 | Kushiara 163 MW CCPP (KP)
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 0 | [9 empty] | 15150
103 | Kamalaghat 54 MW PP(Banco Energy) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 35 | 662760
104 | Keranigonj 300 MW PP (APR) | [17 empty] | 24 |  | 60 | 106 | 107 | 106 | 150 | 154 | 0 | 600515
105 | Bramhangoan 100 MW PP (Aggreko) | [17 empty] | 50 |  | 25 | 25 | 25 | 50 | 50 | 50 | 0 | 263847
106 | Mymensingh 200 MW PP (United) | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 59 | 57 | 48 | 58 | 58 | 57 | 58 | 86 |  | 87 | 87 | 87 | 88 | 88 | 88 | 53 | 1447200
112 | Aurahati 100MW PP (Aggreko) | [17 empty] | 51 |  | 25 | 25 | 25 | 50 | 50 | 50 | 0 | 264433
114 | Kodda 149 MW PP Unit-1 (Summit) | 100 | 90 | 88 | 90 | 90 | 88 | 89 | 89 | 91 | 123 | 125 | 126 | 125 | 131 | 134 | 134 | 134 | 134 |  | 135 | 135 | 135 | 144 | 149 | 149 | 149 | 2878992
115 | Juldah 100 MW PP Unit-3 (Acorn) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 11 | 25 | 25 |  | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 863040
116 | Chandpur 200MW (Desh energy) | 24 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 22 | 28 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 23 | 660480
117 | Ashuganj 150MW PP (Midland) | 65 | 65 | 56 | 61 | 68 | 70 | 70 | 70 | 68 | 65 | 68 | 71 | 67 | 67 | 68 | 68 | 67 | 68 |  | 71 | 72 | 72 | 73 | 67 | 73 | 80 | 1647636
118 | Bibiyana-III 400 MW CCPP | 408 | 406 | 407 | 407 | 353 | 352 | 408 | 409 | 389 | 408 | 410 | 409 | 380 | 355 | 355 | 412 | 366 | 400 |  | 409 | 409 | 409 | 408 | 409 | 410 | 409 | 9468000
| Jamalpur 115 MW PP (United) | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 87 | 77 | 78 | 78 | 78 | 78 | 78 | 78 | 97 |  | 97 | 97 | 97 | 97 | 97 | 87 | 48 | 2049600
| Anwara 300 MW PP (United) | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 140 | 140 | 141 | 141 | 141 | 141 | 141 | 141 | 141 | 276 |  | 284 | 284 | 300 | 300 | 141 | 141 | 141 | 3658255
| Juldah unit-2 (Acorn) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 24 | 25 | 25 | 25 | 25 | 42 |  | 100 | 100 | 100 | 100 | 100 | 100 | 31 | 1013760
| Anlima Energy Ltd. | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 |  | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 2578091
| Bhairob 54.5 MW | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 885960
| Spectra Solar Plant Ltd. | [5 empty] | 0 | 6 | 16 | 24 | 30 | 33 | 34 | 31 | 27 | 19 | 10 | 1 | [9 empty] | 230364
| Chandpur 115(Doreen) | 54 | 49 | 54 | 54 | 53 | 54 | 54 | 53 | 54 | 54 | 38 | 52 | 53 | 54 | 54 | 53 | 72 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 68 | 1685760
| Kanchan Purbachal Power Generation Ltd. | 54 | 54 | 54 | 54 | 42 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 42 | 42 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1266480
Mirsharai 150 MW (Oil)
Mirsharai 150 MW (Gas)
120 | Eastern Zone Total | 6492 | 6397 | 6392 | 6299 | 6201 | 6172 | 6278 | 6242 | 6250 | 6323 | 6371 | 6397 | 6412 | 6468 | 6365 | 6374 | 6439 | 7494 |  | 7764 | 7939 | 8014 | 8132 | 7862 | 7689 | 6652 | 162601487
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | 16 | 16 | [11 empty] | 16 | 16 | 16 | 16 | 16 |  | 9 | 16 | 16 | 16 | 16 | 16 | 0 | 192000
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [16 empty] | 6 | 36 |  | 30 | 28 | 28 | 28 | 22 | 0 |  | 135360
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 72 | 72 | 72 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 28 | 54 | 55 | 54 | 54 | 54 | 71 |  | 75 | 75 | 75 | 75 | 75 | 75 | 74 | 1202400
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 0 | 13 | 39 | 61 | 78 | 86 | 84 | 83 | 67 | 48 | 23 | 4 | [9 empty] | 593280
131 | Rampal 1320 MW (BIFPCL) | [16 empty] | 155 | 188 |  | 277 | 285 | 304 | 304 | 304 | 236 | 303 | 1990600
132 | United Payra Power Ltd. | [25 empty] | 0 | 0
133 | Bhola Nutan Biddut BD LTD (GAS) | 221 | 221 | 220 | 220 | 180 | 180 | 180 | 183 | 183 | 183 | 215 | 212 | 213 | 212 | 213 | 215 | 213 | 202 |  | 205 | 223 | 222 | 205 | 222 | 222 | 221 | 5000618
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [17 empty] | 16 |  | 32 | 32 | 32 | 32 | 32 | 32 | 16 | 203808
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 89 | 89 | 89 | 85 | 89 | 88 | 89 | 0 |  |  | 0 | 62 | 56 | 62 | 64 | 56 | 64 | 50 |  | 54 | 63 | 65 | 50 | 65 | 65 | 65 | 1450648
140 | Bhola 33 MW PP (Venture) | 25 | 25 | 23 | 23 | 23 | 23 | 19 | 18 | 15 | 18 | 19 | 19 | 18 | 21 | 21 | 19 | 21 | 29 |  | 32 | 32 | 34 | 31 | 32 | 31 | 31 | 566136
141 | Noapara 100 MW PP (Bangla Trac) | [17 empty] | 30 | [7 empty] | 0 | 29760
142 | Noapara 40 MW PP (Khanjahan Ali) | [17 empty] | 8 |  | 8 | 8 | 8 | 8 | 8 | 0 | 0 | 45000
143 | Gopalganj 100 MW Peaking PP | [16 empty] | 10 | 45 |  | 75 | 60 | 62 | 65 | 64 | 64 | 64 | 402304
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | 105 | 105 | 67 | 50 | 50 | 32 | 32 | 32 | 15 | 0 | 0 | 15 | 15 | 50 | 50 | 50 | 50 | 105 |  | 105 | 105 | 105 | 105 | 105 | 67 | 0 | 1436688
146 | Bheramara HVDC | 920 | 919 | 921 | 920 | 920 | 920 | 921 | 921 | 921 | 920 | 921 | 919 | 920 | 921 | 917 | 917 | 918 | 917 |  | 917 | 917 | 918 | 917 | 917 | 917 | 918 | 22225454
147 | Bheramara 410 MW CCPP | 210 | 210 | 210 | 210 | 215 | 215 | 215 | 215 | 210 | 200 | 200 | 200 | 190 | 190 | 190 | 190 | 195 | 200 |  | 200 | 200 | 215 | 225 | 235 | 240 | 240 | 5169600
148 | Payra 1320 MW | 890 | 870 | 840 | 840 | 800 | 800 | 750 | 770 | 770 | 770 | 750 | 810 | 830 | 860 | 890 | 880 | 730 | 720 |  | 760 | 770 | 790 | 810 | 770 | 760 | 730 | 21169800
149
150 | Barapukuria TPP Unit-1 | 82 | 82 | 82 | 83 | 83 | 82 | 82 | 81 | 82 | 80 | 80 | 78 | 78 | 78 | 77 | 80 | 79 | 79 |  | 80 | 80 | 80 | 81 | 81 | 81 | 83 | 1926982
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [17 empty] | 32 |  | 32 | 32 | 32 | 32 | 32 | 32 | 0 | 198484
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 1 | 3 | 4 | 5 | 5 | 5 | 5 | 4 | 3 | 2 | 0 | [9 empty] | 40140
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 181 | 180 | 180 | 182 | 182 | 182 | 185 | 183 | 181 | 176 | 174 | 171 | 170 | 160 | 148 | 142 | 138 | 138 |  | 20 | [6 empty] | 3281900
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 146 | 145 | 146 | 147 | 148 | 149 | 150 | 148 | 146 | 146 | 147 | 143 | 140 | 139 | 138 | 138 | 138 | 138 |  | 138 | 137 | 137 | 143 | 149 | 152 | 157 | 3729036
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 302 | 305 | 313 | 312 | 316 | 317 | 317 | 306 | 257 | 259 | 300 | 280 | 257 | 267 | 266 | 278 | 279 | 272 |  | 297 | 330 | 351 | 374 | 400 | 416 | 404 | 7401818
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [13 empty] | 4 | 4 | 4 | 4 | 4 |  | 8 | 8 | [5 empty] | 27513
162 | Bogra 22 MW PP (GBB) | 22 | 21 | 22 | 22 | 22 | 22 | 22 | 21 | 20 | 19 | 19 | 18 | 18 | 18 | 19 | 19 | 20 | 20 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 479760
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 235854
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | 42 | 42 | 16 | 16 | 16 | 8 | 8 | 8 | 8 | 0 | 0 | 16 | 42 | 42 | 42 | 34 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 34 | 656799
167 | Katakhali 50 MW Peaking PP | [19 empty] | 32 | 32 | 32 | 32 | 32 | 0 | 0 | 122595
168 | Santahar 50 MW Peaking PP | [17 empty] | 15 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 181273
169 | Natore 52 MW PP (Rajlanka) | [17 empty] | 8 |  | 8 | 8 | 8 | 8 | 8 | 0 | 0 | 47731
170 | Chapainawabganj 100 MW Peaking PP | 32 | [16 empty] | 85 |  | 85 | 86 | 86 | 86 | 86 | 63 | 40 | 538784
171 | Baghabari 200 MW PP (Paramount) | [17 empty] | 3 | [7 empty] | 0 | 10538
| Bagura 113 MW PP (Confidence)-2 | 113 | 70 | 35 | 35 | 35 | 35 | 35 | 39 | 35 | 35 | 35 | 69 | 113 | 113 | 113 | 113 | 50 | 80 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2004672
172 | Confidence Power Bogura Unit-1 113 MW | 113 | 70 | 35 | 35 | 35 | 35 | 35 | 70 | 35 | 0 | 0 | 90 | 113 | 113 | 113 | 50 | 50 | 113 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 1894656
173 | Rangpur 20 MW GTPP | [20 empty] | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | 107 | 70 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 52 | 56 | 107 | 107 | 103 | 106 | 109 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 1817683
177 | Sympa Solar Power 8MW | [6 empty] | 1 | 1 | 4 | 6 | 6 | 0 | 7 | 7 | 5 | 3 | 1 | [9 empty] | 42455
178 | Energypac Power Venture Thakurgaon Ltd. | 35 | 35 | [8 empty] | 0 | 36 | 98 | 113 | 113 | 95 | 36 | 113 |  | 113 | 113 | 113 | 113 | 113 | 113 | 0 | 1337088
178 | Intraco Solar 30 MW | [5 empty] | 0 | 5 | 16 | 25 | 31 | 35 | 35 | 34 | 29 | 21 | 10 | 2 | [9 empty] | 245520