## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2022-10-26 | Wednesday
|  | Date (day): | 2022-10-26 |  | Wednesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 9826.6 | MW |  |  | (b) At Evening Peak Hour : |  | 12433 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2022-10-25 | 2022-10-26 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  |  | Machine problem
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Machine problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 56 | 81 | 80 | 84 |  | 24 | Engine problem
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 409 | 361 | 400 | 400 | 12 |  | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 326 | 340 | 272 | 320 | 40 |  | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 225 | 225 | 225 |  | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 4 | 50 | 70 | 94 |  | 6 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 10 | 125 | 135 |  | 335 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 0 | 0 | 0 | 0 |  | 102 | Under maint
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 45 | 45 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 10 | 19 | 19 |  | 3 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 49 | 90 | 63 | 90 |  | 10 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 213 | 140 | 0 | 0 |  | 335 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 36 | 40 | 74 | 85 |  | 17 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 54 | 17 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 16 | 16 | 20 | 132 |  | 17 | Engine problem
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55 | 0 |  | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 0 | 55 |  |  | 33 kV feeder Fault.
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 33 | 37 | 51 | 53 |  | 27 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 16 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 0 | 26 | 20 | 26 |  | 7 | Engine problem
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 2 | 33 | 41 | 49
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 12 | 140 | 160 | 260 |  | 40 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 150 | 150 |  | Fuel conservation
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 0 | 0 | 0 | 50 | 50 |  | Fuel conservation
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 100 | 0 |  | Fuel conservation
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 3 | 86 | 80 | 134 |  | 15 | Engine problem
36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 70 | 88 | 88 | 88 |  | 17 | Engine problem
37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 63 | 92 | 74 | 92 | 12 |  | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 35 | 162 | 35 | 162
39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 25 | 0 | 30 | 0
40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 42 | 40 | 54 | 54
| Dhaka area Total |  |  |  |  | 6263 | 5847 | 1932 | 2434 | 2321 | 3234 | 750 | 1820
41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 4 | 8 | 25 | 25
43 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 18 | 0 | 20 | 0
44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 37 | 32 | 44 |  | 6 | Engine problem
45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 70 | 70 | 116 | 116 | 114 |  | Low Water Level
46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 151 | 150 | 150 | 150 |  | 75 | ST under maint
47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 68 | 105 | 51 | 105
49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 24 | 25 | 73 |  | Fuel shortage
50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 34 | 17 | 51 | 51 |  | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 44 | 70 | 33 | 70 | 30 |  | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 25 | 90 | 38 | 90 |  | 10 | Engine problem
53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  | 22 | Engine problem
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 10 | 3 | 10 | 15
54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 2 | 0 | 5 | 0
56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 176 | 176 | 140 | 195 | 105 |  | Fuel shortage
57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 36 | 17 | 54 | 54
58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 70 | 105 | 61 | 105
59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 66 | 25 | 100
60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 25 | 107 | 107 |  | 9 | Engine problem
| Mirsharai 150 MW |  | Gas/HSD | BPDB-RPCL | 18.5*9 | 0 | 0 | 5 | 0 | 0 | 0
| Chattogram area Total |  |  |  |  | 2442 | 2382 | 704 | 956 | 908 | 1252 | 841 | 272
61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 0 | 181 | 100 | 200 |  | 75 | ST Under maint.
63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 90 | 270 | 270 | 90 |  | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 275 | 285 | 260 | 300 | 60 |  | Gas shortage
| Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+136*1 | 284 | 284 | 0 | 0 | 0 | 0 |  |  | On test.
65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 11 | 45 | 45 | 45 | 0 |  | Gas shortage
66 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 55 | 23 | 51 | 51 | 51 | 4 |  | Gas shortage
67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 0 | 0 | 0 | 0
69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 6 | 10 | 70 | 70 | 80 |  | Fuel shortage
70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 40 | 43 |  | 9 | Engine problem
71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 50 | 50 | 113 |  | Gas shortage.
72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 6 | 17 | 100 | 200 | 0 |  | Fuel shortage
73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 19 | 22 | 22
74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 44 | 98 | 143 | 166
75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 0 | 20 | 32 | 32 |  | 1 | Engine problem
76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 1 | 0 | 8 | 34 | 18 |  | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 0 | 0 | 12 | 20 |  | 5 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 100 | 100 |  | Fuel conservation
79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 17 | 114 | 114
80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 0 | 0 | 113 |  | Fuel shortage
81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 0 | 35 | 35 | 35 |  | 19 | Engine problem
82 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 14 | 34 | 53 | 115
| Cumilla Area Total |  |  |  |  | 3193 | 3169 | 405 | 910 | 1424 | 1886 | 899 | 109
83 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 105 | 83 | 108 | 110 | 92 |  | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 18 | 18 | 19 |  | 3 | Engine problem
85 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0
86 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1 | 0 | 1.6 | 0
87 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 46 | 88 | 45 | 88 | 112 |  | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 47 | 92 | 90 | 97 |  | 18 | Engine problem
89 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 37 | 0 | 50 | 0
90 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 12 | 12 |  | 10 | Engine problem
| Mymensingh Area Total |  |  |  |  | 717 | 614 | 266 | 293 | 324.6 | 326 | 92 | 31
91 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 0 | 30 | 30 | 30 |  | 40 | Machine problem.
92 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 21 | 30 | 30 | 40 |  | 50 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 | 163 |  | Gas shortage
94 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 0 | 11 | 0 | 0 | 51 |  | Gas shortage
96 | Fenchuganj 44MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 0 | 10 | 0 | 0 | 50 |  | Gas shortage
97 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 11 |  | Gas shortage
98 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 5 | 32 | 60 | 60
99 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 0 | 78 | 30 | 81
100 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
101 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 158 | 158 | 145 | 178 |  | 53 | ST Under maint.
102 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18
103 | Sylhet 50MW PP (EPL) |  | Gas | NENP | 27*2 | 50 | 50 | 0 | 11 | 0 | 0 | 50 |  | Gas shortage
104 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 0 | 8 | 0 | 0 | 25 |  | Gas shortage
105 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 285 | 280 | 300 | 300 |  |  | FGMO
106 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 408 | 407 | 400 | 400
107 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 9 | 10 | 10
108 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 70 | 400 | 380 | 400
| Sylhet Area Total |  |  |  |  | 2522 | 2477 | 975 | 1482 | 1403 | 1517 | 350 | 573
109 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 485 | 800 | 766 | 911
110 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 0 | 0 | 0 | 16 | 99 |  | Fuel shortage
111 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 32 | 22 |  | Fuel shortage
112 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
113 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 76 | 33 |  | Fuel shortage
114 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 260 | 320 | 260 | 320 | 90 |  | Gas shortage
115 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 0 | 0 | 8 | 32 |  | Fuel shortage
116 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 0 | 50 | 50 |  | Fuel conservation
117 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 35 | 75 | 75 |  | 30 | Engine problem
118 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 0 |  |  | Fuel shortage
119 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 86 | 0 | 100 | 0
| Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 2388 | 2384 | 831 | 1155 | 1201 | 1488 | 572 | 30
120 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 0 | 16 |  |  | Line O/L
121 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 5 | 11 | 16 | 27 |  | 13 | Engine problem
122 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 0 | 20 | 65 | 65 |  | 129 | Machine problem
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
123 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 650 | 610 | 1000 | 1000 |  |  | Line O/L
124 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 0 | 85 | 165 | 220
125 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 0 | 0 |  |  | Line O/L
| Barisal Area Total |  |  |  |  | 1958 | 1958 | 655 | 726 | 1246 | 1328 | 0 | 142
126 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
127 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 32 |  | 20 | Engine problem
128 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 4 | 0 | 0 |  | 71 | Engine problem
129 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
130 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 34 | 34 | 16 | 42 |  | 8 | Engine problem
131 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 32 | 18 |  | Fuel shortage
132 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
133 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Fuel shortage
134 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 90 | 182 | 150 | 220 | 0 |  | Gas shortage
135 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 336 | 406 | 300 | 328 | 86 |  | Gas shortage
136 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 25 |  | 25 | Engine problem
137 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 20 | 0 | 20 | 22
138 | Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
139 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 11 | 11
140 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 8 | 0 | 8 | 44 |  | Fuel shortage
141 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 56 | 0 | 86 |  | 18 | Engine problem
142 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 0 | 100 | 100 |  | Fuel conservation
143 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 73 | 70 | 113 | 113
144 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 90 | 70 | 113 | 113
145 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 3 | 0 | 6 | 0
| Rajshahi Area Total |  |  |  |  | 2199 | 2129 | 646 | 830 | 729 | 1132 | 849 | 142
146 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 81 | 78 | 80 | 82
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
147 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 |  | 274 | Under maint
148 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
149 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
150 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 102 | 113 | 100 | 113
151 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 3 | 0 | 8 | 0
152 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 34 | 55 | 70 | 75 | 40 |  | Fuel shortage
| Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 21 | 0 | 12 | 0
| Rangpur Area Total |  |  |  |  | 830 | 750 | 241 | 246 | 270 | 270 | 80 | 359
| Total |  |  |  |  | 22512 | 21710 | 6655 | 9032 | 9826.6 | 12433 | 4433 | 3478
[6 empty] | 41757 | 41467 | 11852 | 16631 | 16631 | 11852
A. |  | 2022-10-25 | (Yesterday) |  |  |  |  | Tuesday
1 | Highest Generation : |  |  | 9032 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
2 | Minimum Generation : |  |  | 2828 | MW at | 3:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 9032 | MW
3 | Day peak Generation : |  |  | 6655 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 8847.86 | MW
4 | Evening peak Generation : |  |  | 9032 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 148.071 | MKWHr | By Solar | 1.1799 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Gas : | 87.961 | MKWHr |  | By Oil: | 27.8874 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 16.9274 | MKWHr |  | By Hydro: | 2.1806 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 4433 | MW | Dhaka | 3595.52 | 3595.52 |  | 0 |  | 18:00 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 3478 | MW | Chittagong | 979.5 | 979.5 |  | 0 |  | 19:00 |  | 0
|  |  | Total = |  |  | 7911 | MW | Khulna | 939.6 | 939.6 |  | 0 |  | 19:30 |  | 0
7 | Total Gas Supplied : |  |  | 824.42 | MMCFD |  |  | Rajshahi | 1009.5 | 1009.5 |  | 0 |  | 20:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 96227883.13 | ii) Oil : | Taka | 360932692.87 | Comilla | 509 | 509 |  | 0 |  | 21:00 |  | 0
|  | iii) Coal : |  | 146382055.45 | Total | Taka | 603542631.45 | Mymensingh | 716 | 716 |  | 0 |  | 22:00 |  | 0
9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0 | MKWHr. | Sylhet | 355 | 355 |  | 0 |  | 23:00 |  | 0
| ii) During Peak Demand : |  |  | 316 | MW (E to W) at | 19:00 | hrs | Barisal | 130.74 | 130.74 |  | 0 |  | 24:00 |  | 0
| iii) Maximum : |  |  | 50 | MW at | 8:00 | hrs | Rangpur | 613 | 613 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 27.3° C |  |  | Total | 8847.86 | 8847.86 |  | 0
B. |  | 2022-10-26 | (Today) |  |  |  | Wednesday |  |  | Probable max. temperature in Dhaka |  |  | 29.8° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 12900 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 467 | MW
2 | Maximum Generation (Generation end) |  |  |  | 12433 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 10000 | MW
4 | Reserve(Generation end) |  |  |  | - | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 211.4832 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 6593 | MW at | 5:00 | 108 | 49 | 71 | 71 | 57 | 52 | 18 | 0 | 41
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 10.7309 | MKWHr. | ii) HVDC Flow at Peak Time |  | 800 | MW at | 19:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.2038 | MKWHr. | iii) Maximum HVDC Flow : |  | 801 | MW at | 19:30 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 96.82 |  | (b) Today: | 96.78 |  | (c) Rule Curve: |  | 108.4
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2022-10-25
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 110 | 0 | 3 | 0 | 251 | 235 |  | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 60 | 0 | 0 | 0 | 101 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 130 | 122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 114 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 182 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 460 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1889 | 1094 | 2983 | 1324 | 182 | 825 | 0 | 15 | 541 | 96 | 0 | 0 | 0 | 0 | 0 | 96.87
2:00 | 0 | 0 | 0 | 110 | 0 | 3 | 0 | 237 | 211 |  | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 60 | 0 | 0 | 0 | 100 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 128 | 122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 115 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 132 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 460 | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1866 | 1017 | 2883 | 1308 | 132 | 782 | 0 | 15 | 542 | 94 | 0 | 0 | 10 | 0 | 0 | 96.86
3:00 | 0 | 0 | 0 | 110 | 0 | 3 | 0 | 235 | 211 |  | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 60 | 0 | 0 | 0 | 115 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 130 | 122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 114 | 0 | 0 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 237 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 167 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 460 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1856 | 972 | 2828 | 1290 | 167 | 710 | 0 | 15 | 540 | 94 | 0 | 0 | 12 | 0 | 0 | 96.85
4:00 | 0 | 0 | 0 | 110 | 0 | 3 | 0 | 234 | 213 |  | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 60 | 0 | 0 | 0 | 140 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 123 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 239 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 201 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 460 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1786 | 1071 | 2857 | 1217 | 201 | 776 | 0 | 15 | 541 | 95 | 0 | 0 | 12 | 0 | 0 | 96.84
5:00 | 0 | 0 | 0 | 110 | 0 | 3 | 0 | 234 | 223 |  | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 60 | 0 | 0 | 0 | 151 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 123 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 201 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 460 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1843 | 1074 | 2917 | 1268 | 201 | 797 | 0 | 0 | 543 | 96 | 0 | 0 | 12 | 0 | 0 | 96.83
6:00 | 0 | 0 | 0 | 110 | 0 | 3 | 0 | 235 | 232 |  | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 60 | 0 | 0 | 0 | 151 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 130 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 211 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 460 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1990 | 1142 | 3132 | 1399 | 211 | 871 | 0 | 0 | 542 | 97 | 0 | 0 | 12 | 0 | 0 | 96.82
7:00 | 0 | 0 | 0 | 170 | 0 | 8 | 0 | 249 | 312 |  | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 60 | 0 | 0 | 0 | 151 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 140 | 0 | 0 | 0 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 195 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 460 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 |  | 2399 | 1224 | 3623 | 1680 | 195 | 1081 | 0 | 0 | 539 | 98 | 0 | 0 | 16 | 14 | 0 | 96.81
8:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 289 | 323 |  | 0 | 190 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 60 | 0 | 0 | 0 | 131 | 0 | 0 | 0 |  | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 275 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 108 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 145 | 0 | 0 | 9 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 15 | 0 | 0 | 328 | 4 | 5 | 15 | 0 | 100 | 1 | 10 | 0 | 0 | 4 | 70 | 11 | 7 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 179 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 5 | 0 | 7 | 0 | 0 | 20 | 460 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 0 | 0 |  | 2805 | 1316 | 4121 | 1756 | 179 | 1186 | 0 | 290 | 542 | 99 | 0 | 0 | 24 | 45 | 0 | 96.81
9:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 354 | 321 |  | 0 | 190 | 0 | 0 | 0 | 5 | 80 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 60 | 0 | 0 | 0 | 131 | 0 | 0 | 0 |  | 0 | 0 | 0 | 44 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 37 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 153 | 0 | 18 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 158 | 0 | 0 | 9 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 25 | 0 | 0 | 349 | 24 | 52 | 68 | 0 | 100 | 40 | 65 | 0 | 0 | 25 | 40 | 35 | 45 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 195 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 16 | 0 | 0 | 84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 357 | 0 | 0 | 35 | 0 | 40 | 0 | 1 | 35 | 470 | 0 | 0 | 0 | 3 | 49 | 0 | 0 | 0 | 0 | 4 |  | 3449 | 1509 | 4958 | 2003 | 195 | 1223 | 0 | 753 | 554 | 99 | 0 | 0 | 28 | 103 | 0 | 96.8
10:00 | 0 | 0 | 0 | 180 | 0 | 31 | 0 | 377 | 359 |  | 0 | 225 | 0 | 0 | 0 | 30 | 140 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 70 | 0 | 0 | 0 | 150 | 0 | 0 | 0 |  | 0 | 0 | 0 | 44 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 35 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 145 | 0 | 18 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 158 | 0 | 0 | 10 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 25 | 0 | 0 | 407 | 24 | 52 | 68 | 2 | 105 | 54 | 68 | 0 | 0 | 25 | 15 | 35 | 14 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 274 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 19 | 0 | 0 | 84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 390 | 0 | 0 | 35 | 0 | 34 | 0 | 3 | 25 | 480 | 0 | 0 | 0 | 1 | 62 | 0 | 0 | 0 | 0 | 17 |  | 3802 | 1660 | 5462 | 2206 | 274 | 1357 | 0 | 821 | 564 | 110 | 0 | 0 | 30 | 100 | 0 | 96.8
11:00 | 0 | 0 | 0 | 180 | 0 | 41 | 0 | 412 | 311 |  | 0 | 225 | 0 | 0 | 0 | 30 | 208 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 70 | 0 | 0 | 0 | 151 | 0 | 0 | 0 |  | 3 | 0 | 0 | 44 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 305 | 0 | 8 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 120 | 0 | 18 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 158 | 19 | 0 | 10 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 25 | 0 | 0 | 363 | 30 | 54 | 62 | 1 | 172 | 36 | 70 | 0 | 0 | 25 | 25 | 36 | 31 | 35 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 |  | 378 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 19 | 0 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 367 | 0 | 0 | 39 | 0 | 34 | 0 | 3 | 60 | 550 | 0 | 0 | 0 | 2 | 81 | 0 | 0 | 0 | 0 | 18 |  | 3821 | 1954 | 5775 | 2251 | 378 | 1286 | 0 | 942 | 633 | 110 | 0 | 0 | 38 | 137 | 0 | #REF!
12:00 | 0 | 0 | 0 | 180 | 0 | 56 | 0 | 409 | 326 |  | 0 | 225 | 0 | 4 | 0 | 45 | 213 | 0 | 0 | 49 | 36 | 16 | 0 | 0 | 0 | 0 | 17 | 55 | 0 | 0 | 25 | 8 | 16 | 0 | 2 | 0 | 0 | 70 | 0 | 0 | 4 | 151 | 0 | 0 | 0 |  | 12 | 0 | 0 | 44 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 275 | 0 | 8 | 0 | 11 | 23 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 44 | 105 | 0 | 18 | 1 | 0 | 21 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 158 | 18 | 0 | 10 | 285 | 0 | 0 | 0 | 12 | 0 | 0 | 46 | 0 | 3 | 18 | 25 | 6 | 6 | 408 | 47 | 70 | 68 | 2 | 176 | 36 | 70 | 17 | 0 | 25 | 70 | 63 | 37 | 35 | 0 | 0 | 0 | 25 | 14 | 42 | 0 | 5 | 0 |  | 485 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 20 | 0 | 0 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 336 | 0 | 0 | 73 | 0 | 102 | 0 | 3 | 90 | 650 | 0 | 0 | 0 | 3 | 86 | 34 | 0 | 0 | 0 | 21 |  | 4282 | 2373 | 6655 | 2441 | 485 | 1304 | 0 | 1363 | 731 | 70 | 5 | 16 | 44 | 196 | 0 | 96.8
13:00 | 0 | 0 | 0 | 180 | 0 | 68 | 0 | 344 | 282 |  | 0 | 225 | 0 | 49 | 0 | 45 | 180 | 0 | 0 | 62 | 65 | 64 | 0 | 0 | 0 | 0 | 17 | 55 | 0 | 0 | 25 | 8 | 22 | 24 | 18 | 0 | 0 | 70 | 0 | 0 | 25 | 151 | 0 | 0 | 0 |  | 12 | 0 | 0 | 44 | 0 | 1 | 0 | 4 | 0 | 0 | 0 | 70 | 270 | 40 | 8 | 0 | 31 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 105 | 0 | 16 | 2 | 0 | 21 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 158 | 18 | 0 | 10 | 260 | 0 | 0 | 0 | 143 | 0 | 0 | 46 | 0 | 26 | 19 | 25 | 0 | 46 | 328 | 47 | 88 | 68 | 2 | 176 | 36 | 70 | 0 | 0 | 25 | 118 | 71 | 39 | 40 | 45 | 0 | 11 | 28 | 22 | 53 | 0 | 9 | 0 |  | 485 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 8 | 0 | 15 | 0 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 304 | 0 | 0 | 89 | 0 | 85 | 0 | 5 | 70 | 690 | 0 | 0 | 0 | 4 | 93 | 34 | 0 | 0 | 0 | 18 |  | 4715 | 2409 | 7124 | 2514 | 485 | 1221 | 0 | 1741 | 768 | 70 | 9 | 64 | 42 | 210 | 0 | 96.79
14:00 | 0 | 0 | 0 | 180 | 0 | 71 | 0 | 305 | 282 |  | 0 | 225 | 0 | 35 | 0 | 45 | 180 | 0 | 0 | 57 | 65 | 32 | 0 | 0 | 0 | 0 | 17 | 55 | 0 | 0 | 22 | 0 | 33 | 28 | 32 | 0 | 0 | 70 | 0 | 0 | 25 | 151 | 0 | 0 | 0 |  | 12 | 0 | 0 | 44 | 0 | 20 | 0 | 2 | 0 | 0 | 0 | 5 | 265 | 46 | 8 | 0 | 34 | 46 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 62 | 75 | 0 | 16 | 2 | 0 | 21 | 0 | 0 | 0 | 0 | 30 | 30 | 0 | 158 | 18 | 0 | 10 | 285 | 0 | 0 | 0 | 220 | 0 | 0 | 46 | 0 | 35 | 15 | 25 | 0 | 68 | 328 | 47 | 88 | 68 | 1 | 176 | 36 | 70 | 0 | 0 | 25 | 143 | 72 | 17 | 90 | 68 | 0 | 17 | 23 | 0 | 23 | 0 | 0 | 0 |  | 486 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 4 | 25 | 0 | 24 | 11 | 8 | 0 | 21 | 0 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 329 | 0 | 0 | 70 | 0 | 49 | 0 | 3 | 70 | 670 | 10 | 0 | 0 | 2 | 76 | 36 | 0 | 0 | 0 | 28 |  | 4806 | 2432 | 7238 | 2464 | 486 | 1326 | 0 | 1838 | 753 | 70 | 0 | 72 | 62 | 167 | 0 | 96.8
15:00 | 0 | 0 | 0 | 180 | 0 | 75 | 0 | 314 | 351 |  | 0 | 225 | 0 | 32 | 0 | 45 | 180 | 0 | 0 | 64 | 50 | 32 | 0 | 0 | 0 | 0 | 17 | 55 | 0 | 0 | 23 | 16 | 33 | 28 | 33 | 0 | 0 | 70 | 0 | 0 | 25 | 152 | 0 | 0 | 0 |  | 12 | 0 | 0 | 44 | 0 | 25 | 0 | 2 | 0 | 0 | 0 | 2 | 305 | 76 | 8 | 0 | 34 | 50 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 16 | 0 | 80 | 84 | 0 | 18 | 1 | 0 | 21 | 0 | 0 | 0 | 0 | 30 | 30 | 0 | 158 | 18 | 0 | 10 | 300 | 0 | 0 | 0 | 210 | 0 | 0 | 46 | 0 | 35 | 11 | 25 | 0 | 50 | 328 | 45 | 70 | 68 | 1 | 176 | 36 | 70 | 0 | 0 | 25 | 256 | 72 | 26 | 90 | 68 | 0 | 17 | 16 | 6 | 37 | 0 | 0 | 0 |  | 573 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 4 | 25 | 0 | 24 | 16 | 8 | 0 | 0 | 0 | 0 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 201 | 0 | 308 | 0 | 0 | 70 | 0 | 49 | 0 | 2 | 70 | 670 | 30 | 0 | 0 | 2 | 56 | 36 | 0 | 0 | 0 | 21 |  | 5127 | 2481 | 7608 | 2722 | 573 | 1396 | 0 | 1805 | 749 | 70 | 0 | 77 | 80 | 136 | 0 | 96.78
16:00 | 0 | 0 | 0 | 180 | 0 | 78 | 0 | 334 | 351 |  | 0 | 225 | 10 | 27 | 0 | 45 | 180 | 0 | 0 | 68 | 50 | 16 | 0 | 0 | 0 | 0 | 17 | 55 | 0 | 0 | 23 | 16 | 0 | 28 | 33 | 0 | 0 | 70 | 0 | 0 | 25 | 151 | 0 | 0 | 0 |  | 12 | 8 | 17 | 44 | 0 | 25 | 0 | 2 | 0 | 0 | 0 | 3 | 305 | 143 | 8 | 0 | 37 | 51 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 16 | 0 | 86 | 83 | 0 | 18 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 7 | 30 | 0 | 158 | 18 | 0 | 9 | 280 | 0 | 0 | 0 | 153 | 0 | 0 | 48 | 0 | 50 | 5 | 25 | 0 | 30 | 328 | 45 | 70 | 68 | 1 | 176 | 36 | 74 | 0 | 0 | 25 | 400 | 72 | 9 | 90 | 55 | 0 | 17 | 9 | 17 | 53 | 0 | 7 | 0 |  | 565 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 4 | 25 | 0 | 8 | 16 | 8 | 0 | 0 | 0 | 0 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 331 | 0 | 0 | 70 | 0 | 34 | 0 | 1 | 35 | 670 | 36 | 0 | 0 | 1 | 28 | 36 | 0 | 0 | 0 | 9 |  | 5254 | 2361 | 7615 | 2875 | 565 | 1418 | 0 | 1696 | 749 | 70 | 7 | 86 | 86 | 63 | 0 | 96.78
17:00 | 0 | 0 | 0 | 180 | 0 | 80 | 0 | 334 | 352 |  | 0 | 225 | 10 | 17 | 0 | 45 | 160 | 0 | 0 | 70 | 65 | 23 | 0 | 0 | 0 | 0 | 35 | 55 | 0 | 0 | 23 | 16 | 33 | 27 | 33 | 0 | 0 | 70 | 0 | 0 | 25 | 150 | 0 | 0 | 0 |  | 12 | 16 | 17 | 44 | 0 | 28 | 0 | 5 | 0 | 0 | 0 | 15 | 265 | 180 | 8 | 0 | 40 | 51 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 20 | 0 | 88 | 83 | 0 | 18 | 0 | 30 | 30 | 11 | 10 | 0 | 0 | 30 | 50 | 0 | 158 | 18 | 11 | 9 | 300 | 8 | 0 | 0 | 136 | 0 | 0 | 58 | 0 | 52 | 1 | 25 | 1 | 30 | 328 | 45 | 88 | 89 | 0 | 176 | 36 | 105 | 17 | 0 | 25 | 350 | 72 | 1 | 101 | 51 | 0 | 19 | 0 | 20 | 54 | 0 | 18 | 0 |  | 565 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 4 | 25 | 0 | 8 | 16 | 8 | 0 | 0 | 0 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 0 | 336 | 0 | 0 | 70 | 0 | 34 | 0 | 0 | 35 | 640 | 53 | 0 | 0 | 0 | 2 | 36 | 0 | 0 | 0 | 1 |  | 5500 | 2293 | 7793 | 2889 | 565 | 1519 | 0 | 1820 | 718 | 70 | 18 | 101 | 88 | 5 | 0 | 96.77
18:00 | 0 | 0 | 0 | 180 | 0 | 81 | 0 | 337 | 352 |  | 0 | 225 | 10 | 51 | 0 | 45 | 140 | 0 | 0 | 83 | 75 | 32 | 0 | 0 | 0 | 0 | 54 | 55 | 0 | 10 | 21 | 16 | 33 | 26 | 41 | 0 | 0 | 70 | 0 | 0 | 25 | 152 | 0 | 0 | 0 |  | 12 | 24 | 34 | 70 | 0 | 33 | 0 | 5 | 0 | 0 | 0 | 70 | 265 | 178 | 8 | 0 | 42 | 50 | 0 | 0 | 0 | 0 | 6 | 19 | 0 | 20 | 0 | 94 | 83 | 0 | 18 | 0 | 30 | 30 | 11 | 10 | 0 | 0 | 30 | 76 | 0 | 158 | 18 | 11 | 9 | 290 | 8 | 0 | 0 | 170 | 0 | 0 | 86 | 0 | 74 | 0 | 60 | 17 | 30 | 402 | 92 | 88 | 105 | 0 | 176 | 52 | 105 | 17 | 0 | 35 | 400 | 92 | 0 | 157 | 51 | 0 | 35 | 0 | 34 | 54 | 0 | 0 | 0 |  | 735 | 0 | 280 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 4 | 60 | 0 | 34 | 32 | 8 | 0 | 0 | 0 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 408 | 7 | 0 | 90 | 0 | 58 | 0 | 0 | 90 | 630 | 72 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 0 |  | 6158 | 2820 | 8978 | 3138 | 735 | 1628 | 0 | 2419 | 708 | 70 | 0 | 186 | 94 | 0 | 0 | 96.77
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 0 | 81 | 0 | 361 | 340 |  | 0 | 225 | 10 | 50 | 0 | 45 | 140 | 0 | 0 | 90 | 40 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 0 | 10 | 21 | 16 | 33 | 26 | 33 | 0 | 0 | 70 | 0 | 0 | 8 | 150 | 0 | 0 | 0 |  | 12 | 0 | 34 | 70 | 0 | 37 | 0 | 3 | 0 | 0 | 0 | 90 | 285 | 181 | 8 | 0 | 45 | 51 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 20 | 0 | 98 | 83 | 0 | 18 | 0 | 30 | 30 | 11 | 10 | 0 | 0 | 32 | 78 | 0 | 158 | 18 | 11 | 9 | 280 | 8 | 0 | 0 | 140 | 0 | 0 | 88 | 0 | 86 | 0 | 90 | 17 | 10 | 407 | 92 | 88 | 105 | 0 | 176 | 17 | 105 | 17 | 0 | 66 | 400 | 92 | 0 | 162 | 25 | 0 | 35 | 0 | 34 | 40 | 0 | 0 | 0 |  | 800 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 11 | 0 | 0 | 0 | 0 | 0 | 4 | 56 | 0 | 34 | 0 | 8 | 0 | 0 | 0 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 406 | 35 | 0 | 70 | 0 | 113 | 0 | 0 | 70 | 610 | 85 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 |  | 6075 | 2957 | 9032 | 3283 | 800 | 1619 | 0 | 2364 | 688 | 70 | 0 | 110 | 98 | 0 | 0 | 96.77
19:30 | 0 | 0 | 0 | 180 | 0 | 81 | 0 | 361 | 341 |  | 0 | 225 | 10 | 24 | 0 | 45 | 140 | 0 | 0 | 50 | 24 | 16 | 0 | 0 | 0 | 0 | 35 | 55 | 0 | 10 | 21 | 16 | 33 | 26 | 33 | 0 | 0 | 70 | 0 | 0 | 8 | 151 | 0 | 0 | 0 |  | 12 | 0 | 34 | 70 | 0 | 39 | 0 | 9 | 0 | 0 | 0 | 90 | 285 | 178 | 8 | 0 | 51 | 51 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 20 | 0 | 94 | 96 | 0 | 18 | 0 | 30 | 30 | 11 | 10 | 0 | 0 | 32 | 78 | 0 | 158 | 18 | 11 | 9 | 290 | 8 | 0 | 0 | 140 | 0 | 0 | 88 | 0 | 70 | 0 | 90 | 17 | 10 | 406 | 96 | 88 | 105 | 0 | 165 | 17 | 105 | 17 | 0 | 60 | 400 | 92 | 0 | 162 | 17 | 0 | 35 | 0 | 34 | 34 | 0 | 0 | 0 |  | 801 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 380 | 35 | 0 | 70 | 0 | 113 | 0 | 0 | 70 | 640 | 115 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 0 |  | 5962 | 3037 | 8999 | 3377 | 801 | 1640 | 0 | 2186 | 718 | 70 | 0 | 113 | 94 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 180 | 0 | 81 | 0 | 362 | 331 |  | 0 | 225 | 10 | 24 | 0 | 45 | 140 | 0 | 0 | 50 | 24 | 16 | 0 | 0 | 0 | 0 | 35 | 55 | 10 | 10 | 21 | 16 | 33 | 26 | 33 | 0 | 13 | 70 | 0 | 0 | 8 | 151 | 0 | 0 | 0 |  | 12 | 0 | 24 | 70 | 0 | 39 | 0 | 12 | 0 | 0 | 0 | 100 | 285 | 178 | 8 | 0 | 51 | 51 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 25 | 6 | 92 | 105 | 0 | 18 | 0 | 30 | 30 | 11 | 10 | 0 | 0 | 32 | 78 | 0 | 158 | 18 | 11 | 9 | 290 | 8 | 0 | 0 | 110 | 0 | 0 | 88 | 0 | 70 | 0 | 90 | 17 | 10 | 405 | 97 | 88 | 105 | 0 | 184 | 17 | 105 | 17 | 0 | 60 | 400 | 92 | 0 | 162 | 17 | 0 | 35 | 0 | 34 | 34 | 0 | 0 | 0 |  | 800 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 357 | 35 | 0 | 70 | 0 | 113 | 0 | 0 | 70 | 620 | 130 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 0 |  | 5986 | 3007 | 8993 | 3406 | 800 | 1625 | 0 | 2186 | 698 | 83 | 0 | 103 | 92 | 0 | 0 | 96.77
21:00 | 0 | 0 | 0 | 180 | 0 | 81 | 0 | 361 | 322 |  | 0 | 225 | 10 | 11 | 0 | 45 | 140 | 0 | 0 | 26 | 7 | 16 | 0 | 0 | 0 | 0 | 35 | 55 | 17 | 10 | 21 | 23 | 33 | 25 | 33 | 0 | 46 | 70 | 0 | 0 | 8 | 150 | 0 | 0 | 0 |  | 12 | 0 | 17 | 44 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 115 | 285 | 178 | 8 | 0 | 51 | 50 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 25 | 7 | 92 | 100 | 0 | 18 | 0 | 30 | 30 | 11 | 10 | 0 | 0 | 32 | 78 | 0 | 158 | 18 | 11 | 9 | 290 | 8 | 0 | 0 | 45 | 0 | 0 | 88 | 0 | 56 | 0 | 90 | 17 | 10 | 406 | 97 | 88 | 105 | 0 | 175 | 17 | 94 | 17 | 0 | 38 | 400 | 67 | 0 | 162 | 17 | 0 | 35 | 0 | 34 | 34 | 0 | 0 | 0 |  | 800 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 378 | 37 | 0 | 70 | 0 | 70 | 0 | 0 | 35 | 630 | 160 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 0 |  | 5776 | 2965 | 8741 | 3425 | 800 | 1681 | 0 | 1852 | 709 | 116 | 0 | 66 | 92 | 0 | 0 | 96.77
22:00 | 0 | 0 | 0 | 180 | 0 | 81 | 0 | 361 | 317 |  | 0 | 225 | 10 | 7 | 0 | 45 | 140 | 0 | 0 | 24 | 7 | 0 | 0 | 0 | 0 | 0 | 35 | 55 | 17 | 10 | 21 | 27 | 33 | 26 | 24 | 0 | 46 | 70 | 0 | 0 | 0 | 150 | 0 | 0 | 0 |  | 12 | 0 | 17 | 44 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 135 | 285 | 178 | 8 | 0 | 51 | 50 | 0 | 0 | 0 | 0 | 0 | 19 | 8 | 25 | 7 | 86 | 100 | 0 | 18 | 0 | 30 | 30 | 11 | 10 | 0 | 0 | 32 | 78 | 0 | 158 | 18 | 11 | 9 | 280 | 8 | 0 | 0 | 0 | 0 | 0 | 88 | 0 | 52 | 0 | 60 | 0 | 10 | 406 | 48 | 88 | 105 | 0 | 175 | 17 | 94 | 0 | 0 | 38 | 400 | 54 | 0 | 162 | 0 | 0 | 35 | 0 | 34 | 34 | 0 | 0 | 0 |  | 800 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 384 | 17 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 610 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5561 | 2824 | 8385 | 3455 | 800 | 1697 | 0 | 1493 | 688 | 116 | 0 | 50 | 86 | 0 | 0 | 96.77
23:00 | 0 | 0 | 0 | 180 | 0 | 81 | 0 | 361 | 311 |  | 0 | 225 | 10 | 7 | 0 | 45 | 140 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 55 | 17 | 10 | 21 | 28 | 33 | 26 | 24 | 0 | 46 | 70 | 0 | 0 | 0 | 151 | 0 | 0 | 0 |  | 12 | 0 | 17 | 44 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 240 | 260 | 178 | 8 | 0 | 51 | 50 | 0 | 0 | 0 | 0 | 0 | 19 | 8 | 25 | 7 | 94 | 102 | 0 | 18 | 0 | 30 | 30 | 11 | 10 | 0 | 0 | 32 | 78 | 0 | 158 | 18 | 11 | 9 | 270 | 8 | 0 | 0 | 0 | 0 | 0 | 88 | 0 | 51 | 0 | 60 | 0 | 0 | 407 | 48 | 88 | 105 | 0 | 175 | 17 | 90 | 0 | 0 | 38 | 400 | 55 | 0 | 129 | 0 | 0 | 35 | 0 | 34 | 34 | 0 | 0 | 0 |  | 800 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 295 | 0 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 580 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5588 | 2692 | 8280 | 3546 | 800 | 1593 | 0 | 1422 | 659 | 116 | 0 | 50 | 94 | 0 | 0 | 96.77
24:00 | 0 | 0 | 0 | 180 | 0 | 81 | 0 | 361 | 307 |  | 0 | 225 | 10 | 7 | 0 | 45 | 140 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 55 | 17 | 10 | 21 | 28 | 33 | 26 | 16 | 0 | 46 | 70 | 0 | 0 | 0 | 151 | 0 | 0 | 0 |  | 12 | 0 | 17 | 44 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 325 | 260 | 178 | 8 | 0 | 51 | 50 | 0 | 0 | 0 | 0 | 0 | 19 | 8 | 25 | 7 | 98 | 103 | 0 | 18 | 0 | 30 | 30 | 11 | 10 | 0 | 0 | 32 | 78 | 0 | 158 | 18 | 11 | 9 | 270 | 0 | 5 | 0 | 0 | 0 | 0 | 48 | 0 | 51 | 0 | 60 | 0 | 0 | 406 | 48 | 88 | 68 | 0 | 175 | 17 | 58 | 0 | 0 | 38 | 380 | 54 | 0 | 53 | 0 | 0 | 35 | 0 | 34 | 34 | 0 | 0 | 0 |  | 800 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 293 | 0 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 580 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5437 | 2519 | 7956 | 3486 | 800 | 1568 | 0 | 1210 | 661 | 116 | 0 | 17 | 98 | 0 | 0 | 96.77
KWH | 0 | 0 | 0 | 3811500 | 0 | 1056954 | 0 | 7786500 | 7166000 |  | 0 | 4816500 | 36131 | 330240 | 0 | 689744 | 2497383 | 0 | 0 | 775680 | 481968 | 257280 | 0 | 0 | 0 | 0 | 462240 | 818442 | 71718 | 61056 | 465500 | 216720 | 338800 | 303400 | 392640 | 0 | 572580 | 1608000 | 0 | 0 | 204321 | 3349832 | 0 | 0 | 0 |  | 167040 | 44544 | 183825 | 789120 | 0 | 218400 | 0 | 402720 | 0 | 0 | 0 | 1081600 | 6153000 | 2154000 | 117090 | 0 | 529488 | 656640 | 0 | 0 | 0 | 0 | 16296 | 193320 | 23940 | 209900 | 32110 | 1203840 | 1880640 | 0 | 269928 | 8100 | 222000 | 314040 | 98400 | 123552 | 0 | 0 | 457728 | 642240 | 0 | 3588110 | 243000 | 74360 | 149040 | 6298500 | 62688 | 5040 | 0 | 1497927 | 0 | 0 | 960000 | 0 | 659232 | 70470 | 737280 | 119520 | 381381 | 8050000 | 883200 | 1248000 | 1378327 | 16824 | 2757491 | 562634 | 1337339 | 112860 | 0 | 551040 | 4761000 | 1054080 | 229080 | 1586880 | 436582 | 0 | 343800 | 109762 | 332160 | 572760 | 0 | 46836 | 0 |  | 10730909 | 0 | 5527872 | 0 | 16320 | 0 | 0 | 0 | 0 | 0 | 0 | 329000 | 116900 | 0 | 0 | 0 | 0 | 0 | 23090 | 372200 | 0 | 364301 | 92236 | 59520 | 0 | 125280 | 0 | 0 | 1916945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2483655 | 0 | 7535636 | 153600 | 0 | 1064064 | 0 | 933628 | 0 | 23230 | 952416 | 15010500 | 1142264 | 0 | 0 | 22020 | 579600 | 393216 | 0 | 0 | 0 | 120790 |  | 97981833 | 50089192 | 148071025 | 57402750 | 10730909 | 30558207 | 0 | 26867407 | 16927445 | 2180580 | 46836 | 973175 | 1203840 | 1179876 | 0
Fuel Cost | 0 | 0 | 0 | 5679135 | 0 | 1405748.82 | 0 | 8175825 | 7739280 |  | 0 | 5249985 | 40105.41 | 3692083.2 | 0 | 9139108 | 2797068.96 | 0 | 0 | 11340441.6 | 6781289.76 | 4170508.8 | 0 | 0 | 0 | 0 | 5879692.8 | 11048967 | 961738.38 | 45792 | 349125 | 0 | 0 | 0 | 6678806.4 | 0 | 154596.6 | 434160 | 0 | 0 | 3340648.35 | 3483825.28 | 0 | 0 | 0 |  | 2179872 | 742993.92 | 3128701.5 | 10661011.2 | 0 | 2526888 | 0 | 1341057.6 | 0 | 0 | 0 | 1200576 | 6706770 | 2498640 | 151046.1 | 0 | 598321.44 | 978393.6 | 0 | 0 | 0 | 0 | 219181.2 | 264848.4 | 17955 | 367325 | 24082.5 | 8643571.2 | 2049897.6 | 0 | 367102.08 | 129114 | 304140 | 414532.8 | 171216 | 213744.96 | 0 | 0 | 887992.32 | 1464307.2 | 0 | 3623991.1 | 522450 | 110796.4 | 295099.2 | 6298500 | 47016 | 3830.4 | 0 | 20446703.55 | 0 | 0 | 12940800 | 0 | 9130363.2 | 823794.3 | 7608729.6 | 1632643.2 | 5060925.87 | 7406000 | 10739712 | 18046080 | 17435836.55 | 0 | 32372944.34 | 6127084.26 | 14215913.57 | 1531510.2 | 0 | 6491251.2 | 4380120 | 13650336 | 3310206 | 20137507.2 | 4968303.16 | 0 | 4490028 | 1311655.9 | 4972435.2 | 7543249.2 | 0 | 0 | 0 |  | 32192727 | 0 | 6191216.64 | 0 | 169891.2 | 0 | 0 | 0 | 0 | 0 | 0 | 368480 | 226786 | 0 | 0 | 0 | 0 | 0 | 403844.1 | 5821208 | 0 | 6032824.56 | 1559710.76 | 811257.6 | 0 | 259329.6 | 0 | 0 | 11137450.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2881039.8 | 0 | 7460279.64 | 2064384 | 0 | 12587877.12 | 0 | 11857075.6 | 0 | 256691.5 | 11562330.24 | 135244605 | 1165109.28 | 0 | 0 | 249046.2 | 6798708 | 6028001.28 | 0 | 0 | 0 | 0 |  | 394517028.58 | 263329873.57 | 657846902.15 | 61657098.32 | 32192727 | 34570784.81 | 0 | 345105725.79 | 146382055.45 | 588756.6 | 0 | 15826967.08 | 8643571.2 | 12879215.9 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 0 | 56 | 0 | 409 | 326 |  | 0 | 225 | 0 | 4 | 0 | 45 | 213 | 0 | 0 | 49 | 36 | 16 | 0 | 0 | 0 | 0 | 17 | 55 | 0 | 0 | 25 | 8 | 16 | 0 | 2 | 0 | 0 | 70 | 0 | 0 | 4 | 151 | 0 | 0 | 0 |  | 12 | 0 | 0 | 44 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 275 | 0 | 8 | 0 | 11 | 23 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 44 | 105 | 0 | 18 | 1 | 0 | 21 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 158 | 18 | 0 | 10 | 285 | 0 | 0 | 0 | 12 | 0 | 0 | 46 | 0 | 3 | 18 | 25 | 6 | 6 | 408 | 47 | 70 | 68 | 2 | 176 | 36 | 70 | 17 | 0 | 25 | 70 | 63 | 37 | 35 | 0 | 0 | 0 | 25 | 14 | 42 | 0 | 5 | 0 |  | 485 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 20 | 0 | 0 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 336 | 0 | 0 | 73 | 0 | 102 | 0 | 3 | 90 | 650 | 0 | 0 | 0 | 3 | 86 | 34 | 0 | 0 | 0 | 21 |  | 6655 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 0 | 81 | 0 | 361 | 340 | 0 | 0 | 225 | 10 | 50 | 0 | 45 | 140 | 0 | 0 | 90 | 40 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 0 | 10 | 21 | 16 | 33 | 26 | 33 | 0 | 0 | 70 | 0 | 0 | 8 | 150 | 0 | 0 | 0 | 0 | 12 | 0 | 34 | 70 | 0 | 37 | 0 | 3 | 0 | 0 | 0 | 90 | 285 | 181 | 8 | 0 | 45 | 51 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 20 | 0 | 98 | 83 | 0 | 18 | 0 | 30 | 30 | 11 | 10 | 0 | 0 | 32 | 78 | 0 | 158 | 18 | 11 | 9 | 280 | 8 | 0 | 0 | 140 | 0 | 0 | 88 | 0 | 86 | 0 | 90 | 17 | 10 | 407 | 92 | 88 | 105 | 0 | 176 | 17 | 105 | 17 | 0 | 66 | 400 | 92 | 0 | 162 | 25 | 0 | 35 | 0 | 34 | 40 | 0 | 0 | 0 |  | 800 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 11 | 0 | 0 | 0 | 0 | 0 | 4 | 56 | 0 | 34 | 0 | 8 | 0 | 0 | 0 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 406 | 35 | 0 | 70 | 0 | 113 | 0 | 0 | 70 | 610 | 85 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 |  | 9032 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 0 | 84 | 0 | 400 | 320 | 0 | 0 | 225 | 135 | 94 | 0 | 55 | 0 | 0 | 0 | 90 | 85 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 28 | 33 | 26 | 49 | 0 | 46 | 70 | 0 | 0 | 25 | 150 | 0 | 0 | 0 | 0 | 12 | 25 | 51 | 70 | 0 | 44 | 0 | 15 | 0 | 0 | 0 | 270 | 300 | 200 | 8 | 50 | 45 | 51 | 0 | 0 | 0 | 43 | 34 | 22 | 11 | 32 | 20 | 166 | 110 | 0 | 19 | 0 | 30 | 40 | 0 | 0 | 0 | 0 | 60 | 81 | 0 | 178 | 18 | 0 | 10 | 300 | 0 | 0 | 100 | 260 | 150 | 50 | 88 | 100 | 134 | 0 | 90 | 200 | 70 | 400 | 97 | 88 | 105 | 0 | 195 | 54 | 105 | 114 | 0 | 100 | 400 | 92 | 0 | 162 | 107 | 0 | 35 |  | 115 | 54 | 0 |  |  |  | 911 | 0 | 320 | 0 | 16 | 0 | 0 | 0 | 32 | 76 | 8 | 65 | 27 | 16 | 0 | 0 | 0 | 32 | 0 | 86 | 0 | 42 | 32 | 8 | 25 | 22 | 0 | 11 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 220 | 0 | 328 | 75 | 100 | 113 | 0 | 113 | 0 | 0 | 113 | 1000 | 220 |  | 0 |  |  | 75
Forecast for Day | 0 | 0 | 0 | 180 | 0 | 80 | 0 | 400 | 272 | 0 | 0 | 225 | 125 | 70 | 0 | 55 | 0 | 0 | 0 | 63 | 74 | 20 | 0 | 0 | 0 | 0 | 17 | 55 | 0 | 19 | 23 | 28 | 33 | 20 | 41 | 0 | 46 | 70 | 0 | 0 | 25 | 150 | 0 | 0 | 0 | 0 | 12 | 24 | 17 | 33 | 0 | 32 | 0 | 10 | 0 | 0 | 0 | 270 | 260 | 100 | 8 | 50 | 45 | 51 | 0 | 0 | 0 | 40 | 8 | 22 | 11 | 32 | 12 | 143 | 108 | 0 | 18 | 1.6 | 30 | 30 | 0 | 0 | 0 | 0 | 60 | 30 | 0 | 145 | 18 | 0 | 10 | 300 | 0 | 0 | 0 | 160 | 0 | 0 | 45 | 0 | 80 | 20 | 38 | 100 | 70 | 400 | 90 | 88 | 51 | 5 | 140 | 54 | 61 | 114 | 0 | 25 | 380 | 74 | 50 | 35 | 107 | 0 | 35 | 30 | 53 | 54 | 0 |  |  |  | 766 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 20 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 300 | 75 | 0 | 113 | 0 | 100 | 0 | 8 | 113 | 1000 | 165 |  | 0 | 6 | 100 | 70 |  |  |  | 12
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 0 | 81 | 0 | 402 | 272 | 0 | 0 | 225 | 125 | 10 | 0 | 45 | 140 | 0 | 0 | 37 | 7 | 20 | 0 | 0 | 0 | 0 | 17 | 35 | 0 | 10 | 23 | 28 | 33 | 20 | 22 | 0 | 46 | 70 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 33 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 270 | 270 | 173 | 8 | 0 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 19 | 5 | 32 | 0 | 76 | 74 | 0 | 18 | 1 | 30 | 30 | 0 | 0 | 0 | 0 | 35 | 30 | 0 | 166 | 18 | 0 | 9 | 290 | 0 | 0 | 0 | 8 | 0 | 0 | 46 | 0 | 9 | 0 | 38 | 0 | 6 | 407 | 47 | 88 | 51 | 1 | 69 | 23 | 51 | 17 | 9 | 19 | 350 | 70 | 13 | 35 | 0 | 0 | 35 | 13 | 30 | 54 | 0 | 0 | 0 | 0 | 564 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 287 | 17 | 0 | 33 | 0 | 90 | 0 | 1 | 50 | 540 | 162 | 0 | 0 | 2 | 40 | 0 | 0 | 0 | 0 | 7 | 0 |  |  |  |  | 27887418 |  | 0
27887418
| Minimum Generation |  | 2828 | 3:00
| Highest Generation |  | 9032 | 19:00
| Day Peak Generation |  | 6655 | 12:00
| Evening Peak Generation |  | 9032 | 19:00
| HVDC Max Flow |  | 801 | 19:30
| HVDC EvPeak Flow |  | 800 | 19:00
| Load factor L.F |  | 68.31% | [161 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2022-10-26
Till now the maximum generation is : - |  |  | 14782 | 21:00 | Hrs on | 2022-04-16
The Summary of Yesterday's |  | 2022-10-25 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 6655 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 6593 | MW
Evening Peak Generation : |  | 9032 | MW Hour : | 19:00 | Available Max Generation : |  | 12433 | MW
E.P. Demand (at gen end) : |  | 9032 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 12900 | MW
Maximum Generation : |  | 9032 | MW Hour : | 19:00 | Reserve(Generation end) |  | - | MW
Total Gen. (MKWH) : |  | 148.071 | System Load Factor : | 68.31% | Load Shed : |  | 467 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | 50 | MW at | 8:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2022-10-26
Actual : | 96.78 | Ft.(MSL) , | Rule curve : | 108.4 | Ft.( MSL )
Gas Consumed : | Total = | 824.42 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 96227883.13
: |  | Coal : | 146382055.45 | Oil : | 360932692.87 | Total : | 603542631.45
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4258.5905 |  |  | 108 | 2.536%
Chittagong Area | 0 | 0:00 | 1206.3846 |  |  | 49 | 4.062%
Khulna Area | 0 | 0:00 | 1592.3275 |  |  | 71 | 4.459%
Rajshahi Area | 0 | 0:00 | 1412.7911 |  |  | 71 | 5.026%
Cumilla Area | 0 | 0:00 | 1202.6695 |  |  | 57 | 4.739%
Mymensingh Area | 0 | 0:00 | 993.5847 |  |  | 52 | 5.234%
Sylhet Area | 0 | 0:00 | 444.0892 |  |  | 18 | 4.053%
Barisal Area | 0 | 0:00 | 362.0104 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 784.4999 |  |  | 41 | 5.226%
Total | 0 |  | 12256.9475 |  |  | 467
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 2
2) Ghorasal-3, 7
3) Ashuganj-5
4) Baghabari-71,100 MW
5) Raozan unit-1 & 2
6) Siddhirganj 210 MW .
7) Shajibazar 330 MW
8) Sirajganj-2
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Ashuganj 225 MW GT STG were synchronized at 12:04,14:45 respectively.
b) Bhola Nutun Biddut GT-2 & STG were synchronized at 13:11,16:06 respectively and STG tripped at 16:22
again synchronized at 17:52 and GT- synchronized at 19:16.
c) Meghnaghat Summit GT-2 & STG was synchronized at 15:58,02:23(26-10-22)respectively.
d) Bibiyana south STG was synchronized at 12:43.
e) Ashuganj(N) GT was synchronized at 12:41.
f) Ghorasal-Bhulta 230 kV Ckt-2 was switched on at 09:58.
g) Ashuganj-Kishoreganj 132 kV Ckt-1 was shut down from 12:30 to 13:01 for tree trimming of Ckt-2.
h) Ghorasal-Joydevpur 132 kV Ckt-1 was switched on at 11:02.
i) Dohazari-Cox's Bazar 132 kV Ckt-2 was shut down from 14:20 to 15:14 for tree trimming .
j) Ghorasal-Joydevpur 132 kV Ckt-1 was under shut down from 14:27 to 15:15 for relay testing.
k) Ghorasal-Joydevpur 132 kV Ckt-2 was under shut down since at 15:20 for relay testing.
l) Tongi-Bashundhara 132 kV Ckt was switched on at 16:14.
m) Patuakhali 132/33 kV T-2 transformer was under shut down from 16:01 to 16:54 due to 33 kV R-phase
bushing oil leakage.
n) Barisal(N)-Bhola 230 kV Ckt-2 was switched on at 19:23.
o) Madaripur-Shariatpur 132 kV Ckt-1 was switched on at 19:28.
p) Madaripur-Barisal(N) 132 kV Ckt-1 was switched on at 17:14.
q) Hasnabad-Sitalakhya 132 Ckt tripped at 02:10 showing dist Z1,B-phase,gen trip and was switched | [5 empty] | About 72 MW power interruption occurred under
on at 02:31(26-10-2022). | [5 empty] | Sitalakhya S/S area from 02:10 to 02:31.
r) Hasnabad-Brahmangaon 132 Ckt tripped at 02:10 showing dist Z1,3-phase,main protection at Hasnabad end and
s) Sylhet-Fenchuganj P/S 132 kV Ckt was under shut down since at 06:36(26-10-22) for D/W.
t) Cox's Bazar 132/33 kV T-3 transformer was under shut down since at 06:50(26-10-22) for C/M. | [5 empty] | About 30 MW power interruption occurred under
Cox's Bazar S/S area since at 06:50.
u) Madunaghat-Chandraghona 132 kV Ckt-2 was shut down since at 07:26 for A/M .
v) Ghorasal-Joydevpur 132 kV Ckt-2 was under shut down since at 07:35(26-10-22) for A/M.
| Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2022-10-25 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 3811500
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 81 | 1056954 | Engine problem
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 361 | 7786500
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 340 | 7166000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 4816500
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 50 | 330240 | Low demand
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 10 | 36131
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 0 | 0 | Under maint.
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 45 | 689744 | Engine problem
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 10 | 61056 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 90 | 775680 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 140 | 2497383
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 40 | 481968 | Low demand
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 462240
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 16 | 257280 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 818442
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 0 | 71718 | Engine problem
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 37 | 682220 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 338800
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 26 | 303400 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 33 | 392640 | Low demand
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 140 | 1497927 | Low demand
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 0 | 0 | Reserve
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 86 | 659232 | Low demand
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 88 | 1248000 | Engine problem
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 92 | 1054080 | Engine problem
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 1586880
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 109762
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 40 | 572760 | Engine problem
| Dhaka area Total |  |  |  | 5847 | 2434 | 39565037
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Machine problem
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 8 | 204321 | Low demand
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 70470
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 37 | 218400
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 70 | 2180580 | Low water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 150 | 3349832 | ST Under maint
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 105 | 1378327
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 44544 | Reserve
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 34 | 183825 | Low demand
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 70 | 789120 | Engine problem
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 90 | 737280 | Engine problem
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 0 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 3 | 402720
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 16824
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 176 | 2757491 | Low demand
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 17 | 562634 | Low demand
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 105 | 1337339
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 66 | 551040 | Low demand
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 25 | 436582 | Low demand
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 46836 | On test.
| Chattogram area Total |  |  |  | 2382 | 956 | 15268165
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 181 | 2154000 | FGMO
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 90 | 1081600 | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 285 | 6153000 | FGMO
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+136*1 | 284 | 0 | 0 | On test.
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 45 | 529488
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 51 | 656640
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 117090 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 0 | 0 | Gas shortage
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 10 | 381381 | Low demand
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Machine problem
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 17 | 119520 | Low demand
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 193320
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 0 | 23940
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 98 | 1203840
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 20 | 209900 | Engine problem
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 16296 | Reserve
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 0 | 32110 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 17 | 112860 | Low demand
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Fuel shortage
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 35 | 343800 | Engine problem
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 34 | 332160 | Low demand
| Cumilla Area Total |  |  |  | 3169 | 910 | 13660945
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 83 | 1880640 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 269928 | Engine problem
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 8100
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 88 | 960000 | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 92 | 883200 | Engine problem
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 229080
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 167040 | Engine problem
| Mymensingh Area Total |  |  |  | 614 | 293 | 4397988
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 30 | 222000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 314040 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Gas shortage
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 11 | 98400 | Gas shortage
| Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 10 | 123552 | Gas shortage
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 0 | 5040 | Engine problem
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 32 | 457728 | GT-9 Under maint.
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 78 | 642240
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 158 | 3588110
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 243000
| Sylhet 50MW PP (EPL) |  | NENP | 27*2 | 50 | 11 | 74360 | Gas shortage
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 8 | 62688 | Gas shortage
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 280 | 6298500 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 407 | 8050000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 9 | 149040
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 400 | 4761000
| Sylhet Area Total |  |  |  | 2477 | 1482 | 25089698
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Fuel shortage
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 800 | 10730909
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 0 | 16320 | Fuel shortage
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 320 | 5527872 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 0 | 0 | Fuel shortage
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 35 | 153600 | Low demand
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Fuel shortage
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 579600
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 0 | 0 | 0 | On test.
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 0 | 0 | 0 | 0 | On test.
| Khulna Area Total |  |  |  | 2384 | 1155 | 17008301
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Reserve
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 11 | 116900 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 20 | 329000 | Gas shortage
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 610 | 15010500
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 85 | 1142264
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Line O/L
| Barisal Area Total |  |  |  | 1958 | 726 | 16598664
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 4 | 23090
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contract Expired
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 34 | 364301 | Engine problem
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 92236 | Reserve
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 182 | 2483655 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 406 | 7535636
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 0 | 125280 | Engine problem
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 0 | 0 | Engine problem
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 8 | 59520 | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 56 | 372200 | Low demand
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Fuel conservation
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 70 | 1064064 | Low demand
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 70 | 952416 | Low demand
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 22020
| Rajshahi Area Total |  |  |  | 2129 | 830 | 13094418
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 78 | 1916945
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under maint.
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 933628
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 23230
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 55 | 393216 | Low demand
| Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 120790
| Rangpur Area Total |  |  |  | 750 | 246 | 3387809
| Total |  |  |  | 21710 | 9032 | 148071025
| Eastern Grid Total |  |  |  | 14489 | 6075 | 97981833
| Western Grid Total |  |  |  | 7221 | 2957 | 50089192
| National Grid Total |  |  |  | 21710 | 9032 | 148071025
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2022-10-25
| (a) ENTIRE EASTERN GRID : |  | 6155.02 | MW | (b) ENTIRE WESTERN GRID : |  | 2692.84 | MW
| i) Dhaka area |  | 3595.52 | MW | i) Khulna area |  | 939.6 | MW
| ii) Chittagong area |  | 979.5 | MW | ii) Rajshahi area |  | 1009.5 | MW
| iii) Comilla area |  | 509 | MW | iii) Barisal area |  | 130.74 | MW
| iv) Mymensingh area |  | 716 | MW | iv) Rangpur area |  | 613 | MW
| v) Sylhet area |  | 355 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 8847.86 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 15 | 20:00 | Chowmuhani | 56 | 20:00 | Kaptai | 4 | 18:00 | Nawabganj | 23.4 | 21:00 | Sholosohor | 28 | 11:00
2 | AKSML | 24 | 18:00 | Chuadanga | 74 | 18:00 | Kazla | 82 | 18:30 | Netrakona | 86 | 18:00 | Shyampur | 138 | 23:00
3 | Aftabnagar | 26.06 | 18:00 | Coxsbazar | 95 | 19:00 | Keranigonj | 60 | 18:00 | New | 65.6 | 12:00 | Siddhirganj | 98 | 18:00
4 | Agargaon | 61 | 13:00 | Cumilla(N) | 70 | 23:00 | Khagrachori | 24 | 19:00 | Niamatpur | 59 | 18:30 | Sirajganj | 87 | 19:00
5 | Agrabad | 56 | 18:00 | Cumilla(S) | 98 | 19:00 | Khulna | 65 | 19:30 | Noapara | 33 | 21:00 | Sonargaon | 79 | 19:00
6 | Amnura | 44 | 18:30 | Daudkandi | 61 | 23:00 | Khulshi | 148 | 18:30 | PHP | 10 | 18:00 | Sreemongol | 32 | 21:00
7 | Ashuganj | 57 | 19:00 | Dhaka | 28 | 13:00 | Kishoreganj | 78 | 21:00 | Pabna | 82 | 18:00 | Srinagar | 18.3 | 23:00
8 | BSRM | 2 | 09:00 | Dhamrai | 84 | 18:30 | Kodda | 239 | 15:00 | Palashbari | 89 | 18:00 | Sunamganj | 28 | 18:30
9 | Bagerhat | 45 | 20:00 | Dhanmondi | 84 | 13:00 | Kulaura | 28 | 18:00 | Panchagarh | 54 | 18:00 | Sylhet | 109 | 18:30
10 | Bakulia | 106 | 18:30 | Dohazari | 76 | 20:00 | Kurigram | 41 | 18:00 | Patuakhali | 44 | 20:00 | TK | 15.5 | 18:00
11 | Banani | 28 | 13:00 | Faridpur | 68 | 22:00 | Kushtia | 108 | 18:30 | Payra | 0.74 | 19:00 | Tangail | 138 | 20:00
12 | Bangabhaban | 13 | 13:00 | Fatullah | 57 | 16:00 | Lalbag | 78 | 13:00 | Postogola | 32 | 13:00 | Thakurgaon | 56 | 19:30
13 | Barapukuria | 42 | 18:00 | Fenchuganj | 31 | 18:00 | Lalmonirhat | 36 | 18:00 | Purbachal | 12 | 13:00 | Tongi | 93 | 17:00
14 | Barguna | 8 | 22:00 | Feni | 70 | 18:30 | Madanganj | 83 | 18:00 | Purbasadipur | 86 | 18:00 | Ullon | 35 | 14:00
15 | Barishal | 58 | 20:00 | GPH | 26 | 03:00 | Madaripur | 45 | 22:00 | Rahanpur_I | 17.8 | 18:00 | Uttara | 61 | 18:00
16 | Barishal-230 | 26 | 22:00 | Ghorashal | 44 | 23:00 | Madartek | 57 | 18:30 | Rahim | 30 | 15:00 | UttaraNew | 20 | 14:00
17 | Baroaulia | 63 | 19:00 | Goalpara | 12 | 11:00 | Madunaghat | 51 | 18:30 | Rajbari | 46 | 18:00 | Zigatola | 40 | 18:00
18 | Baroirhat | 24 | 22:00 | Gollamari | 48 | 13:00 | Magura | 42 | 18:30 | Rajendrapur | 84 | 18:30
19 | Bashundhara | 119 | 18:00 | Gopalganj | 25.2 | 22:00 | Mahasthangarh | 48 | 18:30 | Rajshahi | 107 | 19:00
20 | BashundharaCement | 6 | 12:00 | Gulshan | 84 | 13:00 | Manikganj | 63 | 21:00 | Rajshahi-230 | 24 | 18:30
21 | Beanibazar | 40 | 19:30 | Halishahar | 86 | 15:00 | Maniknagar | 51 | 18:00 | Ramganj | 30 | 23:00
22 | Benapole | 44 | 18:00 | HaripurSBU | 132 | 18:30 | Matarbari | 32 | 20:00 | Rampur | 29 | 15:00
23 | Bhaluka | 102 | 18:30 | Hasnabad | 49 | 16:00 | Matuail | 52 | 10:00 | Rangamati | 11 | 18:30
24 | Bhandaria | 9 | 21:00 | Hathazari | 56 | 18:00 | Millgate | 52 | 13:00 | Rangpur | 112 | 18:00
25 | Bhangura | 24 | 18:00 | Ishurdi | 56 | 18:30 | Mirpur | 94 | 18:00 | Ruppur | 4.4 | 11:00
26 | Bheramara(GK) | 39 | 19:00 | Jaldhaka | 42 | 18:30 | Mirsorai | 2 | 17:00 | SSM | 0 | 00:00
27 | Bhulta | 188 | 19:00 | Jamalpur | 109 | 18:00 | Mithapukur | 30 | 18:00 | Saidpur | 79 | 18:30
28 | Bog-Sherpur | 42 | 18:00 | Jashore | 106 | 18:00 | Modern | 0 | 00:00 | Satkhira | 81 | 18:30
29 | Bogura | 119 | 18:30 | Jhenaidah | 91 | 18:00 | Mogbazar | 93 | 15:00 | Satmasjid | 67 | 14:00
30 | Borhanuddin | 16 | 16:00 | Joydebpur | 117 | 21:00 | Mongla | 20 | 15:00 | Savar | 147 | 12:00
31 | Brahmanbaria | 92 | 23:00 | Joypurhat | 43 | 18:30 | Motijheel | 28 | 13:00 | Shahjadpur | 73 | 18:30
32 | Cantonment | 102 | 13:00 | Juldah | 22 | 18:00 | Munshiganj | 57 | 22:00 | Shahjibazar | 87 | 18:30
33 | Chandpur | 24.5 | 20:00 | KSRM | 38 | 00:00 | Mymensingh | 154 | 18:30 | Shahmirpur | 40.5 | 19:00
34 | Chandraghona | 26 | 18:00 | Kabirpur | 222 | 18:30 | Naogaon | 84 | 18:30 | Shariatpur | 22 | 22:00
35 | Chapai | 58 | 18:30 | Kachua | 20 | 18:30 | Narail | 22 | 18:30 | Sherpur | 92 | 18:30
36 | Charsaidpur | 34 | 23:00 | Kallyanpur | 57 | 21:00 | Narinda | 48 | 15:00 | Shikalbaha | 22 | 18:30
37 | Chauddagram | 23 | 18:00 | Kalurghat | 22 | 09:00 | Narshingdi | 99 | 21:00 | Shikalbaha-230 | N/A | N/A
38 | Chhatak | 16 | 20:00 | Kamrangirchar | 64 | 18:00 | Natore | 99 | 18:00 | Shitalakhya | 103 | 18:00
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2022-10-25 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Bhulta | 405 | 01:00 | 384 | 00:00 | Kaliakoir | 406 | 07:00 | 390 | 16:00
| Bibiana | 413 | 02:00 | 396 | 23:00 | Payra | 428 | 02:00 | 421 | 12:00
| BIPTC | 412 | 02:00 | 397 | 19:00 | Rahanpur_I | 410 | 18:30 | 370 | 07:00
| Gopalganj_I | 435 | 04:00 | 420 | 13:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 240 | 02:00 | 223 | 12:00 | Hasnabad | 239 | 01:00 | 224 | 12:00
| AKSML | 238 | 09:00 | 225 | 07:00 | Hathazari | 238 | 08:00 | 230 | 00:00
| Aminbazar | 240 | 00:00 | 225 | 11:00 | Ishurdi | 246 | 02:00 | 235 | 11:00
| Ashuganj | 245 | 00:00 | 237 | 11:00 | Jhenaidah | 247 | 04:00 | 231 | 12:00
| Baghabari | 240 | 02:00 | 231 | 18:00 | Kaliakoir | 231 | 09:00 | 225 | 07:00
| Barapukuria | 225 | 05:00 | 212 | 22:00 | Keranigonj | 239 | 02:00 | 223 | 12:00
| Barishal | 258 | 04:00 | 235 | 12:00 | Khulna(S) | 250 | 04:00 | 234 | 12:00
| Bheramara | 245 | 02:00 | 231 | 18:00 | Maniknagar | 238 | 01:00 | 226 | 11:00
| Bhulta | 239 | 00:00 | 228 | 11:00 | Meghnaghat | 242 | 06:00 | 232 | 10:00
| Bibiana | 243 | 02:00 | 234 | 12:00 | Mirsorai | 237 | 13:00 | 230 | 00:00
| BIPTC | 246 | 02:00 | 232 | 18:00 | Rajshahi | 251 | 01:00 | 233 | 18:00
| Bogura | 233 | 04:00 | 224 | 18:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 264 | 04:00 | 236 | 12:00 | Rampura | 238 | 02:00 | 223 | 09:00
| BSRM | 238 | 08:00 | 233 | 07:00 | Shikalbaha | 238 | 13:00 | 229 | 07:00
| Cumilla(N) | 240 | 02:00 | 231 | 12:00 | Shyampur | 239 | 02:00 | 224 | 12:00
| Fenchuganj | 243 | 02:00 | 237 | 12:00 | Siddhirganj | 238 | 03:00 | 228 | 12:00
| Ghorashal | N/A | N/A | N/A | N/A | Sirajgonj | 235 | 02:00 | 228 | 18:00
| GPH | 237 | 15:00 | 228 | 04:00 | Tongi | 240 | 00:00 | 225 | 11:00
| Haripur | 237 | 00:00 | 226 | 12:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 135 | 00:00 | 125 | 11:00 | Lalbag | 137 | 02:00 | 131 | 12:00
| Agargaon | 138 | 00:00 | 127 | 12:00 | Lalmonirhat | 136 | 03:00 | 127 | 18:00
| Agrabad | 138 | 08:00 | 134 | 00:00 | Madanganj | 140 | 00:00 | 135 | 21:00
| AKS | 136 | 02:00 | 130 | 17:00 | Madaripur | 146 | 02:00 | 137 | 18:00
| Aminbazar | 138 | 03:00 | 128 | 11:00 | Madartek | 136 | 00:00 | 126 | 11:00
| Amnura | 134 | 01:00 | 130 | 20:00 | Madunaghat | 138 | 01:00 | 135 | 00:00
| Ashuganj | 141 | 00:00 | 137 | 11:00 | Magura | 143 | 02:00 | 132 | 18:00
| Bagerhat | 145 | 04:00 | 134 | 12:00 | Mahasthangarh | 141 | 02:00 | 132 | 22:00
| Bakulia | 139 | 08:00 | 134 | 00:00 | Manikganj | 139 | 00:00 | 127 | 21:00
| Banani | 142 | 00:00 | 128 | 12:00 | Maniknagar | 136 | 00:00 | 126 | 12:00
| Bangabhaban | 136 | 00:00 | 126 | 12:00 | Matarbari | 137 | 08:00 | 122 | 20:00
| Barapukuria | 138 | 05:00 | 125 | 08:00 | Matuail | 140 | 00:00 | 134 | 12:00
| Barguna | 139 | 00:00 | 136 | 10:00 | Millgate | 140 | 02:00 | 128 | 11:00
| Barishal | 148 | 04:00 | 133 | 12:00 | Mirpur | 138 | 02:00 | 127 | 12:00
| Barishal-230 | 147 | 04:00 | 134 | 12:00 | Mithapukur | 140 | 04:00 | 130 | 22:00
| Baroaulia | 140 | 07:00 | 134 | 19:00 | Modern | 138 | 09:00 | 134 | 03:00
| Baroirhat | 140 | 00:00 | 135 | 22:00 | Mogbazar | 137 | 00:00 | 126 | 12:00
| Bashundhara | 141 | 02:00 | 128 | 11:00 | Mongla | 145 | 04:00 | 133 | 12:00
| BashundharaCement | 140 | 00:00 | 135 | 21:00 | Motijheel | 136 | 00:00 | 126 | 12:00
| Beanibazar | 135 | 00:00 | 131 | 12:00 | Munshiganj | 140 | 00:00 | 131 | 13:00
| Benapole | 140 | 00:00 | 130 | 18:00 | Mymensingh | 139 | 00:00 | 126 | 17:00
| Bhaluka | 138 | 00:00 | 125 | 17:00 | Naogaon | 140 | 02:00 | 132 | 22:00
| Bhandaria | 144 | 00:00 | 136 | 12:00 | Narail | 142 | 02:00 | 131 | 18:00
| Bhangura | 146 | 02:00 | 138 | 18:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bheramara | 141 | 02:00 | 135 | 12:00 | Narshingdi | 140 | 00:00 | 131 | 19:00
| Bheramara(GK) | 140 | 02:00 | 135 | 11:00 | Natore | 139 | 02:00 | 132 | 22:00
| Bhulta | 139 | 00:00 | 130 | 19:00 | Nawabganj | 136 | 00:00 | 130 | 11:00
| Bog-Sherpur | 144 | 02:00 | 134 | 22:00 | Netrakona | 139 | 00:00 | 124 | 17:00
| Bogura | 143 | 04:00 | 136 | 17:00 | New | 140 | 00:00 | 129 | 11:00
| Bogura-230 | 143 | 04:00 | 136 | 21:00 | Niamatpur | 140 | 02:00 | 131 | 09:00
| Brahmanbaria | 139 | 00:00 | 132 | 11:00 | Noapara | 143 | 03:00 | 132 | 12:00
| Cantonment | 138 | 02:00 | 126 | 12:00 | Pabna | 140 | 02:00 | 134 | 11:00
| Chandpur | 144 | 00:00 | 137 | 14:00 | Palashbari | 137 | 00:00 | 130 | 18:00
| Chandraghona | 139 | 09:00 | 136 | 01:00 | Panchagarh | 132 | 02:00 | 119 | 08:00
| Chapai | 135 | 01:00 | 129 | 12:00 | Patuakhali | 138 | 04:00 | 136 | 03:00
| Charsaidpur | 141 | 00:00 | 135 | 21:00 | Payra | 139 | 04:00 | 137 | 12:00
| Chauddagram | 141 | 05:00 | 136 | 22:00 | PHP | 141 | 02:00 | 135 | 22:00
| Chhatak | 135 | 00:00 | 124 | 02:00 | Postogola | 139 | 02:00 | 132 | 09:00
| Chowmuhani | 140 | 00:00 | 136 | 22:00 | Purbachal | 142 | 01:00 | 129 | 11:00
| Chuadanga | 141 | 04:00 | 129 | 18:00 | Purbasadipur | 133 | 04:00 | 124 | 22:00
| Coxsbazar | 136 | 08:00 | 118 | 15:00 | Rahim | 137 | 13:00 | 135 | 11:00
| Cumilla(N) | 143 | 00:00 | 137 | 23:00 | Rajbari | 144 | 04:00 | 135 | 17:00
| Cumilla(S) | 143 | 00:00 | 128 | 16:00 | Rajendrapur | 141 | 00:00 | 125 | 16:00
| Daudkandi | 141 | 00:00 | 135 | 22:00 | Rajshahi | 134 | 02:00 | 129 | 22:00
| Dhaka | 136 | 00:00 | 126 | 11:00 | Rajshahi-230 | 134 | 02:00 | 129 | 18:00
| Dhamrai | 137 | 00:00 | 126 | 16:00 | Ramganj | 142 | 07:00 | 134 | 23:00
| Dhanmondi | 141 | 00:00 | 134.7 | 12:00 | Rampur | 137 | 09:00 | 134 | 00:00
| Dohazari | 137 | 13:00 | 120 | 13:00 | Rampura | 136 | 07:00 | 125 | 11:00
| Faridpur | 142 | 04:00 | 135 | 18:00 | Rangamati | 139 | 08:00 | 136 | 00:00
| Fatullah | 138 | 00:00 | 131 | 11:00 | Rangpur | 136 | 02:00 | 126 | 22:00
| Fenchuganj | 138 | 05:00 | 134 | 11:00 | Ruppur | 140 | 02:00 | 136 | 11:00
| Feni | 142 | 01:00 | 137 | 22:00 | Saidpur | 134 | 02:00 | 125 | 18:00
| Ghorashal | 144 | 00:00 | 138 | 12:00 | Satkhira | 142 | 03:00 | 131 | 18:00
| Goalpara | 143 | 04:00 | 133 | 13:00 | Satmasjid | 137 | 00:00 | 127 | 12:00
| Gollamari | 144 | 04:00 | 134 | 12:00 | Savar | 137 | 02:00 | 126 | 12:00
| Gopalganj | 145 | 04:00 | 136 | 12:00 | Shahjadpur | 148 | 01:00 | 140 | 11:00
| Gopalganj_I | 144 | 04:00 | 137 | 13:00 | Shahjibazar | 140 | 00:00 | 135 | 11:00
| Gulshan | 134 | 00:00 | 126 | 11:00 | Shahmirpur | 137 | 09:00 | 133 | 01:00
| Halishahar | 138 | 08:00 | 133 | 07:00 | Shariatpur | 145 | 02:00 | 136 | 12:00
| Haripur | 140 | 00:00 | 135 | 10:00 | Sherpur | 139 | 01:00 | 125 | 14:00
| HaripurSBU | 141 | 00:00 | 135 | 11:00 | Shikalbaha | 139 | 08:00 | 135 | 00:00
| Hasnabad | 138 | 00:00 | 131 | 09:00 | Shikalbaha-230 | 139 | 08:00 | 135 | 07:00
| Hathazari | 140 | 08:00 | 134 | 05:00 | Shitalakhya | 137 | 00:00 | 130 | 09:00
| Ishurdi | 142 | 02:00 | 135 | 11:00 | Sholosohor | 138 | 08:00 | 134 | 00:00
| Jaldhaka | 135 | 04:00 | 123 | 22:00 | Shyampur | 136 | 00:00 | 130 | 11:00
| Jamalpur | 138 | 06:00 | 126 | 17:00 | Shyampur-230 | 137 | 00:00 | 130 | 12:00
| Jashore | 140 | 00:00 | 130 | 12:00 | Siddhirganj | 140 | 00:00 | 134 | 11:00
| Jhenaidah | 142 | 01:00 | 133 | 12:00 | Sirajganj | 142 | 00:00 | 135 | 11:00
| Jhenaidah-230 | 143 | 04:00 | 133 | 12:00 | Sonargaon | 140 | 00:00 | 134 | 22:00
| Joydebpur | 145 | 00:00 | 136 | 10:00 | Sreemongol | 140 | 01:00 | 135 | 10:00
| Joypurhat | 139 | 02:00 | 133 | 08:00 | Srinagar | 136 | 00:00 | 131 | 12:00
| Juldah | 138 | 08:00 | 133 | 00:00 | SSM | 142 | 07:00 | 136 | 00:00
| Kabirpur | 140 | 00:00 | 126 | 12:00 | Sunamganj | 134 | 00:00 | 130 | 14:00
| Kachua | 140 | 15:00 | 136 | 22:00 | Sylhet | 135 | 00:00 | 132 | 12:00
| Kaliakoir | 137 | 07:00 | 129 | 16:00 | Tangail | 139 | 00:00 | 127 | 17:00
| Kallyanpur | 138 | 00:00 | 128 | 12:00 | Thakurgaon | 132 | 02:00 | 120 | 22:00
| Kalurghat | 139 | 08:00 | 135 | 00:00 | TK | 139 | 08:00 | 132 | 18:00
| Kamrangirchar | 138 | 02:00 | 130 | 12:00 | Tongi | 141 | 00:00 | 129 | 11:00
| Kaptai | 138 | 08:00 | 135 | 00:00 | Ullon | 136 | 00:00 | 125 | 11:00
| Kazla | 135 | 00:00 | 126 | 12:00 | Uttara | 139 | 00:00 | 127 | 12:00
| Keranigonj | 137 | 02:00 | 131 | 12:00 | UttaraNew | 137 | 01:00 | 129 | 11:00
| Khagrachori | 137 | 00:00 | 135 | 07:00 | Zigatola | 138 | 02:00 | 130 | 12:00
| Khulna | 143 | 05:00 | 133 | 12:00
| Khulna(S) | 145 | 04:00 | 134 | 12:00
| Khulshi | 136 | 08:00 | 132 | 00:00
| Kishoreganj | 139 | 00:00 | 126 | 13:00
| Kodda | 143 | 13:00 | 125 | 15:00
| KSRM | 137 | 08:00 | 132 | 06:00
| Kulaura | 138 | 02:00 | 134 | 11:00
| Kurigram | 136 | 01:00 | 125 | 18:00
| Kushtia | 140 | 00:00 | 134 | 12:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2022-10-25
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 482 | 5437 | 2519 | 7956 |  |  |  | QF-LDC-11
0:30 | 339 | 3663 | 1806.5 | 5469.5 | Date: | 2022-10-25
1:00 | 196 | 1889 | 1094 | 2983
1:30 | 195 | 1877.5 | 1055.5 | 2933
2:00 | 194 | 1866 | 1017 | 2883
2:30 | 227 | 1861 | 994.5 | 2855.5 | [5 empty] | Gen. at Eve. Peak | 9032 | 9032 MW (19:00 )
3:00 | 260 | 1856 | 972 | 2828 | [6 empty] | 19:00
3:30 | 315 | 1821 | 1021.5 | 2842.5 | [5 empty] | Gen. at Day Peak | 6655 | 6655 MW (12:00 )
4:00 | 370 | 1786 | 1071 | 2857 | [6 empty] | 12:00
4:30 | 345 | 1814.5 | 1072.5 | 2887 | [5 empty] | Highest Generation | 9032
5:00 | 320 | 1843 | 1074 | 2917 | [6 empty] | 19:00
5:30 | 307 | 1916.5 | 1108 | 3024.5
6:00 | 294 | 1990 | 1142 | 3132
6:30 | 219 | 2194.5 | 1183 | 3377.5
7:00 | 144 | 2399 | 1224 | 3623
7:30 | 97 | 2602 | 1270 | 3872
8:00 | 50 | 2805 | 1316 | 4121
8:30 | 78 | 3127 | 1412.5 | 4539.5
9:00 | 106 | 3449 | 1509 | 4958
9:30 | 188 | 3625.5 | 1584.5 | 5210
10:00 | 270 | 3802 | 1660 | 5462
10:30 | 450 | 3811.5 | 1807 | 5618.5
11:00 | 630 | 3821 | 1954 | 5775
11:30 | 710 | 4051.5 | 2163.5 | 6215
12:00 | 790 | 4282 | 2373 | 6655
12:30 | 699 | 4498.5 | 2391 | 6889.5
13:00 | 608 | 4715 | 2409 | 7124
13:30 | 544 | 4760.5 | 2420.5 | 7181
14:00 | 480 | 4806 | 2432 | 7238
14:30 | 535 | 4966.5 | 2456.5 | 7423
15:00 | 590 | 5127 | 2481 | 7608
15:30 | 550 | 5190.5 | 2421 | 7611.5
16:00 | 510 | 5254 | 2361 | 7615
16:30 | 440 | 5377 | 2327 | 7704
17:00 | 370 | 5500 | 2293 | 7793
17:30 | 277 | 5829 | 2556.5 | 8385.5
18:00 | 184 | 6158 | 2820 | 8978
18:30 | 250 | 6116.5 | 2888.5 | 9005
19:00 | 316 | 6075 | 2957 | 9032
19:30 | 400 | 5962 | 3037 | 8999
20:00 | 332 | 5986 | 3007 | 8993 |  |  |  | Executive Engineer
20:30 | 386 | 5881 | 2986 | 8867 |  |  |  | Network Operation Division
21:00 | 440 | 5776 | 2965 | 8741
21:30 | 448 | 5668.5 | 2894.5 | 8563
22:00 | 456 | 5561 | 2824 | 8385 |  |  |  |  | Page 6 of 7
22:30 | 465 | 5574.5 | 2758 | 8332.5
23:00 | 474 | 5588 | 2692 | 8280
23:30 | 478 | 5512.5 | 2605.5 | 8118
24:00 | 482 | 5437 | 2519 | 7956
9032 MW (19:00 )
6655 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2022-10-25 |  | Energy |  | 148071025
[13 empty] | 2022-10-25 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 3486 | 800 | 1568 | 0 | 1210 | 661 | 116 | 0 | 17 | 98 | 0 | 792
0:30 | 2405 | 491 | 1196.5 | 0 | 612.5 | 601 | 106 | 0 | 8.5 | 49 | 0 | 396 | Date: | 2022-10-25
1:00 | 1324 | 182 | 825 | 0 | 15 | 541 | 96 | 0 | 0 | 0 | 0 | 0
1:30 | 1316 | 157 | 803.5 | 0 | 15 | 541.5 | 95 | 0 | 0 | 5 | 0 | 0 | [8 empty] | Total Energy | 148.071 | Total Energy Gen 148.071 MKWHr Energy Not Served 0.570 MKWHr Energy Requirement 148.641 MKWHr
2:00 | 1308 | 132 | 782 | 0 | 15 | 542 | 94 | 0 | 0 | 10 | 0 | 0 | [8 empty] | Energy not Served | 0.57024
2:30 | 1299 | 149.5 | 746 | 0 | 15 | 541 | 94 | 0 | 0 | 11 | 0 | 0 | [8 empty] | Energy Requirement | 148.6413
3:00 | 1290 | 167 | 710 | 0 | 15 | 540 | 94 | 0 | 0 | 12 | 0 | 0
3:30 | 1253.5 | 184 | 743 | 0 | 15 | 540.5 | 94.5 | 0 | 0 | 12 | 0 | 0 | [6 empty] | Shortage
4:00 | 1217 | 201 | 776 | 0 | 15 | 541 | 95 | 0 | 0 | 12 | 0 | 0
4:30 | 1242.5 | 201 | 786.5 | 0 | 7.5 | 542 | 95.5 | 0 | 0 | 12 | 0 | 0
5:00 | 1268 | 201 | 797 | 0 | 0 | 543 | 96 | 0 | 0 | 12 | 0 | 0
5:30 | 1333.5 | 206 | 834 | 0 | 0 | 542.5 | 96.5 | 0 | 0 | 12 | 0 | 0
6:00 | 1399 | 211 | 871 | 0 | 0 | 542 | 97 | 0 | 0 | 12 | 0 | 0
6:30 | 1539.5 | 203 | 976 | 0 | 0 | 540.5 | 97.5 | 0 | 0 | 14 | 7 | 0 |  |  |  |  | Coal
7:00 | 1680 | 195 | 1081 | 0 | 0 | 539 | 98 | 0 | 0 | 16 | 14 | 0
7:30 | 1718 | 187 | 1133.5 | 0 | 145 | 540.5 | 98.5 | 0 | 0 | 20 | 29.5 | 0 |  |  |  | Oil |  |  |  | ,
8:00 | 1756 | 179 | 1186 | 0 | 290 | 542 | 99 | 0 | 0 | 24 | 45 | 0
8:30 | 1879.5 | 187 | 1204.5 | 0 | 521.5 | 548 | 99 | 0 | 0 | 26 | 74 | 0
9:00 | 2003 | 195 | 1223 | 0 | 753 | 554 | 99 | 0 | 0 | 28 | 103 | 0
9:30 | 2104.5 | 234.5 | 1290 | 0 | 787 | 559 | 104.5 | 0 | 0 | 29 | 101.5 | 0
10:00 | 2206 | 274 | 1357 | 0 | 821 | 564 | 110 | 0 | 0 | 30 | 100 | 0
10:30 | 2228.5 | 326 | 1321.5 | 0 | 881.5 | 598.5 | 110 | 0 | 0 | 34 | 118.5 | 0
11:00 | 2251 | 378 | 1286 | 0 | 942 | 633 | 110 | 0 | 0 | 38 | 137 | 0
11:30 | 2346 | 431.5 | 1295 | 0 | 1152.5 | 682 | 90 | 2.5 | 8 | 41 | 166.5 | 0
12:00 | 2441 | 485 | 1304 | 0 | 1363 | 731 | 70 | 5 | 16 | 44 | 196 | 0
12:30 | 2477.5 | 485 | 1262.5 | 0 | 1552 | 749.5 | 70 | 7 | 40 | 43 | 203 | 0
13:00 | 2514 | 485 | 1221 | 0 | 1741 | 768 | 70 | 9 | 64 | 42 | 210 | 0
13:30 | 2514 | 485 | 1221 | 0 | 1741 | 768 | 70 | 9 | 64 | 42 | 210 | 0
14:00 | 2514 | 485 | 1221 | 0 | 1741 | 768 | 70 | 9 | 64 | 42 | 210 | 0
14:30 | 2618 | 529 | 1308.5 | 0 | 1773 | 758.5 | 70 | 4.5 | 70.5 | 61 | 173 | 0
15:00 | 2722 | 573 | 1396 | 0 | 1805 | 749 | 70 | 0 | 77 | 80 | 136 | 0
15:30 | 2798.5 | 569 | 1407 | 0 | 1750.5 | 749 | 70 | 3.5 | 81.5 | 83 | 99.5 | 0
16:00 | 2875 | 565 | 1418 | 0 | 1696 | 749 | 70 | 7 | 86 | 86 | 63 | 0
16:30 | 2889 | 565 | 1468.5 | 0 | 1758 | 733.5 | 70 | 12.5 | 93.5 | 87 | 34 | 0
17:00 | 2889 | 565 | 1519 | 0 | 1820 | 718 | 70 | 18 | 101 | 88 | 5 | 0
17:30 | 3013.5 | 650 | 1573.5 | 0 | 2119.5 | 713 | 70 | 9 | 143.5 | 91 | 2.5 | 0
18:00 | 3138 | 735 | 1628 | 0 | 2419 | 708 | 70 | 0 | 186 | 94 | 0 | 0
18:30 | 3210.5 | 767.5 | 1623.5 | 0 | 2391.5 | 698 | 70 | 0 | 148 | 96 | 0 | 0
19:00 | 3283 | 800 | 1619 | 0 | 2364 | 688 | 70 | 0 | 110 | 98 | 0 | 0
19:30 | 3377 | 801 | 1640 | 0 | 2186 | 718 | 70 | 0 | 113 | 94 | 0 | 0
20:00 | 3406 | 800 | 1625 | 0 | 2186 | 698 | 83 | 0 | 103 | 92 | 0 | 0
20:30 | 3415.5 | 800 | 1653 | 0 | 2019 | 703.5 | 99.5 | 0 | 84.5 | 92 | 0 | 0
21:00 | 3425 | 800 | 1681 | 0 | 1852 | 709 | 116 | 0 | 66 | 92 | 0 | 0
21:30 | 3440 | 800 | 1689 | 0 | 1672.5 | 698.5 | 116 | 0 | 58 | 89 | 0 | 0
22:00 | 3455 | 800 | 1697 | 0 | 1493 | 688 | 116 | 0 | 50 | 86 | 0 | 0
22:30 | 3500.5 | 800 | 1645 | 0 | 1457.5 | 673.5 | 116 | 0 | 50 | 90 | 0 | 0
23:00 | 3546 | 800 | 1593 | 0 | 1422 | 659 | 116 | 0 | 50 | 94 | 0 | 0
23:30 | 3516 | 800 | 1580.5 | 0 | 1316 | 660 | 116 | 0 | 33.5 | 96 | 0 | 0 | Max Temp. in Dhaka |  | 24.7° C | 27.3° C
24:00 | 3486 | 800 | 1568 | 0 | 1210 | 661 | 116 | 0 | 17 | 98 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 148.071 MKWHr Energy Not Served 0.570 MKWHr Energy Requirement 148.641 MKWHr
Note on W13: Author:

## Generation
g | 2022-10-25
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 36 | 34 | 34 | 35 | 36 | 37 | 38 | 39 | 39 | 40 | 40 | 0 | 0 | [7 empty] | 0 | 13 | 46 | 46 | 46 | 46 | 572580
2 | Karnaphuli Hydro PP Unit-4 & 5 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1608000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [11 empty] | 4 | 25 | 25 | 25 | 25 | 25 | 25 |  | 8 | 8 | 8 | 8 |  |  |  | 204321
| Teknaf 20MW PP (Solartech) | [11 empty] | 18 | 19 | 15 | 11 | 5 | 1 | [9 empty] | 70470
6 | Sikalbaha 225MW CCPP (Gas) | 101 | 100 | 115 | 140 | 151 | 151 | 151 | 131 | 131 | 150 | 151 | 151 | 151 | 151 | 152 | 151 | 150 | 152 |  | 150 | 151 | 151 | 150 | 150 | 151 | 151 | 3349832
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [15 empty] | 17 | 17 | 34 |  | 34 | 34 | 24 | 17 | 17 | 17 | 17 | 183825
12 | Hathazari 100 MW peaking PP | [15 empty] | 8 | 16 | 24 |  | 0 | 0 | [5 empty] | 44544
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [7 empty] | 15 | 68 | 68 | 62 | 68 | 68 | 68 | 68 | 68 | 89 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 68 | 1378327
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP | [26 empty] | 0
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | [7 empty] | 30 | 80 | 140 | 208 | 213 | 180 | 180 | 180 | 180 | 160 | 140 |  | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 2497383
18 | Kodda 300 MW PP Unit-2 (Summit) | [11 empty] | 12 | 143 | 220 | 210 | 153 | 136 | 170 |  | 140 | 140 | 110 | 45 |  |  |  | 1497927
19 | Ashuganj 195MW PP (APSCL-United) | [10 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 117090
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 110 | 110 | 110 | 110 | 110 | 110 | 170 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 3811500
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | [8 empty] | 37 | 35 |  | 11 | 31 | 34 | 34 | 37 | 40 | 42 |  | 45 | 51 | 51 | 51 | 51 | 51 | 51 | 529488
33 | Ashuganj 225 MW CCPP | 122 | 122 | 122 | 0 | [8 empty] | 40 | 46 | 76 | 143 | 180 | 178 |  | 181 | 178 | 178 | 178 | 178 | 178 | 178 | 2154000
34 | Ashuganj 450 MW CCPP(South) | 130 | 128 | 130 | 130 | 160 | 230 | 280 | 275 | 290 | 360 | 305 | 275 | 270 | 265 | 305 | 305 | 265 | 265 |  | 285 | 285 | 285 | 285 | 285 | 260 | 260 | 6153000
| Ashuganj 450 MW CCPP(North) | [12 empty] | 70 | 5 | 2 | 3 | 15 | 70 |  | 90 | 90 | 100 | 115 | 135 | 240 | 325 | 1081600
Ashuganj 420 MW CCPP(East)
35 | Ashuganj 55 MW PP (Precision) | [6 empty] | 0 | 3 | 6 | 10 | 20 | 23 | 38 | 46 | 50 | 51 | 51 | 50 |  | 51 | 51 | 51 | 50 | 50 | 50 | 50 | 656640
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 251 | 237 | 235 | 234 | 234 | 235 | 249 | 289 | 354 | 377 | 412 | 409 | 344 | 305 | 314 | 334 | 334 | 337 |  | 361 | 361 | 362 | 361 | 361 | 361 | 361 | 7786500
40 | Meghnaghat 450 MW CCPP(MPL) | 150 | 150 | 150 | 160 | 160 | 170 | 190 | 190 | 190 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 |  | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 4816500
41 | Haripur 360MW CCPP(HPL) | 235 | 211 | 211 | 213 | 223 | 232 | 312 | 323 | 321 | 359 | 311 | 326 | 282 | 282 | 351 | 351 | 352 | 352 |  | 340 | 341 | 331 | 322 | 317 | 311 | 307 | 7166000
42 | RPCL 210MW CCPP | 34 | 34 | 35 | 34 | 34 | 34 | 55 | 108 | 153 | 145 | 120 | 105 | 105 | 75 | 84 | 83 | 83 | 83 |  | 83 | 96 | 105 | 100 | 100 | 102 | 103 | 1880640
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 0 | 1 | 7 | 45 | 14 | 31 | 37 | 39 | 17 | 26 | 9 | 1 | [9 empty] | 229080
44 | Fenchugonj CCPP Phase-1 | [15 empty] | 0 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 222000
45 | Fenchugonj CCPP Phase-2 | [11 empty] | 21 | 21 | 21 | 21 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 314040
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 7 | 7 | 7 | 7 | 7 | 7 | 20 | 20 | 20 | 30 | 20 | 5 | 5 | 30 | 30 | 7 | 30 | 30 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 457728
48 | Shahjibazar 86MW PP (Shahjibazar) | [13 empty] | 30 | 30 | 30 | 50 | 76 |  | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 642240
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 114 | 115 | 114 | 123 | 123 | 130 | 140 | 145 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 |  | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 3588110
51 | Sylhet 20 MW GTPP | [10 empty] | 19 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 243000
52 | Sylhet 50MW PP (EPL) | [16 empty] | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 74360
53 | Sylhet 10MW PP (Desh) | [7 empty] | 9 | 9 | 10 | 10 | 10 | 10 | 10 | 10 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 149040
54 | Hobiganj 11MW PP Cofidence-E | [25 empty] | 5 | 5040
55 | Fenchugonj 51 MW PP (Barakatullah) | [16 empty] | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 98400
56 | Shahjahanulla 25 MW PP | [16 empty] | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 0 | 62688
57 | Bibiana-II 341 MW CCPP (Summit) | 160 | 160 | 165 | 170 | 180 | 180 | 245 | 290 | 300 | 300 | 270 | 285 | 260 | 285 | 300 | 280 | 300 | 290 |  | 280 | 290 | 290 | 290 | 280 | 270 | 270 | 6298500
| Bibiyana South 400 MW | 100 | 100 | 70 | 70 | 80 | 110 | 110 | 70 | 40 | 15 | 25 | 70 | 118 | 143 | 256 | 400 | 350 | 400 |  | 400 | 400 | 400 | 400 | 400 | 400 | 380 | 4761000
58 | Nababganj 55 MW PP (Southern power ) | [21 empty] | 10 | 17 | 17 | 17 | 17 | 71718
59 | Tangail Palli Power Gen 22 MW | [8 empty] | 0 | 0 | 3 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 167040
60 | Barabkunda 22 MW PP (Regent) | [26 empty] | 0
61 | Narshingdi 22 MW PP (Doreen) | [17 empty] | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 61056
62 | Tangail 22 MW PP (Doreen) | [8 empty] | 18 | 18 | 18 | 18 | 16 | 16 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 269928
63 | Impoprt (Tripura) | 0 | 10 | 12 | 12 | 12 | 12 | 16 | 24 | 28 | 30 | 38 | 44 | 42 | 62 | 80 | 86 | 88 | 94 |  | 98 | 94 | 92 | 92 | 86 | 94 | 98 | 1203840
64 | Malancha, Ctg. EPZ (United) | 21 | 30 | 31 | 31 | 31 | 27 | 29 | 13 | 10 | 10 | 9 | 10 | 4 | 2 | 2 | 2 | 5 | 5 |  | 3 | 9 | 12 | 28 | 32 | 36 | 35 | 402720
65 | Feni 22MW PP (Doreen) | [13 empty] | 6 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 193320
66 | Feni 11 MW PP (Doreen) | [23 empty] | 8 | 8 | 8 | 23940
67 | Jangalia 33MW PP (Summit) | [14 empty] | 16 | 16 | 20 | 20 |  | 20 | 20 | 25 | 25 | 25 | 25 | 25 | 209900
68 | Cumilla 25 MW PP (Summit) | [21 empty] | 6 | 7 | 7 | 7 | 7 | 32110
69 | Summit Ashulia | [11 empty] | 25 | 25 | 22 | 23 | 23 | 23 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 465500
70 | Summit Madhabdi | [11 empty] | 8 | 8 | 0 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 23 | 27 | 28 | 28 | 216720
71 | Maona 33 MW PP(Summit) | [11 empty] | 16 | 22 | 33 | 33 | 0 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 338800
72 | Rupganj 33 MW PP(Summit) | [7 empty] | 0 | 0 | 0 | 0 | 0 | 24 | 28 | 28 | 28 | 27 | 26 |  | 26 | 26 | 26 | 25 | 26 | 26 | 26 | 303400
73 | Ghorashal 108MW PP (Regent) | 3 | 3 | 3 | 3 | 3 | 3 | 8 | 12 | 12 | 31 | 41 | 56 | 68 | 71 | 75 | 78 | 80 | 81 |  | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 1056954
| Feni Lanka Power | [11 empty] | 17 | 0 |  |  |  | 17 | 17 |  | 17 | 17 | 17 | 17 |  |  |  | 112860
| Chowmuhani 113 MW | [26 empty] | 0
| Manikgonj 162MW PP(MPGL) | [7 empty] | 17 | 35 | 35 | 35 | 35 | 40 | 90 | 90 | 90 | 101 | 157 |  | 162 | 162 | 162 | 162 | 162 | 129 | 53 | 1586880
77 | Siddhirganj 100 PP(Dutch Bangla) | [7 empty] | 9 | 24 | 24 | 26 | 49 | 62 | 57 | 64 | 68 | 70 | 83 |  | 90 | 50 | 50 | 26 | 24 | 24 | 24 | 775680
78 | Gazipur 52 MW PP | [11 empty] | 2 | 18 | 32 | 33 | 33 | 33 | 41 |  | 33 | 33 | 33 | 33 | 24 | 24 | 16 | 392640
79 | Kodda 150MW PP | [11 empty] | 16 | 64 | 32 | 32 | 16 | 23 | 32 |  | 16 | 16 | 16 | 16 |  |  |  | 257280
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | [11 empty] | 1 | 0 |  |  |  |  | 6 | [8 empty] | 16296
| Gazipur 100 MW PP | [7 empty] | 5 | 52 | 52 | 54 | 70 | 88 | 88 | 70 | 70 | 88 | 88 |  | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 1248000
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 0 | 0 | 0 | 2 | 1 | 2 | 2 | 1 | 1 | 1 | [10 empty] | 16824
| Jodiac Power | [7 empty] | 1 | 40 | 54 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 52 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 562634
| Karnaphuli Power Ltd. | [7 empty] | 10 | 65 | 68 | 70 | 70 | 70 | 70 | 70 | 74 | 105 | 105 |  | 105 | 105 | 105 | 94 | 94 | 90 | 58 | 1337339
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP ( Summit) | [15 empty] | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 36131
87 | Meghnaghat 100 MW(IEL) | [11 empty] | 4 | 49 | 35 | 32 | 27 | 17 | 51 |  | 50 | 24 | 24 | 11 | 7 | 7 | 7 | 330240
| Meghnaghat 104 MW PP (OPCL) | [7 empty] | 11 | 35 | 35 | 36 | 63 | 71 | 72 | 72 | 72 | 72 | 92 |  | 92 | 92 | 92 | 67 | 54 | 55 | 54 | 1054080
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [7 empty] | 33 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 70 |  | 70 | 70 | 70 | 44 | 44 | 44 | 44 | 789120
92 | Fenchuganj 44MW (Energyprima) | [16 empty] | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 123552
93 | Ashuganj 51 MW PP (Midland)
94 | Gagnagar 102 MW PP (Digital Power) | [11 empty] | 36 | 65 | 65 | 50 | 50 | 65 | 75 |  | 40 | 24 | 24 | 7 | 7 |  |  | 481968
95 | Patenga 50MW PP (Baraka) | [12 empty] | 1 | 20 | 25 | 25 | 28 | 33 |  | 37 | 39 | 39 |  |  |  |  | 218400
96 | Chattogram 108 MW PP (ECPV)
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [8 empty] | 5 | 30 | 30 | 45 | 45 | 45 | 45 | 45 | 45 | 45 |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 689744
100 | Manikganj 55 MW PP (Northern) | [7 empty] | 7 | 35 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 818442
101 | Kushiara 163 MW CCPP (KP)
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 1 | 0 | 0 | [9 empty] | 8100
103 | Kamalaghat 54 MW PP(Banco Energy) | [7 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 54 |  | 54 | 35 | 35 | 35 | 35 | 35 | 17 | 462240
104 | Keranigonj 300 MW PP (APR) | [26 empty] | 0
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | [7 empty] | 10 | 24 | 24 | 28 | 46 | 46 | 46 | 46 | 48 | 58 | 86 |  | 88 | 88 | 88 | 88 | 88 | 88 | 48 | 960000
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [11 empty] | 3 | 26 | 35 | 35 | 50 | 52 | 74 |  | 86 | 70 | 70 | 56 | 52 | 51 | 51 | 659232
115 | Juldah 100 MW PP Unit-3 (Acorn) | [7 empty] | 15 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 60 |  | 90 | 90 | 90 | 90 | 60 | 60 | 60 | 737280
116 | Chandpur 200MW (Desh energy) | [11 empty] | 6 | 0 |  |  |  | 1 | 17 |  | 17 | 17 | 17 | 17 |  |  |  | 119520
117 | Ashuganj 150MW PP (Midland) | [11 empty] | 6 | 46 | 68 | 50 | 30 | 30 | 30 |  | 10 | 10 | 10 | 10 | 10 |  |  | 381381
118 | Bibiyana-III 400 MW CCPP | 240 | 240 | 237 | 239 | 239 | 262 | 325 | 328 | 349 | 407 | 363 | 408 | 328 | 328 | 328 | 328 | 328 | 402 |  | 407 | 406 | 405 | 406 | 406 | 407 | 406 | 8050000
| Jamalpur 115 MW PP (United) | [7 empty] | 4 | 24 | 24 | 30 | 47 | 47 | 47 | 45 | 45 | 45 | 92 |  | 92 | 96 | 97 | 97 | 48 | 48 | 48 | 883200
| Anwara 300 MW PP (United) | 15 | 15 | 15 | 15 | 0 |  |  | 100 | 100 | 105 | 172 | 176 | 176 | 176 | 176 | 176 | 176 | 176 |  | 176 | 165 | 184 | 175 | 175 | 175 | 175 | 2757491
| Juldah unit-2 (Acorn) | [7 empty] | 4 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 35 |  | 66 | 60 | 60 | 38 | 38 | 38 | 38 | 551040
| Anlima Energy Ltd. | [12 empty] | 45 | 68 | 68 | 55 | 51 | 51 |  | 25 | 17 | 17 | 17 |  |  |  | 436582
| Bhairob 54.5 MW | [12 empty] | 11 | 17 | 17 | 17 | 19 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 343800
| Spectra Solar Plant Ltd. | [8 empty] | 0 | 0 |  | 25 | 28 | 23 | 16 | 9 | 0 | [9 empty] | 109762
| Chandpur 115(Doreen) | [11 empty] | 14 | 22 |  | 6 | 17 | 20 | 34 |  | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 332160
| Kanchan Purbachal Power Generation Ltd. | [10 empty] | 19 | 42 | 53 | 23 | 37 | 53 | 54 | 54 |  | 40 | 34 | 34 | 34 | 34 | 34 | 34 | 572760
| Mirsharai 150 MW (Oil) | [11 empty] | 5 | 9 |  |  | 7 | 18 | [9 empty] | 46836
Mirsharai 150 MW (Gas)
120 | Eastern Zone Total | 1889 | 1866 | 1856 | 1786 | 1843 | 1990 | 2399 | 2805 | 3449 | 3802 | 3821 | 4282 | 4715 | 4806 | 5127 | 5254 | 5500 | 6158 |  | 6075 | 5962 | 5986 | 5776 | 5561 | 5588 | 5437 | 97981833
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | [17 empty] | 16 | [8 empty] | 16320
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | [17 empty] | 7 |  | 35 | 35 | 35 | 37 | 17 |  |  | 153600
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 0 | 13 | 37 | 49 | 62 | 81 | 86 | 93 | 76 | 56 | 28 | 2 | [9 empty] | 579600
131 | Rampal 1320 MW (BIFPCL)
132 | United Payra Power Ltd. | [26 empty] | 0
133 | Bhola Nutan Biddut BD LTD (GAS) | 45 | 44 | 0 | [10 empty] | 10 | 30 | 36 | 53 | 72 |  | 85 | 115 | 130 | 160 | 180 | 180 | 160 | 1142264
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [26 empty] | 0
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | [19 empty] | 20 | 67 | 67 | 67 | 67 | 64 | 58 | 329000
140 | Bhola 33 MW PP (Venture) | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 6 | 5 | 7 | 7 | 7 | 7 | 8 | 10 |  | 11 | 11 | 11 | 10 | 11 | 8 | 10 | 116900
141 | Noapara 100 MW PP (Bangla Trac) | [26 empty] | 0
142 | Noapara 40 MW PP (Khanjahan Ali) | [26 empty] | 0
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 182 | 132 | 167 | 201 | 201 | 211 | 195 | 179 | 195 | 274 | 378 | 485 | 485 | 486 | 573 | 565 | 565 | 735 |  | 800 | 801 | 800 | 800 | 800 | 800 | 800 | 10730909
147 | Bheramara 410 MW CCPP | 115 | 115 | 115 | 130 | 130 | 130 | 180 | 180 | 180 | 180 | 230 | 260 | 230 | 230 | 230 | 230 | 210 | 280 |  | 320 | 350 | 350 | 350 | 350 | 360 | 260 | 5527872
148 | Payra 1320 MW | 460 | 460 | 460 | 460 | 460 | 460 | 460 | 460 | 470 | 480 | 550 | 650 | 690 | 670 | 670 | 670 | 640 | 630 |  | 610 | 640 | 620 | 630 | 610 | 580 | 580 | 15010500
149
150 | Barapukuria TPP Unit-1 | 81 | 82 | 80 | 81 | 83 | 82 | 79 | 82 | 84 | 84 | 83 | 81 | 78 | 83 | 79 | 79 | 78 | 78 |  | 78 | 78 | 78 | 79 | 78 | 79 | 81 | 1916945
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 0 | 3 | 1 | 2 | 3 | 4 | 2 | 2 | 1 | 0 | [9 empty] | 22020
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | [8 empty] | 13 | 11 | 42 | 90 | 170 | 190 | 201 | 168 | 164 | 172 |  | 182 | 183 | 182 | 185 | 182 | 181 | 165 | 2483655
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 210 | 182 | 148 | 197 | 198 | 257 | 295 | 328 | 357 | 390 | 367 | 336 | 304 | 329 | 308 | 331 | 336 | 408 |  | 406 | 380 | 357 | 378 | 384 | 295 | 293 | 7535636
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [13 empty] | 4 | 4 | 4 | 4 | 4 |  | 4 | [6 empty] | 23090
162 | Bogra 22 MW PP (GBB) | [7 empty] | 16 | 16 | 19 | 19 | 20 | 15 | 21 | [12 empty] | 125280
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | [13 empty] | 0
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | [8 empty] | 25 | 42 | 42 | 34 | 24 | 24 | 24 | 8 | 8 | 34 |  | 34 | 25 | 25 | 25 | 8 | 8 | 8 | 364301
167 | Katakhali 50 MW Peaking PP | [13 empty] | 11 | 16 | 16 | 16 | 32 | [8 empty] | 92236
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka) | [12 empty] | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | [6 empty] | 59520
170 | Chapainawabganj 100 MW Peaking PP | [13 empty] | 25 | 25 | 25 | 25 | 60 |  | 56 | 63 | 63 | 33 | 33 | 33 | 0 | 372200
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [7 empty] | 5 | 35 | 35 | 39 | 73 | 89 | 70 | 70 | 70 | 70 | 90 |  | 70 | 70 | 70 | 70 | 35 | 35 | 35 | 1064064
172 | Confidence Power Bogura Unit-1 113 MW | [7 empty] | 20 | 35 | 25 | 60 | 90 | 70 | 70 | 70 | 35 | 35 | 90 |  | 70 | 70 | 70 | 35 | 35 | 35 | 35 | 952416
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [7 empty] | 7 | 40 | 34 | 34 | 102 | 85 | 49 | 49 | 34 | 34 | 58 |  | 113 | 113 | 113 | 70 | 34 | 34 | 34 | 933628
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 0 | 0 | 1 | 3 | 3 | 3 | 5 | 3 | 2 | 1 | 0 | [9 empty] | 23230
178 | Energypac Power Venture Thakurgaon Ltd. | [11 empty] | 34 | 34 | 36 | 36 | 36 | 36 | 36 |  | 55 | 36 | 36 | 36 |  |  |  | 393216
178 | Intraco Solar 30 MW | [8 empty] | 4 | 17 | 18 | 21 | 18 | 28 | 21 | 9 | 1 | [9 empty] | 120790