## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2022-10-29 | Saturday
|  | Date (day): | 2022-10-29 |  | Saturday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 9928.6 | MW |  |  | (b) At Evening Peak Hour : |  | 12002 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2022-10-28 | 2022-10-29 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Machine problem
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Machine problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 81 | 81 | 80 | 80 |  | 28 | Engine problem
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 402 | 360 | 400 | 400 | 12 |  | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 332 | 305 | 350 | 300 | 60 |  | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 225 | 225 | 225 |  | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 34 | 81 | 70 | 94 |  | 6 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 130 | 124 | 134 | 134 | 201 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 0 | 0 | 0 | 0 |  | 102 | Under maint
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 16 | 16 | 16 | 16 |  | 6 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 52 | 79 | 63 | 90 |  | 10 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 58 | 92 | 74 | 92 |  | 10 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 54 | 17 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 55 | 82 | 16 | 110 |  | 39 | Engine problem
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 35 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 35 | 35 | 35 |  |  | 33 kV feeder fault.
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 47 | 52 | 51 | 53 |  | 27 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 32 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 14 | 8 | 0 | 49
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 51 | 248 | 225 | 275 |  | 25 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 150 | 150 |  | Fuel conservation
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 0 | 0 | 0 | 50 | 50 |  | Fuel conservation
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 50 | 50 |  | Fuel conservation
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 38 | 93 | 80 | 134 |  | 15 | Engine problem
36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 88 | 88 | 88 | 88 |  | 17 | Engine problem
37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 74 | 93 | 74 | 92 | 12 |  | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 35 | 162 | 35 | 162
39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 30 | 0 | 30 | 0
40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 46 | 54 | 54 | 54
| Dhaka area Total |  |  |  |  | 6263 | 5847 | 2178 | 2687 | 2453 | 3143 | 1356 | 1330
41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 16 | 25 | 25 | 25
43 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 20 | 0 | 20 | 0
44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 21 | 30 | 44 |  | 6 | Engine problem
45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 154 | 153 | 152 | 152 | 78 |  | Low Water Level
46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 150 | 141 | 150 | 150 |  | 75 | ST under maint
47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 51 | 105 | 70 | 105
49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 16 | 23 | 0 | 0 | 98 |  | Fuel shortage
50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 17 | 51 | 51 |  | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 22 | 55 | 22 | 55 | 45 |  | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 25 | 50 | 38 | 50 |  | 50 | Engine problem
53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  | 22 | Engine problem
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 33 | 32 | 10 | 25
54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 123 | 282 | 140 | 283 | 17 |  | Engine problem
57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 35 | 54 | 54 | 54
58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 70 | 105 | 70 | 105
59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 43 | 25 | 50
60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 74 | 53 | 17 | 107 |  | 9 | Engine problem
| Mirsharai 150 MW |  | Gas/HSD | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0
| Chattogram area Total |  |  |  |  | 2442 | 2382 | 818 | 1193 | 845 | 1256 | 757 | 312
61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 160 | 179 | 180 | 200 |  | 21 | Gas shortage
63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 260 | 280 | 320 | 320 | 40 |  | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 | 360 |  | Gas shortage
| Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+136*1 | 284 | 284 | 298 | 0 | 0 | 0 |  |  | On test.
65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 0 | 46 | 50 | 50
66 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 55 | 0 | 50 | 50 | 50 | 5 |  | Gas shortage
67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 0 | 177 | 185 | 185 | 10 |  | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 0 | 0 | 0 | 0
69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 25 | 63 | 70 | 140 |  | 10 | Engine problem
70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 47 | 40 | 47 |  | 5 | Engine problem
71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 | 163 |  | Gas shortage.
72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 51 | 51 | 100 | 200
73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 19 | 19
74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 102 | 116 | 143 | 166
75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 14 | 33 | 33 | 33
76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 15 | 32 | 8 | 43 | 9 |  | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 12 | 18 | 15 | 18 |  | 7 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 100 | 100 |  | Fuel conservation
79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 92 | 114 | 114
80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 0 | 9 | 104 |  | Fuel shortage
81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 35 | 35 | 35 | 35 |  | 19 | Engine problem
82 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 47 | 110 | 53 | 115
| Cumilla Area Total |  |  |  |  | 3193 | 3169 | 1063 | 1359 | 1426 | 1855 | 925 | 62
83 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 34 | 67 | 90 | 110 | 92 |  | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 18 | 18 | 18 |  | 4 | Engine problem
85 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0
86 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
87 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 48 | 87 | 45 | 88 | 112 |  | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 49 | 98 | 90 | 98 |  | 17 | Engine problem
89 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 54 | 0 | 50 | 0
90 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 12 | 12 |  | 10 | Engine problem
| Mymensingh Area Total |  |  |  |  | 717 | 614 | 217 | 282 | 306.6 | 326 | 92 | 31
91 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 30 | 30 | 30 | 30 |  | 40 | Machine problem.
92 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 43 | 43 | 43 | 43 |  | 47 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 | 163 |  | Gas shortage
94 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 11 | 11 | 11 | 11 | 40 |  | Gas shortage
96 | Fenchuganj 44MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 10 | 10 | 10 | 10 | 40 |  | Gas shortage
97 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 5 | 0 | 0 | 11 |  | Gas shortage
98 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 62 | 40 | 66 | 65
99 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 0 | 50 | 0 | 50
100 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
101 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 192 | 192 | 190 | 190 |  | 41 | ST Under maint.
102 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 19 | 19
103 | Sylhet 50MW PP (EPL) |  | Gas | NENP | 27*2 | 50 | 50 | 11 | 11 | 11 | 11 | 39 |  | Gas shortage
104 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 8 | 8 | 0 | 0 | 25 |  | Gas shortage
105 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 255 | 305 | 300 |  |  | FGMO
106 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 368 | 329 | 400 | 400
107 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
108 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 350 | 313 | 400 | 400
| Sylhet Area Total |  |  |  |  | 2522 | 2477 | 1418 | 1325 | 1495 | 1539 | 318 | 558
109 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 907 | 907 | 923 | 923
110 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 16 | 32 | 0 | 32 | 83 |  | Fuel shortage
111 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 39 | 0 | 39 | 15 |  | Fuel shortage
112 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
113 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 74 | 0 | 75 | 34 |  | Fuel shortage
114 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 170 | 175 | 225 | 225 | 185 |  | Gas shortage
115 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 0 | 0 | 8 | 32 |  | Fuel shortage
116 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 0 | 50 | 50 |  | Fuel conservation
117 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 17 | 56 | 75 | 55 |  | 50 | Engine problem
118 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 0 |  |  | Fuel shortage
119 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 87 | 0 | 100 | 0
| Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 2388 | 2384 | 1197 | 1283 | 1323 | 1407 | 645 | 50
120 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 0 | 16 |  |  | Line O/L
121 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 14 | 17 | 16 | 22 |  | 18 | Engine problem
122 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 87 | 74 | 87 | 87 |  | 107 | Machine problem
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
123 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 670 | 770 | 810 | 810 |  |  | Line O/L
124 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 162 | 180 | 195 | 220
125 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 0 | 0 |  |  | Line O/L
| Barisal Area Total |  |  |  |  | 1958 | 1958 | 933 | 1041 | 1108 | 1155 | 0 | 125
126 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
127 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 24 | 0 | 32 |  | 20 | Engine problem
128 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 4 | 0 | 22 |  | 49 | Engine problem
129 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
130 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 25 | 16 | 34 | 42 |  | 8 | Engine problem
131 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 32 | 0 | 32 | 18 |  | Fuel shortage
132 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
133 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Fuel shortage
134 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 131 | 131 | 157 | 157 | 63 |  | Gas shortage
135 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 221 | 233 | 260 | 260 | 154 |  | Gas shortage
136 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 35 | 0 | 35 |  | 15 | Engine problem
137 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 0 | 0 | 0 | 0
138 | Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
139 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 11 | 11
140 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 16 | 8 | 8 | 44 |  | Fuel shortage
141 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 50 | 0 | 86 |  | 18 | Engine problem
142 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 0 | 100 | 100 |  | Fuel conservation
143 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 69 | 100 | 113 | 113
144 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 90 | 113 | 113 | 113
145 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
| Rajshahi Area Total |  |  |  |  | 2199 | 2129 | 549 | 754 | 702 | 1011 | 980 | 110
146 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 75 | 78 | 80 | 82
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
147 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 |  | 274 | Under maint
148 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
149 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
150 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 75 | 34 | 100 | 113
151 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 6 | 0 | 8 | 0
152 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 35 | 35 | 70 | 115
| Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 30 | 0 | 12 | 0
| Rangpur Area Total |  |  |  |  | 830 | 750 | 221 | 147 | 270 | 310 | 40 | 359
| Total |  |  |  |  | 22512 | 21710 | 8594 | 10071 | 9928.6 | 12002 | 5113 | 2937
A. |  | 2022-10-28 | (Yesterday) |  |  |  |  | Friday
1 | Highest Generation : |  |  | 10071 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
2 | Minimum Generation : |  |  | 7289 | MW at | 6:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 10071 | MW
3 | Day peak Generation : |  |  | 8594 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 9282.89 | MW
4 | Evening peak Generation : |  |  | 10071 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 207.6148 | MKWHr | By Solar | 1.614 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Gas : | 115.39 | MKWHr |  | By Oil: | 42.79 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 19.7611 | MKWHr |  | By Hydro: | 3.6844 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 5113 | MW | Dhaka | 3434.1 | 3434.1 |  | 0 |  | 18:00 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 2937 | MW | Chittagong | 975.5 | 975.5 |  | 0 |  | 19:00 |  | 0
|  |  | Total = |  |  | 8050 | MW | Khulna | 1082.8 | 1082.8 |  | 0 |  | 19:30 |  | 0
7 | Total Gas Supplied : |  |  | 838.55 | MMCFD |  |  | Rajshahi | 1000.8 | 1000.8 |  | 0 |  | 20:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 122711969.75 | ii) Oil : | Taka | 560112287.69 | Comilla | 836 | 836 |  | 0 |  | 21:00 |  | 0
|  | iii) Coal : |  | 172298763.29 | Total | Taka | 855123020.73 | Mymensingh | 757 | 757 |  | 0 |  | 22:00 |  | 0
9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0 | MKWHr. | Sylhet | 399 | 399 |  | 0 |  | 23:00 |  | 0
| ii) During Peak Demand : |  |  | 266 | MW (E to W) at | 19:00 | hrs | Barisal | 223.69 | 223.69 |  | 0 |  | 24:00 |  | 0
| iii) Maximum : |  |  | 168 | MW at | 19:30 | hrs | Rangpur | 574 | 574 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 31.7° C |  |  | Total | 9282.89 | 9282.89 |  | 0
B. |  | 2022-10-29 | (Today) |  |  |  | Saturday |  |  | Probable max. temperature in Dhaka |  |  | 30.3° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 11000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 12002 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 9000 | MW
4 | Reserve(Generation end) |  |  |  | 1002 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 226.7662 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 7120 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.9244 | MKWHr. | ii) HVDC Flow at Peak Time |  | 907 | MW at | 19:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.4509 | MKWHr. | iii) Maximum HVDC Flow : |  | 908 | MW at | 4:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 96.6 |  | (b) Today: | 96.36 |  | (c) Rule Curve: |  | 108.7
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2022-10-28
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 0 | 84 | 0 | 392 | 266 |  | 0 | 225 | 123 | 60 | 0 | 55 | 0 | 0 | 0 | 60 | 58 | 75 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 16 | 23 | 28 | 33 | 33 | 49 | 0 | 84 | 70 | 0 | 0 | 25 | 152 | 0 | 0 | 0 |  | 12 | 24 | 34 | 22 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 280 | 0 | 153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 18 | 11 | 25 | 18 | 112 | 107 | 0 | 16 | 0 | 30 | 43 | 11 | 10 | 0 | 0 | 32 | 30 | 0 | 191 | 19 | 11 | 10 | 341 | 8 | 5 | 0 | 276 | 0 | 0 | 48 | 0 | 135 | 0 | 25 | 51 | 68 | 367 | 49 | 88 | 68 | 0 | 69 | 54 | 51 | 17 | 0 | 25 | 360 | 55 | 0 | 35 | 107 | 0 | 35 | 0 | 53 | 54 | 298 | 0 | 0 |  | 906 | 0 | 195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 0 | 240 | 56 | 0 | 50 | 0 | 34 | 0 | 0 | 35 | 590 | 169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6169 | 2515 | 8684 | 3167 | 906 | 1561 | 0 | 1989 | 662 | 154 | 0 | 133 | 112 | 0 | 0 | 96.65
2:00 | 0 | 0 | 0 | 180 | 0 | 84 | 0 | 359 | 267 |  | 0 | 225 | 136 | 59 | 0 | 55 | 0 | 0 | 0 | 60 | 58 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 16 | 23 | 28 | 33 | 33 | 0 | 0 | 80 | 70 | 0 | 0 | 25 | 150 | 0 | 0 | 0 |  | 12 | 0 | 34 | 22 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 280 | 0 | 141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 18 | 11 | 25 | 18 | 108 | 106 | 0 | 16 | 0 | 30 | 43 | 11 | 10 | 0 | 0 | 32 | 30 | 0 | 192 | 19 | 11 | 10 | 325 | 8 | 5 | 0 | 210 | 0 | 0 | 48 | 0 | 74 | 0 | 25 | 51 | 67 | 329 | 49 | 88 | 68 | 0 | 69 | 54 | 51 | 17 | 0 | 25 | 320 | 58 | 0 | 35 | 107 | 0 | 35 | 0 | 53 | 53 | 298 | 0 | 0 |  | 906 | 0 | 195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 135 | 0 | 244 | 56 | 0 | 50 | 0 | 0 | 0 | 0 | 35 | 580 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5763 | 2468 | 8231 | 3043 | 906 | 1559 | 0 | 1779 | 652 | 150 | 0 | 34 | 108 | 0 | 0 | 96.64
3:00 | 0 | 0 | 0 | 180 | 0 | 84 | 0 | 352 | 267 |  | 0 | 225 | 133 | 60 | 0 | 55 | 0 | 0 | 0 | 60 | 58 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 16 | 23 | 28 | 33 | 33 | 0 | 0 | 80 | 70 | 0 | 0 | 25 | 152 | 0 | 0 | 0 |  | 12 | 0 | 0 | 22 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 280 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 8 | 33 | 18 | 106 | 107 | 0 | 18 | 0 | 30 | 43 | 11 | 10 | 0 | 0 | 32 | 30 | 0 | 191 | 19 | 11 | 10 | 280 | 8 | 5 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 25 | 51 | 68 | 328 | 49 | 88 | 68 | 0 | 69 | 54 | 51 | 17 | 0 | 25 | 320 | 55 | 0 | 35 | 34 | 0 | 35 | 0 | 53 | 54 | 298 | 0 | 0 |  | 905 | 0 | 195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 136 | 0 | 250 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 640 | 168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5306 | 2511 | 7817 | 3133 | 905 | 1515 | 0 | 1296 | 712 | 150 | 0 | 0 | 106 | 0 | 0 | 96.63
4:00 | 0 | 0 | 0 | 180 | 0 | 81 | 0 | 352 | 331 |  | 0 | 225 | 133 | 39 | 0 | 55 | 0 | 0 | 0 | 60 | 7 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 16 | 23 | 28 | 33 | 33 | 0 | 0 | 80 | 70 | 0 | 0 | 0 | 151 | 0 | 0 | 0 |  | 12 | 0 | 0 | 22 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 280 | 0 | 135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 8 | 33 | 0 | 102 | 107 | 0 | 18 | 0 | 30 | 43 | 11 | 10 | 0 | 0 | 32 | 30 | 0 | 191 | 19 | 11 | 10 | 290 | 8 | 5 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 25 | 51 | 10 | 328 | 24 | 88 | 68 | 0 | 68 | 17 | 51 | 17 | 0 | 25 | 320 | 55 | 0 | 35 | 0 | 0 | 35 | 0 | 53 | 54 | 298 | 0 | 0 |  | 908 | 0 | 195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 137 | 0 | 262 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 650 | 168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5097 | 2516 | 7613 | 3109 | 908 | 1617 | 0 | 1005 | 722 | 150 | 0 | 0 | 102 | 0 | 0 | 96.62
5:00 | 0 | 0 | 0 | 180 | 0 | 81 | 0 | 352 | 321 |  | 0 | 225 | 133 | 10 | 0 | 55 | 0 | 0 | 0 | 25 | 7 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 0 | 23 | 0 | 33 | 0 | 0 | 0 | 80 | 70 | 0 | 0 | 0 | 151 | 0 | 0 | 0 |  | 12 | 0 | 0 | 10 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 270 | 0 | 133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 8 | 33 | 12 | 96 | 108 | 0 | 18 | 0 | 30 | 43 | 11 | 10 | 0 | 0 | 32 | 30 | 0 | 191 | 19 | 11 | 10 | 290 | 8 | 5 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 25 | 51 | 10 | 369 | 8 | 34 | 68 | 0 | 70 | 17 | 51 | 17 | 0 | 10 | 360 | 55 | 0 | 35 | 0 | 0 | 35 | 0 | 53 | 0 | 299 | 0 | 0 |  | 906 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 137 | 0 | 269 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 640 | 169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4877 | 2519 | 7396 | 3124 | 906 | 1616 | 0 | 792 | 712 | 150 | 0 | 0 | 96 | 0 | 0 | 96.61
6:00 | 0 | 0 | 0 | 180 | 0 | 81 | 0 | 352 | 306 |  | 0 | 225 | 133 | 9 | 0 | 40 | 0 | 0 | 0 | 9 | 7 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 0 | 23 | 20 | 33 | 0 | 0 | 0 | 80 | 70 | 0 | 0 | 0 | 151 | 0 | 0 | 0 |  | 12 | 0 | 0 | 10 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 270 | 0 | 133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 8 | 33 | 12 | 90 | 109 | 0 | 18 | 0 | 30 | 43 | 11 | 10 | 0 | 0 | 32 | 30 | 0 | 191 | 19 | 11 | 10 | 290 | 8 | 5 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 10 | 17 | 10 | 370 | 8 | 17 | 68 | 0 | 70 | 17 | 51 | 17 | 5 | 10 | 360 | 54 | 0 | 35 | 0 | 0 | 35 | 0 | 53 | 12 | 299 | 0 | 0 |  | 906 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 138 | 0 | 272 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 630 | 168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4773 | 2516 | 7289 | 3152 | 906 | 1603 | 0 | 686 | 702 | 150 | 0 | 0 | 90 | 0 | 0 | 96.6
7:00 | 0 | 0 | 0 | 180 | 0 | 78 | 0 | 356 | 316 |  | 0 | 225 | 150 | 8 | 0 | 30 | 0 | 0 | 0 | 8 | 7 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 16 | 23 | 28 | 33 | 33 | 0 | 0 | 81 | 70 | 0 | 0 | 0 | 151 | 0 | 0 | 0 |  | 12 | 0 | 0 | 10 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 270 | 0 | 131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 8 | 33 | 12 | 90 | 108 | 0 | 18 | 0 | 30 | 43 | 11 | 10 | 0 | 0 | 32 | 30 | 0 | 191 | 19 | 11 | 10 | 310 | 8 | 5 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 5 | 10 | 17 | 10 | 407 | 8 | 17 | 17 | 1 | 70 | 17 | 17 | 17 | 9 | 10 | 400 | 20 | 6 | 35 | 0 | 0 | 35 | 4 | 20 | 17 | 298 | 0 | 0 |  | 906 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 139 | 0 | 274 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 650 | 169 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 2 |  | 4790 | 2547 | 7337 | 3283 | 906 | 1651 | 0 | 505 | 722 | 151 | 0 | 0 | 90 | 29 | 0 | 96.59
8:00 | 0 | 0 | 0 | 180 | 0 | 78 | 0 | 399 | 310 |  | 0 | 225 | 125 | 9 | 0 | 30 | 0 | 0 | 0 | 16 | 7 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 16 | 23 | 28 | 33 | 33 | 0 | 0 | 81 | 70 | 0 | 0 | 2 | 152 | 0 | 0 | 0 |  | 12 | 0 | 0 | 22 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 260 | 0 | 123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 8 | 33 | 12 | 86 | 73 | 0 | 18 | 1 | 30 | 43 | 11 | 10 | 0 | 0 | 32 | 30 | 0 | 191 | 19 | 11 | 10 | 290 | 8 | 5 | 0 | 2 | 0 | 0 | 47 | 0 | 0 | 11 | 25 | 28 | 10 | 386 | 47 | 26 | 37 | 1 | 70 | 17 | 35 | 17 | 9 | 19 | 360 | 36 | 24 | 35 | 6 | 0 | 35 | 15 | 35 | 28 | 298 | 0 | 0 |  | 907 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 139 | 0 | 258 | 17 | 0 | 6 | 0 | 34 | 0 | 1 | 35 | 680 | 177 | 0 | 0 | 2 | 33 | 0 | 0 | 0 | 0 | 9 |  | 4944 | 2685 | 7629 | 3208 | 907 | 1589 | 0 | 839 | 752 | 151 | 0 | 0 | 86 | 97 | 0 | 96.59
9:00 | 0 | 0 | 0 | 180 | 0 | 78 | 0 | 399 | 275 |  | 0 | 225 | 135 | 9 | 0 | 55 | 0 | 0 | 0 | 32 | 7 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 16 | 23 | 28 | 33 | 33 | 0 | 0 | 82 | 70 | 0 | 0 | 8 | 151 | 0 | 0 | 0 |  | 12 | 0 | 0 | 22 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 260 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 8 | 22 | 12 | 86 | 73 | 0 | 18 | 2 | 30 | 43 | 11 | 10 | 0 | 0 | 32 | 30 | 0 | 191 | 19 | 11 | 9 | 270 | 8 | 5 | 0 | 15 | 0 | 0 | 47 | 0 | 15 | 16 | 25 | 51 | 10 | 328 | 47 | 34 | 51 | 2 | 120 | 17 | 60 | 17 | 9 | 25 | 340 | 72 | 37 | 35 | 17 | 0 | 35 | 22 | 52 | 36 | 299 | 0 | 0 |  | 907 | 0 | 195 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 246 | 17 | 0 | 35 | 0 | 38 | 0 | 2 | 35 | 650 | 167 | 0 | 0 | 3 | 57 | 0 | 0 | 0 | 0 | 20 |  | 5098 | 2703 | 7801 | 3112 | 907 | 1513 | 0 | 1148 | 722 | 152 | 0 | 0 | 86 | 161 | 0 | 96.59
10:00 | 0 | 0 | 0 | 180 | 0 | 78 | 0 | 388 | 252 |  | 0 | 225 | 142 | 8 | 0 | 55 | 0 | 0 | 0 | 32 | 7 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 16 | 23 | 28 | 33 | 33 | 0 | 0 | 82 | 70 | 0 | 0 | 8 | 151 | 0 | 0 | 0 |  | 12 | 0 | 0 | 22 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 260 | 0 | 131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 8 | 18 | 12 | 94 | 72 | 0 | 18 | 2 | 30 | 43 | 11 | 10 | 0 | 0 | 30 | 30 | 0 | 192 | 18 | 11 | 9 | 280 | 8 | 5 | 0 | 15 | 0 | 0 | 48 | 0 | 16 | 19 | 25 | 51 | 10 | 350 | 49 | 34 | 51 | 4 | 123 | 17 | 70 | 17 | 0 | 25 | 320 | 74 | 48 | 35 | 17 | 0 | 35 | 28 | 30 | 36 | 292 | 0 | 0 |  | 907 | 0 | 190 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 136 | 0 | 234 | 17 | 0 | 35 | 0 | 34 | 0 | 4 | 35 | 640 | 160 | 0 | 0 | 5 | 76 | 0 | 0 | 0 | 0 | 25 |  | 5097 | 2701 | 7798 | 3091 | 907 | 1487 | 0 | 1144 | 712 | 152 | 0 | 0 | 94 | 211 | 0 | 96.58
11:00 | 0 | 0 | 0 | 180 | 0 | 81 | 0 | 402 | 332 |  | 0 | 225 | 150 | 8 | 0 | 40 | 0 | 0 | 0 | 32 | 7 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 16 | 23 | 20 | 33 | 33 | 0 | 0 | 84 | 70 | 0 | 0 | 8 | 151 | 0 | 0 | 0 |  | 12 | 0 | 0 | 22 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 260 | 0 | 136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 8 | 15 | 12 | 80 | 34 | 0 | 18 | 2 | 30 | 43 | 11 | 10 | 0 | 0 | 30 | 30 | 0 | 192 | 18 | 11 | 9 | 290 | 8 | 5 | 0 | 15 | 0 | 0 | 48 | 0 | 16 | 20 | 25 | 46 | 10 | 410 | 49 | 34 | 51 | 4 | 123 | 17 | 70 | 17 | 0 | 25 | 392 | 74 | 53 | 35 | 17 | 0 | 35 | 31 | 17 | 36 | 292 | 0 | 0 |  | 907 | 0 | 180 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132 | 0 | 235 | 17 | 0 | 35 | 0 | 34 | 0 | 5 | 35 | 680 | 161 | 0 | 0 | 5 | 84 | 0 | 0 | 0 | 0 | 30 |  | 5264 | 2741 | 8005 | 3175 | 907 | 1592 | 0 | 1111 | 752 | 154 | 0 | 0 | 80 | 234 | 0 | #REF!
12:00 | 0 | 0 | 0 | 180 | 0 | 81 | 0 | 402 | 332 |  | 0 | 225 | 130 | 34 | 0 | 55 | 0 | 0 | 0 | 52 | 58 | 55 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 16 | 23 | 24 | 33 | 33 | 14 | 0 | 84 | 70 | 0 | 0 | 16 | 150 | 0 | 0 | 0 |  | 12 | 16 | 0 | 22 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 260 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 19 | 8 | 14 | 12 | 102 | 34 | 0 | 18 | 2 | 30 | 43 | 11 | 10 | 0 | 0 | 62 | 0 | 0 | 192 | 18 | 11 | 10 | 300 | 8 | 5 | 0 | 51 | 0 | 0 | 48 | 0 | 38 | 20 | 25 | 51 | 25 | 368 | 49 | 88 | 51 | 4 | 123 | 35 | 70 | 17 | 0 | 25 | 350 | 74 | 54 | 35 | 74 | 0 | 35 | 30 | 47 | 46 | 298 | 0 | 0 |  | 907 | 0 | 170 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 8 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131 | 0 | 221 | 17 | 0 | 69 | 0 | 75 | 0 | 6 | 90 | 670 | 162 | 0 | 0 | 5 | 87 | 35 | 0 | 0 | 0 | 30 |  | 5694 | 2900 | 8594 | 3148 | 907 | 1540 | 0 | 1689 | 745 | 154 | 0 | 71 | 102 | 238 | 0 | 96.56
13:00 | 0 | 0 | 0 | 180 | 0 | 81 | 0 | 395 | 305 |  | 0 | 225 | 123 | 53 | 0 | 55 | 0 | 0 | 0 | 70 | 58 | 123 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 16 | 23 | 19 | 33 | 33 | 49 | 0 | 84 | 70 | 0 | 0 | 25 | 150 | 0 | 0 | 0 |  | 12 | 15 | 0 | 22 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 260 | 0 | 153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 19 | 8 | 14 | 12 | 112 | 34 | 0 | 18 | 2 | 30 | 43 | 11 | 10 | 0 | 0 | 62 | 0 | 0 | 192 | 18 | 11 | 10 | 280 | 8 | 5 | 0 | 145 | 0 | 0 | 48 | 0 | 94 | 19 | 25 | 51 | 46 | 409 | 49 | 88 | 51 | 4 | 123 | 36 | 70 | 17 | 0 | 25 | 370 | 74 | 50 | 90 | 107 | 0 | 35 | 30 | 68 | 54 | 298 | 0 | 0 |  | 907 | 0 | 170 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 8 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131 | 0 | 204 | 17 | 0 | 106 | 0 | 86 | 0 | 6 | 70 | 650 | 183 | 0 | 0 | 5 | 80 | 35 | 0 | 0 | 0 | 28 |  | 6142 | 2903 | 9045 | 3190 | 907 | 1498 | 0 | 2097 | 725 | 154 | 0 | 138 | 112 | 224 | 0 | 96.55
14:00 | 0 | 0 | 0 | 180 | 0 | 81 | 0 | 381 | 270 |  | 0 | 225 | 140 | 53 | 0 | 55 | 0 | 0 | 0 | 30 | 24 | 32 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 16 | 24 | 15 | 33 | 33 | 16 | 0 | 84 | 70 | 0 | 0 | 8 | 149 | 0 | 0 | 0 |  | 12 | 16 | 0 | 22 | 0 | 11 | 0 | 35 | 0 | 0 | 0 | 260 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 8 | 19 | 11 | 17 | 12 | 106 | 34 | 0 | 18 | 2 | 30 | 43 | 11 | 10 | 0 | 0 | 61 | 0 | 0 | 192 | 18 | 11 | 10 | 270 | 8 | 5 | 0 | 95 | 0 | 0 | 48 | 0 | 88 | 16 | 25 | 51 | 61 | 374 | 49 | 50 | 51 | 3 | 123 | 17 | 70 | 17 | 0 | 25 | 345 | 36 | 44 | 90 | 25 | 0 | 35 | 25 | 71 | 54 | 0 | 0 | 0 |  | 908 | 0 | 170 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 8 | 0 | 0 | 0 | 0 | 84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 128 | 0 | 200 | 17 | 0 | 35 | 0 | 40 | 0 | 6 | 35 | 620 | 200 | 0 | 0 | 5 | 68 | 35 | 0 | 0 | 0 | 25 |  | 5344 | 2727 | 8071 | 2834 | 908 | 1477 | 0 | 1600 | 704 | 154 | 0 | 94 | 106 | 194 | 0 | 96.57
15:00 | 0 | 0 | 0 | 180 | 0 | 81 | 0 | 404 | 334 |  | 0 | 225 | 115 | 56 | 0 | 55 | 0 | 0 | 0 | 33 | 58 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 16 | 24 | 15 | 33 | 33 | 16 | 0 | 83 | 70 | 0 | 0 | 8 | 151 | 0 | 0 | 0 |  | 12 | 16 | 0 | 22 | 0 | 25 | 0 | 33 | 0 | 0 | 0 | 325 | 0 | 181 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 47 | 8 | 19 | 11 | 28 | 12 | 108 | 34 | 0 | 18 | 2 | 30 | 43 | 11 | 10 | 0 | 0 | 50 | 0 | 0 | 192 | 18 | 11 | 10 | 275 | 8 | 5 | 0 | 95 | 0 | 0 | 47 | 0 | 52 | 11 | 25 | 51 | 60 | 409 | 49 | 65 | 51 | 2 | 123 | 39 | 70 | 17 | 0 | 25 | 350 | 63 | 32 | 90 | 17 | 0 | 35 | 21 | 72 | 54 | 0 | 0 | 0 |  | 907 | 0 | 170 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 82 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 8 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 128 | 0 | 200 | 17 | 0 | 80 | 0 | 35 | 0 | 4 | 90 | 620 | 203 | 0 | 0 | 3 | 48 | 0 | 0 | 0 | 0 | 18 |  | 5586 | 2745 | 8331 | 2969 | 907 | 1523 | 0 | 1751 | 700 | 153 | 0 | 79 | 108 | 141 | 0 | 96.54
16:00 | 0 | 0 | 0 | 180 | 0 | 81 | 0 | 405 | 326 |  | 0 | 225 | 134 | 38 | 0 | 55 | 0 | 0 | 0 | 48 | 24 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 16 | 24 | 22 | 33 | 33 | 8 | 0 | 82 | 70 | 0 | 0 | 8 | 150 | 0 | 0 | 0 |  | 12 | 22 | 0 | 22 | 0 | 25 | 0 | 36 | 0 | 0 | 0 | 325 | 0 | 180 | 55 | 0 | 40 | 20 | 0 | 0 | 0 | 15 | 8 | 19 | 11 | 33 | 18 | 98 | 45 | 0 | 18 | 1 | 30 | 43 | 11 | 10 | 0 | 0 | 62 | 0 | 0 | 192 | 18 | 11 | 10 | 280 | 8 | 5 | 0 | 60 | 0 | 0 | 48 | 0 | 18 | 6 | 25 | 51 | 10 | 410 | 49 | 50 | 60 | 1 | 123 | 17 | 78 | 17 | 4 | 19 | 350 | 74 | 16 | 93 | 17 | 0 | 35 | 8 | 72 | 54 | 0 | 0 | 0 |  | 907 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 128 | 0 | 225 | 17 | 0 | 35 | 0 | 0 | 0 | 2 | 35 | 620 | 220 | 0 | 0 | 1 | 20 | 0 | 0 | 0 | 0 | 8 |  | 5513 | 2572 | 8085 | 3054 | 907 | 1654 | 0 | 1404 | 700 | 152 | 0 | 53 | 98 | 63 | 0 | 96.53
17:00 | 0 | 0 | 0 | 180 | 0 | 81 | 0 | 405 | 326 |  | 0 | 225 | 135 | 25 | 0 | 55 | 0 | 0 | 0 | 24 | 24 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 16 | 24 | 22 | 33 | 32 | 8 | 0 | 81 | 70 | 0 | 0 | 8 | 150 | 0 | 0 | 0 |  | 12 | 23 | 0 | 22 | 0 | 33 | 0 | 24 | 0 | 0 | 0 | 325 | 0 | 184 | 128 | 0 | 43 | 43 | 0 | 0 | 0 | 15 | 8 | 19 | 11 | 33 | 18 | 92 | 46 | 0 | 18 | 0 | 30 | 43 | 11 | 10 | 0 | 0 | 63 | 0 | 0 | 192 | 18 | 11 | 10 | 300 | 8 | 5 | 0 | 75 | 0 | 0 | 48 | 0 | 17 | 0 | 25 | 51 | 10 | 410 | 50 | 50 | 102 | 0 | 123 | 17 | 105 | 17 | 0 | 10 | 350 | 74 | 2 | 54 | 17 | 0 | 35 | 1 | 54 | 54 | 0 | 0 | 0 |  | 908 | 0 | 175 | 0 | 16 | 0 | 0 | 0 | 3 | 22 | 0 | 87 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 128 | 0 | 226 | 17 | 0 | 35 | 0 | 0 | 0 | 1 | 35 | 650 | 222 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 1 |  | 5576 | 2627 | 8203 | 3068 | 908 | 1764 | 0 | 1405 | 728 | 151 | 0 | 79 | 92 | 8 | 0 | 96.52
18:00 | 0 | 0 | 0 | 180 | 0 | 81 | 0 | 403 | 305 |  | 0 | 225 | 126 | 45 | 0 | 55 | 0 | 0 | 0 | 42 | 75 | 115 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 0 | 24 | 20 | 33 | 32 | 16 | 0 | 82 | 70 | 0 | 0 | 10 | 150 | 0 | 0 | 0 |  | 12 | 23 | 51 | 55 | 0 | 41 | 0 | 26 | 0 | 0 | 0 | 280 | 0 | 180 | 177 | 0 | 46 | 46 | 0 | 0 | 0 | 42 | 15 | 19 | 11 | 33 | 14 | 116 | 46 | 0 | 18 | 0 | 30 | 43 | 11 | 10 | 0 | 0 | 40 | 81 | 0 | 192 | 18 | 11 | 10 | 280 | 8 | 5 | 0 | 140 | 0 | 0 | 85 | 0 | 80 | 0 | 40 | 140 | 25 | 358 | 97 | 67 | 105 | 0 | 275 | 29 | 105 | 17 | 0 | 14 | 350 | 92 | 0 | 120 | 51 | 0 | 35 | 0 | 69 | 54 | 0 | 0 | 0 |  | 907 | 0 | 180 | 0 | 21 | 0 | 0 | 0 | 51 | 56 | 0 | 77 | 16 | 0 | 0 | 0 | 0 | 0 | 4 | 81 | 0 | 8 | 26 | 16 | 35 | 0 | 0 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129 | 0 | 226 | 34 | 0 | 40 | 0 | 24 | 0 | 0 | 90 | 680 | 200 | 0 | 0 | 0 | 0 | 91 | 0 | 0 | 0 | 0 |  | 6551 | 3070 | 9621 | 2919 | 907 | 1831 | 0 | 2454 | 758 | 152 | 0 | 484 | 116 | 0 | 0 | 96.51
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 0 | 81 | 0 | 360 | 305 |  | 0 | 225 | 124 | 81 | 0 | 55 | 0 | 0 | 0 | 79 | 92 | 82 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 16 | 24 | 28 | 33 | 32 | 8 | 0 | 83 | 70 | 0 | 0 | 25 | 141 | 0 | 0 | 0 |  | 12 | 23 | 51 | 55 | 0 | 21 | 0 | 32 | 0 | 0 | 0 | 280 | 0 | 179 | 177 | 0 | 46 | 50 | 0 | 0 | 0 | 47 | 32 | 19 | 11 | 33 | 18 | 116 | 67 | 0 | 18 | 0 | 30 | 43 | 11 | 10 | 0 | 0 | 40 | 50 | 0 | 192 | 18 | 11 | 10 | 255 | 8 | 5 | 0 | 248 | 0 | 0 | 87 | 0 | 93 | 0 | 50 | 51 | 63 | 329 | 98 | 88 | 105 | 0 | 282 | 54 | 105 | 92 | 0 | 43 | 313 | 93 | 0 | 162 | 53 | 0 | 35 | 0 | 110 | 54 | 0 | 0 | 0 |  | 907 | 0 | 175 | 0 | 32 | 0 | 0 | 0 | 39 | 74 | 0 | 74 | 17 | 0 | 0 | 0 | 0 | 24 | 4 | 50 | 0 | 16 | 32 | 16 | 35 | 0 | 0 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131 | 0 | 233 | 56 | 0 | 100 | 0 | 34 | 0 | 0 | 113 | 770 | 180 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 |  | 6846 | 3225 | 10071 | 2843 | 907 | 1771 | 0 | 2972 | 848 | 153 | 0 | 461 | 116 | 0 | 0 | 96.48
19:30 | 0 | 0 | 0 | 180 | 0 | 81 | 0 | 395 | 320 |  | 0 | 225 | 150 | 93 | 0 | 55 | 0 | 0 | 0 | 89 | 92 | 48 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 16 | 24 | 26 | 33 | 32 | 0 | 0 | 83 | 70 | 0 | 0 | 25 | 151 | 0 | 0 | 0 |  | 12 | 0 | 17 | 55 | 0 | 4 | 0 | 42 | 0 | 0 | 0 | 280 | 0 | 179 | 177 | 0 | 46 | 50 | 0 | 0 | 0 | 0 | 0 | 19 | 11 | 33 | 18 | 114 | 98 | 0 | 18 | 0 | 30 | 43 | 11 | 10 | 0 | 0 | 40 | 50 | 0 | 192 | 18 | 11 | 10 | 300 | 8 | 5 | 0 | 180 | 0 | 0 | 87 | 0 | 52 | 0 | 50 | 51 | 90 | 328 | 99 | 88 | 105 | 0 | 283 | 54 | 105 | 114 | 0 | 50 | 320 | 93 | 0 | 162 | 53 | 0 | 35 | 0 | 115 | 54 | 0 | 0 | 0 |  | 907 | 0 | 180 | 0 | 32 | 0 | 0 | 0 | 0 | 26 | 0 | 87 | 16 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132 | 0 | 233 | 56 | 0 | 113 | 0 | 34 | 0 | 0 | 113 | 800 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6801 | 3061 | 9862 | 2942 | 907 | 1866 | 0 | 2862 | 879 | 153 | 0 | 139 | 114 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 180 | 0 | 81 | 0 | 393 | 320 |  | 0 | 225 | 150 | 90 | 0 | 55 | 0 | 0 | 0 | 89 | 50 | 48 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 16 | 24 | 28 | 33 | 33 | 0 | 0 | 83 | 70 | 0 | 0 | 0 | 151 | 0 | 0 | 0 |  | 12 | 0 | 17 | 55 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 300 | 0 | 189 | 177 | 0 | 46 | 50 | 0 | 0 | 0 | 0 | 0 | 19 | 8 | 33 | 18 | 120 | 110 | 0 | 19 | 0 | 30 | 43 | 11 | 10 | 0 | 0 | 68 | 50 | 0 | 192 | 18 | 11 | 10 | 285 | 8 | 5 | 0 | 180 | 0 | 0 | 87 | 0 | 52 | 0 | 50 | 51 | 10 | 403 | 98 | 88 | 105 | 0 | 283 | 54 | 105 | 114 | 1 | 50 | 350 | 93 | 0 | 162 | 17 | 0 | 35 | 0 | 115 | 54 | 0 | 0 | 0 |  | 906 | 0 | 180 | 0 | 32 | 0 | 0 | 0 | 0 | 26 | 0 | 87 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132 | 0 | 232 | 61 | 0 | 113 | 0 | 34 | 0 | 0 | 113 | 790 | 222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6776 | 3048 | 9824 | 3116 | 906 | 1893 | 0 | 2677 | 868 | 153 | 0 | 91 | 120 | 0 | 0 | 96.49
21:00 | 0 | 0 | 0 | 180 | 0 | 81 | 0 | 402 | 322 |  | 0 | 225 | 140 | 92 | 0 | 55 | 0 | 0 | 0 | 89 | 50 | 16 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 16 | 24 | 28 | 33 | 33 | 0 | 0 | 84 | 70 | 0 | 0 | 0 | 151 | 0 | 0 | 0 |  | 12 | 0 | 17 | 55 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 285 | 0 | 179 | 177 | 0 | 46 | 51 | 0 | 0 | 0 | 0 | 0 | 19 | 11 | 33 | 18 | 120 | 110 | 0 | 19 | 0 | 30 | 43 | 11 | 10 | 0 | 0 | 68 | 50 | 0 | 192 | 18 | 11 | 10 | 280 | 8 | 5 | 0 | 180 | 0 | 0 | 88 | 0 | 52 | 0 | 50 | 51 | 10 | 406 | 98 | 88 | 105 | 0 | 285 | 17 | 105 | 114 | 9 | 50 | 350 | 92 | 0 | 162 | 17 | 0 | 35 | 0 | 115 | 54 | 0 | 0 | 0 |  | 906 | 0 | 190 | 0 | 32 | 0 | 0 | 0 | 0 | 26 | 0 | 87 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 133 | 0 | 246 | 75 | 0 | 113 | 0 | 34 | 0 | 0 | 35 | 790 | 222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6677 | 3009 | 9686 | 3117 | 906 | 1895 | 0 | 2568 | 867 | 154 | 0 | 59 | 120 | 0 | 0 | 96.48
22:00 | 0 | 0 | 0 | 180 | 0 | 81 | 0 | 401 | 322 |  | 0 | 225 | 140 | 45 | 0 | 55 | 0 | 0 | 0 | 89 | 40 | 16 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 16 | 24 | 28 | 33 | 33 | 0 | 0 | 84 | 70 | 0 | 0 | 0 | 152 | 0 | 0 | 0 |  | 12 | 0 | 17 | 55 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 285 | 0 | 180 | 177 | 0 | 50 | 51 | 0 | 0 | 0 | 0 | 0 | 19 | 11 | 33 | 18 | 118 | 112 | 0 | 19 | 0 | 30 | 43 | 11 | 10 | 0 | 0 | 68 | 50 | 0 | 185 | 18 | 11 | 10 | 285 | 8 | 5 | 0 | 95 | 0 | 0 | 88 | 0 | 52 | 0 | 50 | 51 | 10 | 406 | 99 | 88 | 105 | 0 | 123 | 17 | 105 | 114 | 9 | 50 | 350 | 93 | 0 | 162 | 17 | 0 | 35 | 0 | 115 | 54 | 0 | 0 | 0 |  | 908 | 0 | 190 | 0 | 32 | 0 | 0 | 0 | 0 | 26 | 0 | 87 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 135 | 0 | 253 | 76 | 0 | 113 | 0 | 34 | 0 | 0 | 35 | 790 | 222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6379 | 3023 | 9402 | 3119 | 908 | 1910 | 0 | 2267 | 867 | 154 | 0 | 59 | 118 | 0 | 0 | 96.47
23:00 | 0 | 0 | 0 | 180 | 0 | 81 | 0 | 400 | 323 |  | 0 | 225 | 135 | 34 | 0 | 55 | 0 | 0 | 0 | 89 | 40 | 16 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 0 | 24 | 28 | 33 | 33 | 0 | 0 | 84 | 70 | 0 | 0 | 0 | 151 | 0 | 0 | 0 |  | 12 | 0 | 17 | 55 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 285 | 0 | 180 | 177 | 0 | 50 | 49 | 0 | 0 | 0 | 0 | 0 | 19 | 11 | 33 | 18 | 118 | 112 | 0 | 17 | 0 | 30 | 43 | 11 | 10 | 0 | 0 | 69 | 50 | 0 | 180 | 18 | 11 | 10 | 280 | 8 | 5 | 0 | 45 | 0 | 0 | 88 | 0 | 52 | 0 | 50 | 51 | 10 | 407 | 99 | 88 | 105 | 0 | 123 | 17 | 105 | 17 | 9 | 50 | 370 | 91 | 0 | 122 | 17 | 0 | 35 | 0 | 115 | 54 | 0 | 0 | 0 |  | 907 | 0 | 195 | 0 | 25 | 0 | 0 | 0 | 0 | 26 | 0 | 87 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 138 | 0 | 253 | 76 | 0 | 113 | 0 | 34 | 0 | 0 | 35 | 790 | 223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6165 | 3023 | 9188 | 3124 | 907 | 1899 | 0 | 2060 | 867 | 154 | 0 | 59 | 118 | 0 | 0 | 96.46
24:00 | 0 | 0 | 0 | 180 | 0 | 81 | 0 | 400 | 322 |  | 0 | 225 | 133 | 35 | 0 | 55 | 0 | 0 | 0 | 60 | 40 | 0 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 0 | 21 | 28 | 33 | 33 | 0 | 0 | 84 | 70 | 0 | 0 | 0 | 151 | 0 | 0 | 0 |  | 12 | 0 | 17 | 22 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 285 | 0 | 180 | 177 | 0 | 50 | 49 | 0 | 0 | 0 | 0 | 0 | 19 | 11 | 33 | 10 | 114 | 113 | 0 | 19 | 0 | 30 | 43 | 11 | 10 | 0 | 0 | 69 | 50 | 0 | 178 | 19 | 11 | 10 | 280 | 8 | 5 | 0 | 15 | 0 | 0 | 48 | 0 | 49 | 0 | 25 | 51 | 10 | 406 | 49 | 88 | 105 | 0 | 123 | 17 | 63 | 17 | 9 | 29 | 400 | 71 | 0 | 54 | 17 | 0 | 35 | 0 | 115 | 54 | 0 | 0 | 0 |  | 907 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 144 | 0 | 264 | 76 | 0 | 113 | 0 | 34 | 0 | 0 | 35 | 790 | 221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5802 | 2988 | 8790 | 3155 | 907 | 1903 | 0 | 1675 | 865 | 154 | 0 | 17 | 114 | 0 | 0 | 96.45
KWH | 0 | 0 | 0 | 4381650 | 0 | 1913181 | 0 | 9381890 | 7380000 |  | 0 | 5308800 | 3249775 | 956160 | 0 | 1276094 | 0 | 0 | 0 | 1189440 | 876384 | 636000 | 0 | 0 | 0 | 0 | 637920 | 879634 | 600384 | 313380 | 465500 | 557640 | 812880 | 790000 | 234240 | 0 | 2000422 | 1684000 | 0 | 0 | 241135 | 3657260 | 0 | 0 | 0 |  | 297840 | 182592 | 234999 | 686280 | 0 | 190080 | 0 | 867840 | 0 | 0 | 0 | 7079300 | 0 | 3822000 | 1321454 | 0 | 381816 | 419040 | 0 | 0 | 0 | 217344 | 161611 | 438948 | 238680 | 688600 | 333300 | 2450880 | 1833600 | 0 | 421380 | 14450 | 717000 | 957240 | 264600 | 299880 | 0 | 0 | 1096992 | 758400 | 0 | 4568540 | 441000 | 261660 | 237240 | 7082000 | 192000 | 121100 | 0 | 2353527 | 0 | 0 | 1324800 | 0 | 1027870 | 141480 | 723840 | 1374720 | 812945 | 9069000 | 1324800 | 1642800 | 1755527 | 25563 | 3093709 | 794256 | 1755520 | 758100 | 84000 | 651840 | 8440000 | 1641600 | 366270 | 1795680 | 895745 | 0 | 886680 | 213664 | 1659840 | 1104120 | 4150900 | 0 | 0 |  | 21924363 | 0 | 4594464 | 0 | 294720 | 0 | 0 | 0 | 70560 | 242944 | 0 | 1946836 | 327606 | 0 | 0 | 0 | 0 | 31716 | 10728 | 104428 | 0 | 367920 | 50240 | 80640 | 59004 | 0 | 0 | 0 | 1796509 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3473027 | 0 | 5789309 | 875040 | 0 | 1454016 | 0 | 714739 | 0 | 38390 | 1176960 | 17964600 | 4543336 | 0 | 0 | 37380 | 573120 | 296256 | 0 | 0 | 0 | 203676 |  | 138572251 | 69042527 | 207614778 | 75365923 | 21924363 | 40024121 | 0 | 40949412 | 19761109 | 3684422 | 0 | 1840555 | 2450880 | 1613993 | 0
Fuel Cost | 0 | 0 | 0 | 6528658.5 | 0 | 2544530.73 | 0 | 9850984.5 | 7970400 |  | 0 | 5786592 | 3607250.25 | 10689868.8 | 0 | 16908245.5 | 0 | 0 | 0 | 17389612.8 | 12330722.88 | 10309560 | 0 | 0 | 0 | 0 | 8114342.4 | 11875059 | 8051149.44 | 235035 | 349125 | 0 | 0 | 0 | 3984422.4 | 0 | 540113.94 | 454680 | 0 | 0 | 3942557.25 | 3803550.4 | 0 | 0 | 0 |  | 3886812 | 3045634.56 | 3999682.98 | 9271642.8 | 0 | 2199225.6 | 0 | 2889907.2 | 0 | 0 | 0 | 7858023 | 0 | 4433520 | 1704675.66 | 0 | 431452.08 | 624369.6 | 0 | 0 | 0 | 3753530.88 | 2173667.95 | 601358.76 | 179010 | 1205050 | 249975 | 17597318.4 | 1998624 | 0 | 573076.8 | 230333 | 982290 | 1263556.8 | 460404 | 518792.4 | 0 | 0 | 2128164.48 | 1729152 | 0 | 4614225.4 | 948150 | 389873.4 | 469735.2 | 7082000 | 144000 | 92036 | 0 | 32125643.55 | 0 | 0 | 17858304 | 0 | 14235999.5 | 1653901.2 | 7470028.8 | 18778675.2 | 10787780.15 | 8343480 | 16109568 | 23754888 | 22207416.55 | 0 | 36320143.66 | 8649447.84 | 18661177.6 | 10287417 | 1082760 | 7678675.2 | 7764800 | 21258720 | 5292601.5 | 22787179.2 | 10193578.1 | 0 | 11580040.8 | 2553284.8 | 24847804.8 | 14541260.4 | 0 | 0 | 0 |  | 65773089 | 0 | 5145799.68 | 0 | 3068035.2 | 0 | 0 | 0 | 1270785.6 | 4372992 | 0 | 2180456.32 | 635555.64 | 0 | 0 | 0 | 0 | 531877.32 | 187632.72 | 1633253.92 | 0 | 6092755.2 | 849558.4 | 1099123.2 | 995397.48 | 0 | 0 | 0 | 10437717.29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4028711.32 | 0 | 5731415.91 | 11760537.6 | 0 | 17201009.28 | 0 | 9077185.3 | 0 | 424209.5 | 14288294.4 | 161861046 | 4634202.72 | 0 | 0 | 422767.8 | 6722697.6 | 4541604.48 | 0 | 0 | 0 | 0 |  | 611820306.59 | 344967710.88 | 956788017.47 | 75933113.04 | 65773089 | 46778856.71 | 0 | 529162381.83 | 172298763.29 | 994793.94 | 0 | 30949905.86 | 17597318.4 | 17299795.4 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 0 | 81 | 0 | 402 | 332 |  | 0 | 225 | 130 | 34 | 0 | 55 | 0 | 0 | 0 | 52 | 58 | 55 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 16 | 23 | 24 | 33 | 33 | 14 | 0 | 84 | 70 | 0 | 0 | 16 | 150 | 0 | 0 | 0 |  | 12 | 16 | 0 | 22 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 260 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 19 | 8 | 14 | 12 | 102 | 34 | 0 | 18 | 2 | 30 | 43 | 11 | 10 | 0 | 0 | 62 | 0 | 0 | 192 | 18 | 11 | 10 | 300 | 8 | 5 | 0 | 51 | 0 | 0 | 48 | 0 | 38 | 20 | 25 | 51 | 25 | 368 | 49 | 88 | 51 | 4 | 123 | 35 | 70 | 17 | 0 | 25 | 350 | 74 | 54 | 35 | 74 | 0 | 35 | 30 | 47 | 46 | 298 | 0 | 0 |  | 907 | 0 | 170 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 8 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131 | 0 | 221 | 17 | 0 | 69 | 0 | 75 | 0 | 6 | 90 | 670 | 162 | 0 | 0 | 5 | 87 | 35 | 0 | 0 | 0 | 30 |  | 8594 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 0 | 81 | 0 | 360 | 305 | 0 | 0 | 225 | 124 | 81 | 0 | 55 | 0 | 0 | 0 | 79 | 92 | 82 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 16 | 24 | 28 | 33 | 32 | 8 | 0 | 83 | 70 | 0 | 0 | 25 | 141 | 0 | 0 | 0 | 0 | 12 | 23 | 51 | 55 | 0 | 21 | 0 | 32 | 0 | 0 | 0 | 280 | 0 | 179 | 177 | 0 | 46 | 50 | 0 | 0 | 0 | 47 | 32 | 19 | 11 | 33 | 18 | 116 | 67 | 0 | 18 | 0 | 30 | 43 | 11 | 10 | 0 | 0 | 40 | 50 | 0 | 192 | 18 | 11 | 10 | 255 | 8 | 5 | 0 | 248 | 0 | 0 | 87 | 0 | 93 | 0 | 50 | 51 | 63 | 329 | 98 | 88 | 105 | 0 | 282 | 54 | 105 | 92 | 0 | 43 | 313 | 93 | 0 | 162 | 53 | 0 | 35 | 0 | 110 | 54 | 0 | 0 | 0 |  | 907 | 0 | 175 | 0 | 32 | 0 | 0 | 0 | 39 | 74 | 0 | 74 | 17 | 0 | 0 | 0 | 0 | 24 | 4 | 50 | 0 | 16 | 32 | 16 | 35 | 0 | 0 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131 | 0 | 233 | 56 | 0 | 100 | 0 | 34 | 0 | 0 | 113 | 770 | 180 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 |  | 10071 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 0 | 80 | 0 | 400 | 300 | 0 | 0 | 225 | 134 | 94 | 0 | 55 | 0 | 0 | 0 | 90 | 92 | 110 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 16 | 25 | 28 | 33 | 33 | 49 | 0 | 82 | 70 | 0 | 0 | 25 | 150 | 0 | 0 | 0 | 0 | 12 | 0 | 51 | 55 | 0 | 44 | 0 | 25 | 0 | 0 | 0 | 320 | 0 | 200 | 185 | 0 | 50 | 50 | 0 | 0 | 0 | 47 | 43 | 19 | 11 | 33 | 18 | 166 | 110 | 0 | 18 | 0 | 30 | 43 | 11 | 10 | 0 | 0 | 65 | 50 | 0 | 190 | 19 | 11 | 10 | 300 | 0 | 0 | 100 | 275 | 150 | 50 | 88 | 50 | 134 | 0 | 50 | 200 | 140 | 400 | 98 | 88 | 105 | 0 | 283 | 54 | 105 | 114 | 9 | 50 | 400 | 92 | 0 | 162 | 107 | 0 | 35 |  | 115 | 54 | 0 |  |  |  | 923 | 0 | 225 | 0 | 32 | 0 | 0 | 0 | 39 | 75 | 8 | 87 | 22 | 16 | 0 | 0 | 0 | 32 | 22 | 86 | 0 | 42 | 32 | 8 | 35 | 0 | 0 | 11 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 157 | 0 | 260 | 55 | 100 | 113 | 0 | 113 | 0 | 0 | 113 | 810 | 220 |  | 0 |  |  | 115
Forecast for Day | 0 | 0 | 0 | 180 | 0 | 80 | 0 | 400 | 350 | 0 | 0 | 225 | 134 | 70 | 0 | 55 | 0 | 0 | 0 | 63 | 74 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 16 | 23 | 28 | 33 | 33 | 0 | 0 | 82 | 70 | 0 | 0 | 25 | 150 | 0 | 0 | 0 | 0 | 12 | 0 | 17 | 22 | 0 | 30 | 0 | 10 | 0 | 0 | 0 | 320 | 0 | 180 | 185 | 0 | 50 | 50 | 0 | 0 | 0 | 40 | 8 | 19 | 11 | 33 | 15 | 143 | 90 | 0 | 18 | 1.6 | 30 | 43 | 11 | 10 | 0 | 0 | 66 | 0 | 0 | 190 | 19 | 11 | 10 | 305 | 0 | 0 | 0 | 225 | 0 | 0 | 45 | 0 | 80 | 20 | 38 | 100 | 70 | 400 | 90 | 88 | 70 | 5 | 140 | 54 | 70 | 114 | 0 | 25 | 400 | 74 | 50 | 35 | 17 | 0 | 35 | 30 | 53 | 54 | 0 |  |  |  | 923 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 8 | 0 | 0 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 157 | 0 | 260 | 75 | 0 | 113 | 0 | 100 | 0 | 8 | 113 | 810 | 195 |  | 0 | 6 | 100 | 70 |  |  |  | 12
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 0 | 70 | 0 | 400 | 352 | 0 | 0 | 225 | 134 | 12 | 0 | 55 | 0 | 0 | 0 | 46 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 16 | 24 | 8 | 30 | 33 | 0 | 0 | 80 | 70 | 0 | 0 | 17 | 151 | 0 | 0 | 0 | 0 | 12 | 0 | 17 | 22 | 0 | 22 | 0 | 15 | 0 | 0 | 0 | 320 | 0 | 181 | 185 | 0 | 50 | 50 | 0 | 0 | 0 | 0 | 0 | 19 | 8 | 33 | 0 | 102 | 91 | 0 | 19 | 1 | 30 | 43 | 11 | 10 | 0 | 0 | 65 | 0 | 0 | 110 | 19 | 11 | 10 | 305 | 0 | 0 | 0 | 27 | 0 | 0 | 47 | 0 | 0 | 10 | 25 | 17 | 6 | 407 | 47 | 35 | 34 | 1 | 69 | 17 | 51 | 17 | 9 | 25 | 370 | 0 | 26 | 35 | 17 | 0 | 35 | 7 | 53 | 17 | 0 | 0 | 0 | 0 | 717 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 157 | 0 | 232 | 53 | 0 | 35 | 0 | 34 | 0 | 2 | 35 | 720 | 195 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 0 | 16 | 0 |  |  |  |  | 42789967 |  | 0
42789967
| Minimum Generation |  | 7289 | 6:00
| Highest Generation |  | 10071 | 19:00
| Day Peak Generation |  | 8594 | 12:00
| Evening Peak Generation |  | 10071 | 19:00
| HVDC Max Flow |  | 908 | 4:00
| HVDC EvPeak Flow |  | 907 | 19:00
| Load factor L.F |  | 85.9% | [161 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2022-10-29
Till now the maximum generation is : - |  |  | 14782 | 21:00 | Hrs on | 2022-04-16
The Summary of Yesterday's |  | 2022-10-28 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 8594 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 7120 | MW
Evening Peak Generation : |  | 10071 | MW Hour : | 19:00 | Available Max Generation : |  | 12002 | MW
E.P. Demand (at gen end) : |  | 10071 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 11000 | MW
Maximum Generation : |  | 10071 | MW Hour : | 19:00 | Reserve(Generation end) |  | 1002 | MW
Total Gen. (MKWH) : |  | 207.6148 | System Load Factor : | 85.9% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | 168 | MW at | 19:30 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2022-10-29
Actual : | 96.36 | Ft.(MSL) , | Rule curve : | 108.7 | Ft.( MSL )
Gas Consumed : | Total = | 838.55 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 122711969.75
: |  | Coal : | 172298763.29 | Oil : | 560112287.69 | Total : | 855123020.73
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3906.3763 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1106.6085 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1460.6313 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1295.9437 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1103.2006 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 911.4085 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 407.36 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 332.0697 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 719.6165 |  |  | 0 | 0%
Total | 0 |  | 11243.215 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 2
2) Ghorasal-3, 7
3) Ashuganj-5
4) Baghabari-71,100 MW
5) Raozan unit-1 & 2
6) Siddhirganj 210 MW .
7) Shajibazar 330 MW
8) Sirajganj-2
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Pabna-Shahjadpur 132 kV Ckt was under shut down from 08:52 to 11:50 for breaker maintenance at
Shahjadpur end.
b) Mongla 132/33 kV T-1 transformer was shut down at 08:35 for A/M.
c) Sherpur(Bogura) 132 kV Bus-1 was under shut down from 09:11 to 17:33 for A/M.
d) Payra-Patuakhali 132 kV Ckt-1 was under shut down from 09:26 to 15:48 for C/M.
e) Shahjibazar Unit-9 was synchronized at 11:22.
f) Ashuganj(East) 400 MW GT tripped at 13:56 due to low gas pressure.
g) Sylhet 255 MW ST tripped at 04:27(29/10/2022) due generator vibration.
h) Halishahar 132/33 kV T-1 transformer was shut down at 07:12(29/10/2022) for A/M.
i) Sonargaon S/S-Orion Sonargaon P.P. 132 kV Ckt was shut down at 07:12(29/10/2022) for A/M.
j) Norail 132/33 kV T-2 transformer was under shut down from 07:07(29/10/2022) to 09:05(29/10/2022) for C/M. | [5 empty] | About 20 MW power interruption occurred under
Norail S/S area from 07:07(29/10/2022) to 09:05.
k) Madunaghat-Chandraghona 132 kV Ckt-2 was shut down at 07:42(29/10/2022) for A/M.
| Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2022-10-28 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Machine problem
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4381650
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 81 | 1913181 | Engine problem
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 360 | 9381890 | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 305 | 7380000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 5308800 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 81 | 956160 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 124 | 3249775 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 0 | 0 | Under maint.
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 55 | 1276094
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 16 | 313380 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 79 | 1189440 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 92 | 876384 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 637920
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 82 | 636000 | Engine problem
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 879634
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 600384 | Engine problem
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 52 | 1023140 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 812880
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 32 | 790000 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 8 | 234240 | Engine problem
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 248 | 2353527 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Fuel conservation
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 0 | 0 | Fuel conservation
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Fuel conservation
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 93 | 1027870 | Engine problem
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 88 | 1642800 | Engine problem
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 93 | 1641600 | Engine problem
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 1795680
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 213664
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 54 | 1104120
| Dhaka area Total |  |  |  | 5847 | 2687 | 51620213
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Machine problem
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 25 | 241135
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 141480
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 21 | 190080 | Engine problem
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 153 | 3684422 | Low water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 141 | 3657260 | ST Under maint
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 105 | 1755527
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 23 | 182592 | Fuel shortage
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 234999 | Engine problem
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 55 | 686280 | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 50 | 723840 | Engine problem
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 0 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 32 | 867840
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 25563
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 282 | 3093709 | Engine problem
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 794256
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 105 | 1755520
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 43 | 651840 | Engine problem
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 53 | 895745 | Engine problem
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Chattogram area Total |  |  |  | 2382 | 1193 | 19582088
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 179 | 3822000 | Gas shortage
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 280 | 7079300 | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | Gas shortage
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+136*1 | 284 | 0 | 4150900 | On test.
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 46 | 381816 | Gas shortage
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 50 | 419040 | Gas shortage
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 177 | 1321454 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 0 | 0 | Gas shortage
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 63 | 812945 | Fuel shortage
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 47 | 217344 | Engine problem
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Machine problem
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 51 | 1374720 | High voltage
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 438948
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 238680
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 116 | 2450880
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 688600 | Engine problem
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 32 | 161611 | Engine problem
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 18 | 333300 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Fuel conservation
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 92 | 758100 | Engine problem
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 84000 | Fuel shortage
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 35 | 886680 | Engine problem
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 110 | 1659840
| Cumilla Area Total |  |  |  | 3169 | 1359 | 27280158
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 67 | 1833600 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 421380 | Engine problem
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 14450
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 87 | 1324800 | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 98 | 1324800 | Engine problem
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 366270
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 297840 | Engine problem
| Mymensingh Area Total |  |  |  | 614 | 282 | 5583140
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 30 | 717000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 43 | 957240 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Gas shortage
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 11 | 264600 | Gas shortage
| Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 10 | 299880 | Gas shortage
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 5 | 121100 | Gas shortage
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 40 | 1096992 | Gas shortage
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 50 | 758400
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 192 | 4568540 | Machine problem
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 441000
| Sylhet 50MW PP (EPL) |  | NENP | 27*2 | 50 | 11 | 261660 | Gas shortage
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 8 | 192000 | Gas shortage
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 255 | 7082000 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 329 | 9069000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 237240
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 313 | 8440000
| Sylhet Area Total |  |  |  | 2477 | 1325 | 34506652
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Fuel shortage
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 907 | 21924363
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 32 | 294720 | Fuel shortage
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 39 | 70560 | Fuel shortage
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 74 | 242944 | Fuel shortage
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 175 | 4594464 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 0 | 0 | Fuel shortage
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Fuel conservation
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 56 | 875040 | Engine problem
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Fuel shortage
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 573120
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 0 | 0 | 0 | On test.
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 0 | 0 | 0 | 0 | On test.
| Khulna Area Total |  |  |  | 2384 | 1283 | 28575211
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Line O/L
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 17 | 327606 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 74 | 1946836 | Gas shortage
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 770 | 17964600 | Line O/L
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 180 | 4543336
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Line O/L
| Barisal Area Total |  |  |  | 1958 | 1041 | 24782378
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 24 | 31716 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 4 | 10728 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contract Expired
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 16 | 367920 | Engine problem
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 50240 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 131 | 3473027 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 233 | 5789309 | Gas shortage
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 35 | 59004 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 0 | 0 | Gas shortage
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 0 | 0 | Gas shortage
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 16 | 80640 | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 50 | 104428 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Fuel conservation
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 100 | 1454016
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 1176960
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 37380
| Rajshahi Area Total |  |  |  | 2129 | 754 | 12635368
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 78 | 1796509
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under maint.
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 34 | 714739 | low demand.
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 38390
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 35 | 296256
| Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 203676
| Rangpur Area Total |  |  |  | 750 | 147 | 3049570
| Total |  |  |  | 21710 | 10071 | 207614778
| Eastern Grid Total |  |  |  | 14489 | 6846 | 138572251
| Western Grid Total |  |  |  | 7221 | 3225 | 69042527
| National Grid Total |  |  |  | 21710 | 10071 | 207614778
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2022-10-28
| (a) ENTIRE EASTERN GRID : |  | 6401.6 | MW | (b) ENTIRE WESTERN GRID : |  | 2881.29 | MW
| i) Dhaka area |  | 3434.1 | MW | i) Khulna area |  | 1082.8 | MW
| ii) Chittagong area |  | 975.5 | MW | ii) Rajshahi area |  | 1000.8 | MW
| iii) Comilla area |  | 836 | MW | iii) Barisal area |  | 223.69 | MW
| iv) Mymensingh area |  | 757 | MW | iv) Rangpur area |  | 574 | MW
| v) Sylhet area |  | 399 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 9282.89 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 20 | 11:00 | Chowmuhani | 121 | 21:00 | Kaptai | 4 | 18:00 | Nawabganj | 35.2 | 18:00 | Sholosohor | 25 | 18:00
2 | AKSML | 50 | 03:00 | Chuadanga | 74 | 18:00 | Kazla | 77 | 20:00 | Netrakona | 86 | 18:00 | Shyampur | 172 | 00:00
3 | Aftabnagar | 26 | 12:00 | Coxsbazar | 100 | 18:30 | Keranigonj | 48 | 00:00 | New | 56 | 12:00 | Siddhirganj | 84 | 18:00
4 | Agargaon | 58 | 13:00 | Cumilla(N) | 109 | 18:00 | Khagrachori | 26 | 18:00 | Niamatpur | 71 | 18:30 | Sirajganj | 73 | 18:00
5 | Agrabad | 44 | 18:00 | Cumilla(S) | 124 | 18:30 | Khulna | 54 | 18:30 | Noapara | 28 | 18:00 | Sonargaon | 93 | 15:00
6 | Amnura | 38 | 18:00 | Daudkandi | 102 | 20:00 | Khulshi | 138 | 01:00 | PHP | 6 | 18:30 | Sreemongol | 44 | 18:00
7 | Ashuganj | 56 | 00:00 | Dhaka | 18 | 12:00 | Kishoreganj | 92 | 20:00 | Pabna | 77 | 18:30 | Srinagar | 30.9 | 20:00
8 | BSRM | 87 | 02:00 | Dhamrai | 84 | 18:00 | Kodda | 219 | 00:00 | Palashbari | 92 | 18:00 | Sunamganj | 35 | 19:30
9 | Bagerhat | 68 | 18:30 | Dhanmondi | 78 | 13:00 | Kulaura | 36 | 18:00 | Panchagarh | 52 | 18:00 | Sylhet | 108 | 18:00
10 | Bakulia | 90 | 19:00 | Dohazari | 80 | 18:00 | Kurigram | 44 | 09:00 | Patuakhali | 76 | 00:00 | TK | 16.8 | 18:00
11 | Banani | 23 | 18:00 | Faridpur | 95 | 18:30 | Kushtia | 100 | 18:00 | Payra | 0.86 | 11:00 | Tangail | 150 | 18:30
12 | Bangabhaban | 3 | 13:00 | Fatullah | 59 | 12:00 | Lalbag | 69 | 01:00 | Postogola | 30 | 12:00 | Thakurgaon | 60 | 18:00
13 | Barapukuria | 39 | 12:00 | Fenchuganj | 33 | 17:00 | Lalmonirhat | 33 | 18:00 | Purbachal | 12 | 12:00 | Tongi | 102 | 12:00
14 | Barguna | 12 | 00:00 | Feni | 79 | 18:00 | Madanganj | 82 | 18:00 | Purbasadipur | 89 | 18:00 | Ullon | 30 | 19:30
15 | Barishal | 78 | 13:00 | GPH | 86 | 20:00 | Madaripur | 68 | 20:00 | Rahanpur_I | 14.8 | 17:00 | Uttara | 61 | 18:00
16 | Barishal-230 | 40 | 00:00 | Ghorashal | 49 | 00:00 | Madartek | 57 | 13:00 | Rahim | 36 | 10:00 | UttaraNew | 11 | 13:00
17 | Baroaulia | 59 | 12:00 | Goalpara | 20 | 00:00 | Madunaghat | 48 | 18:00 | Rajbari | 44 | 18:00 | Zigatola | 39 | 12:00
18 | Baroirhat | 37 | 18:00 | Gollamari | 52 | 13:00 | Magura | 40 | 18:00 | Rajendrapur | 86 | 19:30
19 | Bashundhara | 115 | 13:00 | Gopalganj | 69.8 | 18:30 | Mahasthangarh | 46 | 18:30 | Rajshahi | 98 | 21:00
20 | BashundharaCement | 1 | 00:00 | Gulshan | 68 | 18:30 | Manikganj | 69 | 19:30 | Rajshahi-230 | 24 | 00:00
21 | Beanibazar | 44 | 18:00 | Halishahar | 62 | 18:30 | Maniknagar | 46 | 13:00 | Ramganj | 60 | 20:00
22 | Benapole | 44 | 18:00 | HaripurSBU | 146 | 01:00 | Matarbari | 31 | 18:00 | Rampur | 28 | 18:30
23 | Bhaluka | 116 | 20:00 | Hasnabad | 56 | 23:00 | Matuail | 47 | 02:00 | Rangamati | 12 | 18:00
24 | Bhandaria | 31 | 21:00 | Hathazari | 48 | 18:00 | Millgate | 54 | 12:00 | Rangpur | 98 | 18:30
25 | Bhangura | 24 | 18:00 | Ishurdi | 52 | 18:30 | Mirpur | 99 | 18:00 | Ruppur | 3.6 | 10:00
26 | Bheramara(GK) | 43 | 18:00 | Jaldhaka | 46 | 18:00 | Mirsorai | 1 | 00:00 | SSM | 3 | 12:00
27 | Bhulta | 211 | 04:00 | Jamalpur | 108 | 18:00 | Mithapukur | 22 | 18:00 | Saidpur | 69 | 18:30
28 | Bog-Sherpur | 50 | 18:00 | Jashore | 89 | 19:00 | Modern | 0 | 00:00 | Satkhira | 76 | 18:00
29 | Bogura | 114 | 18:00 | Jhenaidah | 86 | 18:30 | Mogbazar | 86 | 13:00 | Satmasjid | 75 | 13:00
30 | Borhanuddin | 17 | 22:00 | Joydebpur | 143 | 00:00 | Mongla | 26 | 00:00 | Savar | 146 | 15:00
31 | Brahmanbaria | 120 | 18:30 | Joypurhat | 38 | 18:00 | Motijheel | 21 | 12:00 | Shahjadpur | 65 | 18:00
32 | Cantonment | 112 | 18:00 | Juldah | 24 | 12:00 | Munshiganj | 76 | 21:00 | Shahjibazar | 88 | 18:00
33 | Chandpur | 43 | 01:00 | KSRM | 30 | 14:00 | Mymensingh | 162 | 18:00 | Shahmirpur | 34.5 | 00:00
34 | Chandraghona | 26 | 18:00 | Kabirpur | 221 | 18:00 | Naogaon | 90 | 18:30 | Shariatpur | 48 | 20:00
35 | Chapai | 61 | 18:30 | Kachua | 52 | 20:00 | Narail | 38 | 18:00 | Sherpur | 96 | 18:00
36 | Charsaidpur | 49.07 | 11:00 | Kallyanpur | 72 | 12:00 | Narinda | 38 | 12:00 | Shikalbaha | 25 | 18:00
37 | Chauddagram | 31 | 19:30 | Kalurghat | 1 | 00:00 | Narshingdi | 131 | 21:00 | Shikalbaha-230 | N/A | N/A
38 | Chhatak | 20 | 18:00 | Kamrangirchar | 63 | 12:00 | Natore | 88 | 18:00 | Shitalakhya | 86 | 13:00
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2022-10-28 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Bhulta | 399 | 19:00 | 381 | 11:00 | Kaliakoir | 398 | 02:00 | 377 | 11:00
| Bibiana | 404 | 18:30 | 392 | 07:00 | Payra | 422 | 06:00 | 417 | 19:30
| BIPTC | 401 | 04:00 | 394 | 18:00 | Rahanpur_I | 415 | 18:00 | 382 | 19:30
| Gopalganj_I | 423 | 06:00 | 415 | 11:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 229 | 18:30 | 217 | 11:00 | Hasnabad | 229 | 18:30 | 218 | 09:00
| AKSML | 237 | 19:00 | 228 | 05:00 | Hathazari | 240 | 18:00 | 226 | 06:00
| Aminbazar | 228 | 01:00 | 226 | 00:00 | Ishurdi | 238 | 00:00 | 228 | 11:00
| Ashuganj | 242 | 18:30 | 230 | 07:00 | Jhenaidah | 237 | 01:00 | 228 | 07:00
| Baghabari | 234 | 00:00 | 227 | 07:00 | Kaliakoir | 230 | 02:00 | 218 | 12:00
| Barapukuria | 226 | 00:00 | 210 | 07:00 | Keranigonj | 229 | 19:00 | 217 | 11:00
| Barishal | 245 | 06:00 | 241 | 21:00 | Khulna(S) | 242 | 00:00 | 232 | 11:00
| Bheramara | 235 | 00:00 | 225 | 11:00 | Maniknagar | 231 | 19:00 | 220 | 11:00
| Bhulta | 233 | 01:00 | 222 | 11:00 | Meghnaghat | 234 | 18:30 | 227 | 07:00
| Bibiana | 238 | 18:00 | 231 | 07:00 | Mirsorai | 238 | 18:00 | 221 | 07:00
| BIPTC | 238 | 00:00 | 227 | 11:00 | Rajshahi | 241 | 00:00 | 228 | 11:00
| Bogura | 230 | 00:00 | 221 | 08:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 248 | 06:00 | 245 | 02:00 | Rampura | 230 | 18:00 | 220 | 11:00
| BSRM | 237 | 18:00 | 224 | 07:00 | Shikalbaha | 239 | 19:00 | 223 | 07:00
| Cumilla(N) | 235 | 18:30 | 224 | 11:00 | Shyampur | 230 | 19:00 | 218 | 11:00
| Fenchuganj | 240 | 01:00 | 234 | 07:00 | Siddhirganj | 232 | 19:00 | 225 | 16:00
| Ghorashal | N/A | N/A | N/A | N/A | Sirajgonj | 231 | 00:00 | 225 | 10:00
| GPH | 237 | 18:00 | 222 | 07:00 | Tongi | 233 | 18:30 | 218 | 11:00
| Haripur | 230 | 21:00 | 221 | 11:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 133 | 01:00 | 126 | 11:00 | Lalbag | 134 | 19:00 | 127 | 11:00
| Agargaon | 137 | 01:00 | 130 | 11:00 | Lalmonirhat | 157 | 16:00 | 124 | 07:00
| Agrabad | 139 | 19:00 | 130 | 06:00 | Madanganj | 138 | 19:00 | 130 | 10:00
| AKS | 137 | 20:00 | 130 | 04:00 | Madaripur | 138 | 03:00 | 135 | 16:00
| Aminbazar | 138 | 01:00 | 136 | 02:00 | Madartek | 133 | 01:00 | 125 | 11:00
| Amnura | 134 | 00:00 | 125 | 07:00 | Madunaghat | 140 | 19:00 | 132 | 07:00
| Ashuganj | 137 | 18:00 | 135 | 07:00 | Magura | 137 | 01:00 | 132 | 11:00
| Bagerhat | 137 | 23:00 | 132 | 07:00 | Mahasthangarh | 139 | 00:00 | 130 | 07:00
| Bakulia | 139 | 18:00 | 131 | 06:00 | Manikganj | 133 | 00:00 | 122 | 17:00
| Banani | 140 | 01:00 | 128 | 11:00 | Maniknagar | 130 | 19:00 | 124 | 11:00
| Bangabhaban | 130 | 19:00 | 124 | 11:00 | Matarbari | 129 | 19:00 | 120 | 07:00
| Barapukuria | 139 | 00:00 | 128 | 07:00 | Matuail | 136.6 | 19:00 | 130 | 11:00
| Barguna | 137 | 03:00 | 134 | 12:00 | Millgate | 137 | 00:00 | 128 | 11:00
| Barishal | 138 | 03:00 | 135 | 20:00 | Mirpur | 138 | 18:30 | 130 | 11:00
| Barishal-230 | 140 | 06:00 | 136 | 13:00 | Mithapukur | 140 | 00:00 | 129 | 07:00
| Baroaulia | 141 | 18:00 | 132 | 06:00 | Modern | 137 | 18:30 | 130 | 07:00
| Baroirhat | 139 | 19:00 | 131 | 11:00 | Mogbazar | 134 | 01:00 | 127 | 11:00
| Bashundhara | 138 | 00:00 | 125 | 11:00 | Mongla | 136 | 19:00 | 131 | 07:00
| BashundharaCement | 138 | 19:00 | 130 | 10:00 | Motijheel | 130 | 19:00 | 124 | 11:00
| Beanibazar | 132 | 01:00 | 129 | 14:00 | Munshiganj | 138 | 19:00 | 131 | 09:00
| Benapole | 134 | 00:00 | 130 | 07:00 | Mymensingh | 133 | 09:00 | 123 | 07:00
| Bhaluka | 134 | 09:00 | 120 | 11:00 | Naogaon | 135 | 00:00 | 128 | 07:00
| Bhandaria | 139 | 03:00 | 135 | 19:00 | Narail | 136 | 02:00 | 130 | 11:00
| Bhangura | 141 | 00:00 | 137 | 07:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bheramara | 137 | 00:00 | 133 | 11:00 | Narshingdi | 134 | 13:00 | 128 | 05:00
| Bheramara(GK) | 140 | 00:00 | 135 | 11:00 | Natore | 136 | 00:00 | 129 | 07:00
| Bhulta | 131 | 13:00 | 126 | 06:00 | Nawabganj | 133 | 01:00 | 126 | 11:00
| Bog-Sherpur | 139 | 00:00 | 131 | 07:00 | Netrakona | 130 | 13:00 | 126 | 00:00
| Bogura | 139 | 00:00 | 131 | 07:00 | New | 138 | 00:00 | 128 | 11:00
| Bogura-230 | 140 | 00:00 | 134 | 07:00 | Niamatpur | 134 | 19:00 | 126 | 07:00
| Brahmanbaria | 132 | 19:00 | 129 | 10:00 | Noapara | 137 | 01:00 | 131 | 11:00
| Cantonment | 136 | 01:00 | 129 | 11:00 | Pabna | 137 | 00:00 | 131 | 11:00
| Chandpur | 142 | 18:00 | 132 | 09:00 | Palashbari | 137 | 00:00 | 129 | 16:00
| Chandraghona | 139 | 18:00 | 133 | 07:00 | Panchagarh | 137 | 00:00 | 121 | 07:00
| Chapai | 133 | 00:00 | 125 | 11:00 | Patuakhali | 136 | 00:00 | 133 | 11:00
| Charsaidpur | 138 | 19:00 | 131 | 07:00 | Payra | 138 | 06:00 | 136 | 07:00
| Chauddagram | 139 | 21:00 | 131 | 11:00 | PHP | 138 | 19:00 | 131 | 07:00
| Chhatak | 130 | 00:00 | 129 | 12:00 | Postogola | 140 | 19:00 | 132 | 11:00
| Chowmuhani | 137 | 21:00 | 130 | 10:00 | Purbachal | 139 | 01:00 | 128 | 11:00
| Chuadanga | 134 | 05:00 | 128 | 11:00 | Purbasadipur | 137 | 00:00 | 121 | 07:00
| Coxsbazar | 129 | 18:00 | 119 | 23:00 | Rahim | 136 | 18:00 | 131 | 11:00
| Cumilla(N) | 139 | 18:30 | 132 | 11:00 | Rajbari | 136 | 00:00 | 132 | 16:00
| Cumilla(S) | 139 | 18:30 | 130 | 13:00 | Rajendrapur | 135 | 00:00 | 121 | 08:00
| Daudkandi | 137 | 18:00 | 130 | 10:00 | Rajshahi | 134 | 00:00 | 126 | 07:00
| Dhaka | 133 | 02:00 | 126 | 11:00 | Rajshahi-230 | 132 | 00:00 | 125 | 11:00
| Dhamrai | 129 | 01:00 | 122 | 11:00 | Ramganj | 138 | 18:00 | 130 | 06:00
| Dhanmondi | 136 | 00:00 | 131 | 10:00 | Rampur | 138 | 18:30 | 131 | 10:00
| Dohazari | 137 | 18:00 | 130 | 11:00 | Rampura | 132 | 00:00 | 126 | 11:00
| Faridpur | 135 | 00:00 | 132 | 16:00 | Rangamati | 139 | 19:00 | 132 | 07:00
| Fatullah | 138 | 19:00 | 130 | 11:00 | Rangpur | 137 | 00:00 | 125 | 17:00
| Fenchuganj | 137 | 01:00 | 133 | 13:00 | Ruppur | 139 | 00:00 | 133 | 11:00
| Feni | 140 | 19:00 | 133 | 07:00 | Saidpur | 137 | 00:00 | 125 | 17:00
| Ghorashal | 139 | 13:00 | 132 | 11:00 | Satkhira | 135 | 00:00 | 130 | 07:00
| Goalpara | 137 | 03:00 | 131 | 11:00 | Satmasjid | 136 | 00:00 | 129 | 11:00
| Gollamari | 137 | 00:00 | 133 | 01:00 | Savar | 140 | 19:00 | 128 | 11:00
| Gopalganj | 138 | 18:30 | 133 | 11:00 | Shahjadpur | 143 | 00:00 | 138 | 11:00
| Gopalganj_I | 138 | 01:00 | 134 | 16:00 | Shahjibazar | 134 | 00:00 | 132 | 11:00
| Gulshan | 132 | 01:00 | 126 | 11:00 | Shahmirpur | 138 | 18:00 | 130 | 07:00
| Halishahar | 139 | 19:00 | 130 | 07:00 | Shariatpur | 138 | 08:00 | 133 | 22:00
| Haripur | 136 | 18:00 | 131 | 11:00 | Sherpur | 137 | 22:00 | 117 | 07:00
| HaripurSBU | 137 | 18:30 | 132 | 05:00 | Shikalbaha | 140 | 19:00 | 131 | 07:00
| Hasnabad | 139 | 18:00 | 134 | 07:00 | Shikalbaha-230 | 140 | 19:00 | 131 | 07:00
| Hathazari | 140 | 18:00 | 132 | 06:00 | Shitalakhya | 140 | 18:30 | 130 | 11:00
| Ishurdi | 138 | 00:00 | 132 | 11:00 | Sholosohor | 139 | 18:00 | 129 | 07:00
| Jaldhaka | 136 | 00:00 | 121 | 12:00 | Shyampur | 136 | 19:30 | 130 | 11:00
| Jamalpur | 139 | 23:00 | 119 | 07:00 | Shyampur-230 | 137 | 19:00 | 130 | 11:00
| Jashore | 135 | 00:00 | 129 | 11:00 | Siddhirganj | 136 | 18:00 | 130 | 11:00
| Jhenaidah | 138 | 00:00 | 132 | 11:00 | Sirajganj | 138 | 01:00 | 133 | 11:00
| Jhenaidah-230 | 137 | 01:00 | 133 | 07:00 | Sonargaon | 137 | 18:30 | 129 | 07:00
| Joydebpur | 140 | 00:00 | 131 | 11:00 | Sreemongol | 136 | 18:00 | 132 | 15:00
| Joypurhat | 136 | 18:30 | 129 | 07:00 | Srinagar | 133 | 01:00 | 127 | 11:00
| Juldah | 139 | 18:00 | 132 | 10:00 | SSM | 141 | 18:30 | 132 | 05:00
| Kabirpur | 134 | 13:00 | 122 | 07:00 | Sunamganj | 131 | 06:00 | 128 | 14:00
| Kachua | 139 | 08:00 | 132 | 11:00 | Sylhet | 133 | 03:00 | 132 | 00:00
| Kaliakoir | 135 | 00:00 | 118 | 11:00 | Tangail | 134 | 01:00 | 126 | 11:00
| Kallyanpur | 140 | 18:30 | 131 | 11:00 | Thakurgaon | 138 | 00:00 | 119 | 19:30
| Kalurghat | 140 | 19:00 | 131 | 07:00 | TK | 139 | 18:00 | 131 | 05:00
| Kamrangirchar | 133 | 18:00 | 126 | 11:00 | Tongi | 139 | 00:00 | 129 | 11:00
| Kaptai | 138 | 00:00 | 135 | 01:00 | Ullon | 132 | 00:00 | 126 | 11:00
| Kazla | 129 | 02:00 | 124 | 11:00 | Uttara | 139 | 21:00 | 130 | 10:00
| Keranigonj | 133 | 19:00 | 126 | 11:00 | UttaraNew | 138 | 01:00 | 129 | 11:00
| Khagrachori | 138 | 18:30 | 131 | 07:00 | Zigatola | 134 | 18:30 | 126 | 11:00
| Khulna | 137 | 00:00 | 131 | 07:00
| Khulna(S) | 138 | 01:00 | 132 | 11:00
| Khulshi | 137 | 18:00 | 129 | 03:00
| Kishoreganj | 131 | 06:00 | 127 | 11:00
| Kodda | 140 | 00:00 | 120 | 11:00
| KSRM | 139 | 18:30 | 131 | 07:00
| Kulaura | 135 | 00:00 | 133 | 11:00
| Kurigram | 136 | 00:00 | 122 | 07:00
| Kushtia | 138 | 00:00 | 133 | 11:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2022-10-28
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 804 | 5802 | 2988 | 8790 |  |  |  | QF-LDC-11
0:30 | 622 | 5985.5 | 2751.5 | 8737 | Date: | 2022-10-28
1:00 | 440 | 6169 | 2515 | 8684
1:30 | 508 | 5966 | 2491.5 | 8457.5
2:00 | 576 | 5763 | 2468 | 8231
2:30 | 656 | 5534.5 | 2489.5 | 8024 | [5 empty] | Gen. at Eve. Peak | 10071 | 10071 MW (19:00 )
3:00 | 736 | 5306 | 2511 | 7817 | [6 empty] | 19:00
3:30 | 763 | 5201.5 | 2513.5 | 7715 | [5 empty] | Gen. at Day Peak | 8594 | 8594 MW (12:00 )
4:00 | 790 | 5097 | 2516 | 7613 | [6 empty] | 12:00
4:30 | 805 | 4987 | 2517.5 | 7504.5 | [5 empty] | Highest Generation | 10071
5:00 | 820 | 4877 | 2519 | 7396 | [6 empty] | 19:00
5:30 | 835 | 4825 | 2517.5 | 7342.5
6:00 | 850 | 4773 | 2516 | 7289
6:30 | 815 | 4781.5 | 2531.5 | 7313
7:00 | 780 | 4790 | 2547 | 7337
7:30 | 665 | 4867 | 2616 | 7483
8:00 | 550 | 4944 | 2685 | 7629
8:30 | 700 | 5021 | 2694 | 7715
9:00 | 850 | 5098 | 2703 | 7801
9:30 | 920 | 5097.5 | 2702 | 7799.5
10:00 | 990 | 5097 | 2701 | 7798
10:30 | 990 | 5180.5 | 2721 | 7901.5
11:00 | 990 | 5264 | 2741 | 8005
11:30 | 970 | 5479 | 2820.5 | 8299.5
12:00 | 950 | 5694 | 2900 | 8594
12:30 | 770 | 5918 | 2901.5 | 8819.5
13:00 | 590 | 6142 | 2903 | 9045
13:30 | 717 | 5743 | 2815 | 8558
14:00 | 844 | 5344 | 2727 | 8071
14:30 | 877 | 5465 | 2736 | 8201
15:00 | 910 | 5586 | 2745 | 8331
15:30 | 885 | 5549.5 | 2658.5 | 8208
16:00 | 860 | 5513 | 2572 | 8085
16:30 | 815 | 5544.5 | 2599.5 | 8144
17:00 | 770 | 5576 | 2627 | 8203
17:30 | 579 | 6063.5 | 2848.5 | 8912
18:00 | 388 | 6551 | 3070 | 9621
18:30 | 327 | 6698.5 | 3147.5 | 9846
19:00 | 266 | 6846 | 3225 | 10071
19:30 | 168 | 6801 | 3061 | 9862
20:00 | 168 | 6776 | 3048 | 9824 |  |  |  | Executive Engineer
20:30 | 209 | 6726.5 | 3028.5 | 9755 |  |  |  | Network Operation Division
21:00 | 250 | 6677 | 3009 | 9686
21:30 | 298 | 6528 | 3016 | 9544
22:00 | 346 | 6379 | 3023 | 9402 |  |  |  |  | Page 6 of 7
22:30 | 485 | 6272 | 3023 | 9295
23:00 | 624 | 6165 | 3023 | 9188
23:30 | 714 | 5983.5 | 3005.5 | 8989
24:00 | 804 | 5802 | 2988 | 8790
10071 MW (19:00 )
8594 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2022-10-28 |  | Energy |  | 207614778
[13 empty] | 2022-10-28 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 3155 | 907 | 1903 | 0 | 1675 | 865 | 154 | 0 | 17 | 114 | 0 | 792
0:30 | 3161 | 906.5 | 1732 | 0 | 1832 | 763.5 | 154 | 0 | 75 | 113 | 0 | 396 | Date: | 2022-10-28
1:00 | 3167 | 906 | 1561 | 0 | 1989 | 662 | 154 | 0 | 133 | 112 | 0 | 0
1:30 | 3105 | 906 | 1560 | 0 | 1884 | 657 | 152 | 0 | 83.5 | 110 | 0 | 0 | [8 empty] | Total Energy | 207.6148 | Total Energy Gen 207.615 MKWHr Energy Not Served 0.570 MKWHr Energy Requirement 208.185 MKWHr
2:00 | 3043 | 906 | 1559 | 0 | 1779 | 652 | 150 | 0 | 34 | 108 | 0 | 0 | [8 empty] | Energy not Served | 0.57024
2:30 | 3088 | 905.5 | 1537 | 0 | 1537.5 | 682 | 150 | 0 | 17 | 107 | 0 | 0 | [8 empty] | Energy Requirement | 208.185
3:00 | 3133 | 905 | 1515 | 0 | 1296 | 712 | 150 | 0 | 0 | 106 | 0 | 0
3:30 | 3121 | 906.5 | 1566 | 0 | 1150.5 | 717 | 150 | 0 | 0 | 104 | 0 | 0 | [6 empty] | Shortage
4:00 | 3109 | 908 | 1617 | 0 | 1005 | 722 | 150 | 0 | 0 | 102 | 0 | 0
4:30 | 3116.5 | 907 | 1616.5 | 0 | 898.5 | 717 | 150 | 0 | 0 | 99 | 0 | 0
5:00 | 3124 | 906 | 1616 | 0 | 792 | 712 | 150 | 0 | 0 | 96 | 0 | 0
5:30 | 3138 | 906 | 1609.5 | 0 | 739 | 707 | 150 | 0 | 0 | 93 | 0 | 0
6:00 | 3152 | 906 | 1603 | 0 | 686 | 702 | 150 | 0 | 0 | 90 | 0 | 0
6:30 | 3217.5 | 906 | 1627 | 0 | 595.5 | 712 | 150.5 | 0 | 0 | 90 | 14.5 | 0 |  |  |  |  | Coal
7:00 | 3283 | 906 | 1651 | 0 | 505 | 722 | 151 | 0 | 0 | 90 | 29 | 0
7:30 | 3245.5 | 906.5 | 1620 | 0 | 672 | 737 | 151 | 0 | 0 | 88 | 63 | 0 |  |  |  | Oil |  |  |  | ,
8:00 | 3208 | 907 | 1589 | 0 | 839 | 752 | 151 | 0 | 0 | 86 | 97 | 0
8:30 | 3160 | 907 | 1551 | 0 | 993.5 | 737 | 151.5 | 0 | 0 | 86 | 129 | 0
9:00 | 3112 | 907 | 1513 | 0 | 1148 | 722 | 152 | 0 | 0 | 86 | 161 | 0
9:30 | 3101.5 | 907 | 1500 | 0 | 1146 | 717 | 152 | 0 | 0 | 90 | 186 | 0
10:00 | 3091 | 907 | 1487 | 0 | 1144 | 712 | 152 | 0 | 0 | 94 | 211 | 0
10:30 | 3133 | 907 | 1539.5 | 0 | 1127.5 | 732 | 153 | 0 | 0 | 87 | 222.5 | 0
11:00 | 3175 | 907 | 1592 | 0 | 1111 | 752 | 154 | 0 | 0 | 80 | 234 | 0
11:30 | 3161.5 | 907 | 1566 | 0 | 1400 | 748.5 | 154 | 0 | 35.5 | 91 | 236 | 0
12:00 | 3148 | 907 | 1540 | 0 | 1689 | 745 | 154 | 0 | 71 | 102 | 238 | 0
12:30 | 3169 | 907 | 1519 | 0 | 1893 | 735 | 154 | 0 | 104.5 | 107 | 231 | 0
13:00 | 3190 | 907 | 1498 | 0 | 2097 | 725 | 154 | 0 | 138 | 112 | 224 | 0
13:30 | 3190 | 907 | 1498 | 0 | 2097 | 725 | 154 | 0 | 138 | 112 | 224 | 0
14:00 | 3190 | 907 | 1498 | 0 | 2097 | 725 | 154 | 0 | 138 | 112 | 224 | 0
14:30 | 3079.5 | 907 | 1510.5 | 0 | 1924 | 712.5 | 153.5 | 0 | 108.5 | 110 | 182.5 | 0
15:00 | 2969 | 907 | 1523 | 0 | 1751 | 700 | 153 | 0 | 79 | 108 | 141 | 0
15:30 | 3011.5 | 907 | 1588.5 | 0 | 1577.5 | 700 | 152.5 | 0 | 66 | 103 | 102 | 0
16:00 | 3054 | 907 | 1654 | 0 | 1404 | 700 | 152 | 0 | 53 | 98 | 63 | 0
16:30 | 3068 | 907.5 | 1709 | 0 | 1404.5 | 714 | 151.5 | 0 | 66 | 95 | 35.5 | 0
17:00 | 3068 | 908 | 1764 | 0 | 1405 | 728 | 151 | 0 | 79 | 92 | 8 | 0
17:30 | 2993.5 | 907.5 | 1797.5 | 0 | 1929.5 | 743 | 151.5 | 0 | 281.5 | 104 | 4 | 0
18:00 | 2919 | 907 | 1831 | 0 | 2454 | 758 | 152 | 0 | 484 | 116 | 0 | 0
18:30 | 2881 | 907 | 1801 | 0 | 2713 | 803 | 152.5 | 0 | 472.5 | 116 | 0 | 0
19:00 | 2843 | 907 | 1771 | 0 | 2972 | 848 | 153 | 0 | 461 | 116 | 0 | 0
19:30 | 2942 | 907 | 1866 | 0 | 2862 | 879 | 153 | 0 | 139 | 114 | 0 | 0
20:00 | 3116 | 906 | 1893 | 0 | 2677 | 868 | 153 | 0 | 91 | 120 | 0 | 0
20:30 | 3116.5 | 906 | 1894 | 0 | 2622.5 | 867.5 | 153.5 | 0 | 75 | 120 | 0 | 0
21:00 | 3117 | 906 | 1895 | 0 | 2568 | 867 | 154 | 0 | 59 | 120 | 0 | 0
21:30 | 3118 | 907 | 1902.5 | 0 | 2417.5 | 867 | 154 | 0 | 59 | 119 | 0 | 0
22:00 | 3119 | 908 | 1910 | 0 | 2267 | 867 | 154 | 0 | 59 | 118 | 0 | 0
22:30 | 3121.5 | 907.5 | 1904.5 | 0 | 2163.5 | 867 | 154 | 0 | 59 | 118 | 0 | 0
23:00 | 3124 | 907 | 1899 | 0 | 2060 | 867 | 154 | 0 | 59 | 118 | 0 | 0
23:30 | 3139.5 | 907 | 1901 | 0 | 1867.5 | 866 | 154 | 0 | 38 | 116 | 0 | 0 | Max Temp. in Dhaka |  | 24.7° C | 31.7° C
24:00 | 3155 | 907 | 1903 | 0 | 1675 | 865 | 154 | 0 | 17 | 114 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 207.615 MKWHr Energy Not Served 0.570 MKWHr Energy Requirement 208.185 MKWHr
Note on W13: Author:

## Generation
g | 2022-10-28
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 84 | 80 | 80 | 80 | 80 | 80 | 81 | 81 | 82 | 82 | 84 | 84 | 84 | 84 | 83 | 82 | 81 | 82 |  | 83 | 83 | 83 | 84 | 84 | 84 | 84 | 2000422
2 | Karnaphuli Hydro PP Unit-4 & 5 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1684000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 25 | 25 | 25 | 0 |  |  |  | 2 | 8 | 8 | 8 | 16 | 25 | 8 | 8 | 8 | 8 | 10 |  | 25 | 25 | 0 |  |  |  |  | 241135
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 5 | 11 | 16 | 19 | 20 | 20 | 19 | 16 | 11 | 6 | 0 | [9 empty] | 141480
6 | Sikalbaha 225MW CCPP (Gas) | 152 | 150 | 152 | 151 | 151 | 151 | 151 | 152 | 151 | 151 | 151 | 150 | 150 | 149 | 151 | 150 | 150 | 150 |  | 141 | 151 | 151 | 151 | 152 | 151 | 151 | 3657260
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 34 | 34 | 0 | [13 empty] | 0 | 51 |  | 51 | 17 | 17 | 17 | 17 | 17 | 17 | 234999
12 | Hathazari 100 MW peaking PP | 24 | 0 | [8 empty] | 0 | 16 | 15 | 16 | 16 | 22 | 23 | 23 |  | 23 | 0 | [5 empty] | 182592
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 68 | 68 | 68 | 68 | 68 | 68 | 17 | 37 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 60 | 102 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 1755527
| Daudkandi 200 MW PP (B.Trac) |  | 0
14 | Titas 50 MW Peaking PP | 0 | 0 | [11 empty] | 46 | 47 | 15 | 15 | 42 |  | 47 | 0 | [5 empty] | 217344
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 276 | 210 | 0 | 0 | 0 | 0 | 0 | 2 | 15 | 15 | 15 | 51 | 145 | 95 | 95 | 60 | 75 | 140 |  | 248 | 180 | 180 | 180 | 95 | 45 | 15 | 2353527
19 | Ashuganj 195MW PP (APSCL-United) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 55 | 128 | 177 |  | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 1321454
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4381650
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 40 | 43 | 46 |  | 46 | 46 | 46 | 46 | 50 | 50 | 50 | 381816
33 | Ashuganj 225 MW CCPP | 153 | 141 | 140 | 135 | 133 | 133 | 131 | 123 | 120 | 131 | 136 | 160 | 153 | 170 | 181 | 180 | 184 | 180 |  | 179 | 179 | 189 | 179 | 180 | 180 | 180 | 3822000
34 | Ashuganj 450 MW CCPP(South) | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ashuganj 450 MW CCPP(North) | 280 | 280 | 280 | 280 | 270 | 270 | 270 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 325 | 325 | 325 | 280 |  | 280 | 280 | 300 | 285 | 285 | 285 | 285 | 7079300
| Ashuganj 420 MW CCPP(East) | 298 | 298 | 298 | 298 | 299 | 299 | 298 | 298 | 299 | 292 | 292 | 298 | 298 | 0 | [12 empty] | 4150900
35 | Ashuganj 55 MW PP (Precision) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [7 empty] | 4 | 20 | 43 | 46 |  | 50 | 50 | 50 | 51 | 51 | 49 | 49 | 419040
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 392 | 359 | 352 | 352 | 352 | 352 | 356 | 399 | 399 | 388 | 402 | 402 | 395 | 381 | 404 | 405 | 405 | 403 |  | 360 | 395 | 393 | 402 | 401 | 400 | 400 | 9381890
40 | Meghnaghat 450 MW CCPP(MPL) | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 |  | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 5308800
41 | Haripur 360MW CCPP(HPL) | 266 | 267 | 267 | 331 | 321 | 306 | 316 | 310 | 275 | 252 | 332 | 332 | 305 | 270 | 334 | 326 | 326 | 305 |  | 305 | 320 | 320 | 322 | 322 | 323 | 322 | 7380000
42 | RPCL 210MW CCPP | 107 | 106 | 107 | 107 | 108 | 109 | 108 | 73 | 73 | 72 | 34 | 34 | 34 | 34 | 34 | 45 | 46 | 46 |  | 67 | 98 | 110 | 110 | 112 | 112 | 113 | 1833600
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 0 | 6 | 24 | 37 | 48 | 53 | 54 | 50 | 44 | 32 | 16 | 2 | 0 | [8 empty] | 366270
44 | Fenchugonj CCPP Phase-1 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 717000
45 | Fenchugonj CCPP Phase-2 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 957240
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 30 | 30 | 62 | 62 | 61 | 50 | 62 | 63 | 40 |  | 40 | 40 | 68 | 68 | 68 | 69 | 69 | 1096992
48 | Shahjibazar 86MW PP (Shahjibazar) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 0 | [5 empty] | 81 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 758400
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 191 | 192 | 191 | 191 | 191 | 191 | 191 | 191 | 191 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192 |  | 192 | 192 | 192 | 192 | 185 | 180 | 178 | 4568540
51 | Sylhet 20 MW GTPP | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 19 | 441000
52 | Sylhet 50MW PP (EPL) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 261660
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 9 | 9 | 9 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 237240
54 | Hobiganj 11MW PP Cofidence-E | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 121100
55 | Fenchugonj 51 MW PP (Barakatullah) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 264600
56 | Shahjahanulla 25 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 192000
57 | Bibiana-II 341 MW CCPP (Summit) | 341 | 325 | 280 | 290 | 290 | 290 | 310 | 290 | 270 | 280 | 290 | 300 | 280 | 270 | 275 | 280 | 300 | 280 |  | 255 | 300 | 285 | 280 | 285 | 280 | 280 | 7082000
| Bibiyana South 400 MW | 360 | 320 | 320 | 320 | 360 | 360 | 400 | 360 | 340 | 320 | 392 | 350 | 370 | 345 | 350 | 350 | 350 | 350 |  | 313 | 320 | 350 | 350 | 350 | 370 | 400 | 8440000
58 | Nababganj 55 MW PP (Southern power ) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 600384
59 | Tangail Palli Power Gen 22 MW | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 297840
60 | Barabkunda 22 MW PP (Regent) | [26 empty] | 0
61 | Narshingdi 22 MW PP (Doreen) | 16 | 16 | 16 | 16 | 0 | 0 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 0 |  | 16 | 16 | 16 | 16 | 16 |  |  | 313380
62 | Tangail 22 MW PP (Doreen) | 16 | 16 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 19 | 19 | 19 | 17 | 19 | 421380
63 | Impoprt (Tripura) | 112 | 108 | 106 | 102 | 96 | 90 | 90 | 86 | 86 | 94 | 80 | 102 | 112 | 106 | 108 | 98 | 92 | 116 |  | 116 | 114 | 120 | 120 | 118 | 118 | 114 | 2450880
64 | Malancha, Ctg. EPZ (United) | 32 | 36 | 36 | 36 | 39 | 40 | 42 | 42 | 33 | 33 | 33 | 33 | 41 | 35 | 33 | 36 | 24 | 26 |  | 32 | 42 | 42 | 41 | 42 | 42 | 42 | 867840
65 | Feni 22MW PP (Doreen) | 18 | 18 | 18 | 18 | 18 | 18 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 438948
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 8 | 11 | 11 | 11 | 11 | 238680
67 | Jangalia 33MW PP (Summit) | 25 | 25 | 33 | 33 | 33 | 33 | 33 | 33 | 22 | 18 | 15 | 14 | 14 | 17 | 28 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 688600
68 | Cumilla 25 MW PP (Summit) | 18 | 18 | 18 | 0 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 18 | 18 | 14 |  | 18 | 18 | 18 | 18 | 18 | 18 | 10 | 333300
69 | Summit Ashulia | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 21 | 465500
70 | Summit Madhabdi | 28 | 28 | 28 | 28 | 0 | 20 | 28 | 28 | 28 | 28 | 20 | 24 | 19 | 15 | 15 | 22 | 22 | 20 |  | 28 | 26 | 28 | 28 | 28 | 28 | 28 | 557640
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 812880
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 0 | 0 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 32 | 32 |  | 32 | 32 | 33 | 33 | 33 | 33 | 33 | 790000
73 | Ghorashal 108MW PP (Regent) | 84 | 84 | 84 | 81 | 81 | 81 | 78 | 78 | 78 | 78 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 |  | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 1913181
| Feni Lanka Power | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 92 | 114 | 114 | 114 | 114 | 17 | 17 | 758100
| Chowmuhani 113 MW | [5 empty] | 5 | 9 | 9 | 9 | 0 | [5 empty] | 4 | 0 |  |  |  |  | 1 | 9 | 9 | 9 | 9 | 84000
| Manikgonj 162MW PP(MPGL) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 90 | 90 | 90 | 93 | 54 | 120 |  | 162 | 162 | 162 | 162 | 162 | 122 | 54 | 1795680
77 | Siddhirganj 100 PP(Dutch Bangla) | 60 | 60 | 60 | 60 | 25 | 9 | 8 | 16 | 32 | 32 | 32 | 52 | 70 | 30 | 33 | 48 | 24 | 42 |  | 79 | 89 | 89 | 89 | 89 | 89 | 60 | 1189440
78 | Gazipur 52 MW PP | 49 | 0 | [9 empty] | 14 | 49 | 16 | 16 | 8 | 8 | 16 |  | 8 | 0 | [5 empty] | 234240
79 | Kodda 150MW PP | 75 |  | 0 | [8 empty] | 55 | 123 | 32 | 16 | 16 | 16 | 115 |  | 82 | 48 | 48 | 16 | 16 | 16 |  | 636000
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 16 | 16 | 0 | 0 | 0 | 0 | [5 empty] | 15 | 25 | 8 | 8 | 8 | 8 | 15 |  | 32 | 0 | [5 empty] | 161611
| Gazipur 100 MW PP | 88 | 88 | 88 | 88 | 34 | 17 | 17 | 26 | 34 | 34 | 34 | 88 | 88 | 50 | 65 | 50 | 50 | 67 |  | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 1642800
| Kaptai 7 MW Solar PP | [6 empty] | 1 | 1 | 2 | 4 | 4 | 4 | 4 | 3 | 2 | 1 | 0 | [9 empty] | 25563
| Jodiac Power | 54 | 54 | 54 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 36 | 17 | 39 | 17 | 17 | 29 |  | 54 | 54 | 54 | 17 | 17 | 17 | 17 | 794256
| Karnaphuli Power Ltd. | 51 | 51 | 51 | 51 | 51 | 51 | 17 | 35 | 60 | 70 | 70 | 70 | 70 | 70 | 70 | 78 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 63 | 1755520
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP ( Summit) | 123 | 136 | 133 | 133 | 133 | 133 | 150 | 125 | 135 | 142 | 150 | 130 | 123 | 140 | 115 | 134 | 135 | 126 |  | 124 | 150 | 150 | 140 | 140 | 135 | 133 | 3249775
87 | Meghnaghat 100 MW(IEL) | 60 | 59 | 60 | 39 | 10 | 9 | 8 | 9 | 9 | 8 | 8 | 34 | 53 | 53 | 56 | 38 | 25 | 45 |  | 81 | 93 | 90 | 92 | 45 | 34 | 35 | 956160
| Meghnaghat 104 MW PP (OPCL) | 55 | 58 | 55 | 55 | 55 | 54 | 20 | 36 | 72 | 74 | 74 | 74 | 74 | 36 | 63 | 74 | 74 | 92 |  | 93 | 93 | 93 | 92 | 93 | 91 | 71 | 1641600
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 22 | 22 | 22 | 22 | 10 | 10 | 10 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 22 | 686280
92 | Fenchuganj 44MW (Energyprima) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 299880
93 | Ashuganj 51 MW PP (Midland)
94 | Gagnagar 102 MW PP (Digital Power) | 58 | 58 | 58 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 58 | 58 | 24 | 58 | 24 | 24 | 75 |  | 92 | 92 | 50 | 50 | 40 | 40 | 40 | 876384
95 | Patenga 50MW PP (Baraka) | [13 empty] | 11 | 25 | 25 | 33 | 41 |  | 21 | 4 | 0 |  |  |  |  | 190080
96 | Chattogram 108 MW PP (ECPV) | [26 empty] | 0
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 55 | 55 | 55 | 55 | 55 | 40 | 30 | 30 | 55 | 55 | 40 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1276094
100 | Manikganj 55 MW PP (Northern) | 35 | 35 | 35 | 35 | 35 | 35 | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 55 | 55 | 55 | 35 | 35 | 35 | 35 | 879634
101 | Kushiara 163 MW CCPP (KP)
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 0 | [9 empty] | 14450
103 | Kamalaghat 54 MW PP(Banco Energy) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 637920
104 | Keranigonj 300 MW PP (APR) | [26 empty] | 0
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 48 | 48 | 48 | 48 | 48 | 24 | 16 | 47 | 47 | 48 | 48 | 48 | 48 | 48 | 47 | 48 | 48 | 85 |  | 87 | 87 | 87 | 88 | 88 | 88 | 48 | 1324800
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 135 | 74 | 0 | [5 empty] | 15 | 16 | 16 | 38 | 94 | 88 | 52 | 18 | 17 | 80 |  | 93 | 52 | 52 | 52 | 52 | 52 | 49 | 1027870
115 | Juldah 100 MW PP Unit-3 (Acorn) | 25 | 25 | 25 | 25 | 25 | 10 | 10 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 40 |  | 50 | 50 | 50 | 50 | 50 | 50 | 25 | 723840
116 | Chandpur 200MW (Desh energy) | 51 | 51 | 51 | 51 | 51 | 17 | 17 | 28 | 51 | 51 | 46 | 51 | 51 | 51 | 51 | 51 | 51 | 140 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1374720
117 | Ashuganj 150MW PP (Midland) | 68 | 67 | 68 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 25 | 46 | 61 | 60 | 10 | 10 | 25 |  | 63 | 90 | 10 | 10 | 10 | 10 | 10 | 812945
118 | Bibiyana-III 400 MW CCPP | 367 | 329 | 328 | 328 | 369 | 370 | 407 | 386 | 328 | 350 | 410 | 368 | 409 | 374 | 409 | 410 | 410 | 358 |  | 329 | 328 | 403 | 406 | 406 | 407 | 406 | 9069000
| Jamalpur 115 MW PP (United) | 49 | 49 | 49 | 24 | 8 | 8 | 8 | 47 | 47 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 50 | 97 |  | 98 | 99 | 98 | 98 | 99 | 99 | 49 | 1324800
| Anwara 300 MW PP (United) | 69 | 69 | 69 | 68 | 70 | 70 | 70 | 70 | 120 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 275 |  | 282 | 283 | 283 | 285 | 123 | 123 | 123 | 3093709
| Juldah unit-2 (Acorn) | 25 | 25 | 25 | 25 | 10 | 10 | 10 | 19 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 19 | 10 | 14 |  | 43 | 50 | 50 | 50 | 50 | 50 | 29 | 651840
| Anlima Energy Ltd. | 107 | 107 | 34 | 0 |  |  |  | 6 | 17 | 17 | 17 | 74 | 107 | 25 | 17 | 17 | 17 | 51 |  | 53 | 53 | 17 | 17 | 17 | 17 | 17 | 895745
| Bhairob 54.5 MW | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 886680
| Spectra Solar Plant Ltd. | [5 empty] | 0 | 4 | 15 | 22 | 28 | 31 | 30 | 30 | 25 | 21 | 8 | 1 | 0 | [8 empty] | 213664
| Chandpur 115(Doreen) | 53 | 53 | 53 | 53 | 53 | 53 | 20 | 35 | 52 | 30 | 17 | 47 | 68 | 71 | 72 | 72 | 54 | 69 |  | 110 | 115 | 115 | 115 | 115 | 115 | 115 | 1659840
| Kanchan Purbachal Power Generation Ltd. | 54 | 53 | 54 | 54 | 0 | 12 | 17 | 28 | 36 | 36 | 36 | 46 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1104120
| Mirsharai 150 MW (Oil) | [26 empty] | 0
Mirsharai 150 MW (Gas)
120 | Eastern Zone Total | 6169 | 5763 | 5306 | 5097 | 4877 | 4773 | 4790 | 4944 | 5098 | 5097 | 5264 | 5694 | 6142 | 5344 | 5586 | 5513 | 5576 | 6551 |  | 6846 | 6801 | 6776 | 6677 | 6379 | 6165 | 5802 | 138572251
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | 0 |  |  |  |  | 0 | 0 |  | 3 | 16 | 16 | 16 | 16 | 16 | 16 | 0 | 16 | 21 |  | 32 | 32 | 32 | 32 | 32 | 25 | 0 | 294720
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [16 empty] | 3 | 51 |  | 39 | 0 | [5 empty] | 70560
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 56 | 56 | 56 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 34 |  | 56 | 56 | 61 | 75 | 76 | 76 | 76 | 875040
130 | Mongla Orion 100 MW Solar PP | [6 empty] | 11 | 33 | 57 | 76 | 84 | 87 | 80 | 68 | 48 | 20 | 3 | 0 | [8 empty] | 573120
131 | Rampal 1320 MW (BIFPCL)
132 | United Payra Power Ltd. | [26 empty] | 0
133 | Bhola Nutan Biddut BD LTD (GAS) | 169 | 170 | 168 | 168 | 169 | 168 | 169 | 177 | 167 | 160 | 161 | 162 | 183 | 200 | 203 | 220 | 222 | 200 |  | 180 | 180 | 222 | 222 | 222 | 223 | 221 | 4543336
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [26 empty] | 0
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP |  |  | 89 | 88 | 87 | 87 | 87 | 87 | 87 | 87 | 83 | 87 | 87 | 88 | 82 | 86 | 87 | 77 |  | 74 | 87 | 87 | 87 | 87 | 87 | 87 | 1946836
140 | Bhola 33 MW PP (Venture) | 9 | 0 |  | 19 | 17 | 16 | 15 | 12 | 13 | 12 | 14 | 14 | 14 | 14 | 11 | 10 | 12 | 16 |  | 17 | 16 | 17 | 18 | 20 | 19 | 17 | 327606
141 | Noapara 100 MW PP (Bangla Trac) | [26 empty] | 0
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP | 0 | 0 | [14 empty] | 22 | 56 |  | 74 | 26 | 26 | 26 | 26 | 26 | 0 | 242944
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 906 | 906 | 905 | 908 | 906 | 906 | 906 | 907 | 907 | 907 | 907 | 907 | 907 | 908 | 907 | 907 | 908 | 907 |  | 907 | 907 | 906 | 906 | 908 | 907 | 907 | 21924363
147 | Bheramara 410 MW CCPP | 195 | 195 | 195 | 195 | 205 | 210 | 205 | 200 | 195 | 190 | 180 | 170 | 170 | 170 | 170 | 170 | 175 | 180 |  | 175 | 180 | 180 | 190 | 190 | 195 | 200 | 4594464
148 | Payra 1320 MW | 590 | 580 | 640 | 650 | 640 | 630 | 650 | 680 | 650 | 640 | 680 | 670 | 650 | 620 | 620 | 620 | 650 | 680 |  | 770 | 800 | 790 | 790 | 790 | 790 | 790 | 17964600
149
150 | Barapukuria TPP Unit-1 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 75 | 75 | 84 | 80 | 80 | 78 | 78 |  | 78 | 79 | 78 | 77 | 77 | 77 | 75 | 1796509
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [19 empty] | 24 | 24 | [5 empty] | 31716
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 2 | 3 | 5 | 5 | 5 | 5 | 5 | 3 | 1 | 0 | [9 empty] | 37380
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 134 | 135 | 136 | 137 | 137 | 138 | 139 | 139 | 140 | 136 | 132 | 131 | 131 | 128 | 128 | 128 | 128 | 129 |  | 131 | 132 | 132 | 133 | 135 | 138 | 144 | 3473027
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 240 | 244 | 250 | 262 | 269 | 272 | 274 | 258 | 246 | 234 | 235 | 221 | 204 | 200 | 200 | 225 | 226 | 226 |  | 233 | 233 | 232 | 246 | 253 | 253 | 264 | 5789309
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | 0 | 0 | [15 empty] | 4 |  | 4 | 0 | [5 empty] | 10728
162 | Bogra 22 MW PP (GBB) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [19 empty] | 0
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit)
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | 25 | 25 | 0 |  |  |  |  | 16 | 16 | 16 | 16 | 25 | 25 | 25 | 25 | 0 |  | 8 |  | 16 | 25 | 25 | 25 | 25 | 25 | 25 | 367920
167 | Katakhali 50 MW Peaking PP | 0 | 0 | [15 empty] | 26 |  | 32 | 0 | [5 empty] | 50240
168 | Santahar 50 MW Peaking PP | 0 | 0 | [15 empty] | 35 |  | 35 | 0 | [5 empty] | 59004
169 | Natore 52 MW PP (Rajlanka) | 0 | 0 | [9 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 16 |  | 16 | 0 | [5 empty] | 80640
170 | Chapainawabganj 100 MW Peaking PP | 0 | 0 | [15 empty] | 81 |  | 50 | 24 | 0 |  |  |  |  | 104428
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 50 | 50 | 0 |  |  |  |  | 6 | 35 | 35 | 35 | 69 | 106 | 35 | 80 | 35 | 35 | 40 |  | 100 | 113 | 113 | 113 | 113 | 113 | 113 | 1454016
172 | Confidence Power Bogura Unit-1 113 MW | 35 | 35 | 0 |  |  |  |  | 35 | 35 | 35 | 35 | 90 | 70 | 35 | 90 | 35 | 35 | 90 |  | 113 | 113 | 113 | 35 | 35 | 35 | 35 | 1176960
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | 34 | 0 | [5 empty] | 34 | 38 | 34 | 34 | 75 | 86 | 40 | 35 | 0 |  | 24 |  | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 714739
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 2 | 4 | 5 | 6 | 6 | 6 | 4 | 2 | 1 | 0 | [8 empty] | 38390
178 | Energypac Power Venture Thakurgaon Ltd. | 0 | 0 | [9 empty] | 35 | 35 | 35 |  |  |  | 91 |  | 35 | 0 | [5 empty] | 296256
178 | Intraco Solar 30 MW | [6 empty] | 2 | 9 | 20 | 25 | 30 | 30 | 28 | 25 | 18 | 8 | 1 | 0 | [8 empty] | 203676