## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2022-11-06 | Sunday
|  | Date (day): | 2022-11-06 |  | Sunday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 9530.6 | MW |  |  | (b) At Evening Peak Hour : |  | 12188 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2022-11-05 | 2022-11-06 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Line O/L
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 140 | 180 | 180 |  | 365 | Machine problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 73 | 73 | 73 | 73 |  | 35 | Engine problem
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 397 | 348 | 0 | 0 | 412 |  | Gas line maintenance
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 248 | 192 | 200 | 250 | 110 |  | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 200 | 190 | 200 | 200 | 250 |  | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 46 | 92 | 70 | 92 |  | 8 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 135 | 112 | 0 | 0 | 335 |  | Gas line maintenance
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 0 | 0 | 0 | 0 |  | 102 | Under maint
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 63 | 88 | 70 | 88 |  | 12 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 58 | 92 | 60 | 92 |  | 10 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 54 | 17 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 98 | 132 | 115 | 132 |  | 17 | Engine problem
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 42 | 51 | 52 | 55 |  | 25 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 0 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 28 | 29 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 49 | 49 | 49 | 49
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 185 | 276 | 275 | 280 |  | 20 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 150 | 150 |  | Fuel conservation
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 0 | 0 | 0 | 50 | 50 |  | Fuel conservation
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 50 | 50 |  | Fuel conservation
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 149 | 133 | 134 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 88 | 100 | 70 | 100 |  | 5 | Engine problem
37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 71 | 93 | 74 | 92 | 12 |  | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 35 | 144 | 35 | 162
39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 30 | 0 | 30 | 0
40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 17 | 17 | 38 |  | Fuel shortage
| Dhaka area Total |  |  |  |  | 6263 | 5847 | 2359 | 2788 | 2154 | 2748 | 2003 | 1279
41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 6 | 25 | 25 | 25
43 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 9 | 0 | 20 | 0
44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 39 | 44 | 24 | 44 |  | 6 | Engine problem
45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 118 | 154 | 154 | 154 | 76 |  | Low Water Level
46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 151 | 150 | 150 | 150 |  | 75 | ST under maint
47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 51 | 105 | 70 | 105
49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 23 | 22 | 22 | 76 |  | Fuel shortage
50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 17 | 51 | 17 | 51 | 51 |  | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 100 | 66 | 22 | 75 | 25 |  | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 50 | 50 | 25 | 50 |  | 50 | Engine problem
53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  | 22 | Engine problem
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 3 | 12 | 7 | 15
54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 123 | 300 | 125 | 300
57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 36 | 36 | 36 | 54
58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 71 | 91 | 70 | 105 |  | 5
59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 50 | 50 | 25 | 50 |  | 50 | Engine problem
60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 107 | 107 | 107 | 107 |  | 9 | Engine problem
| Mirsharai 150 MW |  | Gas/HSD | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0
| Chattogram area Total |  |  |  |  | 2442 | 2382 | 935 | 1264 | 904 | 1307 | 696 | 367
61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 169 | 191 | 175 | 190 | 31 |  | Gas shortage
63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 340 | 310 | 360 | 360 | 0
64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 | 360 |  | Gas shortage
| Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+136*1 | 284 | 284 | 0 | 0 | 0 | 0 |  |  | On test.
65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 47 | 50 | 50 | 51
66 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 55 | 48 | 30 | 30 | 55
67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 168 | 168 | 170 | 180
68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 0 | 0 | 0 | 0
69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 40 | 68 | 64 | 100 |  | 50 | Engine problem
70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 19 | 43 | 32 | 43 |  | 9 | Engine problem
71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 49 | 50 | 50 | 50 | 113 |  | Gas shortage.
72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 51 | 200 | 51 | 200
73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 19 | 16 | 19
74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 10 | 10 | 10 | 10
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 128 | 136 | 143 | 166
75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 7 | 30 | 33 | 33
76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 29 | 8 | 43 | 9 |  | Engine problem
77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 12 | 21 | 21 | 21 |  | 4 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 100 | 100 |  | Fuel conservation
79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 96 | 114 | 17 | 114
80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 0 | 9 | 104 |  | Fuel shortage
81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 35 | 17 | 35 |  | 19 | Engine problem
82 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 52 | 115 | 53 | 115
| Cumilla Area Total |  |  |  |  | 3193 | 3169 | 1261 | 1619 | 1300 | 1894 | 851 | 82
83 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 33 | 55 | 102 | 100 | 102 |  | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 13 | 13 | 18 | 18 |  | 4 | Gas shortage
85 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0
86 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1 | 0 | 1.6 | 0
87 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 48 | 88 | 48 | 98 | 102 |  | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 49 | 99 | 50 | 100 |  | 15 | Engine problem
89 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 35 | 0 | 50 | 0
90 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 6 | 12 | 12 |  | 10 | Engine problem
| Mymensingh Area Total |  |  |  |  | 717 | 614 | 185 | 261 | 281.6 | 328 | 102 | 29
91 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 30 | 30 | 30 | 30 |  | 40 | Machine problem.
92 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 43 | 42 | 0 | 43 |  | 47 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 | 163 |  | Gas shortage
94 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 53 | 41 | 41 | 53 | 50 |  | Gas shortage
96 | Fenchuganj 44MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 44 | 30 | 30 | 44 | 6 |  | Gas shortage
97 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0
98 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 62 | 65 | 66 | 65
99 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 20 | 81 | 0 | 80
100 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
101 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 90 | 20 | 145 |  | 86 | ST Sync process.
102 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 19 | 19
103 | Sylhet 50MW PP (EPL) |  | Gas | NENP | 27*2 | 50 | 50 | 23 | 16 | 11 | 11 | 39 |  | Gas shortage
104 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 0 | 0 | 0 | 0 | 25 |  | Gas shortage
105 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 290 | 270 | 330 | 330 |  |  | FGMO
106 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 408 | 415 | 400 | 400
107 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 8 | 10 | 10 | 10
108 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 380 | 398 | 400 | 400
| Sylhet Area Total |  |  |  |  | 2522 | 2477 | 1379 | 1506 | 1357 | 1630 | 283 | 603
109 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 912 | 913 | 918 | 918
110 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 0 | 49 | 0 | 49 | 66 |  | Fuel shortage
111 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 42 | 0 | 42 | 12 |  | Fuel shortage
112 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
113 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 82 | 0 | 82 | 27 |  | Fuel shortage
114 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 180 | 170 | 190 | 190 | 220 |  | Gas shortage
115 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 8 | 0 | 8 | 32 |  | Fuel shortage
116 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 0 | 50 | 50 |  | Fuel conservation
117 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 54 | 60 | 94 |  | 11 | Engine problem
118 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Fuel shortage
119 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 84 | 0 | 100 | 0
| Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 2388 | 2384 | 1176 | 1318 | 1268 | 1433 | 758 | 11
120 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 0 | 16 |  |  | Line O/L
121 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 0 | 0 | 16 | 22 |  | 18 | Engine problem
122 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 62 | 60 | 65 | 65 |  | 129 | Machine problem
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
123 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 630 | 900 | 850 | 950 |  |  | Line O/L
124 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 64 | 220 | 220 | 220
125 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 0 | 0 |  |  | Line O/L
| Barisal 307 MW |  | Coal | BCPCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Barisal Area Total |  |  |  |  | 1958 | 1958 | 756 | 1180 | 1151 | 1273 | 0 | 147
126 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
127 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 32 | 0 | 32 |  | 20 | Engine problem
128 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 18 | 0 | 22 |  | 49 | Engine problem
129 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
130 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 8 | 34 | 0 | 42 |  | 8 | Engine problem
131 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 32 | 0 | 32 | 18 |  | Fuel shortage
132 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 176 | 161 | 160 | 160 | 50 |  | Gas shortage
133 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Fuel shortage
134 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
135 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 250 | 231 | 270 | 270 | 144 |  | Gas shortage
136 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 34 | 0 | 34 |  | 16 | Engine problem
137 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 16 | 20 | 20 | 20
138 | Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
139 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 8 | 11
140 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 8 | 8 | 43 | 9 |  | Fuel shortage
141 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 86 | 0 | 86 |  | 18 | Engine problem
142 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 0 | 100 | 100 |  | Fuel conservation
143 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 94 | 35 | 95 |  | 18 | Engine problem
144 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 75 | 113 | 95 | 113
145 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
| Rajshahi Area Total |  |  |  |  | 2199 | 2129 | 541 | 874 | 602 | 1060 | 932 | 129
146 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 10 | 80 | 80
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
147 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 250 | 250 | 250 | 250
148 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
149 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
150 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 113 | 113 | 50 | 70
151 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 6 | 0 | 8 | 0
152 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 0 | 114 | 113 | 115
| Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 33 | 0 | 12 | 0
| Rangpur Area Total |  |  |  |  | 830 | 750 | 402 | 487 | 513 | 515 | 40 | 85
| Total |  |  |  |  | 22512 | 21710 | 8994 | 11297 | 9530.6 | 12188 | 5665 | 2732
A. |  | 2022-11-05 | (Yesterday) |  |  |  |  | Saturday
1 | Highest Generation : |  |  | 11297 | MW at | 20:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 20:00 | hrs.
2 | Minimum Generation : |  |  | 7474 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 11297 | MW
3 | Day peak Generation : |  |  | 8994 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 10814.8 | MW
4 | Evening peak Generation : |  |  | 11297 | MW at | 20:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 222.3088 | MKWHr | By Solar | 1.4416 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Gas : | 112.9074 | MKWHr |  | By Oil: | 55.4797 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 25.4439 | MKWHr |  | By Hydro: | 3.3908 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 5665 | MW | Dhaka | 4271.72 | 4271.72 |  | 0 |  | 18:00 |  | 686
|  |  | For Plants S/D or M/C prob = |  |  | 2732 | MW | Chittagong | 1189.3 | 1189.3 |  | 0 |  | 19:00 |  | 353
|  |  | Total = |  |  | 8397 | MW | Khulna | 1147.6 | 1147.6 |  | 0 |  | 19:30 |  | 229
7 | Total Gas Supplied : |  |  | 836.68 | MMCFD |  |  | Rajshahi | 987.4 | 987.4 |  | 0 |  | 20:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 125314607.34 | ii) Oil : | Taka | 738352780.15 | Comilla | 1044 | 1044 |  | 0 |  | 21:00 |  | 0
|  | iii) Coal : |  | 199775227.03 | Total | Taka | 1063442614.52 | Mymensingh | 858 | 858 |  | 0 |  | 22:00 |  | 0
9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0 | MKWHr. | Sylhet | 437 | 437 |  | 0 |  | 23:00 |  | 0
| ii) During Peak Demand : |  |  | 1030 | MW (E to W) at | 20:00 | hrs | Barisal | 261.78 | 261.78 |  | 0 |  | 24:00 |  | 0
| iii) Maximum : |  |  | 580 | MW at | 7:00 | hrs | Rangpur | 618 | 618 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 31.7° C |  |  | Total | 10814.8 | 10814.8 |  | 0
B. |  | 2022-11-06 | (Today) |  |  |  | Sunday |  |  | Probable max. temperature in Dhaka |  |  | 30.2° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 12400 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 278 | MW
2 | Maximum Generation (Generation end) |  |  |  | 12188 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 10500 | MW
4 | Reserve(Generation end) |  |  |  | - | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 244.0143 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 8214 | MW at | 5:00 | 66 | 25 | 40 | 44 | 34 | 33 | 10 | 0 | 26
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 20.8662 | MKWHr. | ii) HVDC Flow at Peak Time |  | 913 | MW at | 20:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.7792 | MKWHr. | iii) Maximum HVDC Flow : |  | 913 | MW at | 14:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 94.88 |  | (b) Today: | 94.64 |  | (c) Rule Curve: |  | 108.6
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2022-11-05
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 0 | 73 | 0 | 384 | 245 |  | 0 | 210 | 138 | 0 | 0 | 55 | 0 | 0 | 0 | 8 | 58 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 35 | 22 | 25 | 27 | 33 | 32 | 0 | 0 | 83 | 70 | 0 | 0 | 0 | 151 | 0 | 0 | 0 |  | 6 | 8 | 11 | 75 | 0 | 26 | 0 | 29 | 0 | 0 | 0 | 310 | 0 | 181 | 168 | 52 | 51 | 50 | 0 | 0 | 0 | 0 | 34 | 0 | 10 | 33 | 20 | 106 | 109 | 0 | 16 | 0 | 30 | 43 | 0 | 0 | 0 | 0 | 63 | 0 | 0 | 145 | 19 | 0 | 10 | 290 | 0 | 0 | 0 | 275 | 0 | 0 | 48 | 0 | 132 | 0 | 25 | 51 | 20 | 354 | 49 | 70 | 68 | 0 | 70 | 36 | 74 | 17 | 0 | 25 | 350 | 52 | 0 | 35 | 107 | 0 | 17 | 0 | 53 | 17 | 0 | 0 | 0 |  | 912 | 0 | 195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 81 | 0 | 249 | 0 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 680 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 |  | 5686 | 2886 | 8572 | 3078 | 912 | 1674 | 0 | 1555 | 1075 | 153 | 0 | 19 | 106 | 0 | 0 | 94.93
2:00 | 0 | 0 | 0 | 180 | 0 | 73 | 0 | 358 | 261 |  | 0 | 210 | 128 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 35 | 22 | 25 | 27 | 33 | 32 | 0 | 0 | 83 | 70 | 0 | 0 | 0 | 151 | 0 | 0 | 0 |  | 6 | 8 | 17 | 77 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 285 | 0 | 186 | 168 | 50 | 48 | 51 | 0 | 0 | 0 | 0 | 30 | 0 | 10 | 33 | 19 | 100 | 109 | 0 | 16 | 0 | 30 | 43 | 0 | 0 | 0 | 0 | 63 | 0 | 0 | 145 | 19 | 0 | 10 | 280 | 0 | 0 | 0 | 210 | 0 | 0 | 8 | 0 | 133 | 0 | 25 | 51 | 0 | 353 | 49 | 17 | 68 | 0 | 70 | 17 | 72 | 0 | 0 | 25 | 350 | 47 | 0 | 35 | 68 | 0 | 17 | 0 | 53 | 17 | 0 | 0 | 0 |  | 911 | 0 | 195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 81 | 0 | 249 | 0 | 0 | 166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 670 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63 |  | 5335 | 2870 | 8205 | 3026 | 911 | 1667 | 0 | 1260 | 1063 | 153 | 0 | 25 | 100 | 0 | 0 | 94.92
3:00 | 0 | 0 | 0 | 180 | 0 | 73 | 0 | 345 | 268 |  | 0 | 210 | 128 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 35 | 22 | 25 | 27 | 33 | 33 | 0 | 0 | 83 | 70 | 0 | 0 | 0 | 151 | 0 | 0 | 0 |  | 6 | 8 | 17 | 66 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 280 | 0 | 181 | 168 | 51 | 48 | 52 | 0 | 0 | 0 | 0 | 8 | 0 | 10 | 33 | 19 | 98 | 111 | 0 | 16 | 0 | 30 | 43 | 0 | 0 | 0 | 0 | 63 | 0 | 0 | 145 | 19 | 0 | 10 | 290 | 0 | 0 | 0 | 210 | 0 | 0 | 8 | 0 | 105 | 0 | 25 | 51 | 0 | 353 | 49 | 0 | 68 | 0 | 70 | 17 | 72 | 0 | 0 | 25 | 350 | 17 | 0 | 35 | 68 | 0 | 17 | 0 | 53 | 17 | 0 | 0 | 0 |  | 912 | 0 | 195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 80 | 0 | 249 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64 |  | 5221 | 2773 | 7994 | 2986 | 912 | 1678 | 0 | 1149 | 993 | 153 | 0 | 25 | 98 | 0 | 0 | 94.9
4:00 | 0 | 0 | 0 | 180 | 0 | 73 | 0 | 345 | 269 |  | 0 | 210 | 128 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 35 | 22 | 25 | 27 | 33 | 33 | 0 | 0 | 83 | 70 | 0 | 0 | 0 | 151 | 0 | 0 | 0 |  | 6 | 8 | 17 | 66 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 280 | 0 | 181 | 168 | 50 | 48 | 52 | 0 | 0 | 0 | 0 | 8 | 0 | 10 | 33 | 15 | 90 | 110 | 0 | 16 | 0 | 30 | 43 | 0 | 0 | 0 | 0 | 63 | 0 | 0 | 145 | 19 | 0 | 10 | 280 | 0 | 0 | 0 | 180 | 0 | 0 | 8 | 0 | 80 | 0 | 25 | 51 | 0 | 353 | 49 | 0 | 68 | 0 | 70 | 17 | 72 | 0 | 0 | 25 | 350 | 18 | 0 | 35 | 68 | 0 | 17 | 0 | 53 | 17 | 0 | 0 | 0 |  | 748 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 81 | 0 | 249 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 530 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64 |  | 5139 | 2552 | 7691 | 2978 | 748 | 1683 | 0 | 1090 | 924 | 153 | 0 | 25 | 90 | 0 | 0 | 94.9
5:00 | 0 | 0 | 0 | 180 | 0 | 73 | 0 | 346 | 275 |  | 0 | 210 | 128 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 35 | 22 | 25 | 27 | 33 | 33 | 0 | 0 | 83 | 70 | 0 | 0 | 0 | 152 | 0 | 0 | 0 |  | 3 | 8 | 17 | 66 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 315 | 0 | 201 | 168 | 50 | 48 | 51 | 0 | 0 | 0 | 0 | 8 | 0 | 10 | 33 | 15 | 94 | 110 | 0 | 0 | 0 | 30 | 43 | 0 | 0 | 0 | 0 | 63 | 0 | 0 | 0 | 19 | 0 | 10 | 290 | 0 | 0 | 0 | 145 | 0 | 0 | 8 | 0 | 40 | 0 | 25 | 51 | 0 | 353 | 49 | 0 | 68 | 0 | 70 | 17 | 72 | 0 | 0 | 25 | 350 | 17 | 0 | 35 | 17 | 0 | 17 | 0 | 53 | 17 | 0 | 0 | 0 |  | 724 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 81 | 0 | 249 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 520 | 162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 |  | 4932 | 2542 | 7474 | 2879 | 724 | 1716 | 0 | 968 | 915 | 153 | 0 | 25 | 94 | 0 | 0 | 94.89
6:00 | 0 | 0 | 0 | 180 | 0 | 73 | 0 | 362 | 277 |  | 0 | 210 | 125 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 35 | 22 | 25 | 27 | 33 | 17 | 0 | 0 | 83 | 70 | 0 | 0 | 0 | 152 | 0 | 0 | 0 |  | 6 | 8 | 17 | 66 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 280 | 0 | 182 | 168 | 50 | 48 | 51 | 0 | 0 | 0 | 0 | 8 | 0 | 10 | 33 | 15 | 88 | 110 | 0 | 13 | 0 | 30 | 43 | 32 | 7 | 0 | 0 | 63 | 10 | 0 | 0 | 19 | 0 | 9 | 290 | 0 | 0 | 0 | 170 | 0 | 0 | 8 | 0 | 17 | 0 | 25 | 51 | 0 | 407 | 49 | 0 | 68 | 0 | 70 | 20 | 72 | 0 | 0 | 25 | 401 | 20 | 0 | 35 | 27 | 0 | 17 | 0 | 53 | 17 | 0 | 0 | 0 |  | 724 | 0 | 215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 8 | 80 | 0 | 249 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 530 | 162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 |  | 5058 | 2579 | 7637 | 2925 | 724 | 1786 | 0 | 1029 | 907 | 153 | 0 | 25 | 88 | 0 | 0 | 94.88
7:00 | 0 | 0 | 0 | 180 | 0 | 73 | 0 | 371 | 277 |  | 0 | 210 | 123 | 0 | 0 | 55 | 0 | 0 | 0 | 1 | 58 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 35 | 22 | 25 | 27 | 33 | 33 | 0 | 0 | 83 | 70 | 0 | 0 | 0 | 152 | 0 | 0 | 0 |  | 6 | 8 | 17 | 87 | 0 | 7 | 0 | 21 | 0 | 0 | 0 | 325 | 0 | 202 | 168 | 50 | 48 | 52 | 0 | 0 | 0 | 0 | 8 | 0 | 10 | 33 | 15 | 82 | 108 | 0 | 13 | 0 | 30 | 43 | 53 | 22 | 0 | 0 | 53 | 20 | 0 | 0 | 19 | 6 | 9 | 300 | 0 | 0 | 0 | 203 | 0 | 0 | 12 | 0 | 39 | 4 | 25 | 51 | 1 | 408 | 49 | 0 | 68 | 0 | 70 | 36 | 65 | 14 | 0 | 25 | 400 | 34 | 6 | 35 | 51 | 0 | 17 | 3 | 53 | 17 | 0 | 0 | 0 |  | 723 | 0 | 215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 81 | 0 | 250 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 0 | 0 | 108 | 0 | 0 | 0 | 520 | 163 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 2 | 0 |  | 5346 | 2607 | 7953 | 2998 | 723 | 1850 | 0 | 1247 | 851 | 153 | 0 | 25 | 82 | 24 | 0 | 94.87
8:00 | 0 | 0 | 0 | 180 | 0 | 73 | 0 | 373 | 276 |  | 0 | 210 | 125 | 7 | 0 | 55 | 0 | 0 | 0 | 8 | 58 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 35 | 22 | 22 | 24 | 33 | 32 | 0 | 0 | 84 | 35 | 0 | 0 | 0 | 152 | 0 | 0 | 0 |  | 6 | 8 | 17 | 100 | 0 | 29 | 0 | 2 | 0 | 0 | 0 | 315 | 0 | 185 | 168 | 50 | 45 | 51 | 0 | 0 | 0 | 0 | 8 | 0 | 8 | 16 | 15 | 90 | 73 | 0 | 13 | 1 | 30 | 43 | 53 | 36 | 0 | 0 | 40 | 20 | 0 | 0 | 19 | 22 | 9 | 290 | 0 | 0 | 0 | 226 | 0 | 0 | 47 | 0 | 86 | 10 | 25 | 51 | 13 | 408 | 49 | 0 | 68 | 2 | 70 | 36 | 71 | 17 | 0 | 25 | 400 | 49 | 21 | 35 | 100 | 0 | 17 | 12 | 53 | 0 | 0 | 0 | 0 |  | 723 | 0 | 215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 20 | 0 | 11 | 79 | 0 | 250 | 0 | 0 | 179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 113 | 0 | 2 | 0 | 540 | 160 | 0 | 0 | 2 | 31 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5491 | 2673 | 8164 | 2933 | 723 | 1825 | 0 | 1499 | 869 | 119 | 0 | 25 | 90 | 81 | 0 | 94.86
9:00 | 0 | 0 | 0 | 180 | 0 | 73 | 0 | 370 | 276 |  | 0 | 215 | 130 | 8 | 0 | 55 | 0 | 0 | 0 | 32 | 58 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 35 | 22 | 23 | 27 | 33 | 31 | 26 | 0 | 83 | 35 | 0 | 0 | 0 | 151 | 0 | 0 | 0 |  | 6 | 8 | 17 | 100 | 0 | 35 | 0 | 18 | 0 | 0 | 0 | 310 | 0 | 211 | 168 | 50 | 48 | 50 | 0 | 0 | 0 | 0 | 8 | 0 | 8 | 13 | 0 | 80 | 73 | 0 | 13 | 1 | 30 | 43 | 53 | 44 | 0 | 0 | 40 | 20 | 0 | 0 | 19 | 24 | 9 | 280 | 0 | 0 | 0 | 223 | 0 | 0 | 47 | 0 | 133 | 15 | 25 | 0 | 43 | 408 | 49 | 0 | 57 | 3 | 118 | 36 | 71 | 34 | 0 | 25 | 400 | 60 | 35 | 35 | 107 | 0 | 17 | 20 | 53 | 0 | 0 | 0 | 0 |  | 724 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 19 | 0 | 11 | 80 | 0 | 250 | 0 | 0 | 182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 281 | 0 | 0 | 0 | 0 | 113 | 0 | 3 | 0 | 550 | 160 | 0 | 0 | 3 | 55 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5690 | 2674 | 8364 | 2931 | 724 | 1820 | 0 | 1651 | 880 | 118 | 0 | 25 | 80 | 135 | 0 | 94.85
10:00 | 0 | 0 | 0 | 180 | 0 | 73 | 0 | 361 | 272 |  | 0 | 215 | 130 | 8 | 0 | 55 | 0 | 0 | 0 | 42 | 58 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 35 | 22 | 23 | 19 | 33 | 30 | 49 | 0 | 85 | 35 | 0 | 0 | 0 | 151 | 0 | 0 | 0 |  | 6 | 8 | 17 | 100 | 0 | 39 | 0 | 18 | 0 | 0 | 0 | 330 | 0 | 207 | 168 | 50 | 45 | 48 | 0 | 0 | 0 | 0 | 8 | 0 | 8 | 10 | 12 | 92 | 33 | 0 | 13 | 2 | 30 | 43 | 53 | 44 | 0 | 0 | 67 | 20 | 0 | 0 | 19 | 25 | 8 | 290 | 0 | 0 | 0 | 180 | 0 | 0 | 47 | 0 | 132 | 18 | 25 | 16 | 10 | 404 | 49 | 4 | 51 | 3 | 122 | 36 | 71 | 17 | 0 | 25 | 350 | 59 | 43 | 35 | 107 | 0 | 17 | 25 | 53 | 0 | 0 | 0 | 0 |  | 912 | 0 | 195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 540 | 64 | 0 | 0 | 4 | 74 | 0 | 0 | 0 | 0 | 30 | 0 |  | 5622 | 2573 | 8195 | 2856 | 912 | 1698 | 0 | 1498 | 790 | 120 | 0 | 25 | 92 | 204 | 0 | 94.84
11:00 | 0 | 0 | 0 | 180 | 0 | 73 | 0 | 375 | 258 |  | 0 | 215 | 135 | 11 | 0 | 55 | 0 | 0 | 0 | 26 | 58 | 40 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 23 | 19 | 33 | 30 | 41 | 0 | 83 | 35 | 0 | 0 | 0 | 151 | 0 | 0 | 0 |  | 6 | 8 | 17 | 100 | 0 | 39 | 0 | 3 | 0 | 0 | 0 | 350 | 0 | 198 | 168 | 48 | 47 | 47 | 0 | 0 | 0 | 0 | 8 | 0 | 10 | 7 | 12 | 114 | 33 | 0 | 13 | 1 | 30 | 43 | 53 | 44 | 0 | 0 | 63 | 20 | 0 | 0 | 18 | 25 | 8 | 310 | 0 | 0 | 0 | 180 | 0 | 0 | 48 | 0 | 132 | 20 | 50 | 51 | 27 | 404 | 49 | 88 | 51 | 4 | 123 | 36 | 71 | 23 | 0 | 27 | 390 | 37 | 38 | 35 | 107 | 0 | 17 | 29 | 53 | 0 | 0 | 0 | 0 |  | 912 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 17 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 108 | 0 | 6 | 18 | 580 | 64 | 0 | 0 | 2 | 83 | 0 | 0 | 0 | 0 | 33 | 0 |  | 5883 | 2728 | 8611 | 2932 | 912 | 1654 | 0 | 1770 | 830 | 118 | 0 | 65 | 114 | 216 | 153.903 | #REF!
12:00 | 0 | 0 | 0 | 180 | 0 | 73 | 0 | 397 | 248 |  | 0 | 200 | 135 | 46 | 0 | 55 | 0 | 0 | 0 | 63 | 58 | 98 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 22 | 23 | 19 | 0 | 28 | 49 | 0 | 83 | 35 | 0 | 0 | 6 | 151 | 0 | 0 | 0 |  | 6 | 0 | 17 | 100 | 0 | 39 | 0 | 3 | 0 | 0 | 0 | 340 | 0 | 169 | 168 | 49 | 47 | 48 | 0 | 0 | 0 | 19 | 8 | 0 | 10 | 7 | 12 | 128 | 33 | 0 | 13 | 1 | 30 | 43 | 53 | 44 | 0 | 0 | 62 | 20 | 0 | 0 | 18 | 23 | 8 | 290 | 0 | 0 | 0 | 185 | 0 | 0 | 48 | 0 | 149 | 9 | 50 | 51 | 40 | 408 | 49 | 88 | 51 | 4 | 123 | 36 | 71 | 96 | 0 | 50 | 380 | 71 | 35 | 35 | 107 | 0 | 17 | 30 | 52 | 0 | 0 | 0 | 0 |  | 912 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 16 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 113 | 0 | 6 | 75 | 630 | 64 | 0 | 0 | 5 | 84 | 0 | 0 | 0 | 0 | 33 | 0 |  | 6119 | 2875 | 8994 | 2870 | 912 | 1643 | 0 | 2102 | 880 | 118 | 0 | 134 | 128 | 207 | 189.8445 | 94.82
13:00 | 0 | 0 | 0 | 180 | 0 | 73 | 0 | 385 | 240 |  | 0 | 215 | 135 | 52 | 0 | 55 | 0 | 0 | 0 | 72 | 58 | 115 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 22 | 23 | 19 | 33 | 28 | 49 | 0 | 82 | 35 | 0 | 0 | 19 | 152 | 0 | 0 | 0 |  | 6 | 0 | 16 | 100 | 0 | 39 | 0 | 2 | 0 | 0 | 0 | 320 | 0 | 174 | 168 | 49 | 50 | 30 | 0 | 0 | 0 | 40 | 8 | 0 | 10 | 7 | 12 | 130 | 33 | 0 | 15 | 2 | 30 | 42 | 53 | 40 | 0 | 0 | 40 | 20 | 0 | 0 | 18 | 24 | 8 | 300 | 0 | 0 | 0 | 218 | 0 | 0 | 48 | 0 | 149 | 18 | 50 | 51 | 48 | 358 | 49 | 88 | 51 | 4 | 123 | 36 | 56 | 96 | 0 | 50 | 350 | 73 | 22 | 35 | 107 | 0 | 17 | 28 | 53 | 0 | 0 | 0 | 0 |  | 912 | 0 | 180 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 16 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 238 | 17 | 0 | 7 | 0 | 113 | 0 | 7 | 70 | 690 | 87 | 0 | 0 | 4 | 79 | 17 | 0 | 0 | 0 | 31 | 0 |  | 6113 | 3005 | 9118 | 2777 | 912 | 1649 | 0 | 2227 | 940 | 117 | 0 | 171 | 130 | 195 | 259.8842 | 94.84
14:00 | 0 | 0 | 0 | 180 | 70 | 73 | 0 | 361 | 240 |  | 0 | 215 | 135 | 64 | 0 | 55 | 0 | 0 | 0 | 71 | 58 | 132 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 0 | 23 | 24 | 33 | 28 | 49 | 0 | 82 | 35 | 0 | 0 | 25 | 150 | 0 | 0 | 0 |  | 6 | 0 | 16 | 100 | 0 | 39 | 0 | 2 | 0 | 0 | 0 | 300 | 0 | 192 | 168 | 50 | 50 | 30 | 0 | 0 | 0 | 41 | 8 | 1 | 10 | 7 | 12 | 132 | 33 | 0 | 15 | 2 | 30 | 42 | 53 | 43 | 0 | 0 | 40 | 20 | 0 | 0 | 18 | 24 | 8 | 290 | 0 | 0 | 0 | 255 | 0 | 0 | 49 | 0 | 149 | 16 | 50 | 51 | 50 | 360 | 49 | 88 | 51 | 3 | 123 | 36 | 66 | 96 | 0 | 50 | 350 | 73 | 27 | 70 | 107 | 0 | 17 | 22 | 39 | 0 | 0 | 0 | 0 |  | 913 | 0 | 180 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 16 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 232 | 35 | 0 | 35 | 0 | 113 | 0 | 7 | 70 | 640 | 125 | 0 | 0 | 4 | 65 | 17 | 0 | 0 | 0 | 27 | 0 |  | 6239 | 2978 | 9217 | 2768 | 913 | 1674 | 0 | 2361 | 890 | 117 | 0 | 189 | 132 | 173 | 260.8057 | 94.83
15:00 | 0 | 0 | 0 | 180 | 80 | 73 | 0 | 369 | 230 |  | 0 | 215 | 135 | 66 | 0 | 55 | 0 | 0 | 0 | 71 | 58 | 132 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 22 | 23 | 24 | 33 | 28 | 49 | 0 | 82 | 70 | 0 | 0 | 25 | 150 | 0 | 0 | 0 |  | 6 | 0 | 16 | 100 | 0 | 39 | 0 | 2 | 0 | 0 | 0 | 280 | 0 | 200 | 168 | 50 | 46 | 30 | 0 | 0 | 0 | 38 | 8 | 16 | 10 | 8 | 21 | 132 | 34 | 0 | 13 | 1 | 30 | 41 | 53 | 43 | 0 | 0 | 64 | 20 | 0 | 0 | 18 | 25 | 10 | 300 | 0 | 0 | 0 | 258 | 0 | 0 | 49 | 0 | 149 | 12 | 50 | 51 | 50 | 355 | 49 | 90 | 51 | 2 | 123 | 36 | 71 | 96 | 0 | 50 | 389 | 73 | 31 | 90 | 107 | 0 | 23 | 12 | 53 | 0 | 0 | 3 | 0 |  | 912 | 0 | 170 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 15 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 217 | 35 | 0 | 35 | 0 | 113 | 0 | 5 | 35 | 640 | 221 | 0 | 0 | 2 | 46 | 17 | 0 | 0 | 0 | 17 | 0 |  | 6422 | 2974 | 9396 | 2858 | 912 | 1757 | 0 | 2378 | 890 | 152 | 3 | 186 | 132 | 128 | 188.0013 | 94.79
16:00 | 0 | 0 | 0 | 180 | 130 | 70 | 0 | 361 | 227 |  | 0 | 215 | 135 | 69 | 0 | 55 | 0 | 0 | 0 | 71 | 58 | 132 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 22 | 23 | 23 | 33 | 28 | 49 | 0 | 82 | 70 | 0 | 0 | 25 | 150 | 0 | 0 | 0 |  | 6 | 0 | 16 | 76 | 0 | 42 | 0 | 2 | 0 | 0 | 0 | 305 | 0 | 202 | 168 | 50 | 44 | 30 | 0 | 0 | 0 | 42 | 8 | 16 | 10 | 8 | 20 | 126 | 33 | 0 | 13 | 0 | 30 | 41 | 53 | 43 | 0 | 0 | 63 | 20 | 0 | 0 | 18 | 25 | 10 | 295 | 0 | 0 | 0 | 260 | 0 | 0 | 49 | 0 | 134 | 5 | 50 | 51 | 53 | 366 | 49 | 93 | 51 | 1 | 123 | 36 | 71 | 114 | 0 | 50 | 388 | 73 | 11 | 90 | 107 | 0 | 35 | 4 | 53 | 0 | 0 | 0 | 0 |  | 912 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 15 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 0 | 113 | 0 | 2 | 0 | 620 | 221 | 0 | 0 | 0 | 21 | 17 | 0 | 0 | 0 | 8 | 0 |  | 6447 | 2828 | 9275 | 2966 | 912 | 1750 | 0 | 2246 | 870 | 152 | 0 | 201 | 126 | 52 | 207.3544 | 94.78
17:00 | 0 | 0 | 0 | 180 | 120 | 73 | 0 | 359 | 212 |  | 0 | 195 | 135 | 68 | 0 | 55 | 0 | 0 | 0 | 77 | 58 | 132 | 0 | 0 | 0 | 0 | 22 | 55 | 35 | 22 | 23 | 26 | 33 | 26 | 49 | 0 | 83 | 70 | 0 | 0 | 25 | 150 | 0 | 0 | 0 |  | 6 | 0 | 17 | 76 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 280 | 0 | 199 | 168 | 52 | 49 | 30 | 0 | 0 | 0 | 35 | 12 | 16 | 10 | 8 | 20 | 134 | 33 | 0 | 13 | 0 | 30 | 42 | 53 | 43 | 0 | 0 | 64 | 20 | 0 | 0 | 18 | 25 | 10 | 315 | 0 | 0 | 0 | 260 | 0 | 0 | 49 | 0 | 134 | 0 | 50 | 51 | 58 | 415 | 49 | 90 | 87 | 0 | 123 | 36 | 83 | 114 | 0 | 50 | 398 | 73 | 1 | 144 | 107 | 0 | 35 | 1 | 68 | 0 | 0 | 0 | 0 |  | 913 | 0 | 170 | 0 | 16 | 0 | 0 | 0 | 10 | 56 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 24 | 5 | 72 | 0 | 25 | 32 | 0 | 0 | 17 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219 | 5 | 0 | 9 | 0 | 113 | 0 | 0 | 25 | 660 | 221 | 0 | 0 | 0 | 2 | 54 | 0 | 0 | 0 | 1 | 0 |  | 6541 | 3132 | 9673 | 2989 | 913 | 1740 | 0 | 2446 | 910 | 153 | 0 | 383 | 134 | 5 | 0 | 94.77
18:00 | 0 | 0 | 0 | 180 | 120 | 73 | 0 | 349 | 198 |  | 0 | 195 | 120 | 75 | 0 | 55 | 0 | 0 | 0 | 88 | 92 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 23 | 24 | 33 | 26 | 49 | 0 | 83 | 70 | 0 | 0 | 25 | 150 | 0 | 0 | 0 |  | 6 | 21 | 51 | 66 | 0 | 14 | 0 | 2 | 0 | 0 | 0 | 280 | 0 | 200 | 168 | 50 | 50 | 30 | 0 | 0 | 0 | 40 | 34 | 19 | 10 | 8 | 20 | 152 | 33 | 0 | 13 | 0 | 30 | 43 | 53 | 40 | 0 | 0 | 68 | 81 | 0 | 0 | 18 | 23 | 10 | 280 | 0 | 0 | 0 | 268 | 0 | 0 | 86 | 0 | 132 | 0 | 50 | 51 | 65 | 414 | 98 | 90 | 105 | 0 | 273 | 36 | 91 | 114 | 0 | 50 | 372 | 87 | 0 | 144 | 107 | 0 | 35 | 0 | 105 | 0 | 0 | 0 | 0 |  | 912 | 0 | 170 | 0 | 49 | 0 | 0 | 0 | 51 | 75 | 8 | 43 | 0 | 0 | 0 | 0 | 0 | 32 | 5 | 86 | 0 | 34 | 40 | 8 | 35 | 17 | 0 | 11 | 0 | 0 | 249 | 0 | 0 | 161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 222 | 54 | 0 | 41 | 0 | 113 | 0 | 0 | 100 | 810 | 210 | 0 | 0 | 0 | 0 | 108 | 0 | 0 | 0 | 0 | 0 |  | 7012 | 3644 | 10656 | 2940 | 912 | 1722 | 0 | 3150 | 1059 | 153 | 0 | 568 | 152 | 0 | 686 | 94.76
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 110 | 73 | 0 | 348 | 192 |  | 0 | 190 | 112 | 86 | 0 | 55 | 0 | 0 | 0 | 88 | 92 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 23 | 22 | 33 | 26 | 49 | 0 | 83 | 70 | 0 | 0 | 25 | 150 | 0 | 0 | 0 |  | 6 | 23 | 51 | 66 | 0 | 37 | 0 | 8 | 0 | 0 | 0 | 310 | 0 | 199 | 168 | 49 | 50 | 30 | 0 | 0 | 0 | 43 | 25 | 19 | 10 | 15 | 20 | 140 | 47 | 0 | 13 | 0 | 30 | 42 | 53 | 40 | 0 | 0 | 68 | 81 | 0 | 35 | 18 | 26 | 10 | 285 | 0 | 0 | 0 | 276 | 0 | 0 | 87 | 0 | 133 | 0 | 50 | 95 | 73 | 415 | 99 | 100 | 105 | 0 | 284 | 36 | 91 | 114 | 0 | 50 | 400 | 93 | 0 | 144 | 107 | 0 | 35 | 0 | 115 | 0 | 0 | 0 | 0 |  | 912 | 0 | 170 | 0 | 49 | 0 | 0 | 0 | 43 | 84 | 8 | 60 | 0 | 0 | 0 | 0 | 0 | 32 | 13 | 86 | 0 | 34 | 35 | 8 | 38 | 20 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 228 | 54 | 0 | 90 | 0 | 113 | 0 | 0 | 113 | 900 | 222 | 0 | 0 | 0 | 0 | 114 | 0 | 0 | 0 | 0 | 0 |  | 7244 | 3848 | 11092 | 3056 | 912 | 1738 | 0 | 3363 | 1150 | 153 | 0 | 580 | 140 | 0 | 353 | 94.73
19:30 | 0 | 0 | 0 | 180 | 120 | 73 | 0 | 348 | 192 |  | 0 | 190 | 112 | 92 | 0 | 55 | 0 | 0 | 0 | 88 | 92 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 23 | 26 | 33 | 28 | 49 | 0 | 84 | 70 | 0 | 0 | 25 | 150 | 0 | 0 | 0 |  | 6 | 23 | 51 | 66 | 0 | 44 | 0 | 5 | 0 | 0 | 0 | 310 | 0 | 194 | 168 | 50 | 50 | 30 | 0 | 0 | 0 | 43 | 29 | 19 | 10 | 16 | 21 | 142 | 52 | 0 | 13 | 0 | 30 | 42 | 53 | 40 | 0 | 0 | 67 | 81 | 0 | 35 | 18 | 26 | 10 | 290 | 0 | 0 | 0 | 276 | 0 | 0 | 88 | 0 | 133 | 0 | 50 | 200 | 70 | 416 | 99 | 100 | 105 | 0 | 300 | 36 | 91 | 114 | 0 | 50 | 400 | 93 | 0 | 144 | 107 | 0 | 35 | 0 | 115 | 0 | 0 | 0 | 0 |  | 912 | 0 | 170 | 0 | 32 | 0 | 0 | 0 | 42 | 82 | 8 | 60 | 0 | 0 | 0 | 0 | 0 | 32 | 18 | 86 | 0 | 34 | 32 | 8 | 38 | 21 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 228 | 56 | 0 | 94 | 0 | 113 | 0 | 0 | 113 | 910 | 222 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 0 |  | 7404 | 3848 | 11252 | 3075 | 912 | 1741 | 0 | 3489 | 1160 | 154 | 0 | 579 | 142 | 0 | 229 | 0
20:00 | 0 | 0 | 0 | 180 | 140 | 73 | 0 | 348 | 192 |  | 0 | 190 | 112 | 92 | 0 | 55 | 0 | 0 | 0 | 88 | 92 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 26 | 33 | 29 | 49 | 0 | 84 | 70 | 0 | 0 | 25 | 150 | 0 | 0 | 0 |  | 6 | 23 | 51 | 66 | 0 | 44 | 0 | 12 | 0 | 0 | 0 | 310 | 0 | 191 | 168 | 50 | 50 | 30 | 0 | 0 | 0 | 43 | 29 | 19 | 10 | 30 | 21 | 136 | 55 | 0 | 13 | 0 | 30 | 42 | 41 | 30 | 0 | 0 | 65 | 81 | 0 | 90 | 18 | 16 | 10 | 270 | 0 | 0 | 0 | 276 | 0 | 0 | 88 | 0 | 133 | 0 | 50 | 200 | 68 | 415 | 99 | 100 | 105 | 0 | 300 | 36 | 91 | 114 | 0 | 50 | 398 | 93 | 0 | 144 | 107 | 0 | 35 | 0 | 115 | 0 | 0 | 0 | 0 |  | 913 | 0 | 170 | 0 | 49 | 0 | 0 | 0 | 42 | 82 | 8 | 60 | 0 | 0 | 0 | 0 | 0 | 32 | 18 | 86 | 0 | 34 | 32 | 8 | 34 | 20 | 0 | 11 | 10 | 0 | 250 | 0 | 0 | 161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 231 | 54 | 0 | 94 | 0 | 113 | 0 | 0 | 113 | 900 | 220 | 0 | 0 | 0 | 0 | 114 | 0 | 0 | 0 | 0 | 0 |  | 7438 | 3859 | 11297 | 3162 | 913 | 1696 | 0 | 3501 | 1160 | 154 | 0 | 575 | 136 | 0 | 0 | 94.74
21:00 | 0 | 0 | 0 | 180 | 150 | 52 | 0 | 322 | 204 |  | 0 | 200 | 0 | 89 | 0 | 55 | 0 | 0 | 0 | 88 | 92 | 98 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 26 | 33 | 29 | 24 | 0 | 84 | 70 | 0 | 0 | 25 | 150 | 0 | 0 | 0 |  | 6 | 23 | 51 | 66 | 0 | 44 | 0 | 16 | 0 | 0 | 0 | 310 | 0 | 186 | 168 | 50 | 51 | 30 | 0 | 0 | 0 | 43 | 40 | 19 | 10 | 33 | 21 | 134 | 102 | 0 | 13 | 0 | 30 | 42 | 0 | 0 | 0 | 0 | 63 | 40 | 0 | 145 | 18 | 0 | 10 | 275 | 0 | 0 | 0 | 276 | 0 | 0 | 88 | 0 | 137 | 0 | 50 | 136 | 72 | 409 | 99 | 100 | 105 | 0 | 284 | 36 | 91 | 99 | 8 | 50 | 361 | 93 | 0 | 144 | 107 | 0 | 35 | 0 | 112 | 0 | 0 | 0 | 0 |  | 899 | 0 | 180 | 0 | 49 | 0 | 0 | 0 | 33 | 82 | 8 | 60 | 11 | 0 | 0 | 0 | 0 | 32 | 18 | 86 | 0 | 34 | 32 | 8 | 35 | 19 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 231 | 54 | 0 | 94 | 0 | 113 | 0 | 0 | 113 | 900 | 220 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 0 |  | 7093 | 3849 | 10942 | 3213 | 899 | 1476 | 0 | 3383 | 1150 | 154 | 0 | 533 | 134 | 0 | 0 | 94.73
22:00 | 0 | 0 | 0 | 180 | 150 | 52 | 0 | 260 | 218 |  | 0 | 210 | 0 | 89 | 0 | 55 | 0 | 0 | 0 | 88 | 92 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 26 | 33 | 30 | 39 | 0 | 84 | 70 | 0 | 0 | 25 | 150 | 0 | 0 | 0 |  | 6 | 23 | 51 | 66 | 0 | 44 | 0 | 31 | 0 | 0 | 0 | 310 | 0 | 178 | 168 | 50 | 51 | 30 | 0 | 0 | 0 | 43 | 35 | 17 | 10 | 33 | 21 | 144 | 98 | 0 | 13 | 0 | 30 | 42 | 0 | 0 | 0 | 0 | 63 | 81 | 0 | 145 | 18 | 0 | 10 | 270 | 0 | 0 | 0 | 276 | 0 | 0 | 88 | 0 | 149 | 0 | 50 | 80 | 68 | 407 | 99 | 105 | 105 | 0 | 124 | 36 | 91 | 99 | 0 | 50 | 335 | 93 | 0 | 144 | 107 | 0 | 35 | 0 | 115 | 0 | 0 | 0 | 0 |  | 899 | 0 | 180 | 0 | 49 | 0 | 0 | 0 | 0 | 10 | 8 | 40 | 21 | 0 | 0 | 0 | 0 | 32 | 16 | 86 | 0 | 34 | 24 | 8 | 33 | 16 | 0 | 11 | 73 | 0 | 250 | 0 | 0 | 164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 231 | 57 | 0 | 94 | 0 | 113 | 0 | 0 | 113 | 900 | 220 | 0 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 |  | 6911 | 3795 | 10706 | 3092 | 899 | 1558 | 0 | 3186 | 1223 | 154 | 0 | 450 | 144 | 0 | 0 | 94.72
23:00 | 0 | 0 | 0 | 180 | 150 | 52 | 0 | 233 | 217 |  | 0 | 215 | 0 | 92 | 0 | 47 | 0 | 0 | 0 | 88 | 92 | 64 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 26 | 33 | 30 | 49 | 0 | 84 | 70 | 0 | 0 | 25 | 151 | 0 | 0 | 0 |  | 6 | 23 | 51 | 66 | 0 | 44 | 0 | 38 | 0 | 0 | 0 | 310 | 0 | 182 | 170 | 50 | 51 | 30 | 0 | 0 | 0 | 0 | 34 | 17 | 10 | 33 | 21 | 142 | 105 | 0 | 13 | 0 | 30 | 42 | 0 | 0 | 0 | 0 | 63 | 81 | 0 | 145 | 18 | 0 | 10 | 280 | 0 | 0 | 0 | 276 | 0 | 0 | 88 | 0 | 149 | 0 | 50 | 51 | 80 | 365 | 99 | 90 | 105 | 0 | 124 | 36 | 91 | 17 | 0 | 50 | 360 | 92 | 0 | 108 | 107 | 0 | 35 | 0 | 115 | 0 | 0 | 0 | 0 |  | 900 | 0 | 180 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 8 | 0 | 0 | 0 | 20 | 0 | 11 | 77 | 0 | 250 | 0 | 0 | 164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 57 | 0 | 94 | 0 | 56 | 0 | 0 | 113 | 870 | 223 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 0 | 0 | 0 |  | 6642 | 3512 | 10154 | 3090 | 900 | 1586 | 0 | 2899 | 1197 | 154 | 0 | 186 | 142 | 0 | 0 | 94.71
24:00 | 0 | 0 | 0 | 180 | 180 | 62 | 0 | 232 | 252 |  | 0 | 215 | 0 | 62 | 0 | 40 | 0 | 0 | 0 | 65 | 58 | 64 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 22 | 25 | 26 | 33 | 32 | 41 | 0 | 84 | 70 | 0 | 0 | 25 | 151 | 0 | 0 | 0 |  | 6 | 23 | 51 | 22 | 0 | 34 | 0 | 32 | 0 | 0 | 0 | 315 | 0 | 168 | 170 | 50 | 51 | 31 | 0 | 0 | 0 | 0 | 34 | 16 | 10 | 33 | 21 | 136 | 104 | 0 | 13 | 0 | 30 | 42 | 0 | 0 | 0 | 0 | 60 | 81 | 0 | 145 | 18 | 0 | 10 | 320 | 0 | 0 | 0 | 276 | 0 | 0 | 55 | 0 | 149 | 0 | 25 | 51 | 70 | 407 | 49 | 70 | 63 | 0 | 124 | 36 | 61 | 17 | 0 | 25 | 400 | 72 | 0 | 35 | 107 | 0 | 35 | 0 | 79 | 11 | 0 | 0 | 0 |  | 899 | 0 | 175 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 8 | 0 | 0 | 0 | 20 | 0 | 8 | 74 | 0 | 250 | 0 | 0 | 164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 238 | 57 | 0 | 94 | 0 | 56 | 0 | 0 | 113 | 810 | 220 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 |  | 6269 | 3374 | 9643 | 3181 | 899 | 1670 | 0 | 2283 | 1134 | 154 | 0 | 186 | 136 | 0 | 0 | 94.7
KWH | 0 | 0 | 0 | 4378500 | 1304600 | 1651818 | 0 | 8445950 | 5798000 |  | 0 | 4786100 | 2693091 | 975360 | 0 | 1319012 | 0 | 0 | 0 | 1123200 | 1580832 | 1494240 | 0 | 0 | 0 | 0 | 660960 | 781284 | 905614 | 454140 | 600000 | 574200 | 775080 | 712100 | 702240 | 0 | 1946803 | 1444000 | 0 | 0 | 311086 | 3509324 | 0 | 0 | 0 |  | 144960 | 224388 | 616332 | 1880520 | 0 | 689280 | 0 | 374880 | 0 | 0 | 0 | 7698000 | 0 | 4614000 | 4064727 | 1193950 | 1141632 | 989280 | 0 | 0 | 0 | 415328 | 453518 | 168336 | 244260 | 511200 | 408090 | 2779200 | 1656960 | 0 | 325512 | 12500 | 716000 | 965760 | 762600 | 577224 | 0 | 0 | 1403232 | 778560 | 0 | 1298760 | 433000 | 310520 | 225180 | 7135000 | 0 | 0 | 0 | 5678073 | 0 | 0 | 1144800 | 0 | 2919168 | 130815 | 897600 | 1534080 | 980218 | 9358000 | 1472400 | 1387572 | 1784799 | 24238 | 3131345 | 830036 | 1855883 | 1322400 | 14280 | 913920 | 9031000 | 1479360 | 290030 | 1797120 | 2295818 | 0 | 612720 | 187906 | 1670400 | 151560 | 0 | 5018 | 0 |  | 20866181 | 0 | 4656096 | 0 | 390720 | 0 | 0 | 0 | 165600 | 404352 | 34875 | 1274000 | 56350 | 0 | 0 | 0 | 0 | 164873 | 69322 | 541568 | 0 | 283528 | 163099 | 36163 | 171144 | 348000 | 0 | 227970 | 983563 | 0 | 6073100 | 0 | 0 | 4137773 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6157309 | 473280 | 0 | 732480 | 0 | 1838544 | 0 | 39507 | 1059552 | 17972700 | 3981300 | 0 | 0 | 32220 | 554400 | 793920 | 0 | 0 | 0 | 170010 | 414545 |  | 147040782 | 75268044 | 222308826 | 72217425 | 20866181 | 40689939 | 0 | 51044480 | 25443908 | 3390803 | 5018 | 4430246 | 2779200 | 1441626 | 0
Fuel Cost | 0 | 0 | 0 | 6523965 | 1461152 | 2196917.94 | 0 | 8868247.5 | 6261840 |  | 0 | 5216849 | 2989331.01 | 10904524.8 | 0 | 17476909 | 0 | 0 | 0 | 16421184 | 22242306.24 | 24221630.4 | 0 | 0 | 0 | 0 | 8407411.2 | 10547334 | 12144283.74 | 340605 | 450000 | 0 | 0 | 0 | 11945102.4 | 0 | 525636.81 | 389880 | 0 | 0 | 5086256.1 | 3649696.96 | 0 | 0 | 0 |  | 1891728 | 3742791.84 | 10489970.64 | 25405825.2 | 0 | 7974969.6 | 0 | 1248350.4 | 0 | 0 | 0 | 8544780 | 0 | 5352240 | 5243497.83 | 1456619 | 1290044.16 | 1474027.2 | 0 | 0 | 0 | 7172714.56 | 6099817.1 | 230620.32 | 183195 | 894600 | 306067.5 | 19954656 | 1806086.4 | 0 | 442696.32 | 199250 | 980920 | 1274803.2 | 1326924 | 998597.52 | 0 | 0 | 2722270.08 | 1775116.8 | 0 | 1311747.6 | 930950 | 462674.8 | 445856.4 | 7135000 | 0 | 0 | 0 | 77505696.45 | 0 | 0 | 15431904 | 0 | 40430476.8 | 1529227.35 | 9263232 | 20955532.8 | 13007492.86 | 8609360 | 17904384 | 20064291.12 | 22577707.35 | 0 | 36761990.3 | 9039092.04 | 19728036.29 | 17944968 | 184069.2 | 10765977.6 | 8308520 | 19157712 | 4190933.5 | 22805452.8 | 26126408.84 | 0 | 8002123.2 | 2245476.7 | 25005888 | 1996045.2 | 0 | 0 | 0 |  | 62598543 | 0 | 5214827.52 | 0 | 4067395.2 | 0 | 0 | 0 | 2982456 | 7278336 | 501153.75 | 1426880 | 109319 | 0 | 0 | 0 | 0 | 2764920.21 | 1212441.78 | 8470123.52 | 0 | 4695223.68 | 2758004.09 | 492901.69 | 2887199.28 | 720360 | 0 | 172573.29 | 5714501.03 | 0 | 32126699 | 0 | 0 | 4799816.68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6095735.91 | 6360883.2 | 0 | 8665238.4 | 0 | 23349508.8 | 0 | 436552.35 | 12862961.28 | 161934027 | 4060926 | 0 | 0 | 364408.2 | 6503112 | 12170793.6 | 0 | 0 | 0 | 0 | 0 |  | 768582468.97 | 393797821.46 | 1162380290.43 | 77553283.53 | 62598543 | 47761323.81 | 0 | 664372191.83 | 199775227.03 | 915516.81 | 0 | 73980588.32 | 19954656 | 15468960.1 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 0 | 73 | 0 | 397 | 248 |  | 0 | 200 | 135 | 46 | 0 | 55 | 0 | 0 | 0 | 63 | 58 | 98 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 22 | 23 | 19 | 0 | 28 | 49 | 0 | 83 | 35 | 0 | 0 | 6 | 151 | 0 | 0 | 0 |  | 6 | 0 | 17 | 100 | 0 | 39 | 0 | 3 | 0 | 0 | 0 | 340 | 0 | 169 | 168 | 49 | 47 | 48 | 0 | 0 | 0 | 19 | 8 | 0 | 10 | 7 | 12 | 128 | 33 | 0 | 13 | 1 | 30 | 43 | 53 | 44 | 0 | 0 | 62 | 20 | 0 | 0 | 18 | 23 | 8 | 290 | 0 | 0 | 0 | 185 | 0 | 0 | 48 | 0 | 149 | 9 | 50 | 51 | 40 | 408 | 49 | 88 | 51 | 4 | 123 | 36 | 71 | 96 | 0 | 50 | 380 | 71 | 35 | 35 | 107 | 0 | 17 | 30 | 52 | 0 | 0 | 0 | 0 |  | 912 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 16 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 113 | 0 | 6 | 75 | 630 | 64 | 0 | 0 | 5 | 84 | 0 | 0 | 0 | 0 | 33 | 0 |  | 8994 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 140 | 73 | 0 | 348 | 192 | 0 | 0 | 190 | 112 | 92 | 0 | 55 | 0 | 0 | 0 | 88 | 92 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 26 | 33 | 29 | 49 | 0 | 84 | 70 | 0 | 0 | 25 | 150 | 0 | 0 | 0 | 0 | 6 | 23 | 51 | 66 | 0 | 44 | 0 | 12 | 0 | 0 | 0 | 310 | 0 | 191 | 168 | 50 | 50 | 30 | 0 | 0 | 0 | 43 | 29 | 19 | 10 | 30 | 21 | 136 | 55 | 0 | 13 | 0 | 30 | 42 | 41 | 30 | 0 | 0 | 65 | 81 | 0 | 90 | 18 | 16 | 10 | 270 | 0 | 0 | 0 | 276 | 0 | 0 | 88 | 0 | 133 | 0 | 50 | 200 | 68 | 415 | 99 | 100 | 105 | 0 | 300 | 36 | 91 | 114 | 0 | 50 | 398 | 93 | 0 | 144 | 107 | 0 | 35 | 0 | 115 | 0 | 0 | 0 | 0 |  | 913 | 0 | 170 | 0 | 49 | 0 | 0 | 0 | 42 | 82 | 8 | 60 | 0 | 0 | 0 | 0 | 0 | 32 | 18 | 86 | 0 | 34 | 32 | 8 | 34 | 20 | 0 | 11 | 10 | 0 | 250 | 0 | 0 | 161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 231 | 54 | 0 | 94 | 0 | 113 | 0 | 0 | 113 | 900 | 220 | 0 | 0 | 0 | 0 | 114 | 0 | 0 | 0 | 0 | 0 |  | 11297 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 180 | 73 | 0 | 0 | 250 | 0 | 0 | 200 | 0 | 92 | 0 | 55 | 0 | 0 | 0 | 88 | 92 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 49 | 0 | 84 | 70 | 0 | 0 | 25 | 150 | 0 | 0 | 0 | 0 | 12 | 22 | 51 | 75 | 0 | 44 | 0 | 15 | 0 | 0 | 0 | 360 | 0 | 190 | 180 | 50 | 51 | 55 | 0 | 0 | 0 | 43 | 43 | 19 | 10 | 33 | 21 | 166 | 100 | 0 | 18 | 0 | 30 | 43 | 53 | 44 | 0 | 0 | 65 | 80 | 0 | 145 | 19 | 11 | 10 | 330 | 0 | 0 | 100 | 280 | 150 | 50 | 98 | 50 | 149 | 0 | 50 | 200 | 100 | 400 | 100 | 100 | 105 | 0 | 300 | 54 | 105 | 114 | 9 | 50 | 400 | 92 | 0 | 162 | 107 | 0 | 35 |  | 115 | 17 | 0 |  |  |  | 918 | 0 | 190 | 0 | 49 | 0 | 0 | 0 | 42 | 82 | 8 | 65 | 22 | 16 | 0 | 0 | 0 | 32 | 22 | 86 | 0 | 42 | 32 | 43 | 34 | 20 | 0 | 11 | 80 | 0 | 250 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 270 | 94 | 100 | 95 | 0 | 70 | 0 | 0 | 113 | 950 | 220 |  | 0 |  |  | 115
Forecast for Day | 0 | 0 | 0 | 180 | 180 | 73 | 0 | 0 | 200 | 0 | 0 | 200 | 0 | 70 | 0 | 55 | 0 | 0 | 0 | 70 | 60 | 115 | 0 | 0 | 0 | 0 | 17 | 55 | 55 | 22 | 25 | 27 | 33 | 33 | 49 | 0 | 84 | 70 | 0 | 0 | 25 | 150 | 0 | 0 | 0 | 0 | 12 | 22 | 17 | 22 | 0 | 24 | 0 | 7 | 0 | 0 | 0 | 360 | 0 | 175 | 170 | 50 | 50 | 30 | 0 | 0 | 0 | 32 | 8 | 16 | 10 | 33 | 21 | 143 | 102 | 0 | 18 | 1.6 | 30 | 0 | 41 | 30 | 0 | 0 | 66 | 0 | 0 | 20 | 19 | 11 | 10 | 330 | 0 | 0 | 0 | 275 | 0 | 0 | 48 | 0 | 134 | 20 | 25 | 51 | 64 | 400 | 50 | 70 | 70 | 5 | 125 | 36 | 70 | 17 | 0 | 25 | 400 | 74 | 50 | 35 | 107 | 0 | 17 | 30 | 53 | 17 | 0 |  |  |  | 918 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 20 | 0 | 8 | 80 | 0 | 250 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 60 | 0 | 35 | 0 | 50 | 0 | 8 | 95 | 850 | 220 |  | 0 | 6 | 100 | 113 |  |  |  | 12
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 180 | 52 | 0 | 0 | 253 | 0 | 0 | 200 | 0 | 52 | 0 | 55 | 0 | 0 | 0 | 63 | 58 | 48 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 25 | 27 | 33 | 33 | 42 | 0 | 83 | 70 | 0 | 0 | 17 | 151 | 0 | 0 | 0 | 0 | 6 | 0 | 17 | 22 | 0 | 32 | 0 | 6 | 0 | 0 | 0 | 360 | 0 | 160 | 170 | 50 | 50 | 30 | 0 | 0 | 0 | 0 | 8 | 16 | 10 | 10 | 21 | 108 | 102 | 0 | 13 | 1 | 30 | 0 | 0 | 0 | 0 | 0 | 64 | 0 | 0 | 20 | 19 | 0 | 10 | 330 | 0 | 0 | 0 | 275 | 0 | 0 | 48 | 0 | 134 | 10 | 25 | 51 | 60 | 407 | 49 | 70 | 68 | 1 | 69 | 36 | 54 | 17 | 0 | 25 | 398 | 74 | 23 | 35 | 107 | 0 | 17 | 11 | 35 | 17 | 0 | 0 | 0 | 0 | 709 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 8 | 80 | 0 | 250 | 0 | 0 | 166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 235 | 6 | 0 | 35 | 0 | 42 | 0 | 2 | 95 | 790 | 220 | 0 | 0 | 2 | 30 | 35 | 0 | 0 | 0 | 12 | 0 | 0 |  |  |  |  | 55479744 |  | 0
55479744
| Minimum Generation |  | 7474 | 5:00
| Highest Generation |  | 11297 | 20:00
| Day Peak Generation |  | 8994 | 12:00
| Evening Peak Generation |  | 11297 | 20:00
| HVDC Max Flow |  | 913 | 14:00
| HVDC EvPeak Flow |  | 913 | 20:00
| Load factor L.F |  | 81.99% | [161 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2022-11-06
Till now the maximum generation is : - |  |  | 14782 | 21:00 | Hrs on | 2022-04-16
The Summary of Yesterday's |  | 2022-11-05 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 8994 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 8214 | MW
Evening Peak Generation : |  | 11297 | MW Hour : | 20:00 | Available Max Generation : |  | 12188 | MW
E.P. Demand (at gen end) : |  | 11297 | MW Hour : | 20:00 | Max Demand (Evening) : |  | 12400 | MW
Maximum Generation : |  | 11297 | MW Hour : | 20:00 | Reserve(Generation end) |  | - | MW
Total Gen. (MKWH) : |  | 222.3088 | System Load Factor : | 81.99% | Load Shed : |  | 278 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | 580 | MW at | 7:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2022-11-06
Actual : | 94.64 | Ft.(MSL) , | Rule curve : | 108.6 | Ft.( MSL )
Gas Consumed : | Total = | 836.68 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 125314607.34
: |  | Coal : | 199775227.03 | Oil : | 738352780.15 | Total : | 1063442614.52
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4098.4931 |  |  | 66 | 1.61%
Chittagong Area | 0 | 0:00 | 1161.0318 |  |  | 25 | 2.153%
Khulna Area | 0 | 0:00 | 1532.4656 |  |  | 40 | 2.61%
Rajshahi Area | 0 | 0:00 | 1359.6786 |  |  | 44 | 3.236%
Cumilla Area | 0 | 0:00 | 1157.4564 |  |  | 34 | 2.937%
Mymensingh Area | 0 | 0:00 | 956.2319 |  |  | 33 | 3.451%
Sylhet Area | 0 | 0:00 | 427.3941 |  |  | 10 | 2.34%
Barisal Area | 0 | 0:00 | 348.401 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 755.0075 |  |  | 26 | 3.444%
Total | 0 |  | 11796.16 |  |  | 278
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 2
2) Ghorasal-3, 7
3) Ashuganj-5
4) Baghabari-71,100 MW
5) Raozan unit-1 & 2
6) Siddhirganj 210 MW .
7) Shajibazar 330 MW
8) Sirajganj-2
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Ghorashal GIS-Ishurdi 230 kV Ckt-1 was under shut down from 08:35 to 14:49 for D/W.
b) Comilla(N)-Ashuganj 230 kV Ckt-2 was under shut down from 08:25 to 16:26 for A/M.
c) Aminbazar-Kallyanpur 132 kV Ckt-2 was under shut down from 08:26 to 17:13 for A/M.
d) Haripur-Bhulta 230 kV Ckt-1 was under shut down from 08:42 to 16:59 for A/M.
e) Mirpur-Uttara 132 kV Ckt was under shut down from 08:53 to 16:59 for C/M.
f) Bibiyana-Fenchuganj 230 kV Ckt-1 was under shut down from 08:55 to 17:44 for A/M.
g) Siddirganj 230/132 kV MTR-2 transformer was under shut down from 08:56 to 14:52 for A/M.
h) Motijheel-Bangabhaban 132 kV Ckt-2 was under shut down from 08:56 to 14:52 for A/M.
i) Comilla(N)-Meghnaghat 230 kV Ckt-1 was under shut down from 09:10 to 17:18 for A/M.
j) Mymensingh-Kishoreganj 132 kV Ckt-2 was under shut down from 09:12 to 16:50 for A/M.
k) HVDC 230 kV 20DF22 Filter was under shut down from 09:09 to 15:16 for A/M.
l) Tangail 33 kV Capacitor bank 4,5 was under shut down from 08:44 to 14:50 for A/M.
m) Sreemangal 132/33 kV T-1 transformer was shut down from 08:17 to 13:37 for A/M.
n) Barapukuria 230/132 kV T0-2 transformer was under shut down from 09:10 to 10:32 for A/M.
o) New Tongi 132 kV bus coupler was under shut down from 09:47 to 15:59 for A/M.
p) Manikganj-Kabirpur 132 kV Ckt-2 was under shut down from 11:01 to 13:58 for C/M.
q) Barapukuria-Rangpur 132 kV both Ckt tripped at 09:54 showing O/C,E/F relay and was switched on at 10:38.
r) Barapukuria-Saidpur 132 kV both Ckt tripped at 09:54 showing O/C,E/F relay and was switched on at 10:43.
s) Barapukuria 230/132 kV T0-1 tripped at 09:54 showing O/C relay at 132 kV side & 521 main 1,main 2 | [5 empty] | About 107 MW power interruption occurred under Barapukuria,
operated and was switched on at 10:26. | [5 empty] | Saidpur S/S area from 09:54 to 10:26.
t) Above the tripping Barapukuria #01 got trip and was synchronized at 19:52. | [5 empty] | About 229 MW power interruption occurred under
u) Palashbari-Mithapukur 132 kV both Ckt tripped at 10:07 from Polashbari end showing dist R-phase at Ckt-2 | [5 empty] | Rangpur Zone from 10:07 to 10:15.
and O/C at Ckt-1 and were switched on at 10:15.
v) Tongi-Metro Rail under ground cable 132 kV Ckt was under shut down since at 11:05 for D/W.
w) Chandpur 132/33 kV T-1 transformer 33 kV side tripped at 10:36 showing O/C,E/F relay due to 33 kV | [5 empty] | About 17 MW power interruption occurred under Chandpur
Chandpur-2 feeder fault and was switched on at 10:40. | [5 empty] | S/S area from 10:36 to 10:40.
x) Bogura(New)-Sherpur 132 kV Ckt-1 was under shut down from 08:01 to 15:30 for A/M.
y) Natore-Rajshahi 132 kV Ckt-1 was under shut down from 08:15 to 15:55 for A/M.
z) Kurigram 132 kV bus was under shut down from 08:13 to 16:29 for A/M.
aa) Gallamari 132/33 kV T-2 transformer was shut down from 08:30 to 16:23 for A/M.
ab) Noapara 132/33 kV T-4 transformer was shut down from 07:59 to 16:05 for A/M.
ac) Nutun Biddut ST tripped at 08:27 and was synchronized at 13:25.
ad) Ghorasal #07 GT was synchronized at 13:20.
ae) Rajbari 132/33 kV T-2 transformer was shut down from 12:42 to 15:56 for C/M. | [5 empty] | About 4 MW power interruption occurred under Rajbari
S/S area from 12:42 to 15:56.
af) Khulna(C) 132/33 kV T-1 transformer was shut down from 12:37 to 13:43 for C/M by WZPDCL. | [5 empty] | About 15 MW power interruption occurred under Khulna©
S/S area from 12:37 to 13:43.
ag) Sreemangal 132/33 kV T-2 & T-3 transformer were under shut down from 13:45 to 17:20 for A/M.
ah) Chattak-Sunamganj 132 kV Ckt tripped at 17:17 showing dist Z1 R-phase at Chattak end & dist Z1 VT fail | [5 empty] | About 27 MW power interruption occurred under Sunamganj
at Sunamganj end and was switched on at 17:51. | [5 empty] | S/S area from 17:17 to 17:51.
ai) Sylhet 225 MW GT was synchronized at 18:46.
aj) Haripur 412 MW CCPP was under shut down since at 01:57 due to GTCL line maintenance works.
ak) Satkhira 132/33 kV T-1 & T-1 transformer 33 kV side tripped at 04:45(06-11-22) due to 33 kV feeder fault | [5 empty] | About 45 MW power interruption occurred under Satkhira
and were switched on at 04:58. | [5 empty] | S/S area from 04:45 to 04:58.
al) Barguna 132/33 kV T-2 transformer was shut down since 06:58(06-11-2022) for A/M.
am) Aminbazar-Kallyanpur 132 kV Ckt-2 was under shut down since at 07:40(6-11-2022) for A/M.
| Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2022-11-05 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Machine problem
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4378500
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 140 | 1304600
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 73 | 1651818 | Engine problem
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 348 | 8445950 | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 192 | 5798000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 190 | 4786100 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 92 | 975360 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 112 | 2693091 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 0 | 0 | Under maint.
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 55 | 1319012
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 454140
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 88 | 1123200 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 92 | 1580832 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 660960
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 132 | 1494240 | Fuel shortage
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 781284
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 905614
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 51 | 1174200 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 775080
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 29 | 712100
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 49 | 702240 | 0:00
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 276 | 5678073 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Fuel conservation
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 0 | 0 | Fuel conservation
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Fuel conservation
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 133 | 2919168 | Engine problem
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 100 | 1387572
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 93 | 1479360 | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 144 | 1797120 | Engine problem
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 187906
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 151560 | Fuel shortage
| Dhaka area Total |  |  |  | 5847 | 2788 | 55317080
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Machine problem
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 25 | 311086
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 130815
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 44 | 689280 | Engine problem
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 154 | 3390803 | Low water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 150 | 3509324 | ST Under maint
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 105 | 1784799
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 23 | 224388 | Fuel shortage
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 616332 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 66 | 1880520 | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 50 | 897600 | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 0 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 12 | 374880
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 24238
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 300 | 3131345
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 36 | 830036 | Engine problem
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 91 | 1855883 | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 50 | 913920
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 107 | 2295818 | Engine problem
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 5018 | On test.
| Chattogram area Total |  |  |  | 2382 | 1264 | 22866085
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 191 | 4614000 | Gas shortage
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 310 | 7698000 | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | Gas shortage
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+136*1 | 284 | 0 | 0 | On test.
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 50 | 1141632
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 30 | 989280 | Gas shortage
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 168 | 4064727
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 0 | 0 | Gas shortage
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 68 | 980218 | Fuel shortage
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 43 | 415328 | Engine problem
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1193950 | Machine problem
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 200 | 1534080
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 168336 | Engine problem
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 10 | 244260
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 136 | 2779200
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 30 | 511200
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 29 | 453518 | Engine problem
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 21 | 408090 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Fuel conservation
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 1322400
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 14280 | Fuel shortage
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 35 | 612720 | Engine problem
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 115 | 1670400
| Cumilla Area Total |  |  |  | 3169 | 1619 | 30815619
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 55 | 1656960 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 13 | 325512 | Engine problem
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 12500
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 88 | 1144800 | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 99 | 1472400 | Engine problem
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 290030
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 144960 | Engine problem
| Mymensingh Area Total |  |  |  | 614 | 261 | 5047162
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 30 | 716000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 42 | 965760 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Gas shortage
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 41 | 762600
| Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 30 | 577224 | Gas shortage
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 0 | 0 | Gas shortage
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 65 | 1403232
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 778560
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 90 | 1298760 | ST Under maint
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 433000 | Gas shortage
| Sylhet 50MW PP (EPL) |  | NENP | 27*2 | 50 | 16 | 310520 | Gas shortage
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 0 | 0 | Gas shortage
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 270 | 7135000 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 415 | 9358000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 225180
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 398 | 9031000
| Sylhet Area Total |  |  |  | 2477 | 1506 | 32994836
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Fuel shortage
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 913 | 20866181
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 49 | 390720 | Fuel shortage
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 42 | 165600 | Engine problem
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 82 | 404352 | Engine problem
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 170 | 4656096 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 8 | 34875 | Fuel shortage
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Fuel conservation
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 54 | 473280 | Fuel shortage
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Fuel shortage
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 554400
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 0 | 0 | 0 | On test.
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 0 | 0 | 0 | 0 | On test.
| Khulna Area Total |  |  |  | 2384 | 1318 | 27545504
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Line O/L
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 0 | 56350 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 60 | 1274000 | Gas shortage
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 900 | 17972700 | Line O/L
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 3981300
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Line O/L
| Barisal 307 MW |  | BCPCL | 0 | 0 | 0 | 414545 | On test.
| Barisal Area Total |  |  |  | 1958 | 1180 | 23698895
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 32 | 164873 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 18 | 69322 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contract Expired
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 34 | 283528 | Engine problem
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 163099 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 161 | 4137773 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 231 | 6157309 | Gas shortage
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 34 | 171144 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 20 | 348000
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 227970
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 8 | 36163 | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 86 | 541568 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Fuel conservation
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 94 | 732480 | Engine problem
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 1059552
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 32220
| Rajshahi Area Total |  |  |  | 2129 | 874 | 14125001
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 10 | 983563 | start up process
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 250 | 6073100
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 1838544
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 39507
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 114 | 793920
| Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 170010
| Rangpur Area Total |  |  |  | 750 | 487 | 9898644
| Total |  |  |  | 21710 | 11297 | 222308826
| Eastern Grid Total |  |  |  | 14489 | 7438 | 147040782
| Western Grid Total |  |  |  | 7221 | 3859 | 75268044
| National Grid Total |  |  |  | 21710 | 11297 | 222308826
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2022-11-05
| (a) ENTIRE EASTERN GRID : |  | 7800.02 | MW | (b) ENTIRE WESTERN GRID : |  | 3014.78 | MW
| i) Dhaka area |  | 4271.72 | MW | i) Khulna area |  | 1147.6 | MW
| ii) Chittagong area |  | 1189.3 | MW | ii) Rajshahi area |  | 987.4 | MW
| iii) Comilla area |  | 1044 | MW | iii) Barisal area |  | 261.78 | MW
| iv) Mymensingh area |  | 858 | MW | iv) Rangpur area |  | 618 | MW
| v) Sylhet area |  | 437 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 10814.8 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 20 | 12:00 | Chowmuhani | 166 | 20:00 | Kaptai | 4 | 18:00 | Nawabganj | 31.9 | 13:00 | Sholosohor | 30 | 17:00
2 | AKSML | 91 | 04:00 | Chuadanga | 78 | 18:00 | Kazla | 98 | 18:30 | Netrakona | 91 | 20:00 | Shyampur | 168 | 09:00
3 | Aftabnagar | 30 | 18:00 | Coxsbazar | 102 | 21:00 | Keranigonj | 58 | 18:00 | New | 62 | 18:00 | Siddhirganj | 102 | 16:00
4 | Agargaon | 71 | 13:00 | Cumilla(N) | 147 | 20:00 | Khagrachori | 30 | 18:00 | Niamatpur | 67 | 18:00 | Sirajganj | 81 | 18:00
5 | Agrabad | 76 | 18:00 | Cumilla(S) | 152 | 18:00 | Khulna | 82 | 12:00 | Noapara | 36 | 18:00 | Sonargaon | 100 | 22:00
6 | Amnura | 43 | 18:30 | Daudkandi | 114 | 19:30 | Khulshi | 177 | 17:00 | PHP | 10 | 18:30 | Sreemongol | 49 | 21:00
7 | Ashuganj | 55 | 18:00 | Dhaka | 32 | 14:00 | Kishoreganj | 114 | 20:00 | Pabna | 85 | 18:00 | Srinagar | 32.84 | 20:00
8 | BSRM | 73 | 03:00 | Dhamrai | 96 | 18:30 | Kodda | 294 | 16:00 | Palashbari | 104 | 18:00 | Sunamganj | 44 | 20:00
9 | Bagerhat | 77 | 19:00 | Dhanmondi | 118 | 14:00 | Kulaura | 34 | 19:00 | Panchagarh | 51 | 18:30 | Sylhet | 125 | 17:00
10 | Bakulia | 123 | 18:00 | Dohazari | 74 | 21:00 | Kurigram | 49 | 19:00 | Patuakhali | 74 | 22:00 | TK | 24.7 | 18:00
11 | Banani | 30 | 12:00 | Faridpur | 110 | 18:00 | Kushtia | 108 | 18:00 | Payra | 0.81 | 12:00 | Tangail | 154 | 20:00
12 | Bangabhaban | 6 | 10:00 | Fatullah | 69 | 17:00 | Lalbag | 70 | 17:00 | Postogola | 35 | 12:00 | Thakurgaon | 62 | 18:30
13 | Barapukuria | 45 | 18:30 | Fenchuganj | 37 | 21:00 | Lalmonirhat | 35 | 18:30 | Purbachal | 14 | 18:30 | Tongi | 119 | 12:00
14 | Barguna | 12 | 18:00 | Feni | 86 | 18:30 | Madanganj | 90 | 18:00 | Purbasadipur | 89 | 18:00 | Ullon | 37 | 19:00
15 | Barishal | 77 | 18:00 | GPH | 98 | 00:00 | Madaripur | 69 | 20:00 | Rahanpur_I | 11.9 | 14:00 | Uttara | 69 | 18:30
16 | Barishal-230 | 54 | 19:00 | Ghorashal | 60 | 19:30 | Madartek | 74 | 23:00 | Rahim | 37 | 11:00 | UttaraNew | 19 | 00:00
17 | Baroaulia | 64 | 14:00 | Goalpara | 18 | 18:00 | Madunaghat | 57 | 18:00 | Rajbari | 50 | 18:00 | Zigatola | 45 | 20:00
18 | Baroirhat | 36 | 17:00 | Gollamari | 40 | 19:00 | Magura | 44 | 18:00 | Rajendrapur | 98 | 19:00
19 | Bashundhara | 135 | 19:00 | Gopalganj | 76.6 | 18:00 | Mahasthangarh | 46 | 18:00 | Rajshahi | 103 | 18:30
20 | BashundharaCement | 6 | 11:00 | Gulshan | 84 | 12:00 | Manikganj | 70 | 19:30 | Rajshahi-230 | 31 | 18:00
21 | Beanibazar | 45 | 21:00 | Halishahar | 90 | 15:00 | Maniknagar | 54 | 12:00 | Ramganj | 76 | 18:30
22 | Benapole | 42 | 18:00 | HaripurSBU | 160 | 11:00 | Matarbari | 34 | 21:00 | Rampur | 26 | 23:00
23 | Bhaluka | 132 | 21:00 | Hasnabad | 75 | 18:00 | Matuail | 62 | 11:00 | Rangamati | 14 | 18:00
24 | Bhandaria | 32 | 20:00 | Hathazari | 54 | 21:00 | Millgate | 68 | 16:00 | Rangpur | 112 | 18:30
25 | Bhangura | 24 | 18:00 | Ishurdi | 60 | 18:00 | Mirpur | 108 | 19:00 | Ruppur | 3 | 18:00
26 | Bheramara(GK) | 43 | 18:00 | Jaldhaka | 41 | 19:30 | Mirsorai | N/A | N/A | SSM | 3 | 01:00
27 | Bhulta | 222 | 18:30 | Jamalpur | 122 | 20:00 | Mithapukur | 22 | 18:00 | Saidpur | 85 | 18:00
28 | Bog-Sherpur | 50 | 18:30 | Jashore | 100 | 18:00 | Modern | 0 | 00:00 | Satkhira | 87 | 18:00
29 | Bogura | 119 | 18:00 | Jhenaidah | 96 | 18:00 | Mogbazar | 105 | 14:00 | Satmasjid | 77 | 14:00
30 | Borhanuddin | 33 | 18:30 | Joydebpur | 185 | 19:00 | Mongla | 30 | 09:00 | Savar | 157 | 17:00
31 | Brahmanbaria | 140 | 21:00 | Joypurhat | 42 | 20:00 | Motijheel | 28 | 11:00 | Shahjadpur | 77 | 18:00
32 | Cantonment | 124 | 19:00 | Juldah | 25 | 23:00 | Munshiganj | 94 | 23:00 | Shahjibazar | 101 | 21:00
33 | Chandpur | 63 | 18:30 | KSRM | 28 | 11:00 | Mymensingh | 166 | 19:00 | Shahmirpur | 42.5 | 00:00
34 | Chandraghona | 28 | 18:00 | Kabirpur | 276 | 15:00 | Naogaon | 90 | 19:00 | Shariatpur | 50 | 18:00
35 | Chapai | 49 | 13:00 | Kachua | 46 | 19:00 | Narail | 44 | 18:00 | Sherpur | 96 | 19:00
36 | Charsaidpur | 40.1 | 01:00 | Kallyanpur | 81 | 19:30 | Narinda | 60 | 12:00 | Shikalbaha | 28 | 21:00
37 | Chauddagram | 44 | 19:00 | Kalurghat | 7 | 13:00 | Narshingdi | 159 | 20:00 | Shikalbaha-230 | N/A | N/A
38 | Chhatak | 21 | 21:00 | Kamrangirchar | 55 | 00:00 | Natore | 104 | 18:00 | Shitalakhya | 96 | 19:30
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2022-11-05 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Bhulta | 396 | 06:00 | 380 | 10:00 | Kaliakoir | 395 | 00:00 | 387 | 16:00
| Bibiana | 404 | 22:00 | 394 | 05:00 | Payra | 423 | 04:00 | 416 | 19:00
| BIPTC | 407 | 04:00 | 393 | 17:00 | Rahanpur_I | 415 | 06:00 | 393 | 11:00
| Gopalganj_I | 426 | 06:00 | 413 | 12:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 229 | 18:00 | 214 | 11:00 | Hasnabad | 229 | 18:00 | 215 | 11:00
| AKSML | 238 | 00:00 | 222 | 02:00 | Hathazari | 238 | 11:00 | 228 | 04:00
| Aminbazar | 231 | 18:00 | 217 | 11:00 | Ishurdi | 240 | 06:00 | 229 | 10:00
| Ashuganj | 242 | 10:00 | 232 | 12:00 | Jhenaidah | 239 | 04:00 | 228 | 12:00
| Baghabari | 237 | 05:00 | 230 | 12:00 | Kaliakoir | 229 | 01:00 | 221 | 16:00
| Barapukuria | 232 | 11:00 | 225 | 07:00 | Keranigonj | 228 | 18:00 | 214 | 11:00
| Barishal | 246 | 06:00 | 240 | 12:00 | Khulna(S) | 245 | 06:00 | 233 | 12:00
| Bheramara | 238 | 06:00 | 226 | 12:00 | Maniknagar | 230 | 18:00 | 217 | 11:00
| Bhulta | 232 | 18:00 | 221 | 10:00 | Meghnaghat | 232 | 03:00 | 222 | 12:00
| Bibiana | 238 | 13:00 | 232 | 17:00 | Mirsorai | N/A | N/A | N/A | N/A
| BIPTC | 240 | 06:00 | 228 | 12:00 | Rajshahi | 242 | 20:00 | 230 | 12:00
| Bogura | 235 | 20:00 | 225 | 10:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 248 | 05:00 | 243 | 13:00 | Rampura | 227 | 08:00 | 217 | 12:00
| BSRM | 237 | 18:00 | 226 | 02:00 | Shikalbaha | 240 | 20:00 | 229 | 03:00
| Cumilla(N) | 232 | 08:00 | 224 | 18:00 | Shyampur | 233 | 02:00 | 215 | 11:00
| Fenchuganj | 241 | 18:00 | 234 | 00:00 | Siddhirganj | 230 | 02:00 | 220 | 12:00
| Ghorashal | N/A | N/A | N/A | N/A | Sirajgonj | 234 | 06:00 | 228 | 16:00
| GPH | 238 | 18:00 | 225 | 02:00 | Tongi | 232 | 04:00 | 217 | 12:00
| Haripur | 227 | 00:00 | 217 | 11:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 136 | 04:00 | 128 | 12:00 | Lalbag | 134 | 18:00 | 125 | 11:00
| Agargaon | 137 | 18:00 | 127 | 12:00 | Lalmonirhat | 135 | 09:00 | 113 | 10:00
| Agrabad | 137 | 08:00 | 131 | 17:00 | Madanganj | 137 | 18:00 | 128 | 12:00
| AKS | 137 | 19:30 | 130 | 22:00 | Madaripur | 140 | 06:00 | 132 | 18:30
| Aminbazar | 140 | 18:00 | 130 | 10:00 | Madartek | 136 | 06:00 | 128 | 11:00
| Amnura | 137 | 22:00 | 126 | 10:00 | Madunaghat | 138 | 08:00 | 132 | 17:00
| Ashuganj | 137 | 18:00 | 134 | 23:00 | Magura | 137 | 00:00 | 131 | 12:00
| Bagerhat | 138 | 00:00 | 130 | 12:00 | Mahasthangarh | 139 | 22:00 | 130 | 16:00
| Bakulia | 139 | 07:00 | 132 | 01:00 | Manikganj | 136 | 18:00 | 125 | 10:00
| Banani | 137 | 00:00 | 125 | 12:00 | Maniknagar | 128 | 07:00 | 119 | 12:00
| Bangabhaban | 129 | 06:00 | 120 | 12:00 | Matarbari | 133 | 13:00 | 120 | 19:30
| Barapukuria | 139 | 06:00 | 127 | 12:00 | Matuail | 135 | 18:00 | 127 | 11:00
| Barguna | 138 | 04:00 | 134 | 18:30 | Millgate | 137 | 01:00 | 126 | 10:00
| Barishal | 139 | 05:00 | 133 | 12:00 | Mirpur | 138 | 18:00 | 127 | 11:00
| Barishal-230 | 140 | 06:00 | 134 | 12:00 | Mithapukur | 139 | 22:00 | 118 | 10:00
| Baroaulia | 140 | 07:00 | 134 | 02:00 | Modern | 138 | 20:00 | 131 | 17:00
| Baroirhat | 137 | 13:00 | 131 | 00:00 | Mogbazar | 137 | 03:00 | 130 | 10:00
| Bashundhara | 139 | 18:00 | 126 | 10:00 | Mongla | 138 | 06:00 | 128 | 12:00
| BashundharaCement | 137 | 18:00 | 128 | 11:00 | Motijheel | 129 | 06:00 | 120 | 11:00
| Beanibazar | 133 | 09:00 | 126 | 21:00 | Munshiganj | 138 | 18:00 | 129 | 11:00
| Benapole | 137 | 03:00 | 127 | 12:00 | Mymensingh | 133 | 09:00 | 119 | 19:30
| Bhaluka | 132 | 15:00 | 115 | 17:00 | Naogaon | 138 | 22:00 | 128 | 16:00
| Bhandaria | 140 | 06:00 | 132 | 12:00 | Narail | 138 | 06:00 | 129 | 18:30
| Bhangura | 142 | 06:00 | 135 | 12:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bheramara | 139 | 06:00 | 134 | 12:00 | Narshingdi | 133 | 07:00 | 121 | 11:00
| Bheramara(GK) | 140 | 04:00 | 134 | 16:00 | Natore | 136 | 06:00 | 130 | 10:00
| Bhulta | 129 | 04:00 | 121 | 12:00 | Nawabganj | 134 | 06:00 | 124 | 12:00
| Bog-Sherpur | 139 | 22:00 | 131 | 10:00 | Netrakona | 130 | 08:00 | 119 | 19:30
| Bogura | 138 | 00:00 | 133 | 10:00 | New | 138 | 18:00 | 127 | 10:00
| Bogura-230 | 139 | 00:00 | 131 | 10:00 | Niamatpur | 137 | 00:00 | 127 | 12:00
| Brahmanbaria | 133 | 07:00 | 128 | 21:00 | Noapara | 138 | 06:00 | 129 | 12:00
| Cantonment | 136 | 18:00 | 126 | 11:00 | Pabna | 139 | 06:00 | 132 | 12:00
| Chandpur | 139 | 19:00 | 132 | 00:00 | Palashbari | 136 | 20:00 | 129 | 12:00
| Chandraghona | 139 | 11:00 | 134 | 03:00 | Panchagarh | 138 | 22:00 | 116 | 10:00
| Chapai | 136 | 22:00 | 124 | 12:00 | Patuakhali | 137 | 05:00 | 133 | 18:00
| Charsaidpur | 137 | 18:00 | 129 | 11:00 | Payra | 138 | 05:00 | 136 | 16:00
| Chauddagram | 137 | 13:00 | 131 | 00:00 | PHP | 137 | 18:00 | 126 | 02:00
| Chhatak | 130 | 18:00 | 125 | 21:00 | Postogola | 139 | 06:00 | 130 | 11:00
| Chowmuhani | 134 | 18:00 | 128 | 23:00 | Purbachal | 137 | 00:00 | 125 | 12:00
| Chuadanga | 137 | 06:00 | 127 | 12:00 | Purbasadipur | 136 | 22:00 | 108 | 10:00
| Coxsbazar | 132 | 11:00 | 119 | 23:00 | Rahim | 139 | 22:00 | 129 | 10:00
| Cumilla(N) | 139 | 18:00 | 133 | 09:00 | Rajbari | 138 | 06:00 | 133 | 12:00
| Cumilla(S) | 139 | 18:00 | 126 | 17:00 | Rajendrapur | 137 | 18:00 | 125 | 11:00
| Daudkandi | 136 | 13:00 | 128 | 11:00 | Rajshahi | 134 | 22:00 | 125 | 12:00
| Dhaka | 137 | 18:00 | 128 | 11:00 | Rajshahi-230 | 133 | 18:00 | 124 | 12:00
| Dhamrai | 138 | 18:00 | 130 | 11:00 | Ramganj | 135 | 13:00 | 129 | 00:00
| Dhanmondi | 135 | 18:00 | 128 | 10:00 | Rampur | 138 | 13:00 | 130 | 17:00
| Dohazari | 136 | 08:00 | 128 | 17:00 | Rampura | 137 | 05:00 | 128 | 12:00
| Faridpur | 138 | 06:00 | 132 | 12:00 | Rangamati | 138 | 07:00 | 133 | 17:00
| Fatullah | 137 | 18:00 | 128 | 11:00 | Rangpur | 137 | 18:00 | 114 | 10:00
| Fenchuganj | 138 | 18:00 | 131 | 21:00 | Ruppur | 139 | 06:00 | 134 | 12:00
| Feni | 138 | 13:00 | 129 | 04:00 | Saidpur | 137 | 22:00 | 116 | 10:00
| Ghorashal | 139 | 00:00 | 133 | 10:00 | Satkhira | 138 | 06:00 | 128 | 18:30
| Goalpara | 140 | 06:00 | 131 | 12:00 | Satmasjid | 137 | 18:00 | 127 | 11:00
| Gollamari | 139 | 06:00 | 133 | 16:00 | Savar | 140 | 18:00 | 127 | 11:00
| Gopalganj | 139 | 06:00 | 133 | 12:00 | Shahjadpur | 142 | 06:00 | 137 | 10:00
| Gopalganj_I | 140 | 06:00 | 134 | 12:00 | Shahjibazar | 135 | 18:00 | 130 | 21:00
| Gulshan | 137 | 18:00 | 127 | 12:00 | Shahmirpur | 138 | 13:00 | 132 | 00:00
| Halishahar | 139 | 13:00 | 130 | 17:00 | Shariatpur | 139 | 06:00 | 132 | 18:30
| Haripur | 134 | 04:00 | 128 | 11:00 | Sherpur | 135 | 09:00 | 119 | 17:00
| HaripurSBU | 139 | 09:00 | 129 | 13:00 | Shikalbaha | 139 | 13:00 | 128 | 18:00
| Hasnabad | 139 | 18:00 | 132 | 11:00 | Shikalbaha-230 | 139 | 08:00 | 134 | 00:00
| Hathazari | 139 | 11:00 | 134 | 03:00 | Shitalakhya | 139 | 06:00 | 129 | 12:00
| Ishurdi | 139 | 06:00 | 134 | 12:00 | Sholosohor | 138 | 09:00 | 131 | 17:00
| Jaldhaka | 135 | 22:00 | 112 | 10:00 | Shyampur | 135 | 18:00 | 127 | 10:00
| Jamalpur | 137 | 23:00 | 123 | 17:00 | Shyampur-230 | 136 | 06:00 | 127 | 12:00
| Jashore | 136 | 00:00 | 119 | 18:30 | Siddhirganj | 136 | 18:00 | 128 | 11:00
| Jhenaidah | 139 | 06:00 | 131 | 12:00 | Sirajganj | 139 | 00:00 | 131 | 10:00
| Jhenaidah-230 | 139 | 06:00 | 131 | 12:00 | Sonargaon | 132 | 00:00 | 129 | 10:00
| Joydebpur | 140 | 18:00 | 130 | 10:00 | Sreemongol | 136 | 07:00 | 132 | 21:00
| Joypurhat | 138 | 22:00 | 127 | 10:00 | Srinagar | 133 | 06:00 | 124 | 12:00
| Juldah | 139 | 15:00 | 132 | 17:00 | SSM | 141 | 07:00 | 134 | 22:00
| Kabirpur | 136 | 18:00 | 122 | 12:00 | Sunamganj | 131 | 08:00 | 123 | 21:00
| Kachua | 137 | 13:00 | 131 | 23:00 | Sylhet | 134 | 08:00 | 128 | 21:00
| Kaliakoir | 137 | 08:00 | 131 | 3:00 | Tangail | 135 | 15:00 | 125 | 17:00
| Kallyanpur | 138 | 18:00 | 127 | 11:00 | Thakurgaon | 138 | 22:00 | 108 | 10:00
| Kalurghat | 139 | 09:00 | 132 | 17:00 | TK | 139 | 07:00 | 132 | 17:00
| Kamrangirchar | 133 | 05:00 | 124 | 12:00 | Tongi | 138 | 04:00 | 127 | 12:00
| Kaptai | 138 | 00:00 | 135 | 16:00 | Ullon | 137 | 05:00 | 128 | 11:00
| Kazla | 128 | 07:00 | 120 | 11:00 | Uttara | 138 | 18:00 | 124 | 12:00
| Keranigonj | 133 | 04:00 | 124 | 11:00 | UttaraNew | 136 | 02:00 | 130 | 16:00
| Khagrachori | 138 | 08:00 | 133 | 02:00 | Zigatola | 133 | 18:00 | 124 | 11:00
| Khulna | 138 | 00:00 | 130 | 12:00
| Khulna(S) | 139 | 06:00 | 131 | 12:00
| Khulshi | 137 | 13:00 | 129 | 17:00
| Kishoreganj | 132 | 09:00 | 123 | 19:30
| Kodda | 140 | 18:00 | 125 | 05:00
| KSRM | 139 | 18:00 | 133 | 03:00
| Kulaura | 136 | 08:00 | 131 | 21:00
| Kurigram | 134 | 06:00 | 128 | 18:30
| Kushtia | 139 | 06:00 | 132 | 12:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2022-11-05
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 1450 | 6269 | 3374 | 9643 |  |  |  | QF-LDC-11
0:30 | 1305 | 5977.5 | 3130 | 9107.5 | Date: | 2022-11-05
1:00 | 1160 | 5686 | 2886 | 8572
1:30 | 1162 | 5510.5 | 2878 | 8388.5
2:00 | 1164 | 5335 | 2870 | 8205
2:30 | 1142 | 5278 | 2821.5 | 8099.5 | [5 empty] | Gen. at Eve. Peak | 11297 | 11297 MW (20:00 )
3:00 | 1120 | 5221 | 2773 | 7994 | [6 empty] | 20:00
3:30 | 1075 | 5180 | 2662.5 | 7842.5 | [5 empty] | Gen. at Day Peak | 8994 | 8994 MW (12:00 )
4:00 | 1030 | 5139 | 2552 | 7691 | [6 empty] | 12:00
4:30 | 1019 | 5035.5 | 2547 | 7582.5 | [5 empty] | Highest Generation | 11297
5:00 | 1008 | 4932 | 2542 | 7474 | [6 empty] | 20:00
5:30 | 979 | 4995 | 2560.5 | 7555.5
6:00 | 950 | 5058 | 2579 | 7637
6:30 | 765 | 5202 | 2593 | 7795
7:00 | 580 | 5346 | 2607 | 7953
7:30 | 581 | 5418.5 | 2640 | 8058.5
8:00 | 582 | 5491 | 2673 | 8164
8:30 | 581 | 5590.5 | 2673.5 | 8264
9:00 | 580 | 5690 | 2674 | 8364
9:30 | 797 | 5656 | 2623.5 | 8279.5
10:00 | 1014 | 5622 | 2573 | 8195
10:30 | 982 | 5752.5 | 2650.5 | 8403
11:00 | 950 | 5883 | 2728 | 8611
11:30 | 870 | 6001 | 2801.5 | 8802.5
12:00 | 790 | 6119 | 2875 | 8994
12:30 | 710 | 6116 | 2940 | 9056
13:00 | 630 | 6113 | 3005 | 9118
13:30 | 685 | 6176 | 2991.5 | 9167.5
14:00 | 740 | 6239 | 2978 | 9217
14:30 | 730 | 6330.5 | 2976 | 9306.5
15:00 | 720 | 6422 | 2974 | 9396
15:30 | 765 | 6434.5 | 2901 | 9335.5
16:00 | 810 | 6447 | 2828 | 9275
16:30 | 995 | 6494 | 2980 | 9474
17:00 | 1180 | 6541 | 3132 | 9673
17:30 | 930 | 6776.5 | 3388 | 10164.5
18:00 | 680 | 7012 | 3644 | 10656
18:30 | 820 | 7128 | 3746 | 10874
19:00 | 960 | 7244 | 3848 | 11092
19:30 | 1050 | 7404 | 3848 | 11252
20:00 | 1030 | 7438 | 3859 | 11297 |  |  |  | Executive Engineer
20:30 | 1160 | 7265.5 | 3854 | 11119.5 |  |  |  | Network Operation Division
21:00 | 1290 | 7093 | 3849 | 10942
21:30 | 1330 | 7002 | 3822 | 10824
22:00 | 1370 | 6911 | 3795 | 10706 |  |  |  |  | Page 6 of 7
22:30 | 1414 | 6776.5 | 3653.5 | 10430
23:00 | 1458 | 6642 | 3512 | 10154
23:30 | 1454 | 6455.5 | 3443 | 9898.5
24:00 | 1450 | 6269 | 3374 | 9643
11297 MW (20:00 )
8994 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2022-11-05 |  | Energy |  | 222308826
[13 empty] | 2022-11-05 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 3181 | 899 | 1670 | 0 | 2283 | 1134 | 154 | 0 | 186 | 136 | 0 | 792
0:30 | 3129.5 | 905.5 | 1672 | 0 | 1919 | 1104.5 | 153.5 | 0 | 102.5 | 121 | 0 | 396 | Date: | 2022-11-05
1:00 | 3078 | 912 | 1674 | 0 | 1555 | 1075 | 153 | 0 | 19 | 106 | 0 | 0
1:30 | 3052 | 911.5 | 1670.5 | 0 | 1407.5 | 1069 | 153 | 0 | 22 | 103 | 0 | 0 | [8 empty] | Total Energy | 222.3088 | Total Energy Gen 222.309 MKWHr Energy Not Served 2.778 MKWHr Energy Requirement 225.087 MKWHr
2:00 | 3026 | 911 | 1667 | 0 | 1260 | 1063 | 153 | 0 | 25 | 100 | 0 | 0 | [8 empty] | Energy not Served | 2.778
2:30 | 3006 | 911.5 | 1672.5 | 0 | 1204.5 | 1028 | 153 | 0 | 25 | 99 | 0 | 0 | [8 empty] | Energy Requirement | 225.0868
3:00 | 2986 | 912 | 1678 | 0 | 1149 | 993 | 153 | 0 | 25 | 98 | 0 | 0
3:30 | 2982 | 830 | 1680.5 | 0 | 1119.5 | 958.5 | 153 | 0 | 25 | 94 | 0 | 0 | [6 empty] | Shortage
4:00 | 2978 | 748 | 1683 | 0 | 1090 | 924 | 153 | 0 | 25 | 90 | 0 | 0
4:30 | 2928.5 | 736 | 1699.5 | 0 | 1029 | 919.5 | 153 | 0 | 25 | 92 | 0 | 0
5:00 | 2879 | 724 | 1716 | 0 | 968 | 915 | 153 | 0 | 25 | 94 | 0 | 0
5:30 | 2902 | 724 | 1751 | 0 | 998.5 | 911 | 153 | 0 | 25 | 91 | 0 | 0
6:00 | 2925 | 724 | 1786 | 0 | 1029 | 907 | 153 | 0 | 25 | 88 | 0 | 0
6:30 | 2961.5 | 723.5 | 1818 | 0 | 1138 | 879 | 153 | 0 | 25 | 85 | 12 | 0 |  |  |  |  | Coal
7:00 | 2998 | 723 | 1850 | 0 | 1247 | 851 | 153 | 0 | 25 | 82 | 24 | 0
7:30 | 2965.5 | 723 | 1837.5 | 0 | 1373 | 860 | 136 | 0 | 25 | 86 | 52.5 | 0 |  |  |  | Oil |  |  |  | ,
8:00 | 2933 | 723 | 1825 | 0 | 1499 | 869 | 119 | 0 | 25 | 90 | 81 | 0
8:30 | 2932 | 723.5 | 1822.5 | 0 | 1575 | 874.5 | 118.5 | 0 | 25 | 85 | 108 | 0
9:00 | 2931 | 724 | 1820 | 0 | 1651 | 880 | 118 | 0 | 25 | 80 | 135 | 0
9:30 | 2893.5 | 818 | 1759 | 0 | 1574.5 | 835 | 119 | 0 | 25 | 86 | 169.5 | 0
10:00 | 2856 | 912 | 1698 | 0 | 1498 | 790 | 120 | 0 | 25 | 92 | 204 | 0
10:30 | 2894 | 912 | 1676 | 0 | 1634 | 810 | 119 | 0 | 45 | 103 | 210 | 76.9515
11:00 | 2932 | 912 | 1654 | 0 | 1770 | 830 | 118 | 0 | 65 | 114 | 216 | 153.903
11:30 | 2901 | 912 | 1648.5 | 0 | 1936 | 855 | 118 | 0 | 99.5 | 121 | 211.5 | 171.8737
12:00 | 2870 | 912 | 1643 | 0 | 2102 | 880 | 118 | 0 | 134 | 128 | 207 | 189.8445
12:30 | 2823.5 | 912 | 1646 | 0 | 2164.5 | 910 | 117.5 | 0 | 152.5 | 129 | 201 | 225.3251
13:00 | 2777 | 912 | 1649 | 0 | 2227 | 940 | 117 | 0 | 171 | 130 | 195 | 260.8057
13:30 | 2777 | 912 | 1649 | 0 | 2227 | 940 | 117 | 0 | 171 | 130 | 195 | 260.8057
14:00 | 2777 | 912 | 1649 | 0 | 2227 | 940 | 117 | 0 | 171 | 130 | 195 | 260.8057
14:30 | 2817.5 | 912 | 1703 | 0 | 2302.5 | 915 | 134.5 | 1.5 | 178.5 | 131 | 161.5 | 224.4035
15:00 | 2858 | 912 | 1757 | 0 | 2378 | 890 | 152 | 3 | 186 | 132 | 128 | 188.0013
15:30 | 2912 | 912 | 1753.5 | 0 | 2312 | 880 | 152 | 1.5 | 193.5 | 129 | 90 | 197.6778
16:00 | 2966 | 912 | 1750 | 0 | 2246 | 870 | 152 | 0 | 201 | 126 | 52 | 207.3544
16:30 | 2989 | 912.5 | 1745 | 0 | 2346 | 890 | 152.5 | 0 | 292 | 130 | 28.5 | 103.6772
17:00 | 2989 | 913 | 1740 | 0 | 2446 | 910 | 153 | 0 | 383 | 134 | 5 | 0
17:30 | 2964.5 | 912.5 | 1731 | 0 | 2798 | 984.5 | 153 | 0 | 475.5 | 143 | 2.5 | 343
18:00 | 2940 | 912 | 1722 | 0 | 3150 | 1059 | 153 | 0 | 568 | 152 | 0 | 686
18:30 | 2998 | 912 | 1730 | 0 | 3256.5 | 1104.5 | 153 | 0 | 574 | 146 | 0 | 519.5
19:00 | 3056 | 912 | 1738 | 0 | 3363 | 1150 | 153 | 0 | 580 | 140 | 0 | 353
19:30 | 3075 | 912 | 1741 | 0 | 3489 | 1160 | 154 | 0 | 579 | 142 | 0 | 176.5
20:00 | 3162 | 913 | 1696 | 0 | 3501 | 1160 | 154 | 0 | 575 | 136 | 0 | 0
20:30 | 3187.5 | 906 | 1586 | 0 | 3442 | 1155 | 154 | 0 | 554 | 135 | 0 | 0
21:00 | 3213 | 899 | 1476 | 0 | 3383 | 1150 | 154 | 0 | 533 | 134 | 0 | 0
21:30 | 3152.5 | 899 | 1517 | 0 | 3284.5 | 1186.5 | 154 | 0 | 491.5 | 139 | 0 | 0
22:00 | 3092 | 899 | 1558 | 0 | 3186 | 1223 | 154 | 0 | 450 | 144 | 0 | 0
22:30 | 3091 | 899.5 | 1572 | 0 | 3042.5 | 1210 | 154 | 0 | 318 | 143 | 0 | 0
23:00 | 3090 | 900 | 1586 | 0 | 2899 | 1197 | 154 | 0 | 186 | 142 | 0 | 0
23:30 | 3135.5 | 899.5 | 1628 | 0 | 2591 | 1165.5 | 154 | 0 | 186 | 139 | 0 | 0 | Max Temp. in Dhaka |  | 24.7° C | 31.7° C
24:00 | 3181 | 899 | 1670 | 0 | 2283 | 1134 | 154 | 0 | 186 | 136 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 222.309 MKWHr Energy Not Served 2.778 MKWHr Energy Requirement 225.087 MKWHr
Note on W13: Author:

## Generation
g | 2022-11-05
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 84 | 83 | 85 | 83 | 83 | 82 | 82 | 82 | 82 | 83 | 83 |  | 83 | 84 | 84 | 84 | 84 | 84 | 84 | 1946803
2 | Karnaphuli Hydro PP Unit-4 & 5 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1444000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [11 empty] | 6 | 19 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 311086
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 4 | 10 | 15 | 18 | 20 | 9 | 18 | 16 | 12 | 5 | 0 | [9 empty] | 130815
6 | Sikalbaha 225MW CCPP (Gas) | 151 | 151 | 151 | 151 | 152 | 152 | 152 | 152 | 151 | 151 | 151 | 151 | 152 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 151 | 151 | 3509324
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 11 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 16 | 16 | 16 | 16 | 17 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 616332
12 | Hathazari 100 MW peaking PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | [6 empty] | 21 |  | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 224388
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 57 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 87 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 63 | 1784799
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP | [11 empty] | 19 | 40 | 41 | 38 | 42 | 35 | 40 |  | 43 | 43 | 43 | 43 | 43 | 0 | 0 | 415328
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 275 | 210 | 210 | 180 | 145 | 170 | 203 | 226 | 223 | 180 | 180 | 185 | 218 | 255 | 258 | 260 | 260 | 268 |  | 276 | 276 | 276 | 276 | 276 | 276 | 276 | 5678073
19 | Ashuganj 195MW PP (APSCL-United) | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 |  | 168 | 168 | 168 | 168 | 168 | 170 | 170 | 4064727
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4378500
24
25 | Ghorasal 365 MW CCPP Unit-7 | [13 empty] | 70 | 80 | 130 | 120 | 120 |  | 110 | 120 | 140 | 150 | 150 | 150 | 180 | 1304600
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 51 | 48 | 48 | 48 | 48 | 48 | 48 | 45 | 48 | 45 | 47 | 47 | 50 | 50 | 46 | 44 | 49 | 50 |  | 50 | 50 | 50 | 51 | 51 | 51 | 51 | 1141632
33 | Ashuganj 225 MW CCPP | 181 | 186 | 181 | 181 | 201 | 182 | 202 | 185 | 211 | 207 | 198 | 169 | 174 | 192 | 200 | 202 | 199 | 200 |  | 199 | 194 | 191 | 186 | 178 | 182 | 168 | 4614000
34 | Ashuganj 450 MW CCPP(South)
| Ashuganj 450 MW CCPP(North) | 310 | 285 | 280 | 280 | 315 | 280 | 325 | 315 | 310 | 330 | 350 | 340 | 320 | 300 | 280 | 305 | 280 | 280 |  | 310 | 310 | 310 | 310 | 310 | 310 | 315 | 7698000
Ashuganj 420 MW CCPP(East)
35 | Ashuganj 55 MW PP (Precision) | 50 | 51 | 52 | 52 | 51 | 51 | 52 | 51 | 50 | 48 | 47 | 48 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 31 | 989280
36 | Chandpur 150 MW CCPP | 52 | 50 | 51 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 48 | 49 | 49 | 50 | 50 | 50 | 52 | 50 |  | 49 | 50 | 50 | 50 | 50 | 50 | 50 | 1193950
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 384 | 358 | 345 | 345 | 346 | 362 | 371 | 373 | 370 | 361 | 375 | 397 | 385 | 361 | 369 | 361 | 359 | 349 |  | 348 | 348 | 348 | 322 | 260 | 233 | 232 | 8445950
40 | Meghnaghat 450 MW CCPP(MPL) | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 215 | 215 | 215 | 200 | 215 | 215 | 215 | 215 | 195 | 195 |  | 190 | 190 | 190 | 200 | 210 | 215 | 215 | 4786100
41 | Haripur 360MW CCPP(HPL) | 245 | 261 | 268 | 269 | 275 | 277 | 277 | 276 | 276 | 272 | 258 | 248 | 240 | 240 | 230 | 227 | 212 | 198 |  | 192 | 192 | 192 | 204 | 218 | 217 | 252 | 5798000
42 | RPCL 210MW CCPP | 109 | 109 | 111 | 110 | 110 | 110 | 108 | 73 | 73 | 33 | 33 | 33 | 33 | 33 | 34 | 33 | 33 | 33 |  | 47 | 52 | 55 | 102 | 98 | 105 | 104 | 1656960
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 0 | 6 | 21 | 35 | 43 | 38 | 35 | 22 | 27 | 31 | 11 | 1 | [9 empty] | 290030
44 | Fenchugonj CCPP Phase-1 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 716000
45 | Fenchugonj CCPP Phase-2 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 42 | 42 | 41 | 41 | 42 | 43 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 965760
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 63 | 63 | 63 | 63 | 63 | 63 | 53 | 40 | 40 | 67 | 63 | 62 | 40 | 40 | 64 | 63 | 64 | 68 |  | 68 | 67 | 65 | 63 | 63 | 63 | 60 | 1403232
48 | Shahjibazar 86MW PP (Shahjibazar) |  |  |  |  | 0 | 10 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 81 |  | 81 | 81 | 81 | 40 | 81 | 81 | 81 | 778560
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 145 | 145 | 145 | 145 | 0 | [14 empty] | 35 | 35 | 90 | 145 | 145 | 145 | 145 | 1298760
51 | Sylhet 20 MW GTPP | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 433000
52 | Sylhet 50MW PP (EPL) | [5 empty] | 0 | 6 | 22 | 24 | 25 | 25 | 23 | 24 | 24 | 25 | 25 | 25 | 23 |  | 26 | 26 | 16 |  |  |  | 0 | 310520
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 9 | 9 | 9 | 9 | 8 | 8 | 8 | 8 | 8 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 225180
54 | Hobiganj 11MW PP Cofidence-E
55 | Fenchugonj 51 MW PP (Barakatullah) |  |  |  |  | 0 | 32 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 |  | 53 | 53 | 41 |  |  |  | 0 | 762600
56 | Shahjahanulla 25 MW PP | [25 empty] | 0 | 0
57 | Bibiana-II 341 MW CCPP (Summit) | 290 | 280 | 290 | 280 | 290 | 290 | 300 | 290 | 280 | 290 | 310 | 290 | 300 | 290 | 300 | 295 | 315 | 280 |  | 285 | 290 | 270 | 275 | 270 | 280 | 320 | 7135000
| Bibiyana South 400 MW | 350 | 350 | 350 | 350 | 350 | 401 | 400 | 400 | 400 | 350 | 390 | 380 | 350 | 350 | 389 | 388 | 398 | 372 |  | 400 | 400 | 398 | 361 | 335 | 360 | 400 | 9031000
58 | Nababganj 55 MW PP (Southern power ) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 55 | 55 | 55 | 35 | 35 | 35 | 35 | 905614
59 | Tangail Palli Power Gen 22 MW | 6 | 6 | 6 | 6 | 3 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 144960
60 | Barabkunda 22 MW PP (Regent) | [25 empty] | 0 | 0
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 454140
62 | Tangail 22 MW PP (Doreen) | 16 | 16 | 16 | 16 | 0 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 15 | 15 | 13 | 13 | 13 | 13 |  | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 325512
63 | Impoprt (Tripura) | 106 | 100 | 98 | 90 | 94 | 88 | 82 | 90 | 80 | 92 | 114 | 128 | 130 | 132 | 132 | 126 | 134 | 152 |  | 140 | 142 | 136 | 134 | 144 | 142 | 136 | 2779200
64 | Malancha, Ctg. EPZ (United) | 29 | 29 | 29 | 29 | 29 | 29 | 21 | 2 | 18 | 18 | 3 | 3 | 2 | 2 | 2 | 2 | 4 | 2 |  | 8 | 5 | 12 | 16 | 31 | 38 | 32 | 374880
65 | Feni 22MW PP (Doreen) | [13 empty] | 1 | 16 | 16 | 16 | 19 |  | 19 | 19 | 19 | 19 | 17 | 17 | 16 | 168336
66 | Feni 11 MW PP (Doreen) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 8 | 8 | 8 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 244260
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 16 | 13 | 10 | 7 | 7 | 7 | 7 | 8 | 8 | 8 | 8 |  | 15 | 16 | 30 | 33 | 33 | 33 | 33 | 511200
68 | Cumilla 25 MW PP (Summit) | 20 | 19 | 19 | 15 | 15 | 15 | 15 | 15 |  | 12 | 12 | 12 | 12 | 12 | 21 | 20 | 20 | 20 |  | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 408090
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 22 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 |  | 23 | 23 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 24 | 27 | 19 | 19 | 19 | 19 | 24 | 24 | 23 | 26 | 24 |  | 22 | 26 | 26 | 26 | 26 | 26 | 26 | 574200
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 775080
72 | Rupganj 33 MW PP(Summit) | 32 | 32 | 33 | 33 | 33 | 17 | 33 | 32 | 31 | 30 | 30 | 28 | 28 | 28 | 28 | 28 | 26 | 26 |  | 26 | 28 | 29 | 29 | 30 | 30 | 32 | 712100
73 | Ghorashal 108MW PP (Regent) | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 70 | 73 | 73 |  | 73 | 73 | 73 | 52 | 52 | 52 | 62 | 1651818
| Feni Lanka Power | 17 | 0 |  |  |  |  | 14 | 17 | 34 | 17 | 23 | 96 | 96 | 96 | 96 | 114 | 114 | 114 |  | 114 | 114 | 114 | 99 | 99 | 17 | 17 | 1322400
| Chowmuhani 113 MW | [22 empty] | 8 |  |  | 0 | 14280
| Manikgonj 162MW PP(MPGL) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 70 | 90 | 90 | 144 | 144 |  | 144 | 144 | 144 | 144 | 144 | 108 | 35 | 1797120
77 | Siddhirganj 100 PP(Dutch Bangla) | 8 | 0 |  |  |  |  | 1 | 8 | 32 | 42 | 26 | 63 | 72 | 71 | 71 | 71 | 77 | 88 |  | 88 | 88 | 88 | 88 | 88 | 88 | 65 | 1123200
78 | Gazipur 52 MW PP | [8 empty] | 26 | 49 | 41 | 49 | 49 | 49 | 49 | 49 | 49 | 49 |  | 49 | 49 | 49 | 24 | 39 | 49 | 41 | 702240
79 | Kodda 150MW PP | [10 empty] | 40 | 98 | 115 | 132 | 132 | 132 | 132 | 132 |  | 132 | 132 | 132 | 98 | 132 | 64 | 64 | 1494240
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 34 | 30 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 12 | 34 |  | 25 | 29 | 29 | 40 | 35 | 34 | 34 | 453518
| Gazipur 100 MW PP | 70 | 17 | 0 | [6 empty] | 4 | 88 | 88 | 88 | 88 | 90 | 93 | 90 | 90 |  | 100 | 100 | 100 | 100 | 105 | 90 | 70 | 1387572
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 0 | 2 | 3 | 3 | 4 | 4 | 4 | 3 | 2 | 1 | [10 empty] | 24238
| Jodiac Power | 36 | 17 | 17 | 17 | 17 | 20 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 |  | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 830036
| Karnaphuli Power Ltd. | 74 | 72 | 72 | 72 | 72 | 72 | 65 | 71 | 71 | 71 | 71 | 71 | 56 | 66 | 71 | 71 | 83 | 91 |  | 91 | 91 | 91 | 91 | 91 | 91 | 61 | 1855883
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP ( Summit) | 138 | 128 | 128 | 128 | 128 | 125 | 123 | 125 | 130 | 130 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 120 |  | 112 | 112 | 112 |  |  |  | 0 | 2693091
87 | Meghnaghat 100 MW(IEL) | [7 empty] | 7 | 8 | 8 | 11 | 46 | 52 | 64 | 66 | 69 | 68 | 75 |  | 86 | 92 | 92 | 89 | 89 | 92 | 62 | 975360
| Meghnaghat 104 MW PP (OPCL) | 52 | 47 | 17 | 18 | 17 | 20 | 34 | 49 | 60 | 59 | 37 | 71 | 73 | 73 | 73 | 73 | 73 | 87 |  | 93 | 93 | 93 | 93 | 93 | 92 | 72 | 1479360
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 75 | 77 | 66 | 66 | 66 | 66 | 87 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 76 | 76 | 66 |  | 66 | 66 | 66 | 66 | 66 | 66 | 22 | 1880520
92 | Fenchuganj 44MW (Energyprima) |  |  |  |  | 0 | 7 | 22 | 36 | 44 | 44 | 44 | 44 | 40 | 43 | 43 | 43 | 43 | 40 |  | 40 | 40 | 30 |  |  |  | 0 | 577224
93 | Ashuganj 51 MW PP (Midland)
94 | Gagnagar 102 MW PP (Digital Power) | 58 | 58 | 55 | 50 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 92 |  | 92 | 92 | 92 | 92 | 92 | 92 | 58 | 1580832
95 | Patenga 50MW PP (Baraka) | 26 | 0 |  |  |  |  | 7 | 29 | 35 | 39 | 39 | 39 | 39 | 39 | 39 | 42 |  | 14 |  | 37 | 44 | 44 | 44 | 44 | 44 | 34 | 689280
96 | Chattogram 108 MW PP (ECPV) | [25 empty] | 0 | 0
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 47 | 40 | 1319012
100 | Manikganj 55 MW PP (Northern) | [7 empty] | 17 | 17 | 17 | 35 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 781284
101 | Kushiara 163 MW CCPP (KP)
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 1 | 2 | 1 | 1 | 2 | 2 | 1 | 0 | 0 | [9 empty] | 12500
103 | Kamalaghat 54 MW PP(Banco Energy) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 22 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 17 | 660960
104 | Keranigonj 300 MW PP (APR) | [25 empty] | 0 | 0
105 | Bramhangoan 100 MW PP (Aggreko) | [25 empty] | 0 | 0
106 | Mymensingh 200 MW PP (United) | 48 | 8 | 8 | 8 | 8 | 8 | 12 | 47 | 47 | 47 | 48 | 48 | 48 | 49 | 49 | 49 | 49 | 86 |  | 87 | 88 | 88 | 88 | 88 | 88 | 55 | 1144800
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 132 | 133 | 105 | 80 | 40 | 17 | 39 | 86 | 133 | 132 | 132 | 149 | 149 | 149 | 149 | 134 | 134 | 132 |  | 133 | 133 | 133 | 137 | 149 | 149 | 149 | 2919168
115 | Juldah 100 MW PP Unit-3 (Acorn) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 25 | 897600
116 | Chandpur 200MW (Desh energy) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 16 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 95 | 200 | 200 | 136 | 80 | 51 | 51 | 1534080
117 | Ashuganj 150MW PP (Midland) | 20 | 0 |  |  |  |  | 1 | 13 | 43 | 10 | 27 | 40 | 48 | 50 | 50 | 53 | 58 | 65 |  | 73 | 70 | 68 | 72 | 68 | 80 | 70 | 980218
118 | Bibiyana-III 400 MW CCPP | 354 | 353 | 353 | 353 | 353 | 407 | 408 | 408 | 408 | 404 | 404 | 408 | 358 | 360 | 355 | 366 | 415 | 414 |  | 415 | 416 | 415 | 409 | 407 | 365 | 407 | 9358000
| Jamalpur 115 MW PP (United) | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 98 |  | 99 | 99 | 99 | 99 | 99 | 99 | 49 | 1472400
| Anwara 300 MW PP (United) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 118 | 122 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 273 |  | 284 | 300 | 300 | 284 | 124 | 124 | 124 | 3131345
| Juldah unit-2 (Acorn) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 27 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 25 | 913920
| Anlima Energy Ltd. | 107 | 68 | 68 | 68 | 17 | 27 | 51 | 100 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 |  | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 2295818
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 23 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 612720
| Spectra Solar Plant Ltd. | [6 empty] | 3 | 12 | 20 | 25 | 29 | 30 | 28 | 22 | 12 | 4 | 1 | [9 empty] | 187906
| Chandpur 115(Doreen) | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 52 | 53 | 39 | 53 | 53 | 68 | 105 |  | 115 | 115 | 115 | 112 | 115 | 115 | 79 | 1670400
| Kanchan Purbachal Power Generation Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | [18 empty] | 11 | 151560
| Mirsharai 150 MW (Oil) | [14 empty] | 3 | [10 empty] | 0 | 5018
Mirsharai 150 MW (Gas)
120 | Eastern Zone Total | 5686 | 5335 | 5221 | 5139 | 4932 | 5058 | 5346 | 5491 | 5690 | 5622 | 5883 | 6119 | 6113 | 6239 | 6422 | 6447 | 6541 | 7012 |  | 7244 | 7404 | 7438 | 7093 | 6911 | 6642 | 6269 | 147040782
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | [12 empty] | 32 | 32 | 32 |  | 16 | 49 |  | 49 | 32 | 49 | 49 | 49 | 49 | 16 | 390720
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [16 empty] | 10 | 51 |  | 43 | 42 | 42 | 33 | 0 |  |  | 165600
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | [12 empty] | 17 | 35 | 35 |  | 5 | 54 |  | 54 | 56 | 54 | 54 | 57 | 57 | 57 | 473280
130 | Mongla Orion 100 MW Solar PP | [6 empty] | 9 | 31 | 55 | 74 | 83 | 84 | 79 | 65 | 46 | 21 | 2 | [9 empty] | 554400
131 | Rampal 1320 MW (BIFPCL)
132 | United Payra Power Ltd. | [25 empty] | 0 | 0
133 | Bhola Nutan Biddut BD LTD (GAS) | 163 | 163 | 163 | 160 | 162 | 162 | 163 | 160 | 160 | 64 | 64 | 64 | 87 | 125 | 221 | 221 | 221 | 210 |  | 222 | 222 | 220 | 220 | 220 | 223 | 220 | 3981300
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [25 empty] | 0 | 0
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW | 65 | 63 | 64 | 64 | 65 | 48 | [20 empty] | 414545
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 70 | 70 | 70 | 68 | 68 | 40 | 30 | 30 | 30 | 30 | 65 | 62 | 66 | 30 | 30 | 60 | 60 | 43 |  | 60 | 60 | 60 | 60 | 40 | 70 | 70 | 1274000
140 | Bhola 33 MW PP (Venture) | [7 empty] | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | [5 empty] | 11 | 21 | 20 | 19 | 56350
141 | Noapara 100 MW PP (Bangla Trac) | [25 empty] | 0 | 0
142 | Noapara 40 MW PP (Khanjahan Ali) | [17 empty] | 8 |  | 8 | 8 | 8 | 8 | 8 | 0 | 0 | 34875
143 | Gopalganj 100 MW Peaking PP | [15 empty] | 11 | 56 | 75 |  | 84 | 82 | 82 | 82 | 10 | 0 |  | 404352
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 912 | 911 | 912 | 748 | 724 | 724 | 723 | 723 | 724 | 912 | 912 | 912 | 912 | 913 | 912 | 912 | 913 | 912 |  | 912 | 912 | 913 | 899 | 899 | 900 | 899 | 20866181
147 | Bheramara 410 MW CCPP | 195 | 195 | 195 | 200 | 205 | 215 | 215 | 215 | 205 | 195 | 180 | 180 | 180 | 180 | 170 | 175 | 170 | 170 |  | 170 | 170 | 170 | 180 | 180 | 180 | 175 | 4656096
148 | Payra 1320 MW | 680 | 670 | 600 | 530 | 520 | 530 | 520 | 540 | 550 | 540 | 580 | 630 | 690 | 640 | 640 | 620 | 660 | 810 |  | 900 | 910 | 900 | 900 | 900 | 870 | 810 | 17972700
149
150 | Barapukuria TPP Unit-1 | 81 | 81 | 80 | 81 | 81 | 80 | 81 | 79 | 80 | [12 empty] | 10 |  | 73 | 77 | 74 | 983563
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 249 | 249 | 249 | 249 | 249 | 249 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 249 |  | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 6073100
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [16 empty] | 24 | 32 |  | 32 | 32 | 32 | 32 | 32 | 0 |  | 164873
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 2 | 3 | 4 | 2 | 5 | 4 | 4 | 2 | 0 | 0 | [9 empty] | 32220
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 165 | 166 | 145 | 140 | 140 | 140 | 145 | 179 | 182 | 180 | 177 | 176 | 170 | 168 | 163 | 163 | 162 | 161 |  | 161 | 161 | 161 | 162 | 164 | 164 | 164 | 4137773
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 276 | 272 | 287 | 304 | 320 | 328 | 331 | 310 | 281 | 270 | 214 | 250 | 238 | 232 | 217 | 221 | 219 | 222 |  | 228 | 228 | 231 | 231 | 231 | 230 | 238 | 6157309
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [16 empty] | 5 | 5 |  | 13 | 18 | 18 | 18 | 16 | 0 |  | 69322
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 0 | 0 | 0 | 15 | 22 | 20 | 19 | 0 | 17 | 16 | 16 | 16 | 15 | 15 | 17 | 17 |  | 20 | 21 | 20 | 19 | 16 | 20 | 20 | 348000
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 227970
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | [7 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 25 | 34 |  | 34 | 34 | 34 | 34 | 34 | 8 | 8 | 283528
167 | Katakhali 50 MW Peaking PP | [16 empty] | 32 | 40 |  | 35 | 32 | 32 | 32 | 24 | 0 |  | 163099
168 | Santahar 50 MW Peaking PP | [17 empty] | 35 |  | 38 | 38 | 34 | 35 | 33 | 0 |  | 171144
169 | Natore 52 MW PP (Rajlanka) | [17 empty] | 8 |  | 8 | 8 | 8 | 8 | 8 | 0 | 0 | 36163
170 | Chapainawabganj 100 MW Peaking PP | [16 empty] | 72 | 86 |  | 86 | 86 | 86 | 86 | 86 | 48 | 48 | 541568
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [12 empty] | 7 | 35 | 35 |  | 9 | 41 |  | 90 | 94 | 94 | 94 | 94 | 94 | 94 | 732480
172 | Confidence Power Bogura Unit-1 113 MW | [10 empty] | 18 | 75 | 70 | 70 | 35 |  | 25 | 100 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 1059552
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) |  |  |  |  | 0 | 40 | 108 | 113 | 113 |  | 108 | 113 | 113 | 113 | 113 | 113 | 113 | 113 |  | 113 | 113 | 113 | 113 | 113 | 56 | 56 | 1838544
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 2 | 3 | 5 | 6 | 6 | 7 | 7 | 5 | 2 | 0 | [9 empty] | 39507
178 | Energypac Power Venture Thakurgaon Ltd. | [12 empty] | 17 | 17 | 17 | 17 | 54 | 108 |  | 114 | 115 | 114 | 115 | 113 | 72 | 35 | 793920
178 | Intraco Solar 30 MW | [6 empty] | 2 |  | 0 | 30 | 33 | 33 | 31 | 27 | 17 | 8 | 1 | [9 empty] | 170010