## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on forecasted generation & Demand of national grid on | [6 empty] | 2019-05-19 | Sunday
|  | Date (day): | 2019-05-19 |  | Sunday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13828 | MW |  |  | (b) At Evening Peak Hour : |  | 14146 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2019-05-18 | 2019-05-19 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | Gas | PDB | 2*55 | 110 | 85 | 74 | 74 | 74 | 74
| Ghorasal GT: Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 145 | 0 | 0 |  |  | On test.
| Ghorasal GT: Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 140 | 140 | 140
| Ghorasal ST: Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint.
2 | Ghorasal ST: Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 370 | 260 | 360 | 360
3 | Ghorashal 78MW (MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 50 | 69 | 50 | 50 | 28 |  | Gas shortage
4 | Ghorashal (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 85 | 106 | 50 | 106 | 2
5 | Haripur GT: Unit-1, 2 |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 | 40 |  | Gas shortage
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 347 | 350 | 412 | 412 |  |  | FGMO
7 | Haripur NEPC 110MW |  | HFO | IPP | 8*15 | 110 | 110 | 0 | 55 | 110 | 110
8 | Haripur Power CCPP 360MW |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 344 | 259 | 360 | 360
9 | Meghnaghat CCPP 450MW |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 300 | 450 | 450
10 | Meghnaghat (IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 56 | 100 | 100
11 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 280 | 270 | 335 | 335 |  |  | FGMO
12 | Madanganj 102MW |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 64 | 100 | 100
13 | Madanganj-55 MW |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 55 | 55 | 55
14 | Keraniganj (Powerpac) 100MW |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 60 | 100 | 100
15 | Narshingdi (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 19 | 19 | 19
16 | Siddhirgonj ST 210MW |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 115 |  | Gas shortage
17 | Siddhirgonj GT Unit-1& 2 |  | Gas | EGCB | 2*105 | 210 | 210 | 185 | 76 | 80 | 80 | 130 |  | Gas shortage
| Siddhirganj Desh |  | HSD | QRPP | 96*1.2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
18 | Siddhirganj (Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 50 | 100 | 100
19 | Siddhirganj CCPP-335 MW |  | Gas | EGCB | 1*217 | 217 | 217 | 0 | 0 | 0 | 0 | 217 |  | Gas shortage
0 | Pagla (DPA ) |  | HSD | QRPP | 100*0.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
20 | Gagnagar (Orion) |  | HFO | IPP | 12*8.924 | 102 | 102 | 30 | 100 | 102 | 102
21 | Katpotti 51 MW |  | HFO | IPP | 7*7.9 | 51 | 51 | 46 | 30 | 48 | 48
22 | Banco Energy 54MW |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 35 | 54 | 54
23 | Kodda 149MW |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 149 | 149 | 149
24 | Northern 55 MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 36 | 56 | 55 | 55
25 | Southern 55MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 55 | 55
26 | Bosila 108MW |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 62 | 64 | 64 | 64 |  | 44 | Engine problem
27 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 50 | 47 | 50 | 50 |  | 30 | Engine problem
28 | Summit Maona |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 17 | 0 | 33 | 33
29 | Summit Rupganj |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
30 | Gazipur (RPCL) |  | HFO | IPP | 6*8.9 | 52 | 52 | 48 | 48 | 48 | 48
31 | Tongi GT |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
32 | Summit Gazipur -2 |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 140 | 300 | 300
33 | APR Energy , Keranigonj |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 300 | 300
34 | Bramhangoan 100 MW (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 100 | 100
35 | Aggreko Aurahati 100MW |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 100 | 100
36 | Summit Gazipur-1 150MW |  | HFO | IPP | 149 | 149 | 149 | 50 | 135 | 149 | 149
| Gazipur 100 MW |  | HFO | RPCL | 100 MW | 0 | 0 | 0 | 0 | 0 | 0
| Dhaka area Total |  |  |  |  | 5934 | 5698 | 2592 | 3300 | 4535 | 4591 | 637 | 264
37 | Chattogram ST-1 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chittgong ST-2 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 150 | 150 | 150 | 150 | 30 |  | Gas shortage
38 | Raozan 25 MW (RPCL) |  | HFO | IPP | 3*8.9 | 25 | 25 | 25 | 25 | 25 | 25
39 | Teknaf Solartech 20MW |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 17.4 | 0 | 20 | 0
40 | Patenga 50MW |  | HFO | IPP | 8*6.98 | 50 | 50 | 39 | 43 | 43 | 43
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 32 | 37 | 37 | 37 |  | 193 | Low water lavel
42 | Sikalbaha ST 60MW |  | Gas | PDB | 1*60 | 60 | 40 | 0 | 0 | 0 | 0 |  | 40 | Under S/D
43 | Sikalbaha 225MW |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 226 | 230 | 225 | 225
44 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 145 | 100 | 145 | 145
45 | Sikalbaha (Energis) |  | HFO | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 51 | 30 | 33 | 33 | 33 |  | 18 | Engine problem
46 | Hathazari peaking |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 85 | 76 | 76
47 | Dohazari Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 85 | 85 | 85
48 | Juldah (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 10 | 88 | 100 | 100
49 | Juldah 100 MW Unit-3 |  | HFO | IPP | 0 | 100 | 100 | 90 | 100 | 100 | 100
50 | Barabkunda (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 14 | 14 | 14 | 14
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 35 | 10 | 35
51 | Chattogram ECPV 108 MW |  | HFO | IPP | 16*7 | 108 | 108 | 90 | 103 | 100 | 100
| Chattogram area Total |  |  |  |  | 1761 | 1681 | 870.4 | 1128 | 1163 | 1168 | 210 | 251
52 | Ashuganj ST: Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
| Ashuganj ST: Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
| Ashuganj ST: Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
53 | Ashuganj CCPP 225 MW |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 198 | 185 | 221 | 221
54 | Ashuganj CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 240 | 180 | 260 | 260 |  | 100 | ST under maint
55 | Ashuganj CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 350 | 300 | 360 | 360
56 | Ashuganj Engines TSK |  | Gas | APSCL | 14*3.968 | 53 | 45 | 33 | 33 | 36 | 36 |  | 9 | Engine problem
57 | Ashuganj (Precision) 55MW |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 30 | 5 | 30 | 25 |  | Gas shortage
58 | Ashuganj (United) 53MW |  | Gas | QRPP | 14*4 | 53 | 53 | 5 | 5 | 5 | 5 | 48 |  | Gas Shortage
59 | Ashuganj 195MW Modular |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 63 | 63 | 63 | 63 | 132 |  | Gas shortage
60 | Ashuganj (Midland) 51MW |  | Gas | IPP | 6*9.34 | 51 | 51 | 15 | 45 | 45 | 45 |  | 6 | Engine problem
61 | Midland 150MW |  | HFO | IPP | 23*7.015 | 150 | 150 | 33 | 100 | 150 | 150
62 | B.Baria (Aggreko) 85MW |  | Gas | QRPP | 86*1.10 | 85 | 85 | 0 | 0 | 0 | 0 |  |  | Contract expired
63 | Daudkandi Peaking 52MW |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
64 | Chandpur CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 100 | 100 | 100 | 100
65 | Chandpur Desh 200MW |  | HFO | IPP | 0 | 200 | 200 | 35 | 200 | 200 | 200
66 | Feni (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 22 | 22
67 | Feni, Mohipal (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
** | Tripura |  |  | Imported power | 0 | 160 | 160 | 134 | 168 | 148 | 187
68 | Jangalia (Summit) 33MW |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
69 | Lakdhanvi 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 25 | 34 | 52 | 52
70 | Summit Cumilla 25MW |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 0 | 21 | 20 | 20
71 | Daudkandi bangla trak |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 200 | 200
| Cumilla Area Total |  |  |  |  | 2951 | 2891 | 1280 | 1508 | 1931 | 2045 | 603 | 115
72 | Mymensingh RPCL 210MW |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 149 | 152 | 150 | 150 | 52 |  | Gas shortage
73 | Tangail (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 0 | 22 | 22
74 | Jamalpur 95MW |  | HFO | IPP | 12*8.924 | 95 | 95 | 0 | 60 | 95 | 95
75 | Sarishabari (Solar) |  | Solar | IPP | 1*3 | 3 | 3 | 0.9 | 0 | 2 | 0
76 | United Mymensingh PPL |  | HFO | IPP | 200 | 200 | 200 | 0 | 7 | 200 | 200
77 | United Jamalpur PPL |  | HFO | IPP | 115 MW | 115 | 115 | 98 | 98 | 98 | 98 |  | 17 | Engine problem
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 267.9 | 317 | 567 | 565 | 52 | 0
78 | Fenchugonj CCPP-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 58 | 60 | 60 | 60
79 | Fenchugonj CCPP-2 |  | Gas | PDB | !F71 | 104 | 90 | 48 | 48 | 48 | 48
80 | Kushiara 163 MW CCPP GT |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 100 | 100 | 163
81 | Shajibazar 330 MW |  | Gas | PDB | 3*110 | 330 | 330 | 311 | 311 | 330 | 330 |  |  | FGMO
82 | Fenchugonj (Barakatullah) 51MW |  | Gas | RPP | 19*2.90 | 51 | 51 | 26 | 46 | 50 | 50
83 | Fenchuganj (EPL) 44MW |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 50 | 30 | 44 | 44
84 | Hobiganj 11MW |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 11 | 11 | 11
85 | Shahjibazar GT: Unit- 8, 9 |  | Gas | PDB | 2*35 | 70 | 66 | 63 | 63 | 66 | 66 |  |  | FGMO
86 | Shahjibazar 86MW |  | Gas | RPP | 32*2.90 | 86 | 86 | 30 | 84 | 86 | 86
87 | Shahjibazar (EPL) 50MW |  | Gas | RPP | 27*2.0 | 50 | 50 | 45 | 44 | 46 | 46
88 | Sylhet GT 150 MW |  | Gas | PDB | 1*142 | 142 | 142 | 75 | 75 | 130 | 130
89 | Sylhet GT 20 MW |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 19 | 19
90 | Sylhet (EPL) 50MW |  | Gas | RPP | 27*2 | 50 | 50 | 42 | 45 | 40 | 40 |  | 10 | Engine problem
91 | Shahjahanulla 25 MW |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 24 | 25 | 25
92 | Summit Bibiana- 2 |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 275 | 280 | 341 | 341 |  |  | FGMO
| Bibiyana-3 285 MW |  | Gas | PDB | 285 MW | 0 | 0 | 120 | 150 | 150 | 150 |  |  | On test
93 | Sylhet (Desh) 10MW |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1594 | 1549 | 1307 | 1381 | 1556 | 1619 | 0 | 10
94 | Bheramara GT-1,2,3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 32 | 0 | 32
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 930 | 931 | 943 | 943
| Khulna (KPCL-1 & 3) |  | HFO | IPP | 19*6.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
95 | Khulna (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 35 | 115 | 115 | 115
96 | Faridpur Peaking |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 25 | 35 | 35
97 | Khulna CCPP 225MW |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 |  |  | Reserve
98 | Gopalganj Peaking |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 63 | 50 | 80
99 | Bheramara 360 MW |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 |  | 410 | Under maint. |  | 28/05/2019
100 | Noapara (KZA) 40MW |  | HFO | QRPP | 5*8.5 | 40 | 40 | 32 | 40 | 40 | 40
0 | Khulna (Aggreeco) 55MW |  | HSD | QRPP | 71*0.85 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
101 | Bangla Trak Noapara |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 57 | 100 | 100
102 | Labon Chora 105 MW |  | HFO | IPP | 6*18.445 | 105 | 105 | 36 | 105 | 105 | 105
103 | Madhumati Power Plant |  | HFO | IPP | 100 MW | 105 | 105 | 72 | 107 | 108 | 108 |  |  | On Test
| Khulna Area Total |  |  |  |  | 2328 | 2314 | 1105 | 1475 | 1496 | 1558 | 0 | 410
104 | Summit Barisal 110 MW |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 110 | 110 | 110
105 | Barisal GT: Unit-1, 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 10 | 0 | 20
106 | Bhola (Venture) 33MW |  | Gas | RPP | 1*34.50 | 33 | 33 | 18 | 33 | 33 | 33
107 | Bhola CCPP 194MW |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 176 | 175 | 176 | 176
108 | Bhola Aggreko 95MW |  | Gas | QRPP | 96*1.10 | 95 | 95 | 94 | 96 | 95 | 95
| Barisal Area Total |  |  |  |  | 472 | 462 | 288 | 424 | 414 | 434 | 0 | 0
109 | Baghabari GT 71MW |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 55 | 60 | 60
| Baghabari GT 100MW |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0
110 | Baghabari Peaking 50MW |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 50 | 50
111 | Bera Peaking |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 27 | 35 | 35
112 | Amnura 50MW |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 50 | 50 | 50
113 | Katakhali (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 50 | 50 | 50
114 | Katakhali Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 42 | 44 | 44
115 | Sirajgonj Unit-1 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 202 | 175 | 200 | 200 |  |  | FGMO
116 | Sirajgonj Unit-2 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 177 | 152 | 200 | 200 |  |  | FGMO
117 | Sirajgonj Unit-3 225MW |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 179 | 162 | 220 | 220 |  |  | FGMO
118 | Sirajgonj Unit-4 414 MW(Gas) |  | Gas | SNWPGCL | 1*282+1*132 | 414 | 414 | 0 | 250 | 414 | 414
119 | Santahar Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 6 | 42 | 40 | 40
120 | Bogra (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
121 | Bogra (EPL) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 8 | 11 | 14 | 14
122 | Ullapara (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
123 | Rajlanka 52 MW |  | HFO | IPP | 52 | 52 | 52 | 10 | 50 | 52 | 52
124 | Chapainawabganj-100 MW |  | HFO | PDB | 104 | 104 | 104 | 0 | 93 | 95 | 95
125 | Paramount Baghabari |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
126 | Confidence CPBL-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 108 | 108 | 108
| Rajshahi Area Total |  |  |  |  | 2080 | 2070 | 609 | 1350 | 1865 | 1865 | 0 | 0
127 | Barapukuria Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under overhauling
| Barapukuria Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 65 | 65 | 67 | 67
128 | Barapukuria Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 199 | 199 | 199 | 199 | 75
129 | Rangpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 16 | 17 | 17
130 | Saidpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 16 | 18 | 18
| Rangpur Area Total |  |  |  |  | 564 | 484 | 264 | 296 | 301 | 301 | 75 | 85
| Total |  |  |  |  | 18329 | 17786 | 8583.3 | 11179 | 13828 | 14146 | 1577 | 1135
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 8281.5524 | 10786 | 13341.8739 | 13648.6945
A. |  | 2019-05-18 | (Yesterday) |  |  |  |  | Saturday
1 | Highest Generation : |  |  | 11179 | MW at | 19:30 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:30 | hrs.
2 | Minimum Generation : |  |  | 7004.5 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 11179 | MW
3 | Day peak Generation : |  |  | 8583.3 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 10786 | MW
4 | Evening peak Generation : |  |  | 11179 | MW at | 19:30 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 217.6441 | MKWHr | By Solar | 0.13457 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas: | 145.9872 | MKWHr |  | By Oil: | 38.9647 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal: | 6.4095 | MKWHr |  | By Hydro: | 0.73524 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1577 | MW | Dhaka | 4126 | 4126 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1135 | MW | Chittagong | 1088 | 1088 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 2712 | MW | Khulna | 1461 | 1461 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1333.09 | MMCFD |  |  | Rajshahi | 1067 | 1067 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 103485370.444 | ii) Oil : | Taka | 306104366.03 | Comilla | 1135 | 1135 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 28178764.52 | Total | Taka | 437768500.994 | Mymensingh | 502 | 502 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 1.73 | MKWHr. | Sylhet | 412 | 412 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -240 | MW (E to W) at | 19:30 | hrs | Barisal | 334 | 334 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -340 | MW at | 15:00 | hrs | Rangpur | 661 | 661 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 35.5° C |  |  | Total | 10786 | 10786 |  | 0
B. |  | 2019-05-19 | (Today) |  |  |  | Sunday |  |  | Probable max. temperature in Dhaka |  |  | 37.6° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 12000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 14146 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 9800 | MW
4 | Reserve(Generation end) |  |  |  | 2146 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 233.6282 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 8042.5 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 22.3178 | MKWHr. | ii) HVDC Flow at Peak Time |  | 931 | MW at | 19:30 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.095 | MKWHr. | iii) Maximum HVDC Flow : |  | 939 | MW at | 1:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 72.95 |  | (b) Today: | 72.85 |  | (c) Rule Curve: |  | 78.58
.
** Wapda control unable to give gas reading.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2019-05-18
Plant Name | Ghorasal ST: Unit-1,2 | Ghorasal GT: Unit-3 | Ghorasal GT: Unit-4 | Ghorasal ST: Unit-5 | Ghorasal ST: Unit-7 | Ghorashal (Regent) | Ghorashal 78MW (MAX) | Haripur 412 MW CCPP | Haripur Power CCPP 360MW | Haripur NEPC 110MW | Haripur GT: Unit-1, 2 | Meghnaghat CCPP 450MW | Meghnaghat CCPP(Summit) | Meghnaghat (IEL) | Madanganj 102MW | Madanganj-55 MW | Siddhirganj CCPP-335 MW | Siddhirgonj ST 210MW | Siddhirgonj GT Unit-1& 2 | Siddhirganj Desh | Siddhirganj (Dutch Bangla) | Gagnagar (Orion) | Kodda 149MW | Keraniganj (Powerpac) 100MW | Bosila 108MW | Pagla (DPA ) | Katpotti 51 MW | Banco Energy 54MW | Northern 55 MW | Southern 55MW | Narshingdi (Doreen) | Summit Ashulia | Summit Madhabdi | Summit Maona | Summit Rupganj | Gazipur (RPCL) | Tongi GT | Kaptai Unit-1, 2 & 3 | Kaptai Unit-4 & 5 | Chattogram ST-1 (Raozan) | Chittgong ST-2 (Raozan) | Raozan 25 MW (RPCL) | Sikalbaha 225MW (Gas) | Sikalbaha 225MW (Oil) | Sikalbaha GT 150MW (Gas) | Sikalbaha GT 150MW (Oil) | Sikalbaha ST 60MW | Sikalbaha (Energis) | Hathazari peaking | Dohazari Peaking | Juldah (Acorn) | Chattogram ECPV 108 MW | Patenga 50MW | Barabkunda (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj ST: Unit- 3 | Ashuganj ST: Unit- 4 | Ashuganj ST: Unit- 5 | Ashuganj CCPP(North) | Ashuganj CCPP(South) | Ashuganj CCPP 225 MW | Ashuganj 195MW Modular | Chandpur CCPP | Ashuganj Engines TSK | Ashuganj (Precision) 55MW | Ashuganj (United) 53MW | Ashuganj (Midland) 51MW | B.Baria (Aggreko) 85MW | Daudkandi Peaking 52MW | Lakdhanvi 52 MW | Feni (Doreen) 22MW | Feni, Mohipal (Doreen) | Jangalia (Summit) 33MW | Summit Cumilla 25MW | Tripura | Mymensingh RPCL 210MW | Jamalpur 95MW | Tangail (Doreen) 22MW | Sarishabari (Solar) | Fenchugonj CCPP-1 | Fenchugonj CCPP-2 | Fenchugonj (Barakatullah) 51MW | Fenchuganj (EPL) 44MW | Kushiara 163 MW CCPP GT | Shajibazar 330 MW | Shahjibazar GT: Unit- 8, 9 | Shahjibazar 86MW | Shahjibazar (EPL) 50MW | Sylhet GT 150 MW | Sylhet GT 20 MW | Sylhet (EPL) 50MW | Sylhet (Desh) 10MW | Summit Bibiana- 2 | Shahjahanulla 25 MW | Hobiganj 11MW | Daudkandi bangla trak | Summit Gazipur -2 | APR Energy , Keranigonj | Bramhangoan 100 MW (Aggreko) | United Mymensingh PPL | Aggreko Aurahati 100MW | Summit Gazipur-1 150MW | Teknaf Solartech 20MW | Juldah 100 MW Unit-3 | Chandpur Desh 200MW | Midland 150MW | Bibiyana-3 285 MW | United Jamalpur PPL | Gazipur 100 MW | Baraka Sikalbaha PL | EasternBlank | Bheramara (HVDC ) | Bheramara GT-1,2,3 | Bheramara 360 MW | Khulna (KPCL-1 & 3) | Khulna (KPCL-2) | Khulna CCPP 225MW | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur Peaking | Gopalganj Peaking | Noapara (KZA) 40MW | Bhola CCPP 194MW | Bhola (Venture) 33MW | Summit Barisal 110 MW | Barisal GT: Unit-1, 2 | Baghabari GT 100MW | Baghabari GT 71MW | Baghabari Peaking 50MW | Bera Peaking | Chapainawabganj-100 MW | Amnura 50MW | Katakhali (Northern) | Katakhali Peaking | Rajlanka 52 MW | Santahar Peaking | Bogra (GBB) | Bogra (EPL) | Ullapara (Summit) | Barapukuria Unit-1 | Barapukuria Unit-2 | Barapukuria Unit-3 | Rangpur GT | Saidpur GT | Sirajgonj Unit-1 225MW (Gas) | Sirajgonj Unit-1 225MW (Oil) | Sirajgonj Unit-2 225MW (Gas) | Sirajgonj Unit-2 225MW (Oil) | Bhola Aggreko 95MW | Bangla Trak Noapara | Sirajgonj Unit-3 225 MW(Gas) | Sirajgonj Unit-3 225 MW(Oil) | Sirajgonj Unit-4 414 MW(Gas) | Labon Chora 105 MW | Paramount Baghabari | Confidence CPBL-2 | Madhumati Power Plant | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 74 | 0 | 0 | 0 | 250 | 42 | 60 | 325 | 280 | 0 | 0 | 350 | 252 | 0 | 0 | 0 | 0 | 0 | 125 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 48 | 0 | 18 | 17 | 19 | 25 | 26 | 16 | 30 | 0 | 0 | 32 | 0 | 0 | 150 | 25 | 203 | 0 | 90 | 0 | 0 | 32 | 0 | 0 | 78 | 71 | 43 | 14 | 34 | 0 | 0 | 0 | 260 | 300 | 183 | 63 | 100 | 36 | 5 | 5 | 45 | 0 | 0 | 0 | 22 | 0 | 33 | 0 | 102 | 155 | 8 | 17 | 0 | 60 | 48 | 47 | 50 | 130 | 313 | 66 | 50 | 46 | 110 | 19 | 43 | 10 | 255 | 24 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 100 | 34 | 50 | 119 | 50 | 0 | 0 |  | 939 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 22 | 8 | 32 | 177 | 38 | 80 | 0 | 105 | 60 | 0 | 0 | 47 | 24 | 0 | 0 | 0 | 0 | 22 | 8 | 0 | 0 | 67 | 199 | 0 | 0 | 180 | 0 | 184 | 0 | 97 | 60 | 186 | 0 | 0 | 70 | 0 | 54 | 108 |  | 5756 | 2882 | 8638 | 4115 | 939 | 1680 | 1427 | 266 | 32 | 77 | 102 | 0 | 0 | 73
2:00 | 74 | 0 | 0 | 0 | 250 | 42 | 77 | 325 | 280 | 0 | 0 | 350 | 265 | 0 | 0 | 0 | 0 | 0 | 125 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 48 | 0 | 18 | 17 | 0 | 25 | 26 | 16 | 30 | 0 | 0 | 32 | 0 | 0 | 150 | 8 | 203 | 0 | 90 | 0 | 0 | 32 | 0 | 0 | 10 | 18 | 46 | 14 | 42 | 0 | 0 | 0 | 260 | 300 | 183 | 63 | 100 | 36 | 5 | 5 | 45 | 0 | 0 | 0 | 22 | 11 | 33 | 0 | 102 | 152 | 8 | 17 | 0 | 60 | 48 | 47 | 50 | 130 | 312 | 65 | 47 | 46 | 110 | 19 | 43 | 10 | 255 | 24 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 100 | 34 | 12 | 119 | 50 | 0 | 0 |  | 928 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 9 | 0 | 32 | 177 | 38 | 32 | 0 | 102 | 60 | 0 | 0 | 47 | 24 | 0 | 0 | 0 | 0 | 22 | 8 | 0 | 0 | 67 | 199 | 0 | 0 | 181 | 0 | 185 | 0 | 96 | 60 | 186 | 0 | 0 | 70 | 0 | 54 | 108 |  | 5605 | 2800 | 8405 | 4101 | 928 | 1701 | 1219 | 266 | 32 | 56 | 102 | 0 | 0 | 72.99
3:00 | 74 | 0 | 0 | 0 | 250 | 42 | 76 | 326 | 280 | 0 | 0 | 350 | 280 | 0 | 0 | 0 | 0 | 0 | 125 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 48 | 0 | 18 | 17 | 0 | 25 | 18 | 16 | 30 | 0 | 0 | 32 | 0 | 0 | 150 | 8 | 203 | 0 | 90 | 0 | 0 | 32 | 0 | 0 | 10 | 18 | 47 | 14 | 42 | 0 | 0 | 0 | 260 | 300 | 190 | 63 | 100 | 33 | 5 | 5 | 45 | 0 | 0 | 0 | 22 | 11 | 33 | 0 | 110 | 153 | 8 | 17 | 0 | 60 | 48 | 47 | 50 | 130 | 317 | 66 | 50 | 46 | 120 | 19 | 43 | 10 | 275 | 22 | 3 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 100 | 34 | 12 | 119 | 50 | 0 | 0 |  | 929 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 9 | 0 | 32 | 177 | 38 | 32 | 0 | 102 | 60 | 0 | 0 | 47 | 24 | 0 | 0 | 0 | 0 | 22 | 9 | 0 | 0 | 67 | 199 | 0 | 0 | 184 | 0 | 188 | 0 | 96 | 60 | 190 | 0 | 0 | 70 | 0 | 54 | 108 |  | 5655 | 2812 | 8467 | 4115 | 929 | 1724 | 1235 | 266 | 32 | 56 | 110 | 0 | 0 | 72.98
4:00 | 74 | 0 | 0 | 0 | 250 | 42 | 76 | 348 | 280 | 0 | 0 | 350 | 285 | 0 | 0 | 0 | 0 | 0 | 125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 18 | 17 | 0 | 25 | 22 | 16 | 30 | 0 | 0 | 32 | 0 | 0 | 150 | 8 | 203 | 0 | 90 | 0 | 0 | 32 | 0 | 0 | 10 | 18 | 46 | 14 | 42 | 0 | 0 | 0 | 260 | 300 | 198 | 63 | 100 | 30 | 5 | 5 | 45 | 0 | 0 | 0 | 22 | 11 | 33 | 0 | 98 | 152 | 0 | 17 | 0 | 60 | 48 | 47 | 50 | 130 | 313 | 66 | 50 | 46 | 120 | 19 | 43 | 10 | 285 | 22 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 20 | 0 | 120 | 50 | 0 | 0 |  | 929 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 9 | 0 | 32 | 177 | 38 | 16 | 0 | 102 | 60 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 22 | 10 | 0 | 0 | 67 | 199 | 0 | 0 | 198 | 0 | 200 | 0 | 97 | 60 | 204 | 0 | 0 | 70 | 0 | 0 | 108 |  | 5592 | 2760 | 8352 | 4182 | 929 | 1736 | 1053 | 266 | 32 | 56 | 98 | 0 | 0 | 72.97
5:00 | 74 | 0 | 0 | 0 | 250 | 12 | 40 | 326 | 280 | 0 | 0 | 350 | 267 | 0 | 0 | 0 | 0 | 0 | 125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 18 | 17 | 19 | 25 | 22 | 16 | 29 | 0 | 0 | 32 | 0 | 0 | 150 | 8 | 203 | 0 | 90 | 0 | 0 | 32 | 0 | 0 | 10 | 18 | 46 | 14 | 42 | 0 | 0 | 0 | 220 | 300 | 183 | 63 | 100 | 30 | 5 | 5 | 45 | 0 | 0 | 0 | 22 | 11 | 33 | 0 | 94 | 153 | 0 | 17 | 0 | 60 | 48 | 11 | 10 | 130 | 312 | 66 | 10 | 10 | 75 | 0 | 12 | 10 | 250 | 22 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 70 | 8 | 0 | 0 |  | 929 | 0 | 0 | 0 | 112 | 0 | 0 | 0 | 0 | 0 | 32 | 177 | 34 | 0 | 0 | 103 | 60 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 4 | 10 | 3 | 0 | 67 | 199 | 0 | 0 | 182 | 0 | 186 | 0 | 95 | 0 | 188 | 0 | 0 | 53 | 0 | 0 | 81 |  | 5026 | 2562 | 7588 | 3972 | 929 | 1428 | 820 | 266 | 32 | 47 | 94 | 0 | 0 | 72.96
6:00 | 74 | 0 | 0 | 0 | 250 | 12 | 40 | 326 | 280 | 0 | 0 | 320 | 280 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 18 | 17 | 19 | 25 | 22 | 16 | 29 | 0 | 0 | 32 | 0 | 0 | 150 | 8 | 203 | 0 | 90 | 0 | 0 | 32 | 0 | 0 | 10 | 12 | 43 | 14 | 38 | 0 | 0 | 0 | 200 | 270 | 158 | 63 | 100 | 30 | 5 | 5 | 45 | 0 | 0 | 0 | 22 | 11 | 33 | 0 | 90 | 152 | 0 | 17 | 0 | 60 | 48 | 11 | 10 | 130 | 289 | 66 | 10 | 10 | 75 | 0 | 12 | 10 | 255 | 22 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 70 | 0 | 0 | 69 | 8 | 0 | 0 |  | 930 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 16 | 177 | 29 | 0 | 0 | 103 | 60 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 4 | 10 | 3 | 0 | 67 | 199 | 0 | 0 | 156 | 0 | 147 | 0 | 96 | 0 | 164 | 0 | 0 | 17 | 0 | 0 | 35 |  | 4842.6 | 2268 | 7110.6 | 3758 | 930 | 1395 | 616 | 266 | 32 | 23 | 90 | 0.6 | 0 | 72.95
7:00 | 74 | 0 | 0 | 0 | 250 | 12 | 40 | 336 | 280 | 0 | 0 | 320 | 290 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 18 | 17 | 19 | 25 | 22 | 16 | 29 | 2 | 0 | 32 | 0 | 0 | 150 | 0 | 205 | 0 | 130 | 0 | 0 | 32 | 0 | 0 | 10 | 12 | 6 | 13 | 19 | 0 | 0 | 0 | 200 | 270 | 172 | 63 | 100 | 30 | 5 | 5 | 10 | 0 | 0 | 0 | 22 | 11 | 33 | 0 | 90 | 151 | 0 | 17 | 0.1 | 60 | 48 | 11 | 10 | 100 | 290 | 66 | 10 | 10 | 76 | 0 | 12 | 10 | 280 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4 | 50 | 0 | 0 | 70 | 8 | 0 | 0 |  | 930 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 177 | 26 | 0 | 0 | 102 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 10 | 3 | 0 | 65 | 199 | 0 | 0 | 166 | 0 | 157 | 0 | 96 | 0 | 165 | 0 | 0 | 17 | 0 | 0 | 17 |  | 4786.5 | 2218 | 7004.5 | 3831 | 930 | 1333 | 521 | 264 | 32 | 0 | 90 | 3.5 | 0 | 72.94
8:00 | 74 | 0 | 0 | 0 | 330 | 12 | 40 | 350 | 280 | 0 | 0 | 320 | 290 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 18 | 17 | 19 | 25 | 22 | 16 | 29 | 24 | 0 | 32 | 0 | 0 | 150 | 0 | 231 | 0 | 140 | 0 | 0 | 32 | 0 | 0 | 10 | 12 | 5 | 13 | 12 | 0 | 0 | 0 | 250 | 270 | 201 | 63 | 100 | 30 | 5 | 5 | 10 | 0 | 0 | 0 | 22 | 0 | 33 | 0 | 100 | 150 | 0 | 17 | 0.7 | 60 | 48 | 11 | 10 | 100 | 315 | 66 | 10 | 10 | 80 | 0 | 12 | 10 | 285 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 3.7 | 65 | 0 | 0 | 71 | 8 | 0 | 0 |  | 930 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 177 | 25 | 0 | 0 | 102 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | 3 | 0 | 65 | 199 | 0 | 0 | 173 | 0 | 170 | 0 | 95 | 0 | 172 | 0 | 0 | 17 | 0 | 0 | 18 |  | 5071.4 | 2242 | 7313.4 | 4090 | 930 | 1327 | 566 | 264 | 32 | 0 | 100 | 4.4 | 0 | 72.94
9:00 | 74 | 0 | 0 | 0 | 330 | 12 | 40 | 350 | 305 | 0 | 0 | 350 | 290 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 18 | 17 | 19 | 25 | 22 | 16 | 29 | 24 | 0 | 32 | 0 | 0 | 150 | 0 | 229 | 0 | 143 | 0 | 0 | 32 | 0 | 0 | 10 | 43 | 25 | 14 | 3 | 0 | 0 | 0 | 250 | 300 | 199 | 63 | 100 | 30 | 5 | 5 | 10 | 0 | 0 | 0 | 0 | 11 | 33 | 0 | 108 | 152 | 0 | 17 | 0.5 | 60 | 48 | 11 | 10 | 100 | 325 | 64 | 10 | 10 | 82 | 0 | 12 | 10 | 280 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 16 | 80 | 0 | 0 | 71 | 8 | 0 | 0 |  | 930 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 177 | 19 | 0 | 0 | 102 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | 3 | 0 | 64 | 199 | 0 | 0 | 174 | 0 | 177 | 0 | 96 | 0 | 175 | 0 | 0 | 17 | 0 | 0 | 17 |  | 5241.5 | 2246 | 7487.5 | 4135 | 930 | 1363 | 640 | 263 | 32 | 0 | 108 | 16.5 | 0 | 0
10:00 | 74 | 0 | 0 | 0 | 340 | 52 | 40 | 358 | 352 | 0 | 0 | 400 | 300 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 18 | 0 | 18 | 17 | 19 | 25 | 22 | 16 | 12 | 24 | 0 | 33 | 0 | 0 | 150 | 5 | 225 | 0 | 146 | 0 | 0 | 32 | 0 | 0 | 10 | 73 | 38 | 14 | 2 | 0 | 0 | 0 | 250 | 353 | 203 | 63 | 100 | 27 | 5 | 5 | 10 | 0 | 0 | 0 | 0 | 11 | 33 | 0 | 108 | 151 | 0 | 17 | 0.9 | 57 | 48 | 11 | 10 | 130 | 315 | 64 | 10 | 44 | 87 | 0 | 12 | 10 | 270 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 15.5 | 80 | 0 | 0 | 120 | 24 | 0 | 0 |  | 930 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 177 | 20 | 0 | 0 | 101 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | 3 | 0 | 64 | 199 | 0 | 0 | 177 | 0 | 169 | 0 | 93 | 0 | 203 | 0 | 0 | 17 | 0 | 0 | 18 |  | 5653.4 | 2267 | 7920.4 | 4301 | 930 | 1551 | 718 | 263 | 33 | 0 | 108 | 16.4 | 0 | 0
11:00 | 74 | 0 | 0 | 0 | 380 | 51 | 40 | 342 | 345 | 0 | 0 | 400 | 285 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 16 | 0 | 0 | 51 | 0 | 37 | 0 | 18 | 17 | 19 | 25 | 22 | 17 | 29 | 37 | 0 | 33 | 0 | 0 | 150 | 25 | 230 | 0 | 145 | 0 | 0 | 32 | 0 | 0 | 10 | 92 | 39 | 14 | 3 | 0 | 0 | 0 | 250 | 353 | 185 | 63 | 100 | 30 | 5 | 5 | 10 | 0 | 0 | 4 | 0 | 0 | 33 | 6 | 128 | 151 | 0 | 20 | 2 | 58 | 48 | 11 | 20 | 130 | 310 | 64 | 10 | 44 | 74 | 0 | 41 | 10 | 260 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 15.8 | 90 | 18 | 3 | 120 | 98 | 0 | 0 |  | 930 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 176 | 21 | 0 | 0 | 100 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | 5 | 0 | 65 | 199 | 0 | 0 | 195 | 0 | 166 | 0 | 93 | 0 | 180 | 0 | 0 | 17 | 0 | 0 | 17 |  | 5957.8 | 2260 | 8217.8 | 4305 | 930 | 1574 | 966 | 264 | 33 | 0 | 128 | 17.8 | 0 | 0
12:00 | 74 | 0 | 0 | 0 | 370 | 85 | 50 | 347 | 344 | 0 | 0 | 450 | 280 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 30 | 0 | 0 | 62 | 0 | 46 | 0 | 36 | 35 | 0 | 25 | 25 | 17 | 33 | 48 | 0 | 32 | 0 | 0 | 150 | 25 | 226 | 0 | 145 | 0 | 0 | 30 | 0 | 0 | 10 | 90 | 39 | 14 | 2 | 0 | 0 | 0 | 240 | 350 | 198 | 63 | 100 | 33 | 5 | 5 | 15 | 0 | 0 | 25 | 0 | 11 | 33 | 0 | 134 | 149 | 0 | 20 | 0.9 | 58 | 48 | 26 | 50 | 130 | 311 | 63 | 30 | 45 | 75 | 0 | 42 | 10 | 275 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 17.4 | 90 | 35 | 33 | 120 | 98 | 0 | 0 |  | 930 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 32 | 176 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 6 | 22 | 8 | 5 | 0 | 65 | 199 | 0 | 0 | 202 | 0 | 177 | 0 | 94 | 0 | 179 | 0 | 0 | 36 | 0 | 0 | 72 |  | 6317.3 | 2266 | 8583.3 | 4183 | 930 | 1769 | 1247 | 264 | 32 | 6 | 134 | 18.3 | 0 | 0
13:00 | 74 | 0 | 100 | 0 | 370 | 100 | 70 | 340 | 343 | 0 | 0 | 450 | 275 | 0 | 0 | 0 | 0 | 0 | 189 | 0 | 0 | 50 | 0 | 0 | 61 | 0 | 47 | 0 | 36 | 35 | 0 | 25 | 23 | 33 | 33 | 48 | 0 | 32 | 0 | 0 | 150 | 25 | 230 | 0 | 145 | 0 | 0 | 16 | 0 | 0 | 10 | 90 | 42 | 13 | 12 | 0 | 0 | 0 | 240 | 345 | 194 | 63 | 100 | 33 | 5 | 5 | 33 | 0 | 0 | 43 | 0 | 11 | 33 | 2 | 138 | 149 | 0 | 17 | 0.8 | 60 | 48 | 50 | 50 | 163 | 318 | 63 | 50 | 45 | 90 | 0 | 41 | 10 | 275 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 17.1 | 100 | 70 | 70 | 120 | 100 | 0 | 0 |  | 930 | 0 | 0 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 32 | 176 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 24 | 0 | 0 | 24 | 6 | 22 | 9 | 5 | 0 | 64 | 199 | 0 | 0 | 197 | 0 | 166 | 0 | 94 | 0 | 180 | 0 | 0 | 72 | 0 | 0 | 107 |  | 6692.9 | 2420 | 9112.9 | 4296 | 930 | 1914 | 1493 | 263 | 32 | 29 | 138 | 17.9 | 0 | 0
14:00 | 74 | 0 | 141 | 0 | 340 | 101 | 69 | 366 | 339 | 0 | 0 | 450 | 285 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 60 | 0 | 0 | 59 | 0 | 48 | 10 | 56 | 50 | 10 | 25 | 23 | 33 | 33 | 48 | 0 | 32 | 0 | 0 | 150 | 25 | 227 | 0 | 145 | 0 | 0 | 16 | 0 | 0 | 50 | 97 | 45 | 14 | 6 | 0 | 0 | 0 | 240 | 345 | 190 | 63 | 100 | 33 | 5 | 5 | 45 | 0 | 0 | 52 | 0 | 11 | 33 | 8 | 142 | 149 | 0 | 17 | 1.6 | 52 | 48 | 50 | 50 | 163 | 316 | 61 | 84 | 45 | 85 | 0 | 40 | 10 | 290 | 24 | 0 | 0 | 0 | 75 | 0 | 0 | 50 | 66 | 15.8 | 100 | 80 | 90 | 120 | 100 | 0 | 0 |  | 930 | 0 | 0 | 0 | 95 | 0 | 0 | 0 | 0 | 0 | 32 | 176 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | 23 | 24 | 0 | 0 | 29 | 6 | 22 | 11 | 0 | 0 | 64 | 199 | 0 | 0 | 198 | 0 | 176 | 0 | 92 | 7 | 179 | 0 | 0 | 54 | 0 | 0 | 90 |  | 7068.4 | 2447 | 9515.4 | 4329 | 930 | 1964 | 1809 | 263 | 32 | 29 | 142 | 17.4 | 0 | 0
15:00 | 74 | 0 | 140 | 0 | 300 | 101 | 68 | 335 | 339 | 0 | 0 | 450 | 265 | 50 | 0 | 0 | 0 | 0 | 142 | 0 | 0 | 85 | 82 | 0 | 60 | 0 | 47 | 35 | 56 | 55 | 19 | 25 | 23 | 33 | 33 | 0 | 0 | 30 | 0 | 0 | 150 | 25 | 231 | 0 | 135 | 0 | 0 | 16 | 0 | 0 | 88 | 96 | 38 | 13 | 3 | 0 | 0 | 0 | 240 | 345 | 184 | 63 | 100 | 33 | 30 | 5 | 45 | 0 | 0 | 52 | 0 | 11 | 33 | 15 | 162 | 149 | 37 | 17 | 1.7 | 51 | 48 | 50 | 50 | 100 | 310 | 50 | 84 | 45 | 73 | 0 | 40 | 10 | 265 | 24 | 2 | 0 | 0 | 0 | 0 | 7 | 0 | 72 | 12.3 | 100 | 140 | 135 | 299 | 100 | 0 | 0 |  | 930 | 0 | 0 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 32 | 176 | 26 | 48 | 0 | 0 | 0 | 0 | 0 | 23 | 40 | 0 | 0 | 48 | 7 | 22 | 11 | 5 | 0 | 64 | 199 | 0 | 0 | 190 | 0 | 154 | 0 | 93 | 0 | 160 | 0 | 53 | 72 | 0 | 95 | 105 |  | 7232 | 2652 | 9884 | 4322 | 930 | 1953 | 2098 | 263 | 30 | 112 | 162 | 14 | 0 | 0
16:00 | 74 | 34 | 140 | 0 | 260 | 104 | 68 | 327 | 289 | 0 | 0 | 340 | 263 | 100 | 0 | 13 | 0 | 0 | 139 | 0 | 0 | 100 | 80 | 0 | 59 | 0 | 47 | 35 | 56 | 55 | 19 | 25 | 26 | 33 | 33 | 9 | 0 | 30 | 0 | 0 | 150 | 25 | 232 | 0 | 100 | 0 | 0 | 16 | 0 | 0 | 88 | 97 | 37 | 11 | 7 | 0 | 0 | 0 | 240 | 350 | 184 | 63 | 100 | 33 | 30 | 5 | 45 | 0 | 4 | 8 | 0 | 11 | 33 | 20 | 158 | 150 | 50 | 17 | 1 | 54 | 48 | 50 | 50 | 100 | 312 | 62 | 85 | 46 | 73 | 0 | 42 | 10 | 250 | 24 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 100 | 7.5 | 100 | 180 | 100 | 299 | 100 | 0 | 0 |  | 931 | 0 | 0 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 24 | 175 | 23 | 48 | 0 | 0 | 50 | 0 | 0 | 30 | 50 | 0 | 0 | 16 | 6 | 22 | 11 | 5 | 0 | 64 | 200 | 0 | 0 | 184 | 0 | 146 | 0 | 94 | 0 | 154 | 0 | 146 | 90 | 0 | 108 | 90 |  | 7130.5 | 2766 | 9896.5 | 4335 | 931 | 1880 | 2170 | 264 | 30 | 120 | 158 | 8.5 | 0 | 0
17:00 | 74 | 43 | 140 | 0 | 260 | 106 | 68 | 349 | 289 | 0 | 0 | 340 | 285 | 56 | 0 | 15 | 0 | 0 | 100 | 0 | 0 | 100 | 80 | 0 | 60 | 0 | 24 | 35 | 56 | 55 | 0 | 25 | 26 | 33 | 33 | 48 | 0 | 30 | 0 | 0 | 150 | 0 | 228 | 0 | 100 | 0 | 0 | 16 | 0 | 0 | 40 | 103 | 46 | 11 | 8 | 0 | 0 | 0 | 240 | 342 | 191 | 63 | 100 | 33 | 30 | 5 | 45 | 0 | 8 | 8 | 0 | 11 | 33 | 15 | 148 | 149 | 28 | 17 | 0.5 | 54 | 48 | 48 | 50 | 100 | 313 | 61 | 85 | 46 | 82 | 0 | 44 | 10 | 280 | 24 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 102 | 3.2 | 100 | 200 | 50 | 296 | 50 | 0 | 0 |  | 930 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 5 | 16 | 8 | 175 | 24 | 48 | 0 | 0 | 50 | 0 | 0 | 30 | 24 | 0 | 0 | 8 | 7 | 22 | 11 | 8 | 0 | 64 | 200 | 0 | 0 | 195 | 0 | 159 | 0 | 96 | 0 | 167 | 0 | 200 | 53 | 0 | 50 | 53 |  | 6959.7 | 2652 | 9611.7 | 4343 | 930 | 1970 | 1777 | 264 | 30 | 146 | 148 | 3.7 | 0 | 0
18:00 | 74 | 43 | 140 | 0 | 260 | 106 | 69 | 334 | 289 | 0 | 0 | 340 | 290 | 56 | 3 | 15 | 0 | 0 | 100 | 0 | 0 | 100 | 80 | 0 | 62 | 0 | 24 | 35 | 56 | 55 | 0 | 25 | 23 | 33 | 33 | 48 | 0 | 36 | 0 | 0 | 150 | 25 | 229 | 0 | 101 | 0 | 0 | 22 | 3 | 0 | 40 | 103 | 46 | 13 | 24 | 0 | 0 | 0 | 240 | 345 | 198 | 63 | 100 | 33 | 30 | 5 | 45 | 0 | 8 | 8 | 0 | 0 | 33 | 15 | 152 | 150 | 28 | 17 | 0 | 54 | 48 | 22 | 0 | 100 | 316 | 61 | 0 | 10 | 82 | 0 | 12 | 10 | 290 | 24 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 100 | 0 | 100 | 200 | 50 | 200 | 50 | 0 | 0 |  | 932 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 19 | 34 | 8 | 175 | 21 | 48 | 0 | 0 | 55 | 0 | 5 | 30 | 24 | 0 | 0 | 8 | 7 | 22 | 11 | 11 | 0 | 63 | 199 | 0 | 0 | 195 | 0 | 156 | 0 | 96 | 0 | 165 | 0 | 200 | 53 | 0 | 50 | 53 |  | 6702 | 2689 | 9391 | 4242 | 932 | 1765 | 1816 | 262 | 36 | 186 | 152 | 0 | 0 | 0
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 74 | 140 | 140 | 0 | 260 | 106 | 69 | 342 | 259 | 55 | 0 | 300 | 272 | 56 | 48 | 32 | 0 | 0 | 76 | 0 | 20 | 100 | 140 | 35 | 61 | 0 | 30 | 35 | 56 | 55 | 19 | 25 | 14 | 33 | 33 | 48 | 0 | 37 | 0 | 0 | 150 | 25 | 231 | 0 | 100 | 0 | 0 | 33 | 85 | 25 | 88 | 103 | 46 | 14 | 34 | 0 | 0 | 0 | 180 | 300 | 184 | 63 | 100 | 33 | 30 | 5 | 45 | 0 | 8 | 16 | 0 | 11 | 33 | 20 | 182 | 150 | 42 | 0 | 0 | 60 | 48 | 17 | 10 | 100 | 313 | 63 | 10 | 10 | 73 | 0 | 38 | 10 | 240 | 24 | 11 | 0 | 60 | 0 | 0 | 7 | 0 | 125 | 0 | 100 | 200 | 90 | 150 | 70 | 0 | 0 |  | 931 | 32 | 0 | 0 | 115 | 0 | 0 | 0 | 25 | 48 | 40 | 176 | 31 | 110 | 0 | 0 | 55 | 50 | 17 | 90 | 50 | 25 | 30 | 42 | 36 | 22 | 11 | 11 | 0 | 65 | 199 | 16 | 16 | 186 | 0 | 153 | 0 | 96 | 2 | 161 | 0 | 250 | 105 | 0 | 70 | 53 |  | 7135 | 3319 | 10454 | 4146 | 931 | 1756 | 2520 | 264 | 37 | 618 | 182 | 0 | 0 | 0
19:30 | 74 | 145 | 140 | 0 | 260 | 106 | 69 | 350 | 259 | 55 | 0 | 300 | 270 | 56 | 64 | 55 | 0 | 0 | 76 | 0 | 50 | 100 | 149 | 60 | 64 | 0 | 30 | 35 | 56 | 55 | 19 | 25 | 22 | 0 | 33 | 48 | 0 | 37 | 0 | 0 | 150 | 25 | 230 | 0 | 100 | 0 | 0 | 33 | 85 | 85 | 88 | 103 | 43 | 14 | 35 | 0 | 0 | 0 | 180 | 300 | 185 | 63 | 100 | 33 | 30 | 5 | 45 | 0 | 0 | 34 | 0 | 11 | 33 | 21 | 168 | 152 | 60 | 0 | 0 | 60 | 48 | 46 | 30 | 100 | 311 | 63 | 84 | 44 | 75 | 0 | 45 | 10 | 280 | 24 | 11 | 0 | 140 | 0 | 0 | 7 | 0 | 135 | 0 | 100 | 200 | 100 | 150 | 98 | 0 | 0 |  | 931 | 32 | 0 | 0 | 115 | 0 | 0 | 0 | 25 | 63 | 40 | 175 | 33 | 110 | 10 | 0 | 55 | 50 | 27 | 93 | 50 | 50 | 42 | 50 | 42 | 22 | 11 | 11 | 0 | 65 | 199 | 16 | 16 | 175 | 0 | 152 | 0 | 96 | 57 | 162 | 0 | 250 | 105 | 0 | 108 | 107 |  | 7634 | 3545 | 11179 | 4125 | 931 | 1963 | 2956 | 264 | 37 | 735 | 168 | 0 | 0 | 0
20:00 | 74 | 189 | 140 | 0 | 260 | 107 | 70 | 330 | 258 | 13 | 0 | 300 | 260 | 50 | 55 | 55 | 0 | 0 | 74 | 0 | 30 | 50 | 98 | 50 | 64 | 0 | 47 | 35 | 56 | 55 | 19 | 25 | 24 | 0 | 33 | 48 | 0 | 38 | 0 | 0 | 150 | 25 | 229 | 0 | 100 | 0 | 0 | 33 | 85 | 85 | 100 | 103 | 43 | 14 | 35 | 0 | 0 | 0 | 180 | 300 | 184 | 63 | 100 | 33 | 30 | 5 | 45 | 0 | 0 | 34 | 0 | 11 | 33 | 21 | 166 | 152 | 50 | 0 | 0 | 60 | 48 | 52 | 32 | 100 | 312 | 40 | 86 | 46 | 73 | 0 | 45 | 10 | 235 | 24 | 11 | 0 | 120 | 0 | 0 | 7 | 0 | 125 | 0 | 100 | 200 | 100 | 151 | 100 | 0 | 0 |  | 930 | 48 | 0 | 0 | 115 | 0 | 0 | 0 | 25 | 52 | 40 | 175 | 32 | 110 | 12 | 0 | 55 | 50 | 26 | 91 | 40 | 50 | 47 | 52 | 42 | 22 | 11 | 11 | 0 | 65 | 199 | 16 | 16 | 180 | 0 | 147 | 0 | 97 | 77 | 156 | 0 | 250 | 105 | 0 | 108 | 106 |  | 7393 | 3558 | 10951 | 4118 | 930 | 1931 | 2811 | 264 | 38 | 693 | 166 | 0 | 0 | 0
21:00 | 74 | 204 | 120 | 0 | 300 | 107 | 74 | 348 | 354 | 0 | 0 | 390 | 290 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 64 | 0 | 47 | 35 | 56 | 55 | 0 | 25 | 11 | 0 | 33 | 50 | 0 | 38 | 0 | 0 | 150 | 25 | 230 | 0 | 131 | 0 | 0 | 33 | 0 | 85 | 10 | 103 | 46 | 13 | 36 | 0 | 0 | 0 | 180 | 300 | 199 | 63 | 100 | 33 | 30 | 5 | 45 | 0 | 0 | 0 | 0 | 11 | 33 | 8 | 172 | 152 | 16 | 0 | 0 | 60 | 60 | 53 | 50 | 100 | 313 | 65 | 86 | 46 | 85 | 0 | 44 | 10 | 290 | 24 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 100 | 200 | 0 | 300 | 100 | 0 | 0 |  | 931 | 44 | 0 | 0 | 115 | 0 | 0 | 0 | 25 | 51 | 40 | 175 | 37 | 110 | 0 | 0 | 55 | 50 | 26 | 91 | 50 | 16 | 0 | 51 | 42 | 22 | 11 | 11 | 0 | 64 | 199 | 17 | 16 | 192 | 0 | 158 | 0 | 97 | 100 | 174 | 0 | 300 | 105 | 0 | 108 | 105 |  | 7042 | 3588 | 10630 | 4457 | 931 | 2250 | 2072 | 263 | 38 | 447 | 172 | 0 | 0 | 0
22:00 | 74 | 208 | 130 | 0 | 330 | 107 | 0 | 355 | 354 | 0 | 0 | 390 | 295 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 47 | 35 | 18 | 55 | 0 | 25 | 24 | 0 | 33 | 50 | 0 | 38 | 0 | 0 | 150 | 25 | 230 | 0 | 131 | 0 | 0 | 32 | 0 | 34 | 10 | 103 | 46 | 13 | 39 | 0 | 0 | 0 | 250 | 360 | 204 | 63 | 100 | 33 | 30 | 5 | 45 | 0 | 0 | 0 | 0 | 11 | 33 | 9 | 162 | 152 | 16 | 0 | 0 | 60 | 60 | 50 | 50 | 163 | 326 | 64 | 87 | 46 | 85 | 19 | 45 | 10 | 290 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 100 | 200 | 0 | 300 | 100 | 0 | 0 |  | 931 | 32 | 0 | 0 | 115 | 0 | 0 | 0 | 25 | 49 | 32 | 175 | 37 | 110 | 0 | 0 | 55 | 50 | 26 | 93 | 50 | 16 | 0 | 50 | 42 | 22 | 11 | 11 | 0 | 64 | 199 | 16 | 16 | 196 | 0 | 165 | 0 | 96 | 100 | 176 | 0 | 300 | 105 | 0 | 0 | 105 |  | 7204 | 3470 | 10674 | 4742 | 931 | 2240 | 1915 | 263 | 38 | 383 | 162 | 0 | 0 | 0
23:00 | 74 | 209 | 130 | 0 | 350 | 108 | 0 | 378 | 351 | 0 | 0 | 430 | 300 | 0 | 0 | 0 | 0 | 0 | 195 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 46 | 35 | 18 | 55 | 0 | 25 | 28 | 0 | 35 | 50 | 0 | 36 | 0 | 0 | 150 | 25 | 229 | 0 | 140 | 0 | 0 | 33 | 0 | 34 | 50 | 103 | 46 | 13 | 38 | 0 | 0 | 0 | 250 | 360 | 205 | 63 | 100 | 33 | 30 | 5 | 45 | 0 | 0 | 6 | 0 | 11 | 33 | 9 | 156 | 153 | 16 | 20 | 0 | 60 | 60 | 50 | 50 | 163 | 318 | 65 | 87 | 46 | 85 | 19 | 44 | 10 | 300 | 25 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 100 | 200 | 0 | 297 | 100 | 0 | 0 |  | 931 | 32 | 0 | 0 | 115 | 0 | 0 | 0 | 25 | 50 | 40 | 175 | 37 | 110 | 0 | 0 | 60 | 50 | 26 | 93 | 50 | 16 | 0 | 50 | 42 | 22 | 11 | 11 | 0 | 65 | 199 | 16 | 16 | 204 | 0 | 170 | 0 | 98 | 100 | 178 | 0 | 360 | 105 | 0 | 0 | 105 |  | 7399 | 3562 | 10961 | 4868 | 931 | 2348 | 1974 | 264 | 36 | 384 | 156 | 0 | 0 | 0
24:00 | 74 | 209 | 130 | 0 | 363 | 108 | 0 | 343 | 355 | 0 | 0 | 430 | 250 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 66 | 0 | 47 | 35 | 18 | 55 | 0 | 25 | 28 | 33 | 33 | 49 | 0 | 36 | 0 | 0 | 150 | 25 | 230 | 0 | 137 | 0 | 0 | 33 | 0 | 34 | 60 | 103 | 46 | 13 | 38 | 0 | 0 | 0 | 250 | 360 | 182 | 63 | 100 | 33 | 30 | 5 | 45 | 0 | 0 | 25 | 0 | 11 | 33 | 9 | 146 | 153 | 8 | 20 | 0 | 60 | 48 | 50 | 50 | 163 | 314 | 62 | 87 | 46 | 74 | 19 | 43 | 10 | 280 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 100 | 197 | 0 | 303 | 100 | 0 | 0 |  | 922 | 14 | 0 | 0 | 115 | 0 | 0 | 0 | 25 | 50 | 40 | 175 | 36 | 110 | 0 | 0 | 60 | 50 | 26 | 93 | 50 | 16 | 0 | 50 | 41 | 22 | 11 | 11 | 0 | 65 | 199 | 17 | 16 | 194 | 0 | 163 | 0 | 98 | 100 | 169 | 0 | 360 | 105 | 0 | 0 | 104 |  | 7290 | 3507 | 10797 | 4791 | 922 | 2330 | 1942 | 264 | 36 | 366 | 146 | 0 | 0 | 0
KWH | 1672000 | 1218600 | 1525000 | 0 | 7076455 | 1612090 | 1271648 | 8334330 | 7355000 | 73600 | 0 | 8755875 | 6849484 | 399360 | 132024 | 141442 | 0 | 0 | 3304000 | 0 | 72000 | 751824 | 537120 | 105675 | 985920 | 0 | 950208 | 358200 | 791069 | 852580 | 236340 | 600000 | 537660 | 473400 | 734900 | 694848 | 0 | 735240 | 0 | 0 | 3700000 | 418165 | 5264635 | 0 | 2854630 | 0 | 0 | 705600 | 171048 | 273192 | 775080 | 1712640 | 948960 | 323472 | 557760 | 0 | 0 | 0 | 5875500 | 7797000 | 4667000 | 1555636 | 2337520 | 736920 | 389280 | 120000 | 867806 | 0 | 25944 | 340488 | 150552 | 226620 | 820300 | 164200 | 3095040 | 3555120 | 371520 | 333972 | 10100 | 1375000 | 1171412 | 841800 | 832000 | 3281514 | 7220000 | 1499808 | 1137600 | 848520 | 2183050 | 123000 | 791020 | 248040 | 6807500 | 555024 | 126288 | 0 | 198218 | 0 | 0 | 79200 | 30655 | 1029600 | 124470 | 2217600 | 2261280 | 849750 | 3914800 | 1605600 | 0 | 0 |  | 22317818 | 191500 | 0 | 0 | 1816320 | 0 | 0 | 0 | 198240 | 370048 | 603750 | 4305603 | 676398 | 109920 | 6591 | 1185000 | 1148000 | 284494 | 132873 | 934868 | 552190 | 121209 | 64327 | 410400 | 268690 | 410880 | 225540 | 109332 | 0 | 1555636 | 4853900 | 90000 | 89000 | 4773164 | 0 | 4218455 | 0 | 2298922 | 836160 | 4441218 | 0 | 2233090 | 1497120 | 0 | 841920 | 1835200 |  | 151636341 | 66007776 | 217644117 | 102869280 | 22317818 | 43117919 | 35326779 | 6409536 | 735240 | 3637935 | 3095040 | 134570 | 0
Fuel Cost | 1437920 | 1047996 | 1311500 | 0 | 4528931.2 | 1305792.9 | 1195349.12 | 5083941.3 | 4486550 | 707296 | 0 | 5866436.25 | 104043661.96 | 2507980.8 | 881920.32 | 864210.62 | 0 | 0 | 3667440 | 0 | 450000 | 4954520.16 | 5193950.4 | 673149.75 | 5905660.8 | 0 | 6337887.36 | 2553966 | 4944181.25 | 5345676.6 | 177255 | 450000 | 0 | 0 | 0 | 6573262.08 | 0 | 0 | 0 | 0 | 4070000 | 3960022.55 | 3474659.1 | 0 | 3282824.5 | 0 | 0 | 6202224 | 1842186.96 | 2658158.16 | 4797745.2 | 11063654.4 | 6206198.4 | 274951.2 | 0 | 0 | 0 | 0 | 3642810 | 5379930 | 3266900 | 1073388.84 | 2244019.2 | 493736.4 | 334780.8 | 110400 | 711600.92 | 0 | 281232.96 | 2526420.96 | 115925.04 | 169965 | 631631 | 123150 | 21170073.6 | 2666340 | 3414268.8 | 257158.44 | 0 | 1430000 | 1218268.48 | 808128 | 748800 | 2559580.92 | 5054000 | 1709781.12 | 1217232 | 933372 | 2488677 | 157440 | 735648.6 | 230677.2 | 4356800 | 416268 | 95978.88 | 0 | 1439062.68 | 0 | 0 | 566280 | 522667.75 | 0 | 0 | 0 | 21120355.2 | 7936665 | 3405876 | 0 | 0 | 0 |  | 113820871.8 | 5582225 | 0 | 0 | 15057292.8 | 0 | 0 | 0 | 2232182.4 | 4359165.44 | 4757550 | 2970866.07 | 669634.02 | 813408 | 221984.88 | 1244250 | 1205400 | 3257456.3 | 1424398.56 | 8376417.28 | 4776443.5 | 1078760.1 | 685082.55 | 4071168 | 3162481.3 | 451968 | 212007.6 | 82764.324 | 0 | 9442710.52 | 18736054 | 2900700 | 2382530 | 3245751.52 | 0 | 2952918.5 | 0 | 0 | 14490652.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 338094351.13 | 234665095.264 | 572759446.394 | 75477223.274 | 113820871.8 | 28008147.17 | 261544213.84 | 28178764.52 | 0 | 44560152.19 | 21170073.6 | 0 | 0
Yesterday Day Peak | 74 | 0 | 0 | 0 | 370 | 85 | 50 | 347 | 344 | 0 | 0 | 450 | 280 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 30 | 0 | 0 | 62 | 0 | 46 | 0 | 36 | 35 | 0 | 25 | 25 | 17 | 33 | 48 | 0 | 32 | 0 | 0 | 150 | 25 | 226 | 0 | 145 | 0 | 0 | 30 | 0 | 0 | 10 | 90 | 39 | 14 | 2 | 0 | 0 | 0 | 240 | 350 | 198 | 63 | 100 | 33 | 5 | 5 | 15 | 0 | 0 | 25 | 0 | 11 | 33 | 0 | 134 | 149 | 0 | 20 | 0.9 | 58 | 48 | 26 | 50 | 130 | 311 | 63 | 30 | 45 | 75 | 0 | 42 | 10 | 275 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 17.4 | 90 | 35 | 33 | 120 | 98 | 0 | 0 |  | 930 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 32 | 176 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 6 | 22 | 8 | 5 | 0 | 65 | 199 | 0 | 0 | 202 | 0 | 177 | 0 | 94 | 0 | 179 | 0 | 0 | 36 | 0 | 0 | 72 |  | 8583.3 | DayPeak
Yesterday Evening Peak | 74 | 145 | 140 | 0 | 260 | 106 | 69 | 350 | 259 | 55 | 0 | 300 | 270 | 56 | 64 | 55 | 0 | 0 | 76 | 0 | 50 | 100 | 149 | 60 | 64 | 0 | 30 | 35 | 56 | 55 | 19 | 25 | 22 | 0 | 33 | 48 | 0 | 37 | 0 | 0 | 150 | 25 | 230 | 0 | 100 | 0 | 0 | 33 | 85 | 85 | 88 | 103 | 43 | 14 | 35 | 0 | 0 | 0 | 180 | 300 | 185 | 63 | 100 | 33 | 30 | 5 | 45 | 0 | 0 | 34 | 0 | 11 | 33 | 21 | 168 | 152 | 60 | 0 | 0 | 60 | 48 | 46 | 30 | 100 | 311 | 63 | 84 | 44 | 75 | 0 | 45 | 10 | 280 | 24 | 11 | 0 | 140 | 0 | 0 | 7 | 0 | 135 | 0 | 100 | 200 | 100 | 150 | 98 | 0 | 0 |  | 931 | 32 | 0 | 0 | 115 | 0 | 0 | 0 | 25 | 63 | 40 | 175 | 33 | 110 | 10 | 0 | 55 | 50 | 27 | 93 | 50 | 50 | 42 | 50 | 42 | 22 | 11 | 11 | 0 | 65 | 199 | 16 | 16 | 175 | 0 | 152 | 0 | 96 | 57 | 162 | 0 | 250 | 105 | 0 | 108 | 107 |  | 11179 | EvPeak
Forecast for Evening | 74 | 0 | 140 | 0 | 360 | 106 | 50 | 412 | 360 | 110 | 0 | 450 | 335 | 100 | 100 | 55 | 0 | 0 | 80 | 0 | 100 | 102 | 149 | 100 | 64 | 0 | 48 | 54 | 55 | 55 | 19 | 25 | 25 | 33 | 33 | 48 | 0 | 37 | 0 | 0 | 150 | 25 | 225 | 0 | 145 | 0 | 0 | 33 | 76 | 85 | 100 | 100 | 43 | 14 | 35 | 0 | 0 | 0 | 260 | 360 | 221 | 63 | 100 | 36 | 30 | 5 | 45 | 0 | 50 | 52 | 22 | 11 | 33 | 20 | 187 | 150 | 95 | 22 | 0 | 60 | 48 | 50 | 44 | 163 | 330 | 66 | 86 | 46 | 130 | 19 | 40 | 10 | 341 | 25 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 150 | 98 | 0 |  |  | 943 | 32 | 0 | 0 | 115 | 0 | 0 | 0 | 35 | 80 | 40 | 176 | 33 | 110 | 20 | 0 | 60 | 50 | 35 | 95 | 50 | 50 | 44 | 52 | 40 | 22 | 14 | 11 | 0 | 67 | 199 | 17 | 18 | 200 | 0 | 200 | 0 | 95 | 100 | 220 | 0 | 414 | 105 | 200 | 108 | 108
Forecast for Day | 74 | 0 | 140 | 0 | 360 | 50 | 50 | 412 | 360 | 110 | 0 | 450 | 335 | 100 | 100 | 55 | 0 | 0 | 80 | 0 | 100 | 102 | 149 | 100 | 64 | 0 | 48 | 54 | 55 | 55 | 19 | 25 | 25 | 33 | 33 | 48 | 0 | 37 | 0 | 0 | 150 | 25 | 225 | 0 | 145 | 0 | 0 | 33 | 76 | 85 | 100 | 100 | 43 | 14 | 10 | 0 | 0 | 0 | 260 | 360 | 221 | 63 | 100 | 36 | 5 | 5 | 45 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 148 | 150 | 95 | 22 | 2 | 60 | 48 | 50 | 44 | 100 | 330 | 66 | 86 | 46 | 130 | 19 | 40 | 10 | 341 | 25 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 20 | 100 | 200 | 150 | 150 | 98 |  |  |  | 943 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 35 | 50 | 40 | 176 | 33 | 110 | 0 | 0 | 60 | 50 | 35 | 95 | 50 | 50 | 44 | 52 | 40 | 22 | 14 | 11 | 0 | 67 | 199 | 17 | 18 | 200 | 0 | 200 | 0 | 95 | 100 | 220 | 0 | 414 | 105 | 0 | 108 | 108
Generation at 08:00(Today) | 74 | 134 | 130 | 0 | 300 | 12 | 0 | 359 | 303 | 0 | 0 | 360 | 300 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 17 | 18 | 17 | 0 | 25 | 22 | 33 | 33 | 46 | 0 | 35 | 0 | 0 | 150 | 8 | 231 | 0 | 139 | 0 | 0 | 16 | 0 | 0 | 10 | 52 | 18 | 14 | 8 | 0 | 0 | 0 | 220 | 270 | 199 | 63 | 100 | 10 | 5 | 5 | 10 | 0 | 0 | 0 | 0 | 8 | 33 | 20 | 114 | 122 | 0 | 0 | 1 | 60 | 48 | 11 | 10 | 100 | 330 | 65 | 10 | 10 | 83 | 19 | 12 | 0 | 290 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 6.3 | 75 | 34 | 0 | 181 | 0 | 0 | 0 | 0 | 931 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 176 | 23 | 16 | 0 | 0 | 60 | 0 | 0 | 30 | 12 | 0 | 0 | 0 | 6 | 22 | 11 | 8 | 0 | 67 | 199 | 0 | 0 | 174 | 0 | 167 | 0 | 95 | 0 | 174 | 0 | 260 | 70 | 0 | 0 | 86 | 0
199
| Minimum Generation |  | 7004.5 | 7:00
| Highest Generation |  | 11179 | 19:30
| Day Peak Generation |  | 8583.3 | 12:00
| Evening Peak Generation |  | 11179 | 19:30
| HVDC Max Flow |  | 939 | 1:00
| HVDC EvPeak Flow |  | 931 | 19:30
| Load factor L.F |  | 81.12%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2019-05-19
Till now the maximum generation is : - |  |  | 12494 MW | 20:00 | Hrs on | 2019-05-11
The Summary of Yesterday's |  | 2019-05-18 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 8583.3 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 8042.5 | MW
Evening Peak Generation : |  | 11179 | MW Hour : | 19:30 | Available Max Generation : |  | 14146 | MW
E.P. Demand (at gen end) : |  | 11179 | MW Hour : | 19:30 | Max Demand (Evening) : |  | 12000 | MW
Maximum Generation : |  | 11179 | MW Hour : | 19:30 | Reserve(Generation end) |  | 2146 | MW
Total Gen. (MKWH) : |  | 217.6441 | System Load Factor : | 81.12% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -340 | MW at | 15:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2019-05-19
Actual : | 72.85 | Ft.(MSL) , | Rule curve : | 78.58 | Ft.( MSL )
Gas Consumed : | Total = | 1333.09 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 103485370.444
|  | Coal : | 28178764.52 | Oil : | 306104366.03 | Total : | 437768500.994
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4305.1868 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1466.5918 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1314.4791 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1187.9067 |  |  | 0 | 0%
Comilla Area | 0 | 0:00 | 1073.4037 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 866.2053 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 481.0064 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 222.9364 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 668.0765 |  |  | 0 | 0%
Total | 0 |  | 11585.7927 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1 | 7) Ghorashal Unit-3,5
|  |  |  | 2) Khulna ST 110 MW | 8) Siddhirhganj 335 MW
|  |  |  | 3) Sikalbaha ST 60 MW | 9) Raozan # 1
4) Bheramara 410 MW.
5) Siddhirganj ST
6) Ashuganj #3,4,5
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Pabna 132/33 kV T1 transformer was under shut down from 11:17 to 12:01 due to oil level low.
b) Pabna 132/33 kV T2 transformer tripped at 11:50 showing O/C and was switched on at 11:59. |  |  |  |  | About 63 MW power interruption occurred under Pabna S/S area
from 11:50 to 11:59.
c) Tongi 132/33 kV T1 & T2 transformers tripped at 11:54 due to 33 kV bus fault and were |  |  |  |  | About 30 MW power interruption occurred under Tongi S/S area
switched on at 14:10. |  |  |  |  | from 11:54 to 14:10.
d) Sonargaon 132/33 kV T2 transformer was under shut down from 08:20 to 10:49 for D/W.
e) Sirajganj-Bogura 132 kV Ckt-2 was switched on at 12:06.
f) Maniknagar 230/132 kV T2 transformer was switched on at 09:01.
g) Maniknagar-Siddhirganj 230 kV Ckt-2 was switched on at 08:59.
h) Halishahar-Khulshi 132 kV Ckt-1,2 tripped at 12:10 due to mental disorder man climbing and were
switched on at 13:10.
i) Baghabari 100 MW tripped at 11:32 due to Unit transformer got fired.
j) Ghorasal Unit-4 was synchronized at 12:22.
k) Shahjadpur-Baghabari 132 kV Ckt-1 tripped at 15:08 showing Dist ,CD B-phase and was
switched on 15:08.
l) Sirajganj Unit-4 GT & ST were synchronized at 14:17 & 15:43 respectively.
m) Ghorasal Unit-3 GT was synchronized at 15:52.
n) Baghabari 71 MW was synchronized at 15:41.
o) Shahjibazar-Ashuganj 132 kV Ckt-3 was switched on at 18:04.
p) Ruppur 132/11 kV T2 transformer was switched on at 16:18.
q) B.Baria 132/33 kV T1 transformer was under shut down from 21:27 to 21:59 for red hot maintenance
at 33 kV Y-phase isolator.
r) Sherpur-United Mymensingh P/S 132 kV Ckt-1 tripped at 23:35 form both ends showing DistZ1, E/F
, O/C at Sherpur end & Dist , E/F ,O/C at United Mymensingh end and was switched on at 23:52.
s) Hathazari-Baroierhat 132 kV Ckt-1 tripped at 07:26(19/05/2019) from Hathazari end showing
Dist R-phase and was switched on at 07:46.
Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2019-05-18 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | PDB | 2*55 | 85 | 74 | 1672000
| Ghorasal GT: Unit-3 |  | PDB | 1*210 | 170 | 145 | 1218600
| Ghorasal GT: Unit-4 |  | PDB | 1*210 | 180 | 140 | 1525000
| Ghorasal ST: Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal ST: Unit-7 |  | PDB | 1*243+1*122 | 365 | 260 | 7076455 | Frequency control
3 | Ghorashal 78MW (MAX) |  | QRPP | 2*40 | 78 | 69 | 1271648 | Gas shortage
4 | Ghorashal (Regent) |  | IPP | 34*3.35 | 108 | 106 | 1612090
5 | Haripur GT: Unit-1, 2 |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Gas shortage
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 350 | 8334330 | FGMO
7 | Haripur NEPC 110MW |  | IPP | 8*15 | 110 | 55 | 73600 | Low demand
8 | Haripur Power CCPP 360MW |  | IPP | 1*235+1*125 | 360 | 259 | 7355000 | Gas shortage
9 | Meghnaghat CCPP 450MW |  | IPP | 2*150+1*150 | 450 | 300 | 8755875 | Frequency control
10 | Meghnaghat (IEL) |  | QRPP | 12*8.9 | 100 | 56 | 399360 | Low demand
11 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 270 | 6849484 | FGMO
12 | Madanganj 102MW |  | QRPP | 6*17 | 100 | 64 | 132024 | Low demand
13 | Madanganj-55 MW |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 141442
14 | Keraniganj (Powerpac) 100MW |  | QRPP | 8*13.45 | 100 | 60 | 105675 | Low demand
15 | Narshingdi (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 236340
16 | Siddhirgonj ST 210MW |  | PDB | 1*210 | 115 | 0 | 0 | Gas shortage
17 | Siddhirgonj GT Unit-1& 2 |  | EGCB | 2*105 | 210 | 76 | 3304000 | Gas shortage
| Siddhirganj Desh |  | QRPP | 96*1.2 | 0 | 0 | 0 | Contract Expired
18 | Siddhirganj (Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 50 | 72000 | Low demand
19 | Siddhirganj CCPP-335 MW |  | EGCB | 1*217 | 217 | 0 | 0 | Gas shortage
0 | Pagla (DPA ) |  | QRPP | 100*0.5 | 0 | 0 | 0 | Contract Expired
20 | Gagnagar (Orion) |  | IPP | 12*8.924 | 102 | 100 | 751824
21 | Katpotti 51 MW |  | IPP | 7*7.9 | 51 | 30 | 950208 | Engine problem
22 | Banco Energy 54MW |  | IPP | 3*18 | 54 | 35 | 358200 | Engine problem
23 | Kodda 149MW |  | BPDB-RPCL | 9*17.06 | 149 | 149 | 537120
24 | Northern 55 MW |  | IPP | 3*19.3 | 55 | 56 | 791069
25 | Southern 55MW |  | IPP | 3*19.3 | 55 | 55 | 852580
26 | Bosila 108MW |  | IPP | 12*8.775+1*3.5 | 108 | 64 | 985920 | Engine problem
27 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 47 | 1137660 | Engine problem
28 | Summit Maona |  | SIPP,REB | 4*8.73 | 33 | 0 | 473400 | Machine tripped
29 | Summit Rupganj |  | SIPP,REB | 4*8.73 | 33 | 33 | 734900
30 | Gazipur (RPCL) |  | IPP | 6*8.9 | 52 | 48 | 694848
31 | Tongi GT |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
32 | Summit Gazipur -2 |  | IPP | 18*17.076 | 300 | 140 | 198218 | Low demand
33 | APR Energy , Keranigonj |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
34 | Bramhangoan 100 MW (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
35 | Aggreko Aurahati 100MW |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 30655 | Reserve
36 | Summit Gazipur-1 150MW |  | IPP | 149 | 149 | 135 | 1029600 | Low demand
| Gazipur 100 MW |  | RPCL | 100 MW | 0 | 0 | 0 | on test
| Dhaka area Total |  |  |  | 5698 | 3300 | 59661125
37 | Chattogram ST-1 (Raozan) |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chittgong ST-2 (Raozan) |  | PDB | 1*210 | 180 | 150 | 3700000 | Gas shortage
38 | Raozan 25 MW (RPCL) |  | IPP | 3*8.9 | 25 | 25 | 418165
39 | Teknaf Solartech 20MW |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 124470
40 | Patenga 50MW |  | IPP | 8*6.98 | 50 | 43 | 948960
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 37 | 735240 | Low water level
42 | Sikalbaha ST 60MW |  | PDB | 1*60 | 40 | 0 | 0 | Under maint.
43 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 230 | 5264635 | FGMO
44 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 100 | 2854630 | FGMO
45 | Sikalbaha (Energis) |  | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 33 | 705600 | Engine problem
46 | Hathazari peaking |  | PDB | 11*8.9 | 98 | 85 | 171048
47 | Dohazari Peaking |  | PDB | 6*17 | 102 | 85 | 273192
48 | Juldah (Acorn) |  | QRPP | 8*13.45 | 100 | 88 | 775080 | Engine problem
49 | Juldah 100 MW Unit-3 |  | IPP | 0 | 100 | 100 | 2217600
50 | Barabkunda (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 14 | 323472 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 35 | 557760
51 | Chattogram ECPV 108 MW |  | IPP | 16*7 | 108 | 103 | 1712640
| Chattogram area Total |  |  |  | 1681 | 1128 | 20782492
52 | Ashuganj ST: Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage
| Ashuganj ST: Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj ST: Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
53 | Ashuganj CCPP 225 MW |  | APSCL | 1*142+1*75 | 221 | 185 | 4667000 | FGMO
54 | Ashuganj CCPP(North) |  | APSCL | 1*360 | 360 | 180 | 5875500 | ST Under Maint.
55 | Ashuganj CCPP(South) |  | APSCL | 1*360 | 360 | 300 | 7797000 | Frequency control
56 | Ashuganj Engines TSK |  | APSCL | 14*3.968 | 45 | 33 | 736920 | Engine problem
57 | Ashuganj (Precision) 55MW |  | RPP | 15*4 | 55 | 30 | 389280 | Gas shortage
58 | Ashuganj (United) 53MW |  | QRPP | 14*4 | 53 | 5 | 120000 | Gas shortage
59 | Ashuganj 195MW Modular |  | IPP | 20*9.73+1*16 | 195 | 63 | 1555636 | Gas shortage
60 | Ashuganj (Midland) 51MW |  | IPP | 6*9.34 | 51 | 45 | 867806 | Engine problem
61 | Midland 150MW |  | IPP | 23*7.015 | 150 | 100 | 849750 | Low demand
62 | B.Baria (Aggreko) 85MW |  | QRPP | 86*1.10 | 85 | 0 | 0 | Contract Expired
63 | Daudkandi Peaking 52MW |  | PDB | 6*8.92 | 52 | 0 | 25944 | Reserve
64 | Chandpur CCPP |  | PDB | 1*106+1*57 | 163 | 100 | 2337520
65 | Chandpur Desh 200MW |  | IPP | 0 | 200 | 200 | 2261280
66 | Feni (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 0 | 150552
67 | Feni, Mohipal (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 226620
** | Tripura |  | Imported power | 0 | 160 | 168 | 3095040
68 | Jangalia (Summit) 33MW |  | SIPP, PDB | 4*8.73 | 33 | 33 | 820300
69 | Lakdhanvi 52 MW |  | IPP | 6*8.92 | 52 | 34 | 340488 | Low demand
70 | Summit Cumilla 25MW |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 164200
71 | Daudkandi bangla trak |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Cumilla Area Total |  |  |  | 2891 | 1508 | 32280836
72 | Mymensingh RPCL 210MW |  | IPP | 4*35+1*70 | 202 | 152 | 3555120 | Engine problem
73 | Tangail (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 0 | 333972
74 | Jamalpur 95MW |  | IPP | 12*8.924 | 95 | 60 | 371520 | Low demand
75 | Sarishabari (Solar) |  | IPP | 1*3 | 3 | 0 | 10100
76 | United Mymensingh PPL |  | IPP | 200 | 200 | 7 | 79200 | Low demand
77 | United Jamalpur PPL |  | IPP | 115 MW | 115 | 98 | 1605600
| Mymensingh Area Total |  |  |  | 637 | 317 | 5955512
78 | Fenchugonj CCPP-1 |  | PDB | 2*32+1*33 | 70 | 60 | 1375000
79 | Fenchugonj CCPP-2 |  | PDB | 2*35+1*35 | 90 | 48 | 1171412
80 | Kushiara 163 MW CCPP GT |  | IPP | 1*109+1*54 | 163 | 100 | 3281514 | Frequency control
81 | Shajibazar 330 MW |  | PDB | 3*110 | 330 | 311 | 7220000 | FGMO
82 | Fenchugonj (Barakatullah) 51MW |  | RPP | 19*2.90 | 51 | 46 | 841800
83 | Fenchuganj (EPL) 44MW |  | RPP | 12*3.3+5*2 | 44 | 30 | 832000 | Low demand
84 | Hobiganj 11MW |  | SIPP, REB | 4*2.90 | 11 | 11 | 126288
85 | Shahjibazar GT: Unit- 8, 9 |  | PDB | 2*35 | 66 | 63 | 1499808 | FGMO
86 | Shahjibazar 86MW |  | RPP | 32*2.90 | 86 | 84 | 1137600
87 | Shahjibazar (EPL) 50MW |  | RPP | 27*2.0 | 50 | 44 | 848520
88 | Sylhet GT 150 MW |  | PDB | 1*142 | 142 | 75 | 2183050 | Frequency control
89 | Sylhet GT 20 MW |  | PDB | 1*20 | 20 | 0 | 123000
90 | Sylhet (EPL) 50MW |  | RPP | 27*2 | 50 | 45 | 791020
91 | Shahjahanulla 25 MW |  | SIPP, REB | 3*9.34 | 25 | 24 | 555024
92 | Summit Bibiana- 2 |  | IPP | 1*222+1*119 | 341 | 280 | 6807500 | FGMO
| Bibiyana-3 285 MW |  | PDB | 285 MW | 0 | 150 | 3914800 | On test
93 | Sylhet (Desh) 10MW |  | RPP | 6*1.95 | 10 | 10 | 248040
| Sylhet Area Total |  |  |  | 1549 | 1381 | 32956376
94 | Bheramara GT-1,2,3 |  | PDB | 3*20 | 46 | 32 | 191500
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 931 | 22317818
| Khulna (KPCL-1 & 3) |  | IPP | 19*6.5 | 0 | 0 | 0 | Contract Expired
95 | Khulna (KPCL-2) |  | QRPP | 7*17 | 115 | 115 | 1816320
96 | Faridpur Peaking |  | PDB | 8*6.89 | 54 | 25 | 198240
97 | Khulna CCPP 225MW |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
98 | Gopalganj Peaking |  | PDB | 16*6.98 | 109 | 63 | 370048
99 | Bheramara 360 MW |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Under maint.
100 | Noapara (KZA) 40MW |  | QRPP | 5*8.5 | 40 | 40 | 603750
0 | Khulna (Aggreeco) 55MW |  | QRPP | 71*0.85 | 0 | 0 | 0 | Contract Expired
101 | Bangla Trak Noapara |  | IPP | 70*1.4 | 100 | 57 | 836160 | Low demand
102 | Labon Chora 105 MW |  | IPP | 6*18.445 | 105 | 105 | 1497120
103 | Madhumati Power Plant |  | IPP | 100 MW | 105 | 107 | 1835200
| Khulna Area Total |  |  |  | 2314 | 1475 | 29666156
104 | Summit Barisal 110 MW |  | IPP | 7*17.076 | 110 | 110 | 109920
105 | Barisal GT: Unit-1, 2 |  | PDB | 2*20 | 30 | 10 | 6591
106 | Bhola (Venture) 33MW |  | RPP | 1*34.50 | 33 | 33 | 676398
107 | Bhola CCPP 194MW |  | PDB | 2*63+1*68 | 194 | 175 | 4305603 | FGMO
108 | Bhola Aggreko 95MW |  | QRPP | 96*1.10 | 95 | 96 | 2298922
| Barisal Area Total |  |  |  | 462 | 424 | 7397434
109 | Baghabari GT 71MW |  | PDB | 1*71 | 71 | 55 | 1148000
| Baghabari GT 100MW |  | PDB | 1*100 | 100 | 0 | 1185000 | Under maint.
110 | Baghabari Peaking 50MW |  | PDB | 6*8.9 | 52 | 50 | 284494
111 | Bera Peaking |  | PDB | 9*8.29 | 71 | 27 | 132873
112 | Amnura 50MW |  | QRPP | 7*7.79 | 50 | 50 | 552190
113 | Katakhali (Northern) |  | QRPP | 6*8.9 | 50 | 50 | 121209
114 | Katakhali Peaking |  | PDB | 6*8.7 | 50 | 42 | 64327
115 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 175 | 4773164 | FGMO
116 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 152 | 4218455 | FGMO
117 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 162 | 4441218 | FGMO
118 | Sirajgonj Unit-4 414 MW(Gas) |  | SNWPGCL | 1*282+1*132 | 414 | 250 | 2233090 | Frequency control
119 | Santahar Peaking |  | PDB | 6*8.7 | 50 | 42 | 268690
120 | Bogra (GBB) |  | RPP | 6*4 | 22 | 22 | 410880
121 | Bogra (EPL) |  | RPP | 5*3.3+5*2 | 10 | 11 | 225540
122 | Ullapara (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 109332
123 | Rajlanka 52 MW |  | IPP | 6*8.92 | 52 | 50 | 410400
124 | Chapainawabganj-100 MW |  | PDB | 12*8.924 | 104 | 93 | 934868
125 | Paramount Baghabari |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
126 | Confidence CPBL-2 |  | IPP | 113 MW | 113 | 108 | 841920
| Rajshahi Area Total |  |  |  | 2070 | 1350 | 22355650
107 | Barapukuria Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under overhauling
| Barapukuria Unit-2 |  | PDB | 1*125 | 85 | 65 | 1555636
108 | Barapukuria Unit-3 |  | PDB | 1*275 | 274 | 199 | 4853900
129 | Rangpur GT |  | PDB | 1*20 | 20 | 16 | 90000
130 | Saidpur GT |  | PDB | 1*20 | 20 | 16 | 89000
| Rangpur Area Total |  |  |  | 484 | 296 | 6588536
| Total |  |  |  | 17786 | 11179 | 217644117
| Eastern Grid Total |  |  |  | 12456 | 7634 | 151636341
| Western Grid Total |  |  |  | 5330 | 3545 | 66007776
| National Grid Total |  |  |  | 17786 | 11179 | 217644117
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date: | 2019-05-18 | [5 empty] | QF-LDC-09
| (a) ENTIRE EASTERN GRID : |  |  | 7263 | MW | (b) ENTIRE WESTERN GRID : |  |  | 3523
| i) Dhaka area |  |  | 4126 | MW | i) Khulna area |  |  | 1461
| ii) Chittagong area |  |  | 1088 | MW | ii) Rajshahi area |  |  | 1067
| iii) Comilla area |  |  | 1135 | MW | iii) Barisal area |  |  | 334
| iv) Mymensingh area |  |  | 502 | MW | iv) Rangpur area |  |  | 661
| v) Sylhet area |  |  | 412 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  |  | 10786 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
SL NO | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
1 | Siddhirganj | 126 | 1600 | Jamalpur | 69 | 2200 | Jessore | 131 | 2000
2 | Munsiganj | 123 | 2100 | Sherpur | 84 | 2100 | Jhenida | 107 | 2000
3 | Sonargaon | 67 | 1930 | Srimongal | 33 | 1930 | Bottail | 132 | 2000
4 | Shyampur | 188 | 1400 | Shahjibazar | 96 | 2000 | G.K Project | 54 | 1930
5 | Bhulta | 188 | 1500 | Fenchuganj | 37 | 2000 | Faridpur | 180 | 2000
6 | Madanganj | 46 | 2100 | Kulawara | 40 | 1830 | Madaripur | 123 | 2200
7 | Shitalakhya | 99 | 1930 | Sylhet | 120 | 2000 | Gopalganj | 97 | 2200
8 | Rahim steel | 7 | 1200 | Chatak | 25 | 1900 | Bagerhat | 84 | 1930
9 | Matuail | 98 | 1200 | Sunamganj | 26 | 1900 | Mongla | 34 | 1200
10 | Ghorasal | 77 | 2000 | Biani Bazar | 40 | 1900 | Satkhira | 102 | 2000
11 | Narsingdi | 131 | 1930 | Comilla (S) | 172 | 2100 | Gallamari | 54 | 2000
12 | Haripur (SBU) | 87 | 2000 | Comilla(N) | 129 | 2000 | Magura | 52 | 1930
13 | Ullon | 101 | 1930 | Chandpur | 120 | 1900 | Chuadanga | 84 | 2000
14 | Hasnabad | 226 | 2000 | Feni | 141 | 1930 | Barisal | 114 | 2200
15 | Magbazar | 112 | 1500 | Chowmuhani | 196 | 2100 | Patuakhali | 106 | 2100
16 | Maniknagar | 104 | 1930 | Ashuganj | 45 | 2100 | Bhandaria | 57 | 2000
17 | Bangabhaban | 20 | 1300 | Daudkandi | 124 | 2000 | Barisal (N) | 44 | 2000
18 | Narinda | 96 | 1400 | B.Baria | 149 | 2000 | Sariatpur | 37 | 2200
19 | Dhanmondi | 148 | 1700 | Ramganj | 80 | 1930 | Benapol | 39 | 1930
20 | Lalbag | 94 | 1300 | Madunaghat | 61 | 1900 | Ishurdi | 64 | 2000
21 | Madartek | 58 | 2000 | Hathazari | 101 | 2000 | Ruppur Paromanobik | 2 | 2000
22 | Mirpur | 117 | 1930 | Khulshi | 193 | 2100 | Natore | 110 | 2000
23 | Kalyanpur | 129 | 1930 | Halishahar | 137 | 1930 | Bogra | 187 | 1930
24 | Gulshan | 126 | 1500 | Baraulia | 162 | 100 | Noagaon | 108 | 2000
25 | Uttara | 87 | 1930 | Sikalbaha | 38 | 2000 | Rajshahi | 154 | 2000
26 | Uttara New | 18 | 1300 | Dohazari | 102 | 1900 | C.Nawabganj | 73 | 2000
27 | Kamrangirchar | 85 | 1400 | Cox'sbazar | 95 | 2000 | Amnura | 33 | 2100
28 | Savar | 149 | 1500 | Chandraghona | 28 | 1930 | Pabna | 119 | 2000
29 | Bhasantec | 160 | 1930 | Kaptai | 4 | 1830 | Shahjadpur | 83 | 2100
30 | Agargaon | 59 | 1900 | A. Khaer Stl. | 0 | 100 | Serajganj | 71 | 2100
31 | Satmosjid | 117 | 1930 | Bakulia | 126 | 2100 | Niyamatpur | 59 | 2100
32 | Tongi | 121 | 1830 | Julda | 16 | 100 | Joypurhat | 50 | 2100
33 | Kabirpur | 203 | 1700 | TK chemical | 5 | 1000 | Mohastangor | 15 | 2000
34 | Basundhara | 142 | 1300 | Modern Steel | 14 | 1300 | Rangpur | 121 | 1930
35 | Manikganj | 92 | 1900 | Shahmirpur | 31 | 1400 | Lalmonirhat | 77 | 2100
36 | Joydevpur | 200 | 1900 | Khagrachhari | 18 | 1930 | Saidpur | 98 | 2000
37 | New Tongi | 118 | 1400 | Matarbari | 29 | 1930 | Purbasadipur | 104 | 2000
38 | Korda | 228 | 1700 | Baroiar Hat | 28 | 1930 | Thakurgaon | 73 | 2100
39 | Dhamrai | 56 | 1930 | Rangamati | 12 | 1900 | Palashbari | 102 | 1930
40 | Valuka | 36 | 1400 | Abul Khair 230 | 135 | 100 | Barapukuria | 50 | 2100
41 | Tangail | 152 | 1900 | BSRM | 151 | 1100 | Panchagar | 39 | 2000
42 | Mymensing | 192 | 1830 | Goalpara | 25 | 2300 | Joldhaka | 15 | 2000
43 | Kishorganj | 104 | 1900 | Central (S) | 93 | 2000
44 | Netrokona | 74 | 2200 | Noapara | 90 | 1930
| Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  |  | (24) Director,System Planning,PDB.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2019-05-18
| Sub-Station | Maxm | Hour | Minm | Hour | Sub-Station | Maxm | Hour | Minm
|  | Voltage |  | Voltage |  |  | Voltage |  | Voltage
SL NO | 400 KV | KV |  | KV |  |  | KV |  | KV
1 | Bibiyana | 396 | 5:00 | 378 | 22:00 | Kaliakoir | 389 | 19:00 | 358
2 | Bheramara | 393 | 6:00 | 384 | 10:00 | Bhulta | 399 | 5:00 | 382
3 | Ashuganj(N) | 374 | 5:00 | 358 | 17:00
SL NO | 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
1 | Ghorasal | 237 | 5:00 | 215 | 22:00 | Hathazari | 226 | 4:00 | 218
2 | Ishurdi | 239 | 5:00 | 230 | 10:00 | Megnaghat | 238 | 5:00 | 232
3 | Ashuganj | 234 | 21:00 | 225 | 14:00 | Fenchuganj | 226 | 5:00 | 215
4 | Serajganj | 230 | 1:00 | 233 | 22:00 | Siddhirganj | 224 | 6:00 | 214
5 | Baghabari | 235 | 6:00 | 222 | 21:00 | Maniknagar | 224 | 5:00 | 213
6 | Barapukuria | 230 | 6:00 | 213 | 22:00 | Old Airport | 234 | 18:30 | 222
7 | Bogra | 228 | 3:00 | 205 | 21:00 | Barisal | 218 | 5:00 | 210
8 | Khulna South | 222 | 5:00 | 215 | 23:00 | AKSML | 222 | 5:00 | 212
9 | Rampura | 223 | 2:00 | 216 | 15:00 | BSRM | 235 | 5:00 | 228
10 | Haripur | 225 | 1:00 | 215 | 21:00 | Bibiyana | 225 | 5:00 | 216
11 | Hasnabad | 224 | 1:00 | 215 | 22:00 | Bhulta | 238 | 6:00 | 228
12 | Aminbazar | 223 | 4:00 | 209 | 23:00 | Ashuganj (S) | 229 | 5:00 | 218
13 | Tongi | 231 | 1:00 | 222 | 22:00 | Kaliakoir | 394 | 6:00 | 384
14 | Comilla (N) | 221 | 1:00 | 214 | 22:00
SL NO | 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
1 | Siddhirganj | 133 | 1930 | 128 | 1200 | Hathazari | 131 | 100 | 126
2 | Munsiganj | 135 | 1830 | 126 | 1200 | Khulshi | 128 | 1900 | 124
3 | Megnaghat | 133 | 1930 | 127 | 1300 | Halishahar | 134 | 1930 | 127
4 | Shyampur | 130 | 1900 | 124 | 1200 | Baraulia | 131 | 1930 | 125
5 | Bhulta | 126 | 100 | 119 | 1400 | Sikalbaha | 132 | 1900 | 128
6 | Madanganj | 130 | 600 | 123 | 1300 | Dohazari | 132 | 1930 | 125
7 | Shitalakhya | 136 | 1900 | 122 | 2100 | Cox'sbazar | 131 | 2100 | 117
8 | Rahim steal | 133 | 1930 | 128 | 1100 | Chandraghona | 131 | 400 | 127
9 | Matuail | 132 | 400 | 126 | 1400 | Kaptai | 130 | 100 | 126
10 | Ghorasal | 138 | 2100 | 137 | 1800 | A. Khaer Stl. | 129 | 400 | 125
11 | Narsinghdi | 133 | 2100 | 121 | 1600 | Bakulia | 131 | 1830 | 104
12 | Haripur (SBU) | 134 | 500 | 128 | 1300 | Julda | 132 | 100 | 127
13 | Ullon | 130 | 600 | 121 | 1300 | TK Chemical | 133 | 1830 | 130
14 | Hasnabad | 130 | 1900 | 123 | 1400 | Modern Steel | 132 | 700 | 125
15 | Magbazar | 130 | 600 | 121 | 1500 | Shahmirpur | 131 | 1830 | 127
16 | Maniknagar | 135 | 600 | 130 | 1300 | Khagrachhari | 131 | 1930 | 125
17 | Bangabhaban | 135 | 600 | 130 | 1300 | Matarbari | 122 | 1100 | 116
18 | Narinda | 135 | 600 | 130 | 1300 | Baroiar Hat | 130 | 100 | 120
19 | Dhanmondi | 130 | 600 | 121 | 1300 | Rangamati | 131 | 100 | 126
20 | Lalbag | 130 | 600 | 117 | 1300 | Goalpara | 135 | 300 | 119
21 | Madartek | 130 | 600 | 121 | 1500 | Central s/s | 135 | 500 | 120
22 | Mirpur | 133 | 600 | 126 | 1000 | Noapara | 129 | 100 | 115
23 | Kalyanpur | 135 | 200 | 128 | 1500 | Jessore | 126 | 900 | 107
24 | Gulshan | 129 | 500 | 120 | 1400 | Jhenida | 126 | 800 | 104
25 | Uttara | 131 | 100 | 124 | 1300 | Bottail | 132 | 800 | 115
26 | Uttara New | 132 | 100 | 125 | 1500 | G.K.Project | 140 | 500 | 124
27 | Kamrangirchar | 130 | 1900 | 120 | 1200 | Faridpur | 130 | 900 | 116
28 | Savar | 132 | 100 | 125 | 1500 | Madaripur | 132 | 1800 | 120
29 | Bhasantec | 136 | 600 | 127 | 1700 | Gopalganj | 137 | 1800 | 126
30 | Agargaon | 136 | 100 | 128 | 1700 | Bagerhat | 127 | 200 | 119
31 | Satmosjid | 137 | 600 | 128 | 1700 | Mongla | 130 | 200 | 118
32 | Tongi | 135 | 1930 | 129 | 2100 | Satkhira | 131 | 100 | 117
33 | Kabirpur | 136 | 500 | 126 | 1700 | Gallamari | 135 | 100 | 121
34 | Basundhara | 130 | 1800 | 118 | 1300 | Magura | 125 | 800 | 102
35 | Manikganj | 136 | 1830 | 127 | 1500 | Chuadanga | 121 | 700 | 95
36 | Joydevpur | 140 | 2000 | 132 | 1200 | Barisal | 133 | 1500 | 125
37 | New Tongi | 134 | 600 | 127 | 1500 | Patuakhali | 132 | 100 | 123
38 | Kodda | 135 | 2000 | 118 | 1000 | Bhandaria | 132 | 200 | 120
39 | Dhamrai | 136 | 600 | 128 | 1500 | Barisal (N) | 135 | 900 | 129
40 | Valuka | 136 | 1930 | 130 | 100 | Sariatpur | 130 | 1800 | 119
41 | Tangail | 140 | 500 | 129 | 1700 | Benapol | 127 | 100 | 108
42 | Mymensing | 136 | 1100 | 127 | 1700 | Ishurdi | 144 | 800 | 130
43 | Kishorganj | 136 | 1200 | 127 | 2300 | Ruppur Paromanobik | 139 | 700 | 127
44 | Netrokona | 137 | 600 | 124 | 2300 | Natore | 134 | 600 | 124
45 | Jamalpur | 138 | 1100 | 129 | 2200 | Bogra | 136 | 600 | 125
46 | Sherpur | 137 | 1100 | 127 | 1700 | Noagaon | 132 | 600 | 120
47 | Srimongal | 137 | 900 | 134 | 1800 | Rajshahi | 133 | 1830 | 121
48 | Shahjibazar | 136 | 900 | 131 | 1900 | C.Nawabganj | 130 | 1830 | 115
49 | Fenchuganj | 137 | 700 | 133 | 1800 | Amnura | 132 | 1830 | 119
50 | Khulawara | 135 | 800 | 132 | 1830 | Pabna | 137 | 900 | 124
51 | Sylhet | 136 | 600 | 132 | 1900 | Shahjadpur | 142 | 700 | 132
52 | Chatak | 137 | 500 | 131 | 1900 | Serajganj | 137 | 100 | 127
53 | Sunamganj | 137 | 600 | 130 | 1900 | Niyamatpur | 131 | 700 | 114
54 | Biani Bazar | 136 | 600 | 130 | 1900 | Joypurhat | 134 | 600 | 116
55 | Comilla(s) | 130 | 700 | 120 | 1900 | Mohastangor | 135 | 600 | 122
56 | Comilla(n) | 135 | 700 | 130 | 2200 | Rangpur | 132 | 700 | 115
57 | Chandpur | 133 | 1600 | 125 | 2100 | Lalmonirhat | 131 | 600 | 107
58 | Feni | 127 | 700 | 120 | 2100 | Saidpur | 132 | 700 | 114
59 | Chowmuhani | 124 | 900 | 113 | 2100 | Purbasadipur | 130 | 600 | 112
60 | Ashuganj | 140 | 600 | 135 | 1300 | Thakurgaon | 126 | 600 | 100
61 | Daudkandi | 132 | 700 | 125 | 1300 | Palashbari | 131 | 700 | 117
62 | B.Baria | 136 | 2100 | 130 | 1700 | Barapukuria | 135 | 600 | 122

## L-Curve
Date | 2019-05-18
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 180 | 7290 | 3507 | 10797 |  |  |  | QF-LDC-12
0:30 | 145 | 6523 | 3194.5 | 9717.5 | Date: | 2019-05-18
1:00 | 110 | 5756 | 2882 | 8638
1:30 | 120 | 5680.5 | 2841 | 8521.5
2:00 | 130 | 5605 | 2800 | 8405
2:30 | 120 | 5630 | 2806 | 8436 | [5 empty] | Gen. at Eve. Peak | 11179 | 10933 MW (20:00 )
3:00 | 110 | 5655 | 2812 | 8467 | [6 empty] | 19:30
3:30 | 95 | 5623.5 | 2786 | 8409.5 | [5 empty] | Gen. at Day Peak | 8583.3 | 8751.9 MW (12:00 )
4:00 | 80 | 5592 | 2760 | 8352 | [6 empty] | 12:00
4:30 | 60 | 5309 | 2661 | 7970 | [5 empty] | Highest Generation | 11179
5:00 | 40 | 5026 | 2562 | 7588 | [6 empty] | 19:30
5:30 | 40 | 4934.3 | 2415 | 7349.3
6:00 | 40 | 4842.6 | 2268 | 7110.6
6:30 | 30 | 4814.55 | 2243 | 7057.55
7:00 | 20 | 4786.5 | 2218 | 7004.5
7:30 | 80 | 4928.95 | 2230 | 7158.95
8:00 | 140 | 5071.4 | 2242 | 7313.4
8:30 | 130 | 5156.45 | 2244 | 7400.45
9:00 | 120 | 5241.5 | 2246 | 7487.5
9:30 | 110 | 5447.45 | 2256.5 | 7703.95
10:00 | 100 | 5653.4 | 2267 | 7920.4
10:30 | 70 | 5805.6 | 2263.5 | 8069.1
11:00 | 40 | 5957.8 | 2260 | 8217.8
11:30 | 85 | 6137.55 | 2263 | 8400.55
12:00 | 130 | 6317.3 | 2266 | 8583.3
12:30 | 215 | 6505.1 | 2343 | 8848.1
13:00 | 300 | 6692.9 | 2420 | 9112.9
13:30 | 310 | 6880.65 | 2433.5 | 9314.15
14:00 | 320 | 7068.4 | 2447 | 9515.4
14:30 | 330 | 7150.2 | 2549.5 | 9699.7
15:00 | 340 | 7232 | 2652 | 9884
15:30 | 260 | 7181.25 | 2709 | 9890.25
16:00 | 180 | 7130.5 | 2766 | 9896.5
16:30 | 190 | 7045.1 | 2709 | 9754.1
17:00 | 200 | 6959.7 | 2652 | 9611.7
17:30 | 180 | 6830.85 | 2670.5 | 9501.35
18:00 | 160 | 6702 | 2689 | 9391
18:30 | 180 | 6918.5 | 3004 | 9922.5
19:00 | 200 | 7135 | 3319 | 10454
19:30 | 240 | 7634 | 3545 | 11179
20:00 | 260 | 7393 | 3558 | 10951 |  |  |  | Executive Engineer
20:30 | 260 | 7217.5 | 3573 | 10790.5 |  |  |  | Network Operation Division
21:00 | 260 | 7042 | 3588 | 10630
21:30 | 260 | 7123 | 3529 | 10652
22:00 | 260 | 7204 | 3470 | 10674 |  |  |  |  | Page 6 of 7
22:30 | 240 | 7301.5 | 3516 | 10817.5
23:00 | 220 | 7399 | 3562 | 10961
23:30 | 200 | 7344.5 | 3534.5 | 10879
24:00 | 180 | 7290 | 3507 | 10797
10933 MW (20:00 )
8751.9 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2019-05-18 |  | Energy | 217644117
[10 empty] | 2019-05-18 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 4791 | 922 | 2330 | 1942 | 264 | 36 | 366 | 0 | 146
0:30 | 4453 | 930.5 | 2005 | 1684.5 | 265 | 34 | 221.5 | 0 | 124 | Date: | 2019-05-18
1:00 | 4115 | 939 | 1680 | 1427 | 266 | 32 | 77 | 0 | 102
1:30 | 4108 | 933.5 | 1690.5 | 1323 | 266 | 32 | 66.5 | 0 | 102 | [7 empty] | Total Energy | 217.6441 | Total Energy Gen 165.409 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 165.409 MKWHr
2:00 | 4101 | 928 | 1701 | 1219 | 266 | 32 | 56 | 0 | 102 | [7 empty] | Energy not Served | 0
2:30 | 4108 | 928.5 | 1712.5 | 1227 | 266 | 32 | 56 | 0 | 106 | [7 empty] | Energy Requirement | 217.6441
3:00 | 4115 | 929 | 1724 | 1235 | 266 | 32 | 56 | 0 | 110
3:30 | 4148.5 | 929 | 1730 | 1144 | 266 | 32 | 56 | 0 | 104 | [6 empty] | Shortage
4:00 | 4182 | 929 | 1736 | 1053 | 266 | 32 | 56 | 0 | 98
4:30 | 4077 | 929 | 1582 | 936.5 | 266 | 32 | 51.5 | 0 | 96
5:00 | 3972 | 929 | 1428 | 820 | 266 | 32 | 47 | 0 | 94
5:30 | 3865 | 929.5 | 1411.5 | 718 | 266 | 32 | 35 | 0 | 92
6:00 | 3758 | 930 | 1395 | 616 | 266 | 32 | 23 | 0 | 90
6:30 | 3794.5 | 930 | 1364 | 568.5 | 265 | 32 | 11.5 | 0 | 90 |  |  |  |  | Coal
7:00 | 3831 | 930 | 1333 | 521 | 264 | 32 | 0 | 0 | 90
7:30 | 3960.5 | 930 | 1330 | 543.5 | 264 | 32 | 0 | 0 | 95 |  |  |  | Oil |  |  |  | ,
8:00 | 4090 | 930 | 1327 | 566 | 264 | 32 | 0 | 0 | 100
8:30 | 4112.5 | 930 | 1345 | 603 | 263.5 | 32 | 0 | 0 | 104
9:00 | 4135 | 930 | 1363 | 640 | 263 | 32 | 0 | 0 | 108
9:30 | 4218 | 930 | 1457 | 679 | 263 | 32.5 | 0 | 0 | 108
10:00 | 4301 | 930 | 1551 | 718 | 263 | 33 | 0 | 0 | 108
10:30 | 4303 | 930 | 1562.5 | 842 | 263.5 | 33 | 0 | 0 | 118
11:00 | 4305 | 930 | 1574 | 966 | 264 | 33 | 0 | 0 | 128
11:30 | 4244 | 930 | 1671.5 | 1106.5 | 264 | 32.5 | 3 | 0 | 131
12:00 | 4183 | 930 | 1769 | 1247 | 264 | 32 | 6 | 0 | 134
12:30 | 4239.5 | 930 | 1841.5 | 1370 | 263.5 | 32 | 17.5 | 0 | 136
13:00 | 4296 | 930 | 1914 | 1493 | 263 | 32 | 29 | 0 | 138
13:30 | 4296 | 930 | 1914 | 1493 | 263 | 32 | 29 | 0 | 138
14:00 | 4296 | 930 | 1914 | 1493 | 263 | 32 | 29 | 0 | 138
14:30 | 4309 | 930 | 1933.5 | 1795.5 | 263 | 31 | 70.5 | 0 | 150
15:00 | 4322 | 930 | 1953 | 2098 | 263 | 30 | 112 | 0 | 162
15:30 | 4328.5 | 930.5 | 1916.5 | 2134 | 263.5 | 30 | 116 | 0 | 160
16:00 | 4335 | 931 | 1880 | 2170 | 264 | 30 | 120 | 0 | 158
16:30 | 4339 | 930.5 | 1925 | 1973.5 | 264 | 30 | 133 | 0 | 153
17:00 | 4343 | 930 | 1970 | 1777 | 264 | 30 | 146 | 0 | 148
17:30 | 4292.5 | 931 | 1867.5 | 1796.5 | 263 | 33 | 166 | 0 | 150
18:00 | 4242 | 932 | 1765 | 1816 | 262 | 36 | 186 | 0 | 152
18:30 | 4194 | 931.5 | 1760.5 | 2168 | 263 | 36.5 | 402 | 0 | 167
19:00 | 4146 | 931 | 1756 | 2520 | 264 | 37 | 618 | 0 | 182
19:30 | 4125 | 931 | 1963 | 2956 | 264 | 37 | 735 | 0 | 168
20:00 | 4118 | 930 | 1931 | 2811 | 264 | 38 | 693 | 0 | 166
20:30 | 4287.5 | 930.5 | 2090.5 | 2441.5 | 263.5 | 38 | 570 | 0 | 169
21:00 | 4457 | 931 | 2250 | 2072 | 263 | 38 | 447 | 0 | 172
21:30 | 4599.5 | 931 | 2245 | 1993.5 | 263 | 38 | 415 | 0 | 167
22:00 | 4742 | 931 | 2240 | 1915 | 263 | 38 | 383 | 0 | 162
22:30 | 4805 | 931 | 2294 | 1944.5 | 263.5 | 37 | 383.5 | 0 | 159
23:00 | 4868 | 931 | 2348 | 1974 | 264 | 36 | 384 | 0 | 156
23:30 | 4829.5 | 926.5 | 2339 | 1958 | 264 | 36 | 375 | 0 | 151 | Max Temp. in Dhaka |  | 35.5° C
24:00 | 4791 | 922 | 2330 | 1942 | 264 | 36 | 366 | 0 | 146
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 165.409 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 165.409 MKWHr
Note on W13: Author:

## Generation
2019-05-18
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Kaptai Unit-1, 2 & 3 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 33 | 33 | 32 | 32 | 32 | 30 | 30 | 30 | 36 |  | 37 | 37 | 38 | 38 | 38 | 36 | 36 | 735240
2 | Kaptai Unit-4 & 5
3 | Chattogram ST-1 (Raozan)
4 | Chittgong ST-2 (Raozan) | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3700000
5 | Raozan 25 MW (RPCL) | 25 | 8 | 8 | 8 | 8 | 8 | 0 | 0 |  | 5 | 25 | 25 | 25 | 25 | 25 | 25 | 0 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 418165
| Teknaf Solartech 20MW |  |  |  |  | 0 | 0.6 | 3.4 | 3.7 | 16 | 15.5 | 15.8 | 17.4 | 17.1 | 15.8 | 12.3 | 7.5 | 3.2 | 0 |  | 0 | [6 empty] | 124470
6 | Sikalbaha 225MW (Gas) | 203 | 203 | 203 | 203 | 203 | 203 | 205 | 231 | 229 | 225 | 230 | 226 | 230 | 227 | 231 | 232 | 228 | 229 |  | 231 | 230 | 229 | 230 | 230 | 229 | 230 | 5264635
7 | Sikalbaha 225MW (Oil)
8 | Sikalbaha ST 60MW
9 | Sikalbaha GT 150MW (Gas) | 90 | 90 | 90 | 90 | 90 | 90 | 130 | 140 | 143 | 146 | 145 | 145 | 145 | 145 | 135 | 100 | 100 | 101 |  | 100 | 100 | 100 | 131 | 131 | 140 | 137 | 2854630
10 | Sikalbaha GT 150MW (Oil)
| Dohazari Peaking | [19 empty] | 25 | 85 | 85 | 85 | 34 | 34 | 34 | 273192
12 | Hathazari peaking | [17 empty] | 3 |  | 85 | 85 | 85 | 0 |  |  |  | 171048
Baraka Sikalbaha PL
Daudkandi bangla trak
14 | Daudkandi Peaking 52MW | [15 empty] | 4 | 8 | 8 |  | 8 | 0 | [5 empty] | 25944
15 | Siddhirgonj ST 210MW
16 | Siddhirgonj GT Unit-1& 2 | 125 | 125 | 125 | 125 | 125 | 100 | 100 | 100 | 100 | 150 | 150 | 185 | 189 | 187 | 142 | 139 | 100 | 100 |  | 76 | 76 | 74 | 120 | 160 | 195 | 185 | 3304000
17 | Siddhirganj CCPP-335 MW
18 | Summit Gazipur -2 | [19 empty] | 60 | 140 | 120 | 0 |  |  |  | 198218
19 | Ashuganj 195MW Modular | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 |  | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 1555636
20 | Ghorasal ST: Unit-1,2 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 |  | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 1672000
21 | Ghorasal GT: Unit-3 | [15 empty] | 34 | 43 | 43 |  | 140 | 145 | 189 | 204 | 208 | 209 | 209 | 1218600
22 | Ghorasal GT: Unit-4 | [12 empty] | 100 | 141 | 140 | 140 | 140 | 140 |  | 140 | 140 | 140 | 120 | 130 | 130 | 130 | 1525000
23 | Ghorasal ST: Unit-5
24
25 | Ghorasal ST: Unit-7 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 330 | 330 | 340 | 380 | 370 | 370 | 340 | 300 | 260 | 260 | 260 |  | 260 | 260 | 260 | 300 | 330 | 350 | 363 | 7076455
26
28 | Ashuganj ST: Unit- 3
29 | Ashuganj ST: Unit- 4
30 | Ashuganj ST: Unit- 5
32 | Ashuganj Engines TSK | 36 | 36 | 33 | 30 | 30 | 30 | 30 | 30 | 30 | 27 | 30 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 736920
33 | Ashuganj CCPP 225 MW | 183 | 183 | 190 | 198 | 183 | 158 | 172 | 201 | 199 | 203 | 185 | 198 | 194 | 190 | 184 | 184 | 191 | 198 |  | 184 | 185 | 184 | 199 | 204 | 205 | 182 | 4667000
34 | Ashuganj CCPP(South) | 300 | 300 | 300 | 300 | 300 | 270 | 270 | 270 | 300 | 353 | 353 | 350 | 345 | 345 | 345 | 350 | 342 | 345 |  | 300 | 300 | 300 | 300 | 360 | 360 | 360 | 7797000
| Ashuganj CCPP(North) | 260 | 260 | 260 | 260 | 220 | 200 | 200 | 250 | 250 | 250 | 250 | 240 | 240 | 240 | 240 | 240 | 240 | 240 |  | 180 | 180 | 180 | 180 | 250 | 250 | 250 | 5875500
35 | Ashuganj (Precision) 55MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 389280
36 | Chandpur CCPP | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2337520
37 | Tongi GT
38 | Haripur GT: Unit-1, 2
39 | Haripur 412 MW CCPP | 325 | 325 | 326 | 348 | 326 | 326 | 336 | 350 | 350 | 358 | 342 | 347 | 340 | 366 | 335 | 327 | 349 | 334 |  | 342 | 350 | 330 | 348 | 355 | 378 | 343 | 8334330
40 | Meghnaghat CCPP 450MW | 350 | 350 | 350 | 350 | 350 | 320 | 320 | 320 | 350 | 400 | 400 | 450 | 450 | 450 | 450 | 340 | 340 | 340 |  | 300 | 300 | 300 | 390 | 390 | 430 | 430 | 8755875
41 | Haripur Power CCPP 360MW | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 305 | 352 | 345 | 344 | 343 | 339 | 339 | 289 | 289 | 289 |  | 259 | 259 | 258 | 354 | 354 | 351 | 355 | 7355000
42 | Mymensingh RPCL 210MW | 155 | 152 | 153 | 152 | 153 | 152 | 151 | 150 | 152 | 151 | 151 | 149 | 149 | 149 | 149 | 150 | 149 | 150 |  | 150 | 152 | 152 | 152 | 152 | 153 | 153 | 3555120
43 | Haripur NEPC 110MW | [19 empty] | 55 | 55 | 13 | 0 |  |  |  | 73600
44 | Fenchugonj CCPP-1 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 57 | 58 | 58 | 60 | 52 | 51 | 54 | 54 | 54 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1375000
45 | Fenchugonj CCPP-2 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 |  | 48 | 48 | 48 | 60 | 60 | 60 | 48 | 1171412
46 | Shajibazar 330 MW | 313 | 312 | 317 | 313 | 312 | 289 | 290 | 315 | 325 | 315 | 310 | 311 | 318 | 316 | 310 | 312 | 313 | 316 |  | 313 | 311 | 312 | 313 | 326 | 318 | 314 | 7220000
47 | Shahjibazar GT: Unit- 8, 9 | 66 | 65 | 66 | 66 | 66 | 66 | 66 | 66 | 64 | 64 | 64 | 63 | 63 | 61 | 50 | 62 | 61 | 61 |  | 63 | 63 | 40 | 65 | 64 | 65 | 62 | 1499808
48 | Shahjibazar 86MW | 50 | 47 | 50 | 50 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 30 | 50 | 84 | 84 | 85 | 85 | 0 |  | 10 | 84 | 86 | 86 | 87 | 87 | 87 | 1137600
49 | Shahjibazar (EPL) 50MW | 46 | 46 | 46 | 46 | 10 | 10 | 10 | 10 | 10 | 44 | 44 | 45 | 45 | 45 | 45 | 46 | 46 | 10 |  | 10 | 44 | 46 | 46 | 46 | 46 | 46 | 848520
50 | Sylhet GT 150 MW | 110 | 110 | 120 | 120 | 75 | 75 | 76 | 80 | 82 | 87 | 74 | 75 | 90 | 85 | 73 | 73 | 82 | 82 |  | 73 | 75 | 73 | 85 | 85 | 85 | 74 | 2183050
51 | Sylhet GT 20 MW | 19 | 19 | 19 | 19 | 0 | [18 empty] | 19 | 19 | 19 | 123000
52 | Sylhet (EPL) 50MW | 43 | 43 | 43 | 43 | 12 | 12 | 12 | 12 | 12 | 12 | 41 | 42 | 41 | 40 | 40 | 42 | 44 | 12 |  | 38 | 45 | 45 | 44 | 45 | 44 | 43 | 791020
53 | Sylhet (Desh) 10MW | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 248040
54 | Hobiganj 11MW | 11 | 11 | 3 | 3 | 8 | 8 | [8 empty] | 2 | 8 | 8 | 11 |  | 11 | 11 | 11 | 10 | 11 | 11 | 11 | 126288
55 | Fenchugonj (Barakatullah) 51MW | 47 | 47 | 47 | 47 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 26 | 50 | 50 | 50 | 50 | 48 | 22 |  | 17 | 46 | 52 | 53 | 50 | 50 | 50 | 841800
56 | Shahjahanulla 25 MW | 24 | 24 | 22 | 22 | 22 | 22 | 16 | 21 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 25 | 24 | 555024
57 | Summit Bibiana- 2 | 255 | 255 | 275 | 285 | 250 | 255 | 280 | 285 | 280 | 270 | 260 | 275 | 275 | 290 | 265 | 250 | 280 | 290 |  | 240 | 280 | 235 | 290 | 290 | 300 | 280 | 6807500
58 | Southern 55MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 35 | 50 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 852580
59 | Sikalbaha (Energis) | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 30 | 16 | 16 | 16 | 16 | 16 | 22 |  | 33 | 33 | 33 | 33 | 32 | 33 | 33 | 705600
60 | Barabkunda (Regent) | 14 | 14 | 14 | 14 | 14 | 14 | 13 | 13 | 14 | 14 | 14 | 14 | 13 | 14 | 13 | 11 | 11 | 13 |  | 14 | 14 | 14 | 13 | 13 | 13 | 13 | 323472
61 | Narshingdi (Doreen) | 19 |  | 0 | 0 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 0 | 0 | 10 | 19 | 19 | 0 | 0 |  | 19 | 19 | 19 | 0 |  |  |  | 236340
62 | Tangail (Doreen) 22MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 20 | 20 | 17 | 17 | 17 | 17 | 17 | 17 |  | 0 | 0 | 0 | 0 |  | 20 | 20 | 333972
63 | Tripura | 102 | 102 | 110 | 98 | 94 | 90 | 90 | 100 | 108 | 108 | 128 | 134 | 138 | 142 | 162 | 158 | 148 | 152 |  | 182 | 168 | 166 | 172 | 162 | 156 | 146 | 3095040
64 | Malancha, Ctg. EPZ (United) | 34 | 42 | 42 | 42 | 42 | 38 | 19 | 12 | 3 | 2 | 3 | 2 | 12 | 6 | 3 | 7 | 8 | 24 |  | 34 | 35 | 35 | 36 | 39 | 38 | 38 | 557760
65 | Feni (Doreen) 22MW | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 0 | 0 | 0 | [15 empty] | 150552
66 | Feni, Mohipal (Doreen) | 0 | 11 | 11 | 11 | 11 | 11 | 11 | 0 | 11 | 11 | 0 | 11 | 11 | 11 | 11 | 11 | 11 | 0 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 226620
67 | Jangalia (Summit) 33MW | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 820300
68 | Summit Cumilla 25MW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 6 | 0 | 2 | 8 | 15 | 20 | 15 | 15 |  | 20 | 21 | 21 | 8 | 9 | 9 | 9 | 164200
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 26 | 26 | 18 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 25 | 23 | 23 | 23 | 26 | 26 | 23 |  | 14 | 22 | 24 | 11 | 24 | 28 | 28 | 537660
71 | Summit Maona | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 17 | 17 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 0 | 0 |  |  |  | 33 | 473400
72 | Summit Rupganj | 30 | 30 | 30 | 30 | 29 | 29 | 29 | 29 | 29 | 12 | 29 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 35 | 33 | 734900
73 | Ghorashal (Regent) | 42 | 42 | 42 | 42 | 12 | 12 | 12 | 12 | 12 | 52 | 51 | 85 | 100 | 101 | 101 | 104 | 106 | 106 |  | 106 | 106 | 107 | 107 | 107 | 108 | 108 | 1612090
76 | Siddhirganj Desh
77 | Siddhirganj (Dutch Bangla) | [19 empty] | 20 | 50 | 30 | 0 |  |  |  | 72000
78 | Gazipur (RPCL) | [5 empty] | 0 | 2 | 24 | 24 | 24 | 37 | 48 | 48 | 48 | 0 | 9 | 48 | 48 |  | 48 | 48 | 48 | 50 | 50 | 50 | 49 | 694848
79 | Kodda 149MW | [13 empty] | 0 | 82 | 80 | 80 | 80 |  | 140 | 149 | 98 | 0 |  |  |  | 537120
80 | Jamalpur 95MW | 8 | 8 | 8 | 0 | [10 empty] | 37 | 50 | 28 | 28 |  | 42 | 60 | 50 | 16 | 16 | 16 | 8 | 371520
81 | Lakdhanvi 52 MW | [10 empty] | 4 | 25 | 43 | 52 | 52 | 8 | 8 | 8 |  | 16 | 34 | 34 | 0 |  | 6 | 25 | 340488
Gazipur 100 MW
82 | Madanganj 102MW | [17 empty] | 3 |  | 48 | 64 | 55 | 0 |  |  |  | 132024
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj (Powerpac) 100MW | [17 empty] | 0 |  | 35 | 60 | 50 | 0 |  |  |  | 105675
86 | Meghnaghat CCPP(Summit) | 252 | 265 | 280 | 285 | 267 | 280 | 290 | 290 | 290 | 300 | 285 | 280 | 275 | 285 | 265 | 263 | 285 | 290 |  | 272 | 270 | 260 | 290 | 295 | 300 | 250 | 6849484
87 | Meghnaghat (IEL) | [13 empty] | 0 | 50 | 100 | 56 | 56 |  | 56 | 56 | 50 | 0 |  |  |  | 399360
88 | Ghorashal 78MW (MAX) | 60 | 77 | 76 | 76 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 50 | 70 | 69 | 68 | 68 | 68 | 69 |  | 69 | 69 | 70 | 74 | 0 |  |  | 1271648
90 | Ashuganj (United) 53MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 120000
91 | Juldah (Acorn) | 78 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 50 | 88 | 88 | 40 | 40 |  | 88 | 88 | 100 | 10 | 10 | 50 | 60 | 775080
92 | Fenchuganj (EPL) 44MW | 50 | 50 | 50 | 50 | 10 | 10 | 10 | 10 | 10 | 10 | 20 | 50 | 50 | 50 | 50 | 50 | 50 | 0 |  | 10 | 30 | 32 | 50 | 50 | 50 | 50 | 832000
93 | Ashuganj (Midland) 51MW | 45 | 45 | 45 | 45 | 45 | 45 | 10 | 10 | 10 | 10 | 10 | 15 | 33 | 45 | 45 | 45 | 45 | 45 |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 867806
94 | Gagnagar (Orion) | [9 empty] | 3 | 16 | 30 | 50 | 60 | 85 | 100 | 100 | 100 |  | 100 | 100 | 50 | 0 |  |  |  | 751824
95 | Patenga 50MW | 43 | 46 | 47 | 46 | 46 | 43 | 6 | 5 | 25 | 38 | 39 | 39 | 42 | 45 | 38 | 37 | 46 | 46 |  | 46 | 43 | 43 | 46 | 46 | 46 | 46 | 948960
96 | Chattogram ECPV 108 MW | 71 | 18 | 18 | 18 | 18 | 12 | 12 | 12 | 43 | 73 | 92 | 90 | 90 | 97 | 96 | 97 | 103 | 103 |  | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 1712640
97 | Katpotti 51 MW | 48 | 48 | 48 | 48 | 18 | 18 | 18 | 18 | 18 | 18 | 37 | 46 | 47 | 48 | 47 | 47 | 24 | 24 |  | 30 | 30 | 47 | 47 | 47 | 46 | 47 | 950208
98 | Bosila 108MW | 51 | 51 | 51 | 0 | 0 | 0 | 0 | 0 |  | 0 | 51 | 62 | 61 | 59 | 60 | 59 | 60 | 62 |  | 61 | 64 | 64 | 64 | 65 | 65 | 66 | 985920
99 | Madanganj-55 MW | [15 empty] | 13 | 15 | 15 |  | 32 | 55 | 55 | 0 |  |  |  | 141442
100 | Northern 55 MW | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 36 | 36 | 56 | 56 | 56 | 56 | 56 |  | 56 | 56 | 56 | 56 | 18 | 18 | 18 | 791069
101 | Kushiara 163 MW CCPP GT | 130 | 130 | 130 | 130 | 130 | 130 | 100 | 100 | 100 | 130 | 130 | 130 | 163 | 163 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 163 | 163 | 163 | 3281514
102 | Sarishabari (Solar) | [5 empty] | 0 | 0.1 | 0.7 | 0.5 | 0.9 | 2 | 0.9 | 0.8 | 1.6 | 1.7 | 1 | 0.5 | 0 |  | 0 | 0 | 0 | 0 |  |  |  | 10100
103 | Banco Energy 54MW | [13 empty] | 10 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 358200
104 | APR Energy , Keranigonj | [13 empty] | 75 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
105 | Bramhangoan 100 MW (Aggreko)
106 | United Mymensingh PPL | 7 | 7 | 7 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 7 | 7 | 7 | 7 |  | 7 | 7 | 7 | 0 |  |  |  | 79200
112 | Aggreko Aurahati 100MW | [13 empty] | 50 | 0 | 0 | [10 empty] | 30655
114 | Summit Gazipur-1 150MW | [7 empty] | 8 | 17 | 17 | 36 | 50 | 50 | 66 | 72 | 100 | 102 | 100 |  | 125 | 135 | 125 | 42 | 35 | 35 | 35 | 1029600
115 | Juldah 100 MW Unit-3 | 100 | 100 | 100 | 100 | 100 | 70 | 50 | 65 | 80 | 80 | 90 | 90 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2217600
116 | Chandpur Desh 200MW | 34 | 34 | 34 | 20 | 0 | [5 empty] | 18 | 35 | 70 | 80 | 140 | 180 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 197 | 2261280
117 | Midland 150MW | 50 | 12 | 12 | 0 | 0 | 0 | 0 | 0 |  | 0 | 3 | 33 | 70 | 90 | 135 | 100 | 50 | 50 |  | 90 | 100 | 100 | 0 |  |  |  | 849750
118 | Bibiyana-3 285 MW | 119 | 119 | 119 | 120 | 70 | 69 | 70 | 71 | 71 | 120 | 120 | 120 | 120 | 120 | 299 | 299 | 296 | 200 |  | 150 | 150 | 151 | 300 | 300 | 297 | 303 | 3914800
| United Jamalpur PPL | 50 | 50 | 50 | 50 | 8 | 8 | 8 | 8 | 8 | 24 | 98 | 98 | 100 | 100 | 100 | 100 | 50 | 50 |  | 70 | 98 | 100 | 100 | 100 | 100 | 100 | 1605600
120 | Eastern Zone Total | 5756 | 5605 | 5655 | 5592 | 5026 | 4842.6 | 4786.5 | 5071.4 | 5241.5 | 5653.4 | 5957.8 | 6317.3 | 6692.9 | 7068.4 | 7232 | 7130.5 | 6959.7 | 6702 |  | 7135 | 7634 | 7393 | 7042 | 7204 | 7399 | 7290 | 151636341
121
122
123 | Khulna 60MW
124 | Khulna (KPCL-1 & 3)
125 | Khulna (KPCL-2) | 115 | 115 | 115 | 115 | 112 | 32 | 16 | 16 | 16 | 16 | 16 | 35 | 66 | 95 | 99 | 99 | 49 | 49 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 1816320
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur Peaking | 22 | 9 | 9 | 9 | 0 | [11 empty] | 5 | 19 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 198240
Khulna CCPP 225MW
129 | Labon Chora 105 MW | 70 | 70 | 70 | 70 | 53 | 17 | 17 | 17 | 17 | 17 | 17 | 36 | 72 | 54 | 72 | 90 | 53 | 53 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 1497120
130
131
132
133
| Summit Barisal 110 MW | 80 | 32 | 32 | 16 | 0 | [8 empty] | 16 | 48 | 48 | 48 | 48 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 109920
136 | Barisal GT: Unit-1, 2 | [20 empty] | 10 | 12 | 0 |  |  |  | 6591
137 | Bhola Aggreko 95MW | 97 | 96 | 96 | 97 | 95 | 96 | 96 | 95 | 96 | 93 | 93 | 94 | 94 | 92 | 93 | 94 | 96 | 96 |  | 96 | 96 | 97 | 97 | 96 | 98 | 98 | 2298922
| Bhola CCPP 194MW | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 176 | 176 | 176 | 176 | 176 | 175 | 175 | 175 |  | 176 | 175 | 175 | 175 | 175 | 175 | 175 | 4305603
140 | Bhola (Venture) 33MW | 38 | 38 | 38 | 38 | 34 | 29 | 26 | 25 | 19 | 20 | 21 | 18 | 24 | 24 | 26 | 23 | 24 | 21 |  | 31 | 33 | 32 | 37 | 37 | 37 | 36 | 676398
141 | Bangla Trak Noapara | 60 | 60 | 60 | 60 | 0 | [8 empty] | 7 | 0 |  |  |  |  | 2 | 57 | 77 | 100 | 100 | 100 | 100 | 836160
142 | Noapara (KZA) 40MW | 32 | 32 | 32 | 32 | 32 | 16 | 8 | 8 | 8 | 8 | 8 | 32 | 32 | 32 | 32 | 24 | 8 | 8 |  | 40 | 40 | 40 | 40 | 32 | 40 | 40 | 603750
143 | Gopalganj Peaking | 8 | 0 | [14 empty] | 16 | 34 |  | 48 | 63 | 52 | 51 | 49 | 50 | 50 | 370048
144 | Bheramara GT-1,2,3 | [19 empty] | 32 | 32 | 48 | 44 | 32 | 32 | 14 | 191500
145 | Madhumati Power Plant | 108 | 108 | 108 | 108 | 81 | 35 | 17 | 18 | 17 | 18 | 17 | 72 | 107 | 90 | 105 | 90 | 53 | 53 |  | 53 | 107 | 106 | 105 | 105 | 105 | 104 | 1835200
146 | Bheramara HVDC | 939 | 928 | 929 | 929 | 929 | 930 | 930 | 930 | 930 | 930 | 930 | 930 | 930 | 930 | 930 | 931 | 930 | 932 |  | 931 | 931 | 930 | 931 | 931 | 931 | 922 | 22317818
147 | Bheramara 360 MW
148
149
150 | Barapukuria Unit-1
151 | Barapukuria Unit-2 | 67 | 67 | 67 | 67 | 67 | 67 | 65 | 65 | 64 | 64 | 65 | 65 | 64 | 64 | 64 | 64 | 64 | 63 |  | 65 | 65 | 65 | 64 | 64 | 65 | 65 | 1555636
152 | Barapukuria Unit-3 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 200 | 200 | 199 |  | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 4853900
153 | Baghabari GT 71MW | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 0 | 0 |  | 0 | 50 | 50 | 55 |  | 55 | 55 | 55 | 55 | 55 | 60 | 60 | 1148000
156 | Baghabari GT 100MW | 105 | 102 | 102 | 102 | 103 | 103 | 102 | 102 | 102 | 101 | 100 | 0 | 0 | [13 empty] | 1185000
| Baghabari Peaking 50MW | [19 empty] | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 284494
157 | Sirajgonj Unit-1 225MW (Gas) | 180 | 181 | 184 | 198 | 182 | 156 | 166 | 173 | 174 | 177 | 195 | 202 | 197 | 198 | 190 | 184 | 195 | 195 |  | 186 | 175 | 180 | 192 | 196 | 204 | 194 | 4773164
158 | Sirajgonj Unit-1 225MW (Oil) | [24 empty] | 0
| Sirajgonj Unit-2 225MW (Gas) | 184 | 185 | 188 | 200 | 186 | 147 | 157 | 170 | 177 | 169 | 166 | 177 | 166 | 176 | 154 | 146 | 159 | 156 |  | 153 | 152 | 147 | 158 | 165 | 170 | 163 | 4218455
Sirajgonj Unit-2 225MW (Oil)
159 | Sirajgonj Unit-3 225 MW(Gas) | 186 | 186 | 190 | 204 | 188 | 164 | 165 | 172 | 175 | 203 | 180 | 179 | 180 | 179 | 160 | 154 | 167 | 165 |  | 161 | 162 | 156 | 174 | 176 | 178 | 169 | 4441218
| Sirajgonj Unit-3 225 MW(Oil) | [14 empty] | 0 | [10 empty] | 0
160 | Sirajgonj Unit-4 414 MW(Gas) | [14 empty] | 53 | 146 | 200 | 200 |  | 250 | 250 | 250 | 300 | 300 | 360 | 360 | 2233090
161 | Bera Peaking | [17 empty] | 5 |  | 17 | 27 | 26 | 26 | 26 | 26 | 26 | 132873
162 | Bogra (GBB) | 22 | 22 | 22 | 22 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 410880
163 | Bogra (EPL) | 8 | 8 | 9 | 10 | 10 | 10 | 10 | 8 | 8 | 8 | 8 | 8 | 9 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 225540
164 | Ullapara (Summit) |  |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 5 | 5 | 5 | 0 | 5 | 5 | 8 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 109332
165 | Amnura 50MW | 24 | 24 | 24 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 24 | 24 | 40 | 50 | 24 | 24 |  | 50 | 50 | 40 | 50 | 50 | 50 | 50 | 552190
166 | Katakhali (Northern) | [19 empty] | 25 | 50 | 50 | 16 | 16 | 16 | 16 | 121209
167 | Katakhali Peaking | [19 empty] | 30 | 42 | 47 | 0 |  |  |  | 64327
168 | Santahar Peaking | [11 empty] | 6 | 6 | 6 | 7 | 6 | 7 | 7 |  | 36 | 42 | 42 | 42 | 42 | 42 | 41 | 268690
169 | Rajlanka 52 MW | [11 empty] | 10 | 24 | 29 | 48 | 16 | 8 | 8 |  | 42 | 50 | 52 | 51 | 50 | 50 | 50 | 410400
170 | Chapainawabganj-100 MW | 47 | 47 | 47 | 47 | 47 | 23 | 0 | 0 |  |  |  |  | 23 | 23 | 23 | 30 | 30 | 30 |  | 90 | 93 | 91 | 91 | 93 | 93 | 93 | 934868
171 | Paramount Baghabari
172 | Confidence CPBL-2 | 54 | 54 | 54 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 95 | 108 | 50 | 50 |  | 70 | 108 | 108 | 108 | 0 |  |  | 841920
173 | Rangpur GT | 0 | [18 empty] | 16 | 16 | 16 | 17 | 16 | 16 | 17 | 90000
175 | Saidpur GT | 0 | [18 empty] | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 89000
176
177
178
178 | Western Zone Total | 2882 | 2800 | 2812 | 2760 | 2562 | 2268 | 2218 | 2242 | 2246 | 2267 | 2260 | 2266 | 2420 | 2447 | 2652 | 2766 | 2652 | 2689 | 0 | 3319 | 3545 | 3558 | 3588 | 3470 | 3562 | 3507 | 66007776