## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2022-11-18 | Friday
|  | Date (day): | 2022-11-18 |  | Friday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 9749.6 | MW |  |  | (b) At Evening Peak Hour : |  | 11340 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2022-11-17 | 2022-11-18 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Line O/L
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Under maint
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 70 | 71 | 70 | 71 | 37 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 371 | 372 | 350 | 372 | 40 |  | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 322 | 307 | 300 | 307 | 53 |  | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 225 | 225 | 225 |  | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 78 | 83 | 70 | 83 |  | 17 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas line maintenance
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 0 | 0 | 0 | 0 |  | 102 | Under maint
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55 |  |  | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 71 | 78 | 75 | 78 |  | 22 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 41 | 66 | 33 | 66 |  | 36 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 35 | 17 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 98 | 133 | 100 | 133 |  | 16 | Engine problem
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 35 | 35 | 35 |  | 20 | Engine problem
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 35 | 35 | 35 |  | 20 | Engine problem
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 52 | 47 | 42 | 47 |  | 33 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 24 | 24 | 20 | 24 |  | 9 | Engine problem
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 41 | 49 | 50 | 50
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 95 | 262 | 175 | 260 |  | 40 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 40 | 20 | 100 | 150 | 150 |  | Fuel conservation
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 50 | 50 | 50 | 50 | 50 |  | Fuel conservation
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 50 | 50 | 50 | 50 | 50 |  | Fuel conservation
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 86 | 136 | 125 | 136 |  | 13 | Engine problem
36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 105 | 105 | 105 | 105
37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 55 | 66 | 55 | 55 | 49 |  | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 162 | 162 | 162 | 162
39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 28 | 0 | 30 | 0
40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 17 | 17 | 17 | 38 |  | Fuel shortage
| Dhaka area Total |  |  |  |  | 6263 | 5847 | 2498 | 2718 | 2581 | 2855 | 1623 | 1373
41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 17 | 17 | 17 | 17 |  | 8 | Engine problem
43 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 20 | 0 | 20 | 0
44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 14 | 44 | 26 | 44 |  | 6 | Engine problem
45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 46 | 80 | 80 | 80 | 150 |  | Low Water Level
46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 152 | 150 | 150 | 150 |  | 75 | ST under maint
47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 69 | 105 | 68 | 105
49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 23 | 50 | 20 | 40 | 58 |  | Fuel shortage
50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 17 | 51 | 17 | 51 | 51 |  | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 22 | 44 | 33 | 44 | 56 |  | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 25 | 40 | 25 | 40 | 60 |  | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  | 22 | Engine problem
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 0 | 2 | 10 | 20
54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 244 | 290 | 260 | 290 |  | 10 | Engine problem
57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 54 | 36 | 36 | 36 |  | 18 | Engine problem
58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 73 | 91 | 70 | 91 |  | 19 | Engine problem
59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 50 | 25 | 50 | 50 |  | Fuel shortage
60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 107 | 107 | 107 | 107 |  | 9 | Engine problem
| Mirsharai 150 MW |  | Gas/HSD | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0
| Chattogram area Total |  |  |  |  | 2442 | 2382 | 912 | 1157 | 969 | 1165 | 893 | 317
61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 184 | 199 | 0 | 0 |  | 221 | Under maint.
63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint
64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 310 | 295 | 300 | 300 | 60 |  | Gas shortage
| Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+136*1 | 284 | 284 | 288 | 268 | 288 | 288 |  |  | On test.
65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 0 | 0 | 40 | 45
66 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 55 | 0 | 0 | 30 | 30 | 25 |  | Gas shortae
67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 0 | 0 | 8 | 8 | 187 |  | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Gas shortage
69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 62 | 87 | 65 | 87 | 63 |  | Fuel shortage
70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 36 | 37 | 0 | 37 |  | 15 | Engine problem
71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 39 | 40 | 40 | 40 | 123 |  | Gas shortage.
72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 51 | 79 | 51 | 200
73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 8 | 8
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 110 | 124 | 143 | 165
75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 15 | 17 | 33 | 33
76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 28 | 8 | 28 | 24 |  | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 9 | 14 | 15 | 19 |  | 6 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 10 | 40 | 100 | 100 | 100 |  | Fuel conservation
79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 17 | 17 | 17 | 97 |  | Fuel shortage
80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 80 | 107 | 80 | 107
81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 17 |  | 37 | Engine problem
82 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 109 | 109 | 35 | 115
| Cumilla Area Total |  |  |  |  | 3193 | 3169 | 1375 | 1508 | 1300 | 1666 | 864 | 639
83 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 37 | 38 | 70 | 70 | 132 |  | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 10 | 9 | 9 | 9 | 13 |  | Gas shortage
85 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0
86 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
87 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 81 | 85 | 75 | 85 | 115 |  | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 78 | 97 | 50 | 97 |  | 18 | Engine problem
89 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 47 | 0 | 50 | 0
90 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 12 | 12 |  | 10 | Engine problem
| Mymensingh Area Total |  |  |  |  | 717 | 614 | 267 | 241 | 267.6 | 273 | 145 | 28
91 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 30 | 30 | 30 | 30 |  | 40 | Machine problem.
92 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 42 | 42 | 0 | 30 |  | 60 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 | 163 |  | Gas shortage
94 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 31 | 25 | 0 | 0 | 51 |  | Gas shortage
96 | Fenchuganj 44MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 47 | 47 | 0 | 0 | 50 |  | Gas shortage
97 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 2 | 2 | 2 | 2 | 9 |  | Gas shortage
98 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 62 | 68 | 66 | 66
99 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 0 | 78 | 0 | 80
100 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
101 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 20 | 65 | 80 | 80 | 151 |  | Gas shortage
102 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18
103 | Sylhet 50MW PP (EPL) |  | Gas | NENP | 27*2 | 50 | 50 | 21 | 28 | 0 | 0 | 50 |  | Gas shortage
104 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 0 | 0 | 0 | 0 | 25 |  | Gas shortage
105 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 280 | 280 | 300 | 300 |  |  | FGMO
106 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 423 | 422 | 400 | 400
107 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
108 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 400 | 400 | 400 | 400
| Sylhet Area Total |  |  |  |  | 2522 | 2477 | 1386 | 1515 | 1306 | 1416 | 499 | 530
109 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 904 | 904 | 922 | 922
110 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 0 | 49 | 16 | 115
111 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 35 | 0 | 35 |  | 19 | Engine problem
112 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
113 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 52 | 0 | 70 |  | 39 | Engine problem
114 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 125 | 125 | 130 | 150 | 260 |  | Gas shortage
115 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 18 | 0 | 8 | 32 |  | Fuel shortage
116 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 20 | 0 | 50 | 50 |  | Fuel conservation
117 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 95 | 95 | 0 | 95 |  | 10 | Engine problem
118 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Fuel shortage
119 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 76 | 0 | 100 | 0
| Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 0 | 0 | 0 | 0 | 230 | 230 |  |  | On test.
| Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 2388 | 2384 | 1200 | 1298 | 1398 | 1675 | 693 | 68
120 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 0 | 0 |  |  | Line O/L
121 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 17 | 20 | 12 | 20 |  | 20 | Engine problem
122 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 87 | 152 | 120 | 150 |  | 44 | Machine problem
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
123 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 490 | 580 | 800 | 800 |  |  | Line O/L
124 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 167 | 108 | 100 | 108 |  | 110 | GT-1 Under maint.
125 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 0 | 0 |  |  | Line O/L
| Barisal 307 MW |  | Coal | BCPCL | 0 | 0 | 0 | 125 | 243 | 0 | 0 |  |  | On test.
| Barisal Area Total |  |  |  |  | 1958 | 1958 | 886 | 1103 | 1032 | 1078 | 0 | 174
126 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
127 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 30 | 0 | 30 |  | 22 | Engine problem
128 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 4 | 0 | 20 |  | 51 | Engine problem
129 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
130 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 16 | 34 | 34 | 34 |  | 16 | Engine problem
131 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 40 | 0 | 40 | 10 |  | Fuel shortage
132 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 143 | 139 | 140 | 140 | 70 |  | Gas shortage
133 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Fuel shortage
134 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
135 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 134 | 150 | 150 | 200 | 214 |  | Gas shortage
136 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 34 | 0 | 34 |  | 16 | Engine problem
137 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 15 | 14 | 17 | 18 |  | 4 | Engine problem
138 | Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
139 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
140 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 43 | 8 | 43 |  | 9 | Engine problem
141 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 57 | 0 | 57 |  | 47 | Engine problem
142 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 0 | 10 | 190 |  | Fuel shortage
143 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 75 | 94 | 85 | 94 |  | 19 | Engine problem
144 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 38 | 95 | 90 | 95 |  | 18 | Engine problem
145 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 4 | 0 | 6 | 0
| Rajshahi Area Total |  |  |  |  | 2199 | 2129 | 436 | 745 | 541 | 826 | 1095 | 202
146 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal shortage
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
147 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 160 | 160 | 160 | 160 |  |  | Machine problem
148 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
149 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
150 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 106 | 113 | 90 | 113
151 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5 | 0 | 8 | 0
152 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 37 | 113 | 67 | 113
| Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 27 | 0 | 30 | 0
| Rangpur Area Total |  |  |  |  | 830 | 750 | 335 | 386 | 355 | 386 | 125 | 85
| Total |  |  |  |  | 22512 | 21710 | 9295 | 10671 | 9749.6 | 11340 | 5937 | 3416
A. |  | 2022-11-17 | (Yesterday) |  |  |  |  | Thursday
1 | Highest Generation : |  |  | 10671 | MW at | 18:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 18:00 | hrs.
2 | Minimum Generation : |  |  | 7056 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 10671 | MW
3 | Day peak Generation : |  |  | 9295 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 10336.56 | MW
4 | Evening peak Generation : |  |  | 10671 | MW at | 18:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 211.757 | MKWHr | By Solar | 1.3562 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Gas : | 108.8175 | MKWHr |  | By Oil: | 54.6575 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 22.4415 | MKWHr |  | By Hydro: | 1.2757 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 5937 | MW | Dhaka | 4131.34 | 4131.34 |  | 0 |  | 18:00 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 3416 | MW | Chittagong | 1231.8 | 1231.8 |  | 0 |  | 19:00 |  | 0
|  |  | Total = |  |  | 9353 | MW | Khulna | 1129 | 1129 |  | 0 |  | 19:30 |  | 0
7 | Total Gas Supplied : |  |  | 840.29 | MMCFD |  |  | Rajshahi | 948.8 | 948.8 |  | 0 |  | 20:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 111264979.182 | ii) Oil : | Taka | 735448883.28 | Comilla | 849 | 849 |  | 0 |  | 21:00 |  | 0
|  | iii) Coal : |  | 159450427 | Total | Taka | 1006164289.462 | Mymensingh | 774 | 774 |  | 0 |  | 22:00 |  | 0
9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0 | MKWHr. | Sylhet | 386 | 386 |  | 0 |  | 23:00 |  | 0
| ii) During Peak Demand : |  |  | 850 | MW (E to W) at | 18:00 | hrs | Barisal | 246.62 | 246.62 |  | 0 |  | 24:00 |  | 0
| iii) Maximum : |  |  | 370 | MW at | 7:00 | hrs | Rangpur | 640 | 640 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 30.7° C |  |  | Total | 10336.56 | 10336.56 |  | 0
B. |  | 2022-11-18 | (Today) |  |  |  | Friday |  |  | Probable max. temperature in Dhaka |  |  | 28.2° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 10200 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 11340 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 8500 | MW
4 | Reserve(Generation end) |  |  |  | 1140 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | 3 | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 202.4104 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 6877 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 20.7825 | MKWHr. | ii) HVDC Flow at Peak Time |  | 904 | MW at | 18:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.4259 | MKWHr. | iii) Maximum HVDC Flow : |  | 906 | MW at | 2:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 91.24 |  | (b) Today: | 91.07 |  | (c) Rule Curve: |  | 107.3
.

## YesterdayGen
2022-11-17
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 0 | 70 | 0 | 377 | 322 |  | 0 | 225 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 87 | 33 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 35 | 22 | 25 | 27 | 33 | 25 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 |  | 10 | 0 | 17 | 22 | 0 | 19 | 0 | 2 | 0 | 0 | 0 | 0 | 305 | 175 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 22 | 10 | 33 | 9 | 94 | 103 | 0 | 11 | 0 | 30 | 42 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 140 | 19 | 0 | 10 | 270 | 0 | 2 | 0 | 95 | 0 | 0 | 48 | 0 | 44 | 0 | 25 | 100 | 70 | 418 | 49 | 34 | 34 | 0 | 69 | 17 | 53 | 17 | 57 | 25 | 340 | 55 | 0 | 17 | 107 | 0 | 17 | 0 | 17 | 17 | 288 | 0 | 0 |  | 905 | 0 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 0 | 0 | 158 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 35 | 0 | 113 | 0 | 0 | 0 | 0 | 95 | 490 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 |  | 5211 | 2736 | 7947 | 3283 | 905 | 1333 | 0 | 1496 | 773 | 46 | 0 | 17 | 94 | 0 | 0 | 91.29
2:00 | 0 | 0 | 0 | 180 | 0 | 70 | 0 | 374 | 323 |  | 0 | 225 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 35 | 22 | 25 | 27 | 33 | 25 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 |  | 12 | 0 | 17 | 22 | 0 | 9 | 0 | 2 | 0 | 0 | 0 | 0 | 305 | 175 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 22 | 10 | 33 | 9 | 88 | 103 | 0 | 11 | 0 | 30 | 42 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 140 | 19 | 0 | 10 | 260 | 0 | 2 | 0 | 95 | 0 | 0 | 8 | 0 | 44 | 0 | 25 | 100 | 10 | 417 | 49 | 17 | 34 | 0 | 70 | 0 | 53 | 0 | 8 | 25 | 341 | 48 | 0 | 17 | 107 | 0 | 17 | 0 | 18 | 17 | 288 | 0 | 0 |  | 906 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 480 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 |  | 4893 | 2600 | 7493 | 3289 | 906 | 1317 | 0 | 1065 | 765 | 46 | 0 | 17 | 88 | 0 | 0 | 91.28
3:00 | 0 | 0 | 0 | 180 | 0 | 70 | 0 | 376 | 322 |  | 0 | 225 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 35 | 22 | 25 | 27 | 33 | 28 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 152 | 0 | 0 | 0 |  | 12 | 0 | 17 | 22 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 305 | 175 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 22 | 10 | 33 | 9 | 88 | 102 | 0 | 11 | 0 | 30 | 42 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 140 | 19 | 0 | 10 | 295 | 0 | 2 | 0 | 95 | 0 | 0 | 8 | 0 | 43 | 0 | 25 | 100 | 10 | 382 | 49 | 17 | 34 | 0 | 70 | 0 | 53 | 0 | 8 | 25 | 390 | 17 | 0 | 17 | 107 | 0 | 17 | 0 | 18 | 17 | 288 | 0 | 0 |  | 748 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 480 | 183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 126 |  | 4905 | 2328 | 7233 | 3309 | 748 | 1312 | 0 | 947 | 766 | 46 | 0 | 17 | 88 | 0 | 0 | 91.27
4:00 | 0 | 0 | 0 | 180 | 0 | 70 | 0 | 376 | 323 |  | 0 | 225 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 35 | 22 | 25 | 27 | 33 | 30 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 |  | 12 | 0 | 17 | 22 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 305 | 175 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 22 | 10 | 33 | 9 | 86 | 104 | 0 | 11 | 0 | 30 | 42 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 140 | 19 | 0 | 10 | 280 | 0 | 2 | 0 | 95 | 0 | 0 | 8 | 0 | 44 | 0 | 25 | 72 | 10 | 383 | 49 | 17 | 34 | 0 | 70 | 0 | 53 | 0 | 8 | 25 | 400 | 17 | 0 | 17 | 107 | 0 | 17 | 0 | 17 | 17 | 288 | 0 | 0 |  | 717 | 0 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 480 | 183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 |  | 4878 | 2297 | 7175 | 3317 | 717 | 1308 | 0 | 919 | 765 | 46 | 0 | 17 | 86 | 0 | 0 | 91.26
5:00 | 0 | 0 | 0 | 180 | 0 | 70 | 0 | 376 | 323 |  | 0 | 225 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 35 | 22 | 25 | 27 | 33 | 30 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 |  | 12 | 0 | 17 | 22 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 305 | 175 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 22 | 10 | 33 | 9 | 84 | 104 | 0 | 11 | 0 | 30 | 42 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 140 | 19 | 0 | 10 | 270 | 0 | 2 | 0 | 95 | 0 | 0 | 8 | 0 | 43 | 0 | 25 | 51 | 10 | 382 | 49 | 17 | 34 | 0 | 70 | 0 | 53 | 0 | 0 | 25 | 400 | 0 | 0 | 17 | 51 | 0 | 17 | 0 | 18 | 17 | 288 | 0 | 0 |  | 716 | 0 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 480 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 |  | 4768 | 2288 | 7056 | 3316 | 716 | 1292 | 0 | 820 | 765 | 46 | 0 | 17 | 84 | 0 | 0 | 91.25
6:00 | 0 | 0 | 0 | 180 | 0 | 70 | 0 | 376 | 333 |  | 0 | 225 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 1 | 33 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 35 | 22 | 25 | 27 | 33 | 30 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 |  | 12 | 0 | 17 | 22 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 305 | 175 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 22 | 10 | 33 | 9 | 80 | 104 | 0 | 11 | 0 | 30 | 42 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 140 | 19 | 0 | 10 | 290 | 0 | 2 | 0 | 95 | 0 | 0 | 8 | 0 | 44 | 0 | 25 | 51 | 4 | 411 | 49 | 17 | 34 | 0 | 69 | 14 | 53 | 0 | 0 | 25 | 360 | 3 | 0 | 17 | 60 | 0 | 17 | 0 | 18 | 17 | 288 | 0 | 0 |  | 716 | 0 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 490 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 |  | 4804 | 2313 | 7117 | 3319 | 716 | 1323 | 0 | 841 | 775 | 46 | 0 | 17 | 80 | 0 | 0 | 91.24
7:00 | 0 | 0 | 0 | 180 | 0 | 70 | 0 | 377 | 330 |  | 0 | 225 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 14 | 33 | 32 | 0 | 0 | 0 | 0 | 17 | 17 | 35 | 22 | 25 | 27 | 33 | 30 | 4 | 0 | 46 | 0 | 0 | 0 | 3 | 151 | 0 | 0 | 0 |  | 12 | 0 | 17 | 22 | 0 | 7 | 0 | 2 | 0 | 0 | 0 | 0 | 355 | 207 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 22 | 8 | 33 | 9 | 84 | 86 | 0 | 11 | 0 | 30 | 42 | 0 | 0 | 0 | 0 | 68 | 0 | 0 | 135 | 19 | 0 | 10 | 300 | 0 | 2 | 0 | 95 | 0 | 0 | 21 | 0 | 42 | 4 | 25 | 51 | 17 | 412 | 49 | 31 | 34 | 0 | 69 | 36 | 53 | 17 | 21 | 25 | 400 | 30 | 4 | 17 | 90 | 0 | 17 | 2 | 18 | 17 | 288 | 0 | 0 |  | 720 | 0 | 155 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 10 | 0 | 18 | 0 | 50 | 0 | 0 | 38 | 520 | 200 | 0 | 0 | 0 | 7 | 8 | 0 | 0 | 0 | 1 | 125 |  | 5145 | 2479 | 7624 | 3415 | 720 | 1357 | 0 | 1130 | 805 | 46 | 0 | 49 | 84 | 18 | 0 | 91.23
8:00 | 0 | 0 | 0 | 180 | 0 | 70 | 0 | 378 | 332 |  | 0 | 225 | 0 | 21 | 0 | 55 | 0 | 0 | 0 | 58 | 33 | 115 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 25 | 27 | 33 | 30 | 30 | 0 | 46 | 0 | 0 | 0 | 17 | 152 | 0 | 0 | 0 |  | 12 | 0 | 17 | 22 | 0 | 21 | 0 | 2 | 0 | 0 | 0 | 0 | 335 | 210 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 22 | 8 | 23 | 9 | 88 | 72 | 0 | 10 | 1 | 30 | 42 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 100 | 19 | 0 | 10 | 280 | 0 | 2 | 0 | 95 | 0 | 0 | 47 | 0 | 42 | 5 | 25 | 51 | 47 | 376 | 49 | 105 | 34 | 1 | 69 | 36 | 53 | 17 | 57 | 25 | 400 | 53 | 18 | 17 | 107 | 0 | 17 | 10 | 18 | 17 | 288 | 0 | 0 |  | 810 | 0 | 155 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 18 | 0 | 11 | 0 | 0 | 166 | 0 | 0 | 148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 53 | 0 | 100 | 0 | 53 | 0 | 1 | 38 | 540 | 203 | 0 | 0 | 1 | 26 | 109 | 0 | 0 | 0 | 8 | 125 |  | 5443 | 2899 | 8342 | 3279 | 810 | 1321 | 0 | 1764 | 831 | 46 | 0 | 132 | 88 | 71 | 0 | 91.22
9:00 | 0 | 0 | 0 | 180 | 0 | 68 | 0 | 379 | 332 |  | 0 | 225 | 0 | 37 | 0 | 55 | 0 | 0 | 0 | 63 | 33 | 115 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 25 | 27 | 33 | 30 | 41 | 0 | 46 | 0 | 0 | 0 | 17 | 152 | 0 | 0 | 0 |  | 12 | 24 | 17 | 22 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 275 | 176 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 22 | 8 | 16 | 9 | 94 | 73 | 0 | 10 | 1 | 30 | 42 | 22 | 41 | 0 | 0 | 65 | 0 | 0 | 20 | 18 | 7 | 10 | 280 | 0 | 2 | 0 | 95 | 0 | 0 | 47 | 0 | 35 | 16 | 25 | 51 | 64 | 376 | 49 | 105 | 34 | 2 | 69 | 36 | 53 | 17 | 58 | 25 | 400 | 54 | 32 | 17 | 107 | 0 | 17 | 18 | 17 | 17 | 287 | 0 | 0 |  | 904 | 0 | 140 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 16 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 60 | 0 | 105 | 0 | 75 | 0 | 3 | 38 | 540 | 184 | 0 | 0 | 2 | 49 | 113 | 0 | 0 | 0 | 15 | 125 |  | 5465 | 3025 | 8490 | 3109 | 904 | 1358 | 0 | 1860 | 825 | 46 | 0 | 156 | 94 | 138 | 0 | 91.21
10:00 | 0 | 0 | 0 | 180 | 0 | 68 | 0 | 374 | 328 |  | 0 | 225 | 0 | 51 | 0 | 55 | 0 | 0 | 0 | 65 | 41 | 98 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 25 | 27 | 33 | 24 | 41 | 0 | 46 | 0 | 0 | 0 | 17 | 150 | 0 | 0 | 0 |  | 5 | 23 | 17 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 194 | 0 | 44 | 0 | 0 | 0 | 0 | 0 | 7 | 8 | 22 | 8 | 16 | 9 | 98 | 41 | 0 | 10 | 2 | 30 | 42 | 22 | 46 | 0 | 0 | 62 | 0 | 0 | 20 | 18 | 20 | 10 | 290 | 0 | 2 | 0 | 95 | 0 | 0 | 48 | 0 | 44 | 19 | 25 | 51 | 65 | 421 | 49 | 105 | 41 | 4 | 69 | 36 | 59 | 17 | 57 | 25 | 400 | 55 | 41 | 17 | 107 | 0 | 17 | 24 | 18 | 17 | 288 | 0 | 0 |  | 905 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 16 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 145 | 84 | 0 | 94 | 0 | 106 | 0 | 4 | 38 | 480 | 167 | 0 | 0 | 3 | 65 | 75 | 0 | 0 | 0 | 22 | 125 |  | 5579 | 2897 | 8476 | 3153 | 905 | 1350 | 0 | 1830 | 765 | 46 | 0 | 145 | 98 | 184 | 0 | 91.2
11:00 | 0 | 0 | 0 | 180 | 0 | 68 | 0 | 375 | 327 |  | 0 | 225 | 0 | 69 | 0 | 55 | 0 | 0 | 0 | 65 | 41 | 98 | 0 | 0 | 0 | 0 | 17 | 55 | 55 | 22 | 25 | 27 | 33 | 24 | 41 | 0 | 46 | 0 | 0 | 0 | 17 | 151 | 0 | 0 | 0 |  | 12 | 23 | 17 | 22 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 176 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 30 | 8 | 22 | 8 | 15 | 9 | 104 | 41 | 0 | 10 | 2 | 30 | 42 | 31 | 47 | 0 | 0 | 62 | 0 | 0 | 20 | 18 | 20 | 10 | 270 | 0 | 2 | 10 | 95 | 10 | 25 | 58 | 25 | 44 | 20 | 25 | 51 | 65 | 421 | 77 | 105 | 69 | 4 | 219 | 54 | 73 | 17 | 60 | 25 | 350 | 55 | 46 | 154 | 107 | 0 | 17 | 28 | 54 | 17 | 288 | 0 | 0 |  | 904 | 0 | 125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 16 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 135 | 95 | 0 | 70 | 0 | 106 | 0 | 5 | 38 | 480 | 167 | 0 | 0 | 4 | 75 | 36 | 0 | 0 | 0 | 26 | 125 |  | 6085 | 2830 | 8915 | 3066 | 904 | 1330 | 70 | 2252 | 765 | 46 | 0 | 168 | 104 | 210 | 0 | #REF!
12:00 | 0 | 0 | 0 | 180 | 0 | 70 | 0 | 371 | 322 |  | 0 | 225 | 0 | 78 | 0 | 55 | 0 | 0 | 0 | 71 | 41 | 98 | 0 | 0 | 0 | 0 | 17 | 55 | 55 | 22 | 25 | 27 | 33 | 24 | 41 | 0 | 46 | 0 | 0 | 0 | 17 | 152 | 0 | 0 | 0 |  | 12 | 23 | 17 | 22 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 184 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 36 | 8 | 22 | 8 | 15 | 9 | 110 | 37 | 0 | 10 | 2 | 30 | 42 | 31 | 47 | 0 | 0 | 62 | 0 | 0 | 20 | 18 | 21 | 10 | 280 | 0 | 2 | 10 | 95 | 40 | 50 | 81 | 50 | 86 | 20 | 25 | 51 | 62 | 423 | 78 | 105 | 69 | 4 | 244 | 54 | 73 | 17 | 80 | 25 | 400 | 55 | 47 | 162 | 107 | 0 | 17 | 28 | 109 | 17 | 288 | 0 | 0 |  | 904 | 0 | 125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 15 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 95 | 0 | 75 | 0 | 106 | 0 | 5 | 38 | 490 | 167 | 0 | 0 | 4 | 76 | 37 | 0 | 0 | 0 | 27 | 125 |  | 6438 | 2857 | 9295 | 3119 | 904 | 1339 | 150 | 2465 | 775 | 46 | 0 | 174 | 110 | 213 | 0 | 91.19
13:00 | 0 | 0 | 0 | 180 | 0 | 68 | 0 | 373 | 322 |  | 0 | 225 | 0 | 82 | 0 | 55 | 0 | 0 | 0 | 71 | 41 | 82 | 0 | 0 | 0 | 0 | 17 | 55 | 55 | 22 | 25 | 18 | 33 | 24 | 49 | 0 | 46 | 0 | 0 | 0 | 17 | 151 | 0 | 0 | 0 |  | 12 | 31 | 17 | 22 | 0 | 18 | 0 | 2 | 0 | 0 | 0 | 0 | 310 | 192 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 37 | 8 | 22 | 10 | 15 | 9 | 110 | 35 | 0 | 10 | 2 | 30 | 42 | 31 | 47 | 0 | 0 | 62 | 0 | 0 | 25 | 18 | 23 | 10 | 300 | 0 | 2 | 10 | 95 | 123 | 96 | 79 | 65 | 98 | 18 | 25 | 51 | 65 | 423 | 78 | 105 | 69 | 4 | 249 | 54 | 73 | 17 | 87 | 25 | 400 | 65 | 45 | 162 | 90 | 0 | 17 | 26 | 115 | 17 | 288 | 0 | 0 |  | 903 | 0 | 125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 12 | 0 | 0 | 15 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 135 | 95 | 0 | 94 | 0 | 70 | 0 | 5 | 38 | 530 | 152 | 0 | 0 | 4 | 71 | 75 | 0 | 0 | 0 | 24 | 125 |  | 6636 | 2936 | 9572 | 3120 | 903 | 1346 | 294 | 2560 | 815 | 46 | 0 | 179 | 110 | 199 | 0 | 91.18
14:00 | 0 | 0 | 0 | 180 | 0 | 71 | 0 | 385 | 317 |  | 0 | 225 | 0 | 82 | 0 | 55 | 0 | 0 | 0 | 75 | 41 | 98 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 21 | 18 | 33 | 24 | 49 | 0 | 46 | 0 | 0 | 0 | 17 | 151 | 0 | 0 | 0 |  | 12 | 49 | 16 | 22 | 0 | 24 | 0 | 2 | 0 | 0 | 0 | 0 | 305 | 175 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 37 | 8 | 22 | 10 | 15 | 9 | 114 | 35 | 0 | 10 | 2 | 30 | 42 | 31 | 47 | 0 | 0 | 64 | 0 | 0 | 20 | 18 | 24 | 10 | 280 | 0 | 2 | 20 | 95 | 100 | 92 | 56 | 70 | 112 | 16 | 25 | 51 | 65 | 423 | 49 | 105 | 69 | 3 | 69 | 36 | 73 | 17 | 87 | 25 | 400 | 62 | 35 | 72 | 89 | 0 | 17 | 21 | 37 | 17 | 288 | 0 | 0 |  | 904 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 14 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 124 | 95 | 0 | 94 | 0 | 71 | 0 | 5 | 38 | 550 | 168 | 0 | 0 | 3 | 55 | 75 | 0 | 0 | 0 | 20 | 125 |  | 6167 | 2924 | 9091 | 3098 | 904 | 1329 | 282 | 2123 | 835 | 46 | 0 | 200 | 114 | 160 | 0 | 91.2
15:00 | 0 | 0 | 0 | 180 | 0 | 71 | 0 | 382 | 311 |  | 0 | 225 | 0 | 80 | 0 | 55 | 0 | 0 | 0 | 75 | 33 | 98 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 21 | 18 | 33 | 24 | 49 | 0 | 46 | 0 | 0 | 0 | 17 | 151 | 0 | 0 | 0 |  | 12 | 40 | 17 | 22 | 0 | 32 | 0 | 2 | 0 | 0 | 0 | 0 | 270 | 195 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 37 | 8 | 22 | 10 | 16 | 9 | 114 | 35 | 0 | 9 | 1 | 30 | 42 | 31 | 47 | 0 | 0 | 62 | 0 | 0 | 20 | 18 | 24 | 10 | 295 | 0 | 2 | 20 | 95 | 130 | 95 | 51 | 87 | 123 | 11 | 25 | 51 | 65 | 423 | 49 | 105 | 68 | 2 | 69 | 36 | 73 | 17 | 86 | 25 | 400 | 61 | 24 | 72 | 95 | 0 | 17 | 15 | 17 | 17 | 288 | 0 | 0 |  | 903 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 14 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116 | 95 | 0 | 113 | 0 | 70 | 0 | 4 | 38 | 560 | 168 | 0 | 0 | 2 | 37 | 75 | 0 | 0 | 0 | 11 | 145 |  | 6162 | 2920 | 9082 | 3066 | 903 | 1329 | 332 | 2128 | 865 | 46 | 0 | 192 | 114 | 107 | 0 | 91.17
16:00 | 0 | 0 | 0 | 180 | 0 | 71 | 0 | 379 | 312 |  | 0 | 225 | 0 | 76 | 0 | 55 | 0 | 0 | 0 | 65 | 33 | 115 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 21 | 18 | 33 | 24 | 49 | 0 | 46 | 0 | 0 | 0 | 17 | 151 | 0 | 0 | 0 |  | 12 | 40 | 17 | 22 | 0 | 43 | 0 | 2 | 0 | 0 | 0 | 0 | 330 | 190 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 44 | 8 | 22 | 8 | 16 | 0 | 106 | 35 | 0 | 10 | 0 | 30 | 42 | 28 | 47 | 0 | 0 | 61 | 0 | 0 | 20 | 18 | 24 | 10 | 310 | 0 | 2 | 0 | 95 | 0 | 0 | 57 | 0 | 127 | 3 | 25 | 51 | 65 | 405 | 49 | 105 | 76 | 1 | 69 | 36 | 82 | 17 | 105 | 25 | 390 | 53 | 9 | 72 | 107 | 0 | 17 | 5 | 18 | 17 | 267 | 0 | 0 |  | 904 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 14 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 95 | 0 | 94 | 0 | 91 | 0 | 1 | 90 | 560 | 113 | 0 | 0 | 0 | 16 | 75 | 0 | 0 | 0 | 4 | 160 |  | 5864 | 2904 | 8768 | 3059 | 904 | 1304 | 0 | 2214 | 880 | 46 | 0 | 216 | 106 | 39 | 0 | 91.17
17:00 | 0 | 0 | 0 | 180 | 0 | 71 | 0 | 375 | 311 |  | 0 | 225 | 0 | 82 | 0 | 55 | 0 | 0 | 0 | 65 | 33 | 128 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 21 | 26 | 33 | 24 | 49 | 0 | 46 | 0 | 0 | 0 | 17 | 151 | 0 | 0 | 0 |  | 12 | 40 | 18 | 22 | 0 | 44 | 0 | 2 | 0 | 0 | 0 | 0 | 270 | 190 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 44 | 8 | 22 | 8 | 16 | 5 | 108 | 38 | 0 | 10 | 0 | 30 | 42 | 31 | 47 | 0 | 0 | 63 | 0 | 0 | 20 | 18 | 26 | 10 | 310 | 0 | 3 | 0 | 95 | 0 | 0 | 57 | 0 | 134 | 0 | 25 | 51 | 73 | 421 | 49 | 105 | 102 | 0 | 69 | 36 | 91 | 17 | 107 | 25 | 400 | 54 | 1 | 162 | 107 | 0 | 17 | 0 | 46 | 17 | 268 | 0 | 0 |  | 903 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 14 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 95 | 0 | 94 | 0 | 113 | 0 | 0 | 95 | 560 | 108 | 0 | 0 | 0 | 1 | 75 | 0 | 0 | 0 | 0 | 198 |  | 6027 | 2968 | 8995 | 3048 | 903 | 1321 | 0 | 2419 | 918 | 46 | 0 | 230 | 108 | 2 | 0 | 91.16
18:00 | 0 | 0 | 0 | 180 | 0 | 71 | 0 | 372 | 307 |  | 0 | 225 | 0 | 83 | 0 | 55 | 0 | 0 | 0 | 78 | 66 | 133 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 22 | 21 | 26 | 33 | 24 | 49 | 0 | 80 | 0 | 0 | 0 | 17 | 150 | 0 | 0 | 0 |  | 12 | 50 | 51 | 44 | 0 | 44 | 0 | 2 | 0 | 0 | 0 | 0 | 295 | 199 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 37 | 28 | 22 | 8 | 17 | 14 | 124 | 38 | 0 | 9 | 0 | 30 | 42 | 25 | 47 | 0 | 0 | 68 | 78 | 0 | 65 | 18 | 28 | 10 | 280 | 0 | 2 | 40 | 262 | 20 | 50 | 85 | 50 | 136 | 0 | 40 | 79 | 87 | 422 | 97 | 105 | 105 | 0 | 290 | 36 | 91 | 17 | 107 | 50 | 400 | 66 | 0 | 162 | 107 | 0 | 17 | 0 | 109 | 17 | 268 | 0 | 0 |  | 904 | 0 | 125 | 0 | 49 | 0 | 0 | 0 | 35 | 52 | 18 | 152 | 20 | 0 | 0 | 0 | 0 | 30 | 4 | 57 | 0 | 34 | 40 | 43 | 34 | 14 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 139 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 150 | 95 | 0 | 94 | 0 | 113 | 0 | 0 | 95 | 580 | 108 | 0 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 243 |  | 7139 | 3532 | 10671 | 3212 | 904 | 1365 | 180 | 3300 | 983 | 80 | 0 | 523 | 124 | 0 | 0 | 91.16
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 0 | 71 | 0 | 371 | 307 |  | 0 | 225 | 0 | 82 | 0 | 55 | 0 | 0 | 0 | 80 | 66 | 82 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 21 | 26 | 33 | 24 | 49 | 0 | 80 | 0 | 0 | 0 | 17 | 151 | 0 | 0 | 0 |  | 12 | 0 | 51 | 44 | 0 | 44 | 0 | 2 | 0 | 0 | 0 | 0 | 240 | 180 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 37 | 39 | 22 | 8 | 25 | 18 | 122 | 57 | 0 | 8 | 0 | 30 | 42 | 5 | 30 | 0 | 0 | 69 | 81 | 0 | 68 | 18 | 29 | 10 | 270 | 0 | 2 | 0 | 260 | 0 | 0 | 87 | 0 | 136 | 0 | 50 | 85 | 95 | 423 | 99 | 105 | 105 | 0 | 300 | 36 | 91 | 17 | 107 | 50 | 400 | 55 | 0 | 162 | 107 | 0 | 17 | 0 | 115 | 17 | 268 | 0 | 0 |  | 905 | 0 | 130 | 0 | 16 | 0 | 0 | 0 | 0 | 88 | 8 | 152 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 34 | 40 | 8 | 0 | 19 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 154 | 95 | 0 | 113 | 0 | 113 | 0 | 0 | 95 | 650 | 108 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | 0 | 293 |  | 6875 | 3481 | 10356 | 3177 | 905 | 1331 | 0 | 3285 | 1103 | 80 | 0 | 353 | 122 | 0 | 0 | 91.14
19:30 | 0 | 0 | 0 | 180 | 0 | 71 | 0 | 369 | 307 |  | 0 | 225 | 0 | 83 | 0 | 55 | 0 | 0 | 0 | 80 | 66 | 64 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 21 | 26 | 33 | 24 | 41 | 0 | 80 | 0 | 0 | 0 | 17 | 151 | 0 | 0 | 0 |  | 12 | 0 | 51 | 44 | 0 | 44 | 0 | 4 | 0 | 0 | 0 | 0 | 240 | 180 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 37 | 42 | 22 | 8 | 25 | 18 | 114 | 75 | 0 | 8 | 0 | 30 | 0 | 5 | 30 | 0 | 0 | 68 | 81 | 0 | 67 | 18 | 29 | 10 | 290 | 0 | 2 | 0 | 260 | 0 | 0 | 87 | 0 | 136 | 0 | 50 | 85 | 88 | 421 | 99 | 105 | 105 | 0 | 300 | 36 | 91 | 17 | 108 | 50 | 400 | 55 | 0 | 162 | 107 | 0 | 17 | 0 | 115 | 17 | 268 | 0 | 0 |  | 905 | 0 | 135 | 0 | 16 | 0 | 0 | 0 | 0 | 77 | 8 | 152 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 8 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 145 | 95 | 0 | 113 | 0 | 70 | 0 | 0 | 95 | 670 | 108 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 307 |  | 6831 | 3324 | 10155 | 3152 | 905 | 1348 | 0 | 3158 | 1137 | 80 | 0 | 261 | 114 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 180 | 0 | 71 | 0 | 367 | 303 |  | 0 | 225 | 0 | 84 | 0 | 55 | 0 | 0 | 0 | 80 | 66 | 64 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 21 | 26 | 33 | 24 | 41 | 0 | 80 | 0 | 0 | 0 | 17 | 151 | 0 | 0 | 0 |  | 12 | 0 | 51 | 44 | 0 | 44 | 0 | 2 | 0 | 0 | 0 | 0 | 240 | 180 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 37 | 42 | 22 | 8 | 28 | 21 | 118 | 74 | 0 | 10 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 70 | 81 | 0 | 68 | 19 | 29 | 10 | 280 | 0 | 2 | 0 | 260 | 0 | 0 | 86 | 0 | 136 | 0 | 50 | 85 | 90 | 418 | 99 | 105 | 105 | 0 | 300 | 36 | 91 | 17 | 107 | 50 | 360 | 54 | 0 | 162 | 107 | 0 | 17 | 0 | 115 | 17 | 288 | 0 | 0 |  | 905 | 0 | 135 | 0 | 60 | 0 | 0 | 0 | 0 | 77 | 8 | 138 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 34 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161 | 95 | 0 | 113 | 0 | 100 | 0 | 0 | 95 | 690 | 108 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 0 | 160 |  | 6771 | 3355 | 10126 | 3125 | 905 | 1314 | 0 | 3313 | 1010 | 80 | 0 | 261 | 118 | 0 | 0 | 91.15
21:00 | 0 | 0 | 0 | 180 | 0 | 71 | 0 | 370 | 252 |  | 0 | 225 | 0 | 83 | 0 | 55 | 0 | 0 | 0 | 80 | 66 | 64 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 21 | 18 | 33 | 24 | 41 | 0 | 80 | 0 | 0 | 0 | 17 | 151 | 0 | 0 | 0 |  | 12 | 0 | 51 | 44 | 0 | 44 | 0 | 2 | 0 | 0 | 0 | 0 | 240 | 172 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 37 | 42 | 22 | 8 | 33 | 21 | 116 | 75 | 0 | 9 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 70 | 81 | 0 | 68 | 19 | 0 | 10 | 260 | 0 | 2 | 0 | 260 | 0 | 0 | 88 | 0 | 136 | 0 | 50 | 85 | 88 | 415 | 99 | 105 | 105 | 0 | 300 | 36 | 81 | 17 | 108 | 50 | 292 | 54 | 0 | 162 | 107 | 0 | 17 | 0 | 115 | 17 | 288 | 0 | 0 |  | 905 | 0 | 140 | 0 | 83 | 0 | 0 | 0 | 0 | 77 | 8 | 147 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 34 | 0 | 0 | 0 | 20 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161 | 95 | 0 | 94 | 0 | 113 | 0 | 0 | 95 | 760 | 106 | 0 | 0 | 0 | 0 | 95 | 0 | 0 | 0 | 0 | 0 |  | 6523 | 3298 | 9821 | 3060 | 905 | 1211 | 0 | 3268 | 920 | 80 | 0 | 261 | 116 | 0 | 0 | 91.14
22:00 | 0 | 0 | 0 | 180 | 0 | 71 | 0 | 379 | 313 |  | 0 | 225 | 0 | 83 | 0 | 55 | 0 | 0 | 0 | 80 | 66 | 36 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 21 | 24 | 33 | 27 | 41 | 0 | 80 | 0 | 0 | 0 | 17 | 151 | 0 | 0 | 0 |  | 12 | 0 | 51 | 44 | 0 | 44 | 0 | 2 | 0 | 0 | 0 | 0 | 240 | 176 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 37 | 8 | 22 | 8 | 33 | 21 | 110 | 100 | 0 | 9 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 40 | 81 | 0 | 84 | 19 | 0 | 10 | 270 | 0 | 2 | 0 | 260 | 0 | 0 | 88 | 0 | 135 | 0 | 50 | 85 | 88 | 418 | 99 | 105 | 105 | 0 | 69 | 36 | 73 | 17 | 107 | 50 | 356 | 55 | 0 | 162 | 107 | 0 | 17 | 0 | 115 | 17 | 288 | 0 | 0 |  | 905 | 0 | 145 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162 | 95 | 0 | 70 | 0 | 70 | 0 | 0 | 95 | 770 | 109 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | 0 | 0 |  | 6386 | 3014 | 9400 | 3158 | 905 | 1287 | 0 | 2806 | 930 | 80 | 0 | 124 | 110 | 0 | 0 | 91.14
23:00 | 0 | 0 | 0 | 180 | 0 | 71 | 0 | 375 | 312 |  | 0 | 225 | 0 | 84 | 0 | 55 | 0 | 0 | 0 | 80 | 66 | 32 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 21 | 26 | 33 | 27 | 42 | 0 | 46 | 0 | 0 | 0 | 17 | 151 | 0 | 0 | 0 |  | 12 | 0 | 32 | 44 | 0 | 44 | 0 | 6 | 0 | 0 | 0 | 0 | 240 | 176 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 22 | 8 | 33 | 21 | 102 | 103 | 0 | 9 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 40 | 81 | 0 | 84 | 19 | 0 | 10 | 290 | 0 | 2 | 0 | 260 | 0 | 0 | 88 | 0 | 79 | 0 | 50 | 85 | 75 | 419 | 99 | 105 | 67 | 0 | 69 | 36 | 67 | 17 | 101 | 50 | 400 | 55 | 0 | 35 | 107 | 0 | 17 | 0 | 67 | 17 | 288 | 0 | 0 |  | 906 | 0 | 150 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 151 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 95 | 0 | 70 | 0 | 70 | 0 | 0 | 35 | 790 | 108 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | 0 | 0 |  | 6061 | 2989 | 9050 | 3221 | 906 | 1315 | 0 | 2446 | 950 | 46 | 0 | 64 | 102 | 0 | 0 | 91.13
24:00 | 0 | 0 | 0 | 180 | 0 | 71 | 0 | 376 | 312 |  | 0 | 225 | 0 | 53 | 0 | 55 | 0 | 0 | 0 | 80 | 33 | 32 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 21 | 27 | 33 | 28 | 50 | 0 | 46 | 0 | 0 | 0 | 17 | 151 | 0 | 0 | 0 |  | 12 | 0 | 17 | 22 | 0 | 9 | 0 | 7 | 0 | 0 | 0 | 0 | 280 | 176 | 0 | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 22 | 8 | 33 | 21 | 106 | 103 | 0 | 9 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 71 | 81 | 0 | 84 | 19 | 0 | 10 | 280 | 0 | 2 | 0 | 130 | 15 | 25 | 53 | 25 | 43 | 0 | 25 | 85 | 70 | 418 | 50 | 105 | 34 | 0 | 69 | 36 | 53 | 17 | 75 | 27 | 394 | 56 | 0 | 35 | 107 | 0 | 17 | 0 | 37 | 17 | 288 | 0 | 0 |  | 905 | 0 | 150 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 139 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 95 | 0 | 70 | 0 | 70 | 0 | 0 | 35 | 810 | 108 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | 0 | 0 |  | 5659 | 3003 | 8662 | 3284 | 905 | 1309 | 65 | 1928 | 970 | 46 | 0 | 49 | 106 | 0 | 0 | 91.13
KWH | 0 | 0 | 0 | 4347000 | 0 | 1642409 | 0 | 9121800 | 7594000 |  | 0 | 5200400 | 0 | 1218240 | 0 | 1329172 | 0 | 0 | 0 | 1312493 | 1018656 | 1563360 | 0 | 0 | 0 | 0 | 517680 | 677122 | 911630 | 498528 | 600000 | 581580 | 813900 | 642500 | 758880 | 0 | 1275715 | 0 | 0 | 0 | 301721 | 3539916 | 0 | 0 | 0 |  | 287760 | 323520 | 583589 | 650520 | 0 | 550080 | 0 | 54240 | 0 | 0 | 0 | 0 | 7064000 | 4477000 | 0 | 1005940 | 0 | 0 | 0 | 0 | 0 | 443840 | 323443 | 507024 | 205200 | 602500 | 263270 | 2425920 | 1641600 | 0 | 234612 | 11500 | 716000 | 777000 | 291600 | 511560 | 0 | 0 | 1523136 | 581760 | 0 | 1825300 | 438000 | 261000 | 244440 | 7016500 | 0 | 61056 | 129600 | 3291927 | 576092 | 458819 | 1252800 | 388916 | 1969632 | 131625 | 744000 | 1668480 | 1435200 | 9768000 | 1518000 | 2013696 | 1527200 | 26520 | 3003382 | 772089 | 1668538 | 339720 | 1636320 | 750720 | 9159200 | 1152000 | 302780 | 1804320 | 2436327 | 0 | 443520 | 178277 | 1256640 | 433800 | 6781700 | 0 | 0 |  | 20782545 | 0 | 3457440 | 0 | 316800 | 0 | 0 | 0 | 42440 | 289664 | 27000 | 2496471 | 406000 | 0 | 0 | 0 | 0 | 29427 | 8183 | 172072 | 0 | 462249 | 74713 | 48000 | 42518 | 416160 | 0 | 245016 | 0 | 0 | 3865700 | 0 | 0 | 3642273 | 0 | 0 | 0 | 0 | 24000 | 0 | 0 | 3781200 | 1550400 | 836 | 1848576 | 0 | 1491158 | 0 | 33250 | 1404960 | 15427400 | 3779318 | 0 | 0 | 27960 | 484560 | 1381056 | 0 | 0 | 0 | 159773 | 3148400 |  | 140389452 | 71367518 | 211756970 | 77036962 | 20782545 | 31780587 | 1578263 | 49505907 | 22441500 | 1275715 | 0 | 3573326 | 2425920 | 1356245 | 0
Fuel Cost | 0 | 0 | 0 | 6477030 | 0 | 2184403.97 | 0 | 9577890 | 8201520 |  | 0 | 5668436 | 0 | 13619923.2 | 0 | 17611529 | 0 | 0 | 0 | 19188647.66 | 14332489.92 | 25342065.6 | 0 | 0 | 0 | 0 | 6584889.6 | 9141147 | 12224958.3 | 373896 | 450000 | 0 | 0 | 0 | 12908548.8 | 0 | 344443.05 | 0 | 0 | 0 | 4933138.35 | 3681512.64 | 0 | 0 | 0 |  | 3755268 | 5396313.6 | 9932684.78 | 8788525.2 | 0 | 6364425.6 | 0 | 180619.2 | 0 | 0 | 0 | 0 | 7699760 | 5193320 | 0 | 1227246.8 | 0 | 0 | 0 | 0 | 0 | 7665116.8 | 4350308.35 | 694622.88 | 153900 | 1054375 | 197452.5 | 17418105.6 | 1789344 | 0 | 319072.32 | 183310 | 980920 | 1025640 | 507384 | 884998.8 | 0 | 0 | 2954883.84 | 1326412.8 | 0 | 1843553 | 941700 | 388890 | 483991.2 | 7016500 | 0 | 46402.56 | 2716416 | 44934803.55 | 12074888.32 | 9483788.73 | 16887744 | 8038893.72 | 27279403.2 | 1538696.25 | 7678080 | 22791436.8 | 19045104 | 8986560 | 18458880 | 29118044.16 | 19319080 | 0 | 35259704.68 | 8408049.21 | 17736558.94 | 4610000.4 | 21092164.8 | 8843481.6 | 8426464 | 14918400 | 4375171 | 22896820.8 | 27725401.26 | 0 | 5792371.2 | 2130410.15 | 18811900.8 | 5713146 | 0 | 0 | 0 |  | 62347635 | 0 | 3872332.8 | 0 | 3297888 | 0 | 0 | 0 | 764344.4 | 5213952 | 387990 | 2796047.52 | 787640 | 0 | 0 | 0 | 0 | 493490.79 | 143120.67 | 2691206.08 | 0 | 7654843.44 | 1263396.83 | 654240 | 717278.66 | 861451.2 | 0 | 185477.112 | 0 | 0 | 20449553 | 0 | 0 | 4225036.68 | 0 | 0 | 0 | 0 | 503520 | 0 | 0 | 3743388 | 20837376 | 17530.92 | 21868654.08 | 0 | 18937706.6 | 0 | 367412.5 | 17056214.4 | 139000874 | 3854904.36 | 0 | 0 | 316227.6 | 5683888.8 | 21171588.48 | 0 | 0 | 0 | 0 | 0 |  | 728703379.49 | 372166209.922 | 1100869589.412 | 75174439.652 | 62347635 | 36090539.53 | 32835037.69 | 642990875.38 | 159450427 | 344443.05 | 0 | 59622970.21 | 17418105.6 | 14595116.3 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 0 | 70 | 0 | 371 | 322 |  | 0 | 225 | 0 | 78 | 0 | 55 | 0 | 0 | 0 | 71 | 41 | 98 | 0 | 0 | 0 | 0 | 17 | 55 | 55 | 22 | 25 | 27 | 33 | 24 | 41 | 0 | 46 | 0 | 0 | 0 | 17 | 152 | 0 | 0 | 0 |  | 12 | 23 | 17 | 22 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 184 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 36 | 8 | 22 | 8 | 15 | 9 | 110 | 37 | 0 | 10 | 2 | 30 | 42 | 31 | 47 | 0 | 0 | 62 | 0 | 0 | 20 | 18 | 21 | 10 | 280 | 0 | 2 | 10 | 95 | 40 | 50 | 81 | 50 | 86 | 20 | 25 | 51 | 62 | 423 | 78 | 105 | 69 | 4 | 244 | 54 | 73 | 17 | 80 | 25 | 400 | 55 | 47 | 162 | 107 | 0 | 17 | 28 | 109 | 17 | 288 | 0 | 0 |  | 904 | 0 | 125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 15 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 95 | 0 | 75 | 0 | 106 | 0 | 5 | 38 | 490 | 167 | 0 | 0 | 4 | 76 | 37 | 0 | 0 | 0 | 27 | 125 |  | 9295 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 0 | 71 | 0 | 372 | 307 | 0 | 0 | 225 | 0 | 83 | 0 | 55 | 0 | 0 | 0 | 78 | 66 | 133 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 22 | 21 | 26 | 33 | 24 | 49 | 0 | 80 | 0 | 0 | 0 | 17 | 150 | 0 | 0 | 0 | 0 | 12 | 50 | 51 | 44 | 0 | 44 | 0 | 2 | 0 | 0 | 0 | 0 | 295 | 199 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 37 | 28 | 22 | 8 | 17 | 14 | 124 | 38 | 0 | 9 | 0 | 30 | 42 | 25 | 47 | 0 | 0 | 68 | 78 | 0 | 65 | 18 | 28 | 10 | 280 | 0 | 2 | 40 | 262 | 20 | 50 | 85 | 50 | 136 | 0 | 40 | 79 | 87 | 422 | 97 | 105 | 105 | 0 | 290 | 36 | 91 | 17 | 107 | 50 | 400 | 66 | 0 | 162 | 107 | 0 | 17 | 0 | 109 | 17 | 268 | 0 | 0 |  | 904 | 0 | 125 | 0 | 49 | 0 | 0 | 0 | 35 | 52 | 18 | 152 | 20 | 0 | 0 | 0 | 0 | 30 | 4 | 57 | 0 | 34 | 40 | 43 | 34 | 14 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 139 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 150 | 95 | 0 | 94 | 0 | 113 | 0 | 0 | 95 | 580 | 108 | 0 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 243 |  | 10671 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 0 | 71 | 0 | 372 | 307 | 0 | 0 | 225 | 0 | 83 | 0 | 55 | 0 | 0 | 0 | 78 | 66 | 133 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 22 | 21 | 26 | 33 | 24 | 50 | 0 | 80 | 0 | 0 | 0 | 17 | 150 | 0 | 0 | 0 | 0 | 12 | 40 | 51 | 44 | 0 | 44 | 0 | 20 | 0 | 0 | 0 | 0 | 300 | 0 | 8 | 40 | 45 | 30 | 0 | 0 | 0 | 37 | 28 | 22 | 8 | 33 | 19 | 165 | 70 | 0 | 9 | 0 | 30 | 30 | 0 | 0 | 0 | 0 | 66 | 80 | 0 | 80 | 18 | 0 | 10 | 300 | 0 | 2 | 100 | 260 | 150 | 50 | 85 | 50 | 136 | 0 | 40 | 200 | 87 | 400 | 97 | 105 | 105 | 0 | 290 | 36 | 91 | 17 | 107 | 50 | 400 | 55 | 0 | 162 | 107 | 0 | 17 |  | 115 | 17 | 288 |  |  |  | 922 | 0 | 150 | 0 | 115 | 0 | 0 | 0 | 35 | 70 | 8 | 150 | 20 | 0 | 0 | 0 | 0 | 30 | 20 | 57 | 0 | 34 | 40 | 43 | 34 | 18 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 200 | 95 | 10 | 94 | 0 | 113 | 0 | 0 | 95 | 800 | 108 |  | 0 |  |  | 113 | 230
Forecast for Day | 0 | 0 | 0 | 180 | 0 | 70 | 0 | 350 | 300 | 0 | 0 | 225 | 0 | 70 | 0 | 55 | 0 | 0 | 0 | 75 | 33 | 100 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 22 | 20 | 33 | 20 | 50 | 0 | 80 | 0 | 0 | 0 | 17 | 150 | 0 | 0 | 0 | 0 | 12 | 20 | 17 | 33 | 0 | 26 | 0 | 10 | 0 | 0 | 0 | 0 | 300 | 0 | 8 | 40 | 40 | 30 | 0 | 0 | 0 | 0 | 8 | 22 | 8 | 33 | 15 | 143 | 70 | 0 | 9 | 1.6 | 30 | 0 | 0 | 0 | 0 | 0 | 66 | 0 | 0 | 80 | 18 | 0 | 10 | 300 | 0 | 2 | 100 | 175 | 100 | 50 | 75 | 50 | 125 | 20 | 25 | 51 | 65 | 400 | 50 | 105 | 68 | 5 | 260 | 36 | 70 | 17 | 80 | 25 | 400 | 55 | 50 | 162 | 107 | 0 | 17 | 30 | 35 | 17 | 288 |  |  |  | 922 | 0 | 130 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 8 | 0 | 17 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 85 | 0 | 90 | 0 | 8 | 90 | 800 | 100 |  | 0 | 6 | 100 | 67 | 230 |  |  | 30
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 0 | 68 | 0 | 375 | 323 | 0 | 0 | 225 | 0 | 2 | 0 | 55 | 0 | 0 | 0 | 43 | 33 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 35 | 22 | 25 | 27 | 33 | 29 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 0 | 12 | 0 | 17 | 22 | 0 | 18 | 0 | 12 | 0 | 0 | 0 | 0 | 280 | 0 | 8 | 45 | 45 | 30 | 0 | 0 | 0 | 0 | 8 | 22 | 8 | 30 | 19 | 82 | 74 | 0 | 9 | 1 | 30 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 0 | 84 | 18 | 0 | 10 | 310 | 0 | 2 | 0 | 60 | 0 | 0 | 47 | 25 | 52 | 10 | 25 | 51 | 57 | 418 | 49 | 50 | 34 | 1 | 65 | 36 | 53 | 17 | 36 | 25 | 400 | 56 | 19 | 31 | 57 | 0 | 17 | 8 | 18 | 17 | 308 | 0 | 0 | 0 | 567 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 208 | 36 | 0 | 37 | 0 | 60 | 0 | 1 | 38 | 690 | 105 | 0 | 0 | 1 | 26 | 0 | 0 | 0 | 0 | 9 | 0 | 0 |  |  |  |  | 54657496 |  | 0
54657496
| Minimum Generation |  | 7056 | 5:00
| Highest Generation |  | 10671 | 18:00
| Day Peak Generation |  | 9295 | 12:00
| Evening Peak Generation |  | 10671 | 18:00
| HVDC Max Flow |  | 906 | 2:00
| HVDC EvPeak Flow |  | 904 | 18:00
| Load factor L.F |  | 82.68% | [161 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2022-11-18
Till now the maximum generation is : - |  |  | 14782 | 21:00 | Hrs on | 2022-04-16
The Summary of Yesterday's |  | 2022-11-17 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 9295 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 6877 | MW
Evening Peak Generation : |  | 10671 | MW Hour : | 18:00 | Available Max Generation : |  | 11340 | MW
E.P. Demand (at gen end) : |  | 10671 | MW Hour : | 18:00 | Max Demand (Evening) : |  | 10200 | MW
Maximum Generation : |  | 10671 | MW Hour : | 18:00 | Reserve(Generation end) |  | 1140 | MW
Total Gen. (MKWH) : |  | 211.757 | System Load Factor : | 82.68% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | 370 | MW at | 7:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2022-11-18
Actual : | 91.07 | Ft.(MSL) , | Rule curve : | 107.3 | Ft.( MSL )
Gas Consumed : | Total = | 840.29 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 111264979.182
: |  | Coal : | 159450427 | Oil : | 735448883.28 | Total : | 1006164289.462
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4098.4931 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1161.0318 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1532.4656 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1359.6786 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1157.4564 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 956.2319 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 427.3941 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 348.401 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 755.0075 |  |  | 0 | 0%
Total | 0 |  | 11796.16 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1, 2 |  | 10) Ashuganj-225 MW
2) Ghorasal-3, 4, 7
3) Ashuganj-5
4) Baghabari-71,100 MW
5) Raozan unit-1 & 2
6) Siddhirganj 210 MW .
7) Shajibazar 330 MW
8) Sirajganj-2
9) Ashuganj(N)-360 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Ashuganj-Kishorganj 132 kV Ckt-1 was under shut down from 08:31 to 15:20 for A/M.
b) Shahjibazar 132/33 kV T-2 transformer was under shut down from 08:27 to 15:50 for A/M.
c) Cumilla(N)-Bibiyana 230 kV Ckt-1 was under shut down from 08:45 to 15:52 for A/M.
d) Joydevpur-Ghorasal 132 kV Ckt-1 was under shut down from 08:52 to 16:28 for A/M.
e) Fenchuganj 230 kV bus-1 was under shut down from 08:37 to 15:12 for A/M.
f) Bhulta 400 kV bus-1 was under shut down from 08:50 to 15:04 for A/M.
g) Hasnabad 132 kV bus coupler was under shut down from 09:29 to 14:17 for A/M.
h) Hasnabad-Keraniganj 230 kV Ckt-1 was under shut down from 09:37 to 13:16 for A/M.
i) Bagerhat-Mongla 132 kV Ckt-1 was under shut down from 09:08 to 15:38 for A/M.
j) Barishal(N) 132/33 kV T-5 transformer was under shut down from 08:40 to 17:28 for A/M.
k) Bogura 230/132 kV T-1 transformer was under shut down from 08:30 to 15:38 for A/M.
l) Niamatpur 132/33 kV T-3 transformer was under shut down from 08:22 to 16:15 for A/M.
m) Rajshahi(O)-Rajshahi(N) 132 kV Ckt-1 was under shut down from 09:09 to 16:33 for A/M.
n) Kurigram 132/33 kV T-1 transformer was under shut down from 08:21 to 16:28 for A/M.
o) TK Chemical-Sikalbaha 132 kV Ckt was under shut down from 08:51 to 15:38 for A/M.
p) Haripur 230/132 kV T-2 transformer was under shut down from 09:38 to 13:36 for A/M.
q) HVDC 10CF14 filter was under shut down from 10:24 to 14:14 for C/M.
r) Mymensing-Kishorganj 132 kV Ckt-1 was under shut down from 12:46 to 13:38 for C/M.
s) Bogura-Mohastanghor 132 kV Ckt-1 was under shut down from 10:54 to 13:48 for C/M.
t) Hasnabad-Keraniganj 230 kV Ckt-2 was under shut down from 13:17 to 16:52 for A/M.
u) Khulna(S)-Rampal 230 kV Ckt-1 was under shut down from 12:23 to 17:36 for D/W.
v) Khulna(S) 230 kV bus-2 was under shut down from 12:41 to 16:31 for D/W.
w) Khulna(S)-Rampal 230 kV Ckt-2 was under shut down from 10:23 to 11:58 for D/W.
x) Aminbazar-Megnaghat 230 kV Ckt-1 was under shut down from 15:11 to 17:25 for D/W.
y) Jamalpur-Mymensing 132 kV Ckt-1 was under shut down from 08:10 to 16:26 for A/M.
z) Bhola-225 MW CCPP GT-1 was shut down at 15:52 due to bore scope inspection was synchronized
at 17:10.
aa) Sylhet-225 MW CCPP ST was synchronized at 17:41.
ab) Rangpur 33 kV bus-2 is under shut down since 07:10 to 10:33(18/11/22) for C/M. | [5 empty] | About 40 MW power interruption occurred
under Rangpur S/S area from 07:10 to 10:33.
ac) Ashuganj-225 MW CCPP ST & GT were shut down at 04:42 & 04:53(18/11/22) for MI.
ad) Kaptai #3 was shut down at 22:20. #2 tripped at 00:31(18/11/22) and synchronized at 01:10(18/11/22).
ae) Khulna(S)-Rampal 230 kV Ckt-2 is under shut down since 07:50(18/11/22) for D/W.
| Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2022-11-17 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Line O/L
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4347000
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 71 | 1642409 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 372 | 9121800 | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 307 | 7594000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 5200400 | GT-2 S/D due to Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 83 | 1218240 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 0 | 0 | Under maint.
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 55 | 1329172
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 498528
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 78 | 1312493 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 66 | 1018656 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 35 | 517680 | Engine problem
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 133 | 1563360 | Engine problem
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 35 | 677122 | Engine problem
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 911630 | Engine problem
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 47 | 1181580 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 813900
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 24 | 642500 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 49 | 758880 | 0:00
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 262 | 3291927 | Fuel shortage
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 20 | 576092 | Fuel conservation
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 50 | 458819 | Fuel conservation
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 50 | 388916 | Fuel conservation
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 136 | 1969632 | Engine problem
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 2013696
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 66 | 1152000 | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 1804320
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 178277
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 433800 | Fuel shortage
| Dhaka area Total |  |  |  | 5847 | 2718 | 52616829
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Machine problem
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 17 | 301721 | Engine problem
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 131625
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 44 | 550080
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 80 | 1275715 | Low water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 150 | 3539916 | ST Under maint
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 105 | 1527200 | Engine problem
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 50 | 323520 | Fuel shortage
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 583589 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 44 | 650520 | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 40 | 744000 | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 0 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 2 | 54240
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 26520
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 290 | 3003382 | Engine problem
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 36 | 772089 | Engine problem
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 91 | 1668538 | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 50 | 750720
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 107 | 2436327 | Engine problem
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Chattogram area Total |  |  |  | 2382 | 1157 | 18339702
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 199 | 4477000 | Gas shortage
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 0 | 0 | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 295 | 7064000 | FGMO
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+136*1 | 284 | 268 | 6781700 | On test.
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 0 | 0 | Gas shortage
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 0 | 0 | Gas shortage
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 0 | 0 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 0 | 0 | Gas shortage
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 87 | 1435200 | Fuel shortage
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 37 | 443840 | Engine problem
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 40 | 1005940 | Machine problem
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 79 | 1668480 | High voltage
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 507024
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 205200
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 124 | 2425920
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 17 | 602500 | Engine problem
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 28 | 323443 | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 14 | 263270 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 40 | 129600 | Fuel conservation
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 17 | 339720 | Fuel shortage
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 107 | 1636320 | Engine problem
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 443520 | Engine problem
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 109 | 1256640
| Cumilla Area Total |  |  |  | 3169 | 1508 | 31009317
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 38 | 1641600 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 9 | 234612 | Gas shortage
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 11500
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 85 | 1252800 | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 97 | 1518000 | Engine problem
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 302780
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 287760 | Engine problem
| Mymensingh Area Total |  |  |  | 614 | 241 | 5249052
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 30 | 716000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 42 | 777000 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Gas shortage
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 25 | 291600 | Gas shortage
| Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 47 | 511560 | Gas shortage
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 2 | 61056 | Gas shortage
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 68 | 1523136
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 78 | 581760
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 65 | 1825300 | Machine problem
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 438000
| Sylhet 50MW PP (EPL) |  | NENP | 27*2 | 50 | 28 | 261000 | Gas shortage
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 0 | 0 | Gas shortage
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 280 | 7016500 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 422 | 9768000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 244440
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 400 | 9159200
| Sylhet Area Total |  |  |  | 2477 | 1515 | 33174552
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Fuel shortage
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 904 | 20782545
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 49 | 316800 | Engine problem
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 35 | 42440 | Line O/L
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 52 | 289664 | Engine problem
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 125 | 3457440 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 18 | 27000 | Fuel shortage
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 20 | 24000 | Fuel conservation
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 95 | 1550400 | Engine problem
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Fuel shortage
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 484560
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 0 | 0 | 0 | On test.
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 0 | 0 | 0 | 0 | On test.
| Khulna Area Total |  |  |  | 2384 | 1298 | 26974849
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Line O/L
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 20 | 406000 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 152 | 2496471 | Gas shortage
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 580 | 15427400 | Line O/L
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 108 | 3779318
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Line O/L
| Barisal 307 MW |  | BCPCL | 0 | 0 | 243 | 3148400 | On test.
| Barisal Area Total |  |  |  | 1958 | 1103 | 25257589
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 30 | 29427 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 4 | 8183 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contract Expired
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 34 | 462249 | Engine problem
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 40 | 74713 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 139 | 3642273 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 150 | 3781200 | Gas shortage
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 34 | 42518 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 14 | 416160 | Engine problem
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 245016
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 43 | 48000 | Engine problem
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 57 | 172072 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 836 | Fuel conservation
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 94 | 1848576 | Engine problem
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 95 | 1404960 | Engine problem
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 27960
| Rajshahi Area Total |  |  |  | 2129 | 745 | 12204143
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 160 | 3865700 | Machine problem
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 1491158
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 33250
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 113 | 1381056
| Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 159773
| Rangpur Area Total |  |  |  | 750 | 386 | 6930937
| Total |  |  |  | 21710 | 10671 | 211756970
| Eastern Grid Total |  |  |  | 14489 | 7139 | 140389452
| Western Grid Total |  |  |  | 7221 | 3532 | 71367518
| National Grid Total |  |  |  | 21710 | 10671 | 211756970
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2022-11-17
| (a) ENTIRE EASTERN GRID : |  | 7372.14 | MW | (b) ENTIRE WESTERN GRID : |  | 2964.42 | MW
| i) Dhaka area |  | 4131.34 | MW | i) Khulna area |  | 1129 | MW
| ii) Chittagong area |  | 1231.8 | MW | ii) Rajshahi area |  | 948.8 | MW
| iii) Comilla area |  | 849 | MW | iii) Barisal area |  | 246.62 | MW
| iv) Mymensingh area |  | 774 | MW | iv) Rangpur area |  | 640 | MW
| v) Sylhet area |  | 386 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 10336.56 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 26 | 09:00 | Chowmuhani | 126 | 19:00 | Kaptai | 4 | 18:00 | Nawabganj | 30 | 01:00 | Sholosohor | 25 | 18:00
2 | AKSML | 82 | 09:00 | Chuadanga | 68 | 18:00 | Kazla | 84 | 12:00 | Netrakona | 84 | 18:00 | Shyampur | 180 | 12:00
3 | Aftabnagar | 27 | 18:00 | Coxsbazar | 95 | 18:00 | Keranigonj | 44 | 18:00 | New | 67 | 12:00 | Siddhirganj | 76 | 18:30
4 | Agargaon | 62 | 13:00 | Cumilla(N) | 88 | 18:30 | Khagrachori | 22 | 18:00 | Niamatpur | 49 | 18:00 | Sirajganj | 69 | 18:30
5 | Agrabad | 68 | 11:00 | Cumilla(S) | 124 | 18:00 | Khulna | 73 | 18:00 | Noapara | 38 | 18:00 | Sonargaon | 95 | 02:00
6 | Amnura | 34 | 13:00 | Daudkandi | 96 | 18:30 | Khulshi | 165 | 11:00 | PHP | 3 | 14:00 | Sreemongol | 43 | 18:00
7 | Ashuganj | 51 | 00:00 | Dhaka | 32 | 12:00 | Kishoreganj | 96 | 18:30 | Pabna | 76 | 18:00 | Srinagar | 28.86 | 21:00
8 | BSRM | 143 | 19:30 | Dhamrai | 104 | 15:00 | Kodda | 276 | 16:00 | Palashbari | 86 | 18:30 | Sunamganj | 32 | 18:00
9 | Bagerhat | 72 | 19:30 | Dhanmondi | 108 | 13:00 | Kulaura | 30 | 18:00 | Panchagarh | 50 | 18:30 | Sylhet | 108 | 18:00
10 | Bakulia | 102 | 18:00 | Dohazari | 62 | 18:00 | Kurigram | 44 | 18:00 | Patuakhali | 77 | 21:00 | TK | 19.8 | 18:00
11 | Banani | 32 | 12:00 | Faridpur | 98 | 18:00 | Kushtia | 96 | 18:00 | Payra | 0.79 | 19:30 | Tangail | 142 | 18:00
12 | Bangabhaban | 13 | 10:00 | Fatullah | 57 | 10:00 | Lalbag | 72 | 18:30 | Postogola | 34 | 13:00 | Thakurgaon | 63 | 18:00
13 | Barapukuria | 42 | 18:30 | Fenchuganj | 31 | 18:00 | Lalmonirhat | 32 | 18:00 | Purbachal | 0 | 00:00 | Tongi | 107 | 11:00
14 | Barguna | 12 | 19:30 | Feni | 83 | 18:00 | Madanganj | 91 | 11:00 | Purbasadipur | 85 | 18:00 | Ullon | 33 | 18:00
15 | Barishal | 72 | 12:00 | GPH | 99 | 16:00 | Madaripur | 60 | 21:00 | Rahanpur_I | 7.6 | 19:30 | Uttara | 60 | 13:00
16 | Barishal-230 | 54 | 18:00 | Ghorashal | 140 | 04:00 | Madartek | 59 | 18:00 | Rahim | 40 | 06:00 | UttaraNew | 21 | 00:00
17 | Baroaulia | 65 | 11:00 | Goalpara | 20 | 13:00 | Madunaghat | 43 | 18:00 | Rajbari | 44 | 18:00 | Zigatola | 36 | 18:00
18 | Baroirhat | 34 | 18:00 | Gollamari | 34 | 18:00 | Magura | 40 | 18:00 | Rajendrapur | 100 | 20:00
19 | Bashundhara | 133 | 18:30 | Gopalganj | 68 | 18:00 | Mahasthangarh | 42 | 18:00 | Rajshahi | 90 | 18:00
20 | BashundharaCement | 1 | 09:00 | Gulshan | 88 | 13:00 | Manikganj | 66 | 20:00 | Rajshahi-230 | 24 | 18:30
21 | Beanibazar | 38 | 18:00 | Halishahar | 107 | 14:00 | Maniknagar | 58 | 11:00 | Ramganj | 70 | 18:00
22 | Benapole | 42 | 18:00 | HaripurSBU | 160 | 12:00 | Matarbari | 29 | 18:00 | Rampur | 22 | 18:00
23 | Bhaluka | 116 | 19:30 | Hasnabad | 79 | 11:00 | Matuail | 54 | 18:00 | Rangamati | 10 | 18:00
24 | Bhandaria | 34 | 21:00 | Hathazari | 46 | 18:00 | Millgate | 59 | 18:00 | Rangpur | 100 | 18:00
25 | Bhangura | 23 | 18:00 | Ishurdi | 52 | 18:00 | Mirpur | 99.5 | 18:30 | Ruppur | 4 | 15:00
26 | Bheramara(GK) | 37 | 18:00 | Jaldhaka | 46 | 18:00 | Mirsorai | N/A | N/A | SSM | 4 | 02:00
27 | Bhulta | 215 | 18:30 | Jamalpur | 104 | 18:00 | Mithapukur | 18 | 18:00 | Saidpur | 84 | 18:00
28 | Bog-Sherpur | 52 | 19:00 | Jashore | 107 | 20:00 | Modern | 0 | 00:00 | Satkhira | 71 | 18:00
29 | Bogura | 120 | 18:30 | Jhenaidah | 84 | 18:00 | Mogbazar | 104 | 18:00 | Satmasjid | 75 | 18:30
30 | Borhanuddin | 23 | 21:00 | Joydebpur | 138 | 19:00 | Mongla | 36 | 12:00 | Savar | 147 | 11:00
31 | Brahmanbaria | 106 | 18:00 | Joypurhat | 37 | 20:00 | Motijheel | 26 | 12:00 | Shahjadpur | 74 | 18:00
32 | Cantonment | 112 | 13:00 | Juldah | 28 | 00:00 | Munshiganj | 72 | 20:00 | Shahjibazar | 86 | 18:00
33 | Chandpur | 42 | 19:30 | KSRM | 55.5 | 14:00 | Mymensingh | 154 | 18:00 | Shahmirpur | 29.8 | 01:00
34 | Chandraghona | 24 | 18:00 | Kabirpur | 247 | 18:30 | Naogaon | 82 | 18:00 | Shariatpur | 46 | 20:00
35 | Chapai | 49 | 12:00 | Kachua | 46 | 18:00 | Narail | 36 | 18:00 | Sherpur | 90 | 18:00
36 | Charsaidpur | 47.58 | 12:00 | Kallyanpur | 66 | 12:00 | Narinda | 58 | 14:00 | Shikalbaha | 21 | 00:00
37 | Chauddagram | 29 | 18:00 | Kalurghat | 2 | 10:00 | Narshingdi | 136 | 19:30 | Shikalbaha-230 | N/A | N/A
38 | Chhatak | 18 | 18:00 | Kamrangirchar | 69 | 18:30 | Natore | 90 | 18:00 | Shitalakhya | 117 | 12:00
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2022-11-17 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Bhulta | 384 | 20:00 | 370 | 10:00 | Kaliakoir | 400 | 22:00 | 383 | 10:00
| Bibiana | 405 | 20:00 | 392 | 02:00 | Payra | 421 | 05:00 | 412 | 18:00
| BIPTC | 408 | 03:00 | 393 | 10:00 | Rahanpur_I | 412 | 18:00 | 389 | 10:00
| Gopalganj_I | 424 | 05:00 | 409 | 18:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 228 | 21:00 | 215 | 10:00 | Hasnabad | 228 | 22:00 | 215 | 16:00
| AKSML | 239 | 20:00 | 218 | 14:00 | Hathazari | 239 | 21:00 | 227 | 02:00
| Aminbazar | 226 | 22:00 | 216 | 23:00 | Ishurdi | 240 | 00:00 | 232 | 10:00
| Ashuganj | 240 | 21:00 | 230 | 10:00 | Jhenaidah | 241 | 04:00 | 233 | 12:00
| Baghabari | 237 | 22:00 | 231 | 12:00 | Kaliakoir | 230 | 21:00 | 219 | 10:00
| Barapukuria | 231 | 00:00 | 224 | 19:30 | Keranigonj | 227 | 21:00 | 214 | 10:00
| Barishal | 246 | 01:00 | 244 | 00:00 | Khulna(S) | 244 | 08:00 | 236 | 07:00
| Bheramara | 238 | 04:00 | 229 | 10:00 | Maniknagar | 229 | 18:00 | 217 | 10:00
| Bhulta | 229 | 20:00 | 220 | 10:00 | Meghnaghat | 233 | 03:00 | 223 | 16:00
| Bibiana | 238 | 18:30 | 232 | 05:00 | Mirsorai | N/A | N/A | N/A | N/A
| BIPTC | 241 | 04:00 | 231 | 12:00 | Rajshahi | 243 | 05:00 | 233 | 11:00
| Bogura | 236 | 00:00 | 232 | 06:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 250 | 04:00 | 245 | 17:00 | Rampura | 228 | 20:00 | 218 | 10:00
| BSRM | 236 | 19:00 | 221 | 14:00 | Shahmirpur | 139 | 20:00 | 129 | 14:00
| Cumilla(N) | 233 | 20:00 | 220 | 09:00 | Shikalbaha | 241 | 21:00 | 223 | 15:00
| Fenchuganj | 241 | 22:00 | 231 | 09:00 | Shyampur | 227 | 21:00 | 215 | 10:00
| Ghorashal | N/A | N/A | N/A | N/A | Siddhirganj | 228 | 20:00 | 221 | 15:00
| GPH | 238 | 19:00 | 221 | 10:00 | Sirajgonj | 234 | 00:00 | 229 | 10:00
| Haripur | 227 | 22:00 | 218 | 10:00 | Tongi | 228 | 22:00 | 213 | 09:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 136 | 21:00 | 128 | 16:00 | Lalbag | 138 | 05:00 | 130 | 10:00
| Agargaon | 137 | 21:00 | 128 | 10:00 | Lalmonirhat | 135 | 22:00 | 130 | 01:00
| Agrabad | 139 | 21:00 | 128 | 10:00 | Madanganj | 134 | 21:00 | 128 | 10:00
| AKS | 138 | 20:00 | 125 | 15:00 | Madaripur | 140 | 05:00 | 136 | 16:00
| Aminbazar | 136 | 23:00 | 133 | 09:00 | Madartek | 135 | 04:00 | 128 | 10:00
| Amnura | 136 | 21:00 | 127 | 12:00 | Madunaghat | 140 | 19:30 | 130 | 10:00
| Ashuganj | 138 | 00:00 | 135 | 10:00 | Magura | 140 | 01:00 | 133 | 18:00
| Bagerhat | 139 | 00:00 | 130 | 08:00 | Mahasthangarh | 140 | 21:00 | 133 | 03:00
| Bakulia | 139 | 20:00 | 128 | 10:00 | Manikganj | 135 | 14:00 | 127 | 00:00
| Banani | 136 | 21:00 | 126 | 10:00 | Maniknagar | 134 | 21:00 | 120 | 16:00
| Bangabhaban | 133 | 20:00 | 120 | 16:00 | Matarbari | 130 | 20:00 | 121 | 14:00
| Barapukuria | 138 | 00:00 | 134 | 05:00 | Matuail | 133.5 | 20:00 | 127 | 10:00
| Barguna | 136 | 10:00 | 130 | 18:00 | Millgate | 136 | 21:00 | 126 | 15:00
| Barishal | 141 | 04:00 | 128 | 18:00 | Mirpur | 139 | 20:00 | 125 | 00:00
| Barishal-230 | 141 | 01:00 | 138 | 19:30 | Mithapukur | 139 | 20:00 | 133 | 03:00
| Baroaulia | 142 | 21:00 | 128 | 14:00 | Modern | 139 | 20:00 | 127 | 14:00
| Baroirhat | 139 | 18:30 | 130 | 10:00 | Mogbazar | 136 | 00:00 | 130 | 10:00
| Bashundhara | 138 | 22:00 | 127 | 10:00 | Mongla | 138 | 21:00 | 130 | 08:00
| BashundharaCement | 134 | 21:00 | 128 | 10:00 | Motijheel | 133 | 20:00 | 120 | 16:00
| Beanibazar | 133 | 04:00 | 131 | 00:00 | Munshiganj | 134 | 19:00 | 128 | 10:00
| Benapole | 138 | 00:00 | 130 | 08:00 | Mymensingh | 135 | 18:30 | 123 | 13:00
| Bhaluka | 133 | 18:30 | 120 | 15:00 | Naogaon | 138 | 21:00 | 132 | 07:00
| Bhandaria | 141 | 04:00 | 138 | 18:00 | Narail | 139 | 04:00 | 132 | 12:00
| Bhangura | 142 | 21:00 | 137 | 10:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bheramara | 138 | 00:00 | 134 | 16:00 | Narshingdi | 130 | 07:00 | 123 | 15:00
| Bheramara(GK) | 140 | 00:00 | 135 | 15:00 | Natore | 137 | 21:00 | 132 | 11:00
| Bhulta | 128 | 04:00 | 122 | 10:00 | Nawabganj | 138 | 21:00 | 130 | 16:00
| Bog-Sherpur | 140 | 00:00 | 134 | 12:00 | Netrakona | 137 | 22:00 | 121 | 13:00
| Bogura | 140 | 00:00 | 135 | 11:00 | New | 137 | 22:00 | 127 | 10:00
| Bogura-230 | 140 | 00:00 | 135 | 12:00 | Niamatpur | 135 | 03:00 | 130 | 07:00
| Brahmanbaria | 134 | 22:00 | 129 | 15:00 | Noapara | 139 | 04:00 | 131 | 08:00
| Cantonment | 136 | 22:00 | 127 | 10:00 | Pabna | 139 | 00:00 | 134 | 12:00
| Chandpur | 142 | 20:00 | 135 | 10:00 | Palashbari | 138 | 21:00 | 132 | 03:00
| Chandraghona | 141 | 20:00 | 130 | 10:00 | Panchagarh | 138 | 21:00 | 126 | 19:30
| Chapai | 135 | 01:00 | 128 | 12:00 | Patuakhali | 136 | 04:00 | 133 | 12:00
| Charsaidpur | 135 | 20:00 | 128 | 16:00 | Payra | 138.6 | 05:00 | 135 | 18:00
| Chauddagram | 140 | 18:30 | 131 | 10:00 | PHP | 140 | 21:00 | 130 | 10:00
| Chhatak | 131 | 04:00 | 130 | 00:00 | Postogola | 141 | 21:00 | 132 | 10:00
| Chowmuhani | 140 | 21:00 | 132 | 10:00 | Purbachal | 137 | 22:00 | 127 | 16:00
| Chuadanga | 138 | 02:00 | 130 | 12:00 | Purbasadipur | 136 | 20:00 | 127 | 19:00
| Coxsbazar | 130 | 21:00 | 119 | 13:00 | Rahim | 134 | 20:00 | 128 | 10:00
| Cumilla(N) | 139 | 19:00 | 131 | 09:00 | Rajbari | 138 | 04:00 | 132 | 17:00
| Cumilla(S) | 141 | 20:00 | 129 | 12:00 | Rajendrapur | 135 | 17:00 | 124 | 00:00
| Daudkandi | 136 | 20:00 | 129 | 10:00 | Rajshahi | 134 | 21:00 | 128 | 12:00
| Dhaka | 136 | 22:00 | 129 | 10:00 | Rajshahi-230 | 134 | 18:30 | 127 | 11:00
| Dhamrai | 138 | 22:00 | 129 | 10:00 | Ramganj | 141 | 22:00 | 133 | 14:00
| Dhanmondi | 134 | 03:00 | 128 | 10:00 | Rampur | 139 | 21:00 | 128 | 15:00
| Dohazari | 136 | 21:00 | 126 | 14:00 | Rampura | 135 | 00:00 | 129 | 10:00
| Faridpur | 137 | 05:00 | 132 | 17:00 | Rangamati | 139 | 20:00 | 129 | 10:00
| Fatullah | 134 | 22:00 | 126 | 10:00 | Rangpur | 136 | 00:00 | 130 | 04:00
| Fenchuganj | 137 | 20:00 | 134 | 00:00 | Ruppur | 138 | 00:00 | 135 | 10:00
| Feni | 140 | 18:30 | 133 | 10:00 | Saidpur | 138 | 21:00 | 130 | 12:00
| Ghorashal | 138 | 07:00 | 136 | 01:00 | Satkhira | 138 | 00:00 | 128 | 08:00
| Goalpara | 141 | 21:00 | 135 | 08:00 | Satmasjid | 136 | 21:00 | 128 | 10:00
| Gollamari | 140 | 21:00 | 130 | 08:00 | Savar | 141 | 22:00 | 128 | 10:00
| Gopalganj | 140 | 21:00 | 131 | 08:00 | Shahjadpur | 143 | 00:00 | 138 | 10:00
| Gopalganj_I | 139 | 04:00 | 134 | 18:00 | Shahjibazar | 136 | 21:00 | 132 | 10:00
| Gulshan | 135 | 05:00 | 128 | 15:00 | Shariatpur | 139 | 05:00 | 135 | 18:00
| Halishahar | 139 | 21:00 | 127 | 14:00 | Sherpur | 137 | 12:00 | 126 | 15:00
| Haripur | 134 | 20:00 | 128 | 10:00 | Shikalbaha | 140 | 19:30 | 128 | 15:00
| HaripurSBU | 134 | 00:00 | 129 | 12:00 | Shikalbaha-230 | 139 | 19:30 | 129 | 15:00
| Hasnabad | 141 | 21:00 | 133 | 10:00 | Shitalakhya | 140 | 20:00 | 131 | 10:00
| Hathazari | 141 | 19:00 | 131 | 13:00 | Sholosohor | 139 | 20:00 | 128 | 10:00
| Ishurdi | 140 | 21:00 | 135 | 11:00 | Shyampur | 133 | 21:00 | 129 | 11:00
| Jaldhaka | 135 | 09:00 | 128 | 19:30 | Shyampur-230 | 134 | 00:00 | 126 | 10:00
| Jamalpur | 139 | 19:30 | 127 | 15:00 | Siddhirganj | 134 | 21:00 | 128 | 10:00
| Jashore | 137 | 04:00 | 130 | 13:00 | Sirajganj | 140 | 00:00 | 134 | 11:00
| Jhenaidah | 140 | 00:00 | 134 | 12:00 | Sonargaon | 135 | 00:00 | 129 | 07:00
| Jhenaidah-230 | 140 | 04:00 | 134 | 19:30 | Sreemongol | 138 | 17:00 | 134 | 11:00
| Joydebpur | 140 | 08:00 | 135 | 02:00 | Srinagar | 138 | 21:00 | 130 | 10:00
| Joypurhat | 138 | 21:00 | 132 | 08:00 | SSM | 142 | 21:00 | 130 | 15:00
| Juldah | 140 | 21:00 | 127 | 15:00 | Sunamganj | 131 | 09:00 | 129 | 12:00
| Kabirpur | 136 | 21:00 | 124 | 10:00 | Sylhet | 133 | 09:00 | 132 | 00:00
| Kachua | 140 | 20:00 | 134 | 10:00 | Tangail | 134 | 18:30 | 128 | 07:00
| Kaliakoir | 136 | 19:30 | 129 | 10:00 | Thakurgaon | 138 | 09:00 | 127 | 19:30
| Kallyanpur | 140 | 21:00 | 129 | 10:00 | TK | 140 | 22:00 | 128 | 09:00
| Kalurghat | 140 | 20:00 | 129 | 14:00 | Tongi | 139 | 02:00 | 129 | 15:00
| Kamrangirchar | 138 | 21:00 | 130 | 10:00 | Ullon | 136 | 22:00 | 128 | 10:00
| Kaptai | 135 | 00:00 | 130 | 14:00 | Uttara | 136 | 21:00 | 126 | 10:00
| Kazla | 133 | 19:30 | 121 | 10:00 | UttaraNew | 138 | 20:00 | 129 | 10:00
| Keranigonj | 139 | 22:00 | 129 | 10:00 | Zigatola | 138 | 22:00 | 130 | 16:00
| Khagrachori | 138 | 19:00 | 128 | 14:00
| Khulna | 139 | 01:00 | 130 | 08:00
| Khulna(S) | 140 | 05:00 | 130 | 08:00
| Khulshi | 137 | 20:00 | 126 | 14:00
| Kishoreganj | 136 | 00:00 | 125 | 13:00
| Kodda | 140 | 08:00 | 127 | 00:00
| KSRM | 139 | 20:00 | 128 | 15:00
| Kulaura | 135 | 00:00 | 134 | 16:00
| Kurigram | 137 | 21:00 | 129 | 03:00
| Kushtia | 139 | 00:00 | 134 | 16:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2022-11-17
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 1120 | 5659 | 3003 | 8662 |  |  |  | QF-LDC-11
0:30 | 1065 | 5435 | 2869.5 | 8304.5 | Date: | 2022-11-17
1:00 | 1010 | 5211 | 2736 | 7947
1:30 | 1005 | 5052 | 2668 | 7720
2:00 | 1000 | 4893 | 2600 | 7493
2:30 | 1000 | 4899 | 2464 | 7363 | [5 empty] | Gen. at Eve. Peak | 10671 | 10671 MW (18:00 )
3:00 | 1000 | 4905 | 2328 | 7233 | [6 empty] | 18:00
3:30 | 920 | 4891.5 | 2312.5 | 7204 | [5 empty] | Gen. at Day Peak | 9295 | 9295 MW (12:00 )
4:00 | 840 | 4878 | 2297 | 7175 | [6 empty] | 12:00
4:30 | 790 | 4823 | 2292.5 | 7115.5 | [5 empty] | Highest Generation | 10671
5:00 | 740 | 4768 | 2288 | 7056 | [6 empty] | 18:00
5:30 | 715 | 4786 | 2300.5 | 7086.5
6:00 | 690 | 4804 | 2313 | 7117
6:30 | 530 | 4974.5 | 2396 | 7370.5
7:00 | 370 | 5145 | 2479 | 7624
7:30 | 505 | 5294 | 2689 | 7983
8:00 | 640 | 5443 | 2899 | 8342
8:30 | 875 | 5454 | 2962 | 8416
9:00 | 1110 | 5465 | 3025 | 8490
9:30 | 1208 | 5522 | 2961 | 8483
10:00 | 1306 | 5579 | 2897 | 8476
10:30 | 1258 | 5832 | 2863.5 | 8695.5
11:00 | 1210 | 6085 | 2830 | 8915
11:30 | 1020 | 6261.5 | 2843.5 | 9105
12:00 | 830 | 6438 | 2857 | 9295
12:30 | 835 | 6537 | 2896.5 | 9433.5
13:00 | 840 | 6636 | 2936 | 9572
13:30 | 915 | 6401.5 | 2930 | 9331.5
14:00 | 990 | 6167 | 2924 | 9091
14:30 | 1080 | 6164.5 | 2922 | 9086.5
15:00 | 1170 | 6162 | 2920 | 9082
15:30 | 1230 | 6013 | 2912 | 8925
16:00 | 1290 | 5864 | 2904 | 8768
16:30 | 1235 | 5945.5 | 2936 | 8881.5
17:00 | 1180 | 6027 | 2968 | 8995
17:30 | 1015 | 6583 | 3250 | 9833
18:00 | 850 | 7139 | 3532 | 10671
18:30 | 780 | 7007 | 3506.5 | 10513.5
19:00 | 710 | 6875 | 3481 | 10356
19:30 | 650 | 6831 | 3324 | 10155
20:00 | 710 | 6771 | 3355 | 10126 |  |  |  | Executive Engineer
20:30 | 791 | 6647 | 3326.5 | 9973.5 |  |  |  | Network Operation Division
21:00 | 872 | 6523 | 3298 | 9821
21:30 | 821 | 6454.5 | 3156 | 9610.5
22:00 | 770 | 6386 | 3014 | 9400 |  |  |  |  | Page 6 of 7
22:30 | 875 | 6223.5 | 3001.5 | 9225
23:00 | 980 | 6061 | 2989 | 9050
23:30 | 1050 | 5860 | 2996 | 8856
24:00 | 1120 | 5659 | 3003 | 8662
10671 MW (18:00 )
9295 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2022-11-17 |  | Energy |  | 211756970
[13 empty] | 2022-11-17 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 3284 | 905 | 1309 | 65 | 1928 | 970 | 46 | 0 | 49 | 106 | 0 | 0
0:30 | 3283.5 | 905 | 1321 | 32.5 | 1712 | 871.5 | 46 | 0 | 33 | 100 | 0 | 0 | Date: | 2022-11-17
1:00 | 3283 | 905 | 1333 | 0 | 1496 | 773 | 46 | 0 | 17 | 94 | 0 | 0
1:30 | 3286 | 905.5 | 1325 | 0 | 1280.5 | 769 | 46 | 0 | 17 | 91 | 0 | 0 | [8 empty] | Total Energy | 211.757 | Total Energy Gen 211.757 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 211.757 MKWHr
2:00 | 3289 | 906 | 1317 | 0 | 1065 | 765 | 46 | 0 | 17 | 88 | 0 | 0 | [8 empty] | Energy not Served | 0
2:30 | 3299 | 827 | 1314.5 | 0 | 1006 | 765.5 | 46 | 0 | 17 | 88 | 0 | 0 | [8 empty] | Energy Requirement | 211.757
3:00 | 3309 | 748 | 1312 | 0 | 947 | 766 | 46 | 0 | 17 | 88 | 0 | 0
3:30 | 3313 | 732.5 | 1310 | 0 | 933 | 765.5 | 46 | 0 | 17 | 87 | 0 | 0 | [6 empty] | Shortage
4:00 | 3317 | 717 | 1308 | 0 | 919 | 765 | 46 | 0 | 17 | 86 | 0 | 0
4:30 | 3316.5 | 716.5 | 1300 | 0 | 869.5 | 765 | 46 | 0 | 17 | 85 | 0 | 0
5:00 | 3316 | 716 | 1292 | 0 | 820 | 765 | 46 | 0 | 17 | 84 | 0 | 0
5:30 | 3317.5 | 716 | 1307.5 | 0 | 830.5 | 770 | 46 | 0 | 17 | 82 | 0 | 0
6:00 | 3319 | 716 | 1323 | 0 | 841 | 775 | 46 | 0 | 17 | 80 | 0 | 0
6:30 | 3367 | 718 | 1340 | 0 | 985.5 | 790 | 46 | 0 | 33 | 82 | 9 | 0 |  |  |  |  | Coal
7:00 | 3415 | 720 | 1357 | 0 | 1130 | 805 | 46 | 0 | 49 | 84 | 18 | 0
7:30 | 3347 | 765 | 1339 | 0 | 1447 | 818 | 46 | 0 | 90.5 | 86 | 44.5 | 0 |  |  |  | Oil |  |  |  | ,
8:00 | 3279 | 810 | 1321 | 0 | 1764 | 831 | 46 | 0 | 132 | 88 | 71 | 0
8:30 | 3194 | 857 | 1339.5 | 0 | 1812 | 828 | 46 | 0 | 144 | 91 | 104.5 | 0
9:00 | 3109 | 904 | 1358 | 0 | 1860 | 825 | 46 | 0 | 156 | 94 | 138 | 0
9:30 | 3131 | 904.5 | 1354 | 0 | 1845 | 795 | 46 | 0 | 150.5 | 96 | 161 | 0
10:00 | 3153 | 905 | 1350 | 0 | 1830 | 765 | 46 | 0 | 145 | 98 | 184 | 0
10:30 | 3109.5 | 904.5 | 1340 | 35 | 2041 | 765 | 46 | 0 | 156.5 | 101 | 197 | 0
11:00 | 3066 | 904 | 1330 | 70 | 2252 | 765 | 46 | 0 | 168 | 104 | 210 | 0
11:30 | 3092.5 | 904 | 1334.5 | 110 | 2358.5 | 770 | 46 | 0 | 171 | 107 | 211.5 | 0
12:00 | 3119 | 904 | 1339 | 150 | 2465 | 775 | 46 | 0 | 174 | 110 | 213 | 0
12:30 | 3119.5 | 903.5 | 1342.5 | 222 | 2512.5 | 795 | 46 | 0 | 176.5 | 110 | 206 | 0
13:00 | 3120 | 903 | 1346 | 294 | 2560 | 815 | 46 | 0 | 179 | 110 | 199 | 0
13:30 | 3120 | 903 | 1346 | 294 | 2560 | 815 | 46 | 0 | 179 | 110 | 199 | 0
14:00 | 3120 | 903 | 1346 | 294 | 2560 | 815 | 46 | 0 | 179 | 110 | 199 | 0
14:30 | 3093 | 903 | 1337.5 | 313 | 2344 | 840 | 46 | 0 | 185.5 | 112 | 153 | 0
15:00 | 3066 | 903 | 1329 | 332 | 2128 | 865 | 46 | 0 | 192 | 114 | 107 | 0
15:30 | 3062.5 | 903.5 | 1316.5 | 166 | 2171 | 872.5 | 46 | 0 | 204 | 110 | 73 | 0
16:00 | 3059 | 904 | 1304 | 0 | 2214 | 880 | 46 | 0 | 216 | 106 | 39 | 0
16:30 | 3048 | 903.5 | 1312.5 | 0 | 2316.5 | 899 | 46 | 0 | 223 | 107 | 20.5 | 0
17:00 | 3048 | 903 | 1321 | 0 | 2419 | 918 | 46 | 0 | 230 | 108 | 2 | 0
17:30 | 3130 | 903.5 | 1343 | 90 | 2859.5 | 950.5 | 63 | 0 | 376.5 | 116 | 1 | 0
18:00 | 3212 | 904 | 1365 | 180 | 3300 | 983 | 80 | 0 | 523 | 124 | 0 | 0
18:30 | 3194.5 | 904.5 | 1348 | 90 | 3292.5 | 1043 | 80 | 0 | 438 | 123 | 0 | 0
19:00 | 3177 | 905 | 1331 | 0 | 3285 | 1103 | 80 | 0 | 353 | 122 | 0 | 0
19:30 | 3152 | 905 | 1348 | 0 | 3158 | 1137 | 80 | 0 | 261 | 114 | 0 | 0
20:00 | 3125 | 905 | 1314 | 0 | 3313 | 1010 | 80 | 0 | 261 | 118 | 0 | 0
20:30 | 3092.5 | 905 | 1262.5 | 0 | 3290.5 | 965 | 80 | 0 | 261 | 117 | 0 | 0
21:00 | 3060 | 905 | 1211 | 0 | 3268 | 920 | 80 | 0 | 261 | 116 | 0 | 0
21:30 | 3109 | 905 | 1249 | 0 | 3037 | 925 | 80 | 0 | 192.5 | 113 | 0 | 0
22:00 | 3158 | 905 | 1287 | 0 | 2806 | 930 | 80 | 0 | 124 | 110 | 0 | 0
22:30 | 3189.5 | 905.5 | 1301 | 0 | 2626 | 940 | 63 | 0 | 94 | 106 | 0 | 0
23:00 | 3221 | 906 | 1315 | 0 | 2446 | 950 | 46 | 0 | 64 | 102 | 0 | 0
23:30 | 3252.5 | 905.5 | 1312 | 32.5 | 2187 | 960 | 46 | 0 | 56.5 | 104 | 0 | 0 | Max Temp. in Dhaka |  | 24.7° C | 30.7° C
24:00 | 3284 | 905 | 1309 | 65 | 1928 | 970 | 46 | 0 | 49 | 106 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 211.757 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 211.757 MKWHr
Note on W13: Author:

## Generation
g | 2022-11-17
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 80 |  | 80 | 80 | 80 | 80 | 80 | 46 | 46 | 1275715
2 | Karnaphuli Hydro PP Unit-4 & 5 | [26 empty] | 0
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [6 empty] | 3 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 301721
| Teknaf 20MW PP (Solartech) | [6 empty] | 4 | 5 | 16 | 19 | 20 | 20 | 18 | 16 | 11 | 3 | 0 | [9 empty] | 131625
6 | Sikalbaha 225MW CCPP (Gas) | 151 | 151 | 152 | 151 | 151 | 151 | 151 | 152 | 152 | 150 | 151 | 152 | 151 | 151 | 151 | 151 | 151 | 150 |  | 151 | 151 | 151 | 151 | 151 | 151 | 151 | 3539916
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 16 | 17 | 17 | 18 | 51 |  | 51 | 51 | 51 | 51 | 51 | 32 | 17 | 583589
12 | Hathazari 100 MW peaking PP | [8 empty] | 24 | 23 | 23 | 23 | 31 | 49 | 40 | 40 | 40 | 50 |  | 0 | [6 empty] | 323520
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 41 | 69 | 69 | 69 | 69 | 68 | 76 | 102 | 105 |  | 105 | 105 | 105 | 105 | 105 | 67 | 34 | 1527200
| Daudkandi 200 MW PP (B.Trac) | [10 empty] | 10 | 10 | 10 | 20 | 20 | 0 | 0 | 40 |  | 0 | [6 empty] | 129600
14 | Titas 50 MW Peaking PP | [9 empty] | 7 | 30 | 36 | 37 | 37 | 37 | 44 | 44 | 37 |  | 37 | 37 | 37 | 37 | 37 |  | 0 | 443840
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 262 |  | 260 | 260 | 260 | 260 | 260 | 260 | 130 | 3291927
19 | Ashuganj 195MW PP (APSCL-United) | [7 empty] | 0 | 0 | 0 | 0 | [12 empty] | 0 | 0 | 0 | 0
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4347000
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
33 | Ashuganj 225 MW CCPP | 175 | 175 | 175 | 175 | 175 | 175 | 207 | 210 | 176 | 194 | 176 | 184 | 192 | 175 | 195 | 190 | 190 | 199 |  | 180 | 180 | 180 | 172 | 176 | 176 | 176 | 4477000
34 | Ashuganj 450 MW CCPP(South) | 305 | 305 | 305 | 305 | 305 | 305 | 355 | 335 | 275 | 320 | 310 | 310 | 310 | 305 | 270 | 330 | 270 | 295 |  | 240 | 240 | 240 | 240 | 240 | 240 | 280 | 7064000
Ashuganj 450 MW CCPP(North)
| Ashuganj 420 MW CCPP(East) | 288 | 288 | 288 | 288 | 288 | 288 | 288 | 288 | 287 | 288 | 288 | 288 | 288 | 288 | 288 | 267 | 268 | 268 |  | 268 | 268 | 288 | 288 | 288 | 288 | 288 | 6781700
35 | Ashuganj 55 MW PP (Precision) | [25 empty] | 0 | 0
36 | Chandpur 150 MW CCPP | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 44 | 39 | 39 | 39 | 39 | 40 | 40 | 40 | 40 |  | 39 | 39 | 40 | 40 | 40 | 40 | 44 | 1005940
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 377 | 374 | 376 | 376 | 376 | 376 | 377 | 378 | 379 | 374 | 375 | 371 | 373 | 385 | 382 | 379 | 375 | 372 |  | 371 | 369 | 367 | 370 | 379 | 375 | 376 | 9121800
40 | Meghnaghat 450 MW CCPP(MPL) | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 |  | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 5200400
41 | Haripur 360MW CCPP(HPL) | 322 | 323 | 322 | 323 | 323 | 333 | 330 | 332 | 332 | 328 | 327 | 322 | 322 | 317 | 311 | 312 | 311 | 307 |  | 307 | 307 | 303 | 252 | 313 | 312 | 312 | 7594000
42 | RPCL 210MW CCPP | 103 | 103 | 102 | 104 | 104 | 104 | 86 | 72 | 73 | 41 | 41 | 37 | 35 | 35 | 35 | 35 | 38 | 38 |  | 57 | 75 | 74 | 75 | 100 | 103 | 103 | 1641600
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 4 | 18 | 32 | 41 | 46 | 47 | 45 | 35 | 24 | 9 | 1 | 0 | [8 empty] | 302780
44 | Fenchugonj CCPP Phase-1 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 716000
45 | Fenchugonj CCPP Phase-2 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 |  | 42 | 0 | [5 empty] | 777000
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 70 | 70 | 70 | 70 | 70 | 70 | 68 | 40 | 65 | 62 | 62 | 62 | 62 | 64 | 62 | 61 | 63 | 68 |  | 69 | 68 | 70 | 70 | 40 | 40 | 71 | 1523136
48 | Shahjibazar 86MW PP (Shahjibazar) | [16 empty] | 0 | 78 |  | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 581760
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 140 | 140 | 140 | 140 | 140 | 140 | 135 | 100 | 20 | 20 | 20 | 20 | 25 | 20 | 20 | 20 | 20 | 65 |  | 68 | 67 | 68 | 68 | 84 | 84 | 84 | 1825300
51 | Sylhet 20 MW GTPP | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 19 | 19 | 19 | 19 | 19 | 438000
52 | Sylhet 50MW PP (EPL) | [8 empty] | 7 | 20 | 20 | 21 | 23 | 24 | 24 | 24 | 26 | 28 |  | 29 | 29 | 29 | 0 |  |  | 0 | 261000
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 244440
54 | Hobiganj 11MW PP Cofidence-E | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 61056
55 | Fenchugonj 51 MW PP (Barakatullah) | [8 empty] | 22 | 22 | 31 | 31 | 31 | 31 | 31 | 28 | 31 | 25 |  | 5 | 5 | 0 |  |  |  | 0 | 291600
56 | Shahjahanulla 25 MW PP | [25 empty] | 0 | 0
57 | Bibiana-II 341 MW CCPP (Summit) | 270 | 260 | 295 | 280 | 270 | 290 | 300 | 280 | 280 | 290 | 270 | 280 | 300 | 280 | 295 | 310 | 310 | 280 |  | 270 | 290 | 280 | 260 | 270 | 290 | 280 | 7016500
| Bibiyana South 400 MW | 340 | 341 | 390 | 400 | 400 | 360 | 400 | 400 | 400 | 400 | 350 | 400 | 400 | 400 | 400 | 390 | 400 | 400 |  | 400 | 400 | 360 | 292 | 356 | 400 | 394 | 9159200
58 | Nababganj 55 MW PP (Southern power ) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 55 | 55 | 55 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 911630
59 | Tangail Palli Power Gen 22 MW | 10 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 5 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 287760
60 | Barabkunda 22 MW PP (Regent)
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 498528
62 | Tangail 22 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 9 | 10 | 10 | 9 |  | 8 | 8 | 10 | 9 | 9 | 9 | 9 | 234612
63 | Impoprt (Tripura) | 94 | 88 | 88 | 86 | 84 | 80 | 84 | 88 | 94 | 98 | 104 | 110 | 110 | 114 | 114 | 106 | 108 | 124 |  | 122 | 114 | 118 | 116 | 110 | 102 | 106 | 2425920
64 | Malancha, Ctg. EPZ (United) | 2 | 2 | 2 | 5 | 10 | 10 | 2 | 2 | 0 | 0 | 0 | 0 | 2 | 2 | 2 | 2 | 2 | 2 |  | 2 | 4 | 2 | 2 | 2 | 6 | 7 | 54240
65 | Feni 22MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 507024
66 | Feni 11 MW PP (Doreen) | 10 | 10 | 10 | 10 | 10 | 10 | 8 | 8 | 8 | 8 | 8 | 8 | 10 | 10 | 10 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 205200
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 23 | 16 | 16 | 15 | 15 | 15 | 15 | 16 | 16 | 16 | 17 |  | 25 | 25 | 28 | 33 | 33 | 33 | 33 | 602500
68 | Cumilla 25 MW PP (Summit) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 0 | 5 | 14 |  | 18 | 18 | 21 | 21 | 21 | 21 | 21 | 263270
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 600000
70 | Summit Madhabdi | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 18 | 18 | 18 | 18 | 26 | 26 |  | 26 | 26 | 26 | 18 | 24 | 26 | 27 | 581580
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 813900
72 | Rupganj 33 MW PP(Summit) | 25 | 25 | 28 | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 27 | 27 | 28 | 642500
73 | Ghorashal 108MW PP (Regent) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 68 | 68 | 68 | 70 | 68 | 71 | 71 | 71 | 71 | 71 |  | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 1642409
| Feni Lanka Power | 17 | [5 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 339720
| Chowmuhani 113 MW | 57 | 8 | 8 | 8 |  |  | 21 | 57 | 58 | 57 | 60 | 80 | 87 | 87 | 86 | 105 | 107 | 107 |  | 107 | 108 | 107 | 108 | 107 | 101 | 75 | 1636320
| Manikgonj 162MW PP(MPGL) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 154 | 162 | 162 | 72 | 72 | 72 | 162 | 162 |  | 162 | 162 | 162 | 162 | 162 | 35 | 35 | 1804320
77 | Siddhirganj 100 PP(Dutch Bangla) | 87 |  |  |  |  | 1 | 14 | 58 | 63 | 65 | 65 | 71 | 71 | 75 | 75 | 65 | 65 | 78 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1312493
78 | Gazipur 52 MW PP | [6 empty] | 4 | 30 | 41 | 41 | 41 | 41 | 49 | 49 | 49 | 49 | 49 | 49 |  | 49 | 41 | 41 | 41 | 41 | 42 | 50 | 758880
79 | Kodda 150MW PP | [6 empty] | 32 | 115 | 115 | 98 | 98 | 98 | 82 | 98 | 98 | 115 | 128 | 133 |  | 82 | 64 | 64 | 64 | 36 | 32 | 32 | 1563360
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 28 |  | 39 | 42 | 42 | 42 | 8 | 8 | 8 | 323443
| Gazipur 100 MW PP | 34 | 17 | 17 | 17 | 17 | 17 | 31 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2013696
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 1 | 2 | 4 | 4 | 4 | 4 | 3 | 2 | 1 | 0 | [9 empty] | 26520
| Jodiac Power | 17 |  |  |  |  | 14 | 36 | 36 | 36 | 36 | 54 | 54 | 54 | 36 | 36 | 36 | 36 | 36 |  | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 772089
| Karnaphuli Power Ltd. | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 59 | 73 | 73 | 73 | 73 | 73 | 82 | 91 | 91 |  | 91 | 91 | 91 | 81 | 73 | 67 | 53 | 1668538
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL) | [6 empty] | 0 | 21 | 37 | 51 | 69 | 78 | 82 | 82 | 80 | 76 | 82 | 83 |  | 82 | 83 | 84 | 83 | 83 | 84 | 53 | 1218240
| Meghnaghat 104 MW PP (OPCL) | 55 | 48 | 17 | 17 |  | 3 | 30 | 53 | 54 | 55 | 55 | 55 | 65 | 62 | 61 | 53 | 54 | 66 |  | 55 | 55 | 54 | 54 | 55 | 55 | 56 | 1152000
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 44 |  | 44 | 44 | 44 | 44 | 44 | 44 | 22 | 650520
92 | Fenchuganj 44MW (Energyprima) | [8 empty] | 41 | 46 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 |  | 30 | 30 | 0 |  |  |  | 0 | 511560
93 | Ashuganj 51 MW PP (Midland)
94 | Gagnagar 102 MW PP (Digital Power) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 41 | 41 | 41 | 41 | 41 | 33 | 33 | 33 | 66 |  | 66 | 66 | 66 | 66 | 66 | 66 | 33 | 1018656
95 | Patenga 50MW PP (Baraka) | 19 | 9 |  |  |  |  | 7 | 21 | 26 |  | 1 | 14 | 18 | 24 | 32 | 43 | 44 | 44 |  | 44 | 44 | 44 | 44 | 44 | 44 | 9 | 550080
96 | Chattogram 108 MW PP (ECPV) | [25 empty] | 0 | 0
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1329172
100 | Manikganj 55 MW PP (Northern) | [6 empty] | 17 | 35 | 35 | 35 | 55 | 55 | 55 | 35 | 35 | 35 | 35 | 35 |  | 55 | 55 | 55 | 35 | 35 | 35 | 35 | 677122
101 | Kushiara 163 MW CCPP (KP)
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 1 | 0 | 0 | [9 empty] | 11500
103 | Kamalaghat 54 MW PP(Banco Energy) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 |  | 54 | 54 | 54 | 17 | 17 | 17 | 17 | 517680
104 | Keranigonj 300 MW PP (APR) | [10 empty] | 10 | 40 | 123 | 100 | 130 | 0 | 0 | 20 |  | 0 | [5 empty] | 15 | 576092
105 | Bramhangoan 100 MW PP (Aggreko) | [10 empty] | 25 | 50 | 96 | 92 | 95 | 0 | 0 | 50 |  | 0 | [5 empty] | 25 | 458819
106 | Mymensingh 200 MW PP (United) | 48 | 8 | 8 | 8 | 8 | 8 | 21 | 47 | 47 | 48 | 58 | 81 | 79 | 56 | 51 | 57 | 57 | 85 |  | 87 | 87 | 86 | 88 | 88 | 88 | 53 | 1252800
112 | Aurahati 100MW PP (Aggreko) | [10 empty] | 25 | 50 | 65 | 70 | 87 | 0 | 0 | 50 |  | 0 | [5 empty] | 25 | 388916
114 | Kodda 149 MW PP Unit-1 (Summit) | 44 | 44 | 43 | 44 | 43 | 44 | 42 | 42 | 35 | 44 | 44 | 86 | 98 | 112 | 123 | 127 | 134 | 136 |  | 136 | 136 | 136 | 136 | 135 | 79 | 43 | 1969632
115 | Juldah 100 MW PP Unit-3 (Acorn) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 40 |  | 50 | 50 | 50 | 50 | 50 | 50 | 25 | 744000
116 | Chandpur 200MW (Desh energy) | 100 | 100 | 100 | 72 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 79 |  | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 1668480
117 | Ashuganj 150MW PP (Midland) | 70 | 10 | 10 | 10 | 10 | 4 | 17 | 47 | 64 | 65 | 65 | 62 | 65 | 65 | 65 | 65 | 73 | 87 |  | 95 | 88 | 90 | 88 | 88 | 75 | 70 | 1435200
118 | Bibiyana-III 400 MW CCPP | 418 | 417 | 382 | 383 | 382 | 411 | 412 | 376 | 376 | 421 | 421 | 423 | 423 | 423 | 423 | 405 | 421 | 422 |  | 423 | 421 | 418 | 415 | 418 | 419 | 418 | 9768000
| Jamalpur 115 MW PP (United) | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 77 | 78 | 78 | 49 | 49 | 49 | 49 | 97 |  | 99 | 99 | 99 | 99 | 99 | 99 | 50 | 1518000
| Anwara 300 MW PP (United) | 69 | 70 | 70 | 70 | 70 | 69 | 69 | 69 | 69 | 69 | 219 | 244 | 249 | 69 | 69 | 69 | 69 | 290 |  | 300 | 300 | 300 | 300 | 69 | 69 | 69 | 3003382
| Juldah unit-2 (Acorn) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 27 | 750720
| Anlima Energy Ltd. | 107 | 107 | 107 | 107 | 51 | 60 | 90 | 107 | 107 | 107 | 107 | 107 | 90 | 89 | 95 | 107 | 107 | 107 |  | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 2436327
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 443520
| Spectra Solar Plant Ltd. | [6 empty] | 2 | 10 | 18 | 24 | 28 | 28 | 26 | 21 | 15 | 5 | 0 | 0 | [8 empty] | 178277
| Chandpur 115(Doreen) | 17 | 18 | 18 | 17 | 18 | 18 | 18 | 18 | 17 | 18 | 54 | 109 | 115 | 37 | 17 | 18 | 46 | 109 |  | 115 | 115 | 115 | 115 | 115 | 67 | 37 | 1256640
| Kanchan Purbachal Power Generation Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 433800
Mirsharai 150 MW (Oil)
Mirsharai 150 MW (Gas)
120 | Eastern Zone Total | 5211 | 4893 | 4905 | 4878 | 4768 | 4804 | 5145 | 5443 | 5465 | 5579 | 6085 | 6438 | 6636 | 6167 | 6162 | 5864 | 6027 | 7139 |  | 6875 | 6831 | 6771 | 6523 | 6386 | 6061 | 5659 | 140389452
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | [6 empty] | 4 | 32 | 42 | [7 empty] | 0 | 49 |  | 16 | 16 | 60 | 83 | 16 | 16 | 16 | 316800
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [16 empty] | 0 | 35 |  | 0 | [6 empty] | 42440
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 35 | 17 |  |  |  |  | 10 | 53 | 60 | 84 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 |  | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 1550400
130 | Mongla Orion 100 MW Solar PP | [6 empty] | 7 | 26 | 49 | 65 | 75 | 76 | 71 | 55 | 37 | 16 | 1 | 0 | [8 empty] | 484560
131 | Rampal 1320 MW (BIFPCL)
132 | United Payra Power Ltd. | [25 empty] | 0 | 0
133 | Bhola Nutan Biddut BD LTD (GAS) | 220 | 220 | 183 | 183 | 160 | 160 | 200 | 203 | 184 | 167 | 167 | 167 | 152 | 168 | 168 | 113 | 108 | 108 |  | 108 | 108 | 108 | 106 | 109 | 108 | 108 | 3779318
Bhola Nutan Biddut BD LTD (OIL)
Barisal 110 MW PP (Summit )
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW | 125 | 125 | 126 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 145 | 160 | 198 | 243 |  | 293 | 307 | 160 | 0 |  |  |  | 3148400
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 73 | 87 | 87 | 76 | 75 | 87 | 86 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 81 | 152 |  | 152 | 152 | 138 | 147 | 140 | 151 | 139 | 2496471
140 | Bhola 33 MW PP (Venture) | 18 | 17 | 16 | 16 | 16 | 16 | 15 | 14 | 13 | 13 | 14 | 17 | 16 | 16 | 15 | 14 | 16 | 20 |  | 20 | 21 | 22 | 23 | 22 | 21 | 20 | 406000
141 | Noapara 100 MW PP (Bangla Trac) | [16 empty] | 0 | 20 |  | 0 | [5 empty] | 0 | 24000
142 | Noapara 40 MW PP (Khanjahan Ali) | [16 empty] | 0 | 18 |  | 8 | 8 | 8 | 8 |  |  | 0 | 27000
143 | Gopalganj 100 MW Peaking PP | [16 empty] | 0 | 52 |  | 88 | 77 | 77 | 77 |  |  |  | 289664
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 905 | 906 | 748 | 717 | 716 | 716 | 720 | 810 | 904 | 905 | 904 | 904 | 903 | 904 | 903 | 904 | 903 | 904 |  | 905 | 905 | 905 | 905 | 905 | 906 | 905 | 20782545
147 | Bheramara 410 MW CCPP | 155 | 150 | 150 | 155 | 155 | 155 | 155 | 155 | 140 | 130 | 125 | 125 | 125 | 120 | 110 | 110 | 120 | 125 |  | 130 | 135 | 135 | 140 | 145 | 150 | 150 | 3457440
148 | Payra 1320 MW | 490 | 480 | 480 | 480 | 480 | 490 | 520 | 540 | 540 | 480 | 480 | 490 | 530 | 550 | 560 | 560 | 560 | 580 |  | 650 | 670 | 690 | 760 | 770 | 790 | 810 | 15427400
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 158 | 160 | 160 | 160 | 160 | 160 | 160 | 166 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 |  | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 3865700
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [16 empty] | 0 | 30 |  | 0 | [6 empty] | 29427
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 1 | 2 | 3 | 4 | 4 | 4 | 3 | 2 | 0 | 0 | [9 empty] | 27960
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 145 | 145 | 146 | 146 | 147 | 149 | 149 | 148 | 149 | 143 | 143 | 143 | 139 | 139 | 136 | 137 | 140 | 139 |  | 139 | 139 | 139 | 139 | 139 | 140 | 147 | 3642273
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 175 | 169 | 168 | 174 | 186 | 187 | 183 | 167 | 160 | 145 | 135 | 134 | 135 | 124 | 116 | 134 | 150 | 150 |  | 154 | 145 | 161 | 161 | 162 | 169 | 175 | 3781200
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [16 empty] | 0 | 4 |  | 0 | [6 empty] | 8183
162 | Bogra 22 MW PP (GBB) | 21 | 21 | 21 | 22 | 22 | 22 | 22 | 18 | 16 | 16 | 16 | 15 | 15 | 14 | 14 | 14 | 14 | 14 |  | 19 | 22 | 22 | 20 | 22 | 22 | 20 | 416160
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 245016
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | [7 empty] | 34 | 34 | 24 | 8 | 16 | 50 | 50 | 50 | 34 | 34 | 34 |  | 34 | 8 | 34 | 34 | 8 |  |  | 462249
167 | Katakhali 50 MW Peaking PP | [12 empty] | 12 | 0 |  |  | 0 | 40 |  | 40 | 0 | [5 empty] | 74713
168 | Santahar 50 MW Peaking PP | [16 empty] | 0 | 34 |  | 0 | [6 empty] | 42518
169 | Natore 52 MW PP (Rajlanka) | [16 empty] | 0 | 43 |  | 8 | 0 |  |  |  |  | 0 | 48000
170 | Chapainawabganj 100 MW Peaking PP | [16 empty] | 0 | 57 |  | 55 | 32 | 32 | 32 |  |  |  | 172072
171 | Baghabari 200 MW PP (Paramount) | [25 empty] | 0 | 836
| Bagura 113 MW PP (Confidence)-2 | 113 | [5 empty] | 18 | 100 | 105 | 94 | 70 | 75 | 94 | 94 | 113 | 94 | 94 | 94 |  | 113 | 113 | 113 | 94 | 70 | 70 | 70 | 1848576
172 | Confidence Power Bogura Unit-1 113 MW | 95 | 95 | 35 | 35 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 90 | 95 | 95 |  | 95 | 95 | 95 | 95 | 95 | 35 | 35 | 1404960
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | [6 empty] | 50 | 53 | 75 | 106 | 106 | 106 | 70 | 71 | 70 | 91 | 113 | 113 |  | 113 | 70 | 100 | 113 | 70 | 70 | 70 | 1491158
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 3 | 4 | 5 | 5 | 5 | 5 | 4 | 1 | 0 | [9 empty] | 33250
178 | Energypac Power Venture Thakurgaon Ltd. | [6 empty] | 8 | 109 | 113 | 75 | 36 | 37 | 75 | 75 | 75 | 75 | 75 | 113 |  | 75 | 35 | 90 | 95 | 75 | 75 | 75 | 1381056
178 | Intraco Solar 30 MW | [6 empty] | 1 | 8 | 15 | 22 | 26 | 27 | 24 | 20 | 11 | 4 | 0 | [9 empty] | 159773