## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2022-11-22 | Tuesday
|  | Date (day): | 2022-11-22 |  | Tuesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 9715.6 | MW |  |  | (b) At Evening Peak Hour : |  | 11313 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2022-11-21 | 2022-11-22 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Line O/L
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Under maint
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 65 | 71 | 71 | 71 | 37 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 309 | 278 | 300 | 280 | 132 |  | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 274 | 252 | 255 | 255 | 105 |  | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 225 | 225 | 225 |  | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 84 | 90 | 80 | 90 |  | 10 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas line maintenance
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 0 | 0 | 0 | 0 |  | 102 | Under maint
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 45 | 45 | 45 | 45 |  |  | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 22 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 76 | 84 | 75 | 84 |  | 16 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 24 | 50 | 24 | 50 |  | 52 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 35 | 17 | 35
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 98 | 133 | 98 | 133 |  | 16 | Engine problem
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 35 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 35 | 35 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 43 | 42 | 49 | 49 |  | 31 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 16 | 17 | 31 | 33
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 42 | 48 | 42 | 50
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 113 | 240 | 97 | 285 |  | 15 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 103 | 109 | 100 | 150 | 150 |  | Fuel conservation
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 98 | 50 | 50 | 50 | 50 |  | Fuel conservation
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 72 | 50 | 0 | 50 | 50 |  | Fuel conservation
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 142 | 149 | 125 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 105 | 105 | 105 | 105
37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 17 | 17 | 17 | 17 | 87 |  | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 145 | 162 | 90 | 162
39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 30 | 0 | 30 | 0
40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 17 | 17 | 17 | 38 |  | Fuel shortage
| Dhaka area Total |  |  |  |  | 6263 | 5847 | 2463 | 2594 | 2248 | 2730 | 1805 | 1287
41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 17 | 17 | 17 | 17 |  | 8 | Engine problem
43 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 19 | 0 | 20 | 0
44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 18 | 37 | 26 | 44 |  | 6 | Engine problem
45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 46 | 46 | 46 | 46 | 184 |  | Low Water Level
46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 151 | 152 | 150 | 150 |  | 75 | ST under maint
47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 51 | 95 | 51 | 105
49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 24 | 16 | 20 | 34 | 64 |  | Fuel shortage
50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 17 | 51 | 51 |  | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 22 | 44 | 22 | 44 | 56 |  | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 25 | 40 | 25 | 50 | 50 |  | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  | 22 | Engine problem
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 2 | 2 | 2
54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 255 | 283 | 260 | 300
57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 36 | 36 | 36 | 36 |  | 18 | Engine problem
58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 73 | 91 | 70 | 91 |  | 19 | Engine problem
59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 43 | 25 | 50 | 50 |  | Fuel shortage
60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 107 | 107 | 107 | 107 |  | 9 | Engine problem
| Mirsharai 150 MW |  | Gas/HSD | BPDB-RPCL | 18.5*9 | 0 | 0 | 7 | 0 | 0 | 0
| Chattogram area Total |  |  |  |  | 2442 | 2382 | 882 | 1060 | 899 | 1127 | 923 | 307
61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 0 | 0 | 0 | 0 |  | 221 | Under maint.
63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint
64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 250 | 240 | 300 | 300 | 60 |  | Gas shortage
| Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+136*1 | 284 | 284 | 406 | 402 | 400 | 400 |  |  | On test.
65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 40 | 48 | 40 | 40
66 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 55 | 5 | 15 | 15 | 15 | 40 |  | Gas shortae
67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 0 | 0 | 0 | 0 | 195 |  | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Gas shortage
69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 65 | 117 | 75 | 115 | 35 |  | Fuel shortage
70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 22 | 30 | 0 | 35 |  | 17 | Engine problem
71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 30 | 30 | 68 | 68 | 95 |  | Gas shortage.
72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 17 | 65 | 51 | 100
73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 8 | 8
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 116 | 122 | 143 | 165
75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 14 | 15 | 33 | 33
76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 8 | 8 | 8 | 44 |  | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 15 | 15 | 15 | 15 |  | 10 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 70 | 100 | 100 | 100 |  | Fuel conservation
79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 17 | 0 | 0 | 114 |  | Fuel shortage
80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 108 | 107 | 108 | 108 |  |  | Engine problem
81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 32 | 17 | 35 |  | 19 | Engine problem
82 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 115 | 115 | 115 | 115
| Cumilla Area Total |  |  |  |  | 3193 | 3169 | 1275 | 1478 | 1518 | 1682 | 868 | 627
83 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 38 | 35 | 70 | 100 | 102 |  | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 11 | 11 | 11 | 11 | 11 |  | Gas shortage
85 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0
86 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
87 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 76 | 86 | 70 | 95 | 105 |  | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 68 | 96 | 50 | 99 |  | 16 | Engine problem
89 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 45 | 0 | 50 | 0
90 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 12 | 12 | 12 |  | 10 | Engine problem
| Mymensingh Area Total |  |  |  |  | 717 | 614 | 246 | 240 | 264.6 | 317 | 113 | 26
91 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 0 | 0 | 0 | 0 |  | 70 | Machine problem.
92 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 43 | 43 | 43 | 43 |  | 47 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 | 163 |  | Gas shortage
94 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 0 | 0 | 50 | 50
96 | Fenchuganj 44MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 0 | 0 | 33 | 33 | 50 |  | Gas shortage
97 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 3 | 3 | 3 | 3 | 8 |  | Gas shortage
98 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 56 | 66 | 70 | 70
99 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 0 | 81 | 0 | 78
100 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
101 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 164 | 164 | 177 | 177 | 54 |  | Gas shortage
102 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 19 | 19
103 | Sylhet 50MW PP (EPL) |  | Gas | NENP | 27*2 | 50 | 50 | 0 | 0 | 20 | 20 | 30 |  | Gas shortage
104 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 0 | 0 | 22 | 22 | 3
105 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 280 | 280 | 0 | 0 |  | 341 | Under maint. |  | 2022-12-23
106 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 420 | 408 | 400 | 400
107 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 0 | 0 | 10 | 10
108 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 400 | 400 | 400 | 400
| Sylhet Area Total |  |  |  |  | 2522 | 2477 | 1366 | 1445 | 1247 | 1325 | 308 | 888
109 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 896 | 897 | 913 | 913
110 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 0 | 107 | 16 | 115
111 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 31 | 0 | 45 |  | 9 | Engine problem
112 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
113 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 75 | 0 | 75 |  | 34 | Engine problem
114 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 155 | 145 | 175 | 175 | 235 |  | Gas shortage
115 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 16 | 0 | 16 | 24 |  | Fuel shortage
116 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 0 | 50 | 50 |  | Fuel conservation
117 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 17 | 80 | 64 | 94 |  | 11 | Engine problem
118 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Fuel shortage
119 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 77 | 0 | 100 | 0
| Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 2388 | 2384 | 1145 | 1351 | 1268 | 1483 | 660 | 54
120 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 0 | 0 |  |  | Line O/L
121 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 16 | 27 | 15 | 25 |  | 15 | Engine problem
122 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 135 | 130 | 130 | 130 |  | 64 | Machine problem
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
123 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 540 | 640 | 800 | 800 |  |  | Line O/L
124 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 109 | 109 | 110 | 110 |  | 110 | GT-1 Under maint.
125 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 0 | 0 |  |  | Line O/L
| Barisal 307 MW |  | Coal | BCPCL | 0 | 0 | 0 | 174 | 242 | 190 | 200 |  |  | On test.
| Barisal Area Total |  |  |  |  | 1958 | 1958 | 974 | 1148 | 1245 | 1265 | 0 | 189
126 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
127 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 31 | 0 | 30 |  | 22 | Engine problem
128 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 4 | 0 | 20 |  | 51 | Engine problem
129 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
130 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 50 | 25 | 25 | 50 |  | 0 | Engine problem
131 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 32 | 0 | 40 | 10 |  | Fuel shortage
132 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 144 | 152 | 170 | 175 | 35 |  | Gas shortage
133 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Fuel shortage
134 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
135 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 220 | 205 | 255 | 255 | 159 |  | Gas shortage
136 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 32 | 0 | 35 |  | 15 | Engine problem
137 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 15 | 16 | 18 | 18 |  | 4 | Engine problem
138 | Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
139 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
140 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 43 | 8 | 43 |  | 9 | Engine problem
141 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 80 | 0 | 90 |  | 14 | Engine problem
142 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 0 | 10 | 190 |  | Fuel shortage
143 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 35 | 85 | 85 | 113
144 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 37 | 113 | 90 | 113
145 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
| Rajshahi Area Total |  |  |  |  | 2199 | 2129 | 517 | 829 | 668 | 1003 | 1005 | 115
146 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal shortage
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
147 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 160 | 160 | 160 | 160 |  |  | Machine problem
148 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
149 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
150 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 34 | 113 | 90 | 113
151 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 6 | 0 | 8 | 0
152 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 35 | 108 | 70 | 108
| Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 32 | 0 | 30 | 0
| Rangpur Area Total |  |  |  |  | 830 | 750 | 267 | 381 | 358 | 381 | 125 | 85
| Total |  |  |  |  | 22512 | 21710 | 9135 | 10526 | 9715.6 | 11313 | 5807 | 3578
A. |  | 2022-11-21 | (Yesterday) |  |  |  |  | Monday
1 | Highest Generation : |  |  | 10526 | MW at | 18:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 18:00 | hrs.
2 | Minimum Generation : |  |  | 7024 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 10526 | MW
3 | Day peak Generation : |  |  | 9135 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 10280.15 | MW
4 | Evening peak Generation : |  |  | 10526 | MW at | 18:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 209.0708 | MKWHr | By Solar | 1.4109 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Gas : | 105.9675 | MKWHr |  | By Oil: | 54.2252 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 24.4105 | MKWHr |  | By Hydro: | 1.0699 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 5807 | MW | Dhaka | 3985.6 | 3985.6 |  | 0 |  | 18:00 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 3578 | MW | Chittagong | 1286.3 | 1286.3 |  | 0 |  | 19:00 |  | 0
|  |  | Total = |  |  | 9385 | MW | Khulna | 1138.8 | 1138.8 |  | 0 |  | 19:30 |  | 0
7 | Total Gas Supplied : |  |  | 804.93 | MMCFD |  |  | Rajshahi | 932.7 | 932.7 |  | 0 |  | 20:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 103909368.99 | ii) Oil : | Taka | 728574901.1 | Comilla | 843 | 843 |  | 0 |  | 21:00 |  | 0
|  | iii) Coal : |  | 164888141 | Total | Taka | 997372411.09 | Mymensingh | 776 | 776 |  | 0 |  | 22:00 |  | 0
9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0 | MKWHr. | Sylhet | 389 | 389 |  | 0 |  | 23:00 |  | 0
| ii) During Peak Demand : |  |  | 1096 | MW (E to W) at | 18:00 | hrs | Barisal | 251.75 | 251.75 |  | 0 |  | 24:00 |  | 0
| iii) Maximum : |  |  | 566 | MW at | 7:00 | hrs | Rangpur | 677 | 677 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 30.5° C |  |  | Total | 10280.15 | 10280.15 |  | 0
B. |  | 2022-11-22 | (Today) |  |  |  | Tuesday |  |  | Probable max. temperature in Dhaka |  |  | 28.1° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 10800 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 11313 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 9250 | MW
4 | Reserve(Generation end) |  |  |  | 513 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | 3 | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 214.5131 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 6884 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 19.4342 | MKWHr. | ii) HVDC Flow at Peak Time |  | 897 | MW at | 18:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.5526 | MKWHr. | iii) Maximum HVDC Flow : |  | 898 | MW at | 17:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 90.91 |  | (b) Today: | 90.89 |  | (c) Rule Curve: |  | 107.1
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2022-11-21
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 0 | 70 | 0 | 318 | 285 |  | 0 | 225 | 0 | 12 | 0 | 55 | 0 | 0 | 0 | 30 | 8 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 35 | 19 | 25 | 27 | 33 | 32 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 |  | 6 | 0 | 0 | 22 | 0 | 38 | 0 | 4 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 69 | 47 | 20 | 0 | 0 | 0 | 0 | 8 | 22 | 8 | 33 | 15 | 104 | 110 | 0 | 12 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 66 | 78 | 0 | 164 | 0 | 0 | 0 | 280 | 0 | 3 | 0 | 275 | 0 | 0 | 48 | 0 | 144 | 0 | 25 | 17 | 65 | 352 | 49 | 50 | 34 | 0 | 16 | 24 | 53 | 17 | 65 | 25 | 400 | 17 | 0 | 17 | 107 | 0 | 17 | 0 | 47 | 17 | 407 | 0 | 0 |  | 659 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 227 | 70 | 0 | 113 | 0 | 34 | 0 | 0 | 38 | 670 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 |  | 5255 | 2762 | 8017 | 3267 | 659 | 1339 | 0 | 1632 | 970 | 46 | 0 | 0 | 104 | 0 | 0 | 90.91
2:00 | 0 | 0 | 0 | 180 | 0 | 70 | 0 | 318 | 283 |  | 0 | 225 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 30 | 8 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 35 | 19 | 22 | 27 | 33 | 32 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 |  | 6 | 0 | 0 | 22 | 0 | 24 | 0 | 7 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 70 | 47 | 20 | 0 | 0 | 0 | 0 | 8 | 22 | 8 | 33 | 15 | 102 | 110 | 0 | 12 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 66 | 78 | 0 | 164 | 0 | 0 | 0 | 280 | 0 | 3 | 0 | 210 | 0 | 0 | 48 | 0 | 101 | 0 | 25 | 17 | 30 | 352 | 49 | 34 | 34 | 0 | 16 | 17 | 53 | 17 | 36 | 25 | 400 | 17 | 0 | 17 | 107 | 0 | 17 | 0 | 18 | 17 | 407 | 0 | 0 |  | 658 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234 | 35 | 0 | 35 | 0 | 34 | 0 | 0 | 38 | 630 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 136 |  | 5001 | 2608 | 7609 | 3263 | 658 | 1345 | 0 | 1269 | 926 | 46 | 0 | 0 | 102 | 0 | 0 | 90.91
3:00 | 0 | 0 | 0 | 180 | 0 | 70 | 0 | 313 | 274 |  | 0 | 225 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 30 | 8 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 35 | 19 | 22 | 28 | 33 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 |  | 6 | 0 | 0 | 22 | 0 | 19 | 0 | 11 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 70 | 43 | 20 | 0 | 0 | 0 | 0 | 8 | 22 | 8 | 33 | 15 | 98 | 112 | 0 | 12 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 66 | 0 | 0 | 164 | 0 | 0 | 0 | 285 | 0 | 3 | 0 | 57 | 0 | 0 | 48 | 0 | 56 | 0 | 25 | 17 | 10 | 352 | 49 | 34 | 34 | 0 | 16 | 17 | 53 | 17 | 36 | 25 | 400 | 18 | 0 | 17 | 107 | 0 | 17 | 0 | 17 | 17 | 407 | 0 | 0 |  | 660 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 159 | 0 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 240 | 35 | 0 | 35 | 0 | 34 | 0 | 0 | 38 | 620 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143 |  | 4691 | 2613 | 7304 | 3258 | 660 | 1274 | 0 | 1046 | 922 | 46 | 0 | 0 | 98 | 0 | 0 | 90.91
4:00 | 0 | 0 | 0 | 180 | 0 | 70 | 0 | 313 | 276 |  | 0 | 225 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 16 | 8 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 17 | 19 | 22 | 28 | 33 | 32 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 |  | 6 | 0 | 0 | 22 | 0 | 18 | 0 | 17 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 70 | 43 | 20 | 0 | 0 | 0 | 0 | 8 | 22 | 8 | 33 | 15 | 96 | 110 | 0 | 12 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 66 | 0 | 0 | 164 | 0 | 0 | 0 | 280 | 0 | 3 | 0 | 57 | 0 | 0 | 48 | 0 | 52 | 0 | 25 | 17 | 10 | 375 | 49 | 34 | 34 | 0 | 16 | 17 | 53 | 17 | 16 | 25 | 400 | 17 | 0 | 17 | 107 | 0 | 17 | 0 | 18 | 17 | 407 | 0 | 0 |  | 660 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 159 | 0 | 0 | 166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 |  | 4614 | 2465 | 7079 | 3285 | 660 | 1288 | 0 | 805 | 899 | 46 | 0 | 0 | 96 | 0 | 0 | 90.91
5:00 | 0 | 0 | 0 | 180 | 0 | 70 | 0 | 313 | 276 |  | 0 | 225 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 8 | 8 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 17 | 19 | 22 | 28 | 33 | 32 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 |  | 6 | 0 | 0 | 22 | 0 | 18 | 0 | 21 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 69 | 43 | 20 | 0 | 0 | 0 | 0 | 8 | 22 | 8 | 33 | 15 | 92 | 111 | 0 | 13 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 66 | 0 | 0 | 164 | 0 | 0 | 0 | 270 | 0 | 3 | 0 | 45 | 0 | 0 | 0 | 0 | 48 | 0 | 25 | 17 | 10 | 375 | 49 | 34 | 34 | 0 | 16 | 17 | 53 | 17 | 17 | 25 | 390 | 18 | 0 | 17 | 107 | 0 | 17 | 0 | 18 | 17 | 407 | 0 | 0 |  | 660 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 159 | 0 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 156 |  | 4525 | 2499 | 7024 | 3288 | 660 | 1288 | 0 | 735 | 915 | 46 | 0 | 0 | 92 | 0 | 0 | 90.91
6:00 | 0 | 0 | 0 | 180 | 0 | 70 | 0 | 312 | 272 |  | 0 | 225 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 8 | 8 | 0 | 0 | 0 | 0 | 0 | 17 | 4 | 17 | 19 | 22 | 28 | 33 | 32 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 |  | 3 | 0 | 0 | 22 | 0 | 18 | 0 | 28 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 69 | 43 | 20 | 0 | 0 | 0 | 0 | 8 | 22 | 8 | 33 | 15 | 86 | 112 | 0 | 13 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 66 | 0 | 0 | 164 | 0 | 0 | 0 | 300 | 0 | 3 | 0 | 45 | 0 | 0 | 0 | 0 | 53 | 0 | 25 | 17 | 13 | 418 | 56 | 34 | 34 | 0 | 16 | 17 | 53 | 17 | 17 | 25 | 370 | 17 | 0 | 17 | 107 | 0 | 17 | 0 | 18 | 17 | 407 | 0 | 0 |  | 660 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 151 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 159 | 0 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 264 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 30 | 580 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 |  | 4590 | 2499 | 7089 | 3310 | 660 | 1327 | 0 | 781 | 879 | 46 | 0 | 0 | 86 | 0 | 0 | 90.91
7:00 | 0 | 0 | 0 | 180 | 0 | 70 | 0 | 312 | 272 |  | 0 | 225 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 16 | 8 | 32 | 0 | 0 | 0 | 0 | 17 | 27 | 35 | 19 | 22 | 28 | 33 | 32 | 6 | 0 | 46 | 0 | 0 | 0 | 2 | 151 | 0 | 0 | 0 |  | 6 | 0 | 0 | 22 | 0 | 18 | 0 | 28 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 30 | 43 | 20 | 0 | 5 | 0 | 0 | 8 | 22 | 8 | 28 | 15 | 82 | 72 | 0 | 13 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 164 | 0 | 0 | 0 | 320 | 0 | 3 | 0 | 100 | 0 | 0 | 0 | 0 | 60 | 3 | 25 | 17 | 25 | 419 | 99 | 40 | 34 | 1 | 16 | 30 | 53 | 17 | 23 | 25 | 400 | 17 | 5 | 17 | 107 | 0 | 17 | 3 | 18 | 17 | 417 | 0 | 0 |  | 660 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 21 | 0 | 8 | 0 | 0 | 159 | 0 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 259 | 4 | 0 | 36 | 0 | 38 | 0 | 0 | 35 | 590 | 107 | 0 | 0 | 0 | 8 | 18 | 0 | 0 | 0 | 2 | 141 |  | 4845 | 2615 | 7460 | 3282 | 660 | 1343 | 0 | 1103 | 890 | 46 | 0 | 32 | 82 | 22 | 0 | 90.9
8:00 | 0 | 0 | 0 | 180 | 0 | 70 | 0 | 304 | 271 |  | 0 | 225 | 0 | 3 | 0 | 45 | 0 | 0 | 0 | 32 | 8 | 133 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 22 | 28 | 33 | 31 | 50 | 0 | 46 | 0 | 0 | 0 | 17 | 151 | 0 | 0 | 0 |  | 6 | 0 | 0 | 22 | 0 | 18 | 0 | 2 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 20 | 44 | 20 | 0 | 0 | 0 | 0 | 8 | 22 | 8 | 18 | 15 | 88 | 72 | 0 | 13 | 1 | 0 | 43 | 0 | 0 | 0 | 0 | 66 | 0 | 0 | 164 | 0 | 0 | 0 | 300 | 0 | 3 | 0 | 113 | 54 | 50 | 46 | 50 | 110 | 9 | 25 | 17 | 38 | 419 | 49 | 105 | 34 | 2 | 16 | 36 | 53 | 17 | 54 | 25 | 400 | 20 | 21 | 17 | 107 | 0 | 17 | 12 | 18 | 17 | 417 | 0 | 0 |  | 660 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 18 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 255 | 50 | 0 | 81 | 0 | 82 | 0 | 1 | 37 | 640 | 109 | 0 | 0 | 2 | 14 | 53 | 0 | 0 | 0 | 11 | 158 |  | 5346 | 2862 | 8208 | 3228 | 660 | 1285 | 154 | 1583 | 958 | 46 | 0 | 133 | 88 | 73 | 0 | 90.9
9:00 | 0 | 0 | 0 | 180 | 0 | 65 | 0 | 307 | 277 |  | 0 | 225 | 0 | 25 | 0 | 45 | 0 | 0 | 0 | 43 | 8 | 133 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 22 | 28 | 33 | 30 | 50 | 0 | 46 | 0 | 0 | 0 | 17 | 150 | 0 | 0 | 0 |  | 6 | 14 | 0 | 22 | 0 | 18 | 0 | 2 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 34 | 47 | 20 | 0 | 0 | 0 | 0 | 8 | 22 | 8 | 14 | 15 | 94 | 72 | 0 | 13 | 2 | 0 | 43 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 164 | 0 | 0 | 0 | 280 | 0 | 3 | 0 | 113 | 0 | 0 | 46 | 6 | 126 | 14 | 25 | 17 | 45 | 419 | 49 | 105 | 36 | 3 | 16 | 36 | 53 | 17 | 105 | 25 | 400 | 17 | 35 | 17 | 107 | 0 | 17 | 25 | 18 | 17 | 416 | 0 | 0 |  | 754 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 17 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 240 | 53 | 0 | 70 | 0 | 49 | 0 | 3 | 37 | 650 | 109 | 0 | 0 | 3 | 31 | 37 | 0 | 0 | 0 | 17 | 174 |  | 5351 | 2931 | 8282 | 3237 | 754 | 1249 | 6 | 1632 | 984 | 46 | 0 | 147 | 94 | 133 | 0 | 90.9
10:00 | 0 | 0 | 0 | 180 | 0 | 65 | 0 | 312 | 277 |  | 0 | 225 | 0 | 35 | 0 | 45 | 0 | 0 | 0 | 66 | 24 | 117 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 22 | 26 | 33 | 30 | 42 | 0 | 46 | 0 | 0 | 0 | 17 | 151 | 0 | 0 | 0 |  | 6 | 26 | 0 | 22 | 0 | 18 | 0 | 2 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 83 | 47 | 20 | 0 | 0 | 0 | 0 | 8 | 22 | 0 | 14 | 15 | 96 | 72 | 0 | 13 | 2 | 0 | 42 | 0 | 0 | 0 | 0 | 64 | 0 | 0 | 164 | 0 | 0 | 0 | 275 | 0 | 3 | 0 | 115 | 99 | 25 | 46 | 25 | 128 | 17 | 25 | 17 | 55 | 416 | 48 | 105 | 34 | 4 | 16 | 36 | 73 | 17 | 107 | 25 | 400 | 17 | 44 | 17 | 107 | 0 | 17 | 21 | 18 | 17 | 416 | 0 | 0 |  | 801 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 17 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 17 | 0 | 35 | 0 | 34 | 0 | 4 | 37 | 600 | 109 | 0 | 0 | 4 | 69 | 36 | 0 | 0 | 0 | 27 | 176 |  | 5590 | 2904 | 8494 | 3288 | 801 | 1224 | 149 | 1619 | 936 | 46 | 0 | 143 | 96 | 192 | 0 | 90.9
11:00 | 0 | 0 | 0 | 180 | 0 | 65 | 0 | 312 | 277 |  | 0 | 225 | 0 | 67 | 0 | 45 | 0 | 0 | 0 | 76 | 24 | 82 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 19 | 22 | 23 | 33 | 30 | 42 | 0 | 46 | 0 | 0 | 0 | 17 | 151 | 0 | 0 | 0 |  | 6 | 24 | 0 | 22 | 0 | 18 | 0 | 2 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 30 | 41 | 5 | 0 | 0 | 0 | 19 | 8 | 22 | 8 | 14 | 15 | 102 | 39 | 0 | 13 | 2 | 0 | 43 | 0 | 0 | 0 | 0 | 62 | 0 | 0 | 164 | 0 | 0 | 0 | 275 | 0 | 3 | 0 | 113 | 13 | 25 | 76 | 25 | 135 | 19 | 25 | 17 | 60 | 420 | 58 | 105 | 46 | 4 | 219 | 36 | 73 | 17 | 107 | 25 | 400 | 17 | 50 | 24 | 107 | 0 | 17 | 32 | 80 | 17 | 407 | 0 | 0 |  | 847 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 15 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 17 | 0 | 35 | 0 | 34 | 0 | 6 | 37 | 540 | 109 | 0 | 0 | 5 | 76 | 35 | 0 | 0 | 0 | 31 | 174 |  | 5799 | 2832 | 8631 | 3127 | 847 | 1208 | 63 | 2014 | 874 | 46 | 0 | 125 | 102 | 225 | 0 | #REF!
12:00 | 0 | 0 | 0 | 180 | 0 | 65 | 0 | 309 | 274 |  | 0 | 225 | 0 | 84 | 0 | 45 | 0 | 0 | 0 | 76 | 24 | 98 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 0 | 22 | 21 | 33 | 16 | 42 | 0 | 46 | 0 | 0 | 0 | 17 | 151 | 0 | 0 | 0 |  | 6 | 24 | 0 | 22 | 0 | 18 | 0 | 2 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 30 | 40 | 5 | 0 | 0 | 0 | 22 | 8 | 22 | 8 | 14 | 15 | 116 | 38 | 0 | 11 | 2 | 0 | 43 | 0 | 0 | 0 | 0 | 56 | 0 | 0 | 164 | 0 | 0 | 0 | 280 | 0 | 3 | 0 | 113 | 103 | 98 | 76 | 72 | 142 | 19 | 25 | 17 | 65 | 420 | 68 | 105 | 51 | 4 | 255 | 36 | 73 | 17 | 108 | 25 | 400 | 17 | 45 | 145 | 107 | 0 | 17 | 30 | 115 | 17 | 406 | 7 | 0 |  | 896 | 0 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 135 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 15 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 17 | 0 | 35 | 0 | 34 | 0 | 6 | 37 | 540 | 109 | 0 | 0 | 5 | 77 | 35 | 0 | 0 | 0 | 32 | 174 |  | 6232 | 2903 | 9135 | 3097 | 896 | 1211 | 273 | 2251 | 874 | 46 | 7 | 144 | 116 | 220 | 0 | 90.9
13:00 | 0 | 0 | 0 | 180 | 0 | 65 | 0 | 298 | 268 |  | 0 | 225 | 0 | 91 | 0 | 45 | 0 | 0 | 0 | 76 | 24 | 115 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 19 | 22 | 26 | 33 | 16 | 42 | 0 | 46 | 0 | 0 | 0 | 17 | 150 | 0 | 0 | 0 |  | 6 | 24 | 0 | 22 | 0 | 18 | 0 | 2 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 30 | 43 | 5 | 0 | 0 | 0 | 28 | 8 | 22 | 8 | 14 | 15 | 118 | 37 | 0 | 11 | 2 | 0 | 43 | 0 | 0 | 0 | 0 | 57 | 0 | 0 | 164 | 0 | 0 | 0 | 280 | 0 | 3 | 0 | 113 | 100 | 98 | 76 | 92 | 149 | 18 | 25 | 17 | 75 | 416 | 68 | 105 | 51 | 0 | 249 | 36 | 73 | 17 | 100 | 25 | 390 | 17 | 46 | 162 | 107 | 0 | 17 | 31 | 115 | 17 | 407 | 9 | 0 |  | 897 | 0 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 15 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 216 | 17 | 0 | 67 | 0 | 70 | 0 | 6 | 37 | 640 | 109 | 0 | 0 | 0 | 72 | 35 | 0 | 0 | 0 | 29 | 174 |  | 6296 | 3035 | 9331 | 3081 | 897 | 1199 | 290 | 2346 | 974 | 46 | 9 | 167 | 118 | 204 | 0 | 90.89
14:00 | 0 | 0 | 0 | 180 | 0 | 68 | 0 | 293 | 264 |  | 0 | 225 | 0 | 91 | 0 | 45 | 0 | 0 | 0 | 76 | 24 | 126 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 22 | 27 | 33 | 26 | 47 | 0 | 46 | 0 | 0 | 0 | 17 | 148 | 0 | 0 | 0 |  | 7 | 24 | 0 | 22 | 0 | 18 | 0 | 2 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 40 | 43 | 5 | 0 | 0 | 0 | 36 | 8 | 22 | 8 | 14 | 15 | 122 | 35 | 0 | 11 | 2 | 0 | 43 | 0 | 0 | 0 | 0 | 56 | 0 | 0 | 164 | 0 | 0 | 0 | 275 | 0 | 3 | 0 | 113 | 56 | 25 | 66 | 25 | 149 | 15 | 25 | 17 | 87 | 412 | 67 | 105 | 51 | 3 | 277 | 36 | 80 | 17 | 102 | 25 | 400 | 17 | 34 | 82 | 107 | 0 | 17 | 26 | 32 | 17 | 407 | 0 | 0 |  | 897 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 14 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 217 | 17 | 0 | 70 | 0 | 34 | 0 | 5 | 37 | 640 | 109 | 0 | 0 | 0 | 59 | 35 | 0 | 0 | 0 | 23 | 175 |  | 5961 | 3010 | 8971 | 3103 | 897 | 1195 | 106 | 2174 | 975 | 46 | 0 | 186 | 122 | 167 | 0 | 90.9
15:00 | 0 | 0 | 0 | 180 | 0 | 68 | 0 | 285 | 258 |  | 0 | 225 | 0 | 89 | 0 | 45 | 0 | 0 | 0 | 76 | 24 | 126 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 22 | 8 | 33 | 28 | 48 | 0 | 46 | 0 | 0 | 0 | 17 | 147 | 0 | 0 | 0 |  | 12 | 24 | 0 | 22 | 0 | 20 | 0 | 2 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 40 | 43 | 5 | 0 | 0 | 0 | 30 | 8 | 22 | 8 | 15 | 15 | 116 | 35 | 0 | 11 | 1 | 0 | 43 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 164 | 0 | 0 | 0 | 290 | 0 | 3 | 0 | 113 | 46 | 25 | 68 | 25 | 149 | 11 | 25 | 17 | 97 | 406 | 68 | 105 | 51 | 2 | 274 | 36 | 91 | 17 | 106 | 25 | 395 | 17 | 18 | 72 | 107 | 0 | 17 | 18 | 18 | 0 | 407 | 2 | 0 |  | 897 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 14 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 204 | 17 | 0 | 35 | 0 | 34 | 0 | 3 | 37 | 540 | 109 | 0 | 0 | 3 | 41 | 35 | 0 | 0 | 0 | 16 | 171 |  | 5872 | 2791 | 8663 | 3065 | 897 | 1190 | 96 | 2087 | 871 | 46 | 2 | 180 | 116 | 113 | 0 | 90.89
16:00 | 0 | 0 | 0 | 180 | 0 | 68 | 0 | 279 | 258 |  | 0 | 225 | 0 | 87 | 0 | 45 | 0 | 0 | 0 | 80 | 24 | 133 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 22 | 27 | 33 | 17 | 48 | 0 | 46 | 0 | 0 | 0 | 17 | 148 | 0 | 0 | 0 |  | 12 | 24 | 0 | 22 | 0 | 29 | 0 | 2 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 35 | 43 | 15 | 0 | 0 | 0 | 37 | 8 | 22 | 8 | 15 | 15 | 114 | 35 | 0 | 11 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 61 | 0 | 0 | 164 | 0 | 0 | 0 | 310 | 0 | 3 | 0 | 113 | 0 | 0 | 68 | 0 | 149 | 6 | 25 | 17 | 100 | 400 | 68 | 90 | 60 | 1 | 285 | 36 | 91 | 17 | 106 | 25 | 392 | 17 | 11 | 72 | 107 | 0 | 17 | 8 | 17 | 14 | 407 | 15 | 0 |  | 897 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 15 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 35 | 0 | 34 | 0 | 2 | 35 | 530 | 109 | 0 | 0 | 1 | 18 | 0 | 0 | 0 | 0 | 7 | 202 |  | 5835 | 2714 | 8549 | 3056 | 897 | 1216 | 0 | 2065 | 892 | 46 | 15 | 194 | 114 | 54 | 0 | 90.89
17:00 | 0 | 0 | 0 | 180 | 0 | 71 | 0 | 278 | 252 |  | 0 | 225 | 0 | 91 | 0 | 45 | 0 | 0 | 0 | 84 | 24 | 133 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 22 | 27 | 33 | 24 | 48 | 0 | 46 | 0 | 0 | 0 | 17 | 150 | 0 | 0 | 0 |  | 12 | 16 | 17 | 22 | 0 | 37 | 0 | 2 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 30 | 43 | 15 | 0 | 0 | 0 | 37 | 8 | 22 | 8 | 14 | 15 | 114 | 35 | 0 | 11 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 40 | 81 | 0 | 164 | 0 | 0 | 0 | 290 | 0 | 3 | 0 | 113 | 0 | 0 | 57 | 0 | 149 | 0 | 25 | 17 | 107 | 375 | 49 | 105 | 85 | 0 | 285 | 36 | 91 | 17 | 108 | 25 | 350 | 17 | 1 | 162 | 107 | 0 | 17 | 0 | 115 | 17 | 397 | 18 | 0 |  | 898 | 0 | 145 | 0 | 49 | 0 | 0 | 0 | 25 | 7 | 0 | 117 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 15 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 35 | 0 | 48 | 0 | 60 | 0 | 0 | 113 | 550 | 109 | 0 | 0 | 0 | 1 | 72 | 0 | 0 | 0 | 0 | 262 |  | 6023 | 3048 | 9071 | 2957 | 898 | 1248 | 0 | 2581 | 972 | 46 | 18 | 235 | 114 | 2 | 0 | 90.89
18:00 | 0 | 0 | 0 | 180 | 0 | 71 | 0 | 278 | 252 |  | 0 | 225 | 0 | 90 | 0 | 45 | 0 | 0 | 0 | 84 | 50 | 133 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 22 | 22 | 20 | 33 | 17 | 48 | 0 | 46 | 0 | 0 | 0 | 17 | 152 | 0 | 0 | 0 |  | 12 | 16 | 51 | 44 | 0 | 37 | 0 | 2 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 30 | 48 | 15 | 0 | 0 | 0 | 30 | 8 | 22 | 8 | 15 | 15 | 122 | 35 | 0 | 11 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 66 | 81 | 0 | 164 | 0 | 0 | 0 | 280 | 0 | 3 | 70 | 240 | 109 | 50 | 86 | 50 | 149 | 0 | 40 | 65 | 117 | 408 | 96 | 105 | 95 | 0 | 283 | 36 | 91 | 17 | 107 | 43 | 400 | 17 | 0 | 162 | 107 | 0 | 32 | 0 | 115 | 17 | 402 | 0 | 0 |  | 897 | 0 | 145 | 0 | 107 | 0 | 0 | 0 | 31 | 75 | 16 | 130 | 27 | 0 | 0 | 0 | 0 | 31 | 4 | 80 | 0 | 25 | 32 | 43 | 32 | 16 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 205 | 80 | 0 | 85 | 0 | 113 | 0 | 0 | 113 | 640 | 109 | 0 | 0 | 0 | 0 | 108 | 0 | 0 | 0 | 0 | 242 |  | 6817 | 3709 | 10526 | 3072 | 897 | 1283 | 279 | 3270 | 1042 | 46 | 0 | 515 | 122 | 0 | 0 | 90.89
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 0 | 71 | 0 | 278 | 252 |  | 0 | 225 | 0 | 92 | 0 | 45 | 0 | 0 | 0 | 84 | 50 | 133 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 21 | 26 | 33 | 22 | 49 | 0 | 46 | 0 | 0 | 0 | 17 | 151 | 0 | 0 | 0 |  | 12 | 24 | 51 | 44 | 0 | 41 | 0 | 2 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 30 | 48 | 30 | 0 | 0 | 0 | 30 | 9 | 22 | 8 | 23 | 15 | 116 | 44 | 0 | 11 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 40 | 81 | 0 | 164 | 0 | 0 | 0 | 255 | 0 | 3 | 10 | 278 | 21 | 25 | 87 | 25 | 149 | 0 | 50 | 100 | 118 | 339 | 97 | 105 | 105 | 0 | 284 | 36 | 91 | 17 | 108 | 50 | 340 | 17 | 0 | 162 | 107 | 0 | 35 | 0 | 115 | 17 | 402 | 0 | 0 |  | 898 | 0 | 150 | 0 | 114 | 0 | 0 | 0 | 34 | 82 | 24 | 130 | 25 | 0 | 0 | 0 | 0 | 31 | 5 | 89 | 0 | 25 | 32 | 43 | 33 | 20 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 94 | 0 | 94 | 0 | 113 | 0 | 0 | 113 | 640 | 109 | 0 | 0 | 0 | 0 | 112 | 0 | 0 | 0 | 0 | 246 |  | 6627 | 3738 | 10365 | 2947 | 898 | 1220 | 81 | 3467 | 1046 | 46 | 0 | 544 | 116 | 0 | 0 | 90.89
19:30 | 0 | 0 | 0 | 180 | 0 | 71 | 0 | 278 | 252 |  | 0 | 225 | 0 | 91 | 0 | 45 | 0 | 0 | 0 | 84 | 50 | 133 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 21 | 27 | 33 | 28 | 49 | 0 | 46 | 0 | 0 | 0 | 17 | 150 | 0 | 0 | 0 |  | 12 | 24 | 51 | 44 | 0 | 43 | 0 | 2 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 30 | 48 | 30 | 0 | 0 | 0 | 30 | 16 | 22 | 8 | 25 | 15 | 116 | 47 | 0 | 11 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 64 | 81 | 0 | 164 | 0 | 0 | 0 | 255 | 0 | 3 | 0 | 278 | 21 | 0 | 87 | 0 | 149 | 0 | 50 | 100 | 123 | 339 | 98 | 105 | 105 | 0 | 285 | 36 | 91 | 17 | 108 | 50 | 330 | 17 | 0 | 162 | 107 | 0 | 35 | 0 | 115 | 17 | 402 | 0 | 0 |  | 897 | 0 | 150 | 0 | 114 | 0 | 0 | 0 | 33 | 80 | 24 | 115 | 25 | 0 | 0 | 0 | 0 | 25 | 5 | 89 | 0 | 25 | 32 | 43 | 34 | 20 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 151 | 94 | 0 | 94 | 0 | 113 | 0 | 0 | 113 | 600 | 109 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 242 |  | 6607 | 3675 | 10282 | 2958 | 897 | 1221 | 21 | 3485 | 1002 | 46 | 0 | 536 | 116 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 180 | 0 | 71 | 0 | 278 | 256 |  | 0 | 225 | 0 | 91 | 0 | 45 | 0 | 0 | 0 | 84 | 50 | 133 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 22 | 27 | 33 | 28 | 49 | 0 | 46 | 0 | 0 | 0 | 17 | 151 | 0 | 0 | 0 |  | 12 | 24 | 51 | 44 | 0 | 43 | 0 | 2 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 30 | 48 | 40 | 0 | 0 | 0 | 32 | 16 | 22 | 8 | 25 | 15 | 114 | 52 | 0 | 11 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 66 | 81 | 0 | 164 | 0 | 0 | 0 | 260 | 0 | 3 | 0 | 279 | 21 | 0 | 87 | 0 | 149 | 0 | 50 | 100 | 122 | 339 | 98 | 105 | 105 | 0 | 106 | 36 | 91 | 17 | 101 | 50 | 340 | 17 | 0 | 162 | 107 | 0 | 35 | 0 | 115 | 17 | 402 | 0 | 0 |  | 897 | 0 | 155 | 0 | 114 | 0 | 0 | 0 | 33 | 78 | 24 | 130 | 26 | 0 | 0 | 0 | 0 | 25 | 5 | 50 | 0 | 25 | 32 | 43 | 34 | 22 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 151 | 94 | 0 | 94 | 0 | 113 | 0 | 0 | 113 | 600 | 109 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 245 |  | 6459 | 3661 | 10120 | 2998 | 897 | 1243 | 21 | 3299 | 1005 | 46 | 0 | 497 | 114 | 0 | 0 | 90.89
21:00 | 0 | 0 | 0 | 180 | 0 | 71 | 0 | 280 | 256 |  | 0 | 225 | 0 | 87 | 0 | 45 | 0 | 0 | 0 | 77 | 50 | 133 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 22 | 27 | 25 | 29 | 49 | 0 | 46 | 0 | 0 | 0 | 17 | 151 | 0 | 0 | 0 |  | 12 | 24 | 51 | 44 | 0 | 39 | 0 | 2 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 32 | 48 | 52 | 0 | 0 | 0 | 32 | 8 | 22 | 8 | 32 | 15 | 112 | 86 | 0 | 11 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 69 | 81 | 0 | 164 | 0 | 0 | 0 | 270 | 0 | 3 | 0 | 281 | 0 | 0 | 87 | 0 | 149 | 0 | 50 | 100 | 127 | 340 | 99 | 105 | 105 | 0 | 16 | 36 | 91 | 17 | 75 | 50 | 340 | 17 | 0 | 162 | 107 | 0 | 35 | 0 | 115 | 17 | 402 | 0 | 0 |  | 897 | 0 | 165 | 0 | 114 | 0 | 0 | 0 | 0 | 78 | 24 | 130 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 25 | 32 | 8 | 34 | 22 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 94 | 0 | 70 | 0 | 91 | 0 | 0 | 70 | 560 | 109 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 256 |  | 6292 | 3462 | 9754 | 3055 | 897 | 1267 | 0 | 2967 | 976 | 46 | 0 | 434 | 112 | 0 | 0 | 90.89
22:00 | 0 | 0 | 0 | 180 | 0 | 71 | 0 | 285 | 255 |  | 0 | 225 | 0 | 89 | 0 | 45 | 0 | 0 | 0 | 77 | 50 | 32 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 22 | 27 | 33 | 29 | 24 | 0 | 46 | 0 | 0 | 0 | 17 | 151 | 0 | 0 | 0 |  | 12 | 24 | 51 | 44 | 0 | 37 | 0 | 3 | 0 | 0 | 0 | 0 | 210 | 0 | 0 | 32 | 48 | 30 | 0 | 0 | 0 | 0 | 8 | 22 | 8 | 33 | 15 | 110 | 96 | 0 | 10 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 70 | 81 | 0 | 164 | 0 | 0 | 0 | 255 | 0 | 3 | 0 | 263 | 0 | 0 | 87 | 0 | 149 | 0 | 50 | 100 | 127 | 339 | 99 | 105 | 105 | 0 | 16 | 36 | 91 | 17 | 75 | 50 | 300 | 17 | 0 | 162 | 107 | 0 | 35 | 0 | 115 | 17 | 392 | 0 | 0 |  | 897 | 0 | 165 | 0 | 49 | 0 | 0 | 0 | 0 | 40 | 16 | 120 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 154 | 94 | 0 | 70 | 0 | 70 | 0 | 0 | 70 | 530 | 109 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | 0 | 307 |  | 6030 | 3183 | 9213 | 3003 | 897 | 1231 | 0 | 2782 | 997 | 46 | 0 | 147 | 110 | 0 | 0 | 90.89
23:00 | 0 | 0 | 0 | 180 | 0 | 71 | 0 | 289 | 266 |  | 0 | 225 | 0 | 92 | 0 | 45 | 0 | 0 | 0 | 77 | 50 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 22 | 27 | 33 | 32 | 8 | 0 | 46 | 0 | 0 | 0 | 17 | 151 | 0 | 0 | 0 |  | 12 | 0 | 17 | 44 | 0 | 37 | 0 | 6 | 0 | 0 | 0 | 0 | 210 | 0 | 0 | 32 | 48 | 30 | 0 | 0 | 0 | 0 | 8 | 22 | 8 | 33 | 15 | 106 | 99 | 0 | 10 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 71 | 81 | 0 | 164 | 0 | 0 | 0 | 260 | 0 | 3 | 0 | 263 | 0 | 0 | 87 | 0 | 149 | 0 | 50 | 85 | 80 | 329 | 99 | 105 | 57 | 0 | 16 | 36 | 73 | 17 | 75 | 50 | 340 | 17 | 0 | 17 | 107 | 0 | 35 | 0 | 43 | 17 | 392 | 0 | 0 |  | 897 | 0 | 175 | 0 | 49 | 0 | 0 | 0 | 0 | 36 | 16 | 130 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 154 | 94 | 0 | 35 | 0 | 70 | 0 | 0 | 70 | 530 | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 294 |  | 5654 | 3075 | 8729 | 3067 | 897 | 1246 | 0 | 2314 | 984 | 46 | 0 | 69 | 106 | 0 | 0 | 90.89
24:00 | 0 | 0 | 0 | 180 | 0 | 71 | 0 | 299 | 266 |  | 0 | 225 | 0 | 32 | 0 | 45 | 0 | 0 | 0 | 42 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 25 | 27 | 33 | 32 | 8 | 0 | 46 | 0 | 0 | 0 | 17 | 151 | 0 | 0 | 0 |  | 12 | 0 | 17 | 22 | 0 | 37 | 0 | 7 | 0 | 0 | 0 | 0 | 210 | 0 | 0 | 75 | 48 | 30 | 0 | 0 | 0 | 0 | 8 | 22 | 8 | 33 | 15 | 102 | 102 | 0 | 11 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 70 | 81 | 0 | 164 | 0 | 0 | 0 | 180 | 0 | 3 | 0 | 260 | 0 | 0 | 48 | 0 | 149 | 0 | 25 | 85 | 80 | 420 | 49 | 105 | 34 | 0 | 16 | 36 | 73 | 17 | 75 | 30 | 380 | 17 | 0 | 17 | 107 | 0 | 20 | 0 | 27 | 17 | 407 | 0 | 0 |  | 802 | 0 | 180 | 0 | 49 | 0 | 0 | 0 | 0 | 36 | 16 | 130 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 94 | 0 | 35 | 0 | 66 | 0 | 0 | 70 | 530 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 264 |  | 5426 | 2957 | 8383 | 3274 | 802 | 1176 | 0 | 1960 | 954 | 46 | 0 | 69 | 102 | 0 | 0 | 90.89
KWH | 0 | 0 | 0 | 4378500 | 0 | 1629863 | 0 | 7319550 | 6426000 |  | 0 | 5128400 | 0 | 1237440 | 0 | 1108926 | 0 | 0 | 0 | 1320960 | 565488 | 1851840 | 0 | 0 | 0 | 0 | 528480 | 807061 | 860644 | 424872 | 600000 | 600120 | 757800 | 672800 | 718560 | 0 | 1069920 | 0 | 0 | 0 | 308156 | 3412541 | 0 | 0 | 0 |  | 206880 | 325780 | 317448 | 661920 | 0 | 647520 | 0 | 129120 | 0 | 0 | 0 | 0 | 5796000 | 0 | 0 | 1040160 | 1068912 | 548640 | 0 | 0 | 0 | 345632 | 213509 | 511488 | 169020 | 580500 | 345300 | 2552640 | 1664640 | 0 | 266940 | 14100 | 0 | 985080 | 0 | 0 | 0 | 0 | 1496640 | 761280 | 0 | 3807310 | 0 | 0 | 0 | 6905500 | 0 | 72288 | 65664 | 3904145 | 530075 | 448975 | 1300800 | 388564 | 2983968 | 130140 | 743040 | 966240 | 1741309 | 9176000 | 1640400 | 2115372 | 1374981 | 21211 | 2734909 | 794428 | 1774756 | 425220 | 1883280 | 747840 | 9185600 | 437760 | 322670 | 1766880 | 2579345 | 0 | 551520 | 202250 | 1289280 | 426600 | 9755900 | 56872 | 0 |  | 19434181 | 0 | 4146912 | 0 | 611520 | 0 | 0 | 0 | 117600 | 395776 | 123750 | 3205000 | 450100 | 0 | 0 | 0 | 0 | 84656 | 0 | 264932 | 0 | 585417 | 112858 | 139046 | 118451 | 434640 | 0 | 242730 | 0 | 0 | 3906100 | 0 | 0 | 4135645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5131927 | 1086240 | 0 | 1412736 | 0 | 1273104 | 0 | 36754 | 1264800 | 16007200 | 2603809 | 0 | 0 | 23760 | 465120 | 935808 | 0 | 0 | 0 | 194855 | 4497200 |  | 135628162 | 73442627 | 209070789 | 75818248 | 19434181 | 30149279 | 1433278 | 48800038 | 24410500 | 1069920 | 56872 | 3934973 | 2552640 | 1410860 | 0
Fuel Cost | 0 | 0 | 0 | 6523965 | 0 | 2167717.79 | 0 | 7685527.5 | 6940080 |  | 0 | 5589956 | 0 | 13834579.2 | 0 | 14693269.5 | 0 | 0 | 0 | 19312435.2 | 7956416.16 | 30018326.4 | 0 | 0 | 0 | 0 | 6722265.6 | 10895323.5 | 11541236.04 | 318654 | 450000 | 0 | 0 | 0 | 12222705.6 | 0 | 288878.4 | 0 | 0 | 0 | 5038350.6 | 3549042.64 | 0 | 0 | 0 |  | 2699784 | 5434010.4 | 5402964.96 | 8942539.2 | 0 | 7491806.4 | 0 | 429969.6 | 0 | 0 | 0 | 0 | 6317640 | 0 | 0 | 1268995.2 | 1207870.56 | 817473.6 | 0 | 0 | 0 | 5969064.64 | 2871696.05 | 700738.56 | 126765 | 1015875 | 258975 | 18327955.2 | 1814457.6 | 0 | 363038.4 | 224754 | 0 | 1300305.6 | 0 | 0 | 0 | 0 | 2903481.6 | 1735718.4 | 0 | 3845383.1 | 0 | 0 | 0 | 6905500 | 0 | 54938.88 | 1376317.44 | 53291579.25 | 11110372 | 9280313.25 | 17534784 | 8031617.88 | 41327956.8 | 1521336.6 | 7668172.8 | 13198838.4 | 23107170.43 | 8441920 | 19947264 | 30588279.12 | 17393509.65 | 0 | 32107831.66 | 8651320.92 | 18865656.28 | 5770235.4 | 24275479.2 | 8809555.2 | 8450752 | 5668992 | 4662581.5 | 22421707.2 | 29352946.1 | 0 | 7202851.2 | 2416887.5 | 19300521.6 | 5618322 | 0 | 0 | 0 |  | 58302543 | 0 | 4644541.44 | 0 | 6365923.2 | 0 | 0 | 0 | 2117976 | 7123968 | 1778287.5 | 3589600 | 873194 | 0 | 0 | 0 | 0 | 1419681.12 | 0 | 4143536.48 | 0 | 9694505.52 | 1908428.78 | 1895196.98 | 1998268.37 | 899704.8 | 0 | 183746.61 | 0 | 0 | 20663269 | 0 | 0 | 4797348.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5080607.73 | 14599065.6 | 0 | 16712666.88 | 0 | 16168420.8 | 0 | 406131.7 | 15354672 | 144224872 | 2655885.18 | 0 | 0 | 268725.6 | 5455857.6 | 14345936.64 | 0 | 0 | 0 | 0 | 0 |  | 721575501.46 | 367672560.73 | 1089248062.19 | 69813561.89 | 58302543 | 34095807.1 | 29798620.57 | 633240055.38 | 164888141 | 288878.4 | 0 | 65536225.15 | 18327955.2 | 14956274.5 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 0 | 65 | 0 | 309 | 274 |  | 0 | 225 | 0 | 84 | 0 | 45 | 0 | 0 | 0 | 76 | 24 | 98 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 0 | 22 | 21 | 33 | 16 | 42 | 0 | 46 | 0 | 0 | 0 | 17 | 151 | 0 | 0 | 0 |  | 6 | 24 | 0 | 22 | 0 | 18 | 0 | 2 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 30 | 40 | 5 | 0 | 0 | 0 | 22 | 8 | 22 | 8 | 14 | 15 | 116 | 38 | 0 | 11 | 2 | 0 | 43 | 0 | 0 | 0 | 0 | 56 | 0 | 0 | 164 | 0 | 0 | 0 | 280 | 0 | 3 | 0 | 113 | 103 | 98 | 76 | 72 | 142 | 19 | 25 | 17 | 65 | 420 | 68 | 105 | 51 | 4 | 255 | 36 | 73 | 17 | 108 | 25 | 400 | 17 | 45 | 145 | 107 | 0 | 17 | 30 | 115 | 17 | 406 | 7 | 0 |  | 896 | 0 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 135 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 15 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 17 | 0 | 35 | 0 | 34 | 0 | 6 | 37 | 540 | 109 | 0 | 0 | 5 | 77 | 35 | 0 | 0 | 0 | 32 | 174 |  | 9135 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 0 | 71 | 0 | 278 | 252 | 0 | 0 | 225 | 0 | 90 | 0 | 45 | 0 | 0 | 0 | 84 | 50 | 133 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 22 | 22 | 20 | 33 | 17 | 48 | 0 | 46 | 0 | 0 | 0 | 17 | 152 | 0 | 0 | 0 | 0 | 12 | 16 | 51 | 44 | 0 | 37 | 0 | 2 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 30 | 48 | 15 | 0 | 0 | 0 | 30 | 8 | 22 | 8 | 15 | 15 | 122 | 35 | 0 | 11 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 66 | 81 | 0 | 164 | 0 | 0 | 0 | 280 | 0 | 3 | 70 | 240 | 109 | 50 | 86 | 50 | 149 | 0 | 40 | 65 | 117 | 408 | 96 | 105 | 95 | 0 | 283 | 36 | 91 | 17 | 107 | 43 | 400 | 17 | 0 | 162 | 107 | 0 | 32 | 0 | 115 | 17 | 402 | 0 | 0 |  | 897 | 0 | 145 | 0 | 107 | 0 | 0 | 0 | 31 | 75 | 16 | 130 | 27 | 0 | 0 | 0 | 0 | 31 | 4 | 80 | 0 | 25 | 32 | 43 | 32 | 16 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 205 | 80 | 0 | 85 | 0 | 113 | 0 | 0 | 113 | 640 | 109 | 0 | 0 | 0 | 0 | 108 | 0 | 0 | 0 | 0 | 242 |  | 10526 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 0 | 71 | 0 | 280 | 255 | 0 | 0 | 225 | 0 | 90 | 0 | 45 | 0 | 0 | 0 | 84 | 50 | 133 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 22 | 27 | 33 | 33 | 50 | 0 | 46 | 0 | 0 | 0 | 17 | 150 | 0 | 0 | 0 | 0 | 12 | 34 | 51 | 44 | 0 | 44 | 0 | 2 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 68 | 40 | 15 | 0 | 0 | 0 | 35 | 8 | 22 | 8 | 33 | 15 | 165 | 100 | 0 | 11 | 0 | 0 | 43 | 50 | 33 | 0 | 0 | 70 | 78 | 0 | 177 | 19 | 20 | 10 | 0 | 22 | 3 | 100 | 285 | 150 | 50 | 95 | 50 | 149 | 0 | 50 | 100 | 115 | 400 | 99 | 105 | 105 | 0 | 300 | 36 | 91 | 0 | 108 | 50 | 400 | 17 | 0 | 162 | 107 | 0 | 35 |  | 115 | 17 | 400 |  |  |  | 913 | 0 | 175 | 0 | 115 | 0 | 0 | 0 | 45 | 75 | 16 | 130 | 25 | 0 | 0 | 0 | 0 | 30 | 20 | 90 | 0 | 50 | 40 | 43 | 35 | 18 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 255 | 94 | 10 | 113 | 0 | 113 | 0 | 0 | 113 | 800 | 110 |  | 0 |  |  | 108 | 0 |  |  |  | 200
Forecast for Day | 0 | 0 | 0 | 180 | 0 | 71 | 0 | 300 | 255 | 0 | 0 | 225 | 0 | 80 | 0 | 45 | 0 | 0 | 0 | 75 | 24 | 98 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 22 | 27 | 33 | 31 | 42 | 0 | 46 | 0 | 0 | 0 | 17 | 150 | 0 | 0 | 0 | 0 | 12 | 20 | 17 | 22 | 0 | 26 | 0 | 2 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 68 | 40 | 15 | 0 | 0 | 0 | 0 | 8 | 22 | 8 | 33 | 15 | 143 | 70 | 0 | 11 | 1.6 | 0 | 43 | 50 | 33 | 0 | 0 | 70 | 0 | 0 | 177 | 19 | 20 | 10 | 0 | 22 | 3 | 100 | 97 | 100 | 50 | 70 | 0 | 125 | 20 | 25 | 51 | 75 | 400 | 50 | 105 | 51 | 5 | 260 | 36 | 70 | 0 | 108 | 25 | 400 | 17 | 50 | 90 | 107 | 0 | 17 | 30 | 115 | 17 | 400 |  |  |  | 913 | 0 | 175 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 8 | 0 | 18 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 255 | 64 | 0 | 85 | 0 | 90 | 0 | 8 | 90 | 800 | 110 |  | 0 | 6 | 100 | 70 | 0 |  |  | 30 | 190
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 0 | 71 | 0 | 303 | 266 | 0 | 0 | 225 | 0 | 24 | 0 | 30 | 0 | 0 | 0 | 30 | 8 | 98 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 22 | 22 | 27 | 33 | 33 | 42 | 0 | 46 | 0 | 0 | 0 | 5 | 151 | 0 | 0 | 0 | 0 | 12 | 0 | 17 | 22 | 0 | 27 | 0 | 2 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 67 | 43 | 30 | 0 | 0 | 0 | 0 | 8 | 0 | 8 | 20 | 15 | 82 | 70 | 0 | 12 | 1 | 0 | 43 | 50 | 33 | 0 | 0 | 70 | 0 | 0 | 177 | 19 | 23 | 10 | 45 | 22 | 3 | 0 | 97 | 0 | 0 | 46 | 0 | 135 | 9 | 25 | 17 | 75 | 418 | 49 | 105 | 34 | 2 | 16 | 36 | 53 | 0 | 78 | 25 | 400 | 17 | 17 | 17 | 107 | 0 | 17 | 10 | 18 | 17 | 407 | 0 | 0 | 0 | 660 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 8 | 0 | 18 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 249 | 64 | 0 | 35 | 0 | 97 | 0 | 1 | 37 | 690 | 110 | 0 | 0 | 1 | 26 | 72 | 0 | 0 | 0 | 9 | 198 | 0 |  |  |  |  | 54225161 |  | 0
54225161
| Minimum Generation |  | 7024 | 5:00
| Highest Generation |  | 10526 | 18:00
| Day Peak Generation |  | 9135 | 12:00
| Evening Peak Generation |  | 10526 | 18:00
| HVDC Max Flow |  | 898 | 17:00
| HVDC EvPeak Flow |  | 897 | 18:00
| Load factor L.F |  | 82.76% | [161 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2022-11-22
Till now the maximum generation is : - |  |  | 14782 | 21:00 | Hrs on | 2022-04-16
The Summary of Yesterday's |  | 2022-11-21 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 9135 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 6884 | MW
Evening Peak Generation : |  | 10526 | MW Hour : | 18:00 | Available Max Generation : |  | 11313 | MW
E.P. Demand (at gen end) : |  | 10526 | MW Hour : | 18:00 | Max Demand (Evening) : |  | 10800 | MW
Maximum Generation : |  | 10526 | MW Hour : | 18:00 | Reserve(Generation end) |  | 513 | MW
Total Gen. (MKWH) : |  | 209.0708 | System Load Factor : | 82.76% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | 566 | MW at | 7:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2022-11-22
Actual : | 90.89 | Ft.(MSL) , | Rule curve : | 107.1 | Ft.( MSL )
Gas Consumed : | Total = | 804.93 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 103909368.99
: |  | Coal : | 164888141 | Oil : | 728574901.1 | Total : | 997372411.09
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4098.4931 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1161.0318 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1532.4656 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1359.6786 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1157.4564 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 956.2319 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 427.3941 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 348.401 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 755.0075 |  |  | 0 | 0%
Total | 0 |  | 11796.16 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1, 2 |  | 10) Ashuganj-225 MW
|  |  |  | 2) Ghorasal-3, 4, 7 |  | 11) Bibiana-II 341 MW CCPP (Summit)
3) Ashuganj-5
4) Baghabari-71,100 MW
5) Raozan unit-1 & 2
6) Siddhirganj 210 MW .
7) Shajibazar 330 MW
8) Sirajganj-2
9) Ashuganj(N)-360 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Mymensingh-Jamalpur 132 kV Ckt-2 was under shutdown from 08:24 to 16:27 for A/M.
b) Rangamati-Khagrachari 132 kV Ckt-1 was under shutdown from 09:28 to 16:51 for A/M.
c) Baroierhat 132/33 kV T-1 transformer was under shutdown from 08:57 to 17:01 for C/M.
d) Bibiyana-Cumilla(N) 230 kV Ckt-2 was under shutdown from 08:25 to 22:19 for A/M.
e) B.Baria 132/33 kV T-2 transformer was under shutdown from 08:43 to 15:27 for A/M.
f) Chatak 132/33 kV T-1 transformer was under shutdown from 08:55 to 16:15 for A/M.
g) Tongi 132/33 kV T-3 transformer was under shutdown from 09:18 to 16:20 for A/M.
h) Aminbazar-Keraniganj 230 kV Ckt-1 was under shutdown from 10:16 to 18:23 for A/M.
i) Sikalbaha-Dohazari 132 kV Ckt-1 was under shutdown from 08:20 to 16:32 for A/M.
j) Aminbazar 230 kV Bus-2 was shutdown at 09:31 for A/M.
k) Srinagar-Keraniganj 132 kV Ckt-1 was under shutdown from 10:43 to 12:42 for A/M.
l) Rangpur-Barapukuria 132 kV Ckt-1 was under shutdown from 08:10 to 16:20 for A/M.
m) Sirajganj 132/33 kV T-2 transformer was under shutdown from 08:31 to 16:10 for A/M.
n) Mithapukur 132/33 kV T-1 transformer was under shutdown from 09:03 to 17:10 for A/M.
o) Khulna(S)-Jhenaidah 230 kV Ckt-1 was under shutdown from 08:14 to 17:07 for A/M.
p) Joydevpur 132/33 kV T-2 transformer was under shutdown from 11:55 to 11:59 for C/M.
q) Joydevpur 132/33 kV T-4 transformer was under shutdown from 12:15 to 12:37 for C/M.
r) Srinagar-Keraniganj 132 kV Ckt-2 was under shutdown from 13:01 to 15:25 for A/M.
s) Goalpara-Bagerhat 132 kV Ckt was under shutdown from 08:19 to 15:38 for A/M.
t) Norail 132/33 kV T-1 transformer was under shutdown from 09:13 to 16:02 for A/M.
u) Barisal(N) 230/132 kV T-1 transformer was under shutdown from 10:17 to 17:01 for A/M.
v) Patuakhali 132/33 kV T-2 transformer was under shutdown from 12:52 to 15:18 for A/M.
w) Chandpur CCPP ST was synchronized at 08:57 and tripped at 10:13 due to winding temperature high.
x) Bhola CCPP ST was shut down at 12:06 due to lube oil leakage.
y) Patuakhali-Payra 132 kV Ckt-1 was under shutdown from 16:02 to 16:39 for DS check.
z) Bhandaria 132/33 kV T-2 transformer was switched on at 16:09.
aa) Bhandaria 132/33 kV T-4 transformer was switched on at 16:04.
ab) Manikganj-Kabirpur 132 kV Ckt-1 was shutdown at 07:29(22-11-2022) for A/M.
ac) Patuakhali 132/33 T-3 transformer was under shutdown since at 07:05(22-11-2022) for A/M.
ad) Jashore 132/33 T-1 transformer was under shutdown since at 07:11(22-11-2022) for A/M.
ae) Naogaon-Santahar P/P 132 kV Ckt was under shutdown since at 07:42(22-11-2022) for A/M.
| Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2022-11-21 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Line O/L
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4378500
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 71 | 1629863 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 278 | 7319550 | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 252 | 6426000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 5128400 | GT-2 S/D due to Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 90 | 1237440 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 0 | 0 | Under maint.
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 45 | 1108926 | Engine problem
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 424872
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 84 | 1320960 | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 50 | 565488 | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 35 | 528480 | Engine problem
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 133 | 1851840 | Engine problem
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 807061
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 860644 | Engine problem
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 42 | 1200120 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 757800
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 17 | 672800 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 48 | 718560 | Engine problem
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 240 | 3904145 | Fuel shortage
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 109 | 530075 | Fuel conservation
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 50 | 448975 | Fuel conservation
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 50 | 388564 | Fuel conservation
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 2983968
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 2115372
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 17 | 437760 | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 1766880
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 202250
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 426600 | Fuel shortage
| Dhaka area Total |  |  |  | 5847 | 2594 | 50141893
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Machine problem
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 17 | 308156 | Engine problem
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 130140
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 37 | 647520 | Engine problem
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 46 | 1069920 | Low water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 152 | 3412541 | ST Under maint
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 95 | 1374981 | Engine problem
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 16 | 325780 | Fuel shortage
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 317448 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 44 | 661920 | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 40 | 743040 | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 0 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 2 | 129120
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 21211
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 283 | 2734909 | Engine problem
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 36 | 794428 | Engine problem
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 91 | 1774756 | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 43 | 747840 | Engine problem
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 107 | 2579345 | Engine problem
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 56872 | On test.
| Chattogram area Total |  |  |  | 2382 | 1060 | 17829927
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 0 | 0 | Gas shortage
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 0 | 0 | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 240 | 5796000 | Gas shortage
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+136*1 | 284 | 402 | 9755900 | On test.
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 48 | 1068912
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 15 | 548640 | Gas shortage
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 0 | 0 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 0 | 0 | Gas shortage
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 117 | 1741309 | Fuel shortage
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 30 | 345632 | Engine problem
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 30 | 1040160 | Machine problem
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 65 | 966240 | Fuel shortage
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 511488
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 169020 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 122 | 2552640
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 15 | 580500 | Engine problem
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 8 | 213509 | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 15 | 345300 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 70 | 65664 | Fuel conservation
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 17 | 425220 | Fuel shortage
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 107 | 1883280 | Engine problem
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 32 | 551520 | Engine problem
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 115 | 1289280
| Cumilla Area Total |  |  |  | 3169 | 1478 | 29850214
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 35 | 1664640 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 11 | 266940 | Gas shortage
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 14100
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 86 | 1300800 | Engine problem
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 96 | 1640400 | Engine problem
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 322670
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 206880 | Engine problem
| Mymensingh Area Total |  |  |  | 614 | 240 | 5416430
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 0 | 0 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 43 | 985080 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Gas shortage
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 0 | 0 | Gas shortage
| Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 0 | 0 | Gas shortage
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 3 | 72288 | Gas shortage
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 66 | 1496640
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 761280
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 164 | 3807310 | Gas shortage
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50MW PP (EPL) |  | NENP | 27*2 | 50 | 0 | 0 | Gas shortage
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 0 | 0 | Gas shortage
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 280 | 6905500 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 408 | 9176000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 0 | 0
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 400 | 9185600
| Sylhet Area Total |  |  |  | 2477 | 1445 | 32389698
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Fuel shortage
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 897 | 19434181
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 107 | 611520 | Engine problem
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 31 | 117600 | Engine problem
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 75 | 395776 | High voltage
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 145 | 4146912 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 16 | 123750 | Fuel shortage
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Fuel conservation
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 80 | 1086240 | Engine problem
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Fuel shortage
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 465120
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 0 | 0 | 0 | On test.
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 0 | 0 | 0 | 0 | On test.
| Khulna Area Total |  |  |  | 2384 | 1351 | 26381099
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Line O/L
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 27 | 450100 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 130 | 3205000 | Gas shortage
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 640 | 16007200 | Line O/L
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 109 | 2603809 | Machine problem
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Line O/L
| Barisal 307 MW |  | BCPCL | 0 | 0 | 242 | 4497200 | On test.
| Barisal Area Total |  |  |  | 1958 | 1148 | 26763309
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 31 | 84656 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 4 | 0
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contract Expired
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 25 | 585417 | Engine problem
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 112858 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 152 | 4135645 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 205 | 5131927 | Gas shortage
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 118451 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 16 | 434640 | Engine problem
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 242730
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 43 | 139046 | Engine problem
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 80 | 264932 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Fuel conservation
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 85 | 1412736 | Engine problem
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 1264800
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 23760
| Rajshahi Area Total |  |  |  | 2129 | 829 | 13951598
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 160 | 3906100 | Machine problem
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 1273104
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 36754
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 108 | 935808 | Engine problem
| Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 194855
| Rangpur Area Total |  |  |  | 750 | 381 | 6346621
| Total |  |  |  | 21710 | 10526 | 209070789
| Eastern Grid Total |  |  |  | 14489 | 6817 | 135628162
| Western Grid Total |  |  |  | 7221 | 3709 | 73442627
| National Grid Total |  |  |  | 21710 | 10526 | 209070789
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2022-11-21
| (a) ENTIRE EASTERN GRID : |  | 7279.9 | MW | (b) ENTIRE WESTERN GRID : |  | 3000.25 | MW
| i) Dhaka area |  | 3985.6 | MW | i) Khulna area |  | 1138.8 | MW
| ii) Chittagong area |  | 1286.3 | MW | ii) Rajshahi area |  | 932.7 | MW
| iii) Comilla area |  | 843 | MW | iii) Barisal area |  | 251.75 | MW
| iv) Mymensingh area |  | 776 | MW | iv) Rangpur area |  | 677 | MW
| v) Sylhet area |  | 389 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 10280.15 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 24 | 12:00 | Chowmuhani | 131 | 19:00 | Kaptai | 4 | 18:00 | Nawabganj | 27.4 | 21:00 | Sholosohor | 31 | 18:00
2 | AKSML | 91 | 03:00 | Chuadanga | 68 | 18:00 | Kazla | 82 | 13:00 | Netrakona | 85 | 18:00 | Shyampur | 142 | 01:00
3 | Aftabnagar | 26 | 13:00 | Coxsbazar | 96 | 18:00 | Keranigonj | 52 | 18:00 | New | 68 | 12:00 | Siddhirganj | 92 | 12:00
4 | Agargaon | 57 | 18:00 | Cumilla(N) | 86 | 19:30 | Khagrachori | 22 | 18:00 | Niamatpur | 46 | 18:30 | Sirajganj | 63 | 18:30
5 | Agrabad | 62 | 18:00 | Cumilla(S) | 122 | 14:00 | Khulna | 73 | 18:00 | Noapara | 33.5 | 18:30 | Sonargaon | 100 | 00:00
6 | Amnura | 35 | 18:00 | Daudkandi | 102 | 18:00 | Khulshi | 161 | 13:00 | PHP | 5 | 20:00 | Sreemongol | 43 | 19:30
7 | Ashuganj | 52 | 18:30 | Dhaka | 32 | 13:00 | Kishoreganj | 94 | 19:00 | Pabna | 73 | 18:00 | Srinagar | 28.78 | 19:30
8 | BSRM | 139 | 11:00 | Dhamrai | 110 | 18:00 | Kodda | 238 | 15:00 | Palashbari | 88 | 18:00 | Sunamganj | 33 | 19:00
9 | Bagerhat | 77 | 18:00 | Dhanmondi | 106 | 13:00 | Kulaura | 32 | 18:00 | Panchagarh | 54 | 18:00 | Sylhet | 110 | 18:00
10 | Bakulia | 107 | 18:00 | Dohazari | 78 | 18:00 | Kurigram | 46 | 18:00 | Patuakhali | 76 | 20:00 | TK | 16.2 | 00:00
11 | Banani | 31 | 14:00 | Faridpur | 100 | 19:30 | Kushtia | 99 | 18:00 | Payra | 0.8 | 18:30 | Tangail | 144 | 18:00
12 | Bangabhaban | 13 | 10:00 | Fatullah | 61 | 16:00 | Lalbag | 73 | 13:00 | Postogola | 32 | 13:00 | Thakurgaon | 64 | 18:00
13 | Barapukuria | 40 | 18:00 | Fenchuganj | 30 | 18:30 | Lalmonirhat | 34 | 18:00 | Purbachal | 6 | 13:00 | Tongi | 106 | 15:00
14 | Barguna | 12 | 20:00 | Feni | 88 | 18:00 | Madanganj | 82 | 00:00 | Purbasadipur | 88 | 19:00 | Ullon | 29 | 18:00
15 | Barishal | 73 | 13:00 | GPH | 90 | 16:00 | Madaripur | 63 | 20:00 | Rahanpur_I | 12.5 | 22:00 | Uttara | 64 | 13:00
16 | Barishal-230 | 50 | 18:00 | Ghorashal | 56 | 20:00 | Madartek | 61 | 18:00 | Rahim | 39 | 13:00 | UttaraNew | 13 | 11:00
17 | Baroaulia | 63 | 18:00 | Goalpara | 16 | 13:00 | Madunaghat | 43 | 18:00 | Rajbari | 44 | 18:00 | Zigatola | 37 | 19:00
18 | Baroirhat | 38 | 18:00 | Gollamari | 38 | 18:00 | Magura | 42 | 18:00 | Rajendrapur | 98 | 19:30
19 | Bashundhara | 126 | 12:00 | Gopalganj | 69.8 | 18:00 | Mahasthangarh | 42 | 18:00 | Rajshahi | 92 | 18:30
20 | BashundharaCement | 7 | 14:00 | Gulshan | 96 | 16:00 | Manikganj | 59 | 19:30 | Rajshahi-230 | 26 | 18:00
21 | Beanibazar | 38 | 18:00 | Halishahar | 111.5 | 12:00 | Maniknagar | 55 | 13:00 | Ramganj | 62 | 18:00
22 | Benapole | 42 | 18:30 | HaripurSBU | 150 | 20:00 | Matarbari | 36 | 18:00 | Rampur | 25 | 18:30
23 | Bhaluka | 120 | 19:00 | Hasnabad | 61 | 13:00 | Matuail | 58.6 | 10:00 | Rangamati | 12 | 18:00
24 | Bhandaria | 33 | 19:30 | Hathazari | 47 | 18:00 | Millgate | 58 | 16:00 | Rangpur | 115 | 18:00
25 | Bhangura | 21 | 18:00 | Ishurdi | 54 | 18:00 | Mirpur | 97 | 18:00 | Ruppur | 4 | 17:00
26 | Bheramara(GK) | 37 | 18:00 | Jaldhaka | 46 | 18:00 | Mirsorai | 1 | 09:00 | SSM | 0 | 00:00
27 | Bhulta | 220 | 12:00 | Jamalpur | 109 | 18:30 | Mithapukur | 20 | 08:00 | Saidpur | 83 | 18:00
28 | Bog-Sherpur | 48 | 18:00 | Jashore | 91 | 18:00 | Modern | 0 | 00:00 | Satkhira | 73 | 18:00
29 | Bogura | 118 | 18:30 | Jhenaidah | 87 | 18:00 | Mogbazar | 103 | 15:00 | Satmasjid | 73 | 13:00
30 | Borhanuddin | 23 | 21:00 | Joydebpur | 152 | 19:00 | Mongla | 26 | 00:00 | Savar | 135 | 12:00
31 | Brahmanbaria | 110 | 18:30 | Joypurhat | 38 | 18:00 | Motijheel | 27 | 12:00 | Shahjadpur | 69 | 18:00
32 | Cantonment | 104 | 13:00 | Juldah | 21 | 13:00 | Munshiganj | 69 | 00:00 | Shahjibazar | 89 | 18:30
33 | Chandpur | 42 | 20:00 | KSRM | 43 | 18:00 | Mymensingh | 148 | 19:00 | Shahmirpur | 30.8 | 03:00
34 | Chandraghona | 24 | 18:00 | Kabirpur | 241 | 15:00 | Naogaon | 85 | 18:00 | Shariatpur | 46 | 20:00
35 | Chapai | 39 | 11:00 | Kachua | 46 | 19:00 | Narail | 37 | 18:00 | Sherpur | 94 | 18:00
36 | Charsaidpur | 47.7 | 01:00 | Kallyanpur | 63 | 12:00 | Narinda | 56 | 13:00 | Shikalbaha | 22 | 01:00
37 | Chauddagram | 29 | 18:00 | Kalurghat | 6 | 09:00 | Narshingdi | 136 | 18:30 | Shikalbaha-230 | N/A | N/A
38 | Chhatak | 19 | 18:00 | Kamrangirchar | 69 | 18:00 | Natore | 87 | 18:00 | Shitalakhya | 118 | 12:00
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2022-11-21 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Bhulta | 383 | 22:00 | 370 | 15:00 | Kaliakoir | 398 | 19:00 | 39 | 00:00
| Bibiana | 404 | 20:00 | 393 | 10:00 | Payra | 423 | 19:30 | 416 | 13:00
| BIPTC | 408 | 01:00 | 396 | 11:00 | Rahanpur_I | 415 | 18:30 | 390 | 15:00
| Gopalganj_I | 422 | 02:00 | 413 | 10:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 228 | 18:30 | 219 | 10:00 | Hasnabad | 228 | 06:00 | 219 | 15:00
| AKSML | 236 | 19:00 | 221 | 09:00 | Hathazari | 236 | 18:00 | 220 | 10:00
| Aminbazar | 228 | 07:00 | 221 | 09:00 | Ishurdi | 240 | 02:00 | 230 | 16:00
| Ashuganj | 240 | 22:00 | 226 | 15:00 | Jhenaidah | 239 | 00:00 | 228 | 13:00
| Baghabari | 236 | 00:00 | 229 | 12:00 | Kaliakoir | 229 | 19:00 | 219 | 15:00
| Barapukuria | 230 | 19:00 | 223 | 12:00 | Keranigonj | 228 | 22:00 | 218 | 16:00
| Barishal | 248 | 05:00 | 245 | 12:00 | Khulna(S) | 240 | 19:30 | 226 | 13:00
| Bheramara | 237 | 06:00 | 227 | 13:00 | Maniknagar | 228 | 21:00 | 219 | 15:00
| Bhulta | 230 | 21:00 | 220 | 15:00 | Meghnaghat | 232 | 22:00 | 226 | 15:00
| Bibiana | 237 | 02:00 | 231 | 03:00 | Mirsorai | 233 | 19:00 | 213 | 10:00
| BIPTC | 240 | 01:00 | 229 | 13:00 | Rajshahi | 245 | 01:00 | 232 | 13:00
| Bogura | 236 | 19:30 | 227 | 16:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 250 | 01:00 | 248 | 15:00 | Rampura | 228 | 22:00 | 219 | 10:00
| BSRM | 236 | 19:00 | 220 | 10:00 | Shikalbaha | 237 | 18:00 | 227 | 01:00
| Cumilla(N) | 231 | 19:00 | 221 | 10:00 | Shyampur | 238 | 18:30 | 222 | 10:00
| Fenchuganj | 239 | 22:00 | 232 | 10:00 | Siddhirganj | 228 | 22:00 | 219 | 10:00
| Ghorashal | N/A | N/A | N/A | N/A | Sirajgonj | 229 | 04:00 | 220 | 15:00
| GPH | 232 | 14:00 | 226 | 03:00 | Tongi | 234 | 19:30 | 227 | 16:00
| Haripur | 227 | 21:00 | 219 | 10:00 |  | 226 | 19:00 | 212 | 15:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 132 | 02:00 | 125 | 15:00 | Lalbag | 138 | 22:00 | 131 | 15:00
| Agargaon | 132 | 06:00 | 126 | 10:00 | Lalmonirhat | 138 | 07:00 | 129 | 12:00
| Agrabad | 137 | 19:30 | 128 | 10:00 | Madanganj | 135 | 18:30 | 128 | 15:00
| AKS | 136 | 18:00 | 126 | 09:00 | Madaripur | 140 | 06:00 | 136 | 10:00
| Aminbazar | 133 | 17:00 | 126 | 09:00 | Madartek | 133 | 06:00 | 125 | 15:00
| Amnura | 135 | 19:00 | 128 | 10:00 | Madunaghat | 138 | 18:30 | 129 | 02:00
| Ashuganj | 137 | 22:00 | 131 | 11:00 | Magura | 138 | 00:00 | 130 | 13:00
| Bagerhat | 138 | 19:00 | 128 | 13:00 | Mahasthangarh | 138 | 00:00 | 133 | 11:00
| Bakulia | 137 | 18:30 | 125 | 10:00 | Manikganj | 135 | 18:00 | 128 | 04:00
| Banani | 136 | 01:00 | 126 | 15:00 | Maniknagar | 135 | 22:00 | 129 | 10:00
| Bangabhaban | 135 | 22:00 | 129 | 16:00 | Matarbari | 129 | 08:00 | 114 | 10:00
| Barapukuria | 138 | 19:00 | 133 | 05:00 | Matuail | 134 | 22:00 | 129 | 15:00
| Barguna | 136 | 06:00 | 131 | 13:00 | Millgate | 134 | 00:00 | 126 | 15:00
| Barishal | 140 | 00:00 | 128 | 16:00 | Mirpur | 133 | 19:30 | 124 | 10:00
| Barishal-230 | 141 | 05:00 | 138 | 14:00 | Mithapukur | 138 | 19:00 | 131 | 12:00
| Baroaulia | 140 | 19:30 | 126 | 10:00 | Modern | 134 | 18:00 | 130 | 00:00
| Baroirhat | 138 | 18:30 | 130 | 10:00 | Mogbazar | 134 | 03:00 | 126 | 15:00
| Bashundhara | 136 | 01:00 | 126 | 15:00 | Mongla | 138 | 19:00 | 126 | 13:00
| BashundharaCement | 135 | 18:30 | 128 | 15:00 | Motijheel | 135 | 22:00 | 129 | 16:00
| Beanibazar | 132 | 02:00 | 128 | 13:00 | Munshiganj | 135 | 18:30 | 129 | 10:00
| Benapole | 137 | 01:00 | 127 | 13:00 | Mymensingh | 136 | 23:00 | 122 | 11:00
| Bhaluka | 134 | 19:00 | 122 | 08:00 | Naogaon | 138 | 19:00 | 132 | 10:00
| Bhandaria | 141 | 06:00 | 138 | 12:00 | Narail | 138 | 05:00 | 129 | 13:00
| Bhangura | 142 | 01:00 | 136 | 13:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bheramara | 138 | 02:00 | 133 | 13:00 | Narshingdi | 130 | 07:00 | 124 | 12:00
| Bheramara(GK) | 139 | 00:00 | 135 | 10:00 | Natore | 137 | 19:00 | 131 | 12:00
| Bhulta | 129 | 22:00 | 124 | 12:00 | Nawabganj | 137 | 08:00 | 130 | 15:00
| Bog-Sherpur | 139 | 00:00 | 134 | 11:00 | Netrakona | 134 | 23:00 | 121 | 11:00
| Bogura | 140 | 19:00 | 133 | 12:00 | New | 137 | 22:00 | 126 | 15:00
| Bogura-230 | 141 | 19:30 | 134 | 10:00 | Niamatpur | 137 | 19:00 | 128 | 12:00
| Brahmanbaria | 132 | 21:00 | 125 | 14:00 | Noapara | 137 | 00:00 | 128 | 13:00
| Cantonment | 132 | 22:00 | 124 | 15:00 | Pabna | 139 | 00:00 | 134 | 12:00
| Chandpur | 143 | 18:30 | 136 | 01:00 | Palashbari | 136 | 03:00 | 131 | 10:00
| Chandraghona | 139 | 19:30 | 126 | 10:00 | Panchagarh | 137 | 19:30 | 125 | 12:00
| Chapai | 136 | 19:30 | 127 | 15:00 | Patuakhali | 137 | 23:00 | 132 | 10:00
| Charsaidpur | 136 | 20:00 | 130 | 10:00 | Payra | 138 | 01:00 | 136 | 10:00
| Chauddagram | 138 | 19:00 | 132 | 10:00 | PHP | 139 | 19:30 | 130 | 10:00
| Chhatak | 130 | 04:00 | 128 | 12:00 | Postogola | 136 | 19:30 | 129 | 11:00
| Chowmuhani | 140 | 19:00 | 133 | 00:00 | Purbachal | 135 | 01:00 | 126 | 12:00
| Chuadanga | 136 | 02:00 | 128 | 13:00 | Purbasadipur | 137 | 21:00 | 124 | 11:00
| Coxsbazar | 126 | 16:00 | 115 | 13:00 | Rahim | 134 | 19:00 | 130 | 10:00
| Cumilla(N) | 138 | 17:00 | 132 | 10:00 | Rajbari | 137 | 02:00 | 132 | 13:00
| Cumilla(S) | 140 | 19:30 | 129 | 12:00 | Rajendrapur | 137 | 18:30 | 127 | 03:00
| Daudkandi | 135 | 22:00 | 129 | 10:00 | Rajshahi | 135 | 19:00 | 128 | 16:00
| Dhaka | 133 | 06:00 | 126 | 15:00 | Rajshahi-230 | 134 | 20:00 | 127 | 16:00
| Dhamrai | 138 | 22:00 | 130 | 14:00 | Ramganj | 139 | 18:30 | 133 | 04:00
| Dhanmondi | 134 | 19:00 | 130 | 10:00 | Rampur | 136 | 19:00 | 127 | 10:00
| Dohazari | 137 | 19:00 | 122 | 10:00 | Rampura | 132 | 22:00 | 126 | 10:00
| Faridpur | 136 | 04:00 | 132 | 10:00 | Rangamati | 138 | 18:30 | 128 | 10:00
| Fatullah | 135 | 08:00 | 130 | 10:00 | Rangpur | 137 | 19:00 | 127 | 16:00
| Fenchuganj | 135 | 08:00 | 132 | 10:00 | Ruppur | 138 | 01:00 | 134 | 13:00
| Feni | 140 | 19:30 | 133 | 01:00 | Saidpur | 136 | 19:00 | 127 | 12:00
| Ghorashal | 138 | 20:00 | 134 | 16:00 | Satkhira | 136 | 00:00 | 127 | 13:00
| Goalpara | 138 | 02:00 | 130 | 11:00 | Satmasjid | 132 | 22:00 | 126 | 15:00
| Gollamari | 138 | 19:00 | 130 | 12:00 | Savar | 136 | 22:00 | 125 | 15:00
| Gopalganj | 139 | 19:00 | 132 | 13:00 | Shahjadpur | 144 | 04:00 | 138 | 12:00
| Gopalganj_I | 139 | 20:00 | 133 | 13:00 | Shahjibazar | 135 | 23:00 | 130 | 10:00
| Gulshan | 132 | 05:00 | 125 | 15:00 | Shariatpur | 139 | 22:00 | 133 | 15:00
| Halishahar | 138 | 19:00 | 124 | 10:00 | Sherpur | 138 | 11:00 | 124 | 07:00
| Haripur | 134 | 19:00 | 130 | 10:00 | Shikalbaha | 138 | 18:30 | 125 | 10:00
| HaripurSBU | 134 | 05:00 | 129 | 15:00 | Shikalbaha-230 | 138 | 18:30 | 128 | 10:00
| Hasnabad | 136 | 21:00 | 129 | 10:00 | Shitalakhya | 136 | 22:00 | 127 | 10:00
| Hathazari | 140 | 19:00 | 130 | 10:00 | Sholosohor | 138 | 19:00 | 126 | 10:00
| Ishurdi | 139 | 01:00 | 134 | 13:00 | Shyampur | 135 | 08:00 | 128 | 15:00
| Jaldhaka | 135 | 19:30 | 123 | 18:00 | Shyampur-230 | 135 | 22:00 | 130 | 09:00
| Jamalpur | 140 | 11:00 | 128 | 07:00 | Siddhirganj | 134 | 20:00 | 130 | 10:00
| Jashore | 139 | 06:00 | 124 | 12:00 | Sirajganj | 140 | 00:00 | 135 | 12:00
| Jhenaidah | 138 | 00:00 | 132 | 13:00 | Sonargaon | 133 | 19:30 | 126 | 11:00
| Jhenaidah-230 | 139 | 00:00 | 131 | 13:00 | Sreemongol | 135 | 06:00 | 132 | 11:00
| Joydebpur | 140 | 07:00 | 135 | 03:00 | Srinagar | 137 | 22:00 | 130 | 10:00
| Joypurhat | 138 | 01:00 | 131 | 15:00 | SSM | 141 | 19:00 | 130 | 10:00
| Juldah | 138 | 18:30 | 125 | 10:00 | Sunamganj | 130 | 00:00 | 128 | 13:00
| Kabirpur | 136 | 18:00 | 123 | 15:00 | Sylhet | 132 | 01:00 | 130 | 12:00
| Kachua | 140 | 18:30 | 134 | 01:00 | Tangail | 136 | 23:00 | 128 | 07:00
| Kaliakoir | 138 | 00:00 | 129 | 04:00 | Thakurgaon | 139 | 19:30 | 125 | 12:00
| Kallyanpur | 134 | 22:00 | 125 | 10:00 | TK | 139 | 19:00 | 125 | 10:00
| Kalurghat | 139 | 19:30 | 126 | 10:00 | Tongi | 136 | 21:00 | 127 | 15:00
| Kamrangirchar | 137 | 08:00 | 130 | 16:00 | Ullon | 132 | 06:00 | 125 | 15:00
| Kaptai | 137 | 18:00 | 130 | 07:00 | Uttara | 135 | 22:00 | 124 | 10:00
| Kazla | 134 | 22:00 | 126 | 16:00 | UttaraNew | 134 | 22:00 | 125 | 15:00
| Keranigonj | 137 | 08:00 | 129 | 03:00 | Zigatola | 136 | 07:00 | 129 | 16:00
| Khagrachori | 137 | 18:30 | 128 | 10:00
| Khulna | 138 | 19:00 | 128 | 13:00
| Khulna(S) | 138 | 01:00 | 130 | 13:00
| Khulshi | 136 | 19:00 | 125 | 10:00
| Kishoreganj | 132 | 22:00 | 125 | 11:00
| Kodda | 140 | 02:00 | 130 | 01:00
| KSRM | 138 | 19:00 | 125 | 10:00
| Kulaura | 134 | 00:00 | 132 | 10:00
| Kurigram | 135 | 19:30 | 126 | 12:00
| Kushtia | 138 | 00:00 | 133 | 14:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2022-11-21
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 1156 | 5426 | 2957 | 8383 |  |  |  | QF-LDC-11
0:30 | 1028 | 5340.5 | 2859.5 | 8200 | Date: | 2022-11-21
1:00 | 900 | 5255 | 2762 | 8017
1:30 | 895 | 5128 | 2685 | 7813
2:00 | 890 | 5001 | 2608 | 7609
2:30 | 906 | 4846 | 2610.5 | 7456.5 | [5 empty] | Gen. at Eve. Peak | 10526 | 10526 MW (18:00 )
3:00 | 922 | 4691 | 2613 | 7304 | [6 empty] | 18:00
3:30 | 921 | 4652.5 | 2539 | 7191.5 | [5 empty] | Gen. at Day Peak | 9135 | 9135 MW (12:00 )
4:00 | 920 | 4614 | 2465 | 7079 | [6 empty] | 12:00
4:30 | 935 | 4569.5 | 2482 | 7051.5 | [5 empty] | Highest Generation | 10526
5:00 | 950 | 4525 | 2499 | 7024 | [6 empty] | 18:00
5:30 | 917 | 4557.5 | 2499 | 7056.5
6:00 | 884 | 4590 | 2499 | 7089
6:30 | 725 | 4717.5 | 2557 | 7274.5
7:00 | 566 | 4845 | 2615 | 7460
7:30 | 694 | 5095.5 | 2738.5 | 7834
8:00 | 822 | 5346 | 2862 | 8208
8:30 | 983 | 5348.5 | 2896.5 | 8245
9:00 | 1144 | 5351 | 2931 | 8282
9:30 | 1150 | 5470.5 | 2917.5 | 8388
10:00 | 1156 | 5590 | 2904 | 8494
10:30 | 1133 | 5694.5 | 2868 | 8562.5
11:00 | 1110 | 5799 | 2832 | 8631
11:30 | 1050 | 6015.5 | 2867.5 | 8883
12:00 | 990 | 6232 | 2903 | 9135
12:30 | 1141 | 6264 | 2969 | 9233
13:00 | 1292 | 6296 | 3035 | 9331
13:30 | 1311 | 6128.5 | 3022.5 | 9151
14:00 | 1330 | 5961 | 3010 | 8971
14:30 | 1315 | 5916.5 | 2900.5 | 8817
15:00 | 1300 | 5872 | 2791 | 8663
15:30 | 1240 | 5853.5 | 2752.5 | 8606
16:00 | 1180 | 5835 | 2714 | 8549
16:30 | 1178 | 5929 | 2881 | 8810
17:00 | 1176 | 6023 | 3048 | 9071
17:30 | 1136 | 6420 | 3378.5 | 9798.5
18:00 | 1096 | 6817 | 3709 | 10526
18:30 | 1163 | 6722 | 3723.5 | 10445.5
19:00 | 1230 | 6627 | 3738 | 10365
19:30 | 1052 | 6607 | 3675 | 10282
20:00 | 1080 | 6459 | 3661 | 10120 |  |  |  | Executive Engineer
20:30 | 1087 | 6375.5 | 3561.5 | 9937 |  |  |  | Network Operation Division
21:00 | 1094 | 6292 | 3462 | 9754
21:30 | 1061 | 6161 | 3322.5 | 9483.5
22:00 | 1028 | 6030 | 3183 | 9213 |  |  |  |  | Page 6 of 7
22:30 | 1054 | 5842 | 3129 | 8971
23:00 | 1080 | 5654 | 3075 | 8729
23:30 | 1118 | 5540 | 3016 | 8556
24:00 | 1156 | 5426 | 2957 | 8383
10526 MW (18:00 )
9135 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2022-11-21 |  | Energy |  | 209070789
[13 empty] | 2022-11-21 |  |  |  |  | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 3274 | 802 | 1176 | 0 | 1960 | 954 | 46 | 0 | 69 | 102 | 0 | 0
0:30 | 3270.5 | 730.5 | 1257.5 | 0 | 1796 | 962 | 46 | 0 | 34.5 | 103 | 0 | 0 | Date: | 2022-11-21
1:00 | 3267 | 659 | 1339 | 0 | 1632 | 970 | 46 | 0 | 0 | 104 | 0 | 0
1:30 | 3265 | 658.5 | 1342 | 0 | 1450.5 | 948 | 46 | 0 | 0 | 103 | 0 | 0 | [7 empty] | Total Energy | 209.0708 | Total Energy Gen 180.187 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 180.187 MKWHr
2:00 | 3263 | 658 | 1345 | 0 | 1269 | 926 | 46 | 0 | 0 | 102 | 0 | 0 | [7 empty] | Energy not Served | 0
2:30 | 3260.5 | 659 | 1309.5 | 0 | 1157.5 | 924 | 46 | 0 | 0 | 100 | 0 | 0 | [7 empty] | Energy Requirement | 209.0708
3:00 | 3258 | 660 | 1274 | 0 | 1046 | 922 | 46 | 0 | 0 | 98 | 0 | 0
3:30 | 3271.5 | 660 | 1281 | 0 | 925.5 | 910.5 | 46 | 0 | 0 | 97 | 0 | 0 | [5 empty] | Shortage
4:00 | 3285 | 660 | 1288 | 0 | 805 | 899 | 46 | 0 | 0 | 96 | 0 | 0
4:30 | 3286.5 | 660 | 1288 | 0 | 770 | 907 | 46 | 0 | 0 | 94 | 0 | 0
5:00 | 3288 | 660 | 1288 | 0 | 735 | 915 | 46 | 0 | 0 | 92 | 0 | 0
5:30 | 3299 | 660 | 1307.5 | 0 | 758 | 897 | 46 | 0 | 0 | 89 | 0 | 0
6:00 | 3310 | 660 | 1327 | 0 | 781 | 879 | 46 | 0 | 0 | 86 | 0 | 0
6:30 | 3296 | 660 | 1335 | 0 | 942 | 884.5 | 46 | 0 | 16 | 84 | 11 | 0 |  |  |  | Coal
7:00 | 3282 | 660 | 1343 | 0 | 1103 | 890 | 46 | 0 | 32 | 82 | 22 | 0
7:30 | 3255 | 660 | 1314 | 77 | 1343 | 924 | 46 | 0 | 82.5 | 85 | 47.5 | 0 |  |  | Oil |  |  |  | ,
8:00 | 3228 | 660 | 1285 | 154 | 1583 | 958 | 46 | 0 | 133 | 88 | 73 | 0
8:30 | 3232.5 | 707 | 1267 | 80 | 1607.5 | 971 | 46 | 0 | 140 | 91 | 103 | 0
9:00 | 3237 | 754 | 1249 | 6 | 1632 | 984 | 46 | 0 | 147 | 94 | 133 | 0
9:30 | 3262.5 | 777.5 | 1236.5 | 77.5 | 1625.5 | 960 | 46 | 0 | 145 | 95 | 162.5 | 0
10:00 | 3288 | 801 | 1224 | 149 | 1619 | 936 | 46 | 0 | 143 | 96 | 192 | 0
10:30 | 3207.5 | 824 | 1216 | 106 | 1816.5 | 905 | 46 | 0 | 134 | 99 | 208.5 | 0
11:00 | 3127 | 847 | 1208 | 63 | 2014 | 874 | 46 | 0 | 125 | 102 | 225 | 0
11:30 | 3112 | 871.5 | 1209.5 | 168 | 2132.5 | 874 | 46 | 3.5 | 134.5 | 109 | 222.5 | 0
12:00 | 3097 | 896 | 1211 | 273 | 2251 | 874 | 46 | 7 | 144 | 116 | 220 | 0
12:30 | 3089 | 896.5 | 1205 | 281.5 | 2298.5 | 924 | 46 | 8 | 155.5 | 117 | 212 | 0
13:00 | 3081 | 897 | 1199 | 290 | 2346 | 974 | 46 | 9 | 167 | 118 | 204 | 0
13:30 | 3081 | 897 | 1199 | 290 | 2346 | 974 | 46 | 9 | 167 | 118 | 204 | 0
14:00 | 3081 | 897 | 1199 | 290 | 2346 | 974 | 46 | 9 | 167 | 118 | 204 | 0
14:30 | 3073 | 897 | 1194.5 | 193 | 2216.5 | 922.5 | 46 | 5.5 | 173.5 | 117 | 158.5 | 0
15:00 | 3065 | 897 | 1190 | 96 | 2087 | 871 | 46 | 2 | 180 | 116 | 113 | 0
15:30 | 3060.5 | 897 | 1203 | 48 | 2076 | 881.5 | 46 | 8.5 | 187 | 115 | 83.5 | 0
16:00 | 3056 | 897 | 1216 | 0 | 2065 | 892 | 46 | 15 | 194 | 114 | 54 | 0
16:30 | 2957 | 897.5 | 1232 | 0 | 2323 | 932 | 46 | 16.5 | 214.5 | 114 | 28 | 0
17:00 | 2957 | 898 | 1248 | 0 | 2581 | 972 | 46 | 18 | 235 | 114 | 2 | 0
17:30 | 3014.5 | 897.5 | 1265.5 | 139.5 | 2925.5 | 1007 | 46 | 9 | 375 | 118 | 1 | 0
18:00 | 3072 | 897 | 1283 | 279 | 3270 | 1042 | 46 | 0 | 515 | 122 | 0 | 0
18:30 | 3009.5 | 897.5 | 1251.5 | 180 | 3368.5 | 1044 | 46 | 0 | 529.5 | 119 | 0 | 0
19:00 | 2947 | 898 | 1220 | 81 | 3467 | 1046 | 46 | 0 | 544 | 116 | 0 | 0
19:30 | 2958 | 897 | 1221 | 21 | 3485 | 1002 | 46 | 0 | 536 | 116 | 0 | 0
20:00 | 2998 | 897 | 1243 | 21 | 3299 | 1005 | 46 | 0 | 497 | 114 | 0 | 0
20:30 | 3026.5 | 897 | 1255 | 10.5 | 3133 | 990.5 | 46 | 0 | 465.5 | 113 | 0 | 0
21:00 | 3055 | 897 | 1267 | 0 | 2967 | 976 | 46 | 0 | 434 | 112 | 0 | 0
21:30 | 3029 | 897 | 1249 | 0 | 2874.5 | 986.5 | 46 | 0 | 290.5 | 111 | 0 | 0
22:00 | 3003 | 897 | 1231 | 0 | 2782 | 997 | 46 | 0 | 147 | 110 | 0 | 0
22:30 | 3035 | 897 | 1238.5 | 0 | 2548 | 990.5 | 46 | 0 | 108 | 108 | 0 | 0
23:00 | 3067 | 897 | 1246 | 0 | 2314 | 984 | 46 | 0 | 69 | 106 | 0 | 0
23:30 | 3170.5 | 849.5 | 1211 | 0 | 2137 | 969 | 46 | 0 | 69 | 104 | 0 | 0 | Max Temp. in Dhaka |  | 30.5° C
24:00 | 3274 | 802 | 1176 | 0 | 1960 | 954 | 46 | 0 | 69 | 102 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 180.187 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 180.187 MKWHr
Note on W13: Author:

## Generation
g | 2022-11-21
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 |  | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 1069920
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [5 empty] | 0 | 2 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 308156
| Teknaf 20MW PP (Solartech) | [6 empty] | 3 | 9 | 14 | 17 | 19 | 19 | 18 | 15 | 11 | 6 | 0 | [9 empty] | 130140
6 | Sikalbaha 225MW CCPP (Gas) | 151 | 150 | 150 | 151 | 151 | 151 | 151 | 151 | 150 | 151 | 151 | 151 | 150 | 148 | 147 | 148 | 150 | 152 |  | 151 | 150 | 151 | 151 | 151 | 151 | 151 | 3412541
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 0 | [15 empty] | 17 | 51 |  | 51 | 51 | 51 | 51 | 51 | 17 | 17 | 317448
12 | Hathazari 100 MW peaking PP | [7 empty] | 0 | 14 | 26 | 24 | 24 | 24 | 24 | 24 | 24 | 16 | 16 |  | 24 | 24 | 24 | 24 | 24 |  |  | 325780
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 36 | 34 | 46 | 51 | 51 | 51 | 51 | 60 | 85 | 95 |  | 105 | 105 | 105 | 105 | 105 | 57 | 34 | 1374981
| Daudkandi 200 MW PP (B.Trac) | [17 empty] | 70 |  | 10 | [6 empty] | 65664
14 | Titas 50 MW Peaking PP | [9 empty] | 0 | 19 | 22 | 28 | 36 | 30 | 37 | 37 | 30 |  | 30 | 30 | 32 | 32 |  |  | 0 | 345632
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 275 | 210 | 57 | 57 | 45 | 45 | 100 | 113 | 113 | 115 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 240 |  | 278 | 278 | 279 | 281 | 263 | 263 | 260 | 3904145
19 | Ashuganj 195MW PP (APSCL-United) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [7 empty] | 0
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4378500
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 47 | 47 | 43 | 43 | 43 | 43 | 43 | 44 | 47 | 47 | 41 | 40 | 43 | 43 | 43 | 43 | 43 | 48 |  | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 1068912
33 | Ashuganj 225 MW CCPP
34 | Ashuganj 450 MW CCPP(South) | 230 | 230 | 230 | 230 | 230 | 230 | 250 | 270 | 270 | 250 | 250 | 250 | 250 | 230 | 230 | 230 | 240 | 240 |  | 230 | 230 | 230 | 230 | 210 | 210 | 210 | 5796000
Ashuganj 450 MW CCPP(North)
| Ashuganj 420 MW CCPP(East) | 407 | 407 | 407 | 407 | 407 | 407 | 417 | 417 | 416 | 416 | 407 | 406 | 407 | 407 | 407 | 407 | 397 | 402 |  | 402 | 402 | 402 | 402 | 392 | 392 | 407 | 9755900
35 | Ashuganj 55 MW PP (Precision) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 5 | 5 | 5 | 5 | 5 | 15 | 15 | 15 |  | 30 | 30 | 40 | 52 | 30 | 30 | 30 | 548640
36 | Chandpur 150 MW CCPP | 69 | 70 | 70 | 70 | 69 | 69 | 30 | 20 | 34 | 83 | 30 | 30 | 30 | 40 | 40 | 35 | 30 | 30 |  | 30 | 30 | 30 | 32 | 32 | 32 | 75 | 1040160
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 318 | 318 | 313 | 313 | 313 | 312 | 312 | 304 | 307 | 312 | 312 | 309 | 298 | 293 | 285 | 279 | 278 | 278 |  | 278 | 278 | 278 | 280 | 285 | 289 | 299 | 7319550
40 | Meghnaghat 450 MW CCPP(MPL) | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 |  | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 5128400
41 | Haripur 360MW CCPP(HPL) | 285 | 283 | 274 | 276 | 276 | 272 | 272 | 271 | 277 | 277 | 277 | 274 | 268 | 264 | 258 | 258 | 252 | 252 |  | 252 | 252 | 256 | 256 | 255 | 266 | 266 | 6426000
42 | RPCL 210MW CCPP | 110 | 110 | 112 | 110 | 111 | 112 | 72 | 72 | 72 | 72 | 39 | 38 | 37 | 35 | 35 | 35 | 35 | 35 |  | 44 | 47 | 52 | 86 | 96 | 99 | 102 | 1664640
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 5 | 21 | 35 | 44 | 50 | 45 | 46 | 34 | 18 | 11 | 1 | [9 empty] | 322670
44 | Fenchugonj CCPP Phase-1
45 | Fenchugonj CCPP Phase-2 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 42 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 985080
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 66 | 66 | 66 | 66 | 66 | 66 | 65 | 66 | 65 | 64 | 62 | 56 | 57 | 56 | 54 | 61 | 40 | 66 |  | 40 | 64 | 66 | 69 | 70 | 71 | 70 | 1496640
48 | Shahjibazar 86MW PP (Shahjibazar) | 78 | 78 | 0 | [13 empty] | 81 | 81 |  | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 761280
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 |  | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 3807310
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL) | [5 empty] | 0 | 0
53 | Sylhet 10MW PP (Desh) | [25 empty] | 0 | 0
54 | Hobiganj 11MW PP Cofidence-E | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 72288
55 | Fenchugonj 51 MW PP (Barakatullah) | [25 empty] | 0 | 0
56 | Shahjahanulla 25 MW PP
57 | Bibiana-II 341 MW CCPP (Summit) | 280 | 280 | 285 | 280 | 270 | 300 | 320 | 300 | 280 | 275 | 275 | 280 | 280 | 275 | 290 | 310 | 290 | 280 |  | 255 | 255 | 260 | 270 | 255 | 260 | 180 | 6905500
| Bibiyana South 400 MW | 400 | 400 | 400 | 400 | 390 | 370 | 400 | 400 | 400 | 400 | 400 | 400 | 390 | 400 | 395 | 392 | 350 | 400 |  | 340 | 330 | 340 | 340 | 300 | 340 | 380 | 9185600
58 | Nababganj 55 MW PP (Southern power ) | 35 | 35 | 35 | 17 | 17 | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 55 | 55 | 55 | 35 | 35 | 35 | 35 | 860644
59 | Tangail Palli Power Gen 22 MW | 6 | 6 | 6 | 6 | 6 | 3 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 7 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 206880
60 | Barabkunda 22 MW PP (Regent)
61 | Narshingdi 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 0 | 19 | 19 | 19 | 19 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 424872
62 | Tangail 22 MW PP (Doreen) | 12 | 12 | 12 | 12 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 10 | 10 | 11 | 266940
63 | Impoprt (Tripura) | 104 | 102 | 98 | 96 | 92 | 86 | 82 | 88 | 94 | 96 | 102 | 116 | 118 | 122 | 116 | 114 | 114 | 122 |  | 116 | 116 | 114 | 112 | 110 | 106 | 102 | 2552640
64 | Malancha, Ctg. EPZ (United) | 4 | 7 | 11 | 17 | 21 | 28 | 28 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 2 | 2 | 2 | 2 | 3 | 6 | 7 | 129120
65 | Feni 22MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 511488
66 | Feni 11 MW PP (Doreen) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 0 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 169020
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 28 | 18 | 14 | 14 | 14 | 14 | 14 | 14 | 15 | 15 | 14 | 15 |  | 23 | 25 | 25 | 32 | 33 | 33 | 33 | 580500
68 | Cumilla 25 MW PP (Summit) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 345300
69 | Summit Ashulia | 25 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 21 | 21 | 22 | 22 | 22 | 22 | 25 | 600000
70 | Summit Madhabdi | 27 | 27 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 26 | 23 | 21 | 26 | 27 | 8 | 27 | 27 | 20 |  | 26 | 27 | 27 | 27 | 27 | 27 | 27 | 600120
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 25 | 33 | 33 | 33 | 757800
72 | Rupganj 33 MW PP(Summit) | 32 | 32 | 33 | 32 | 32 | 32 | 32 | 31 | 30 | 30 | 30 | 16 | 16 | 26 | 28 | 17 | 24 | 17 |  | 22 | 28 | 28 | 29 | 29 | 32 | 32 | 672800
73 | Ghorashal 108MW PP (Regent) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 65 | 65 | 65 | 65 | 65 | 68 | 68 | 68 | 71 | 71 |  | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 1629863
| Feni Lanka Power | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 425220
| Chowmuhani 113 MW | 65 | 36 | 36 | 16 | 17 | 17 | 23 | 54 | 105 | 107 | 107 | 108 | 100 | 102 | 106 | 106 | 108 | 107 |  | 108 | 108 | 101 | 75 | 75 | 75 | 75 | 1883280
| Manikgonj 162MW PP(MPGL) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 24 | 145 | 162 | 82 | 72 | 72 | 162 | 162 |  | 162 | 162 | 162 | 162 | 162 | 17 | 17 | 1766880
77 | Siddhirganj 100 PP(Dutch Bangla) | 30 | 30 | 30 | 16 | 8 | 8 | 16 | 32 | 43 | 66 | 76 | 76 | 76 | 76 | 76 | 80 | 84 | 84 |  | 84 | 84 | 84 | 77 | 77 | 77 | 42 | 1320960
78 | Gazipur 52 MW PP | 0 | [5 empty] | 6 | 50 | 50 | 42 | 42 | 42 | 42 | 47 | 48 | 48 | 48 | 48 |  | 49 | 49 | 49 | 49 | 24 | 8 | 8 | 718560
79 | Kodda 150MW PP | 0 | [5 empty] | 32 | 133 | 133 | 117 | 82 | 98 | 115 | 126 | 126 | 133 | 133 | 133 |  | 133 | 133 | 133 | 133 | 32 | 16 | 16 | 1851840
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 9 | 16 | 16 | 8 | 8 | 8 | 8 | 213509
| Gazipur 100 MW PP | 50 | 34 | 34 | 34 | 34 | 34 | 40 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 90 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2115372
| Kaptai 7 MW Solar PP | [6 empty] | 1 | 2 | 3 | 4 | 4 | 4 | 0 | 3 | 2 | 1 | [10 empty] | 21211
| Jodiac Power | 24 | 17 | 17 | 17 | 17 | 17 | 30 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 |  | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 794428
| Karnaphuli Power Ltd. | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 73 | 73 | 73 | 73 | 80 | 91 | 91 | 91 | 91 |  | 91 | 91 | 91 | 91 | 91 | 73 | 73 | 1774756
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL) | 12 | 0 | [5 empty] | 3 | 25 | 35 | 67 | 84 | 91 | 91 | 89 | 87 | 91 | 90 |  | 92 | 91 | 91 | 87 | 89 | 92 | 32 | 1237440
| Meghnaghat 104 MW PP (OPCL) | 17 | 17 | 18 | 17 | 18 | 17 | 17 | 20 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 437760
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 44 |  | 44 | 44 | 44 | 44 | 44 | 44 | 22 | 661920
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | [6 empty] | 5
94 | Gagnagar 102 MW PP (Digital Power) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 8 | 565488
95 | Patenga 50MW PP (Baraka) | 38 | 24 | 19 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 20 | 29 | 37 | 37 |  | 41 | 43 | 43 | 39 | 37 | 37 | 37 | 647520
96 | Chattogram 108 MW PP (ECPV) | [25 empty] | 0 | 0
97 | katpotti 52 MW
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 55 | 55 | 55 | 30 | 30 | 30 | 42 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 1108926
100 | Manikganj 55 MW PP (Northern) | 17 | 17 | 17 | 0 |  | 4 | 27 | 35 | 35 | 35 | 55 | 55 | 55 | 35 | 35 | 35 | 35 | 55 |  | 55 | 55 | 55 | 35 | 35 | 35 | 35 | 807061
101 | Kushiara 163 MW CCPP (KP)
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 0 | [10 empty] | 14100
103 | Kamalaghat 54 MW PP(Banco Energy) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 |  | 54 | 54 | 54 | 17 | 17 | 17 | 17 | 528480
104 | Keranigonj 300 MW PP (APR) | [7 empty] | 54 | 0 | 99 | 13 | 103 | 100 | 56 | 46 |  |  | 109 |  | 21 | 21 | 21 |  |  |  | 0 | 530075
105 | Bramhangoan 100 MW PP (Aggreko) | [7 empty] | 50 | 0 | 25 | 25 | 98 | 98 | 25 | 25 |  |  | 50 |  | 25 | [5 empty] | 0 | 448975
106 | Mymensingh 200 MW PP (United) | 48 | 48 | 48 | 48 | 0 |  |  | 46 | 46 | 46 | 76 | 76 | 76 | 66 | 68 | 68 | 57 | 86 |  | 87 | 87 | 87 | 87 | 87 | 87 | 48 | 1300800
112 | Aurahati 100MW PP (Aggreko) | [7 empty] | 50 | 6 | 25 | 25 | 72 | 92 | 25 | 25 |  |  | 50 |  | 25 | [5 empty] | 0 | 388564
114 | Kodda 149 MW PP Unit-1 (Summit) | 144 | 101 | 56 | 52 | 48 | 53 | 60 | 110 | 126 | 128 | 135 | 142 | 149 | 149 | 149 | 149 | 149 | 149 |  | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 2983968
115 | Juldah 100 MW PP Unit-3 (Acorn) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 40 |  | 50 | 50 | 50 | 50 | 50 | 50 | 25 | 743040
116 | Chandpur 200MW (Desh energy) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 65 |  | 100 | 100 | 100 | 100 | 100 | 85 | 85 | 966240
117 | Ashuganj 150MW PP (Midland) | 65 | 30 | 10 | 10 | 10 | 13 | 25 | 38 | 45 | 55 | 60 | 65 | 75 | 87 | 97 | 100 | 107 | 117 |  | 118 | 123 | 122 | 127 | 127 | 80 | 80 | 1741309
118 | Bibiyana-III 400 MW CCPP | 352 | 352 | 352 | 375 | 375 | 418 | 419 | 419 | 419 | 416 | 420 | 420 | 416 | 412 | 406 | 400 | 375 | 408 |  | 339 | 339 | 339 | 340 | 339 | 329 | 420 | 9176000
| Jamalpur 115 MW PP (United) | 49 | 49 | 49 | 49 | 49 | 56 | 99 | 49 | 49 | 48 | 58 | 68 | 68 | 67 | 68 | 68 | 49 | 96 |  | 97 | 98 | 98 | 99 | 99 | 99 | 49 | 1640400
| Anwara 300 MW PP (United) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 219 | 255 | 249 | 277 | 274 | 285 | 285 | 283 |  | 284 | 285 | 106 | 16 | 16 | 16 | 16 | 2734909
| Juldah unit-2 (Acorn) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 43 |  | 50 | 50 | 50 | 50 | 50 | 50 | 30 | 747840
| Anlima Energy Ltd. | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 |  | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 2579345
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 32 |  | 35 | 35 | 35 | 35 | 35 | 35 | 20 | 551520
| Spectra Solar Plant Ltd. | [6 empty] | 3 | 12 | 25 | 21 | 32 | 30 | 31 | 26 | 18 | 8 | [10 empty] | 202250
| Chandpur 115(Doreen) | 47 | 18 | 17 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 80 | 115 | 115 | 32 | 18 | 17 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 43 | 27 | 1289280
| Kanchan Purbachal Power Generation Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 14 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 426600
| Mirsharai 150 MW (Oil) | [10 empty] | 0 | 7 | 9 |  | 2 | 15 | 18 | [8 empty] | 0 | 56872
Mirsharai 150 MW (Gas)
120 | Eastern Zone Total | 5255 | 5001 | 4691 | 4614 | 4525 | 4590 | 4845 | 5346 | 5351 | 5590 | 5799 | 6232 | 6296 | 5961 | 5872 | 5835 | 6023 | 6817 |  | 6627 | 6607 | 6459 | 6292 | 6030 | 5654 | 5426 | 135628162
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | 0 | [15 empty] | 49 | 107 |  | 114 | 114 | 114 | 114 | 49 | 49 | 49 | 611520
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [16 empty] | 25 | 31 |  | 34 | 33 | 33 |  |  |  |  | 117600
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 70 | 35 | 35 | 0 |  |  | 4 | 50 | 53 | 17 | 17 | 17 | 17 | 17 | 17 |  | 35 | 80 |  | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 1086240
130 | Mongla Orion 100 MW Solar PP | [6 empty] | 8 | 14 | 31 | 69 | 76 | 77 | 72 | 59 | 41 | 18 | 1 | [9 empty] | 465120
131 | Rampal 1320 MW (BIFPCL)
132 | United Payra Power Ltd. | [25 empty] | 0 | 0
133 | Bhola Nutan Biddut BD LTD (GAS) | 109 | 108 | 109 | 109 | 109 | 109 | 107 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 |  | 109 | 109 | 109 | 109 | 109 | 106 | 109 | 2603809
Bhola Nutan Biddut BD LTD (OIL)
Barisal 110 MW PP (Summit )
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW | 140 | 136 | 143 | 140 | 156 | 140 | 141 | 158 | 174 | 176 | 174 | 174 | 174 | 175 | 171 | 202 | 262 | 242 |  | 246 | 242 | 245 | 256 | 307 | 294 | 264 | 4497200
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 152 | 152 | 152 | 152 | 152 | 151 | 152 | 107 | 109 | 153 | 110 | 135 | 110 | 130 | 130 | 130 | 117 | 130 |  | 130 | 115 | 130 | 130 | 120 | 130 | 130 | 3205000
140 | Bhola 33 MW PP (Venture) | 20 | 19 | 18 | 16 | 17 | 17 | 16 | 15 | 14 | 14 | 15 | 16 | 14 | 16 | 15 | 14 | 16 | 27 |  | 25 | 25 | 26 | 26 | 26 | 25 | 25 | 450100
141 | Noapara 100 MW PP (Bangla Trac) | [25 empty] | 0 | 0
142 | Noapara 40 MW PP (Khanjahan Ali) | [17 empty] | 16 |  | 24 | 24 | 24 | 24 | 16 | 16 | 16 | 123750
143 | Gopalganj 100 MW Peaking PP | [16 empty] | 7 | 75 |  | 82 | 80 | 78 | 78 | 40 | 36 | 36 | 395776
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 659 | 658 | 660 | 660 | 660 | 660 | 660 | 660 | 754 | 801 | 847 | 896 | 897 | 897 | 897 | 897 | 898 | 897 |  | 898 | 897 | 897 | 897 | 897 | 897 | 802 | 19434181
147 | Bheramara 410 MW CCPP | 175 | 175 | 175 | 180 | 190 | 190 | 185 | 180 | 175 | 165 | 165 | 155 | 155 | 150 | 150 | 145 | 145 | 145 |  | 150 | 150 | 155 | 165 | 165 | 175 | 180 | 4146912
148 | Payra 1320 MW | 670 | 630 | 620 | 600 | 600 | 580 | 590 | 640 | 650 | 600 | 540 | 540 | 640 | 640 | 540 | 530 | 550 | 640 |  | 640 | 600 | 600 | 560 | 530 | 530 | 530 | 16007200
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 160 | 160 | 159 | 159 | 159 | 159 | 159 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 |  | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 3906100
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [17 empty] | 31 |  | 31 | 25 | 25 |  |  |  |  | 84656
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 2 | 3 | 4 | 5 | 5 | 0 | 0 | 3 | 1 | 0 | [9 empty] | 23760
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 166 | 165 | 165 | 166 | 168 | 168 | 168 | 168 | 168 | 165 | 140 | 144 | 151 | 161 | 161 | 161 | 158 | 152 |  | 161 | 162 | 163 | 168 | 173 | 176 | 176 | 4135645
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 227 | 234 | 240 | 253 | 258 | 264 | 259 | 255 | 240 | 220 | 220 | 220 | 216 | 217 | 204 | 200 | 172 | 205 |  | 150 | 151 | 151 | 153 | 154 | 154 | 160 | 5131927
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [17 empty] | 4 |  | 5 | 5 | 5
162 | Bogra 22 MW PP (GBB) | 21 | 21 | 22 | 22 | 22 | 22 | 21 | 18 | 17 | 17 | 15 | 15 | 15 | 14 | 14 | 15 | 15 | 16 |  | 20 | 20 | 22 | 22 | 22 | 22 | 22 | 434640
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 242730
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | [6 empty] | 8 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 8 | 8 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 585417
167 | Katakhali 50 MW Peaking PP | [17 empty] | 32 |  | 32 | 32 | 32 | 32 |  |  | 0 | 112858
168 | Santahar 50 MW Peaking PP | [17 empty] | 32 |  | 33 | 34 | 34 | 34 |  |  |  | 118451
169 | Natore 52 MW PP (Rajlanka) | [17 empty] | 43 |  | 43 | 43 | 43 | 8 |  |  | 0 | 139046
170 | Chapainawabganj 100 MW Peaking PP | [5 empty] | 0 | 0 | [10 empty] | 80 |  | 89 | 89 | 50 | 50 |  |  |  | 264932
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 113 | 35 | 35 | 0 |  | 1 | 36 | 81 | 70 | 35 | 35 | 35 | 67 | 70 | 35 | 35 | 48 | 85 |  | 94 | 94 | 94 | 70 | 70 | 35 | 35 | 1412736
172 | Confidence Power Bogura Unit-1 113 MW | 38 | 38 | 38 | 0 |  | 30 | 35 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 35 | 113 | 113 |  | 113 | 113 | 113 | 70 | 70 | 70 | 70 | 1264800
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | 34 | 34 | 34 | 0 |  |  | 38 | 82 | 49 | 34 | 34 | 34 | 70 | 34 | 34 | 34 | 60 | 113 |  | 113 | 113 | 113 | 91 | 70 | 70 | 66 | 1273104
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 3 | 4 | 6 | 6 | 6 | 5 | 3 | 2 | 0 | [9 empty] | 36754
178 | Energypac Power Venture Thakurgaon Ltd. | 0 | [5 empty] | 18 | 53 | 37 | 36 | 35 | 35 | 35 | 35 | 35 |  | 72 | 108 |  | 112 | 115 | 115 | 115 | 75 | 0 | 0 | 935808
178 | Intraco Solar 30 MW | [6 empty] | 2 | 11 | 17 | 27 | 31 | 32 | 29 | 23 | 16 | 7 | 0 | [9 empty] | 194855