## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID COMPANY OF BANGLADESH LTD.
SYSTEM OPERATION DATA
Month:September 2022
Sl. | Items | Current Month |  | Previous Month |  | This Month Last Year |  | Max. Till-to-date
|  | 2022-09-01 |  | 2022-08-01 |  | 2021-09-01
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 13761 | 2022-09-07 | 13985 | 2022-08-25 | 13509 | 2021-09-11 | 14782 | 2022-04-16
|  |  | 22:00 |  | 21:00 |  | 20:00 |  | 21:00
2 | Minimum Generation (MW) | 8864 | 2022-09-15 | 9620 | 2022-08-12 | 8491 | 2021-09-17 | - | -
|  |  | 6:00 |  | 6:00 |  | 1:00 |  | -
3 | Maximum Evening Peak Generation (MW) | 13712 | 2022-09-01 | 13985 | 2022-08-25 | 13509 | 2021-09-11 | 14782 | 2022-04-16
|  |  | 22:00 |  | 21:00 |  | 20:00 |  | 21:00
4 | Maximum Day Peak Generation (MW) | 11999 | 2022-09-08 | 11848 | 2022-08-25 | 11723 | 2021-09-05 | 12895 | 2022-04-26
|  |  | 12:00 |  | 12:00 |  | 12:00 |  | 12:00
5 | Maximum Evening Peak Demand (MW) Estimated | 14695 | 2022-09-01 | 14745 | 2022-08-31 | 13509 | 2021-09-11 | 14782 | 2022-04-16
|  |  | 20:00 |  | 21:00 |  | 20:00 |  | 12:00
6 | Average Generation (MW) at Evening Peak | 13055.1 |  | 13078.4194 |  | 12742.1667 |  | 13536.33 | 2022-04-27
7 | Average Generation (MW) at Day Peak | 11203.2667 |  | 10988.2258 |  | 10804.6667 |  | 11233.4 | 2022-04-27
8 | Maximum Power Import from India, BIPTC (MW) | 919 | 2022-09-30 | 922 | 2022-08-08 | 907 | 2021-07-01 | 956 | 27/3/2019
|  |  | 11:00 |  | 3:00 |  | 0:30 |  | 19:00
9 | Maximum Power Import from Tripura, India (MW) | 184 | 2022-09-10 | 182 | 2022-08-07 | 172 | 2021-07-10 | 194 | 12/06/19
|  |  | 18:30 |  | 15:00 |  | 23:00 |  | 19:00
10 | Maximum Load Shed (MW) at Evening Peak | 1471 | 2022-09-28 | 1537 | 2022-08-06 | 0 | - | 1459 | 04/05/2010
|  |  | 21:00 |  | 21:00 |  | - |  | 20:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | 12904 | 2022-09-28 | 12132 | 2022-08-06 | - | - | 13792 | 2021-04-27
|  | - | 21:00 | - | 21:00 | - | - |  | 20:00
12 | Minimum Load Shed (MW) at Evening Peak | 0 | 2022-09-13 | 54 | 2022-08-15 | 0 | -
|  |  | 19:00 |  | 21:00
13 | Generation During Min. Load Shed (MW) at Evening Peak | 11790 | 2022-09-13 | 13051 | 2022-08-15 | - | -
|  |  | 19:00 |  | 21:00
14 | Maximum Load Shed (MW) at Day Peak | 1235 | 2022-09-06 | 1638 | 2022-08-12 | - | -
|  |  | 12:00 |  | 10:00
15 | Generation During Max. Load Shed (MW) at Day Peak | 10112 | 2022-09-06 | 9923 | 2022-08-12 | - | -
|  |  | 12:00 |  | 10:00
16 | Minimum Load Shed (MW) at Day Peak | 0 | 2022-09-02 | 0 | 2022-08-15 | - | -
|  |  | 12:00 |  | 10:00
17 | Generation During Min. Load Shed (MW) at Day Peak | 11272 | 2022-09-02 | 10622 | 2022-08-15 | - | -
|  |  | 12:00 |  | 10:00
18 | Nos. of Days Load Shed at Evening Peak | 29 |  | 31 |  | 0
19 | Nos. of Days Load Shed at Day Peak | 20 |  | 30 |  | -
20 | Gross Generation of BPDB (MKWH) | 1767.5579 |  | 1900.8429 |  | 1586.2039 |  | 3805.72 | 2019-09-19
21 | Station Use of BPDB (MKWH) | 88.5941 |  | 135.2896 |  | 134.2992
22 | Net Generation of BPDB (MKWH) | 1678.9638 |  | 1765.5533 |  | 1451.9047
23 | Net Generation of IPP (MKWH) | 5416.8526 |  | 5487.1901 |  | 5324.0599
24 | Net Generation of REB (MKWH) | 111.5457 |  | 127.2082 |  | 141.3247
24 | Net Generation of Rental Power Plant (MKWH) | 401.8248 |  | 411.3038 |  | 490.1064
25 | Total Net Generation (MKHWh) (BPDB, IPP, RPP & REB) | 7609.1868 |  | 7791.2554 |  | 7407.3956 |  | 7842.9924 | April'22
26 | Energy Generation by Gas (MKWH) | 4050.2118 |  | 4273.9758 |  | 4494.9287 |  | 4756.96 | Sep-19
27 | Energy Generation by Diesel (MKWH) | 582.493 |  | 623.3092 |  | 614.1861 |  | 771.52 | July-18
28 | Energy Generation by Furnace Oil (MKWH) | 1974.4688 |  | 1993.2091 |  | 1887.4763 |  | 2365.7466 | April'22
29 | Energy Generation by Hydro (MKWH) | 104.6574 |  | 95.7122 |  | 104.8774 |  | 104.66 | Sep-22
30 | Energy Generation by Solar (MKWH) | 34.9866 |  | 37.0888 |  | 23.2163 |  | 40.58 | March-22
31 | Energy Generation by Coal (MKWH) | 950.9634 |  | 903.25 |  | 417.01 |  | 950.96 | Sep'22
32 | Enegry Import from India (BIPTC & AC) (MKWH) | 744.831 |  | 776.6715 |  | 600.369 |  | 776.67 | August-22
33 | Monthly Load Factor (%) | 91.3054 |  | 92.6177 |  | 81.01 |  | 92.62 | August-22

## QF-LDC-22
Page: 1/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month:September 2022
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quantity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 13761 | 2022-09-07 | 22:00
Generation Period
| Dhaka | MW | 4726.35
| Chattogram | MW | 1382.5
| Cumilla | MW | 1288
| Mymensingh | MW | 949
| Sylhet | MW | 509
a) | Total supply in East zone | MW | 8854.85
| Khulna | MW | 1743.4
| Barisal | MW | 429.78
| Rajshahi | MW | 1379.9
| Rangpur | MW | 825
b) | Total supply in West zone | MW | 4378.08
c) | Total supply in both zone ( a+b) | MW | 13232.93
Ref: | 27.21.0000.603.16.087.20.563 | Date: 23/10/2022
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
Page: 2/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month:September 2022
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Daily Maximum power Export through EWI/ NO-1
| a) Ghorashal end | AMPS | 1000 | 2022-09-06 | 10:00
| b) Ishurdi end | MW | 548 | 2022-09-18 | 16:00
18 | Daily Maximum power Import through EWI/ NO-1
| a) Ghorashal end | AMPS | 1500 | 2022-09-01 | 11:00
| b) Ishurdi end | MW | 0 | 2022-09-06 | 9:00
19 | Daily Maximum Energy Export through EWI/NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
20 | Daily Maximum Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
21 | Total Energy Export through EWI/ NO-1
| a) Ghorashal end | MKWH | -
| b) Ishurdi end | MKWH | 259.05
22 | Total Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | -
| b) Ishurdi end | MKWH | -
23 | Transmission loss of EWI/ NO-1 | % | 3
24 | Daily Maximum power Export through EWI/ NO-2
| a) Ashuganj end | MW | 0 | - | -
| b)Serajganj end | MW | 640 | 2022-09-28 16:00 | 44832.6667
25 | Daily Maximum power Import through EWI/ NO-2
| a) Ashuganj end | MW | 4580 | 2022-09-04 | 24:00
| b)Sirajganj end | MW | - | - | 8:00
26 | Daily Maximum Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 0.009 | 2022-09-19 | 22:00
| b)Sirajganj end | MKWH | - | -
27 | Daily Maximum Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | - | -
| b)Sirajganj end | MKWH
28 | Total Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 0
| b)Sirajganj end | MKWH | 32.5
29 | Total Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | 294.79
| b)Sirajganj end | MKWH | 0
30 | Transmission loss of EWI /NO-2 | % | 3.999%
* Total energy export from Ghorasal end and import from Ishurdi end and the transmission loss of EWI/NO-1 is taken
from the calculation of GMD, PGCB, Ishwardi.
* *Total energy export from Ashuganj end and import from Sirajganj end and the transmission loss of EWI/NO-2 is taken
from the calculation of Sirajganj switching sub station.
* **The energy meter of Ghorasal end is out of order.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.
Ist East-West Interconnector Loss:
| Ghorasal End (KWH): | 109882206.4 | 1000000 | 109.8822 | 836363.65
| Ishurdi End (KWH): | 106928443.1 | 1000000 | 106.9284 | 811272.74
| Difference (-) : | 2953763.3 |  |  | 25090.91
| Loss : | 2.688% |  |  | 3%
2nd East-West Interconnector Loss:
| Ashuganj End (KWH) | 245578000 | 1000000 | 245.578
| Sirajganj End (KWH) | 242062000 | 1000000 | 242.062
| Difference (-) : | 3516000
| Loss : | 1.432%

## QF-LDC-23
QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: September2022
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Kabirpur | 132/33 kV transformer T-2 with 33 kV Bus | 2022-09-03 14:04 | 2022-09-03 15:35 | 1:31 | T | Due to red-hot maint | 120 | 182 | Power interruption
Dhamrai | 132/33 kV transformer T-1 | 2022-09-03 07:33 | 2022-09-03 07:33 | 0:00 | T | Due to red-hot maint | 0 | 0 | Power interruption
Jamalpur | 132/33 kV transformer T-2 | 2022-09-04 15:35 | 2022-09-04 17:32 | 1:57 | T | Due to red-hot maint by PBS feeder | 30 | 58.5 | Power interruption
Savar | 132/33 kV transformers T-1 & T-2 | 2022-09-05 15:18 | 2022-09-05 15:26 | 0:08 | T | Due to L-43 feeder fault | 90 | 12 | Power interruption
Tangail | 132/33 kV transformer T-2 | 2022-09-05 18:35 | 2022-09-05 21:43 | 3:08 | T | Tripped showing E/F . relay | 58 | 181.7333 | Power interruption
| 132/33 kV transformer T-2 | 2022-09-06 16:25 | 2022-09-06 17:24 | 0:59 | T | Tripped showing by TCS | 0 | 0 | No interruption
Savar | 132/33 kV transformer T-3 | 2022-09-08 11:20 | 2022-09-08 13:10 | 1:50 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Netrakona | 132/33 kV transformer T-3 | 2022-09-10 20:57 | 2022-09-10 21:39 | 0:42 | T | Due to red-hot maint by PBS feeder | 25 | 17.5 | Power interruption
Savar | 33 kV Bus-A | 2022-09-11 15:48 | 2022-09-11 18:30 | 2:42 | T | Due to red-hot maint | 0 | 0 | No interruption
| 132/33 kV transformer T-3 | 2022-09-16 23:12 | 2022-09-17 09:44 | 10:32 | E/O | Due to Oil surge trip | 0 | 0 | No interruption
Kodda | 132/33 kV transformer T-2 with 33 kV Bus | 2022-09-18 06:50 | 2022-09-18 08:44 | 1:54 | E/O | Due to red-hot maint.at 33 kV Bus | 20 | 38 | Power interruption
Kishoreganj | 132/33 kV transformer T-2 | 2022-09-20 15:39 | 2022-09-20 16:40 | 1:01 | E/O | Due to red-hot maint.by PDB | 60 | 61 | Power interruption
Kabirpur | 132/33 kV transformer T-1 | 2022-09-20 14:38 | 2022-09-20 14:57 | 0:19 | E/O | Due to red-hot maint.by PBS | 63 | 19.95 | Power interruption
| 132/33 kV transformer T-3 | 2022-09-20 14:36 | 2022-09-20 16:05 | 1:29 | E/O |  | 87 | 129.05 | Power interruption
Kodda | 132/33 kV transformer T-3 | 2022-09-21 05:58 | 2022-09-21 07:36 | 1:38 | T | Due to red-hot maint | 0 | 0 | No interruption
Kishoreganj | 132/33 kV transformer T-2 with 33 kV Bus | 2022-09-29 08:09 | 2022-09-29 09:59 | 1:50 | T | Due to red-hot maint | 0 | 0 | No interruption
|  |  | Total : | 31:40 |  | Unserved Energy: |  | 699.7333
Dhaka (South) Grid Circle :
Sonargaon | 132/33 kV transformer T-1 with 33 kV Bus | 2022-09-02 07:53 | 2022-09-02 09:30 | 1:37 | E/O | Due to red-hot maint. | 20 | 32.3333 | Power interruption
| 132/33 kV transformer T2 | 2022-09-03 11:58 | 2022-09-03 13:45 | 1:47 | E/O | Due to red-hot maint.at 33 kV side | 25 | 44.5833 | Power interruption
Ghorashal | 132/33 kV transformer T1 | 2022-09-02 11:28 | 2022-09-02 18:14 | 6:46 | E/O | Due to Oil leakage | 30 | 203 | Power interruption
Bhulta | 132/33 kV transformer GT1 | 2022-09-05 21:15 | 2022-09-05 22:12 | 0:57 | E/O | Due to red-hot maint. | 50 | 47.5 | Power interruption
Haripur SBU | 132/33 kV transformer T1 | 2022-09-12 15:04 | 2022-09-12 15:45 | 0:41 | T | Due to 33 kV feeder fault | 90 | 61.5 | Power interruption
Sonargaon | 132/33 kV transformer T-2 | 2022-09-13 10:09 | 2022-09-13 11:43 | 1:34 | E/O | Due to red-hot maint.at 33 kV side | 0 | 0 | No interruption
Bhulta | 132/33 kV transformer T1 | 2022-09-14 12:55 | 2022-09-14 13:50 | 0:55 | E/O | Due to red-hot maint. | 40 | 36.6667 | Power interruption
Sreenagar | 132/33 kV transformer T1 | 2022-09-20 15:51 | 2022-09-20 17:03 | 1:12 | E/O | Due to red-hot maint.by PBS | 15 | 18 | Power interruption
Ghorashal | 230/132 kV transformer T1 | 2022-09-26 05:40 | 2022-09-26 05:40 | 0:00 | T | Tripped showing O/C. relay | 0 | 0 | No interruption
Madanganj | 132/33 kV transformer T2 | 2022-09-28 09:58 | 2022-09-28 14:47 | 4:49 | T | Tripped showing PRD. relay | 0 | 0 | No interruption
|  |  | Total : | 20:18 |  | Unserved Energy: |  | 443.5833
Chattogram Grid Circle :
T.k.chemical | 132/33 kV transformer T1 | 2022-09-03 00:58 | 2022-09-03 02:00 | 1:02 | T | Tripped showing O/C. relay | 65 | 67.1667 | Power interruption
GPH Ispat | 230/132 kV transformer T1 | 2022-09-03 02:08 | 2022-09-03 03:09 | 1:01 | T | Tripped showing PRD relay | 0 | 0 | No interruption
Kalurghat | 132/33 kV transformers T-1 & T2 | 2022-09-07 07:40 | 2022-09-07 08:40 | 1:00 | T | Due to 33 kV feeder fault | 120 | 120 | Power interruption
Halishahar | 132/33 kV transformer T3 | 2022-09-09 15:20 | 2022-09-09 17:00 | 1:40 | T | Due to 33 kV feeder fault | 20 | 33.3333 | Power interruption
Madunaghat | 132/33 kV transformer T1 | 2022-09-11 03:11 | 2022-09-11 03:11 | 0:00 | T | Due to bursting of CT | 0 | 0 | Power interruption
Halishahar | 132/33 kV transformers T-1,T2 & T3 | 2022-09-15 16:10 | 2022-09-15 16:40 | 0:30 | T | Due to 33 kV feeder fault | 77 | 38.5 | Power interruption
Hathazari | 132/33 kV transformer T1 | 2022-09-16 06:12 | 2022-09-16 06:35 | 0:23 | E/O | Due to red-hot maint.33 kV side | 0 | 0 | No interruption
| 132/33 kV transformer T2 | 2022-09-16 06:40 | 2022-09-16 09:45 | 3:05 | E/O |  | 0 | 0 | No interruption
Sikalbaha | 230/132 kV transformer T1 & T2 | 2022-09-18 20:20 | 2022-09-18 22:35 | 2:15 | T | Tripped showing O/C. relay | 0 | 0 | No interruption
Baroulia | 132/33 kV transformer T1 | 2022-09-20 08:05 | 2022-09-20 08:49 | 0:44 | T | Tripped showing O/C. relay at 33 kV side | 0 | 0 | No interruption
| 132/33 kV transformer T1 | 2022-09-20 08:05 | 2022-09-20 09:06 | 1:01 | T |  | 0 | 0 | No interruption
Khulshi | 132/33 kV transformers T-1 & T2 | 2022-09-22 16:49 | 2022-09-22 17:03 | 0:14 | T | Due to 33 kV feeder fault | 135 | 31.5 | Power interruption
Chandraghona | 132/33 kV transformers T-1 & T2 | 2022-09-24 08:51 | 2022-09-24 09:37 | 0:46 | T | Due to 33 kV feeder fault | 0 | 0 | No interruption
Cox'sbazar | 132/33 kV transformer T2 | 2022-09-27 06:15 | 2022-09-27 06:54 | 0:39 | E/O | Due to red-hot maint. | 15 | 9.75 | Power interruption
|  |  | Total : | 14:20 |  | Unserved Energy: |  | 300.25
Cumilla Grid Circle :
Ramganj | 132/33 kV transformer T2 with 33 kV Bus-2 | 2022-09-03 06:59 | 2022-09-03 07:46 | 0:47 | E/O | Due to red-hot maint. | 30 | 23.5 | Power interruption
Sreemongal | 132/33 kV transformers T-1 & T3 | 2022-09-04 04:14 | 2022-09-04 04:30 | 0:16 | T | Tripped showing O/C. relay | 0 | 0 | No interruption
Chowmuhani | 132/33 kV transformers T3 | 2022-09-04 14:40 | 2022-09-04 15:40 | 1:00 | E/O | Due to red-hot maint.33 kV side | 0 | 0 | No interruption
Shahjibazar | 132/33 kV transformer T6 | 2022-09-04 17:56 | 2022-09-04 18:09 | 0:13 | T | Due to 33 kV feeder fault | 19 | 4.1167 | Power interruption
Ramganj | 132/33 kV transformer T2 | 2022-09-05 07:25 | 2022-09-05 08:09 | 0:44 | T | Due to 33 kV feeder fault | 30 | 22 | Power interruption
Shahjibazar | 132/33 kV transformer T4 | 2022-09-07 08:44 | 2022-09-07 10:03 | 1:19 | T | Tripped showing PRD relay | 45 | 59.25 | Power interruption
Cumilla(N) | 132/33 kV transformer T3 | 2022-09-08 10:14 | 2022-09-08 10:30 | 0:16 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Chandpur | 132/33 kV transformer T2 | 2022-09-09 16:43 | 2022-09-09 16:57 | 0:14 | T | Due to 33 kV feeder fault | 0 | 0 | No interruption
Cumilla(N) | 132/33 kV transformer T4 | 2022-09-10 10:52 | 2022-09-10 14:08 | 3:16 | T | Due to red-hot maint. | 0 | 0 | No interruption
Feni | 132/33 kV transformer T1 | 2022-09-13 06:52 | 2022-09-13 08:32 | 1:40 | E/O | Due to red-hot maint.33 kV side | 21 | 35 | Power interruption
Cumilla(S) | 132/33 kV transformer T4 | 2022-09-15 15:28 | 2022-09-15 16:27 | 0:59 | E/O | Due to red-hot maint.33 kV side | 0 | 0 | No interruption
Ramganj | 132/33 kV transformer T1 with 33 kV Bus | 2022-09-16 09:15 | 2022-09-16 19:50 | 10:35 | E/O | Due to red-hot maint.33 kV side | 20 | 211.6667 | Power interruption
Sreemongal | 132/33 kV transformers T-1 & T2 | 2022-09-17 19:01 | 2022-09-17 19:05 | 0:04 | T | Due to 33 kV feeder fault | 37 | 2.4667 | Power interruption
Chowmuhani | 132/33 kV transformers T-1 & T2 | 2022-09-18 06:10 | 2022-09-18 06:34 | 0:24 | T | Due to 33 kV feeder fault | 20 | 8 | Power interruption
Chandpur | 132/33 kV transformer T5 | 2022-09-19 09:41 | 2022-09-19 17:53 | 8:12 | E/O | Due to red-hot maint.33 kV side | 0 | 0 | No interruption
Ramganj | 132/33 kV transformer T2 | 2022-09-20 08:08 | 2022-09-20 10:01 | 1:53 | E/O | Due to red-hot maint. | 15 | 28.25 | Power interruption
Cumilla(N) | 230/132 kV transformer T01 | 2022-09-24 13:04 | 2022-09-24 14:42 | 1:38 | T | Tripped showingwinding tem.& diff. relay | 0 | 0 | No interruption
Sreemongal | 132/33 kV transformers T-2 & T3 | 2022-09-25 11:06 | 2022-09-25 13:23 | 2:17 | T | Tripped showing Buchholz & Lockout relay | 20 | 14 | Power interruption 11:06 to 13:23
B.Baria | 132/33 kV transformer T2 | 2022-09-30 00:14 | 2022-09-30 01:11 | 0:57 | E/O | Due to red-hot maint.33 kV side | 80 | 76 | Power interruption
|  |  | Total : | 36:44 |  |  |  | 484.25
Khulna Grid Circle :
Payra | 400 kV Bus coupler | 2022-09-06 08:57 | 2022-09-06 11:03 | 2:06 | T | Due to HVDC block-1 tripped | 0 | 0 | No interruption
Bhandaria | 132/33 kV transformers T-1 & T2 | 2022-09-08 03:18 | 2022-09-08 03:24 | 0:06 | E/O | Due to 33 feeder fault | 0 | 0 | No interruption
Shariatpur | 132/33 kV transformer T2 | 2022-09-10 15:36 | 2022-09-10 17:00 | 1:24 | E/O | Due to red-hot maint by PBS | 10 | 14 | Power interruption
Chuadanga | 132/33 kV transformer T1 with 33 kV Bus | 2022-09-11 07:10 | 2022-09-11 08:57 | 1:47 | E/O | Due to red-hot maint by PBS | 40 | 71.3333 | Power interruption
Faridpur | 132/33 kV transformers T-1 | 2022-09-12 06:59 | 2022-09-12 07:25 | 0:26 | E/O | Due to bursting of L/A | 82 | 35.5333 | Power interruption
| 132/33 kV transformers T-2 | 2022-09-12 06:59 | 2022-09-12 10:16 | 3:17 | E/O
Narail | 132/33 kV transformers T1 & T2 | 2022-09-12 10:20 | 2022-09-12 12:06 | 1:46 | E/O | Due to bursting of PT | 20 | 35.3333 | Power interruption
Shariatpur | 132/33 kV transformers T-1 | 2022-09-12 14:55 | 2022-09-12 15:41 | 0:46 | T | Tripped showing O/C relay at 33 kV | 35 | 26.8333 | Power interruption
| 132/33 kV transformers T-2 | 2022-09-12 14:55 | 2022-09-12 18:41 | 3:46 | T
Rampal | 400/132 kV transformer ICT1 | 2022-09-15 12:17 | 2022-09-15 15:57 | 3:40 | T | Tripped showing PRV relay | 0 | 0 | No interruption
Satkhira | 132/33 kV transformer T1 with 33 kV Bus | 2022-09-17 06:28 | 2022-09-17 07:07 | 0:39 | E/O | Due to red-hot maint | 20 | 13 | Power interruption
Narail | 132/33 kV transformers T1 | 2022-09-17 20:41 | 2022-09-17 22:11 | 1:30 | T | Tripped showing O/C & E/F relay | 28 | 42 | Power interruption
| 132/33 kV transformers T2 | 2022-09-17 20:41 | 2022-09-17 22:13 | 1:32 | T
Chuadanga | 132/33 kV transformers T2 & T3 | 2022-09-19 06:12 | 2022-09-19 07:22 | 1:10 | E/O | Due to red-hot maint at 33 kV side | 35 | 40.8333 | Power interruption
Barisal(S) | 132/33 kV transformer T2 with section-2 | 2022-09-23 07:30 | 2022-09-23 09:59 | 2:29 | E/O |  | 15 | 37.25 | Power interruption
Khulna© | 132/33 kV transformer T3 | 2022-09-27 22:48 | 2022-09-28 00:40 | 1:52 | E/O | Due to red-hot maint at 33 kV side | 0 | 0 | No interruption
Mongla | 132/33 kV transformers T1 & T2 | 2022-09-28 17:54 | 2022-09-28 18:19 | 0:25 | T | Tripped showing E/F relay at 33 kV side | 20 | 8.3333 | Power interruption
|  |  | Total : | 28:41 |  | Unserved Energy: |  | 324.45
HVDC Grid Circle :
Bottail | 132/33 kV transformer T2 | 2022-08-02 16:11 | 2022-08-02 17:56 | 1:45 | E/O | Due to red-hot maint at 33 kV side | 30 | 52.5 | Power interruption
Jhenidah(old) | 132/33 kV transformer T2 | 2022-09-02 22:56 | 2022-09-03 01:05 | 2:09 | E/O | Due to red-hot maint at 33 kV side | 30 | 64.5 | Power interruption
Bottail | 132/33 kV transformer T2 | 2022-09-13 15:39 | 2022-09-13 17:05 | 1:26 | E/O | Due to red-hot maint at 33 kV side | 30 | 43 | Power interruption
Jhenidah(old) | 132/33 kV transformer T2 | 2022-09-16 08:45 | 2022-09-16 10:16 | 1:31 | E/O | Due to red-hot maint at 33 kV side | 15 | 22.75 | Power interruption
HVDC 20DF24 | HVDC 20DF24 filter | 2022-09-20 10:14 | 2022-09-20 11:08 | 0:54 | E/O | Due to emergency maint. | 0 | 0 | No interruption
HVDC | 400 kV Bus reactor | 2022-09-20 11:19 | 2022-09-20 12:52 | 1:33 | E/O |  | 0 | 0 | No interruption
|  |  | Total : | 9:18 |  |  |  | 182.75
Bogura Grid Circle:
Bogura | 132/33 kV transformers T3 & T4 | 2022-09-03 11:44 | 2022-09-03 13:02 | 1:18 | E/O | Due to red-hot maint at 33 kV side | 60 | 78 | Power interruption
Bogura (O) | 132/33 kV transformer T1 | 2022-09-03 12:42 | 2022-09-03 12:42 | 0:00 | E/O | Due to Oil leakage at 33kV B-phase bushing | 0 | 0 | No interruption
Purbasadipur | 132/33 kV transformers T1 & T2 | 2022-09-05 08:05 | 2022-09-05 08:20 | 0:15 | T | Tripped showing E/F. relay | 75 | 18.75 | Power interruption
Niamatpur | 132/33 kV transformer T1 | 2022-09-07 23:12 | 2022-09-08 02:17 | 3:05 | E/O | Due to red-hot maint at 33 kV side | 0 | 0 | No interruption
Rajshahi(N) | 132/33 kV transformer T2 | 2022-09-08 07:06 | 2022-09-08 08:39 | 1:33 | E/O | Due to red-hot maint at 33 kV side | 0 | 0 | No interruption
Saidpur | 132/33 kV transformer T1 | 2022-09-10 11:02 | 2022-09-10 13:25 | 2:23 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Bogura | 132/33 kV transformers T1 & T2 | 2022-09-11 09:04 | 2022-09-11 09:40 | 0:36 | T | Tripped showing 33 kV feeder fault | 45 | 27 | Power interruption
| 230/132 kV transformer T01 | 2022-09-13 10:04 | 2022-09-13 13:05 | 3:01 | T | Tripped showing lockout . relay | 0 | 0 | No interruption
Jaldhaka | 33 kV Bus-2 | 2022-09-14 18:05 | 2022-09-14 19:07 | 1:02 | E/O | Due to red-hot maint | 22 | 22.7333 | Power interruption
Purbasadipur | 132/33 kV transformers T1 & T2 | 2022-09-15 13:27 | 2022-09-15 13:40 | 0:13 | T | Tripped showing 33 kV feeder fault | 88 | 19.0667 | Power interruption
| 132/33 kV transformers T1 & T2 | 2022-09-15 14:59 | 2022-09-15 15:33 | 0:34 | T | Tripped showing O/C & E/F. relay | 70 | 39.6667 | Power interruption
Natore | 132/33 kV transformers T1 & T2 | 2022-09-18 06:41 | 2022-09-18 07:44 | 1:03 | E/O | Due to red-hot maint at 33 kV side | 50 | 52.5 | Power interruption
Purbasadipur | 132/33 kV transformer T3 | 2022-09-25 23:32 | 2022-09-25 23:44 | 0:12 | T | Tripped showing O/C & E/F. relay | 30 | 6 | Power interruption
Rajshahi(N) | 132/33 kV transformer T2 with 33 kV Bus | 2022-09-28 07:11 | 2022-09-28 09:03 | 1:52 | E/O | Due to red-hot maint at 33 kV side | 31 | 57.8667 | Power interruption
Shahjadpur | 132/33 kV transformerT3 | 2022-09-28 10:55 | 2022-09-28 12:30 | 1:35 | E/O | Due to red-hot maint at 33 kV side | 0 | 0 | No interruption
Thaurgaon | Thaurgaon-Panchagarh 132 kV Ckt | 2022-09-28 18:20 | 2022-09-28 19:53 | 1:33 | T | Tripped showing O/C . relay | 45 | 69.75 | Power interruption
|  |  | Total : | 20:15 |  |  |  | 391.3333
Others :
Ashuganj | 230/132 kV transformer OAT12 | 2022-08-02 12:02 | 2022-08-02 12:23 | 0:21 | T | Tripped showing O/C. relay | 0 | 0 | No interruption
| 230/132 kV transformer T01 | 2022-08-08 09:21 | 2022-08-08 15:21 | 6:00 | T | Tripped showing O/C. relay | 0 | 0 | No interruption
| 132/33 kV transformer OAT12 | 2022-08-10 13:17 | 2022-08-10 13:31 | 0:14 | T | Tripped showing O/C. relay | 0 | 0 | No interruption
| 132/33 kV transformer OAT12 | 2022-08-14 13:17 | 2022-08-14 15:04 | 1:47 | T | Tripped showing O/C. relay | 0 | 0 | No interruption
| 132/33 kV transformer OAT12 | 2022-08-18 06:04 | 2022-08-18 10:33 | 4:29 | T | Tripped showing O/C. relay | 0 | 0 | No interruption
| 230/132 kV transformer OAT12 | 2022-08-21 11:15 | 2022-08-21 11:28 | 0:13 | T | Tripped showing O/C. relay | 0 | 0 | No interruption
| 230/132 kV transformer OAT12 | 2022-08-23 08:27 | 2022-08-23 08:36 | 0:09 | T | Tripped showing O/C. relay at 33 kV side | 0 | 0 | No interruption
| 230/132 kV transformer OAT12 | 2022-08-23 23:07 | 2022-08-23 23:23 | 0:16 | T | Tripped showing O/C. relay | 0 | 0 | No interruption
|  |  | Total : | 13:29 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 174:45 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-24
Page: 1/2 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month:September2022
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Kabirpur | Kabirpur-Bibiyana 400 kV Ckt-1 | 2022-09-08 10:02 | 2022-09-08 10:49 | 0:47 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Tangail 132 kV Ckt-1 & 2 | 2022-09-08 19:51 | 2022-09-08 20:07 | 0:16 | T | Tripped showing Dist. relay | 600 | 160 | Power interruption
Mymensingh | Mymensingh-Bhaluka 132 kV Ckt-1 & 2 | 2022-09-08 19:51 | 2022-09-08 20:22 | 0:31 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Joydevpur | Joydevpur-Kodda 132 kV Ckt-2 | 2022-09-12 18:50 | 2022-09-12 18:59 | 0:09 | T | Tripped showing Dist. relay | 60 | 9 | Power interruption
Kaliakoir | Kaliakoir-Bibiyana 400 kV Ckt-2 | 2022-09-29 11:41 | 2022-09-29 12:12 | 0:31 | T | Tripped showing auto reclose relay | 0 | 0 | No interruption
|  |  | Total : | 2:14 |  | Unserved Energy: |  | 169
Dhaka (South) Grid Circle :
Ullon | Ullon-Siddhirganj 132 kV Ckt-1 | 2022-09-01 08:52 | 2022-09-01 12:55 | 4:03 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Ghorashal | Ghorashal-Ishurdi all 230 kV Ckt-2 | 2022-09-06 08:58 | 2022-09-06 09:20 | 0:22 | T | Due to HVDC block-1 tripped | 1246 | 456.8667 | Power interruption
Siddhirganj | Siddhirganj-Matuail 132 kV Ckt | 2022-09-17 05:55 | 2022-09-17 06:06 | 0:11 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Maniknagar | Maniknagar-Matuail 132 kV Ckt | 2022-09-17 05:55 | 2022-09-17 06:28 | 0:33 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Haripur | Haripur-Bhulta 132 kV Ckt | 2022-09-17 16:11 | 2022-09-17 16:31 | 0:20 | T | Tripped showing O/C. relay. | 210 | 70 | Power interruption
Sonargaon | Sonargaon-Daudkandi 132 kV Ckt-2 | 2022-09-29 01:50 | 2022-09-29 02:19 | 0:29 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
|  |  | Total : | 5:58 |  | Unserved Energy: |  | 526.8667
Chattogram Grid Circle :
Baroaulia | Baroaulia-Hathazari 132 kV Ckt-2 | 2022-09-01 06:23 | 2022-09-01 06:23 | 0:00 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Bakulia | Bakulia-Sikalbaha 132 kV Ckt-1 & 2 | 2022-09-08 23:45 | 2022-09-09 00:19 | 0:34 | T | Tripped showing Dist. relay | 400 | 226.6667 | Power interruption
Shahmirpur | Shahmirpur-Sikalbaha 132 kV Ckt-1 | 2022-09-08 23:47 | 2022-09-09 00:39 | 0:52 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
| Shahmirpur-Sikalbaha 132 kV Ckt-2 | 2022-09-08 23:47 | 2022-09-09 00:32 | 0:45 | T |  | 0 | 0 | No interruption
T.K chemical | T.K chemical-Sikalbaha 132 kV Ckt | 2022-09-08 23:44 | 2022-09-09 00:47 | 1:03 | T | Tripped showing E/F. relay | 0 | 0 | No interruption
Juldah | Juldah-Sikalbaha 132 kV Ckt | 2022-09-08 23:44 | 2022-09-09 00:47 | 1:03 | T | Tripped showing Dist. relay | 22 | 23.1 | Power interruption
Baraulia | Baraulia-Sitalpur 132 kV Ckt | 2022-09-09 06:21 | 2022-09-09 07:33 | 1:12 | T | Tripped showing O/C. relay. | 0 | 0 | No interruption
Hathazari | Hathazari-Baroerhat 132 kV Ckt-1 & 2 | 2022-09-18 04:27 | 2022-09-18 04:54 | 0:27 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
| Hathazari-Sikalbaha 230 kV Ckt-1 | 2022-09-18 20:20 | 2022-09-18 21:17 | 0:57 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
| Hathazari-Sikalbaha 230 kV Ckt-2 | 2022-09-18 20:20 | 2022-09-18 21:46 | 1:26 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-Sikalbaha intermediate 230 kV Ckt-1 & 2 | 2022-09-18 20:20 | 2022-09-18 22:55 | 2:35 | T | Tripped showing Gen. relay | 0 | 0 | No interruption
Baroierhat | Baroierhat-Hathazari 132 kV both Ckts-1 & 2 | 2022-09-24 06:23 | 2022-09-24 06:42 | 0:19 | T | Tripped showing Gen. relay | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-Dohazari 132 kV both Ckts | 2022-09-24 03:44 | 2022-09-24 04:06 | 0:22 | T | Tripped showing Dist. relay | 180 | 66 | Power interruption
Hathazari | Hathazari-Baroaulia 132 kV Ckt-1 | 2022-09-24 10:58 | 2022-09-24 11:24 | 0:26 | T | Tripped showing Dist. relay |  | 0 | Power interruption
| Hathazari-Kaptai 132 kV Ckt-1 | 2022-09-25 03:37 | 2022-09-25 04:00 | 0:23 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
| Hathazari-Kaptai 132 kV Ckt-2 | 2022-09-25 03:37 | 2022-09-25 04:02 | 0:25 | T |  | 0 | 0 | No interruption
Chandraghona | Chandraghona-Rangamati 132 kV Ckt-1 | 2022-09-25 03:51 | 2022-09-25 06:33 | 2:42 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
| Chandraghona-Madunaghat 132 kV Ckt-1 | 2022-09-25 03:38 | 2022-09-25 03:38 |  | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Halishahar | Halishahar-Juldah 132 kV Ckt | 2022-09-26 13:20 | 2022-09-26 14:30 | 1:10 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Dohazari | Dohazari-Sikalbaha 132 kV Ckt | 2022-09-28 14:32 | 2022-09-28 19:53 | 5:21 | T | Tripped showing Dist. relay | 180 | 3.5 | Power interruption 14:32 to 14:39
|  |  | Total : | 22:02 |  | Unserved Energy: |  | 319.2667
Cumilla Grid Circle :
Sylhet | Sylhet-Chattak 132 kV Ckt-1 | 2022-09-05 07:27 | 2022-09-05 07:34 | 0:07 | T | Tripped showing Dist. relay. | 10 | 1.1667 | Power interruption
| Sylhet-Chattak 132 kV Ckt-1 | 2022-09-05 08:03 | 2022-09-05 09:02 | 0:59 | T | Tripped showing Dist. relay. | 10 | 2.1667 | Power interruption 08:03to 8:16
Fenchuganj | Fenchuganj-Sylhet 132 kV Ckt-1 | 2022-09-06 00:33 | 2022-09-06 00:43 | 0:10 | T | Tripped showing Dist. relay. | 33 | 5.5 | Power interruption
Cumilla(N) | Cumilla(N)-Comilla(S) 132 kV Ckt-1 | 2022-09-09 13:13 | 2022-09-09 13:50 | 0:37 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV Ckt-2 | 2022-09-10 09:01 | 2022-09-10 12:32 | 3:31 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Dhanmondi 132 kV Ckt-2 | 2022-09-17 09:39 | 2022-09-17 09:58 | 0:19 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
BSRM | BSRM-AKSM 230 kV Ckt | 2022-09-17 13:05 | 2022-09-17 13:31 | 0:26 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Ashuganj | Ashuganj(S)-Ghorashal 230 kV Ckt-1 | 2022-09-26 10:20 | 2022-09-26 11:05 | 0:45 | T | Tripped showing O/C. relay | 0 | 0 | No interruption
| Ashuganj(S)-Ghorashal 230 kV Ckt-2 | 2022-09-26 10:19 | 2022-09-26 11:25 | 1:06 | T | Tripped showing E/F. relay. | 0 | 0 | No interruption
Chowmuhani | Chowmuhani-Ramganj both132 kV Ckt | 2022-09-27 05:58 | 2022-09-27 06:11 | 0:13 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
BSRM | BSRM-GPH 230 kV Ckt | 2022-09-27 11:00 | 2022-09-27 11:14 | 0:14 | T | Tripped showing O/C. relay | 0 | 0 | No interruption
Chowmuhani | Chowmuhani-Feni 132 kV Ckt-2 | 2022-09-27 14:17 | 2022-09-27 14:47 | 0:30 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
|  |  | Total : | 8:57 |  | Unserved Energy: |  | 8.8333
Khulna Grid Circle :
Khulna(S) | Khulna(S)-Rampal 230 kV Ckt-1 | 2022-09-06 08:57 | 2022-09-06 10:20 | 1:23 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
| Khulna(S)-Rampal 230 kV Ckt-2 | 2022-09-06 08:57 | 2022-09-06 12:00 | 3:03 | T |  | 0 | 0 | No interruption
Rampal | Rampal-Gopalganj 400 kV Ckt-1 | 2022-09-06 08:57 | 2022-09-06 10:38 | 1:41 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Gopalganj | Gopalganj-Payra 400 kV Ckt-1 | 2022-09-06 08:57 | 2022-09-06 11:02 | 2:05 | T |  | 0 | 0 | No interruption
| Gopalganj-Payra 400 kV Ckt-2 | 2022-09-06 08:57 | 2022-09-06 20:18 | 11:21 | T |  | 0 | 0 | No interruption
Mongla | Mongla-Bagerhat 132 kV Ckt-2 | 2022-09-09 17:32 | 2022-09-09 17:52 | 0:20 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Gopalganj(O) | Gopalganj(O)-Gollamari 132 kV Ckt-1 | 2022-09-15 02:42 | 2022-09-15 03:31 | 0:49 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Rampal | Rampal-Khulna(S) 230 kV Ckt-1 | 2022-09-15 02:55 | 2022-09-15 09:32 | 6:37 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Goalpara | Goalpara-Bagerhat 132 kV Ckt | 2022-09-15 03:28 | 2022-09-15 03:53 | 0:25 | T |  | 0 | 0 | No interruption
Payra P/P | Payra P/P-Payra S/S 400 kV Ckt | 2022-09-15 12:17 | 2022-09-15 12:28 | 0:11 | T | Tripped showing Dist. relay | 156 | 28.6 | Power interruption
Khulna© | Khulna©-Goalpara 132 kV Ckt-1 | 2022-09-18 12:08 | 2022-09-18 13:07 | 0:59 | T | Tripped showing Dist. relay | 119 | 148.75 | Power interruption 12:08 to 12:38
| Khulna©-Goalpara 132 kV Ckt-2 | 2022-09-18 12:08 | 2022-09-18 13:20 | 1:12 | T |  | 0 | 0 | No interruption
Khulna 225 MW | Khulna 225-Khulna© 132 kV Ckt-1 | 2022-09-18 12:07 | 2022-09-18 12:49 | 0:42 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
| Khulna 225-Khulna© 132 kV Ckt-2 | 2022-09-18 12:07 | 2022-09-18 12:51 | 0:44 | T |  | 0 | 0 | No interruption
Barisal(S) | Barisal(S)-Bhandaria 132 kV Ckt | 2022-09-26 12:13 | 2022-09-26 12:18 | 0:05 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
|  |  | Total : | 31:37 |  | Unserved Energy: |  | 177.35
HVDC Grid Circle :
Jashore | Jashore-Benapole 132 kV Ckt-2 | 2022-09-05 14:08 | 2022-09-05 16:22 | 2:14 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Bheramara | Bheramara-HVDC 230 kV Ckt-1 & 2 | 2022-09-06 08:57 | 2022-09-06 09:51 | 0:54 | T |  | 0 | 0 | No interruption
HVDC | HVDC -Jhenaidah 230 kV Ckt-1 | 2022-09-06 08:57 | 2022-09-06 09:56 | 0:59 | T |  | 0 | 0 | No interruption
| HVDC -Jhenaidah 230 kV Ckt-2 | 2022-09-06 08:57 | 2022-09-06 10:32 | 1:35 | T |  | 0 | 0 | No interruption
Bheramara | Bheramara-HVDC 230 kV Ckt-2 | 2022-09-19 08:46 | 2022-09-19 09:28 | 0:42 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Ishurdi | Ishurdi-Ghorashal 230 kV Ckt-1 | 2022-09-26 10:07 | 2022-09-26 15:48 | 5:41 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
| Ishurdi-Ghorashal 230 kV Ckt-2 | 2022-09-26 10:14 | 2022-09-26 15:46 | 5:32 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Bheramara | Bheramara-HVDC 230 kV Ckt-1 | 2022-09-29 07:59 | 2022-09-29 08:43 | 0:44 | T | Tripped showing E/F. relay | 0 | 0 | No interruption
| Bheramara-HVDC 230 kV Ckt-2 | 2022-09-29 07:59 | 2022-09-29 08:54 | 0:55 | T | Tripped showing Direct & E/F. relay | 0 | 0 | No interruption
Ishurdi | Ishurdi-Ghorashal 230 kV Ckt-2 | 2022-09-29 18:31 | 2022-09-29 19:06 | 0:35 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
|  |  | Total : | 19:51 |  | Unserved Energy: |  | 0
Bogura Grid Circle:
Natore | Natore-Rajshahi 132 kV Ckt-1 | 2022-09-01 07:48 | 2022-09-02 22:38 | 38:50 | E/O | Due to bursting of PT | 0 | 0 | No interruption
Saidpur | Saidpur-Purbasadipur 132 kV Ckt-1 | 2022-09-02 01:56 | 2022-09-02 02:15 | 0:19 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
| Saidpur-Purbasadipur 132 kV Ckt-2 | 2022-09-02 01:56 | 2022-09-02 02:28 | 0:32 | T |  | 0 | 0 | No interruption
Bogura | Bogura-Naogaon 132 kV Ckt-1 | 2022-09-03 13:40 | 2022-09-03 15:09 | 1:29 | T | Tripped showing Dist. relay. | 186 | 275.9 | Power interruption
Barapukuria | Barapukuria-Rangpur 132 kV Ckt-1 & 2 | 2022-09-03 17:30 | 2022-09-03 17:48 | 0:18 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
| Barapukuria-Rangpur 132 kV Ckt-2 | 2022-09-04 01:23 | 2022-09-04 02:23 | 1:00 | T |  | 0 | 0 | No interruption
Rajshahi | Rajshahi-Natore 132 kV Ckt-1 | 2022-09-06 08:57 | 2022-09-06 09:20 | 0:23 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
| Rajshahi-Natore 132 kV Ckt-2 | 2022-09-06 08:57 | 2022-09-06 09:40 | 0:43 | T |  | 0 | 0 | No interruption
| Rajshahi-HVDC 230 kV Ckt-1 & 2 | 2022-09-06 08:57 | 2022-09-06 09:46 | 0:49 | T |  | 0 | 0 | No interruption
Bogura | Bogura -Mohastanghor 132 kV Ckt-1 & 2 | 2022-09-06 15:26 | 2022-09-06 16:12 | 0:46 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
| Bogura-Sirajganj 230 kV Ckt-1 | 2022-09-10 08:40 | 2022-09-10 10:22 | 1:42 | T | Due to red-hot maint. | 0 | 0 | No interruption
| Bogura-Naogaon 132 kV Ckt-1 | 2022-09-11 17:01 | 2022-09-11 17:07 | 0:06 | T | Tripped showing O/C & E/F. relay. | 0 | 0 | No interruption
| Bogura-Naogaon 132 kV Ckt-2 | 2022-09-11 17:01 | 2022-09-11 17:34 | 0:33 | T | Tripped showing Dist. relay. | 148 | 81.4 | Power interruption
| Bogura -Barapukuria 230 kV Ckt-2 | 2022-09-14 15:35 | 2022-09-14 16:39 | 1:04 | T | Tripped showing E/F. relay. | 0 | 0 | No interruption
C.nawabganj | C.nawabganj-Rohanpur 132 kV Ckt | 2022-09-15 15:56 | 2022-09-15 16:20 | 0:24 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Sirajganj | Sirajganj-Sherpur 132 kV Ckt-1 & 2 | 2022-09-25 18:54 | 2022-09-25 19:07 | 0:13 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
| Bogura -Natore 132 kV Ckt-1 | 2022-09-26 12:21 | 2022-09-26 12:38 | 0:17 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Rajshahi(N) | Rajshahi(N)-Amnura 132 kV Ckt | 2022-09-26 19:01 | 2022-09-26 19:54 | 0:53 | E/O | Due to bursting of PT | 54 | 47.7 | Power interruption
C.nawabganj | C.nawabganj-Rajshahi(N) 132 kV Ckt | 2022-09-29 05:23 | 2022-09-29 05:33 | 0:10 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
|  |  | Total : | 50:31 |  | Unserved Energy: |  | 405
Others :
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 405
Total outage period of Sub-station Equipment : |  |  |  | 141:10 | Hours
T = Tripping | [7 empty] | Executive Engineer
E/O = Emergency Outage | [7 empty] | Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-25
Page: 1/4 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: September 2022
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Sherpur | 132/33 kV transformer T-1 | 2022-09-04 15:16 | 2022-09-04 15:51 | 0:35 | S/O | Due to OLTC sample collection | 0 | 0 | No interruption
| 132/33 kV transformer T-1 | 2022-09-04 15:52 | 2022-09-04 16:15 | 0:23 | S/O |  | 0 | 0 | No interruption
Jamalpur | 132/33 kV transformer T-3 | 2022-09-05 17:27 | 2022-09-05 20:01 | 2:34 | S/O | Due to C/M work | 10 | 25.6667 | Power interruption
Agargaon | 132/33 kV transformer T-1 | 2022-09-06 09:12 | 2022-09-06 12:06 | 2:54 | S/O |  | 0 | 0 | No interruption
Tangail | 132/33 kV transformer T-1 | 2022-09-07 15:54 | 2022-09-07 18:13 | 2:19 | S/O | Due to D/W work | 35 | 81.0833 | Power interruption
Jamalpur | 132/33 kV transformer T-3 | 2022-09-07 15:42 | 2022-09-07 17:03 | 1:21 | S/O | Due to fire at 33 kV B-phae PT | 13 | 17.55 | Power interruption
| 132/33 kV transformer T-1 | 2022-09-07 15:45 | 2022-09-07 17:03 | 1:18 | S/O |  | 22 | 28.6 | Power interruption
Mirpur | 132 kV reserve Bus | 2022-09-09 07:10 | 2022-09-09 07:10 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Dhamrai | 132/33 kV transformer T-1 | 2022-09-14 17:22 | 2022-09-14 19:28 | 2:06 | S/O | Due to C/M work | 20 | 42 | Power interruption
Agargaon | 230 kV bus coupler | 2022-09-14 13:40 | 2022-09-14 16:05 | 2:25 | S/O | Due to D/W work | 0 | 0 | No interruption
Joydevpur | 132/33 kV transformer T-3 | 2022-09-15 14:48 | 2022-09-15 14:48 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | 230/132 kV transformer T-03 | 2022-09-15 15:13 | 2022-09-15 18:01 | 2:48 | S/O | Due to C/M work | 0 | 0 | No interruption
Kallyanpur | 132/33 kV transformer T-2 |  | 2022-09-15 17:31 |  | S/O | After maint.work | 0 | 0 | No interruption
Kodda | 132/33 kV transformer T-1 | 2022-09-16 06:17 | 2022-09-16 07:23 | 1:06 | S/O | Due to C/M work | 0 | 0 | No interruption
Agargaon | 230/132 kV transformer T-02 | 2022-09-20 05:30 | 2022-09-20 05:30 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Kabirpur | 132/33 kV transformer T-1 | 2022-09-26 07:41 | 2022-09-26 09:26 | 1:45 | S/O | Due to C/M work | 10 | 17.5 | Power interruption
Agargaon | 230/132 kV transformer T-02 | 2022-09-30 07:02 | 2022-09-30 07:02 | 0:00 | S/O | Due to replacement work | 0 | 0 | No interruption
|  |  | Total : | 21:34 |  | Unserved Energy: |  | 212.4
Dhaka (South) Grid Circle :
Rampura | 230/132 kV transformer T-03 | 2022-09-02 06:50 | 2022-09-02 06:50 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Sitalakhya | 132/33 kV transformer T2 | 2022-09-02 11:21 | 2022-09-02 11:21 | 0:00 | S/O | Due to replacement work | 0 | 0 | No interruption
Keraniganj | 230/132 kV transformer T-03 | 2022-09-03 10:41 | 2022-09-03 14:28 | 3:47 | S/O | Due to C/M work | 0 | 0 | No interruption
| 230/132 kV transformer T-03 | 2022-09-03 14:42 | 2022-09-03 15:40 | 0:58 | S/O | Due to C/M work | 0 | 0 | No interruption
Bhulta | 132/33 kV transformer T1 | 2022-09-07 06:47 | 2022-09-07 06:47 | 0:00 | S/O | Due to maint.work | 0 | 0 | No interruption
Haripur | 230 kV bay | 2022-09-08 10:18 | 2022-09-08 11:23 | 1:05 | S/O | Due to C/M work | 0 | 0 | No interruption
Kamrangirchar | 132/33 kV transformer T2 | 2022-09-10 06:25 | 2022-09-10 12:07 | 5:42 | S/O | Due to C/M work | 20 | 114 | Power interruption
Keraniganj | 132/33 kV transformer T1 | 2022-09-10 09:47 | 2022-09-10 09:47 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Hasnabad | 33 kV Bus | 2022-09-10 16:32 | 2022-09-10 17:49 | 1:17 | S/O | Due to C/M work by PBS | 0 | 0 | No interruption
Keraniganj | 132/33 kV transformer T1 | 2022-09-11 09:51 | 2022-09-11 17:36 | 7:45 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV transformer T1 | 2022-09-12 10:02 | 2022-09-12 15:41 | 5:39 | S/O | Due to D/W work | 0 | 0 | No interruption
Sreenagar | 132/33 kV transformer T | 2022-09-12 18:51 | 2022-09-12 19:55 | 1:04 | S/O | Due to C/M work | 0 | 0 | No interruption
Keraniganj | 132/33 kV transformer T2 | 2022-09-14 10:48 | 2022-09-14 17:34 | 6:46 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV transformer T2 | 2022-09-15 10:41 | 2022-09-15 15:22 | 4:41 | S/O | Due to D/W work | 0 | 0 | No interruption
Hasnabad | 132/33 kV transformer T2 | 2022-09-19 10:33 | 2022-09-19 12:32 | 1:59 | S/O | Due to D/W work | 0 | 0 | No interruption
Haripur | 230 kV breaker | 2022-09-19 10:32 | 2022-09-19 12:32 | 2:00 | S/O | Due to C/M work | 0 | 0 | No interruption
| 230 kV breaker | 2022-09-19 10:32 | 2022-09-19 11:27 | 0:55 | S/O | Due to C/M work | 0 | 0 | No interruption
Madanganj | 132/33 kV transformer T1 | 2022-09-20 09:57 | 2022-09-20 14:12 | 4:15 | S/O | Due to protection test | 0 | 0 | No interruption
Keraniganj | 132/33 kV transformer T1 | 2022-09-22 10:18 | 2022-09-22 18:46 | 8:28 | S/O | Due to D/W work | 0 | 0 | No interruption
Rampura | 132 kV main Bus-2 | 2022-09-23 07:21 | 2022-09-23 07:21 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
| 230/132 kV transformer T-01 | 2022-09-23 06:01 | 2022-09-23 06:01 | 0:00 | S/O | Due to maint.work | 0 | 0 | No interruption
Haripur | 132 kV main Bus | 2022-09-25 09:35 | 2022-09-25 15:31 | 5:56 | S/O | Due to C/M work | 0 | 0 | No interruption
Nawabganj | 132/33 kV transformer T2 | 2022-09-29 17:51 | 2022-09-29 19:12 | 1:21 | S/O | Due to C/M work by PBS | 18 | 24.3 | Power interruption
Narsinghdi | 132/33 kV transformer T3 | 2022-09-30 06:01 | 2022-09-30 08:36 | 2:35 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 66:13 |  | Unserved Energy: |  | 138.3
Chattogram Grid Circle :
Juldah | 132/33 kV transformer T1 | 2022-09-02 07:52 | 2022-09-04 15:36 | 55:44 | S/O | Due to C/M work | 0 | 0 | No interruption
Dohazari | 132/33 kV transformers T-1 & T2 with 33 kV Bus | 2022-09-03 08:53 | 2022-09-03 10:10 | 1:17 | S/O | Due to C/M work | 54 | 69.3 | Power interruption
Shahmirpur | 132/33 kV transformer T1 | 2022-09-03 15:59 | 2022-09-03 17:06 | 1:07 | S/O | Due to SCADA work | 0 | 0 | No interruption
Sholoshahrar | 132/33 kV transformer T-1 | 2022-09-04 12:25 | 2022-09-04 16:20 | 3:55 | S/O | Due to 33 kV Bus maint.by PDB | 0 | 0 | No interruption
| 132/33 kV transformer T-1 | 2022-09-04 16:31 | 2022-09-04 18:10 | 1:39 | S/O |  | 0 | 0 | No interruption
Madunaghat | 132/33 kV transformer T2 | 2022-09-10 08:54 | 2022-09-10 11:06 | 2:12 | S/O | Due to CB change | 0 | 0 | No interruption
Halishahar | 132/33 kV transformer T3 with 33 kV Bus | 2022-09-10 16:39 | 2022-09-10 17:23 | 0:44 | S/O | Due to C/M work by PDB | 0 | 0 | No interruption
| 132/33 kV transformer T-1 | 2022-09-11 14:55 | 2022-09-11 16:24 | 1:29 | S/O | Due to 33 kV cable connection | 0 | 0 | No interruption
| 132/33 kV transformersT-2 & T3 | 2022-09-11 21:00 | 2022-09-11 21:55 | 0:55 | S/O | Due to 33 kV breaker problem | 70 | 64.1667 | Power interruption
Hathazari | 132/33 kV transformer T-1 | 2022-09-16 09:46 | 2022-09-16 14:45 | 4:59 | S/O | Due to C/M work | 0 | 0 | No interruption
G.K | 132/33 kV transformer T-2 with 33 kV Bus | 2022-09-18 09:05 | 2022-09-18 16:06 | 7:01 | S/O | Due to D/W work | 14 | 98.2333 | Power interruption
Sholoshahrar | 132/33 kV transformer T-1 | 2022-09-22 08:55 | 2022-09-22 22:44 | 13:49 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-2 | 2022-09-24 10:36 | 2022-09-24 13:59 | 3:23 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 98:14 |  | Unserved Energy : |  | 231.7
Cumilla Grid Circle :
Feni | 132/33 kV transformer T-1 | 2022-09-01 05:55 | 2022-09-01 08:37 | 2:42 | S/O | Due to maint.work | 33 | 89.1 | Power interruption
Cumilla(N) | 132/33 kV transformer T4 | 2022-09-08 10:06 | 2022-09-08 12:10 | 2:04 | S/O | Due to C/M work | 0 | 0 | No interruption
Beanibazar | 132/33 kV transformers T1 | 2022-09-08 13:30 | 2022-09-08 15:42 | 2:12 | S/O | Due to 33 kV loop connection | 45 | 99 | Power interruption
| 132/33 kV transformers T2 | 2022-09-08 13:30 | 2022-09-08 15:55 | 2:25 | S/O
Feni | 132/33 kV transformers T2 with 33 kV Bus | 2022-09-10 07:09 | 2022-09-10 08:42 | 1:33 | S/O | Due to C/M work | 35 | 54.25 | Power interruption
Cumilla(S) | 132/33 kV transformer T5 | 2022-09-12 14:52 | 2022-09-12 16:30 | 1:38 | S/O | Due to changing work | 0 | 0 | No interruption
Shahjibazar | 132/33 kV transformer T6 | 2022-09-13 09:35 | 2022-09-13 09:35 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer T2 | 2022-09-13 12:57 | 2022-09-13 13:25 | 0:28 | S/O | Due to maint.work | 0 | 0 | No interruption
Ashuganj | 230/6.6 kV auxiliary transformer | 2022-09-14 09:42 | 2022-09-14 09:42 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Kachua | 132/33 kV transformer T1 | 2022-09-16 07:19 | 2022-09-16 07:19 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Chowmuhani | 132/33 kV transformer T3 | 2022-09-16 07:35 | 2022-09-16 09:15 | 1:40 | S/O | Due to C/M work by PDB | 10 | 16.6667 | Power interruption
Kachua | 132/33 kV transformer T2 | 2022-09-16 11:02 | 2022-09-16 13:18 | 2:16 | S/O | Due to C/M work | 0 | 0 | No interruption
Chandpur | 132/33 kV transformer T5 | 2022-09-20 15:01 | 2022-09-20 17:02 | 2:01 | S/O | Due to C/M work | 0 | 0 | No interruption
Chattak | 132 kV Bus-B | 2022-09-21 06:50 | 2022-09-21 06:50 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Shahjibazar | 132/33 kV transformer T4 | 2022-09-21 07:25 | 2022-09-21 08:12 | 0:47 | S/O | Due to C/M work | 35 | 27.4167 | Power interruption
Sylhet | 132/33 kV transformer T4 | 2022-09-22 10:39 | 2022-09-22 15:30 | 4:51 | S/O | Due to Oil sample collection | 0 | 0 | No interruption
Chandpur | 132/33 kV transformer T5 | 2022-09-22 11:55 | 2022-09-22 20:16 | 8:21 | S/O | Due to C/M work | 0 | 0 | No interruption
Cumilla(S) | 132/33 kV transformer T2 | 2022-09-23 08:20 | 2022-09-23 13:14 | 4:54 | S/O | Due to C/M work | 12 | 58.8 | Power interruption
Shahjibazar | 132/33 kV transformer T4 | 2022-09-23 08:01 | 2022-09-23 11:26 | 3:25 | S/O | Due to C/M work | 0 | 0 | No interruption
Chowmuhani | 132/33 kV transformer T3 | 2022-09-24 02:05 | 2022-09-24 02:28 | 0:23 | S/O | Due to auxiliary transformer problem | 20 | 7.6667 | Power interruption
Chandpur | 132/33 kV transformer T2 | 2022-09-24 11:06 | 2022-09-24 13:19 | 2:13 | S/O | Due to C/M work | 0 | 0 | No interruption
Bibiyana | 400/132 kV transformer ICT1 | 2022-09-24 08:31 | 2022-09-24 21:28 | 12:57 | S/O | Due to C/M work | 0 | 0 | No interruption
Ashuganj | 132/33 kV auxiliary transformer | 2022-09-25 09:07 | 2022-09-25 09:07 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 56:50 |  | Unserved Energy : |  | 352.9
Khulna Grid Circle :
Napara | 132/33 kV transformer T1 with 33 kV Bus | 2022-09-02 17:19 | 2022-09-02 17:44 | 0:25 | S/O | Due to C/M work | 10 | 4.1667 | Power interruption
Rajbari | 132/33 kV transformer T1 | 2022-09-03 08:07 | 2022-09-03 11:00 | 2:53 | S/O | Due to C/M work | 0 | 0 | No interruption
Payra S/S | 400/132 kV Transformer ATR-01 | 2022-09-03 09:20 | 2022-09-03 21:06 | 11:46 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132 kV Bus-2 | 2022-09-03 09:33 | 2022-09-03 21:55 | 12:22 | S/O | Due to D/W work | 0 | 0 | No interruption
Payra | 132 kV Bus-2 | 2022-09-04 09:41 | 2022-09-04 23:58 | 14:17 | S/O | Due to D/W work | 0 | 0 | No interruption
| 400/230 kV Transformer ATR-1 | 2022-09-05 08:43 | 2022-09-05 22:38 | 13:55 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132 kV Bus-A | 2022-09-07 10:00 | 2022-09-07 10:00 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Noapara | 132/33 kV transformer T-1 | 2022-09-08 11:15 | 2022-09-08 11:15 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Faridpur | 132/33 kV transformer T-1 with 33 kV Bus | 2022-09-09 10:36 | 2022-09-09 11:57 | 1:21 | S/O | Due to C/M work | 33 | 44.55 | Power interruption
Payra | 400/230 kV Transformer ATR-02 | 2022-09-10 09:41 | 2022-09-10 09:41 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132 kV Bus-2 | 2022-09-10 10:00 | 2022-09-10 10:00 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Rampal | 400 kV MVA reactor |  | 2022-09-10 18:19 |  |  | After maint.work | 0 | 0 | No interruption
Narail | 132/33 kV transformer T-2 | 2022-09-12 07:25 | 2022-09-12 08:42 | 1:17 | S/O | Due to C/M work | 13 | 16.6833 | Power interruption
Chuadanga | 132/33 kV transformers T1 | 2022-09-13 13:45 | 2022-09-13 15:55 | 2:10 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV transformers T2 | 2022-09-13 13:45 | 2022-09-13 17:05 | 3:20 | S/O |  | 0 | 0 | No interruption
Payra | 400/132 kV transformer T04 | 2022-09-15 09:20 | 2022-09-15 09:20 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132 kV Bus-2 | 2022-09-15 09:25 | 2022-09-15 09:25 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Khulna(C) | 132/33 kV transformer T1 | 2022-09-15 13:43 | 2022-09-15 14:44 | 1:01 | S/O | Due to C/M work | 0 | 0 | No interruption
Satkhira | 132/33 kV transformer T2 | 2022-09-16 07:17 | 2022-09-16 07:17 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Narail | 132/33 kV transformer T1 | 2022-09-16 08:22 | 2022-09-16 11:31 | 3:09 | S/O | Due to C/M work by PBS | 15 | 47.25 | Power interruption
Shariatpur | 132/33 kV transformer T2 | 2022-09-16 09:30 | 2022-09-16 11:51 | 2:21 | S/O | Due to C/M work | 0 | 0 | No interruption
Khulna(C) | 132/33 kV transformer T1 | 2022-09-17 16:00 | 2022-09-17 17:18 | 1:18 | S/O | Due to 33/11 kV new feeder addition | 0 | 0 | No interruption
Bhandaria | 132/33 kV transformer T2 | 2022-09-19 14:18 | 2022-09-19 14:38 | 0:20 | S/O | Due to C/M work | 0 | 0 | No interruption
Magura | 132/33 kV transformer T2 | 2022-09-20 16:26 | 2022-09-20 17:46 | 1:20 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV transformer T1 | 2022-09-20 13:37 | 2022-09-20 14:53 | 1:16 | S/O | Due to D/W work | 0 | 0 | No interruption
Goalpara | 132/33 kV transformer T6 | 2022-09-24 07:40 | 2022-09-24 07:40 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Napara | 132/33 kV transformer T2 | 2022-09-27 13:17 | 2022-09-27 14:36 | 1:19 | S/O | Due to C/M work | 15 | 19.75 | Power interruption
| 132/33 kV transformer T4 | 2022-09-27 15:00 | 2022-09-27 15:34 | 0:34 | S/O | Due to C/M work | 24 | 13.6 | Power interruption
Gopalganj | 132/33 kV transformer T1 | 2022-09-27 15:43 | 2022-09-27 16:59 | 1:16 | S/O | Due to C/M work | 0 | 0 | No interruption
Faridpur | 132/33 kV transformer T2 | 2022-09-28 07:08 | 2022-09-28 07:08 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Payra | 132/33 kV transformer T1 | 2022-09-28 10:09 | 2022-09-28 14:36 | 4:27 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132 kV Bus-2 | 2022-09-28 10:22 | 2022-09-28 10:22 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 82:07 |  | Unserved Energy : |  | 146
HVDC Grid Circle
Jhenaidah | 132/33 kV transformer T1 | 2022-09-02 20:54 | 2022-09-02 23:23 | 2:09 | S/O | Due to WZPDCL work | 75 | 161.25 | Power interruption
Bottail | 132/33 kV transformer T2 | 2022-09-10 07:20 | 2022-09-10 07:20 | 1:26 | S/O | Due to C/M work | 48 | 68.8 | Power interruption
Jashore | 132/33 kV transformer T2 | 2022-09-13 10:48 | 2022-09-13 10:54 | 1:31 | S/O | Due to D/W work | 24 | 36.4 | Power interruption
Bottail | 132/33 kV transformer T1 with 33 kV Bus | 2022-09-23 07:11 | 2022-09-23 09:01 | 0:54 | S/O | Due to C/M work | 30 | 27 | Power interruption
Benapole | 132/33 kV transformer T1 | 2022-09-29 14:21 | 2022-09-29 15:02 | 0:41 | S/O | Due to C/M work by PBS | 20 | 13.6667 | Power interruption
Jhenaidah(O) | 132/33 kV transformer T2 | 2022-09-29 15:07 | 2022-09-29 17:06 | 1:59 | S/O | Due to C/M work | 18 | 35.7 | Power interruption
|  |  | Total : | 8:40 |  | Unserved Energy : |  | 342.8167
Bogura Grid Circle:
Naogaon | 132 kV main Bus | 2022-09-01 07:35 | 2022-09-01 10:35 | 3:00 | S/O | Due to C/M work | 55 | 165 | Power interruption
Rangpur | 132/33 kV transformer T3 | 2022-09-01 11:40 | 2022-09-01 14:32 | 2:52 | S/O | Due to PBS work | 0 | 0 | No interruption
Purbasadipur | 132/33 kV transformer T2 | 2022-09-03 16:14 | 2022-09-03 16:35 | 0:21 | S/O | Due to 33 kV Bus maint. | 40 | 14 | Power interruption
Joypurhat | 132/33 kV transformers T1 & T2 | 2022-09-06 10:25 | 2022-09-06 12:57 | 2:32 | S/O | Due to maint.work | 0 | 0 | No interruption
Barapukuria | 230/132 kV transformer T-01 | 2022-09-07 12:47 | 2022-09-07 12:47 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Panchagarh | 132/33 kV transformer T1 | 2022-09-07 13:04 | 2022-09-07 13:04 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Barapukuria | 132/33 kV transformer T5 | 2022-09-08 08:33 | 2022-09-08 10:19 | 1:46 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV transformer T3 | 2022-09-08 10:50 | 2022-09-08 12:05 | 1:15 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV transformer T4 | 2022-09-08 10:50 | 2022-09-08 13:21 | 2:31 | S/O |  | 0 | 0 | No interruption
Palashbari | 132/33 kV transformer T2 | 2022-09-09 10:09 | 2022-09-09 11:30 | 1:21 | S/O | Due to C/M work | 0 | 0 | No interruption
Rajshahi | 132/33 kV transformer T2 | 2022-09-09 16:32 | 2022-09-09 17:35 | 1:03 | S/O | Due to maint.work | 0 | 0 | No interruption
Rajshahi(N) | 132/33 kV transformer T1 | 2022-09-09 15:09 | 2022-09-09 17:53 | 2:44 | S/O | Due to C/M work | 0 | 0 | No interruption
Purbasdipur | 132 kV Bus | 2022-09-10 06:12 | 2022-09-10 09:58 | 3:46 | S/O | Due to C/M work | 195 | 734.5 | Power interruption
Bogura | 132/33 kV transformer T1 | 2022-09-11 06:31 | 2022-09-11 08:52 | 2:21 | S/O | Due to C/M work | 25 | 58.75 | Power interruption
Niamatpur | 132/33 kV transformer T3 | 2022-09-12 06:43 | 2022-09-12 06:43 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Rangpur | 132 kV Bus-1 | 2022-09-13 08:36 | 2022-09-13 18:15 | 9:39 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132 kV Bus-2 | 2022-09-14 09:10 | 2022-09-14 18:01 | 8:51 | S/O | Due to D/W work | 0 | 0 | No interruption
Naogaon | 132/33 kV transformer T1 | 2022-09-14 10:30 | 2022-09-14 10:30 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV transformer T1 | 2022-09-15 10:30 | 2022-09-15 13:20 | 2:50 | S/O | Due to C/M work | 0 | 0 | No interruption
Rangpur | 132/33 kV transformer T1 | 2022-09-16 07:23 | 2022-09-16 07:23 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV transformer T3 | 2022-09-16 07:26 | 2022-09-16 07:26 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Purbasadipur | 132/33 kV transformer T3 |  | 2022-09-16 18:06 |  | S/O | After maint.work | 0 | 0 | No interruption
| 132/33 kV transformer T3 | 2022-09-20 07:06 | 2022-09-20 07:06 | 0:00 | S/O | Due to D/W work | 0 | 0 | Power interruption
Bogura(O) | 132/33 kV transformers T1 & T2 | 2022-09-21 06:38 | 2022-09-21 09:35 | 2:57 | S/O | Due to C/M work | 60 | 177 | Power interruption
Mosathangar | 33 kV full Bus | 2022-09-21 06:47 | 2022-09-21 09:17 | 2:30 | S/O | Due to D/W work | 45 | 112.5 | Power interruption
Palashbari | 132/33 kV transformer T3 | 2022-09-22 10:50 | 2022-09-22 12:30 | 1:40 | S/O | Due to C/M work | 0 | 0 | No interruption
Niamatpur | 132/33 kV transformerT2 | 2022-09-23 06:27 | 2022-09-23 06:27 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV transformerT2 | 2022-09-24 06:23 | 2022-09-24 06:23 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Purbasadipur | 132/33 kV transformer T1 | 2022-09-25 06:23 | 2022-09-25 10:48 | 4:25 | S/O | Due to C/M work | 40 | 176.6667 | Power interruption
Niamatpur | 132/33 kV transformerT2 | 2022-09-25 06:28 | 2022-09-25 06:28 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Sirajganj | 132/33 kV transformerT3 | 2022-09-26 08:14 | 2022-09-26 09:54 | 1:40 | S/O | Due to C/M work by 33 side | 0 | 0 | No interruption
Niamatpur | 132/33 kV transformerT2 | 2022-09-27 06:35 | 2022-09-27 06:35 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV transformerT2 | 2022-09-28 06:37 | 2022-09-28 06:37 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Purbasadipur | 132/33 kV transformer T4 | 2022-09-28 07:05 | 2022-09-28 07:05 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Ishurdi | 132/33 kV transformerT2 | 2022-09-28 09:32 | 2022-09-28 11:10 | 1:38 | S/O | Due to C/M work | 0 | 0 | No interruption
| 230/132 kV transformer T-03 | 2022-09-29 10:58 | 2022-09-29 14:14 | 3:16 | S/O | Due to C/M work | 0 | 0 | No interruption
Mohastangarh | 33 kV Bus | 2022-09-30 06:51 | 2022-09-30 08:13 | 1:22 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 66:20 |  | Unserved Energy : |  | 1438.4167
Others :Nil
|  |  | Total | 0:00 |  | Unserved Energy : |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 399:58 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-26
Page: 1/5 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: September2022
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Joydevpur | Joydevpur -Kodda 132 kV Ckt-1 | 2022-09-01 09:05 | 2022-09-01 19:48 | 10:43 | S/O | Due to D/W work | 0 | 0 | No interruption
Tongi | Tongi 230 kV S/S-Tongi 80 MW P.P 132 kV Ckt | 2022-09-05 11:06 | 2022-09-05 17:05 | 5:59 | S/O | Due to Power Plant work | 0 | 0 | No interruption
Tangail | Tangail-Kaliakoir 132 kV Ckt-2 | 2022-09-07 05:45 | 2022-09-07 07:05 | 1:20 | S/O | Due to C/M work | 100 | 133.3333 | Power interruption
Tongi | Tongi 230 kV S/S-Tongi 80 MW P.P 132 kV Ckt | 2022-09-07 10:28 | 2022-09-07 13:39 | 3:11 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Agargaon 230 kV Ckt-1 | 2022-09-07 10:46 | 2022-09-07 16:46 | 6:00 | S/O | Due to DFDR work | 0 | 0 | No interruption
| Aminbazar-Agargaon 230 kV Ckt-2 | 2022-09-08 09:24 | 2022-09-08 13:10 | 3:46 | S/O | Due to D/W work | 0 | 0 | No interruption
Joydevpur | Joydevpur -Kodda 132 kV Ckt-2 | 2022-09-08 09:52 | 2022-09-08 17:22 | 7:30 | S/O | Due to C/M work | 0 | 0 | No interruption
Uttara | Uttara-Mirpur 132 kV Ckt | 2022-09-09 06:50 | 2022-09-09 06:50 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Tangail | Tangail-Kaliakoir 132 kV Ckt-1 |  | 2022-09-10 17:28 |  | S/O | After maint.work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Mirpur 132 kV Ckt-2 | 2022-09-12 06:53 | 2022-09-12 10:44 | 3:51 | S/O | Due to C/M work | 0 | 0 | No interruption
Agargaon | Agargaon-Cantonment 132 kV Ckt-1 | 2022-09-12 09:39 | 2022-09-12 12:40 | 3:01 | S/O | Due to D/W work | 0 | 0 | No interruption
Joydevpur | Joydevpur-Kodda 132 kV Ckt-1 | 2022-09-12 13:33 | 2022-09-12 14:46 | 1:13 | S/O | Due to C/M work | 0 | 0 | No interruption
Agargaon | Agargaon-Bashantek 132 kV Ckt-2 | 2022-09-13 12:51 | 2022-09-13 14:28 | 1:37 | S/O | Due to D/W work | 0 | 0 | No interruption
| Agargaon-Aminbazar 230 kV Ckt-1 | 2022-09-13 13:14 | 2022-09-13 14:02 | 0:48 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensigh S/S | Mymensigh S/S-Mymensingh RPCL 132 kV Ckt-2 | 2022-09-14 10:40 | 2022-09-14 12:57 | 2:17 | S/O | Due to C/M work | 0 | 0 | No interruption
Agargaon | Agargaon-Aminbazar 230 kV Ckt-1 | 2022-09-21 05:22 | 2022-09-21 05:22 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
| Agargaon-Satmosjid 132 kV Ckt-1 | 2022-09-21 05:48 | 2022-09-21 05:48 | 2:17 | S/O | Due to D/W work | 0 | 0 | No interruption
Tongi | Tongi-Kodda 300 MW 230 kV Ckt | 2022-09-24 08:52 | 2022-09-24 14:23 | 5:31 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Meghnaghat 230 kV Ckt-1 | 2022-09-26 06:12 | 2022-09-26 06:12 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Kishoreganj 132 kV Ckt-1 | 2022-09-28 14:25 | 2022-09-28 15:43 | 1:18 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 60:22 |  | Unserved Energy: |  | 133.3333
Dhaka (South) Grid Circle :
Sonargaon | Sonargaon-OPCL P/S 132 kV Ckt | 2022-09-02 10:01 | 2022-09-02 10:47 | 0:46 | S/O | Due to C/M work | 0 | 0 | No interruption
Maniknagar | Maniknagar-Siddhiganj 230 kV Ckt-1 | 2022-09-09 05:58 | 2022-09-09 05:58 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Ullon | Ullon-Siddhirganj 132 kV Ckt-1 | 2022-09-10 09:11 | 2022-09-10 14:00 | 4:49 | S/O | Due to equipment testing work | 0 | 0 | No interruption
Ghorashal | Ghorashal-Ishurdi 230 kV Ckt-1 | 2022-09-14 13:01 | 2022-09-14 14:55 | 1:54 | S/O | Due to C/M work | 0 | 0 | No interruption
Shyampur | Shyampur-Fatullah 132 kV Ckt-1 | 2022-09-15 08:17 | 2022-09-15 08:17 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Sitalakhya 132 kV Ckt | 2022-09-16 09:25 | 2022-09-16 17:02 | 7:37 | S/O | Due to C/M work by DPDC | 0 | 0 | No interruption
Haripur | Haripur-Ullon 132 kV Ckt | 2022-09-17 09:16 | 2022-09-17 13:54 | 4:38 | S/O | Due to C/M work | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Siddhirganj 335 MW P/P 230 kV Ckt | 2022-09-17 12:43 | 2022-09-17 16:02 | 3:19 | S/O | Due to protection test | 0 | 0 | No interruption
Rampura | Rampura-Ullon 132 kV Ckt-1 | 2022-09-24 09:05 | 2022-09-24 21:18 | 12:13 | S/O | Due to C/M work by DPDC | 0 | 0 | No interruption
Purbachal | Purbachal-Bashundhara 132 kV Ckt |  | 2022-09-24 12:53 |  |  | After maint.work | 0 | 0 | No interruption
Madanganj | Madanganj-Madanganj P/P 132 kV Ckt |  | 2022-09-27 17:42 |  |  |  | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Aminbazar 230 kV Ckt-2 | 2022-09-29 09:35 | 2022-09-29 16:13 | 6:38 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 41:54 |  | Unserved Energy: |  | 0
Chattogram Grid Circle :
Madunaghat | Madunaghat GIS-Kalurghat 132 kV Ckt-1 | 2022-09-02 12:05 | 2022-09-02 12:05 | 0:00 | S/O | Due to SCADA work | 0 | 0 | No interruption
Hathazari | Hathazari-Baroierhat 132 kV Ckt-1 | 2022-09-03 08:24 | 2022-09-03 15:09 | 6:45 | S/O | Due to D/W work | 0 | 0 | No interruption
Bakulia | Bakulia-Sikalbaha 132 kV Ckt-2 | 2022-09-09 16:31 | 2022-09-09 17:23 | 0:52 | S/O | Due to protection test | 0 | 0 | No interruption
| Bakulia-Sikalbaha 132 kV Ckt-1 | 2022-09-10 11:06 | 2022-09-10 13:50 | 2:44 | S/O |  | 0 | 0 | No interruption
Juldah S/S | Juldah S/S-Juldah -1 132 kV Ckt | 2022-09-18 10:44 | 2022-09-18 12:30 | 1:46 | S/O | Due to maint. work | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-Intermediate 230 kV Ckt-2 | 2022-09-22 09:44 | 2022-09-22 15:48 | 6:04 | S/O | Due to SAS. work | 0 | 0 | No interruption
| Sikalbaha-Intermediate 230 kV Ckt-1 | 2022-09-22 15:59 | 2022-09-22 17:05 | 1:06 | S/O | Due to C/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Sikalbaha 230 kV Ckt-1 | 2022-09-23 07:00 | 2022-09-23 07:00 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
| Hathazari-Raozan 132 kV Ckt- 1 & 2 | 2022-09-23 08:57 | 2022-09-23 19:10 | 10:13 | S/O | Due to D/W work | 0 | 0 | No interruption
Khagrachari | Khagrachari-Rangamati 132 kV Ckt-1 | 2022-09-24 09:45 | 2022-09-24 17:25 | 7:40 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Raozan 230 kV both Ckts- | 2022-09-24 08:21 | 2022-09-24 18:35 | 10:14 | S/O | Due to D/W work | 0 | 0 | No interruption
Baroierhat | Baroierhat-Hathazari 132 kV Ckt-1 | 2022-09-24 15:38 | 2022-09-24 16:59 | 1:21 | S/O | Due to C/M work | 0 | 0 | No interruption
Sikalbaha | Sikalbaha 230 kV S/S-interim S/S 230 kV Ckt-1 | 2022-09-25 09:27 | 2022-09-25 17:15 | 7:48 | S/O | Due to D/W work | 0 | 0 | No interruption
Hathazari | Hathazari-Baroierhat 132 kV Ckt-1 | 2022-09-25 09:32 | 2022-09-25 11:58 | 2:26 | S/O | Due to A/M work | 0 | 0 | No interruption
Khagrachari | Khagrachari-Rangamati 132 kV Ckt-1 | 2022-09-26 09:09 | 2022-09-26 17:19 | 8:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Baraulia 132 kV Ckt-1 | 2022-09-26 13:15 | 2022-09-26 13:42 | 0:27 | S/O | Due to removing work | 0 | 0 | No interruption
Khagrachari | Khagrachari-Rangamati 132 kV Ckt-1 | 2022-09-27 08:20 | 2022-09-27 16:53 | 8:33 | S/O | Due to A/M work | 0 | 0 | No interruption
Baroierhat | Baroierhat-Hathazari 132 kV Ckt-1 | 2022-09-27 09:32 | 2022-09-27 15:02 | 5:30 | S/O | Due to C/M work | 0 | 0 | No interruption
Khagrachari | Khagrachari-Rangamati 132 kV Ckt-1 | 2022-09-28 08:30 | 2022-09-28 14:54 | 6:24 | S/O | Due to A/M work | 0 | 0 | No interruption
Rampur | Rampur-Khulshi 132 kV Ckt-1 | 2022-09-29 12:29 | 2022-09-29 13:08 | 0:39 | S/O | Due to D/W work | 0 | 0 | No interruption
| Rampur-Halishahar 132 kV Ckt-1 | 2022-09-29 09:45 | 2022-09-29 11:43 | 1:58 | S/O | Due to D/W work | 0 | 0 | No interruption
| Rampur-Halishahar 132 kV Ckt-2 | 2022-09-29 11:46 | 2022-09-29 12:22 | 0:36 | S/O | Due to D/W work | 0 | 0 | No interruption
Hathazari | Hathazari-Sikalbaha 230 kV Ckt-1 | 2022-09-29 08:52 | 2022-09-29 16:27 | 7:35 | S/O | Due to C/M work | 0 | 0 | No interruption
Rampur | Rampur-Agrabad 132 kV Ckt-1 | 2022-09-29 13:49 | 2022-09-29 15:01 | 1:12 | S/O | Due to D/W work | 0 | 0 | No interruption
| Rampur-Agrabad 132 kV Ckt-2 | 2022-09-29 15:16 | 2022-09-29 15:42 | 0:26 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 100:29 |  | Unserved Energy: |  | 0
Cumilla Grid Circle :
Ashuganj | Ashuganj-Sirajganj 230 kV Ckt-2 | 2022-09-02 06:36 | 2022-09-02 06:36 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
| Ashuganj-Ashuganj(S) 230 kV Ckt-1 | 2022-09-15 06:08 | 2022-09-15 06:08 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
BSRM | BSRM-AKSML 230 kV Ckt | 2022-09-17 15:03 | 2022-09-17 17:15 | 2:12 | S/O | Due to tree trimming | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV Ckt-1 | 2022-09-20 11:59 | 2022-09-20 19:50 | 7:51 | S/O |  | 0 | 0 | No interruption
Chandpur | Chandpur-Kachua 132 kV Ckt-2 | 2022-09-26 06:24 | 2022-09-26 06:24 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Daudkandi | Daudkandi-Cumilla(N) 132 kV Ckt-2 | 2022-09-26 08:44 | 2022-09-26 17:02 | 8:18 | S/O | Due to replacement work | 0 | 0 | No interruption
Chandpur S/S | Chandpur S/S-Chandpur115 MW 132 kV Ckt | 2022-09-26 15:36 | 2022-09-26 16:54 | 1:18 | S/O | Due to SCADA work | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Comilla(S) 132 kV Ckt-3 | 2022-09-28 08:56 | 2022-09-28 14:33 | 5:37 | S/O | Due to C/M work | 0 | 0 | No interruption
| Cumilla(N)-Comilla(S) 132 kV Ckt-1 | 2022-09-29 08:55 | 2022-09-29 13:45 | 4:50 | S/O | Due to C/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-B.Baria 132 kV Ckt-1 | 2022-09-29 08:46 | 2022-09-29 11:27 | 2:41 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 32:47 |  | Unserved Energy: |  | 0
Khulna Grid Circle :
Payra P/S | Payra P/S-Payra S/S 400 kV Ckt-3 | 2022-09-03 09:20 | 2022-09-03 21:06 | 11:46 | S/O | Due to D/W work | 0 | 0 | No interruption
Payra S/S | Payra-Gopalganj 400 kV Ckt-1 | 2022-09-04 09:48 | 2022-09-04 23:23 | 13:35 | S/O | Due to D/W work | 0 | 0 | No interruption
| Payra 230 kV S/S-Tongi MW P/S 132 kV Ckt | 2022-09-05 11:06 | 2022-09-05 17:05 | 5:59 | S/O | Due to power plant work | 0 | 0 | No interruption
Payra P/S | Payra P/S-Payra S/S 400 kV Ckt-1 | 2022-09-05 08:43 | 2022-09-05 22:36 | 13:53 | S/O | Due to C/M work | 0 | 0 | No interruption
| Payra P/S-Payra S/S 400 kV Ckt-1 | 2022-09-07 09:35 | 2022-09-07 22:39 | 13:04 | S/O | Due to D/W work | 0 | 0 | No interruption
Payra | Payra-Patuakhali 132 kV Ckt-2 | 2022-09-12 15:21 | 2022-09-12 15:35 | 0:14 | S/O | Due to SCADA work | 0 | 0 | No interruption
| Payra-Patuakhali 132 kV Ckt-1 | 2022-09-12 14:49 | 2022-09-12 15:16 | 0:27 | S/O |  | 0 | 0 | No interruption
Gopalganj | Gopalganj-Rampal 400 kV Ckt-1 |  | 2022-09-15 16:44 |  | S/O | After maint.work | 0 | 0 | No interruption
| Gopalganj-Rampal 400 kV Ckt-1 |  | 2022-09-15 16:56 |  | S/O |  | 0 | 0 | No interruption
Payra P/S | Payra P/S-Payra S/S 400 kV Ckt-2 | 2022-09-16 08:48 | 2022-09-16 10:09 | 1:21 | S/O | Due to D/W work | 0 | 0 | No interruption
Khulna (S) | Khulna (S)-Rampal 230 kV Ckt-1 | 2022-09-20 10:15 | 2022-09-20 11:28 | 1:13 | S/O | Due to C/M work | 0 | 0 | No interruption
| Khulna (S)-Khulna 30 MW P.P 230 kV Ckt | 2022-09-20 10:59 | 2022-09-20 12:39 | 1:40 | S/O | Due to protection work | 0 | 0 | No interruption
Magura | Magura-Jhenaidah 132 kV Ckt-1 | 2022-09-20 15:03 | 2022-09-20 17:04 | 2:01 | S/O | Due to D/W work | 0 | 0 | No interruption
Gopalganj S/S | Gopalganj S/S-Gopalganj P/S 132 kV Ckt | 2022-09-22 11:07 | 2022-09-22 13:37 | 2:30 | S/O | Due to C/M work | 0 | 0 | No interruption
Faridpur S/S | Faridpur S/S-Faridpur P/P 132 kV Ckt |  | 2022-09-23 16:31 |  | S/O | After maint.work | 0 | 0 | No interruption
| Faridpur S/S-Faridpur P/P 132 kV Ckt | 2022-09-26 12:08 | 2022-09-26 13:38 | 1:30 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 57:27 |  | Unserved Energy: |  | 0
HVDC Grid Circle :
Ishurdi | Ishurdi-HVDC 230 kV Ckt-3 & 4 |  | 2022-09-06 09:35 |  | S/O | after maint.work | 0 | 0 | No interruption
| Ishurdi-Natore 132 kV Ckt-2 | 2022-09-08 08:53 | 2022-09-08 14:17 | 5:24 | S/O | Due to C/M work | 0 | 0 | No interruption
| Ishurdi-Natore 132 kV Ckt-1 | 2022-09-12 11:25 | 2022-09-12 13:53 | 2:28 | S/O | Due to protection work | 0 | 0 | No interruption
Shahjadpur | Shahjadpur-Baghabari 132 kV Ckt-1 | 2022-09-22 08:08 | 2022-09-22 09:46 | 1:38 | S/O | Due to C/M work | 0 | 0 | No interruption
Ishurdi | Ishurdi-Natore 132 kV Ckt-2 | 2022-09-25 08:35 | 2022-09-25 16:24 | 7:49 | S/O | Due to C/M work | 0 | 0 | No interruption
Natore | Natore-Ishurdi 132 kV Ckt-1 | 2022-09-27 08:14 | 2022-09-27 15:09 | 6:55 | S/O | Due to C/M work | 0 | 0 | No interruption
Bheramara | Bheramara-Bahrampur 400 kV Ckt-4 | 2022-09-27 10:39 | 2022-09-27 19:10 | 8:31 | S/O | Due to C/M work | 0 | 0 | No interruption
Ishurdi | Ishurdi-Ruppur 132 kV Ckt-1 | 2022-09-28 11:04 | 2022-09-28 11:43 | 0:39 | S/O | Due to C/M work | 0 | 0 | No interruption
| Ishurdi-Ruppur 132 kV Ckt-2 | 2022-09-28 11:50 | 2022-09-28 12:12 | 0:22 | S/O | Due to C/M work | 0 | 0 | No interruption
| Ishurdi-Pabna 132 kV Ckt | 2022-09-29 09:49 | 2022-09-29 16:05 | 6:16 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 40:02 |  | Unserved Energy: |  | 0
Bogura Grid Circle :
Naogaon | Naogaon-Bogura 132 kV Ckt-1 | 2022-09-01 07:35 | 2022-09-01 10:34 | 2:59 | S/O | Due to C/M work | 90 | 268.5 | Power interruption
Bogura | Bogura-Natore 132 kV Ckt-2 | 2022-09-01 10:44 | 2022-09-01 13:13 | 2:29 | S/O | Due to C/M work | 0 | 0 | No interruption
Naogaon | Naogaon-Santahar P/S 132 kV Ckt | 2022-09-02 08:50 | 2022-09-02 08:50 | 0:00 | S/O | Due to replacemant work | 0 | 0 | No interruption
| Naogaon-Santahar P/S 132 kV Ckt | 2022-09-03 07:40 | 2022-09-03 07:40 | 0:00 | S/O | Due to replacemant work | 0 | 0 | No interruption
Bogura | Bogura-Naogaon 132 kV Ckt-2 | 2022-09-03 12:15 | 2022-09-03 15:05 | 2:50 | S/O | Due to C/M work | 0 | 0 | No interruption
Barapukuria | Barapukuria S/S-Barapukuria P/S 230 kV Ckt-1 | 2022-09-06 11:26 | 2022-09-06 12:40 | 1:14 | S/O | Due to C/M work | 0 | 0 | No interruption
| Barapukuria S/S-Barapukuria P/S 230 kV Ckt-2 | 2022-09-07 08:49 | 2022-09-07 09:41 | 0:52 | S/O | Due to C/M work | 0 | 0 | No interruption
| Barapukuria-Rangpur 132 kV Ckt-1 | 2022-09-07 09:55 | 2022-09-07 11:07 | 1:12 | S/O | Due to C/M work | 0 | 0 | No interruption
| Barapukuria-Rangpur 132 kV Ckt-2 | 2022-09-07 11:35 | 2022-09-07 12:34 | 0:59 | S/O | Due to C/M work | 0 | 0 | No interruption
Bogura | Bogura-Bakerganj 132 kV Ckt | 2022-09-08 11:37 | 2022-09-08 11:40 | 0:03 | S/O | Due to Scada test | 10 | 0.5 | Power interruption
| Bogura-Sirajganj 230 kV Ckt-1 | 2022-09-10 06:57 | 2022-09-10 08:12 | 1:15 | S/O | Due to C/M work | 0 | 0 | No interruption
| Bogura-Naogaon 132 kV Ckt-2 | 2022-09-12 10:41 | 2022-09-12 14:46 | 4:05 | S/O | Due to C/M work | 0 | 0 | No interruption
Natore | Natore-Rajshahi 132 kV Ckt-1 | 2022-09-14 15:57 | 2022-09-14 17:15 | 1:18 | S/O | Due to protection test | 0 | 0 | No interruption
Rangpur S/S | Rangpur S/S-Rangpur 20 MW 132 kV Ckt | 2022-09-18 10:10 | 2022-09-18 10:10 | 0:00 | S/O | Due to maint. work | 0 | 0 | No interruption
Bogura | Bogura-Sirajganj 230 kV Ckt-2 | 2022-09-21 06:16 | 2022-09-21 08:28 | 2:12 | S/O | Due to C/M work | 0 | 0 | No interruption
| Bogura-Naogaon 132 kV Ckt-2 | 2022-09-26 11:45 | 2022-09-26 14:34 | 2:49 | S/O | Due to C/M work | 0 | 0 | No interruption
| Bogura-Natore 132 kV Ckt-1 | 2022-09-26 14:50 | 2022-09-26 14:50 | 0:00 | S/O | Due to CT check | 0 | 0 | No interruption
Natore | Natore-Ishurdi 132 kV Ckt-1 | 2022-09-27 08:14 | 2022-09-27 15:09 | 6:55 | S/O | Due to C/M work | 0 | 0 | No interruption
| Natore-Ishurdi 132 kV Ckt-1 | 2022-09-28 09:00 | 2022-09-28 11:26 | 2:26 | S/O | Due to D/W work | 0 | 0 | No interruption
Rohanpur | Rohanpur-C.nawabganj 132 kV Ckt | 2022-09-29 11:15 | 2022-09-29 13:39 | 2:24 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 36:02 |  | Unserved Energy: |  | 269
Others :
Ullon | Ullon-Dhanmondi 132 kV Ckt-2 | 2022-09-17 09:14 | 2022-09-17 14:00 | 4:46 | S/O | Due to C/M work | 0 | 0 | No interruption
| Ullon-Dhanmondi 132 kV Ckt-1 | 2022-09-24 09:30 | 2022-09-24 21:58 | 12:28 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 17:14 |  | Unserved Energy: |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 386:17 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month:September 2022
| Area | Previous Month (August' 2022) |  |  |  | Current Month (September '2022)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 22 | 3 | 72 | 97 | 15 | 6 | 37 | 58
2 | Dhaka (South) Grid Circle. | 12 | 8 | 44 | 64 | 9 | 7 | 34 | 50
3 | Chattogram Grid Circle. | 15 | 4 | 24 | 43 | 30 | 4 | 38 | 72
4 | Cumilla Grid Circle. | 23 | 4 | 35 | 62 | 23 | 8 | 33 | 64
5 | Khulna Grid Circle. | 20 | 11 | 46 | 77 | 22 | 10 | 47 | 79
6 | HVDC Grid Circle | 9 | 4 | 15 | 28 | 10 | 6 | 16 | 32
7 | Bogura Grid Circle. | 14 | 12 | 45 | 71 | 24 | 10 | 57 | 91
8 | Others | 9 | 0 | 2 | 11 | 8 |  | 2 | 10
9 | Total | 124 | 46 | 283 | 453 | 141 | 51 | 264 | 456
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month:September 2022
| Area | Previous Month (August' 2022) |  |  |  | Current Month (September '2022)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 287.68 | 186.67 | 33 | 507.35 | 620.73 | 248 | 345.73 | 1214.46
2 | Dhaka (South) Grid Circle. | 118.4 | 175.33 |  | 293.73 | 588.37 | 382.08 | 138.3 | 1108.75
3 | Chattogram Grid Circle. | 160.17 | 94.5 | 202 | 456.67 | 609.76 | 9.75 | 231.7 | 851.21
4 | Cumilla Grid Circle. | 252.55 | 60.62 | 323.82 | 636.99 | 118.67 | 374.42 | 352.9 | 845.99
5 | Khulna Grid Circle. | 93.99 | 279.62 | 533.63 | 907.24 | 254.52 | 247.28 | 146 | 647.8
6 | HVDC Grid Circle | 77.15 | 60.9 | 142 | 280.05 |  | 182.75 | 342.82 | 525.57
7 | Bogura Grid Circle. | 85.61 | 268.75 | 489.73 | 844.09 | 537.53 | 258.8 | 1707.42 | 2503.75
8 | Others | Energy unserved ( MWH ) due to Total: 0; Energy unserved ( MWH ) due to Total: 0
9 | Total | 1075.55 | 1126.39 | 1724.18 | 3926.12 | 2729.58 | 1703.08 | 3264.87 | 7697.53
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-29
Page: 1/1 | [9 empty] | QF-LDC-29
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month:September 2022
A) Power Interruption
SL. | Name of | Total Capacity | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of the Sub-Station |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Dhaka (North) | 8801.6 | 8 | 6 | 15 | 2 | 1 | 12 | 912.13
2 | Dhaka (South) | 5031.6 | 7 | 2 | 9 | 0 | 3 | 6 | 581.88
3 | Chattogram | 2042 | 7 | 2 | 9 | 2 | 3 | 4 | 531.95
4 | Khulna | 2434 | 10 | 6 | 16 | 3 | 3 | 10 | 470.45
5 | HVDC | 5954.3 | 4 | 6 | 10 | 0 | 2 | 8 | 525.57
6 | Bogura | 3145.6 | 10 | 6 | 16 | 3 | 2 | 11 | 1829.75
7 | Cumilla | 2981 | 11 | 7 | 18 | 5 | 3 | 10 | 837.15
8 | Others | - | - | - | - | - | - | - | 0
| Total | 30390.1 | [6 empty] | 5688.88
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 99.96%
2 | Dhaka (South) | 99.97%
3 | Chattogram | 99.89%
4 | Khulna | 99.87%
5 | HVDC | 99.87% | [6 empty] | Executive Engineer
6 | Bogura | 99.98% | [6 empty] | Information Management Division
7 | Cumilla | 99.87% | [6 empty] | LDC, PGCB, Dhaka.

## QF-LDC-30
Page: 1/1 | [10 empty] | QF-LDC-30
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month:September 2022
A) Power Interruption
SL. | Name of | Total length | No. of Section in | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of Transmission line | the Transmission |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | (Ckt-KM) | Line | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 2254.4715 | - | 1 | 1 | 2 | 1 | - | 1 |  | 302.33
2 | Dhaka (South) | 990.29 |  | 2 |  | 2 | 2 | - | - | - | 526.87
3 | Chattogram | 917 | - | 4 | - | 4 | 1 | 1 | 2 | - | 319.27
4 | Khulna | 1238.4 | - | 2 |  | 2 | 1 | 1 | - | - | 177.35
5 | HVDC | 1325 | - | - | - | - | - | - | - | - | -
6 | Bogura | 1803.3 | - | 3 | 2 | 5 | 1 | 2 | 2 | - | 674
7 | Cumilla | 1648.16 | - | 3 |  | 3 | 2 | 1 | - | - | 8.8333
8 | Others | - |  |  | - | - | - | - | - | - | -
| Total | 10176.6215 | [8 empty] | 2008.6533
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 99.98%
2 | Dhaka (South) | 99.96%
3 | Chattogram | 99.92%
4 | Khulna | 99.81%
5 | Bheramara (HVDC) | 99.76% | [7 empty] | Executive Engineer
6 | Bogura | 98.73% | [7 empty] | Information Management Division
7 | Cumilla | 99.92% | [7 empty] | LDC, PGCB, Dhaka.

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month:September 2022
Type of | Power failure due to | [7 empty] | Partial |  | Total Grid failure
fault | Trouble In |  | Trouble In Grid S/S |  | Trouble In |  | Lightning in |  | Grid failure |  |  |  | Remarks
| Generation |  | Equipment |  | Transmission Line |  | Transmission Line/Thunder Storm
Period | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration
| No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min.
2022-09-01 | 8 | - | 6 | 11hr56 min | 1 | 53 min | - | - | - | - | - | - | -
* Tripping of a generator is accounted in the category "Trouble in Generation ". Not all tripping cause power interruption.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-32
Page: 1/2 |  |  |  |  | QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the Systems
Month:September 2022
| Total Nos.of | Total | Unserved | Total | Remarks
Sub-station | Interruption | Duration of | Load | Unserved
|  | Interruption | (MW) | Energy
|  | Hrs./Mins. |  | (MWH)
Kabirpur | 1 | 1:31 | 120 | 182 | Due to red-hot maint.of 132/33 kV transformer T-2 with 33 kV Bus
Jamalpur | 1 | 1:57 | 30 | 58.5 | Due to red-hot maint 132/33 kV Transformer T2
Savar | 1 | 0:08 | 90 | 12 | Due to tripping of 132/33 kV transformersT 1 & T2
Tangail | 1 | 3:08 | 58 | 181.7333 | Due to tripping of 132/33 kV transformerT 2
Netrakona | 1 | 0:42 | 25 | 17.5 | Due to tripping of 132/33 kV transformerT 3
Kodda | 1 | 1:54 | 20 | 38 | Due to red-hot maint 132/33 kV Transformer T1 with 33 kV Bus
Kishoreganj | 1 | 1:01 | 60 | 61 | Due to red-hot maint 132/33 kV Transformer T2
Kabirpur | 2 | 0:19 | 63 | 19.95 | Due to tripping of 132/33 kV transformerT1
|  | 1:29 | 87 | 129.05 | Due to tripping of 132/33 kV transformerT3
Kaliakoir | 1 | 0:16 | 600 | 160 | Due to tripping of Kaliakoir-Tangail 132 kV Ckt-1 & 2
Joydevpur | 1 | 0:09 | 60 | 9 | Due to tripping of Joydevpur-Kodda 132 kV Ckt-2
Jamalpur | 1 | 2:34 | 10 | 25.6667 | Due to S/D of 132/33 kV transformer T3
Tangail | 1 | 2:19 | 35 | 81.0833 | Due to S/D of 132/33 kV transformer T1
Jamalpur | 1 | 1:21 | 13 | 17.55 | Due to S/D of 132/33 kV transformer T3
| 1 | 1:18 | 22 | 28.6 | Due to S/D of 132/33 kV transformer T1
Dhamrai | 1 | 2:06 | 20 | 42 | Due to S/D of 132/33 kV transformer T1
Kabirpur | 1 | 1:45 | 10 | 17.5
Kabirpur | 1 | 1:20 | 100 | 133.3333 | Due to S/D of Tangail-Kaliakoir 132 kV Ckt-2
Sonargaon | 2 | 1:37 | 20 | 32.3333 | Due to red-hot maint 132/33 kV Transformer T1
|  | 1:47 | 25 | 44.5833
Ghorashal | 1 | 6:46 | 30 | 203
Bhulta | 1 | 0:57 | 50 | 47.5
Haripur SBU | 1 | 0:41 | 90 | 61.5 | Due to 33 kV feeder fault
Bhulta | 1 | 0:55 | 40 | 36.6667 | Due to red-hot maint 132/33 kV Transformer T1
Sreenagar | 1 | 1:12 | 15 | 18
Ghorashal | 1 | 0:22 | 1246 | 456.8667 | Due to tripping of Ghorashal-Ishurdi all 230 kV Ckt-2
Haripur | 1 | 0:20 | 210 | 70 | Due to ntripping of Haripur-Bhulta 132 kV Ckt
Kamrangirchar | 1 | 5:42 | 20 | 114 | Due to S/D of 132/33 kV transformer T-2
Nawabganj | 1 | 1:21 | 18 | 24.3
T.k.chemical |  | 1:02 | 65 | 67.1667 | Due to tripping of Transformer 132/33 kV Transformer T1
Kalurghat | 1 | 1:00 | 120 | 120
Halishahar | 1 | 1:40 | 20 | 33.3333 | Due to tripping of Transformer 132/33 kV Transformer T3
Halishahar |  | 0:30 | 77 | 38.5 | Due to 33 kV feeder fault
Cox'sbazar |  | 0:39 | 15 | 9.75 | Due to red-hot maint 132/33 kV Transformer T2
Khulshi | 1 | 0:14 | 135 | 31.5 | Due to 33 kV feeder fault
Bakulia | 1 | 0:34 | 400 | 226.6667 | Due to tripping of Bakulia-Sikalbaha 132 kV Ckt-1 & 2
Juldah | 1 | 1:03 | 22 | 23.1 | Due to tripping of Juldah-Sikalbaha 132 kV Ckt
Sikalbaha | 1 | 0:22 | 180 | 66 | Due to tripping of Sikalbaha-Dohazari 132 kV both Ckts
Dohazari | 2 | 5:21 | 180 | 3.5 | Due to tripping of Dohazari-Sikalbaha 132 kV Ckt-1
|  | 1:17 | 54 | 69.3 | Due to S/D of 132/33 kV transformers T-1 & T2 with 33 kV Bus
Halishahar | 1 | 0:55 | 70 | 64.1667 | Due to S/D of 132/33 kV transformersT-2 & T3
G.K | 1 | 7:01 | 14 | 98.2333 | Due to S/D of 132/33 kV transformerT-2 & 33 KV Bus
Ramganj | 2 | 0:47 | 30 | 23.5 | Due to S/D of 132/33 kV transformerT-2 with 33 kV Bus-2
|  | 0:44 | 30 | 22 | Due to 33 kV feeder fault
Shahjibazar | 1 | 0:13 | 19 | 4.1167
Shahjibazar | 1 | 1:19 | 45 | 59.25 | Due to tripping of Transformer 132/33 kV Transformer T4
Feni | 1 | 1:40 | 21 | 35 | Due to red-hot maint 132/33 kV Transformer T1
Ramganj | 1 | 10:35 | 20 | 211.6667 | Due to red-hot maint 132/33 kV Transformer T1 with 33 kV Bus
Sreemongal | 1 | 0:04 | 37 | 2.4667 | Due to 33 kV feeder fault
Chowmuhani | 1 | 0:24 | 20 | 8
Ramganj | 1 | 1:53 | 15 | 28.25 | Due to red-hot maint.of 132/33 kV Transformer T2
Sreemongal | 1 | 2:17 | 20 | 14 | Due to tripping of 132/33 kV transformers T-2 & T3
B.Baria | 1 | 0:57 | 80 | 76 | Due to red-hot manit.of 132/33 kV transformer T-2
Sylhet |  | 0:07 | 10 | 1.1667 | Due to tripping of Sylhet-Chattak 132 kV Ckt-1
| 2 | 0:59 | 10 | 2.1667
Fenchuganj |  | 0:10 | 33 | 5.5 | Due to tripping of Fenchuganj-Sylhet 132 kV Ckt-1
Feni | 1 | 2:42 | 33 | 89.1 | Due to S/D of 132/33 kV transformer T-1
Beanibazar | 1 | 2:12 | 45 | 99 | Due to S/D of 132/33 kV Transformer T1 & T2
Feni | 1 | 1:33 | 35 | 54.25 | Due to S/D of 132/33 kV transformers T2 with 33 kV Bus
Chowmuhani | 1 | 1:40 | 10 | 16.6667 | Due to S/D of132/33 kV transformer T3
Shahjibazar | 1 | 0:47 | 35 | 27.4167 | Due to S/D of132/33 kV transformer T4
Cumilla(S) | 1 | 4:54 | 12 | 58.8 | Due to S/D of132/33 kV transformer T2
Page: 2/2 |  |  |  |  | QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the Systems
Month:September 2022
| Total Nos.of | Total | Unserved | Total | Remarks
Sub-station | Interruption | Duration of | Load | Unserved
|  | Interruption | (MW) | Energy
|  | Hrs./Mins. |  | (MWH)
Chowmuhani | 1 | 0:23 | 20 | 7.6667 | Due to S/D of132/33 kV transformer T3
Shariatpur | 1 | 1:24 | 10 | 14
Chuadanga | 1 | 1:47 | 40 | 71.3333 | Due to red-hot maint by PBS
Faridpur | 1 | 0:26 | 82 | 35.5333 | Due to bursting of L/A
Narail | 1 | 1:46 | 20 | 35.3333 | Due to bursting of PT
Shariatpur | 1 | 0:46 | 35 | 26.8333 | Due to tripping of 132/33 kV transformers T-1 & T2
Satkhira | 1 | 0:39 | 20 | 13 | Due to red-hot maint.of 132/33 kV transformer T-1
Narail | 1 | 1:30 | 28 | 42 | Due to tripping of 132/33 kV transformers T-1 & T2
Chuadanga | 1 | 1:10 | 35 | 40.8333 | Due to red-hot maint.of 132/33 kV transformers T-2 & T3
Barisal(S) | 1 | 2:29 | 15 | 37.25 | Due to red-hot maint.of 132/33 kV transformer T-2
Mongla | 1 | 0:25 | 20 | 8.3333 | Due to tripping 132/33 kV transformers T1 & T2
Payra P/P | 1 | 0:11 | 156 | 28.6 | Due to tripping of Payra P/P-Payra S/S 400 kV Ckt
Khulna© | 1 | 0:59 | 119 | 148.75 | Due to tripping of Khulna©-Goalpara 132 kV Ckt-1
Napara | 1 | 0:25 | 10 | 4.1667 | Due to S/D of 132/33 kV transformer T1 with 33 kV Bus
Faridpur | 1 | 1:21 | 33 | 44.55
Narail | 2 | 3:09 | 15 | 47.25 | Due to S/D of 132/33 kV transformer T1
|  | 1:17 | 13 | 16.6833 | Due to S/D of 132/33 kV transformer T2
Noapara | 2 | 1:19 | 15 | 19.75 | Due to S/D of 132/33 kV transformer T2
|  | 0:34 | 24 | 13.6 | Due to S/D of 132/33 kV transformer T4
Bottail | 1 | 1:45 | 30 | 52.5 | Due to red-hot maint.of 132/33 kV transformer T2
Jhenidah(old) | 1 | 2:09 | 30 | 64.5
Bottail | 1 | 1:26 | 30 | 43
Jhenidah(old) | 1 | 1:31 | 15 | 22.75
Jhenaidah | 1 | 2:09 | 75 | 161.25 | Due to S/D of 132/33 kV transformer T1
Bottail | 1 | 1:26 | 48 | 68.8 | Due to S/D of 132/33 kV transformer T2
Jashore | 1 | 1:31 | 24 | 36.4 | Due to S/D of 132/33 kV transformer T3
Bottail | 1 | 0:54 | 30 | 27 | Due to S/D of 132/33 kV transformer T1
Benapole | 1 | 0:41 | 20 | 13.6667
Jhenaidah(O) | 1 | 1:59 | 18 | 35.7 | Due to S/D of 132/33 kV transformer T2
Purbasadipur | 1 | 0:15 | 75 | 18.75 | Due to tripping of 132/33 kV transformers T1 & T2
Bogura | 1 | 1:18 | 60 | 78 | Due to red-hot maint.of 132/33 kV transformers T3 & T4
Bogura | 1 | 0:36 | 45 | 27 | Due to tripping of 132/33 kV transformers T1 & T2
Jaldhaka | 1 | 1:02 | 22 | 22.7333 | Due to red-hot maint of 33 kV Bus-2
Purbasadipur | 2 | 0:13 | 88 | 19.0667 | Due to tripping of 132/33 kV transformers T1 & T2
| 1 | 0:34 | 70 | 39.6667 | Due to tripping of 132/33 kV transformers T1 & T2
Natore | 1 | 1:03 | 50 | 52.5 | Due to red-hot maint.of 132/33 kV transformers T1 & T2
Purbasadipur | 1 | 0:12 | 30 | 6 | Due to tripping of 132/33 kV transformer T3
Rajshahi(N) | 1 | 1:52 | 31 | 57.8667 | Due to red-hot maint.of 132/33 kV transformer T2 with 33 kV Bus
Thaurgaon | 1 | 1:33 | 45 | 69.75 | Due to tripping of Thaurgaon-Panchagarh 132 kV Ckt
Bogura | 1 | 1:29 | 186 | 275.9 | Due to tripping of Bogura-Naogaon 132 kV Ckt-1
| 1 | 0:33 | 148 | 81.4 | Due to tripping of Bogura-Naogaon 132 kV Ckt-2
Rajshahi(N) | 1 | 0:53 | 54 | 47.7 | Due to bursting of PT
Naogaon | 1 | 3:00 | 55 | 165 | Due to S/D of 132 kV main Bus
| 1 | 0:21 | 40 | 14 | Due to S/D of 132/33 kV transformer T2
Purbasdipur | 1 | 3:46 | 195 | 734.5 | Due to S/D of132 kV Bus
Bogura | 1 | 2:21 | 25 | 58.75 | Due to S/D of 132/33 kV transformer T1
Bogura(O) | 1 | 2:57 | 60 | 177 | Due to S/D of 132/33 kV transformers T1 & T2
Mosathangar | 1 | 2:30 | 45 | 112.5 | Due to S/D of 33 kV Bus
Purbasadipur | 1 | 4:25 | 40 | 176.6667 | Due to S/D of 132/33 kV transformer T1
Naogaon | 1 | 2:59 | 90 | 268.5 | Due to S/D of Naogaon-Bogura 132 kV Ckt-1
Bogura | 1 | 0:03 | 10 | 0.5 | Due to S/d of Bogura-Bakerganj 132 kV Ckt
| Total Unserved energy : |  |  | 7697.0333 | MWH
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-33
Page: 1/3 |  |  | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month: September '2022
Sl. No | Sub-station | Load (MW) | Time
1 | AKS | 14 | 2022-09-09 03:00
2 | AKSML | 184 | 2022-09-30 00:00
3 | Aftabnagar | 35 | 2022-09-01 16:00
4 | Agargaon | 122 | 2022-09-16 00:00
5 | Agrabad | 92 | 2022-09-18 19:00
6 | Amnura | 66 | 2022-09-17 21:00
7 | Ashuganj | 89 | 2022-09-26 23:00
8 | BSRM | 170 | 2022-09-06 12:00
9 | Bagerhat | 107 | 2022-09-08 20:00
10 | Bakulia | 139 | 2022-09-28 19:30
11 | Banani | 66 | 2022-09-01 14:00
12 | Bangabhaban | 22 | 2022-09-01 10:00
13 | Barapukuria | 59 | 2022-09-07 20:00
14 | Barguna | 22 | 2022-09-06 19:30
15 | Barishal | 118 | 2022-09-06 20:00
16 | Barishal-230 | 86 | 2022-09-08 22:00
17 | Baroaulia | 76 | 2022-09-08 12:00
18 | Baroirhat | 62 | 2022-09-29 20:00
19 | Bashundhara | 181 | 2022-09-19 18:30
20 | BashundharaCement | 12 | 2022-09-26 00:00
21 | Beanibazar | 86 | 2022-09-17 19:30
22 | Benapole | 62 | 2022-09-05 22:00
23 | Bhaluka | 162 | 2022-09-11 10:00
24 | Bhandaria | 58 | 2022-09-06 19:00
25 | Bhangura | 37 | 2022-09-03 19:30
26 | Bheramara(GK) | 66 | 2022-09-07 21:00
27 | Bhulta | 317 | 2022-09-12 15:00
28 | Bog-Sherpur | 62 | 2022-09-09 21:00
29 | Bogura | 172 | 2022-09-09 22:00
30 | Borhanuddin | 44 | 2022-09-03 23:00
31 | Brahmanbaria | 180 | 2022-09-09 23:00
32 | Cantonment | 156 | 2022-09-01 17:00
33 | Chandpur | 70 | 2022-09-01 22:00
34 | Chandraghona | 36 | 2022-09-03 18:30
35 | Chapai | 67 | 2022-09-08 22:00
36 | Charsaidpur | 49 | 2022-09-04 15:00
37 | Chauddagram | 67 | 2022-09-08 20:00
38 | Chhatak | 36 | 2022-09-09 21:00
39 | Chowmuhani | 238 | 2022-09-07 21:00
40 | Chuadanga | 113 | 2022-09-07 21:00
41 | Coxsbazar | 129 | 2022-09-08 19:00
42 | Cumilla(N) | 188 | 2022-09-01 22:00
43 | Cumilla(S) | 184 | 2022-09-10 18:30
44 | Daudkandi | 159 | 2022-09-07 20:00
45 | Dhaka | 50 | 2022-09-05 13:00
46 | Dhamrai | 128 | 2022-09-18 19:00
47 | Dhanmondi | 142 | 2022-09-05 13:00
48 | Dohazari | 108 | 2022-09-08 22:00
49 | Faridpur | 164 | 2022-09-01 22:00
50 | Fatullah | 77 | 2022-09-22 10:00
51 | Fenchuganj | 54 | 2022-09-18 18:30
52 | Feni | 124 | 2022-09-17 18:30
53 | GPH | 101 | 2022-09-10 14:00
Page: 2/3 |  |  | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month: September '2022
Sl. No | Sub-station | Load (MW) | Time
54 | Ghorashal | 78 | 2022-09-07 22:00
56 | Goalpara | 29 | 2022-09-08 13:00
57 | Gollamari | 56 | 2022-09-06 12:00
58 | Gopalganj | 109.2 | 2022-09-01 19:00
59 | Gulshan | 136 | 2022-09-08 16:00
60 | Halishahar | 98 | 2022-09-28 09:00
61 | HaripurSBU | 173 | 2022-09-05 10:00
62 | Hasnabad | 106 | 2022-09-01 16:00
63 | Hathazari | 105 | 2022-09-08 19:00
64 | Ishurdi | 81 | 2022-09-03 19:00
65 | Jaldhaka | 76 | 2022-09-02 19:00
66 | Jamalpur | 152 | 2022-09-15 19:00
67 | Jashore | 142 | 2022-09-19 18:30
68 | Jhenaidah | 135 | 2022-09-03 19:00
69 | Joydebpur | 290 | 2022-09-21 12:00
70 | Joypurhat | 62 | 2022-09-07 23:00
71 | Juldah | 32 | 2022-09-17 12:00
72 | KSRM | 53 | 2022-09-26 08:00
73 | Kabirpur | 301 | 2022-09-05 09:00
74 | Kachua | 82 | 2022-09-08 22:00
75 | Kallyanpur | 120 | 2022-09-30 18:00
76 | Kalurghat | 34 | 2022-09-05 12:00
77 | Kamrangirchar | 63 | 2022-09-01 18:30
78 | Kaptai | 10 | 2022-09-02 14:00
79 | Kazla | 97 | 2022-09-07 11:00
80 | Keranigonj | 99 | 2022-09-19 16:00
81 | Khagrachori | 32 | 2022-09-07 18:30
82 | Khulna | 106 | 2022-09-29 19:00
83 | Khulshi | 205 | 2022-09-22 15:00
84 | Kishoreganj | 148 | 2022-09-01 22:00
85 | Kodda | 346 | 2022-09-15 14:00
86 | Kulaura | 56 | 2022-09-30 19:30
87 | Kurigram | 72 | 2022-09-17 19:00
88 | Kushtia | 148 | 2022-09-01 20:00
89 | Lalbag | 104 | 2022-09-17 13:00
90 | Lalmonirhat | 52 | 2022-09-11 19:00
91 | Madanganj | 102 | 2022-09-11 15:00
92 | Madaripur | 115 | 2022-09-01 23:00
93 | Madartek | 98 | 2022-09-01 00:00
94 | Madunaghat | 73 | 2022-09-08 19:00
95 | Magura | 66 | 2022-09-03 19:00
96 | Mahasthangarh | 86 | 2022-09-17 19:00
97 | Manikganj | 95 | 2022-09-18 20:00
98 | Maniknagar | 83 | 2022-09-07 12:00
99 | Matarbari | 43 | 2022-09-03 21:00
100 | Matuail | 68 | 2022-09-24 16:00
101 | Millgate | 72 | 2022-09-28 16:00
101 | Mirpur | 145 | 2022-09-30 18:00
102 | Mirsorai | 4 | 2022-09-08 21:00
Page: 3/3 |  |  | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month: September '2022
Sl. No | Sub-station | Load (MW) | Time
103 | Mithapukur | 36 | 2022-09-18 18:30
104 | Modern | 0 | 2022-09-01 00:00
105 | Mogbazar | 142 | 2022-09-05 11:00
106 | Mongla | 40 | 2022-09-08 09:00
107 | Motijheel | 39 | 2022-09-05 13:00
108 | Munshiganj | 124 | 2022-09-04 23:00
109 | Mymensingh | 241 | 2022-09-18 00:00
110 | Naogaon | 131 | 2022-09-03 21:00
111 | Narail | 48 | 2022-09-03 22:00
112 | Narinda | 80 | 2022-09-05 13:00
113 | Narshingdi | 190 | 2022-09-18 20:00
114 | Natore | 145 | 2022-09-09 21:00
115 | Nawabganj | 57.2 | 2022-09-09 21:00
116 | Netrakona | 129 | 2022-09-23 20:00
117 | New | 86 | 2022-09-01 16:00
118 | Niamatpur | 84 | 2022-09-03 20:00
119 | Noapara | 57 | 2022-09-03 19:00
120 | PHP | 10 | 2022-09-23 22:00
121 | Pabna | 116 | 2022-09-03 21:00
122 | Palashbari | 133 | 2022-09-06 19:30
123 | Panchagarh | 73 | 2022-09-19 19:00
124 | Patuakhali | 138 | 2022-09-07 22:00
125 | Payra | 1.07 | 2022-09-09 11:00
126 | Postogola | 47 | 2022-09-01 00:00
127 | Purbachal | 20 | 2022-09-23 15:00
128 | Purbasadipur | 117 | 2022-09-10 19:00
129 | Rahanpur_I | 10 | 2022-09-24 18:00
130 | Rahim | 33 | 2022-09-02 09:00
131 | Rajbari | 74 | 2022-09-28 21:00
132 | Rajendrapur | 108 | 2022-09-18 20:00
133 | Rajshahi | 164 | 2022-09-10 22:00
134 | Rajshahi-230 | 40 | 2022-09-23 00:00
135 | Ramganj | 120 | 2022-09-01 21:00
136 | Rampur | 39 | 2022-09-08 20:00
137 | Rangamati | 18 | 2022-09-07 18:30
138 | Rangpur | 166 | 2022-09-20 19:00
139 | Ruppur | 5.4 | 2022-09-01 10:00
140 | SSM | 18 | 2022-09-13 10:00
141 | Saidpur | 115 | 2022-09-18 21:00
142 | Satkhira | 131 | 2022-09-01 21:00
143 | Satmasjid | 107 | 2022-09-01 00:00
144 | Savar | 205 | 2022-09-03 13:00
145 | Shahjadpur | 114 | 2022-09-04 20:00
146 | Shahjibazar | 140 | 2022-09-09 03:00
147 | Shahmirpur | 54.5 | 2022-09-07 19:00
148 | Shariatpur | 82 | 2022-09-08 22:00
149 | Sherpur | 154 | 2022-09-09 22:00
150 | Shikalbaha | 34 | 2022-09-09 19:30
151 | Shikalbaha-230 | N/A | N/A
152 | Shitalakhya | 141 | 2022-09-26 18:30
153 | Sholosohor | N/A | N/A
154 | Shyampur | 176 | 2022-09-22 10:00
155 | Siddhirganj | 122 | 2022-09-08 16:00
156 | Sirajganj | 116 | 2022-09-04 20:00
157 | Sonargaon | 117 | 2022-09-19 22:00
158 | Sreemongol | 72 | 2022-09-18 19:30
159 | Srinagar | 47.67 | 2022-09-01 21:00
160 | Sunamganj | 58 | 2022-09-19 22:00
161 | Sylhet | 170 | 2022-09-08 20:00
162 | TK | 33.2 | 2022-09-28 18:00
163 | Tangail | 236 | 2022-09-09 22:00
164 | Thakurgaon | 92 | 2022-09-05 19:00
165 | Tongi | 138 | 2022-09-23 12:00
166 | Ullon | 54 | 2022-09-29 18:00
167 | Uttara | 100 | 2022-09-01 16:00
168 | UttaraNew | 45 | 2022-09-10 13:00
169 | Zigatola | 71 | 2022-09-01 19:00
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID COMPANY OF BANGLADESH LTD. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month:September 2022
Area | MW | Date | Hour | Remarks
Dhaka | 4921.59 | 2022-05-09 | 11:00
Chattogram | 1514.36 | 25/09/2022 | 18:00
Cumilla | 1392 | 2022-08-09 | 22:00
Mymensingh | 1057 | 18/09/2022 | 2:00
Sylhet | 594 | 19/09/2022 | 22:00
Khulna | 1745.2 | 2022-07-09 | 21:00
Barishal | 441.79 | 2022-08-09 | 22:00
Rajshahi | 1436.2 | 2022-09-09 | 22:00
Rangpur | 948 | 2022-10-09 | 19:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-35
| Page: 1/3 | [5 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: September '2022
SL. | 400 KV Substation | Rated | Maxm |  | Minm | Date and Time
No. |  | Voltage | Voltage | Date and Time | Voltage |  | Remarks
|  | kV | kV |  | kV
1 | Bhulta | 400 | 390 | 2022-09-08 06:00 | 73 | 2022-09-28 00:00
2 | Bibiana | 400 | 403 | 2022-09-06 19:00 | 387 | 2022-09-19 16:00
3 | BIPTC | 400 | 407 | 2022-09-06 09:00 | 390 | 2022-09-27 18:30
4 | Gopalganj_I | 400 | 426 | 2022-09-06 18:30 | 318 | 2022-09-06 11:00
5 | Kaliakoir | 400 | 390 | 2022-09-02 03:00 | 277 | 2022-09-02 18:00
6 | Payra | 400 | 422 | 2022-09-12 09:00 | 401 | 2022-09-19 21:00
7 | Rahanpur_I | 400 | 417 | 2022-09-29 09:00 | 370 | 2022-09-24 18:30
|  | Rated | Maxm |  | Minm | Date and Time
SL. | Substation | Voltage | Voltage | Date and Time | Voltage |  | Remarks
No. | 230 KV Substation | kV | kV |  | kV
1 | Agargaon | 230 | 232 | 2022-09-28 07:00 | 209 | 2022-09-17 10:00
2 | AKSML | 230 | 238 | 2022-09-09 04:00 | 222 | 2022-09-15 05:00
3 | Aminbazar | 230 | 233 | 2022-09-24 19:30 | 222 | 2022-09-13 00:00
4 | Ashuganj | 230 | 239 | 2022-09-06 19:00 | 211 | 2022-09-01 05:00
5 | Baghabari | 230 | 235 | 2022-09-06 10:00 | 224 | 2022-09-09 21:00
6 | Barapukuria | 230 | 225 | 2022-09-03 17:00 | 211 | 2022-09-07 00:00
7 | Barishal | 230 | 248 | 2022-09-18 09:00 | 190 | 2022-09-06 11:00
8 | Bheramara | 230 | 258 | 2022-09-28 19:30 | 226 | 2022-09-19 02:00
9 | Bhulta | 230 | 228 | 2022-09-05 06:00 | 213 | 2022-09-17 10:00
10 | Bibiana | 230 | 238 | 2022-09-01 19:30 | 226 | 2022-09-13 12:00
11 | BIPTC | 230 | 237 | 2022-09-11 17:00 | 227 | 2022-09-22 05:00
12 | Bogura | 230 | 257 | 2022-09-07 07:00 | 222 | 2022-09-15 21:00
13 | Borhanuddin | 230 | 250 | 2022-09-13 06:00 | 228 | 2022-09-12 14:00
14 | BSRM | 230 | 235 | 2022-09-26 11:00 | 206 | 2022-09-01 05:00
15 | Cumilla(N) | 230 | 230 | 2022-09-09 03:00 | 215 | 2022-09-01 09:00
16 | Fenchuganj | 230 | 240 | 2022-09-01 19:00 | 232 | 2022-09-22 18:00
17 | Ghorashal | 230 | 239 | 2022-09-06 19:00 | 211 | 2022-09-01 05:00
18 | GPH | 230 | 238 | 2022-09-18 08:00 | 207 | 2022-09-02 05:00
19 | Haripur | 230 | 226 | 2022-09-26 20:00 | 212 | 2022-09-29 16:00
20 | Hasnabad | 230 | 233 | 2022-09-03 04:00 | 214 | 2022-09-21 07:00
21 | Hathazari | 230 | 238 | 2022-09-19 21:00 | 228 | 2022-09-01 18:00
22 | Ishurdi | 230 | 237 | 2022-09-03 07:00 | 223 | 2022-09-14 06:00
23 | Jhenaidah | 230 | 235 | 2022-09-06 10:00 | 218 | 2022-09-07 22:00
24 | Kaliakoir | 230 | 227 | 2022-09-12 06:00 | 215 | 2022-09-17 02:00
25 | Keranigonj | 230 | 225 | 2022-09-26 20:00 | 208 | 2022-09-17 10:00
26 | Khulna(S) | 230 | 253 | 2022-09-20 01:00 | 225 | 2022-09-07 20:00
27 | Maniknagar | 230 | 226 | 2022-09-07 06:00 | 221 | 2022-09-19 16:00
28 | Meghnaghat | 230 | 230 | 2022-09-03 04:00 | 226 | 2022-09-27 17:00
29 | Mirsorai | 230 | 235 | 2022-09-24 09:00 | 205 | 2022-09-09 00:00
30 | Rajshahi | 230 | 238 | 2022-09-29 06:00 | 219 | 2022-09-17 23:00
31 | Rampur | 230 | N/A | N/A | N/A | N/A
32 | Rampura | 230 | 226 | 2022-09-06 18:30 | 222 | 2022-09-13 23:00
33 | Shahmirpur | 230 | 240 | 2022-09-11 21:00 | 221 | 2022-09-01 12:00
34 | Shikalbaha | 230 | 240 | 2022-09-23 09:00 | 216 | 2022-09-18 21:00
35 | Shyampur | 230 | 226 | 2022-09-26 20:00 | 132 | 2022-09-12 18:00
36 | Siddhirganj | 230 | 228 | 2022-09-26 20:00 | 222 | 2022-09-13 18:30
37 | Sirajgonj | 230 | 258 | 2022-09-13 22:00 | 223 | 2022-09-19 05:00
38 | Tongi | 230 | 233 | 2022-09-24 20:00 | 221 | 2022-09-11 19:00
QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: September '2022
|  | Rated | Maxm |  | Minm | Date and Time
SL. | Substation | Voltage | Voltage | Date and Time | Voltage |  | Remarks
No. | 132 KV Substation | kV | kV |  | kV
1 | Aftabnagar | 132 | 139 | 2022-09-12 02:00 | 127 | 2022-09-17 10:00
2 | Agargaon | 132 | 139 | 2022-09-09 04:00 | 125 | 2022-09-26 03:00
3 | Agrabad | 132 | 139 | 2022-09-11 21:00 | 121 | 2022-09-01 08:00
4 | AKS | 132 | 137 | 2022-09-06 09:00 | 120 | 2022-09-01 10:00
5 | Aminbazar | 132 | 138 | 2022-09-14 22:00 | 108 | 2022-09-27 18:30
6 | Amnura | 132 | 137 | 2022-09-13 19:30 | 117 | 2022-09-16 18:00
7 | Ashuganj | 132 | 138 | 2022-09-06 19:00 | 130 | 2022-09-04 17:00
8 | Bagerhat | 132 | 139 | 2022-09-12 17:00 | 120 | 2022-09-06 11:00
9 | Bakulia | 132 | 140 | 2022-09-17 19:00 | 120 | 2022-09-01 10:00
10 | Banani | 132 | 136 | 2022-09-02 12:00 | 123 | 2022-09-01 10:00
11 | Bangabhaban | 132 | 135 | 2022-09-08 06:00 | 129 | 2022-09-18 18:00
12 | Barapukuria | 132 | 138 | 2022-09-03 17:00 | 120 | 2022-09-07 14:00
13 | Barguna | 132 | 141 | 2022-09-02 09:00 | 120 | 2022-09-06 13:00
14 | Barishal | 132 | 142 | 2022-09-02 09:00 | 120 | 2022-09-06 13:00
15 | Barishal-230 | 132 | 141 | 2022-09-03 09:00 | 108 | 2022-09-06 11:00
16 | Baroaulia | 132 | 141 | 2022-09-18 20:00 | 124 | 2022-09-01 10:00
17 | Baroirhat | 132 | 139 | 2022-09-18 05:00 | 117 | 2022-09-01 05:00
18 | Bashundhara | 132 | 136 | 2022-09-03 06:00 | 118 | 2022-09-22 06:00
19 | BashundharaCement | 132 | 137 | 2022-09-04 23:00 | 130 | 2022-09-28 05:00
20 | Beanibazar | 132 | 133 | 2022-09-05 09:00 | 112 | 2022-09-30 02:00
21 | Benapole | 132 | 138 | 2022-09-11 17:00 | 125 | 2022-09-23 21:00
22 | Bhaluka | 132 | 134 | 2022-09-04 05:00 | 107 | 2022-09-10 18:30
23 | Bhandaria | 132 | 142 | 2022-09-13 11:00 | 108 | 2022-09-03 03:00
24 | Bhangura | 132 | 139 | 2022-09-02 17:00 | 113 | 2022-09-15 06:00
25 | Bheramara | 132 | 137 | 2022-09-02 16:00 | 112 | 2022-09-18 00:00
26 | Bheramara(GK) | 132 | 140 | 2022-09-12 09:00 | 128 | 2022-09-06 14:00
27 | Bhulta | 132 | 131 | 2022-09-21 22:00 | 111 | 2022-09-04 01:00
28 | Bog-Sherpur | 132 | 139 | 2022-09-29 06:00 | 135 | 2022-09-30 02:00
29 | Bogura | 132 | 140 | 2022-09-29 05:00 | 110 | 2022-09-09 14:00
30 | Bogura-230 | 132 | 140 | 2022-09-29 06:00 | 129 | 2022-09-09 21:00
31 | Brahmanbaria | 132 | 135 | 2022-09-26 11:00 | 113 | 2022-09-05 10:00
32 | Cantonment | 132 | 137 | 2022-09-06 19:00 | 132 | 2022-09-02 13:00
33 | Chandpur | 132 | 140 | 2022-09-15 13:00 | 116 | 2022-09-04 00:00
34 | Chandraghona | 132 | 140 | 2022-09-18 20:00 | 125 | 2022-09-01 10:00
35 | Chapai | 132 | 137 | 2022-09-11 17:00 | 118 | 2022-09-24 08:00
36 | Charsaidpur | 132 | 135 | 2022-09-23 18:30 | 120 | 2022-09-05 02:00
37 | Chauddagram | 132 | 138 | 2022-09-18 05:00 | 118 | 2022-09-01 05:00
38 | Chhatak | 132 | 132 | 2022-09-03 06:00 | 129 | 2022-09-13 10:00
39 | Chowmuhani | 132 | 138 | 2022-09-06 19:00 | 116 | 2022-09-01 06:00
40 | Chuadanga | 132 | 138 | 2022-09-02 16:00 | 115 | 2022-09-07 20:00
41 | Coxsbazar | 132 | 131 | 2022-09-08 01:00 | 104 | 2022-09-01 18:00
42 | Cumilla(N) | 132 | 137 | 2022-09-09 03:00 | 113 | 2022-09-21 11:00
43 | Cumilla(S) | 132 | 138 | 2022-09-09 04:00 | 122 | 2022-09-01 05:00
44 | Daudkandi | 132 | 138 | 2022-09-09 19:00 | 121 | 2022-09-17 10:00
45 | Dhaka | 132 | 138 | 2022-09-04 03:00 | 126 | 2022-09-17 10:00
46 | Dhamrai | 132 | 138 | 2022-09-06 19:00 | 123 | 2022-09-09 21:00
47 | Dhanmondi | 132 | 133.5 | 2022-09-26 20:00 | 121.6 | 2022-09-17 10:00
48 | Dohazari | 132 | 139 | 2022-09-09 01:00 | 120 | 2022-09-28 14:00
49 | Faridpur | 132 | 135 | 2022-09-01 14:00 | 113 | 2022-09-22 08:00
50 | Fatullah | 132 | 138 | 2022-09-26 20:00 | 124 | 2022-09-17 10:00
51 | Fenchuganj | 132 | 136 | 2022-09-03 06:00 | 129 | 2022-09-08 10:00
52 | Feni | 132 | 140 | 2022-09-18 05:00 | 120 | 2022-09-01 04:00
53 | Ghorashal | 132 | 139 | 2022-09-06 18:30 | 124 | 2022-09-22 22:00
54 | Goalpara | 132 | 140 | 2022-09-12 16:00 | 111 | 2022-09-23 15:00
55 | Gollamari | 132 | 139 | 2022-09-09 17:00 | 123 | 2022-09-06 11:00
56 | Gopalganj | 132 | 139 | 2022-09-01 19:00 | 117 | 2022-09-06 11:00
57 | Gopalganj_I | 132 | 141 | 2022-09-03 09:00 | 114 | 2022-09-01 21:00
58 | Gulshan | 132 | 138 | 2022-09-08 06:00 | 126 | 2022-09-19 12:00
59 | Halishahar | 132 | 139 | 2022-09-11 21:00 | 121 | 2022-09-01 10:00
60 | Haripur | 132 | 133 | 2022-09-06 19:00 | 124 | 2022-09-13 12:00
61 | HaripurSBU | 132 | 142 | 2022-09-18 21:00 | 117 | 2022-09-10 11:00
| Page: 3/3 | [5 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: September '2022
Rated
SL. | Substation | Rated | Maxm |  | Minm | Date and Time
No. | 132 KV Substation | Voltage | Voltage | Date and Time | Voltage |  | Remarks
62 | Hasnabad | kV | kV |  | kV
63 | Hathazari | 132 | 140 | 2022-09-19 16:00 | 124 | 2022-09-01 10:00
64 | Ishurdi | 132 | 138 | 2022-09-03 06:00 | 113 | 2022-09-13 21:00
65 | Jaldhaka | 132 | 136 | 2022-09-03 17:00 | 113 | 2022-09-07 14:00
66 | Jamalpur | 132 | 141 | 2022-09-09 18:00 | 117 | 2022-09-10 19:00
67 | Jashore | 132 | 139 | 2022-09-04 12:00 | 113 | 2022-09-28 05:00
68 | Jhenaidah | 132 | 141 | 2022-09-02 17:00 | 125 | 2022-09-07 20:00
69 | Jhenaidah-230 | 132 | 141 | 2022-09-02 18:00 | 138 | 2022-09-29 06:00
70 | Joydebpur | 132 | 142 | 2022-09-06 18:30 | 124 | 2022-09-17 10:00
71 | Joypurhat | 132 | 136 | 2022-09-06 10:00 | 117 | 2022-09-09 22:00
72 | Juldah | 132 | 140 | 2022-09-11 21:00 | 120 | 2022-09-03 01:00
73 | Kabirpur | 132 | 140 | 2022-09-01 00:00 | 118 | 2022-09-01 18:00
74 | Kachua | 132 | 138 | 2022-09-13 19:00 | 113 | 2022-09-05 18:00
75 | Kaliakoir | 132 | 141 | 2022-09-01 00:00 | 115 | 2022-09-17 02:00
76 | Kallyanpur | 132 | 139 | 2022-09-17 21:00 | 112 | 2022-09-19 12:00
77 | Kalurghat | 132 | 140 | 2022-09-17 19:00 | 123 | 2022-09-01 11:00
78 | Kamrangirchar | 132 | 157 | 2022-09-30 07:00 | 128 | 2022-09-13 12:00
79 | Kaptai | 132 | 137 | 2022-09-05 13:00 | 125 | 2022-09-01 11:00
80 | Kazla | 132 | 138 | 2022-09-25 18:30 | 123 | 2022-09-01 01:00
81 | Keranigonj | 132 | 140 | 2022-09-05 19:00 | 109 | 2022-09-12 15:00
82 | Khagrachori | 132 | 139 | 2022-09-18 06:00 | 123 | 2022-09-01 09:00
83 | Khulna | 132 | 138 | 2022-09-09 17:00 | 122 | 2022-09-06 11:00
84 | Khulna(S) | 132 | 139 | 2022-09-12 17:00 | 126 | 2022-09-06 11:00
85 | Khulshi | 132 | 158 | 2022-09-03 16:00 | 120 | 2022-09-01 09:00
86 | Kishoreganj | 132 | 135 | 2022-09-26 11:00 | 119 | 2022-09-19 16:00
87 | Kodda | 132 | 142 | 2022-09-06 18:30 | 121 | 2022-09-17 10:00
88 | KSRM | 132 | 138 | 2022-09-06 18:30 | 121 | 2022-09-01 10:00
89 | Kulaura | 132 | 134 | 2022-09-03 06:00 | 128 | 2022-09-06 21:00
90 | Kurigram | 132 | 133 | 2022-09-06 09:00 | 114 | 2022-09-06 22:00
91 | Kushtia | 132 | 138 | 2022-09-02 17:00 | 126 | 2022-09-06 15:00
92 | Lalbag | 132 | 141 | 2022-09-26 20:00 | 125 | 2022-09-13 03:00
93 | Lalmonirhat | 132 | 134 | 2022-09-15 14:00 | 116 | 2022-09-18 20:00
94 | Madanganj | 132 | 134 | 2022-09-23 18:30 | 121 | 2022-09-17 10:00
95 | Madaripur | 132 | 139 | 2022-09-01 18:00 | 111 | 2022-09-01 08:00
96 | Madartek | 132 | 139 | 2022-09-08 06:00 | 127 | 2022-09-09 11:00
97 | Madunaghat | 132 | 140 | 2022-09-16 18:30 | 123 | 2022-09-01 10:00
98 | Magura | 132 | 140 | 2022-09-02 18:00 | 125 | 2022-09-07 21:00
99 | Mahasthangarh | 132 | 138 | 2022-09-03 17:00 | 115 | 2022-09-06 16:00
100 | Manikganj | 132 | 137 | 2022-09-10 12:00 | 124 | 2022-09-27 11:00
101 | Maniknagar | 132 | 135 | 2022-09-07 05:00 | 113 | 2022-09-17 00:00
102 | Matarbari | 132 | 135 | 2022-09-25 15:00 | 106 | 2022-09-01 23:00
103 | Matuail | 132 | 133 | 2022-09-26 20:00 | 113.3 | 2022-09-24 03:00
104 | Millgate | 132 | 138 | 2022-09-29 04:00 | 124 | 2022-09-01 09:00
105 | Mirpur | 132 | 138 | 2022-09-26 20:00 | 126 | 2022-09-07 02:00
106 | Mithapukur | 132 | 138 | 2022-09-17 09:00 | 127 | 2022-09-12 13:00
107 | Modern | 132 | 139 | 2022-09-11 21:00 | 121 | 2022-09-01 16:00
108 | Mogbazar | 132 | 140 | 2022-09-04 06:00 | 125 | 2022-09-19 18:30
109 | Mongla | 132 | 137 | 2022-09-12 10:00 | 120 | 2022-09-06 11:00
110 | Motijheel | 132 | 135 | 2022-09-08 06:00 | 113 | 2022-09-11 01:00
111 | Munshiganj | 132 | 134 | 2022-09-26 20:00 | 123 | 2022-09-13 12:00
112 | Mymensingh | 132 | 136 | 2022-09-04 01:00 | 112 | 2022-09-19 03:00
113 | Naogaon | 132 | 137 | 2022-09-29 05:00 | 119 | 2022-09-03 13:00
114 | Narail | 132 | 138 | 2022-09-05 15:00 | 121 | 2022-09-07 20:00
115 | Narinda | 132 | 0 | 2022-09-01 00:00 | N/A | N/A
116 | Narshingdi | 132 | 130 | 2022-09-17 20:00 | 112 | 2022-09-29 01:00
117 | Natore | 132 | 137 | 2022-09-29 06:00 | 126 | 2022-09-08 23:00
118 | Nawabganj | 132 | 141 | 2022-09-26 20:00 | 128 | 2022-09-13 12:00
119 | Netrakona | 132 | 133 | 2022-09-26 11:00 | 103 | 2022-09-09 20:00
120 | New | 132 | 138 | 2022-09-25 19:00 | 124 | 2022-09-01 16:00
121 | Niamatpur | 132 | 137 | 2022-09-30 08:00 | 113 | 2022-09-17 03:00
122 | Noapara | 132 | 138 | 2022-09-09 17:00 | 125 | 2022-09-07 12:00
123 | Pabna | 132 | 139 | 2022-09-15 10:00 | 126 | 2022-09-29 12:00
124 | Palashbari | 132 | 135 | 2022-09-06 11:00 | 13 | 2022-09-07 23:00
125 | Panchagarh | 132 | 136 | 2022-09-08 18:00 | 106 | 2022-09-07 14:00
126 | Patuakhali | 132 | 138 | 2022-09-02 06:00 | 115 | 2022-09-13 17:00
127 | Payra | 132 | 139 | 2022-09-15 19:00 | 128 | 2022-09-16 13:00
128 | PHP | 132 | 139 | 2022-09-18 05:00 | 117 | 2022-09-01 06:00
129 | Postogola | 132 | 149 | 2022-09-04 23:00 | 131 | 2022-09-13 12:00
130 | Purbachal | 132 | 135 | 2022-09-03 02:00 | 123 | 2022-09-01 18:00
131 | Purbasadipur | 132 | 137 | 2022-09-08 18:00 | 112 | 2022-09-07 00:00
132 | Rahim | 132 | 136 | 2022-09-15 00:00 | 123 | 2022-09-21 09:00
133 | Rajbari | 132 | 136 | 2022-09-12 07:00 | 117 | 2022-09-06 15:00
134 | Rajendrapur | 132 | 138 | 2022-09-16 14:00 | 119 | 2022-09-03 18:30
135 | Rajshahi | 132 | 135.7 | 2022-09-06 10:00 | 118 | 2022-09-20 03:00
136 | Rajshahi-230 | 132 | 136 | 2022-09-06 10:00 | 112.9 | 2022-09-03 16:00
137 | Ramganj | 132 | 140 | 2022-09-27 06:00 | 112 | 2022-09-04 00:00
138 | Rampur | 132 | 139 | 2022-09-21 18:30 | 121 | 2022-09-01 11:00
139 | Rampura | 132 | 138 | 2022-09-08 05:00 | 104 | 2022-09-22 04:00
140 | Rangamati | 132 | 138 | 2022-09-06 19:00 | 124 | 2022-09-01 10:00
141 | Rangpur | 132 | 136 | 2022-09-03 17:00 | 112 | 2022-09-15 10:00
142 | Ruppur | 132 | 137 | 2022-09-02 16:00 | 110 | 2022-09-23 21:00
143 | Saidpur | 132 | 137 | 2022-09-15 14:00 | 112 | 2022-09-04 09:00
144 | Satkhira | 132 | 138 | 2022-09-12 10:00 | 118 | 2022-09-06 11:00
145 | Satmasjid | 132 | 138 | 2022-09-06 19:00 | 127 | 2022-09-17 10:00
146 | Savar | 132 | 140 | 2022-09-26 19:00 | 125 | 2022-09-17 11:00
147 | Shahjadpur | 132 | 142 | 2022-09-06 10:00 | 134 | 2022-09-09 21:00
148 | Shahjibazar | 132 | 136 | 2022-09-09 22:00 | 128 | 2022-09-20 17:00
149 | Shariatpur | 132 | 138 | 2022-09-12 10:00 | 109 | 2022-09-06 11:00
150 | Sherpur | 132 | 140 | 2022-09-03 23:00 | 114 | 2022-09-10 19:00
151 | Shikalbaha | 132 | 141 | 2022-09-08 23:00 | 122 | 2022-09-01 10:00
152 | Shikalbaha-230 | 132 | 141 | 2022-09-12 19:00 | 113 | 2022-09-22 09:00
153 | Shitalakhya | 132 | 143 | 2022-09-26 20:00 | 113 | 2022-09-26 18:30
154 | Sholosohor | 132 | N/A | N/A | N/A | N/A
155 | Shyampur | 132 | 135 | 2022-09-02 22:00 | 113 | 2022-09-13 00:00
156 | Shyampur-230 | 132 | 137 | 2022-09-26 19:00 | 113 | 2022-09-21 18:00
157 | Siddhirganj | 132 | 134 | 2022-09-26 20:00 | 123 | 2022-09-17 10:00
158 | Sirajganj | 132 | 138 | 2022-09-02 16:00 | 127 | 2022-09-09 21:00
159 | Sonargaon | 132 | 137 | 2022-09-26 20:00 | 123 | 2022-09-13 12:00
160 | Sreemongol | 132 | 137 | 2022-09-08 23:00 | 130 | 2022-09-02 04:00
161 | Srinagar | 132 | 139 | 2022-09-05 05:00 | 117.9 | 2022-09-08 19:30
162 | SSM | 132 | 142 | 2022-09-18 20:00 | 123 | 2022-09-01 10:00
163 | Sunamganj | 132 | 131 | 2022-09-04 02:00 | 115 | 2022-09-06 21:00
164 | Sylhet | 132 | 134 | 2022-09-05 09:00 | 123 | 2022-09-06 21:00
165 | Tangail | 132 | 138 | 2022-09-02 06:00 | 118 | 2022-09-16 21:00
166 | Thakurgaon | 132 | 139 | 2022-09-08 18:00 | 109 | 2022-09-23 02:00
167 | TK | 132 | 140 | 2022-09-16 18:30 | 122 | 2022-09-01 23:00
168 | Tongi | 132 | 170 | 2022-09-26 10:00 | 112 | 2022-09-21 10:00
169 | Ullon | 132 | 138 | 2022-09-04 04:00 | 125 | 2022-09-17 10:00
170 | Uttara | 132 | 139 | 2022-09-18 08:00 | 125 | 2022-09-01 10:00
171 | UttaraNew | 132 | 137 | 2022-09-02 22:00 | 124 | 2022-09-19 12:00
172 | Zigatola | 132 | 140 | 2022-09-06 22:00 | 127 | 2022-09-17 11:00

## QF-LDC-36
Page: 1/2 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
Month: September 2022
Name of the | Auto transformer |  | Recorded maximum load
sub-station | Name | Capacity ( MVA ) | MW | Amps ( 230kV side ) | Date | Time | Remarks
| TR1 | 225 | 69 | 205
Hasnabad | TR2 | 225 | 69 | 205 | 10.09.2022 | 17:00
| TR3 | 225 | 69 | 205
| TR1 | 225 | 195 | 550
Tongi | TR2 | 225 | 195 | 550 | 23.09.2022 | 12:00
| TR3 | 225 | 195 | 550
Haripur | TR1 | 225 | 135 | 420
| TR2 | 225 | 135 | 420 | 30.09.2022 | 09:00
| TR3 | 225 | 135 | 420
| TR1 | 225 | 200 | 550
Rampura | TR2 | 225 | 200 | 550 | 08.09.2022 | 16:00
| TR3 | 225 | 200 | 550
Keraniganj | ATR1 | 300 | 102 | 284
| ATR2 | 300 | 102 | 284 | 09.09.22 | 21:00
| ATR3 | 300 | 102 | 284
| TR1 | 225 | 160 | 459
Aminbazar | TR2 | 225 | 160 | 459 | 01.09.2022 | 24:00
| TR3 | 225 | 165 | 488
Agargaon | TR1 | 300 | 172 | 513
| TR2 | 300 | 172 | 513 | 01.09.2022 | 18:30
Maniknagar | TR1 | 300 | 154 | 470 | 19.09.2022 | 13:00
| TR2 | 300 | 154 | 470
Cumilla (N) | TR1 | 225 | 177 | 501 | 05.09.22 | 2:00
| TR2 | 225 | 172 | 492
Fenchuganj | AT2 | 300 | 236 | 578 | 06.09.22 | 21:00
| MT1 | 150 | 105 | 204
Hathazari | MT2 | 150 | 105 | 204
| MT3 | 150 | 105 | 204 | 08.09.22 | 19:00
| MT4 | 150 | 105 | 204
| TR1 | 225 | 111 | 366
Ishurdi | TR2 | 225 | 111 | 366 | 06.09.22 | 18:59
| TR3 | 225 | 111 | 366
Khulna(S) | TR1 | 225 | 116 | 297
| TR2 | 225 | 116 | 297 | 06.09.22 | 17:00
| TR3 | 300 | 148 | 378
Bogura | TR1 | 225 | 127 | 613
| TR2 | 225 | 127 | 613 | 09.09.22 | 18:30
| TR3 | 225 | 172 | 780
Baghabari | TR1 | 300 | 170 | 400 | 06.09.22 | 22:00
| TR2 | 225 | 130 | 360
Rajshahi | ATR-01 | 300 | 127 | 330
| ATR-02 | 300 | 127 | 330 | 10.09.22 | 4:00
Barapukuria | TR1 | 225 | 179 | 873 |  |  | Due to unavailability of 230 kV side meters
| TR2 | 225 | 164 | 790 | 10.09.22 | 19:00 | 132 kV current is being provided
| TR6 | 300 | 211 | 1011
Bheramara | Transformer-1 | 225 | 118 | 299
| Transformer-2 | 225 | 118 | 299 | 06.09.2022 | 19:30
Shyampur | ATR-01 | 300 | 112 | 340
| ATR-02 | 300 | 112 | 340 | 30.09.2022 | 24:00
Kaliakoir | TR1 | 300 | 129.9 | 602 | 18.09.2022 | 20:30
Sikalbaha | ATR-1 | 300 | 223 | 671
| ATR-2 | 300 | 223 | 671 | 29.09.2022 | 20:00
Jhenaidah | T1(230/132 kV) | 300 | 179 | 586 | 03.09.2022 | 19:00
| T2(230/132 kV) | 300 | 179 | 586
Page: 2/2 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 400/230 & 400/132 kV Transformer
Month:September 2022
Name of the | Transformer |  | Recorded maximum load |  |  |  | Remarks
sub-station | Name | Capacity ( MVA ) | MW | Amps (400 kV side) | Date | Time
Kaliakoir | TR1(400/230 kV) | 520 | 216 | 600 | 29.09.2022 | 9:30
| TR2(400/230 kV) | 520 | 218.5 | 604
| TR1(400/132 kV) | 325 | 324.4 | 1433 | 24.09.2022 | 2:30
| TR2(400/132 kV) | 325 | 324.2 | 1441
Bibiyana | ICT1(400/230 kV) | 520 | 221 | 322 | 08.09.2022 | 21:00
| ICT2(400/230kV) | 520 | 279 | 419 | 24.09.2023 | 20:00
Bhulta | ATR1(400/230 kV) | 520 | 342 | 590 | 13.09.2022 | 13:15
| ATR2(400/230kV) | 520 | 342 | 590
Ashuganj(N) | GSUT1(400/230 kV) | 567 | 388.6 | 650 | 15.09.2022 | 12:01
Gopalganj | ATR1(400/138 kV) | 325 | 308 | 457 | 01.09.2022 | 24:00
| ATR2(400/138kV) | 325 | 308 | 457
Payra | GSUT1 | 270 | 199 | 872 | 03.09.2022 | 23:27
| GSUT2 | 270 | 207 | 929 | 02.09.2022 | 24:12
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.
423

## QF-LDC-37
Page: 1/2 |  |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
[6 empty] | Report on load shedding | [13 empty] | Report on load shedding
Month: September 2022 | [6 empty] | (For Evening Peak) | [7 empty] | Month: September 2022 | [6 empty] | (For Day Peak)
| Peak Hour |  | Total load shed (SS end) | [12 empty] | Peak Hour |  | Total load shed (SS end)
Date | Generation (Gen End) | Demand (Gen End) |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks | Date | Generation | Demand (Gen End) |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur
2022-09-01 | 13712 | 14695 | 906 | 21:00 | 337 | 0 | 191 | 172 | 64 | 67 | 10 | 0 | 65 | - | 2022-09-01 | 11914 | 12900 | 909 | 12:00 | 530 | 165 | 0 | 42 | 47 | 95 | 23 | 0 | 7 | -
2022-09-02 | 13262 | 13492 | 212 | 21:00 | 50 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | - | 2022-09-02 | 11272 | 11272 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2022-09-03 | 13584 | 13492 | 164 | 19:30 | 74 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 0 |  | 2022-09-03 | 11272 | 11366 | 68 | 12:00 | 24 | 0 | 0 | 0 | 44 | 0 | 0 | 0 | 0 | -
2022-09-04 | 13540 | 13831 | 268 | 21:00 | 91 | 0 | 0 | 0 | 0 | 177 | 0 | 0 | 0 | - | 2022-09-04 | 11374 | 11374 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2022-09-05 | 13417 | 13522 | 97 | 21:00 | 0 | 0 | 0 | 0 | 0 | 97 | 0 | 0 | 0 | - | 2022-09-05 | 11806 | 11938 | 122 | 12:00 | 116 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | -
2022-09-06 | 12580 | 13800 | 1124 | 21:00 | 150 | 50 | 260 | 160 | 152 | 222 | 0 | 0 | 130 | - | 2022-09-06 | 10112 | 11452 | 1235 | 12:00 | 200 | 214 | 539 | 111 | 32 | 25 | 51 | 0 | 63 | -
2022-09-07 | 13631 | 14300 | 617 | 21:00 | 160 | 0 | 0 | 80 | 25 | 227 | 45 | 0 | 80 | - | 2022-09-07 | 11805 | 11805 | 0 | 10:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2022-09-08 | 13287 | 14370 | 998 | 19:30 | 207 | 0 | 19 | 111 | 135 | 265 | 128 | 0 | 133 | - | 2022-09-08 | 11999 | 13000 | 933 | 12:00 | 566 | 150 | 0 | 0 | 20 | 166 | 20 | 0 | 0 | -
2022-09-09 | 12912 | 13141 | 211 | 21:00 | 0 | 0 | 0 | 0 | 0 | 211 | 0 | 0 | 0 | - | 2022-09-09 | 11629 | 11914 | 249 | 12:00 | 0 | 0 | 0 | 0 | 0 | 249 | 0 | 0 | 0 | -
2022-09-10 | 13320 | 13560 | 221 | 21:00 | 76 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | - | 2022-09-10 | 11351 | 11590 | 220 | 11:00 | 15 | 0 | 0 | 0 | 0 | 205 | 0 | 0 | 0 | -
2022-09-11 | 12987 | 13264 | 255 | 20:00 | 0 | 0 | 0 | 0 | 0 | 255 | 0 | 0 | 0 | - | 2022-09-11 | 11469 | 11527 | 53 | 11:00 | 0 | 41 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | -
2022-09-12 | 12165 | 12252 | 80 | 21:00 | 30 | 0 | 0 | 0 | 15 | 17 | 18 | 0 | 0 | - | 2022-09-12 | 10815 | 10815 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2022-09-13 | 11790 | 11790 | 0 | 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2022-09-13 | 9641 | 9641 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2022-09-14 | 11915 | 11975 | 55 | 19:00 | 20 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | - | 2022-09-14 | 10133 | 10133 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2022-09-15 | 12683 | 12683 | 0 | 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2022-09-15 | 10903 | 10903 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2022-09-16 | 12502 | 12558 | 52 | 20:00 | 0 | 0 | 0 | 0 | 4 | 38 | 0 | 0 | 10 | - | 2022-09-16 | 10156 | 10156 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2022-09-17 | 13431 | 13669 | 219 | 21:00 | 40 | 0 | 0 | 0 | 27 | 152 | 0 | 0 | 0 | - | 2022-09-17 | 11391 | 11440 | 45 | 12:00 | 20 | 0 | 0 | 0 | 10 | 15 | 0 | 0 | 0 | -
2022-09-18 | 13498 | 13960 | 426 | 20:00 | 0 | 0 | 56 | 105 | 25 | 176 | 10 | 0 | 54 | - | 2022-09-18 | 11732 | 11840 | 100 | 12:00 | 32 | 0 | 0 | 0 | 10 | 47 | 11 | 0 | 0 | -
2022-09-19 | 13543 | 13964 | 388 | 21:00 | 29 | 0 | 0 | 0 | 51 | 213 | 95 | 0 | 0 | - | 2022-09-19 | 11712 | 12089 | 347 | 12:00 | 193 | 0 | 0 | 0 | 44 | 63 | 47 | 0 | 0 | -
2022-09-20 | 13575 | 14031 | 420 | 20:00 | 75 | 0 | 0 | 0 | 40 | 222 | 83 | 0 | 0 | - | 2022-09-20 | 11336 | 11336 | 0 | 11:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2022-09-21 | 13421 | 13832 | 379 | 21:00 | 100 | 0 | 0 | 0 | 38 | 171 | 20 | 0 | 50 | - | 2022-09-21 | 11629 | 11969 | 313 | 12:00 | 296 | 0 | 0 | 0 | 12 | 0 | 5 | 0 | 0 | -
2022-09-22 | 13138 | 14234 | 1010 | 21:00 | 163 | 0 | 199 | 143 | 122 | 147 | 112 | 0 | 124 | - | 2022-09-22 | 11587 | 11930 | 316 | 10:00 | 286 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | -
2022-09-23 | 13332 | 13487 | 143 | 20:00 | 0 | 0 | 0 | 0 | 10 | 133 | 0 | 0 | 0 | - | 2022-09-23 | 10990 | 10990 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2022-09-24 | 12888 | 13651 | 703 | 21:00 | 142 | 0 | 177 | 134 | 0 | 142 | 0 | 0 | 108 | - | 2022-09-24 | 11098 | 11754 | 605 | 12:00 | 378 | 92 | 4 | 25 | 47 | 59 | 0 | 0 | 0 | -
2022-09-25 | 12911 | 13649 | 680 | 21:00 | 108 | 0 | 168 | 92 | 115 | 119 | 0 | 0 | 78 | - | 2022-09-25 | 11208 | 11642 | 400 | 10:00 | 301 | 32 | 0 | 0 | 41 | 0 | 26 | 0 | 0 | -
2022-09-26 | 12929 | 14200 | 1171 | 21:00 | 360 | 34 | 174 | 130 | 170 | 93 | 100 | 0 | 110 | - | 2022-09-26 | 10982 | 11378 | 365 | 9:00 | 210 | 103 | 0 | 0 | 30 | 0 | 22 | 0 | 0 | -
2022-09-27 | 12847 | 14200 | 1247 | 20:00 | 209 | 0 | 247 | 158 | 170 | 208 | 107 | 0 | 148 | - | 2022-09-27 | 11311 | 11378 | 543 | 12:00 | 222 | 203 | 0 | 0 | 41 | 41 | 36 | 0 | 0 | -
2022-09-28 | 12904 | 14500 | 1471 | 21:00 | 345 | 190 | 230 | 144 | 98 | 177 | 118 | 0 | 169 | - | 2022-09-28 | 11534 | 12500 | 890 | 12:00 | 451 | 183 | 0 | 0 | 43 | 153 | 48 | 0 | 12 | -
2022-09-29 | 12983 | 14429 | 1333 | 21:00 | 192 | 41 | 192 | 164 | 200 | 231 | 159 | 0 | 154 |  | 2022-09-29 | 10966 | 12173 | 1112 | 12:00 | 737 | 206 | 0 | 0 | 102 | 26 | 41 | 0 | 0
2022-09-30 | 13010 | 13921 | 840 | 20:00 | 93 | 0 | 223 | 140 | 40 | 178 | 79 | 0 | 87 |  | 2022-09-30 | 10869 | 11635 | 723 | 12:00 | 493 | 58 | 0 | 0 | 68 | 43 | 61 | 0 | 0
15690
| Max. L/S | - | 1471 | 2022-09-28 | [10 empty] | Max. L/S | - |  | 1235 | 2022-09-06 | 12:00
| Min. L/S | - | 0 | 2022-09-13 | [10 empty] | Min. L/S | - |  | 0 | 2022-09-02 | 12:00
| No. of Days | - | 29 | - | [10 empty] | No. of Days | - | 31
| Average L/S |  | 15690 | [11 empty] | Average L/S |  | 19669
|  | - | - | - | [11 empty] | - | -
|  |  | - | -
[15 empty] | -87 | 0 | 12
[15 empty] | 0 | 0 | 13
[15 empty] | -60 | 0 | 14
[15 empty] | 0 | 0 | 15
[15 empty] | -56 | 0 | 16
[15 empty] | -238 | 49 | 17
[15 empty] | -462 | 108 | 18
[15 empty] | -421 | 377 | 19
[15 empty] | -456 | 0 | 20
[15 empty] | -411 | 340 | 21
[15 empty] | -1096 | 343 | 22
[15 empty] | -155 | 0 | 23
[15 empty] | -763 | 656 | 24
[15 empty] | -738 | 434 | 25
[15 empty] | -1271 | 396 | 26
[15 empty] | -1353 | 67 | 27
[15 empty] | -1596 | 966 | 28
[15 empty] | #REF! | #REF! | 29
[15 empty] | #REF! | #REF! | 30
[15 empty] | #REF! | #REF! | 31

## QF-LDC-38
Page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month: Sptember-2022
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 13761 | 2022-09-07 | 22:00
2 | Maximum Day Peak Genaration | MW | 11999 | 2022-09-08 | 12:00
3 | Maximum Evening Peak Demand | MW | 14695 | 2022-09-01 | 20:00
4 | Minimum Generation | MW | 8864 | 2022-09-15 | 6:00
5 | Average of the daily evening peak Genaration | MW | 13055.1 | - | -
6 | Average of the daily day peak Genaration | MW | 11203.2667 | - | -
7 | Maximum load shed | MW | 1471 | 2022-09-28 | 21:00
8 | Minimum load shed | MW | 0 | 2022-09-13 | 19:30
9 | Total nos. of load shed days | Day | 29 | - | -
10 | Average load shed ( Avg. of the 30 days in the month) | MW/Day | 523 | - | -
11 | Total Generation | MkWh | 8442.6119 | - | -
12 | Total Generation by BPDB | MkWh | 1767.5579 | % of total Gen. | 20.94%
13 | Total Generation by IPP | MkWh | 2757.9834 | '' | 32.67%
14 | A) Total Generation by Generation Companies | MkWh | 2658.8691 | '' | 31.49%
| B) Total Generation by REB | MkWh | 111.5457 | " | 1.321%
| C) Total Generation by RENTAL | MkWh | 401.8248 | " | 4.759%
| D) Total Imported from India (BIPTC) | MkWh | 649.1985 | " | 7.69%
| E) Total Imported from Tripura, India (A.C) | MkWh | 95.6325 | " | 1.133%
15 | Fuel wise Generation.
| A) Gas | MkWh | 4050.2118 | % of total Gen. | 47.97%
| B) Oil | MkWh | 2556.9618 | '' | 30.29%
| C) Hydro | MkWh | 104.6574 | '' | 1.24%
| D) Solar | MkWh | 34.9866 | '' | 0.4144%
| E) Coal | MkWh | 950.9634 | '' | 11.26%
| F) BIPTC (Import from India) | MkWh | 649.1985 | '' | 7.69%
| G) A.C (Import from Tripura, India) | MkWh | 95.6325 | '' | 1.133%
16 | Maximun of the daily total Generation . | MkWh | 304.5978 | 2022-09-07
17 | Monthly Load factor | % | 91.3054 | - | -
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 49028.2097 | - | -
| A) Gas | M.Taka | 4575.4204 | - | -
| B) Liquid fuel | M.Taka | 34397.1566 | - | -
| C) Coal | M.Taka | 7168.2084 | - | -
| D) BIPTC (Import from India) | M.Taka | 2200.783 | - | -
| E) Tripura(Import from India) | M.Taka | 686.6412 | - | -
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 1856.3013 | 2022-09-18
| A) Gas | M.Taka | 167.8458 | 2022-09-03
| B) Liquid fuel | M.Taka | 1444.0592 | 2022-09-18
| C) Coal | M.Taka | 285.1906 | 2022-09-02
| D) BIPTC (Import from India) | M.Taka | 74.045 | 2022-09-23
20 | Average fuel cost of per unit Generation
| A) Including Hydro & Solar | Taka/kWhR | 7.1008
| B) Excluding Hydro & Solar | Taka/kWhR | 7.2195
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 105.76 | 30/09/2022 | 06:00
b) | Actual | FT (MSL) | 97.06 | 30/09/2022 | 06:00
22 | Peak Genaration of September2021 | MW | 13509 | 2022-09-11 | 20:00
23 | Peak Demand of August 2021 | MW | 13509 | 2021-09-11 | 20:00
24 | Maximum peak Generation recorded upto 30/09/2022 | MW | 14782 | 16/04/2022 | 21:00
25 | Maximum peak Demand recorded upto 30/09/2022 | MW | 14782 | 16/04/2022 | 21:00
26 | Maximum load shed recorded upto 30/09/2022 | MW | 1459 | 04/05/2010 | 20:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## FGMO
Power Grid Company Of Bangladesh Ltd.
NLDC, Aftabnagar, Dhaka.
Monthly status of Free Governor Mode of Operation (FGMO) Power Plants
SL | Plant Name | Owner | Installed capacity | FGMO Status
|  |  | (MW) | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
1 | Bibiana-II 341 MW CCPP (Summit) | IPP | 341 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
2 | Shahjibazar GTPP Unit 8 & 9 | BPDB | 70
3 | Sirajgonj 400 MW CCPP Unit-4 | IPP | 414
4 | Sirajgonj 225MW CCPP Unit-3 | NWPGCL | 220
5 | Sirajgonj 225MW CCPP Unit-2 | NWPGCL | 220
6 | Meghnaghat CCPP(Summit) | IPP | 335
7 | Ashuganj 450 MW CCPP(North) | APSCL | 360
8 | Ashuganj 225 MW CCPP | APSCL | 221
9 | Bheramara 410 MW CCPP | NWPGCL | 410
10 | Haripur 412 MW CCPP | EGCB | 412
11 | Fenchugonj CCPP Phase-1 | BPDB | 97
12 | Chandpur 150 MW CCPP | BPDB | 163
13 | Siddhirganj 2x120 MW GTPP | EGCB | 210
14 | Shikalbaha 225 MW CCPP | BPDB | 225
15 | Shikalbaha Peaking GT | BPDB | 150
16 | Shahjibazar 330 MW CCPP | BPDB | 330
17 | Ashuganj 450 MW CCPP(South) | APSCL | 360
18 | Fenchugonj CCPP Phase-2 | BPDB | 104
19 | Bhola 225 MW CCPP | BPDB | 194
20 | Ghorasal 365 MW CCPP Unit-7 | BPDB | 365
21 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | 210
22 | Siddhirganj 335 MW CCPP | EGCB | 335
23 | Bibiyana-III 400 MW CCPP | BPDB | 400
24 | Sylhet 225 MW CCPP | BPDB | 231
25 | RPCL 210 MW CCPP | IPP | 210
26 | Khulna 225 MW CCPP | NWPGCL | 230
27 | a) Baghabari 71 MW GTPP | BPDB | 71
| b) Baghabari 100 MW GTPP | BPDB | 100
28 | Karnaphuli Hydro PP Unit: 1 | BPDB | 40
| Karnaphuli Hydro PP Unit: 2 | BPDB | 40
| Karnaphuli Hydro PP Unit: 3 | BPDB | 50
| Karnaphuli Hydro PP Unit: 4 | BPDB | 50
| Karnaphuli Hydro PP Unit: 5 | BPDB | 50
29 | a) Ghorasal Repowered CCPP Unit-3 | BPDB | 416
| b) Ghorasal Repowered CCPP Unit-4 | BPDB | 410
30 | Bibiyana South 400 MW CCPP | BPDB | 383
31 | Barapukuria 275 MW TPP Unit-3 | BPDB | 274
32 | Shajibazar 100 MW PP | BPDB | 100
33 | Payra 1320 MW Unit-1 | BCPCL | 622
34 | Kushiara 163 MW CCPP (KP) | IPP | 163
35 | Haripur 360MW CCPP(HPL) | IPP | 360
36 | Meghnaghat 450 MW CCPP(MPL) | IPP | 450
due to gas shortage