## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2022-11-23 | Wednesday
|  | Date (day): | 2022-11-23 |  | Wednesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 9505.6 | MW |  |  | (b) At Evening Peak Hour : |  | 11217 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2022-11-22 | 2022-11-23 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Line O/L
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Under maint
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 71 | 71 | 71 | 71 | 37 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 312 | 308 | 300 | 310 | 102 |  | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 268 | 286 | 255 | 286 | 74 |  | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 225 | 225 | 225 |  | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 78 | 92 | 80 | 92 |  | 8 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas line maintenance
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 0 | 0 | 0 | 0 |  | 102 | Under maint
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 45 | 45 | 45 | 45 |  | 10 | Engine problem
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 19 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 72 | 85 | 75 | 85 |  | 15 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 8 | 33 | 24 | 33 | 69 |  | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 54 | 17 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 115 | 133 | 115 | 133 |  | 16 | Engine problem
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 35 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 35 | 35 | 35 |  | 20 | Engine problem
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 49 | 48 | 49 | 48 |  | 32 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 29 | 28 | 31 | 33
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 42 | 49 | 42 | 50
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 97 | 188 | 97 | 275 |  | 25 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 132 | 66 | 100 | 150 | 150 |  | Fuel conservation
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 95 | 80 | 50 | 80 | 20 |  | Fuel conservation
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 92 | 50 | 0 | 50 | 50 |  | Fuel conservation
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 135 | 92 | 125 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 105 | 105 | 105 | 105
37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 30 | 35 | 17 | 17 | 87 |  | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 35 | 162 | 90 | 162
39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 27 | 0 | 30 | 0
40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 17 | 17 | 17 | 38 |  | Fuel shortage
| Dhaka area Total |  |  |  |  | 6263 | 5847 | 2395 | 2574 | 2265 | 2795 | 1783 | 1273
41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 8 | 8 | 17 | 17 |  | 8 | Engine problem
43 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 20 | 0 | 20 | 0
44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 12 | 43 | 26 | 43 |  | 7 | Engine problem
45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 30 | 46 | 46 | 46 | 184 |  | Low Water Level
46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 151 | 150 | 150 | 150 |  | 75 | ST under maint
47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 68 | 97 | 51 | 105
49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 8 | 32 | 20 | 32 | 66 |  | Fuel shortage
50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 17 | 51 | 17 | 51 | 51 |  | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 22 | 44 | 22 | 44 | 56 |  | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 25 | 50 | 25 | 50 | 50 |  | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  | 22 | Engine problem
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 2 | 2 | 2
54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 266 | 300 | 260 | 300
57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 36 | 36 | 36 | 36 |  | 18 | Engine problem
58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 53 | 91 | 70 | 91 |  | 19 | Engine problem
59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 50 | 25 | 50 | 50 |  | Fuel shortage
60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 107 | 107 | 107 | 107 |  | 9 | Engine problem
| Mirsharai 150 MW |  | Gas/HSD | BPDB-RPCL | 18.5*9 | 0 | 0 | 30 | 0 | 0 | 0
| Chattogram area Total |  |  |  |  | 2442 | 2382 | 884 | 1107 | 899 | 1124 | 925 | 308
61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 0 | 0 | 0 | 0 |  | 221 | Under maint.
63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint
64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 250 | 250 | 250 | 250 | 110 |  | Gas shortage
| Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+136*1 | 284 | 284 | 381 | 402 | 400 | 400 |  |  | On test.
65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 42 | 44 | 40 | 44
66 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 55 | 30 | 30 | 15 | 30 | 25 |  | Gas shortae
67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 0 | 0 | 0 | 0 | 195 |  | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 0 | 5 | 5 | 5 | 46 |  | Gas shortage
69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 80 | 120 | 75 | 120 | 30 |  | Fuel shortage
70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 30 | 0 | 30 |  | 22 | Engine problem
71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 60 | 66 | 66 | 66 | 97 |  | Gas shortage.
72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 17 | 147 | 100 | 200
73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 22 | 22 | 22
74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 8 | 8 |  | 3 | Engine problem
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 104 | 120 | 143 | 165
75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 13 | 16 | 33 | 33
76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 8 | 8 | 8 | 44 |  | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 15 | 15 | 15 | 15 |  | 10 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 50 | 20 | 100 | 100 | 100 |  | Fuel conservation
79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 0 | 0 | 114 |  | Fuel shortage
80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 106 | 108 | 108 | 108
81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 34 | 17 | 34 |  | 20 | Engine problem
82 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 115 | 115 | 115 | 115
| Cumilla Area Total |  |  |  |  | 3193 | 3169 | 1315 | 1560 | 1520 | 1753 | 895 | 636
83 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 35 | 39 | 70 | 70 | 132 |  | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 10 | 10 | 10 | 10 | 12 |  | Gas shortage
85 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0
86 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
87 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 77 | 87 | 40 | 55 | 145 |  | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 68 | 97 | 45 | 55 | 60 |  | Fuel shortage
89 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 48 | 0 | 50 | 0
90 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 12 | 12 |  | 10 | Engine problem
| Mymensingh Area Total |  |  |  |  | 717 | 614 | 252 | 245 | 228.6 | 202 | 144 | 10
91 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 0 | 30 | 30 | 30 |  | 40 | Machine problem.
92 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 43 | 43 | 43 | 43 |  | 47 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 | 163 |  | Gas shortage
94 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 53 | 53 | 50 | 50
96 | Fenchuganj 44MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 30 | 25 | 25 | 25 | 25 |  | Gas shortage
97 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 3 | 3 | 3 | 3 | 8 |  | Gas shortage
98 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 62 | 69 | 66 | 66
99 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 0 | 83 | 0 | 83
100 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
101 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 178 | 178 | 177 | 178 | 53 |  | Gas shortage
102 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 19 | 19
103 | Sylhet 50MW PP (EPL) |  | Gas | NENP | 27*2 | 50 | 50 | 25 | 27 | 20 | 27 | 23 |  | Gas shortage
104 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 22 | 24 | 22 | 24
105 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 0 | 0 | 0 | 0 |  | 341 | Under maint. |  | 2022-12-23
106 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 422 | 391 | 400 | 400
107 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
108 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 394 | 400 | 400 | 400
| Sylhet Area Total |  |  |  |  | 2522 | 2477 | 1260 | 1354 | 1265 | 1358 | 272 | 858
109 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 896 | 895 | 913 | 913
110 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 16 | 99 | 16 | 115
111 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 50 | 0 | 50
112 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
113 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 50 | 0 | 75 |  | 34 | Engine problem
114 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 145 | 145 | 150 | 150 | 260 |  | Gas shortage
115 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 8 | 32 | 0 | 32 | 8 |  | Fuel shortage
116 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 0 | 50 | 50 |  | Fuel conservation
117 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 53 | 94 | 64 | 94
118 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Fuel shortage
119 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 77 | 0 | 100 | 0
| Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 2388 | 2384 | 1195 | 1365 | 1243 | 1479 | 669 | 34
120 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 0 | 0 |  |  | Line O/L
121 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 16 | 20 | 15 | 20 |  | 20 | Engine problem
122 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 100 | 115 | 130 | 130 |  | 64 | Machine problem
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
123 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 590 | 630 | 800 | 800 |  |  | Line O/L
124 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 110 | 0 | 0 | 0 |  | 220 | Under maint.
125 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 0 | 0 |  |  | Line O/L
| Barisal 307 MW |  | Coal | BCPCL | 0 | 0 | 0 | 174 | 329 | 190 | 300 |  |  | On test.
| Barisal Area Total |  |  |  |  | 1958 | 1958 | 990 | 1094 | 1135 | 1250 | 0 | 304
126 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
127 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 24 | 0 | 34 |  | 18 | Engine problem
128 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 3 | 0 | 20 |  | 51 | Engine problem
129 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
130 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 16 | 34 | 25 | 34 |  | 16 | Engine problem
131 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 37 | 0 | 37 | 13 |  | Fuel shortage
132 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 159 | 157 | 150 | 160 | 50 |  | Gas shortage
133 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Fuel shortage
134 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
135 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 180 | 187 | 200 | 200 | 214 |  | Gas shortage
136 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 24 | 0 | 24 |  | 26 | Engine problem
137 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 15 | 17 | 17 | 17 |  | 5 | Engine problem
138 | Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
139 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
140 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 43 | 8 | 43 |  | 9 | Engine problem
141 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 80 | 0 | 80 |  | 24 | Engine problem
142 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel shortage
143 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 35 | 113 | 85 | 113
144 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 37 | 95 | 90 | 95
145 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 4 | 0 | 6 | 0
| Rajshahi Area Total |  |  |  |  | 2199 | 2129 | 465 | 825 | 592 | 868 | 1088 | 149
146 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal shortage
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
147 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 160 | 160 | 160 | 160 |  |  | Machine problem
148 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
149 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
150 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 34 | 113 | 90 | 113
151 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 6 | 0 | 8 | 0
152 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 36 | 115 | 70 | 115
| Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 32 | 0 | 30 | 0
| Rangpur Area Total |  |  |  |  | 830 | 750 | 268 | 388 | 358 | 388 | 125 | 85
| Total |  |  |  |  | 22512 | 21710 | 9024 | 10512 | 9505.6 | 11217 | 5901 | 3657
A. |  | 2022-11-22 | (Yesterday) |  |  |  |  | Tuesday
1 | Highest Generation : |  |  | 10512 | MW at | 18:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 18:00 | hrs.
2 | Minimum Generation : |  |  | 6884 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 10512 | MW
3 | Day peak Generation : |  |  | 9024 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 10170.51 | MW
4 | Evening peak Generation : |  |  | 10512 | MW at | 18:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 207.9304 | MKWHr | By Solar | 1.3954 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Gas : | 104.2717 | MKWHr |  | By Oil: | 53.6891 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 25.6989 | MKWHr |  | By Hydro: | 1.0505 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 5901 | MW | Dhaka | 3964.46 | 3964.46 |  | 0 |  | 18:00 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 3657 | MW | Chittagong | 1223.2 | 1223.2 |  | 0 |  | 19:00 |  | 0
|  |  | Total = |  |  | 9558 | MW | Khulna | 1110 | 1110 |  | 0 |  | 19:30 |  | 0
7 | Total Gas Supplied : |  |  | 794.28 | MMCFD |  |  | Rajshahi | 954.2 | 954.2 |  | 0 |  | 20:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 104779769.024 | ii) Oil : | Taka | 717105079.83 | Comilla | 846 | 846 |  | 0 |  | 21:00 |  | 0
|  | iii) Coal : |  | 170742914 | Total | Taka | 992627762.854 | Mymensingh | 764 | 764 |  | 0 |  | 22:00 |  | 0
9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0 | MKWHr. | Sylhet | 365 | 365 |  | 0 |  | 23:00 |  | 0
| ii) During Peak Demand : |  |  | 940 | MW (E to W) at | 18:00 | hrs | Barisal | 242.65 | 242.65 |  | 0 |  | 24:00 |  | 0
| iii) Maximum : |  |  | 740 | MW at | 8:00 | hrs | Rangpur | 701 | 701 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 28.9° C |  |  | Total | 10170.51 | 10170.51 |  | 0
B. |  | 2022-11-23 | (Today) |  |  |  | Wednesday |  |  | Probable max. temperature in Dhaka |  |  | 29.3° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 10800 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 11217 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 9200 | MW
4 | Reserve(Generation end) |  |  |  | 417 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | 3 | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 213.6271 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 6735 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 19.4604 | MKWHr. | ii) HVDC Flow at Peak Time |  | 895 | MW at | 18:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.3645 | MKWHr. | iii) Maximum HVDC Flow : |  | 897 | MW at | 16:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 90.89 |  | (b) Today: | 90.85 |  | (c) Rule Curve: |  | 106.8
.

## YesterdayGen
2022-11-22
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 0 | 71 | 0 | 302 | 271 |  | 0 | 225 | 0 | 25 | 0 | 45 | 0 | 0 | 0 | 30 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 22 | 22 | 27 | 33 | 32 | 8 | 0 | 46 | 0 | 0 | 0 | 17 | 148 | 0 | 0 | 0 |  | 12 | 0 | 17 | 22 | 0 | 37 | 0 | 9 | 0 | 0 | 0 | 0 | 210 | 0 | 0 | 76 | 44 | 30 | 0 | 0 | 0 | 0 | 8 | 22 | 8 | 33 | 15 | 96 | 111 | 0 | 11 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 66 | 81 | 0 | 177 | 19 | 0 | 0 | 130 | 0 | 3 | 0 | 260 | 0 | 0 | 48 | 0 | 149 | 0 | 25 | 17 | 65 | 416 | 49 | 105 | 34 | 0 | 16 | 25 | 73 | 17 | 75 | 25 | 400 | 17 | 0 | 17 | 107 | 0 | 17 | 0 | 28 | 17 | 407 | 0 | 0 |  | 660 | 0 | 180 | 0 | 32 | 0 | 0 | 0 | 0 | 36 | 0 | 130 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 275 | 94 | 0 | 35 | 0 | 56 | 0 | 0 | 70 | 540 | 96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 145 |  | 5286 | 2760 | 8046 | 3321 | 660 | 1230 | 0 | 1779 | 845 | 46 | 0 | 69 | 96 | 0 | 0 | 90.89
2:00 | 0 | 0 | 0 | 180 | 0 | 71 | 0 | 302 | 271 |  | 0 | 225 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 30 | 8 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 17 | 22 | 22 | 27 | 33 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 149 | 0 | 0 | 0 |  | 12 | 0 | 17 | 22 | 0 | 6 | 0 | 14 | 0 | 0 | 0 | 0 | 210 | 0 | 0 | 68 | 43 | 30 | 0 | 0 | 0 | 0 | 8 | 22 | 8 | 33 | 15 | 92 | 111 | 0 | 12 | 0 | 0 | 43 | 42 | 32 | 0 | 0 | 66 | 0 | 0 | 177 | 19 | 15 | 7 | 90 | 0 | 3 | 0 | 263 | 0 | 0 | 0 | 0 | 149 | 0 | 25 | 17 | 10 | 416 | 49 | 17 | 34 | 0 | 16 | 17 | 73 | 17 | 9 | 25 | 400 | 17 | 0 | 17 | 107 | 0 | 17 | 0 | 18 | 17 | 387 | 0 | 0 |  | 660 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 240 | 53 | 0 | 82 | 0 | 0 | 0 | 0 | 70 | 550 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 144 |  | 4832 | 2587 | 7419 | 3279 | 660 | 1187 | 0 | 1284 | 854 | 46 | 0 | 17 | 92 | 0 | 0 | 90.89
3:00 | 0 | 0 | 0 | 180 | 0 | 71 | 0 | 302 | 270 |  | 0 | 225 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 17 | 22 | 22 | 27 | 33 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 154 | 0 | 0 | 0 |  | 12 | 0 | 17 | 22 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 210 | 0 | 0 | 68 | 43 | 30 | 0 | 0 | 0 | 0 | 8 | 22 | 8 | 33 | 15 | 90 | 113 | 0 | 12 | 0 | 0 | 43 | 50 | 33 | 0 | 0 | 66 | 0 | 0 | 177 | 19 | 22 | 9 | 80 | 8 | 3 | 0 | 195 | 0 | 0 | 0 | 0 | 113 | 0 | 25 | 17 | 10 | 416 | 49 | 0 | 34 | 0 | 16 | 17 | 73 | 17 | 9 | 25 | 380 | 17 | 0 | 17 | 51 | 0 | 17 | 0 | 17 | 17 | 407 | 0 | 0 |  | 660 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 275 | 17 | 0 | 35 | 0 | 0 | 0 | 0 | 70 | 550 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142 |  | 4634 | 2536 | 7170 | 3295 | 660 | 1228 | 0 | 982 | 852 | 46 | 0 | 17 | 90 | 0 | 0 | 90.89
4:00 | 0 | 0 | 0 | 180 | 0 | 71 | 0 | 302 | 270 |  | 0 | 225 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 17 | 22 | 22 | 27 | 33 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 |  | 12 | 0 | 17 | 22 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 210 | 0 | 0 | 68 | 44 | 30 | 0 | 0 | 0 | 0 | 8 | 22 | 8 | 33 | 15 | 86 | 111 | 0 | 12 | 0 | 0 | 43 | 50 | 33 | 0 | 0 | 40 | 0 | 0 | 177 | 19 | 23 | 10 | 70 | 17 | 3 | 0 | 100 | 0 | 0 | 0 | 0 | 98 | 0 | 25 | 17 | 10 | 418 | 49 | 0 | 34 | 0 | 16 | 17 | 58 | 0 | 9 | 25 | 360 | 17 | 0 | 17 | 34 | 0 | 17 | 0 | 18 | 17 | 407 | 0 | 0 |  | 660 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 275 | 17 | 0 | 35 | 0 | 0 | 0 | 0 | 70 | 550 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143 |  | 4427 | 2550 | 6977 | 3270 | 660 | 1231 | 0 | 814 | 853 | 46 | 0 | 17 | 86 | 0 | 0 | 90.89
5:00 | 0 | 0 | 0 | 180 | 0 | 71 | 0 | 302 | 270 |  | 0 | 225 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 17 | 22 | 22 | 27 | 33 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 |  | 12 | 0 | 17 | 22 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 210 | 0 | 0 | 67 | 43 | 30 | 0 | 0 | 0 | 0 | 8 | 22 | 8 | 33 | 15 | 84 | 112 | 0 | 12 | 0 | 0 | 43 | 50 | 33 | 0 | 0 | 40 | 0 | 0 | 177 | 19 | 23 | 10 | 50 | 22 | 3 | 0 | 97 | 0 | 0 | 0 | 0 | 98 | 0 | 25 | 17 | 10 | 352 | 49 | 0 | 34 | 0 | 16 | 17 | 53 | 0 | 9 | 25 | 360 | 17 | 0 | 17 | 34 | 0 | 17 | 0 | 18 | 17 | 407 | 0 | 0 |  | 660 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 17 | 0 | 35 | 0 | 0 | 0 | 0 | 70 | 550 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 147 |  | 4335 | 2549 | 6884 | 3208 | 660 | 1206 | 0 | 806 | 857 | 46 | 0 | 17 | 84 | 0 | 0 | 90.89
6:00 | 0 | 0 | 0 | 180 | 0 | 71 | 0 | 304 | 272 |  | 0 | 225 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 6 | 8 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 17 | 22 | 22 | 27 | 33 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 |  | 12 | 0 | 17 | 22 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 210 | 0 | 0 | 67 | 43 | 30 | 0 | 0 | 0 | 0 | 8 | 22 | 8 | 33 | 15 | 82 | 112 | 0 | 12 | 0 | 0 | 43 | 50 | 33 | 0 | 0 | 40 | 0 | 0 | 177 | 19 | 23 | 10 | 40 | 22 | 3 | 0 | 95 | 0 | 0 | 35 | 0 | 104 | 0 | 25 | 17 | 25 | 418 | 49 | 0 | 34 | 0 | 16 | 17 | 53 | 0 | 9 | 25 | 360 | 17 | 0 | 17 | 34 | 0 | 17 | 0 | 18 | 17 | 407 | 0 | 0 |  | 660 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 17 | 0 | 35 | 0 | 34 | 0 | 0 | 70 | 550 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 145 |  | 4458 | 2581 | 7039 | 3276 | 660 | 1203 | 0 | 900 | 855 | 46 | 0 | 17 | 82 | 0 | 0 | 90.89
7:00 | 0 | 0 | 0 | 180 | 0 | 71 | 0 | 304 | 272 |  | 0 | 225 | 0 | 3 | 0 | 30 | 0 | 0 | 0 | 30 | 8 | 64 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 22 | 22 | 27 | 33 | 33 | 26 | 0 | 46 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 |  | 12 | 0 | 17 | 22 | 0 | 4 | 0 | 30 | 0 | 0 | 0 | 0 | 210 | 0 | 0 | 69 | 43 | 30 | 0 | 0 | 0 | 0 | 8 | 22 | 8 | 28 | 15 | 78 | 72 | 0 | 12 | 0 | 0 | 43 | 50 | 33 | 0 | 0 | 70 | 0 | 0 | 177 | 19 | 23 | 10 | 45 | 22 | 3 | 0 | 97 | 0 | 0 | 46 | 0 | 134 | 3 | 25 | 17 | 52 | 417 | 49 | 36 | 34 | 0 | 16 | 31 | 53 | 0 | 17 | 25 | 400 | 17 | 3 | 17 | 82 | 0 | 17 | 2 | 18 | 17 | 407 | 0 | 0 |  | 660 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 8 | 0 | 20 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 261 | 30 | 0 | 35 | 0 | 65 | 0 | 0 | 37 | 610 | 110 | 0 | 0 | 0 | 6 | 17 | 0 | 0 | 0 | 1 | 146 |  | 4805 | 2684 | 7489 | 3303 | 660 | 1196 | 0 | 1194 | 916 | 46 | 0 | 81 | 78 | 15 | 0 | 90.89
8:00 | 0 | 0 | 0 | 180 | 0 | 71 | 0 | 303 | 266 |  | 0 | 225 | 0 | 24 | 0 | 30 | 0 | 0 | 0 | 30 | 8 | 98 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 22 | 22 | 27 | 33 | 33 | 42 | 0 | 46 | 0 | 0 | 0 | 5 | 151 | 0 | 0 | 0 |  | 12 | 0 | 17 | 22 | 0 | 27 | 0 | 2 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 67 | 43 | 30 | 0 | 0 | 0 | 0 | 8 | 0 | 8 | 20 | 15 | 82 | 70 | 0 | 12 | 1 | 0 | 43 | 50 | 33 | 0 | 0 | 70 | 0 | 0 | 177 | 19 | 23 | 10 | 45 | 22 | 3 | 0 | 97 | 0 | 0 | 46 | 0 | 135 | 9 | 25 | 17 | 75 | 418 | 49 | 105 | 34 | 2 | 16 | 36 | 53 | 0 | 78 | 25 | 400 | 17 | 17 | 17 | 107 | 0 | 17 | 10 | 18 | 17 | 407 | 0 | 0 |  | 660 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 8 | 0 | 18 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 249 | 64 | 0 | 35 | 0 | 97 | 0 | 1 | 37 | 690 | 110 | 0 | 0 | 1 | 26 | 72 | 0 | 0 | 0 | 9 | 198 |  | 5163 | 2948 | 8111 | 3355 | 660 | 1147 | 0 | 1582 | 1048 | 46 | 0 | 115 | 82 | 76 | 0 | 90.88
9:00 | 0 | 0 | 0 | 180 | 0 | 71 | 0 | 299 | 269 |  | 0 | 225 | 0 | 25 | 0 | 30 | 0 | 0 | 0 | 33 | 8 | 115 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 22 | 23 | 28 | 33 | 29 | 42 | 0 | 46 | 0 | 0 | 0 | 8 | 150 | 0 | 0 | 0 |  | 12 | 0 | 17 | 22 | 0 | 31 | 0 | 2 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 67 | 41 | 30 | 0 | 0 | 0 | 0 | 8 | 0 | 8 | 4 | 15 | 86 | 70 | 0 | 10 | 1 | 0 | 43 | 50 | 33 | 0 | 0 | 69 | 0 | 0 | 177 | 19 | 23 | 10 | 0 | 22 | 3 | 0 | 97 | 0 | 0 | 46 | 0 | 136 | 14 | 25 | 17 | 79 | 417 | 49 | 105 | 42 | 3 | 16 | 36 | 53 | 0 | 105 | 25 | 350 | 17 | 33 | 17 | 107 | 0 | 17 | 19 | 18 | 17 | 407 | 0 | 0 |  | 754 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 8 | 0 | 15 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 226 | 70 | 0 | 69 | 0 | 95 | 0 | 3 | 37 | 650 | 110 | 0 | 0 | 2 | 48 | 56 | 0 | 0 | 0 | 16 | 199 |  | 5210 | 3020 | 8230 | 3314 | 754 | 1079 | 0 | 1671 | 1009 | 46 | 0 | 132 | 86 | 139 | 0 | 90.88
10:00 | 0 | 0 | 0 | 180 | 0 | 70 | 0 | 305 | 267 |  | 0 | 225 | 0 | 28 | 0 | 30 | 0 | 0 | 0 | 70 | 8 | 115 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 22 | 23 | 28 | 25 | 29 | 42 | 0 | 46 | 0 | 0 | 0 | 8 | 151 | 0 | 0 | 0 |  | 12 | 0 | 17 | 22 | 0 | 31 | 0 | 2 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 66 | 38 | 30 | 0 | 0 | 0 | 0 | 8 | 15 | 8 | 13 | 15 | 90 | 37 | 0 | 10 | 2 | 0 | 43 | 50 | 33 | 0 | 0 | 67 | 0 | 0 | 177 | 19 | 24 | 10 | 0 | 18 | 3 | 25 | 97 | 35 | 25 | 48 | 25 | 136 | 18 | 25 | 17 | 80 | 419 | 49 | 105 | 68 | 4 | 16 | 36 | 53 | 0 | 105 | 25 | 400 | 20 | 42 | 17 | 107 | 0 | 17 | 25 | 18 | 17 | 386 | 0 | 0 |  | 801 | 0 | 160 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 100 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 8 | 0 | 15 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 208 | 53 | 0 | 70 | 0 | 70 | 0 | 4 | 37 | 610 | 110 | 0 | 0 | 3 | 64 | 36 | 0 | 0 | 0 | 25 | 199 |  | 5341 | 2968 | 8309 | 3211 | 801 | 1057 | 110 | 1706 | 969 | 46 | 0 | 132 | 90 | 187 | 0 | 90.88
11:00 | 0 | 0 | 0 | 180 | 0 | 67 | 0 | 312 | 269 |  | 0 | 225 | 0 | 61 | 0 | 30 | 0 | 0 | 0 | 71 | 24 | 115 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 22 | 22 | 28 | 25 | 29 | 42 | 0 | 30 | 0 | 0 | 0 | 8 | 151 | 0 | 0 | 0 |  | 12 | 8 | 17 | 22 | 0 | 31 | 0 | 2 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 63 | 38 | 30 | 0 | 0 | 0 | 0 | 8 | 16 | 8 | 13 | 15 | 94 | 36 | 0 | 10 | 2 | 0 | 43 | 50 | 30 | 0 | 0 | 65 | 0 | 0 | 178 | 19 | 24 | 10 | 0 | 22 | 3 | 10 | 97 | 14 | 25 | 76 | 25 | 136 | 20 | 25 | 17 | 79 | 420 | 68 | 105 | 68 | 4 | 200 | 36 | 53 | 0 | 104 | 25 | 400 | 27 | 47 | 30 | 107 | 0 | 17 | 28 | 68 | 17 | 387 | 13 | 0 |  | 896 | 0 | 155 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 85 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 8 | 0 | 15 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 53 | 0 | 35 | 0 | 34 | 0 | 6 | 37 | 590 | 110 | 0 | 0 | 4 | 73 | 36 | 0 | 0 | 0 | 29 | 200 |  | 5647 | 2953 | 8600 | 3167 | 896 | 1047 | 74 | 1976 | 950 | 30 | 13 | 140 | 94 | 213 | 0 | #REF!
12:00 | 0 | 0 | 0 | 180 | 0 | 71 | 0 | 312 | 268 |  | 0 | 225 | 0 | 78 | 0 | 45 | 0 | 0 | 0 | 72 | 8 | 115 | 0 | 0 | 0 | 0 | 17 | 55 | 17 | 22 | 22 | 27 | 25 | 29 | 42 | 0 | 30 | 0 | 0 | 0 | 8 | 151 | 0 | 0 | 0 |  | 12 | 8 | 17 | 22 | 0 | 12 | 0 | 2 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 60 | 42 | 30 | 0 | 0 | 0 | 0 | 8 | 19 | 8 | 13 | 15 | 104 | 35 | 0 | 10 | 2 | 0 | 43 | 53 | 30 | 0 | 0 | 62 | 0 | 0 | 178 | 18 | 25 | 10 | 0 | 22 | 3 | 50 | 97 | 132 | 95 | 77 | 92 | 135 | 20 | 25 | 17 | 80 | 422 | 68 | 105 | 68 | 4 | 266 | 36 | 53 | 0 | 106 | 25 | 394 | 30 | 48 | 35 | 107 | 0 | 17 | 27 | 115 | 17 | 381 | 30 | 0 |  | 896 | 0 | 145 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 100 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 8 | 0 | 15 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 53 | 0 | 35 | 0 | 34 | 0 | 6 | 37 | 590 | 110 | 0 | 0 | 4 | 77 | 36 | 0 | 0 | 0 | 32 | 174 |  | 6106 | 2918 | 9024 | 3158 | 896 | 1035 | 369 | 2118 | 924 | 30 | 30 | 140 | 104 | 220 | 0 | 90.88
13:00 | 0 | 0 | 0 | 180 | 0 | 70 | 0 | 318 | 277 |  | 0 | 225 | 0 | 89 | 0 | 45 | 0 | 0 | 0 | 72 | 8 | 133 | 0 | 0 | 0 | 0 | 17 | 55 | 17 | 22 | 22 | 26 | 33 | 29 | 49 | 0 | 46 | 0 | 0 | 0 | 8 | 151 | 0 | 0 | 0 |  | 12 | 8 | 17 | 22 | 0 | 12 | 0 | 2 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 60 | 44 | 30 | 0 | 5 | 0 | 27 | 8 | 19 | 8 | 13 | 15 | 110 | 35 | 0 | 10 | 2 | 20 | 43 | 53 | 0 | 0 | 0 | 63 | 1 | 0 | 178 | 18 | 25 | 10 | 0 | 22 | 3 | 78 | 97 | 185 | 96 | 78 | 92 | 135 | 18 | 25 | 17 | 79 | 422 | 68 | 88 | 68 | 4 | 281 | 36 | 53 | 0 | 107 | 25 | 358 | 17 | 46 | 35 | 107 | 0 | 17 | 26 | 115 | 17 | 359 | 9 | 0 |  | 896 | 0 | 145 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 75 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 8 | 0 | 15 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 56 | 0 | 57 | 0 | 90 | 0 | 6 | 37 | 650 | 110 | 0 | 0 | 4 | 71 | 56 | 0 | 0 | 0 | 24 | 198 |  | 6195 | 3067 | 9262 | 3111 | 896 | 1022 | 451 | 2223 | 1008 | 46 | 9 | 185 | 110 | 201 | 0 | 90.88
14:00 | 0 | 0 | 0 | 180 | 0 | 70 | 0 | 318 | 277 |  | 0 | 225 | 0 | 91 | 0 | 45 | 0 | 0 | 0 | 72 | 8 | 133 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 19 | 22 | 27 | 33 | 29 | 49 | 0 | 46 | 0 | 0 | 0 | 1 | 151 | 0 | 0 | 0 |  | 12 | 14 | 17 | 22 | 0 | 26 | 0 | 2 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 60 | 44 | 30 | 0 | 5 | 0 | 30 | 8 | 19 | 8 | 13 | 15 | 110 | 34 | 0 | 10 | 2 | 30 | 43 | 50 | 0 | 0 | 0 | 65 | 1 | 0 | 178 | 18 | 25 | 10 | 0 | 22 | 3 | 20 | 100 | 30 | 25 | 66 | 25 | 135 | 15 | 25 | 17 | 80 | 371 | 68 | 88 | 68 | 3 | 283 | 36 | 53 | 0 | 107 | 25 | 400 | 17 | 37 | 35 | 107 | 0 | 17 | 23 | 30 | 17 | 327 | 7 | 0 |  | 896 | 0 | 145 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 100 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 8 | 0 | 15 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 82 | 0 | 94 | 0 | 106 | 0 | 5 | 37 | 660 | 110 | 0 | 0 | 3 | 56 | 56 | 0 | 0 | 0 | 22 | 199 |  | 5698 | 3165 | 8863 | 3104 | 896 | 1021 | 100 | 2200 | 1019 | 46 | 7 | 194 | 110 | 166 | 0 | 90.88
15:00 | 0 | 0 | 0 | 180 | 0 | 68 | 0 | 326 | 286 |  | 0 | 225 | 0 | 89 | 0 | 45 | 0 | 0 | 0 | 72 | 8 | 133 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 19 | 22 | 27 | 33 | 28 | 45 | 0 | 46 | 0 | 0 | 0 | 8 | 151 | 0 | 0 | 0 |  | 12 | 24 | 17 | 22 | 0 | 35 | 0 | 2 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 59 | 44 | 30 | 0 | 5 | 0 | 30 | 8 | 22 | 8 | 15 | 15 | 104 | 35 | 0 | 10 | 1 | 30 | 43 | 50 | 0 | 0 | 0 | 64 | 1 | 0 | 178 | 18 | 25 | 10 | 0 | 22 | 3 | 0 | 85 | 0 | 0 | 67 | 3 | 136 | 11 | 25 | 17 | 81 | 419 | 69 | 88 | 68 | 2 | 285 | 36 | 53 | 0 | 107 | 25 | 400 | 18 | 25 | 35 | 107 | 0 | 17 | 15 | 18 | 17 | 377 | 0 | 0 |  | 896 | 0 | 145 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 100 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 8 | 0 | 15 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 94 | 0 | 94 | 0 | 113 | 0 | 4 | 37 | 580 | 110 | 0 | 0 | 2 | 38 | 45 | 0 | 0 | 0 | 15 | 200 |  | 5678 | 3065 | 8743 | 3210 | 896 | 1029 | 3 | 2198 | 940 | 46 | 0 | 204 | 104 | 113 | 0 | 90.87
16:00 | 0 | 0 | 0 | 180 | 0 | 70 | 0 | 328 | 286 |  | 0 | 225 | 0 | 91 | 0 | 35 | 0 | 0 | 0 | 77 | 16 | 133 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 22 | 26 | 33 | 28 | 49 | 0 | 46 | 0 | 0 | 0 | 8 | 151 | 0 | 0 | 0 |  | 12 | 25 | 18 | 44 | 0 | 37 | 0 | 2 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 59 | 44 | 30 | 0 | 5 | 0 | 30 | 8 | 22 | 8 | 16 | 15 | 108 | 34 | 0 | 10 | 0 | 30 | 43 | 53 | 25 | 0 | 0 | 60 | 1 | 0 | 178 | 18 | 25 | 10 | 0 | 22 | 3 | 0 | 90 | 100 | 50 | 67 | 50 | 125 | 5 | 30 | 25 | 100 | 414 | 69 | 105 | 83 | 1 | 300 | 36 | 68 | 0 | 107 | 42 | 390 | 25 | 10 | 37 | 107 | 0 | 17 | 6 | 18 | 17 | 402 | 0 | 0 |  | 897 | 0 | 145 | 0 | 16 | 0 | 0 | 0 | 5 | 0 | 8 | 130 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 8 | 0 | 15 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 94 | 0 | 94 | 0 | 113 | 0 | 2 | 113 | 540 | 0 | 0 | 0 | 0 | 13 | 17 | 0 | 0 | 0 | 7 | 200 |  | 6051 | 2970 | 9021 | 3248 | 897 | 938 | 200 | 2429 | 900 | 46 | 0 | 211 | 108 | 44 | 0 | 90.87
17:00 | 0 | 0 | 0 | 180 | 0 | 73 | 0 | 315 | 286 |  | 0 | 225 | 0 | 90 | 0 | 45 | 0 | 0 | 0 | 77 | 33 | 133 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 22 | 26 | 33 | 28 | 49 | 0 | 46 | 0 | 0 | 0 | 8 | 152 | 0 | 0 | 0 |  | 12 | 30 | 51 | 44 | 0 | 38 | 0 | 2 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 65 | 44 | 30 | 0 | 5 | 0 | 30 | 8 | 22 | 8 | 16 | 15 | 106 | 36 | 0 | 10 | 0 | 30 | 43 | 53 | 25 | 0 | 0 | 62 | 1 | 0 | 178 | 18 | 25 | 10 | 0 | 22 | 3 | 0 | 97 | 0 | 0 | 49 | 0 | 7 | 0 | 50 | 109 | 118 | 404 | 50 | 105 | 85 | 0 | 300 | 36 | 87 | 0 | 108 | 50 | 400 | 35 | 0 | 144 | 107 | 0 | 17 | 1 | 57 | 17 | 402 | 0 | 0 |  | 896 | 0 | 145 | 0 | 16 | 0 | 0 | 0 | 36 | 0 | 8 | 130 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 8 | 0 | 16 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 94 | 0 | 106 | 0 | 113 | 0 | 0 | 95 | 550 | 0 | 0 | 0 | 0 | 2 | 17 | 0 | 0 | 0 | 0 | 248 |  | 6054 | 3041 | 9095 | 3246 | 896 | 950 | 0 | 2610 | 958 | 46 | 0 | 280 | 106 | 3 | 0 | 90.87
18:00 | 0 | 0 | 0 | 180 | 0 | 71 | 0 | 308 | 286 |  | 0 | 225 | 0 | 92 | 0 | 45 | 0 | 0 | 0 | 85 | 33 | 133 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 22 | 26 | 33 | 28 | 49 | 0 | 46 | 0 | 0 | 0 | 8 | 150 | 0 | 0 | 0 |  | 12 | 32 | 51 | 44 | 0 | 43 | 0 | 2 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 66 | 44 | 30 | 0 | 5 | 0 | 30 | 8 | 22 | 8 | 16 | 15 | 120 | 39 | 0 | 10 | 0 | 30 | 43 | 53 | 25 | 0 | 0 | 69 | 83 | 0 | 178 | 18 | 27 | 10 | 0 | 24 | 3 | 20 | 188 | 66 | 80 | 87 | 50 | 92 | 0 | 50 | 147 | 120 | 391 | 97 | 105 | 97 | 0 | 300 | 36 | 91 | 0 | 108 | 50 | 400 | 35 | 0 | 162 | 107 | 0 | 34 | 0 | 115 | 17 | 402 | 0 | 0 |  | 895 | 0 | 145 | 0 | 99 | 0 | 0 | 0 | 50 | 50 | 32 | 115 | 20 | 0 | 0 | 0 | 0 | 24 | 3 | 80 | 0 | 34 | 37 | 43 | 24 | 17 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 94 | 0 | 113 | 0 | 113 | 0 | 0 | 95 | 630 | 0 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 329 |  | 6840 | 3672 | 10512 | 3222 | 895 | 1041 | 216 | 3339 | 1119 | 46 | 0 | 514 | 120 | 0 | 0 | 90.87
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 0 | 71 | 0 | 301 | 252 |  | 0 | 225 | 0 | 89 | 0 | 45 | 0 | 0 | 0 | 87 | 33 | 100 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 22 | 26 | 33 | 28 | 49 | 0 | 46 | 0 | 0 | 0 | 10 | 150 | 0 | 0 | 0 |  | 12 | 32 | 51 | 44 | 0 | 44 | 0 | 2 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 66 | 44 | 30 | 0 | 5 | 0 | 31 | 10 | 22 | 8 | 28 | 15 | 110 | 46 | 0 | 11 | 0 | 30 | 43 | 53 | 25 | 0 | 0 | 70 | 84 | 0 | 178 | 18 | 27 | 10 | 0 | 24 | 3 | 0 | 268 | 15 | 0 | 88 | 0 | 95 | 0 | 50 | 155 | 120 | 333 | 98 | 105 | 105 | 0 | 300 | 36 | 91 | 0 | 101 | 50 | 370 | 17 | 0 | 162 | 107 | 0 | 35 | 0 | 115 | 17 | 372 | 0 | 0 |  | 894 | 0 | 150 | 0 | 114 | 0 | 0 | 0 | 41 | 85 | 32 | 109 | 21 | 0 | 0 | 0 | 0 | 24 | 4 | 25 | 0 | 34 | 40 | 11 | 29 | 21 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 94 | 0 | 113 | 0 | 113 | 0 | 0 | 95 | 710 | 0 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 307 |  | 6521 | 3698 | 10219 | 3097 | 894 | 1015 | 15 | 3403 | 1177 | 46 | 0 | 462 | 110 | 0 | 0 | 90.86
19:30 | 0 | 0 | 0 | 180 | 0 | 73 | 0 | 302 | 252 |  | 0 | 225 | 0 | 92 | 0 | 45 | 0 | 0 | 0 | 87 | 33 | 64 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 22 | 26 | 33 | 28 | 49 | 0 | 40 | 0 | 0 | 0 | 17 | 150 | 0 | 0 | 0 |  | 12 | 0 | 17 | 44 | 0 | 44 | 0 | 2 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 65 | 44 | 30 | 0 | 5 | 0 | 31 | 16 | 22 | 8 | 30 | 15 | 108 | 69 | 0 | 11 | 0 | 30 | 43 | 53 | 25 | 0 | 0 | 70 | 84 | 0 | 178 | 18 | 27 | 10 | 0 | 24 | 3 | 0 | 275 | 0 | 0 | 88 | 0 | 108 | 0 | 50 | 120 | 120 | 335 | 98 | 105 | 105 | 0 | 300 | 36 | 91 | 0 | 109 | 50 | 370 | 17 | 0 | 162 | 107 | 0 | 35 | 0 | 115 | 17 | 362 | 0 | 0 |  | 894 | 0 | 150 | 0 | 114 | 0 | 0 | 0 | 0 | 60 | 32 | 130 | 21 | 0 | 0 | 0 | 0 | 24 | 0 | 25 | 0 | 34 | 40 | 0 | 29 | 22 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 210 | 94 | 0 | 113 | 0 | 113 | 0 | 0 | 95 | 720 | 0 | 0 | 0 | 0 | 0 | 74 | 0 | 0 | 0 | 0 | 306 |  | 6424 | 3629 | 10053 | 3136 | 894 | 1039 | 0 | 3360 | 1186 | 40 | 0 | 290 | 108 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 180 | 0 | 73 | 0 | 301 | 274 |  | 0 | 225 | 0 | 92 | 0 | 45 | 0 | 0 | 0 | 87 | 33 | 64 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 22 | 26 | 33 | 28 | 49 | 0 | 40 | 0 | 0 | 0 | 17 | 151 | 0 | 0 | 0 |  | 9 | 0 | 17 | 44 | 0 | 44 | 0 | 3 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 64 | 44 | 30 | 0 | 5 | 0 | 29 | 16 | 22 | 8 | 30 | 15 | 108 | 70 | 0 | 0 | 0 | 30 | 43 | 53 | 25 | 0 | 0 | 70 | 84 | 0 | 178 | 18 | 27 | 10 | 0 | 24 | 3 | 0 | 277 | 0 | 0 | 87 | 0 | 108 | 0 | 50 | 120 | 120 | 384 | 98 | 105 | 105 | 0 | 232 | 36 | 91 | 0 | 109 | 50 | 380 | 17 | 0 | 162 | 107 | 0 | 35 | 0 | 115 | 17 | 363 | 0 | 0 |  | 894 | 0 | 150 | 0 | 114 | 0 | 0 | 0 | 0 | 60 | 32 | 130 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 223 | 94 | 0 | 113 | 0 | 113 | 0 | 0 | 95 | 720 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 0 | 305 |  | 6484 | 3487 | 9971 | 3226 | 894 | 1075 | 0 | 3273 | 1185 | 40 | 0 | 170 | 108 | 0 | 0 | 90.86
21:00 | 0 | 0 | 0 | 180 | 0 | 73 | 0 | 302 | 254 |  | 0 | 225 | 0 | 89 | 0 | 45 | 0 | 0 | 0 | 88 | 33 | 64 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 22 | 27 | 33 | 30 | 49 | 0 | 40 | 0 | 0 | 0 | 17 | 152 | 0 | 0 | 0 |  | 12 | 0 | 17 | 44 | 0 | 44 | 0 | 3 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 65 | 44 | 30 | 0 | 5 | 0 | 31 | 8 | 22 | 8 | 33 | 15 | 112 | 96 | 0 | 10 | 0 | 30 | 43 | 53 | 25 | 0 | 0 | 70 | 84 | 0 | 178 | 18 | 26 | 10 | 0 | 24 | 3 | 0 | 277 | 0 | 0 | 88 | 0 | 111 | 0 | 50 | 120 | 120 | 351 | 98 | 105 | 105 | 0 | 70 | 36 | 91 | 0 | 109 | 50 | 340 | 17 | 0 | 162 | 107 | 0 | 35 | 0 | 115 | 17 | 382 | 0 | 0 |  | 894 | 0 | 165 | 0 | 103 | 0 | 0 | 0 | 0 | 5 | 32 | 115 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 228 | 94 | 0 | 113 | 0 | 113 | 0 | 0 | 95 | 760 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 0 | 307 |  | 6198 | 3447 | 9645 | 3200 | 894 | 1061 | 0 | 2994 | 1227 | 40 | 0 | 117 | 112 | 0 | 0 | 90.86
22:00 | 0 | 0 | 0 | 180 | 0 | 73 | 0 | 302 | 255 |  | 0 | 225 | 0 | 50 | 0 | 45 | 0 | 0 | 0 | 87 | 33 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 22 | 27 | 33 | 30 | 8 | 0 | 40 | 0 | 0 | 0 | 8 | 152 | 0 | 0 | 0 |  | 12 | 0 | 17 | 44 | 0 | 44 | 0 | 7 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 65 | 44 | 30 | 0 | 5 | 0 | 0 | 8 | 22 | 8 | 33 | 15 | 108 | 103 | 0 | 10 | 0 | 30 | 43 | 53 | 25 | 0 | 0 | 40 | 84 | 0 | 178 | 18 | 26 | 10 | 0 | 24 | 3 | 0 | 278 | 0 | 0 | 88 | 0 | 134 | 0 | 50 | 120 | 118 | 352 | 98 | 88 | 105 | 0 | 70 | 36 | 91 | 0 | 109 | 50 | 340 | 17 | 0 | 108 | 107 | 0 | 35 | 0 | 115 | 17 | 382 | 0 | 0 |  | 894 | 0 | 170 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 235 | 70 | 0 | 70 | 0 | 34 | 0 | 0 | 95 | 740 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 0 | 306 |  | 5929 | 3182 | 9111 | 3167 | 894 | 1073 | 0 | 2590 | 1206 | 40 | 0 | 33 | 108 | 0 | 0 | 90.86
23:00 | 0 | 0 | 0 | 180 | 0 | 73 | 0 | 305 | 280 |  | 0 | 225 | 0 | 17 | 0 | 45 | 0 | 0 | 0 | 87 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 19 | 22 | 0 | 33 | 31 | 8 | 0 | 40 | 0 | 0 | 0 | 8 | 151 | 0 | 0 | 0 |  | 12 | 0 | 17 | 44 | 0 | 44 | 0 | 9 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 65 | 44 | 30 | 0 | 5 | 0 | 0 | 8 | 22 | 8 | 33 | 15 | 98 | 111 | 0 | 10 | 0 | 30 | 43 | 53 | 25 | 0 | 0 | 40 | 84 | 0 | 151 | 19 | 27 | 10 | 0 | 24 | 3 | 0 | 281 | 0 | 0 | 86 | 0 | 149 | 0 | 25 | 120 | 86 | 352 | 98 | 105 | 76 | 0 | 70 | 36 | 53 | 0 | 108 | 50 | 370 | 17 | 0 | 17 | 107 | 0 | 34 | 0 | 56 | 17 | 382 | 0 | 0 |  | 894 | 0 | 170 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 70 | 0 | 70 | 0 | 34 | 0 | 0 | 37 | 680 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 0 | 306 |  | 5618 | 3053 | 8671 | 3176 | 894 | 1089 | 0 | 2195 | 1146 | 40 | 0 | 33 | 98 | 0 | 0 | 90.86
24:00 | 0 | 0 | 0 | 180 | 0 | 73 | 0 | 309 | 280 |  | 0 | 225 | 0 | 17 | 0 | 35 | 0 | 0 | 0 | 41 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 19 | 25 | 9 | 33 | 32 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 |  | 12 | 0 | 17 | 22 | 0 | 44 | 0 | 11 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 40 | 45 | 40 | 0 | 5 | 0 | 0 | 8 | 22 | 8 | 33 | 15 | 100 | 111 | 0 | 10 | 0 | 30 | 43 | 53 | 25 | 0 | 0 | 70 | 84 | 0 | 151 | 19 | 28 | 10 | 0 | 24 | 3 | 0 | 191 | 0 | 0 | 48 | 0 | 149 | 0 | 25 | 120 | 75 | 417 | 49 | 105 | 34 | 0 | 70 | 36 | 54 | 0 | 108 | 29 | 363 | 17 | 0 | 17 | 107 | 0 | 17 | 0 | 35 | 17 | 373 | 0 | 0 |  | 801 | 0 | 180 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 111 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 159 | 0 | 0 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 258 | 70 | 0 | 70 | 0 | 47 | 0 | 0 | 35 | 640 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 0 | 306 |  | 5323 | 2944 | 8267 | 3229 | 801 | 1135 | 0 | 1824 | 1105 | 40 | 0 | 33 | 100 | 0 | 0 | 90.86
KWH | 0 | 0 | 0 | 4378500 | 0 | 1679000 | 0 | 7505920 | 6528000 |  | 0 | 5205500 | 0 | 1138560 | 0 | 969318 | 0 | 0 | 0 | 1267200 | 372816 | 1702080 | 0 | 0 | 0 | 0 | 529920 | 732309 | 548166 | 460512 | 600000 | 580860 | 779400 | 740100 | 692160 | 0 | 1050540 | 0 | 0 | 0 | 178023 | 3665040 | 0 | 0 | 0 |  | 293760 | 167746 | 509207 | 694440 | 0 | 654720 | 0 | 167520 | 0 | 0 | 0 | 0 | 6021000 | 0 | 0 | 1541150 | 1023480 | 769440 | 0 | 217844 | 0 | 253472 | 212563 | 446760 | 174780 | 584000 | 345910 | 2364480 | 1647360 | 0 | 252108 | 12700 | 327000 | 894200 | 1145400 | 628488 | 0 | 0 | 1473792 | 676800 | 0 | 4122810 | 421000 | 506220 | 225000 | 536420 | 451210 | 72336 | 214656 | 3864000 | 521665 | 363633 | 1279200 | 367323 | 2933712 | 133380 | 756480 | 1342080 | 1873454 | 9496000 | 1557600 | 1952832 | 1556472 | 26281 | 3078655 | 793353 | 1639266 | 55860 | 1998360 | 787200 | 9136800 | 491520 | 312480 | 1340640 | 2347255 | 0 | 550440 | 180625 | 1290240 | 434160 | 9603300 | 58545 | 0 |  | 19460363 | 0 | 4077216 | 0 | 613440 | 0 | 0 | 0 | 98880 | 228224 | 188625 | 2852000 | 421400 | 0 | 0 | 0 | 0 | 59088 | 3926 | 116057 | 0 | 365676 | 71420 | 139200 | 48667 | 432960 | 0 | 225972 | 0 | 0 | 3903900 | 0 | 0 | 4189173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5337672 | 1614240 | 0 | 1817184 | 0 | 1584739 | 0 | 35989 | 1531968 | 16658300 | 1704300 | 0 | 0 | 27900 | 481680 | 842688 | 0 | 0 | 0 | 184330 | 5136700 |  | 133476507 | 74453877 | 207930384 | 78089689 | 19460363 | 26181964 | 1467277 | 48904494 | 25698900 | 1050540 | 58545 | 3258767 | 2364480 | 1395365 | 0
Fuel Cost | 0 | 0 | 0 | 6523965 | 0 | 2233070 | 0 | 7881216 | 7050240 |  | 0 | 5673995 | 0 | 12729100.8 | 0 | 12843463.5 | 0 | 0 | 0 | 18526464 | 5245521.12 | 27590716.8 | 0 | 0 | 0 | 0 | 6740582.4 | 9886171.5 | 7350906.06 | 345384 | 450000 | 0 | 0 | 0 | 11773641.6 | 0 | 283645.8 | 0 | 0 | 0 | 2910676.05 | 3811641.6 | 0 | 0 | 0 |  | 3833568 | 2798003.28 | 8666703.14 | 9381884.4 | 0 | 7575110.4 | 0 | 557841.6 | 0 | 0 | 0 | 0 | 6562890 | 0 | 0 | 1880203 | 1156532.4 | 1146465.6 | 0 | 363799.48 | 0 | 4377461.44 | 2858972.35 | 612061.2 | 131085 | 1022000 | 259432.5 | 16976966.4 | 1795622.4 | 0 | 342866.88 | 202438 | 447990 | 1180344 | 1992996 | 1087284.24 | 0 | 0 | 2859156.48 | 1543104 | 0 | 4164038.1 | 905150 | 754267.8 | 445500 | 536420 | 338407.5 | 54975.36 | 4499189.76 | 52743600 | 10934098.4 | 7516294.11 | 17243616 | 7592566.41 | 40631911.2 | 1559212.2 | 7806873.6 | 18332812.8 | 24860734.58 | 8736320 | 18940416 | 28237950.72 | 19689370.8 | 0 | 36143409.7 | 8639614.17 | 17425397.58 | 758020.2 | 25758860.4 | 9273216 | 8405856 | 6365184 | 4515336 | 17012721.6 | 26711761.9 | 0 | 7188746.4 | 2158468.75 | 19314892.8 | 5717887.2 | 0 | 0 | 0 |  | 58381089 | 0 | 4566481.92 | 0 | 6385910.4 | 0 | 0 | 0 | 1780828.8 | 4108032 | 2710541.25 | 3194240 | 817516 | 0 | 0 | 0 | 0 | 990905.76 | 68665.74 | 1815131.48 | 0 | 6055594.56 | 1207712.2 | 1897296 | 821012.29 | 896227.2 | 0 | 171060.804 | 0 | 0 | 20651631 | 0 | 0 | 4859440.68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5284295.28 | 21695385.6 | 0 | 21497286.72 | 0 | 20126185.3 | 0 | 397678.45 | 18598091.52 | 150091283 | 1738386 | 0 | 0 | 315549 | 5650106.4 | 12918407.04 | 0 | 0 | 0 | 0 | 0 |  | 703376281.46 | 379691971.394 | 1083068252.854 | 72658360.824 | 58381089 | 32121408.2 | 30542148.68 | 632337758.22 | 170742914 | 283645.8 | 0 | 54225172.93 | 16976966.4 | 14798788.8 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 0 | 71 | 0 | 312 | 268 |  | 0 | 225 | 0 | 78 | 0 | 45 | 0 | 0 | 0 | 72 | 8 | 115 | 0 | 0 | 0 | 0 | 17 | 55 | 17 | 22 | 22 | 27 | 25 | 29 | 42 | 0 | 30 | 0 | 0 | 0 | 8 | 151 | 0 | 0 | 0 |  | 12 | 8 | 17 | 22 | 0 | 12 | 0 | 2 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 60 | 42 | 30 | 0 | 0 | 0 | 0 | 8 | 19 | 8 | 13 | 15 | 104 | 35 | 0 | 10 | 2 | 0 | 43 | 53 | 30 | 0 | 0 | 62 | 0 | 0 | 178 | 18 | 25 | 10 | 0 | 22 | 3 | 50 | 97 | 132 | 95 | 77 | 92 | 135 | 20 | 25 | 17 | 80 | 422 | 68 | 105 | 68 | 4 | 266 | 36 | 53 | 0 | 106 | 25 | 394 | 30 | 48 | 35 | 107 | 0 | 17 | 27 | 115 | 17 | 381 | 30 | 0 |  | 896 | 0 | 145 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 100 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 8 | 0 | 15 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 53 | 0 | 35 | 0 | 34 | 0 | 6 | 37 | 590 | 110 | 0 | 0 | 4 | 77 | 36 | 0 | 0 | 0 | 32 | 174 |  | 9024 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 0 | 71 | 0 | 308 | 286 | 0 | 0 | 225 | 0 | 92 | 0 | 45 | 0 | 0 | 0 | 85 | 33 | 133 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 22 | 26 | 33 | 28 | 49 | 0 | 46 | 0 | 0 | 0 | 8 | 150 | 0 | 0 | 0 | 0 | 12 | 32 | 51 | 44 | 0 | 43 | 0 | 2 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 66 | 44 | 30 | 0 | 5 | 0 | 30 | 8 | 22 | 8 | 16 | 15 | 120 | 39 | 0 | 10 | 0 | 30 | 43 | 53 | 25 | 0 | 0 | 69 | 83 | 0 | 178 | 18 | 27 | 10 | 0 | 24 | 3 | 20 | 188 | 66 | 80 | 87 | 50 | 92 | 0 | 50 | 147 | 120 | 391 | 97 | 105 | 97 | 0 | 300 | 36 | 91 | 0 | 108 | 50 | 400 | 35 | 0 | 162 | 107 | 0 | 34 | 0 | 115 | 17 | 402 | 0 | 0 |  | 895 | 0 | 145 | 0 | 99 | 0 | 0 | 0 | 50 | 50 | 32 | 115 | 20 | 0 | 0 | 0 | 0 | 24 | 3 | 80 | 0 | 34 | 37 | 43 | 24 | 17 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 94 | 0 | 113 | 0 | 113 | 0 | 0 | 95 | 630 | 0 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 329 |  | 10512 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 0 | 71 | 0 | 310 | 286 | 0 | 0 | 225 | 0 | 92 | 0 | 45 | 0 | 0 | 0 | 85 | 33 | 133 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 22 | 26 | 33 | 33 | 50 | 0 | 46 | 0 | 0 | 0 | 17 | 150 | 0 | 0 | 0 | 0 | 12 | 32 | 51 | 44 | 0 | 43 | 0 | 2 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 66 | 44 | 30 | 0 | 5 | 0 | 30 | 8 | 22 | 8 | 33 | 15 | 165 | 70 | 0 | 10 | 0 | 30 | 43 | 50 | 25 | 0 | 0 | 66 | 83 | 0 | 178 | 19 | 27 | 10 | 0 | 24 | 3 | 100 | 275 | 150 | 80 | 55 | 50 | 149 | 0 | 50 | 200 | 120 | 400 | 55 | 105 | 105 | 0 | 300 | 36 | 91 | 0 | 108 | 50 | 400 | 17 | 0 | 162 | 107 | 0 | 34 |  | 115 | 17 | 400 |  |  |  | 913 | 0 | 150 | 0 | 115 | 0 | 0 | 0 | 50 | 75 | 32 | 130 | 20 | 0 | 0 | 0 | 0 | 34 | 20 | 80 | 0 | 34 | 37 | 43 | 24 | 17 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 160 |  | 0 | 0 | 0 | 50 | 0 | 0 | 200 | 94 | 0 | 113 | 0 | 113 | 0 | 0 | 95 | 800 | 0 |  | 0 |  |  | 115 | 0 |  |  |  | 300
Forecast for Day | 0 | 0 | 0 | 180 | 0 | 71 | 0 | 300 | 255 | 0 | 0 | 225 | 0 | 80 | 0 | 45 | 0 | 0 | 0 | 75 | 24 | 115 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 22 | 27 | 33 | 31 | 42 | 0 | 46 | 0 | 0 | 0 | 17 | 150 | 0 | 0 | 0 | 0 | 12 | 20 | 17 | 22 | 0 | 26 | 0 | 2 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 66 | 40 | 15 | 0 | 5 | 0 | 0 | 8 | 22 | 8 | 33 | 15 | 143 | 70 | 0 | 10 | 1.6 | 30 | 43 | 50 | 25 | 0 | 0 | 66 | 0 | 0 | 177 | 19 | 20 | 10 | 0 | 22 | 3 | 100 | 97 | 100 | 50 | 40 | 0 | 125 | 20 | 25 | 100 | 75 | 400 | 45 | 105 | 51 | 5 | 260 | 36 | 70 | 0 | 108 | 25 | 400 | 17 | 50 | 90 | 107 | 0 | 17 | 30 | 115 | 17 | 400 |  |  |  | 913 | 0 | 150 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 8 | 0 | 17 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 64 | 0 | 85 | 0 | 90 | 0 | 8 | 90 | 800 | 0 |  | 0 | 6 | 100 | 70 | 0 |  |  | 30 | 190
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 0 | 70 | 0 | 355 | 290 | 0 | 0 | 225 | 0 | 49 | 0 | 45 | 0 | 0 | 0 | 30 | 8 | 116 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 0 | 22 | 21 | 33 | 33 | 40 | 0 | 40 | 0 | 0 | 0 | 13 | 151 | 0 | 0 | 0 | 0 | 11 | 0 | 17 | 22 | 0 | 25 | 0 | 3 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 31 | 45 | 30 | 0 | 5 | 0 | 0 | 8 | 22 | 8 | 24 | 15 | 92 | 72 | 0 | 10 | 1 | 30 | 43 | 31 | 25 | 0 | 0 | 40 | 0 | 0 | 177 | 19 | 26 | 10 | 0 | 21 | 3 | 0 | 97 | 0 | 0 | 47 | 0 | 112 | 9 | 25 | 51 | 92 | 417 | 47 | 105 | 34 | 1 | 70 | 36 | 53 | 0 | 105 | 25 | 395 | 17 | 18 | 17 | 107 | 0 | 17 | 10 | 35 | 17 | 407 | 0 | 0 | 0 | 659 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 19 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 269 | 53 | 0 | 79 | 0 | 91 | 0 | 1 | 37 | 600 | 0 | 0 | 0 | 1 | 25 | 35 | 0 | 0 | 0 | 0 | 142 | 0 |  |  |  |  | 53689083 |  | 0
53689083
| Minimum Generation |  | 6884 | 5:00
| Highest Generation |  | 10512 | 18:00
| Day Peak Generation |  | 9024 | 12:00
| Evening Peak Generation |  | 10512 | 18:00
| HVDC Max Flow |  | 897 | 16:00
| HVDC EvPeak Flow |  | 895 | 18:00
| Load factor L.F |  | 82.42% | [161 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2022-11-23
Till now the maximum generation is : - |  |  |  | 14782 | 21:00 | Hrs on | 2022-04-16
The Summary of Yesterday's |  |  | 2022-11-22 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 9024 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 6735
Evening Peak Generation : |  |  | 10512 | MW Hour : | 18:00 | Available Max Generation : |  | 11217
E.P. Demand (at gen end) : |  |  | 10512 | MW Hour : | 18:00 | Max Demand (Evening) : |  | 10800
Maximum Generation : |  |  | 10512 | MW Hour : | 18:00 | Reserve(Generation end) |  | 417
Total Gen. (MKWH) : |  |  | 207.9304 | System Load Factor : | 82.42% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 740 | MW at | 8:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2022-11-23
Actual : |  | 90.85 | Ft.(MSL) , | Rule curve : | 106.8 | Ft.( MSL )
Gas Consumed : |  | Total = | 794.28 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 104779769.024
: |  |  | Coal : | 170742914 | Oil : | 717105079.83 | Total : | 992627762.854
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 0 | 0:00 | 4098.4931 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 1161.0318 |  |  | 0 | 0%
Khulna Area |  | 0 | 0:00 | 1532.4656 |  |  | 0 | 0%
Rajshahi Area |  | 0 | 0:00 | 1359.6786 |  |  | 0 | 0%
Cumilla Area |  | 0 | 0:00 | 1157.4564 |  |  | 0 | 0%
Mymensingh Area |  | 0 | 0:00 | 956.2319 |  |  | 0 | 0%
Sylhet Area |  | 0 | 0:00 | 427.3941 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 348.401 |  |  | 0 | 0%
Rangpur Area |  | 0 | 0:00 | 755.0075 |  |  | 0 | 0%
Total |  | 0 |  | 11796.16 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
[5 empty] | 1) Barapukuria ST: Unit-1, 2 |  | 10) Ashuganj-225 MW
[5 empty] | 2) Ghorasal-3, 4, 7 |  | 11) Bibiana-II 341 MW CCPP (Summit)
3) Ashuganj-5
4) Baghabari-71,100 MW
5) Raozan unit-1 & 2
6) Siddhirganj 210 MW .
7) Shajibazar 330 MW
8) Sirajganj-2
9) Ashuganj(N)-360 MW
Outage Time | Restore Time
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
08:11 | 16:20 | Barapukuria-Rangpur 132 kV Ckt-1 Scheduled S/D due to annual maintenance.
08:14 | 17:07 | Jhenaidah-Khulna 230kV Ckt-1 Scheduled S/D due to annual maintenance.
08:19 | 15:38 | Bagerhat-Goalpara 132 kV Ckt-1 Scheduled S/D due to annual maintenance.
08:19 | 16:33 | Dohazari-Sikalbaha 132 kV Ckt-1 Scheduled S/D due to annual maintenance.
08:24 | 16:27 | Jamalpur-Mymensingh 132kV Ckt-2 Scheduled S/D due to annual maintenance.
08:30 | 16:10 | Sirajganj 132/33kV S/S T2-(425) LT Scheduled S/D due to annual maintenance.
08:31 | 16:10 | Sirajganj 132/33kV S/S T2-(425) HT Scheduled S/D due to annual maintenance.
08:43 | 15:27 | Brahmanbaria 132/33kV S/S 402T LT Scheduled S/D due to annual maintenance.
08:43 | 15:27 | Brahmanbaria 132/33kV S/S 402T HT Scheduled S/D due to annual maintenance.
09:03 | 17:11 | Mithapukur 132/33kV S/S TR-1(404T) LT Scheduled S/D due to annual maintenance.
09:03 | 17:10 | Mithapukur 132/33kV S/S TR-1(404T) HT Scheduled S/D due to annual maintenance.
09:12 | 16:03 | Narail 132/33kV S/S TR1 (403-T) LT Scheduled S/D Due to
Annual Maintenance works of TR-01 & Associates equipment.
09:13 | 16:02 | Narail 132/33kV S/S TR1 (403-T) HT Scheduled S/D Due to
Annual Maintenance works ofTR-01 with associated equipment.
09:16 | 16:20 | Tongi 230/132/33kV S/S T-3 LT Scheduled S/D
09:18 | 16:20 | Tongi 230/132/33kV S/S T-3 HT Scheduled S/D
10:43 | 12:41 | Keraniganj-Sreenagar 132kV Ckt-1 Scheduled S/D from
Keraniganj 230/132/33kV end Due to Yearly Maintenance
| 12:36 | Patuakhali 132/33kV S/S 405T (T-1) HT is restored.
| 12:36 | Patuakhali 132/33kV S/S 405T (T-1) LT is restored.
12:51 | 15:19 | Patuakhali 132/33kV S/S 415T (T-2) LT Scheduled S/D Due toTen delta test
12:52 | 14:18 | Patuakhali 132/33kV S/S 415T (T-2) HT Scheduled S/D Due to Ten delta test
13:01 | 15:25 | Keraniganj-Sreenagar (T at Powerpac 100MW) 132kV Ckt-2
Scheduled S/D from Keraniganj 230/132/33kV end Due to Yearly Maintenance
15:58 | 16:39 | Patuakhali-Payra 132kV Ckt-1 Project Work S/D from
Patuakhali 132/33kV end Due to Testing purpose.
| 16:04 | Bheramara(GK) 132/33kV S/S TR-4 HT is restored.
| 16:09 | Bhandaria 132/33kV S/S Transformer-2 HT is restored.
| 16:26 | Bhandaria 132/33kV S/S Transformer-2 LT is restored.
| 16:33 | Naogaon 132/33kV S/S T-1 HT is restored.
| 16:35 | Naogaon 132/33kV S/S T-1 LT is restored.
| 16:55 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-4 (50/75MVA) HT is restored.
| 16:58 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-4 (50/75 MVA) LT is restored.
| 17:13 | Kulaura 132/33kV S/S TR-2 LT is restored.
| 17:13 | Kulaura 132/33kV S/S TR-2 HT is restored.
05:00 |  | Minimum Generation is 6884MW
07:04 |  | Patuakhali 132/33kV S/S 425T (T-3) LT Scheduled S/D Due to Annual Maintenance.
07:09 |  | Patuakhali 132/33kV S/S 425T (T-3) HT Scheduled S/D Due to
T3 xformer & associate Bay for annual maintenance
07:11 |  | Jashore 132/33kV S/S T-1 HT Forced S/D Due to Oil leakage removing on B-ph bushing LT side
07:11 |  | Jashore 132/33kV S/S T-1 LT Forced S/D Due to Oil leakage removing on B-ph bushing
07:29 |  | Manikganj 132/33kV S/S 132/33 kV Transformer GT-4 (50/75
07:42 |  | Naogaon 132/33kV S/S Nao-SPPP Ckt-1 Scheduled S/D Due to A/M.
07:47 |  | Bibiyana-Kaliakoir 400 kV Ckt-1 Scheduled S/D from Bibiyana 400/230kV end Due to For AM
07:52 |  | Jamalpur-Mymensingh 132kV Ckt-2 Scheduled S/D Due to Annual maintenance
07:50 |  | Jhenaidah-Khulna 230kV Ckt-1 Scheduled S/D from Khulna(S)

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2022-11-22 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Line O/L
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4378500
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 71 | 1679000 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 308 | 7505920 | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 286 | 6528000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 5205500 | GT-2 S/D due to Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 92 | 1138560 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 0 | 0 | Under maint.
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 45 | 969318 | Engine problem
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 460512
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 85 | 1267200 | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 33 | 372816 | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 529920
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 133 | 1702080 | Engine problem
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 732309
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 548166 | Engine problem
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 48 | 1180860 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 779400
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 28 | 740100 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 49 | 692160 | 0:00
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 188 | 3864000 | Fuel shortage
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 66 | 521665 | Fuel conservation
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 80 | 363633 | Fuel conservation
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 50 | 367323 | Fuel conservation
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 92 | 2933712 | Engine problem
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 1952832
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 35 | 491520 | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 1340640
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 180625
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 434160 | Fuel shortage
| Dhaka area Total |  |  |  | 5847 | 2574 | 48860431
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Machine problem
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 8 | 178023 | Engine problem
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 133380
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 43 | 654720 | Engine problem
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 46 | 1050540 | Low water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 150 | 3665040 | ST Under maint
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 97 | 1556472 | Engine problem
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 32 | 167746 | Fuel shortage
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 509207 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 44 | 694440 | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 50 | 756480 | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 0 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 2 | 167520
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 26281
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 300 | 3078655
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 36 | 793353 | Engine problem
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 91 | 1639266 | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 50 | 787200
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 107 | 2347255 | Engine problem
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 58545 | On test.
| Chattogram area Total |  |  |  | 2382 | 1107 | 18264123
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 0 | 0 | Gas shortage
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 0 | 0 | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 250 | 6021000 | Gas shortage
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+136*1 | 284 | 402 | 9603300 | On test.
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 44 | 1023480 | Engine problem
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 30 | 769440 | Gas shortage
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 0 | 0 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 5 | 217844 | Gas shortage
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 120 | 1873454 | Fuel shortage
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 30 | 253472 | Engine problem
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 66 | 1541150 | Machine problem
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 147 | 1342080 | High voltage
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 446760
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 174780 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 120 | 2364480
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 16 | 584000 | Engine problem
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 8 | 212563 | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 15 | 345910 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 20 | 214656 | Fuel conservation
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 55860 | Fuel shortage
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 108 | 1998360 | Engine problem
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 34 | 550440 | Engine problem
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 115 | 1290240
| Cumilla Area Total |  |  |  | 3169 | 1560 | 30883269
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 39 | 1647360 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 10 | 252108 | Gas shortage
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 12700
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 87 | 1279200 | Engine problem
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 97 | 1557600 | Engine problem
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 312480
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 293760 | Engine problem
| Mymensingh Area Total |  |  |  | 614 | 245 | 5355208
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 30 | 327000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 43 | 894200 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Gas shortage
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 1145400
| Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 25 | 628488 | Gas shortage
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 3 | 72336 | Gas shortage
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 69 | 1473792
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 83 | 676800
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 178 | 4122810 | Gas shortage
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 421000 | Gas shortage
| Sylhet 50MW PP (EPL) |  | NENP | 27*2 | 50 | 27 | 506220 | Gas shortage
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 451210 | Gas shortage
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 0 | 536420 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 391 | 9496000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 225000
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 400 | 9136800
| Sylhet Area Total |  |  |  | 2477 | 1354 | 30113476
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Fuel shortage
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 895 | 19460363
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 99 | 613440 | Engine problem
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 50 | 98880 | Engine problem
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 50 | 228224 | High voltage
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 145 | 4077216 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 32 | 188625 | Fuel shortage
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Fuel conservation
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 94 | 1614240 | Engine problem
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Fuel shortage
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 481680
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 0 | 0 | 0 | On test.
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 0 | 0 | 0 | 0 | On test.
| Khulna Area Total |  |  |  | 2384 | 1365 | 26762668
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Line O/L
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 20 | 421400 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 115 | 2852000 | Gas shortage
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 630 | 16658300 | Line O/L
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 0 | 1704300 | Under maint.
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Line O/L
| Barisal 307 MW |  | BCPCL | 0 | 0 | 329 | 5136700 | On test.
| Barisal Area Total |  |  |  | 1958 | 1094 | 26772700
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 24 | 59088 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 3 | 3926
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contract Expired
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 34 | 365676 | Engine problem
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 37 | 71420 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 157 | 4189173 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 187 | 5337672 | Gas shortage
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 24 | 48667 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 17 | 432960 | Engine problem
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 225972
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 43 | 139200 | Engine problem
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 80 | 116057 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Fuel conservation
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 1817184
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 95 | 1531968 | Engine problem
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 27900
| Rajshahi Area Total |  |  |  | 2129 | 825 | 14366863
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 160 | 3903900 | Machine problem
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 1584739
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 35989
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 115 | 842688
| Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 184330
| Rangpur Area Total |  |  |  | 750 | 388 | 6551646
| Total |  |  |  | 21710 | 10512 | 207930384
| Eastern Grid Total |  |  |  | 14489 | 6840 | 133476507
| Western Grid Total |  |  |  | 7221 | 3672 | 74453877
| National Grid Total |  |  |  | 21710 | 10512 | 207930384
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2022-11-22
| (a) ENTIRE EASTERN GRID : |  | 7162.66 | MW | (b) ENTIRE WESTERN GRID : |  | 3007.85 | MW
| i) Dhaka area |  | 3964.46 | MW | i) Khulna area |  | 1110 | MW
| ii) Chittagong area |  | 1223.2 | MW | ii) Rajshahi area |  | 954.2 | MW
| iii) Comilla area |  | 846 | MW | iii) Barisal area |  | 242.65 | MW
| iv) Mymensingh area |  | 764 | MW | iv) Rangpur area |  | 701 | MW
| v) Sylhet area |  | 365 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 10170.51 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 24 | 15:00 | Chowmuhani | 124 | 20:00 | Kaptai | 3.5 | 18:00 | Nawabganj | 27 | 20:00 | Sholosohor | 28 | 18:00
2 | AKSML | 85 | 06:00 | Chuadanga | 68 | 18:00 | Kazla | 84 | 13:00 | Netrakona | 82 | 18:00 | Shyampur | 152 | 00:00
3 | Aftabnagar | 26 | 18:00 | Coxsbazar | 97 | 13:00 | Keranigonj | 58 | 19:00 | New | 63 | 12:00 | Siddhirganj | 90 | 15:00
4 | Agargaon | 59 | 13:00 | Cumilla(N) | 87 | 18:00 | Khagrachori | 20 | 18:00 | Niamatpur | 46 | 18:30 | Sirajganj | 72 | 18:30
5 | Agrabad | 56 | 14:00 | Cumilla(S) | 120 | 18:00 | Khulna | 72 | 18:00 | Noapara | 31 | 18:00 | Sonargaon | 94 | 11:00
6 | Amnura | 33 | 18:30 | Daudkandi | 102 | 18:30 | Khulshi | 158 | 13:00 | PHP | 8 | 19:30 | Sreemongol | 39 | 18:00
7 | Ashuganj | 65 | 00:00 | Dhaka | 30 | 12:00 | Kishoreganj | 98 | 20:00 | Pabna | 77 | 18:00 | Srinagar | 29.04 | 20:00
8 | BSRM | 135 | 21:00 | Dhamrai | 100 | 18:00 | Kodda | 245 | 16:00 | Palashbari | 86 | 18:00 | Sunamganj | 33 | 19:30
9 | Bagerhat | 80 | 18:00 | Dhanmondi | 87 | 13:00 | Kulaura | 30 | 18:00 | Panchagarh | 55 | 18:00 | Sylhet | 105 | 18:00
10 | Bakulia | 100 | 18:00 | Dohazari | 74 | 18:30 | Kurigram | 45 | 18:00 | Patuakhali | 75 | 21:00 | TK | 10.7 | 18:00
11 | Banani | 32 | 13:00 | Faridpur | 98 | 18:00 | Kushtia | 93 | 18:00 | Payra | 0.74 | 12:00 | Tangail | 139 | 18:30
12 | Bangabhaban | 12 | 10:00 | Fatullah | 60 | 15:00 | Lalbag | 71 | 18:00 | Postogola | 32 | 13:00 | Thakurgaon | 65 | 18:00
13 | Barapukuria | 41 | 18:00 | Fenchuganj | 30 | 18:00 | Lalmonirhat | 34 | 18:00 | Purbachal | 6 | 13:00 | Tongi | 106 | 11:00
14 | Barguna | 12 | 19:30 | Feni | 84 | 20:00 | Madanganj | 83 | 18:00 | Purbasadipur | 94 | 18:00 | Ullon | 28 | 18:00
15 | Barishal | 69 | 12:00 | GPH | 91 | 22:00 | Madaripur | 59 | 21:00 | Rahanpur_I | 18.6 | 20:00 | Uttara | 60 | 13:00
16 | Barishal-230 | 46 | 18:00 | Ghorashal | 55 | 20:00 | Madartek | 59 | 18:30 | Rahim | 40 | 09:00 | UttaraNew | 16 | 16:00
17 | Baroaulia | 71 | 18:00 | Goalpara | 16 | 13:00 | Madunaghat | 44 | 22:00 | Rajbari | 44 | 18:00 | Zigatola | 35 | 17:00
18 | Baroirhat | 34 | 19:00 | Gollamari | 36 | 12:00 | Magura | 40 | 18:00 | Rajendrapur | 86 | 00:00
19 | Bashundhara | 127 | 18:00 | Gopalganj | 64 | 19:30 | Mahasthangarh | 44 | 18:00 | Rajshahi | 92 | 18:00
20 | BashundharaCement | 7 | 08:00 | Gulshan | 76 | 13:00 | Manikganj | 60 | 19:00 | Rajshahi-230 | 24 | 13:00
21 | Beanibazar | 38 | 18:00 | Halishahar | 111 | 12:00 | Maniknagar | 54 | 13:00 | Ramganj | 70 | 18:00
22 | Benapole | 42 | 18:00 | HaripurSBU | 158 | 16:00 | Matarbari | 30 | 18:00 | Rampur | 21 | 18:00
23 | Bhaluka | 120 | 19:00 | Hasnabad | 59 | 20:00 | Matuail | 58 | 10:00 | Rangamati | 10 | 18:00
24 | Bhandaria | 32 | 19:30 | Hathazari | 51 | 18:00 | Millgate | 56 | 12:00 | Rangpur | 106 | 18:00
25 | Bhangura | 21 | 18:00 | Ishurdi | 54 | 18:00 | Mirpur | 94 | 18:00 | Ruppur | 3.8 | 15:00
26 | Bheramara(GK) | 37 | 18:00 | Jaldhaka | 69 | 18:00 | Mirsorai | 1 | 09:00 | SSM | 14 | 00:00
27 | Bhulta | 211 | 19:30 | Jamalpur | 106 | 18:00 | Mithapukur | 24 | 18:00 | Saidpur | 82 | 18:00
28 | Bog-Sherpur | 48 | 18:00 | Jashore | 88 | 18:30 | Modern | 0 | 00:00 | Satkhira | 71 | 18:00
29 | Bogura | 112 | 19:00 | Jhenaidah | 86 | 18:00 | Mogbazar | 92 | 12:00 | Satmasjid | 71 | 13:00
30 | Borhanuddin | 23 | 20:00 | Joydebpur | 144 | 19:00 | Mongla | 32 | 12:00 | Savar | 145 | 12:00
31 | Brahmanbaria | 104 | 19:30 | Joypurhat | 39 | 18:00 | Motijheel | 27 | 13:00 | Shahjadpur | 76 | 18:00
32 | Cantonment | 104 | 18:00 | Juldah | 27 | 09:00 | Munshiganj | 65 | 13:00 | Shahjibazar | 76 | 18:00
33 | Chandpur | 41 | 19:30 | KSRM | 38 | 13:00 | Mymensingh | 151 | 18:00 | Shahmirpur | 35.4 | 00:00
34 | Chandraghona | 24 | 18:00 | Kabirpur | 238 | 18:00 | Naogaon | 81 | 18:00 | Shariatpur | 46 | 20:00
35 | Chapai | 40 | 18:00 | Kachua | 44 | 18:00 | Narail | 36 | 18:00 | Sherpur | 96 | 18:00
36 | Charsaidpur | 45.9 | 06:00 | Kallyanpur | 66 | 18:00 | Narinda | 51 | 14:00 | Shikalbaha | 22 | 11:00
37 | Chauddagram | 28 | 20:00 | Kalurghat | 6 | 09:00 | Narshingdi | 135 | 19:30 | Shikalbaha-230 | N/A | N/A
38 | Chhatak | 18 | 19:00 | Kamrangirchar | 69 | 13:00 | Natore | 90 | 18:00 | Shitalakhya | 114 | 17:00
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2022-11-22 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Bhulta | 383 | 20:00 | 371 | 15:00 | Kaliakoir | 399 | 01:00 | 187 | 13:00
| Bibiana | 403 | 19:00 | 391 | 11:00 | Payra | 422 | 01:00 | 406 | 19:00
| BIPTC | 408 | 03:00 | 396 | 11:00 | Rahanpur_I | 422 | 18:00 | 381 | 09:00
| Gopalganj_I | 424 | 01:00 | 410 | 21:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 230 | 21:00 | 217 | 15:00 | Hasnabad | 228 | 18:00 | 216 | 15:00
| AKSML | 241 | 19:00 | 221 | 06:00 | Hathazari | 238 | 18:00 | 221 | 02:00
| Aminbazar | 230 | 22:00 | 216 | 15:00 | Ishurdi | 241 | 01:00 | 231 | 11:00
| Ashuganj | 240 | 18:00 | 228 | 15:00 | Jhenaidah | 241 | 01:00 | 227 | 11:00
| Baghabari | 237 | 01:00 | 229 | 12:00 | Kaliakoir | 232 | 21:00 | 216 | 15:00
| Barapukuria | 229 | 19:00 | 223 | 12:00 | Keranigonj | 228 | 20:00 | 217 | 15:00
| Barishal | 248 | 06:00 | 243 | 20:00 | Khulna(S) | 242 | 01:00 | 228 | 13:00
| Bheramara | 239 | 01:00 | 227 | 12:00 | Maniknagar | 228 | 01:00 | 220 | 10:00
| Bhulta | 231 | 20:00 | 220 | 15:00 | Meghnaghat | 232 | 05:00 | 224 | 16:00
| Bibiana | 239 | 20:00 | 229 | 11:00 | Mirsorai | 234 | 22:00 | 218 | 04:00
| BIPTC | 242 | 01:00 | 229 | 12:00 | Rajshahi | 242 | 03:00 | 231 | 13:00
| Bogura | 235 | 06:00 | 229 | 11:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 251 | 15:00 | 247 | 20:00 | Rampura | 229 | 21:00 | 219 | 11:00
| BSRM | 237 | 18:30 | 223 | 00:00 | Shikalbaha | 238 | 17:00 | 222 | 05:00
| Cumilla(N) | 235 | 18:30 | 223 | 15:00 | Shyampur | 228 | 18:00 | 218 | 15:00
| Fenchuganj | 241 | 19:30 | 231 | 15:00 | Siddhirganj | 230 | 20:00 | 225 | 01:00
| Ghorashal | N/A | N/A | N/A | N/A | Sirajgonj | 235 | 01:00 | 229 | 12:00
| GPH | 234 | 22:00 | 221 | 09:00 | Tongi | 230 | 21:00 | 211 | 15:00
| Haripur | 228 | 22:00 | 219 | 16:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 133 | 03:00 | 125 | 15:00 | Lalbag | 137 | 01:00 | 128 | 15:00
| Agargaon | 133 | 21:00 | 125 | 15:00 | Lalmonirhat | 133 | 01:00 | 127 | 12:00
| Agrabad | 138 | 18:30 | 127 | 08:00 | Madanganj | 135 | 18:00 | 128 | 15:00
| AKS | 138 | 20:00 | 125 | 00:00 | Madaripur | 140 | 05:00 | 134 | 12:00
| Aminbazar | 135 | 21:00 | 124 | 10:00 | Madartek | 133 | 03:00 | 126 | 15:00
| Amnura | 138 | 18:00 | 127 | 11:00 | Madunaghat | 140 | 20:00 | 130 | 00:00
| Ashuganj | 138 | 20:00 | 133 | 12:00 | Magura | 138 | 01:00 | 131 | 13:00
| Bagerhat | 138 | 01:00 | 131 | 12:00 | Mahasthangarh | 138 | 19:00 | 132 | 12:00
| Bakulia | 139 | 17:00 | 128 | 00:00 | Manikganj | 136 | 22:00 | 126 | 16:00
| Banani | 137 | 21:00 | 124 | 15:00 | Maniknagar | 135 | 06:00 | 128 | 15:00
| Bangabhaban | 134 | 18:00 | 128 | 15:00 | Matarbari | 130 | 17:00 | 119 | 00:00
| Barapukuria | 138 | 19:00 | 132 | 12:00 | Matuail | 134 | 18:00 | 129 | 15:00
| Barguna | 135 | 04:00 | 129 | 19:00 | Millgate | 136 | 01:00 | 125 | 12:00
| Barishal | 141 | 03:00 | 126 | 19:00 | Mirpur | 134 | 21:00 | 124 | 15:00
| Barishal-230 | 142 | 06:00 | 138 | 12:00 | Mithapukur | 138 | 19:00 | 131 | 10:00
| Baroaulia | 140 | 17:00 | 130 | 00:00 | Modern | 139 | 17:00 | 129 | 01:00
| Baroirhat | 139 | 18:30 | 132 | 00:00 | Mogbazar | 134 | 01:00 | 127 | 16:00
| Bashundhara | 138 | 21:00 | 126 | 13:00 | Mongla | 137 | 18:00 | 132 | 08:00
| BashundharaCement | 135 | 18:00 | 128 | 15:00 | Motijheel | 134 | 18:00 | 128 | 15:00
| Beanibazar | 134 | 22:00 | 130 | 15:00 | Munshiganj | 136 | 18:00 | 129 | 15:00
| Benapole | 138 | 01:00 | 130 | 08:00 | Mymensingh | 136 | 21:00 | 120 | 13:00
| Bhaluka | 132 | 03:00 | 125 | 16:00 | Naogaon | 137 | 16:00 | 131 | 12:00
| Bhandaria | 141 | 05:00 | 135 | 21:00 | Narail | 139 | 01:00 | 130 | 13:00
| Bhangura | 141 | 01:00 | 137 | 10:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bheramara | 138 | 01:00 | 134 | 09:00 | Narshingdi | 131 | 05:00 | 125 | 09:00
| Bheramara(GK) | 139 | 04:00 | 134 | 12:00 | Natore | 137 | 01:00 | 131 | 11:00
| Bhulta | 129 | 18:00 | 124 | 10:00 | Nawabganj | 136 | 01:00 | 130 | 10:00
| Bog-Sherpur | 140 | 02:00 | 133 | 12:00 | Netrakona | 132 | 21:00 | 121 | 13:00
| Bogura | 139 | 03:00 | 133 | 10:00 | New | 137 | 21:00 | 125 | 09:00
| Bogura-230 | 140 | 18:30 | 134 | 11:00 | Niamatpur | 136 | 19:00 | 129 | 12:00
| Brahmanbaria | 133 | 20:00 | 127 | 12:00 | Noapara | 137 | 04:00 | 131 | 07:00
| Cantonment | 132 | 21:00 | 123 | 15:00 | Pabna | 140 | 01:00 | 133 | 12:00
| Chandpur | 142 | 18:00 | 135 | 02:00 | Palashbari | 136 | 01:00 | 128 | 12:00
| Chandraghona | 140 | 19:00 | 128 | 09:00 | Panchagarh | 136 | 19:00 | 124 | 12:00
| Chapai | 135 | 01:00 | 126 | 12:00 | Patuakhali | 136 | 01:00 | 129 | 19:00
| Charsaidpur | 136 | 18:00 | 129 | 10:00 | Payra | 138 | 01:00 | 134 | 19:00
| Chauddagram | 140 | 20:00 | 132 | 04:00 | PHP | 139 | 19:00 | 129 | 03:00
| Chhatak | 133 | 23:00 | 129 | 00:00 | Postogola | 136 | 20:00 | 127 | 15:00
| Chowmuhani | 140 | 17:00 | 130 | 02:00 | Purbachal | 138 | 22:00 | 124 | 15:00
| Chuadanga | 137 | 04:00 | 128 | 12:00 | Purbasadipur | 135 | 19:00 | 126 | 12:00
| Coxsbazar | 128 | 17:00 | 118 | 00:00 | Rahim | 134 | 18:30 | 130 | 09:00
| Cumilla(N) | 139 | 20:00 | 133 | 15:00 | Rajbari | 138 | 01:00 | 132 | 12:00
| Cumilla(S) | 140 | 19:00 | 129 | 13:00 | Rajendrapur | 136 | 15:00 | 122 | 17:00
| Daudkandi | 136 | 13:00 | 131 | 00:00 | Rajshahi | 133 | 00:00 | 128 | 11:00
| Dhaka | 135 | 00:00 | 126 | 15:00 | Rajshahi-230 | 134 | 19:00 | 127 | 08:00
| Dhamrai | 139 | 21:00 | 129 | 15:00 | Ramganj | 139 | 18:00 | 132 | 04:00
| Dhanmondi | 135 | 20:00 | 128.8 | 15:00 | Rampur | 136 | 16:00 | 128 | 04:00
| Dohazari | 140 | 19:00 | 125 | 00:00 | Rampura | 133 | 03:00 | 126 | 11:00
| Faridpur | 136 | 02:00 | 132 | 13:00 | Rangamati | 139 | 17:00 | 130 | 00:00
| Fatullah | 136 | 18:00 | 128 | 15:00 | Rangpur | 136 | 19:00 | 129 | 12:00
| Fenchuganj | 138 | 21:00 | 133 | 00:00 | Ruppur | 138 | 18:00 | 134 | 15:00
| Feni | 140 | 19:00 | 133 | 02:00 | Saidpur | 135 | 19:00 | 129 | 12:00
| Ghorashal | 141 | 21:00 | 135 | 16:00 | Satkhira | 138 | 01:00 | 130 | 08:00
| Goalpara | 139 | 01:00 | 132 | 12:00 | Satmasjid | 132 | 01:00 | 124 | 15:00
| Gollamari | 139 | 01:00 | 132 | 08:00 | Savar | 136 | 19:00 | 122 | 15:00
| Gopalganj | 139 | 01:00 | 133 | 08:00 | Shahjadpur | 142 | 03:00 | 138 | 15:00
| Gopalganj_I | 139 | 01:00 | 135 | 08:00 | Shahjibazar | 137 | 21:00 | 132 | 09:00
| Gulshan | 133 | 21:00 | 125 | 15:00 | Shariatpur | 140 | 02:00 | 133 | 22:00
| Halishahar | 139 | 19:00 | 128 | 00:00 | Sherpur | 140 | 13:00 | 126 | 17:00
| Haripur | 134 | 18:30 | 130 | 09:00 | Shikalbaha | 139 | 17:00 | 128 | 02:00
| HaripurSBU | 135 | 18:00 | 129 | 15:00 | Shikalbaha-230 | 139 | 19:00 | 129 | 05:00
| Hasnabad | 136 | 21:00 | 127 | 15:00 | Shitalakhya | 135 | 22:00 | 125 | 16:00
| Hathazari | 140 | 18:00 | 132 | 00:00 | Sholosohor | 138 | 17:00 | 128 | 00:00
| Ishurdi | 140 | 01:00 | 135 | 11:00 | Shyampur | 135 | 20:00 | 128 | 15:00
| Jaldhaka | 134 | 01:00 | 126 | 12:00 | Shyampur-230 | 135 | 18:00 | 129 | 15:00
| Jamalpur | 141 | 11:00 | 130 | 03:00 | Siddhirganj | 134 | 18:00 | 129 | 15:00
| Jashore | 137 | 03:00 | 129 | 13:00 | Sirajganj | 139 | 00:00 | 132 | 11:00
| Jhenaidah | 138 | 00:00 | 132 | 13:00 | Sonargaon | 134 | 21:00 | 127 | 07:00
| Jhenaidah-230 | 140 | 01:00 | 132 | 12:00 | Sreemongol | 137 | 19:30 | 133 | 12:00
| Joydebpur | 141 | 07:00 | 133 | 15:00 | Srinagar | 137 | 01:00 | 128 | 15:00
| Joypurhat | 137 | 19:00 | 131 | 12:00 | SSM | 141 | 18:30 | 131 | 00:00
| Juldah | 139 | 17:00 | 129 | 09:00 | Sunamganj | 133 | 04:00 | 129 | 00:00
| Kabirpur | 136 | 22:00 | 122 | 12:00 | Sylhet | 135 | 23:00 | 131 | 00:00
| Kachua | 139 | 13:00 | 134 | 02:00 | Tangail | 137 | 03:00 | 124 | 16:00
| Kaliakoir | 139 | 02:00 | 124 | 16:00 | Thakurgaon | 137 | 19:00 | 125 | 12:00
| Kallyanpur | 133 | 18:00 | 124 | 15:00 | TK | 140 | 17:00 | 130 | 09:00
| Kalurghat | 138 | 20:00 | 129 | 00:00 | Tongi | 138 | 21:00 | 128 | 11:00
| Kamrangirchar | 137 | 03:00 | 128 | 15:00 | Ullon | 133 | 21:00 | 127 | 11:00
| Kaptai | 135 | 00:00 | 132 | 01:00 | Uttara | 137 | 22:00 | 124 | 15:00
| Kazla | 134 | 02:00 | 127 | 16:00 | UttaraNew | 134 | 20:00 | 122 | 15:00
| Keranigonj | 137 | 02:00 | 130 | 15:00 | Zigatola | 136 | 22:00 | 128 | 16:00
| Khagrachori | 138 | 19:00 | 130 | 01:00
| Khulna | 138 | 01:00 | 132 | 12:00
| Khulna(S) | 140 | 01:00 | 132 | 13:00
| Khulshi | 137 | 17:00 | 128 | 00:00
| Kishoreganj | 134 | 20:00 | 125 | 13:00
| Kodda | 142 | 21:00 | 125 | 16:00
| KSRM | 141 | 19:00 | 129 | 00:00
| Kulaura | 137 | 20:00 | 133 | 15:00
| Kurigram | 134 | 14:00 | 127 | 12:00
| Kushtia | 139 | 02:00 | 133 | 15:00
Page 7 of 7

## L-Curve
Date | 2022-11-22
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 1130 | 5323 | 2944 | 8267 |  |  |  | QF-LDC-11
0:30 | 1120 | 5304.5 | 2852 | 8156.5 | Date: | 2022-11-22
1:00 | 1110 | 5286 | 2760 | 8046
1:30 | 1120 | 5059 | 2673.5 | 7732.5
2:00 | 1130 | 4832 | 2587 | 7419
2:30 | 1150 | 4733 | 2561.5 | 7294.5 | [5 empty] | Gen. at Eve. Peak | 10512 | 10512 MW (18:00 )
3:00 | 1170 | 4634 | 2536 | 7170 | [6 empty] | 18:00
3:30 | 1175 | 4530.5 | 2543 | 7073.5 | [5 empty] | Gen. at Day Peak | 9024 | 9024 MW (12:00 )
4:00 | 1180 | 4427 | 2550 | 6977 | [6 empty] | 12:00
4:30 | 1185 | 4381 | 2549.5 | 6930.5 | [5 empty] | Highest Generation | 10512
5:00 | 1190 | 4335 | 2549 | 6884 | [6 empty] | 18:00
5:30 | 1110 | 4396.5 | 2565 | 6961.5
6:00 | 1030 | 4458 | 2581 | 7039
6:30 | 893 | 4631.5 | 2632.5 | 7264
7:00 | 756 | 4805 | 2684 | 7489
7:30 | 748 | 4984 | 2816 | 7800
8:00 | 740 | 5163 | 2948 | 8111
8:30 | 1080 | 5186.5 | 2984 | 8170.5
9:00 | 1420 | 5210 | 3020 | 8230
9:30 | 1425 | 5275.5 | 2994 | 8269.5
10:00 | 1430 | 5341 | 2968 | 8309
10:30 | 1405 | 5494 | 2960.5 | 8454.5
11:00 | 1380 | 5647 | 2953 | 8600
11:30 | 1190 | 5876.5 | 2935.5 | 8812
12:00 | 1000 | 6106 | 2918 | 9024
12:30 | 1015 | 6150.5 | 2992.5 | 9143
13:00 | 1030 | 6195 | 3067 | 9262
13:30 | 1223 | 5946.5 | 3116 | 9062.5
14:00 | 1416 | 5698 | 3165 | 8863
14:30 | 1498 | 5688 | 3115 | 8803
15:00 | 1580 | 5678 | 3065 | 8743
15:30 | 1440 | 5864.5 | 3017.5 | 8882
16:00 | 1300 | 6051 | 2970 | 9021
16:30 | 1240 | 6052.5 | 3005.5 | 9058
17:00 | 1180 | 6054 | 3041 | 9095
17:30 | 1060 | 6447 | 3356.5 | 9803.5
18:00 | 940 | 6840 | 3672 | 10512
18:30 | 1040 | 6680.5 | 3685 | 10365.5
19:00 | 1140 | 6521 | 3698 | 10219
19:30 | 1080 | 6424 | 3629 | 10053
20:00 | 910 | 6484 | 3487 | 9971 |  |  |  | Executive Engineer
20:30 | 947 | 6341 | 3467 | 9808 |  |  |  | Network Operation Division
21:00 | 984 | 6198 | 3447 | 9645
21:30 | 962 | 6063.5 | 3314.5 | 9378
22:00 | 940 | 5929 | 3182 | 9111 |  |  |  |  | Page 6 of 7
22:30 | 995 | 5773.5 | 3117.5 | 8891
23:00 | 1050 | 5618 | 3053 | 8671
23:30 | 1090 | 5470.5 | 2998.5 | 8469
24:00 | 1130 | 5323 | 2944 | 8267
10512 MW (18:00 )
9024 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2022-11-22 |  | Energy |  | 207930384
[13 empty] | 2022-11-22 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 3229 | 801 | 1135 | 0 | 1824 | 1105 | 40 | 0 | 33 | 100 | 0 | 0
0:30 | 3275 | 730.5 | 1182.5 | 0 | 1801.5 | 975 | 43 | 0 | 51 | 98 | 0 | 0 | Date: | 2022-11-22
1:00 | 3321 | 660 | 1230 | 0 | 1779 | 845 | 46 | 0 | 69 | 96 | 0 | 0
1:30 | 3300 | 660 | 1208.5 | 0 | 1531.5 | 849.5 | 46 | 0 | 43 | 94 | 0 | 0 | [8 empty] | Total Energy | 207.9304 | Total Energy Gen 207.930 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 207.930 MKWHr
2:00 | 3279 | 660 | 1187 | 0 | 1284 | 854 | 46 | 0 | 17 | 92 | 0 | 0 | [8 empty] | Energy not Served | 0
2:30 | 3287 | 660 | 1207.5 | 0 | 1133 | 853 | 46 | 0 | 17 | 91 | 0 | 0 | [8 empty] | Energy Requirement | 207.9304
3:00 | 3295 | 660 | 1228 | 0 | 982 | 852 | 46 | 0 | 17 | 90 | 0 | 0
3:30 | 3282.5 | 660 | 1229.5 | 0 | 898 | 852.5 | 46 | 0 | 17 | 88 | 0 | 0 | [6 empty] | Shortage
4:00 | 3270 | 660 | 1231 | 0 | 814 | 853 | 46 | 0 | 17 | 86 | 0 | 0
4:30 | 3239 | 660 | 1218.5 | 0 | 810 | 855 | 46 | 0 | 17 | 85 | 0 | 0
5:00 | 3208 | 660 | 1206 | 0 | 806 | 857 | 46 | 0 | 17 | 84 | 0 | 0
5:30 | 3242 | 660 | 1204.5 | 0 | 853 | 856 | 46 | 0 | 17 | 83 | 0 | 0
6:00 | 3276 | 660 | 1203 | 0 | 900 | 855 | 46 | 0 | 17 | 82 | 0 | 0
6:30 | 3289.5 | 660 | 1199.5 | 0 | 1047 | 885.5 | 46 | 0 | 49 | 80 | 7.5 | 0 |  |  |  |  | Coal
7:00 | 3303 | 660 | 1196 | 0 | 1194 | 916 | 46 | 0 | 81 | 78 | 15 | 0
7:30 | 3329 | 660 | 1171.5 | 0 | 1388 | 982 | 46 | 0 | 98 | 80 | 45.5 | 0 |  |  |  | Oil |  |  |  | ,
8:00 | 3355 | 660 | 1147 | 0 | 1582 | 1048 | 46 | 0 | 115 | 82 | 76 | 0
8:30 | 3334.5 | 707 | 1113 | 0 | 1626.5 | 1028.5 | 46 | 0 | 123.5 | 84 | 107.5 | 0
9:00 | 3314 | 754 | 1079 | 0 | 1671 | 1009 | 46 | 0 | 132 | 86 | 139 | 0
9:30 | 3262.5 | 777.5 | 1068 | 55 | 1688.5 | 989 | 46 | 0 | 132 | 88 | 163 | 0
10:00 | 3211 | 801 | 1057 | 110 | 1706 | 969 | 46 | 0 | 132 | 90 | 187 | 0
10:30 | 3189 | 848.5 | 1052 | 92 | 1841 | 959.5 | 38 | 6.5 | 136 | 92 | 200 | 0
11:00 | 3167 | 896 | 1047 | 74 | 1976 | 950 | 30 | 13 | 140 | 94 | 213 | 0
11:30 | 3162.5 | 896 | 1041 | 221.5 | 2047 | 937 | 30 | 21.5 | 140 | 99 | 216.5 | 0
12:00 | 3158 | 896 | 1035 | 369 | 2118 | 924 | 30 | 30 | 140 | 104 | 220 | 0
12:30 | 3134.5 | 896 | 1028.5 | 410 | 2170.5 | 966 | 38 | 19.5 | 162.5 | 107 | 210.5 | 0
13:00 | 3111 | 896 | 1022 | 451 | 2223 | 1008 | 46 | 9 | 185 | 110 | 201 | 0
13:30 | 3111 | 896 | 1022 | 451 | 2223 | 1008 | 46 | 9 | 185 | 110 | 201 | 0
14:00 | 3111 | 896 | 1022 | 451 | 2223 | 1008 | 46 | 9 | 185 | 110 | 201 | 0
14:30 | 3160.5 | 896 | 1025.5 | 227 | 2210.5 | 974 | 46 | 4.5 | 194.5 | 107 | 157 | 0
15:00 | 3210 | 896 | 1029 | 3 | 2198 | 940 | 46 | 0 | 204 | 104 | 113 | 0
15:30 | 3229 | 896.5 | 983.5 | 101.5 | 2313.5 | 920 | 46 | 0 | 207.5 | 106 | 78.5 | 0
16:00 | 3248 | 897 | 938 | 200 | 2429 | 900 | 46 | 0 | 211 | 108 | 44 | 0
16:30 | 3246 | 896.5 | 944 | 100 | 2519.5 | 929 | 46 | 0 | 245.5 | 107 | 23.5 | 0
17:00 | 3246 | 896 | 950 | 0 | 2610 | 958 | 46 | 0 | 280 | 106 | 3 | 0
17:30 | 3234 | 895.5 | 995.5 | 108 | 2974.5 | 1038.5 | 46 | 0 | 397 | 113 | 1.5 | 0
18:00 | 3222 | 895 | 1041 | 216 | 3339 | 1119 | 46 | 0 | 514 | 120 | 0 | 0
18:30 | 3159.5 | 894.5 | 1028 | 115.5 | 3371 | 1148 | 46 | 0 | 488 | 115 | 0 | 0
19:00 | 3097 | 894 | 1015 | 15 | 3403 | 1177 | 46 | 0 | 462 | 110 | 0 | 0
19:30 | 3136 | 894 | 1039 | 0 | 3360 | 1186 | 40 | 0 | 290 | 108 | 0 | 0
20:00 | 3226 | 894 | 1075 | 0 | 3273 | 1185 | 40 | 0 | 170 | 108 | 0 | 0
20:30 | 3213 | 894 | 1068 | 0 | 3133.5 | 1206 | 40 | 0 | 143.5 | 110 | 0 | 0
21:00 | 3200 | 894 | 1061 | 0 | 2994 | 1227 | 40 | 0 | 117 | 112 | 0 | 0
21:30 | 3183.5 | 894 | 1067 | 0 | 2792 | 1216.5 | 40 | 0 | 75 | 110 | 0 | 0
22:00 | 3167 | 894 | 1073 | 0 | 2590 | 1206 | 40 | 0 | 33 | 108 | 0 | 0
22:30 | 3171.5 | 894 | 1081 | 0 | 2392.5 | 1176 | 40 | 0 | 33 | 103 | 0 | 0
23:00 | 3176 | 894 | 1089 | 0 | 2195 | 1146 | 40 | 0 | 33 | 98 | 0 | 0
23:30 | 3202.5 | 847.5 | 1112 | 0 | 2009.5 | 1125.5 | 40 | 0 | 33 | 99 | 0 | 0 | Max Temp. in Dhaka |  | 24.7° C | 28.9° C
24:00 | 3229 | 801 | 1135 | 0 | 1824 | 1105 | 40 | 0 | 33 | 100 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 207.930 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 207.930 MKWHr
Note on W13: Author:

## Generation
g | 2022-11-22
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 30 | 30 | 46 | 46 | 46 | 46 | 46 | 46 |  | 46 | 40 | 40 | 40 | 40 | 40 | 40 | 1050540
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 17 | 0 | [5 empty] | 5 | 8 | 8 | 8 | 8 | 8 | 1 | 8 | 8 | 8 | 8 |  | 10 | 17 | 17 | 17 | 8 | 8 | 0 | 178023
| Teknaf 20MW PP (Solartech) | [6 empty] | 3 | 9 | 14 | 18 | 20 | 20 | 18 | 15 | 11 | 5 | 0 | [9 empty] | 133380
6 | Sikalbaha 225MW CCPP (Gas) | 148 | 149 | 154 | 151 | 151 | 151 | 151 | 151 | 150 | 151 | 151 | 151 | 151 | 151 | 151 | 151 | 152 | 150 |  | 150 | 150 | 151 | 152 | 152 | 151 | 151 | 3665040
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 18 | 51 | 51 |  | 51 | 17 | 17 | 17 | 17 | 17 | 17 | 509207
12 | Hathazari 100 MW peaking PP | [10 empty] | 8 | 8 | 8 | 14 | 24 | 25 | 30 | 32 |  | 32 | 0 | [5 empty] | 167746
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 42 | 68 | 68 | 68 | 68 | 68 | 68 | 83 | 85 | 97 |  | 105 | 105 | 105 | 105 | 105 | 76 | 34 | 1556472
| Daudkandi 200 MW PP (B.Trac) | [9 empty] | 25 | 10 | 50 | 78 | 20 | 0 |  | 0 | 20 |  | 0 | [6 empty] | 214656
14 | Titas 50 MW Peaking PP | [12 empty] | 27 | 30 | 30 | 30 | 30 | 30 |  | 31 | 31 | 29 | 31 |  |  | 0 | 253472
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 260 | 263 | 195 | 100 | 97 | 95 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 100 | 85 | 90 | 97 | 188 |  | 268 | 275 | 277 | 277 | 278 | 281 | 191 | 3864000
19 | Ashuganj 195MW PP (APSCL-United)
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4378500
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 44 | 43 | 43 | 44 | 43 | 43 | 43 | 43 | 41 | 38 | 38 | 42 | 44 | 44 | 44 | 44 | 44 | 44 |  | 44 | 44 | 44 | 44 | 44 | 44 | 45 | 1023480
33 | Ashuganj 225 MW CCPP
34 | Ashuganj 450 MW CCPP(South) | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 300 | 365 | 280 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 |  | 230 | 230 | 270 | 250 | 220 | 240 | 240 | 6021000
Ashuganj 450 MW CCPP(North)
| Ashuganj 420 MW CCPP(East) | 407 | 387 | 407 | 407 | 407 | 407 | 407 | 407 | 407 | 386 | 387 | 381 | 359 | 327 | 377 | 402 | 402 | 402 |  | 372 | 362 | 363 | 382 | 382 | 382 | 373 | 9603300
35 | Ashuganj 55 MW PP (Precision) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 40 | 769440
36 | Chandpur 150 MW CCPP | 76 | 68 | 68 | 68 | 67 | 67 | 69 | 67 | 67 | 66 | 63 | 60 | 60 | 60 | 59 | 59 | 65 | 66 |  | 66 | 65 | 64 | 65 | 65 | 65 | 40 | 1541150
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 302 | 302 | 302 | 302 | 302 | 304 | 304 | 303 | 299 | 305 | 312 | 312 | 318 | 318 | 326 | 328 | 315 | 308 |  | 301 | 302 | 301 | 302 | 302 | 305 | 309 | 7505920
40 | Meghnaghat 450 MW CCPP(MPL) | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 |  | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 5205500
41 | Haripur 360MW CCPP(HPL) | 271 | 271 | 270 | 270 | 270 | 272 | 272 | 266 | 269 | 267 | 269 | 268 | 277 | 277 | 286 | 286 | 286 | 286 |  | 252 | 252 | 274 | 254 | 255 | 280 | 280 | 6528000
42 | RPCL 210MW CCPP | 111 | 111 | 113 | 111 | 112 | 112 | 72 | 70 | 70 | 37 | 36 | 35 | 35 | 34 | 35 | 34 | 36 | 39 |  | 46 | 69 | 70 | 96 | 103 | 111 | 111 | 1647360
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 3 | 17 | 33 | 42 | 47 | 48 | 46 | 37 | 25 | 10 | 0 | [9 empty] | 312480
44 | Fenchugonj CCPP Phase-1 | [12 empty] | 20 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 327000
45 | Fenchugonj CCPP Phase-2 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 894200
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 66 | 66 | 66 | 40 | 40 | 40 | 70 | 70 | 69 | 67 | 65 | 62 | 63 | 65 | 64 | 60 | 62 | 69 |  | 70 | 70 | 70 | 70 | 40 | 40 | 70 | 1473792
48 | Shahjibazar 86MW PP (Shahjibazar) | 81 | 0 | [10 empty] | 1 | 1 | 1 | 1 | 1 | 83 |  | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 676800
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 |  | 178 | 178 | 178 | 178 | 178 | 151 | 151 | 4122810
51 | Sylhet 20 MW GTPP | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 19 | 19 | 421000
52 | Sylhet 50MW PP (EPL) |  | 15 | 22 | 23 | 23 | 23 | 23 | 23 | 23 | 24 | 24 | 25 | 25 | 25 | 25 | 25 | 25 | 27 |  | 27 | 27 | 27 | 26 | 26 | 27 | 28 | 506220
53 | Sylhet 10MW PP (Desh) |  | 7 | 9 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 225000
54 | Hobiganj 11MW PP Cofidence-E | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 72336
55 | Fenchugonj 51 MW PP (Barakatullah) |  | 42 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 53 | 53 | 50 | 50 | 53 | 53 | 53 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 1145400
56 | Shahjahanulla 25 MW PP |  |  | 8 | 17 | 22 | 22 | 22 | 22 | 22 | 18 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 451210
57 | Bibiana-II 341 MW CCPP (Summit) | 130 | 90 | 80 | 70 | 50 | 40 | 45 | 45 | 0 | [16 empty] | 0 | 536420
| Bibiyana South 400 MW | 400 | 400 | 380 | 360 | 360 | 360 | 400 | 400 | 350 | 400 | 400 | 394 | 358 | 400 | 400 | 390 | 400 | 400 |  | 370 | 370 | 380 | 340 | 340 | 370 | 363 | 9136800
58 | Nababganj 55 MW PP (Southern power ) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 35 | 35 |  | 35 | 35 | 55 | 35 | 35 | 17 | 17 | 548166
59 | Tangail Palli Power Gen 22 MW | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 9 | 12 | 12 | 12 | 12 | 293760
60 | Barabkunda 22 MW PP (Regent)
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 460512
62 | Tangail 22 MW PP (Doreen) | 11 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 11 | 11 | 0 | 10 | 10 | 10 | 10 | 252108
63 | Impoprt (Tripura) | 96 | 92 | 90 | 86 | 84 | 82 | 78 | 82 | 86 | 90 | 94 | 104 | 110 | 110 | 104 | 108 | 106 | 120 |  | 110 | 108 | 108 | 112 | 108 | 98 | 100 | 2364480
64 | Malancha, Ctg. EPZ (United) | 9 | 14 | 15 | 27 | 27 | 32 | 30 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 2 | 2 | 3 | 3 | 7 | 9 | 11 | 167520
65 | Feni 22MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  |  | 15 | 16 | 19 | 19 | 19 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 446760
66 | Feni 11 MW PP (Doreen) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 174780
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 28 | 20 | 4 | 13 | 13 | 13 | 13 | 13 | 15 | 16 | 16 | 16 |  | 28 | 30 | 30 | 33 | 33 | 33 | 33 | 584000
68 | Cumilla 25 MW PP (Summit) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 345910
69 | Summit Ashulia | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 23 | 23 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 25 | 600000
70 | Summit Madhabdi | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 28 | 28 | 28 | 27 | 26 | 27 | 27 | 26 | 26 | 26 |  | 26 | 26 | 26 | 27 | 27 | 0 | 9 | 580860
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 25 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 779400
72 | Rupganj 33 MW PP(Summit) | 32 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 29 | 29 | 29 | 29 | 29 | 29 | 28 | 28 | 28 | 28 |  | 28 | 28 | 28 | 30 | 30 | 31 | 32 | 740100
73 | Ghorashal 108MW PP (Regent) | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 70 | 67 | 71 | 70 | 70 | 68 | 70 | 73 | 71 |  | 71 | 73 | 73 | 73 | 73 | 73 | 73 | 1679000
| Feni Lanka Power | 17 | 17 | 17 | 0 | [21 empty] | 0 | 55860
| Chowmuhani 113 MW | 75 | 9 | 9 | 9 | 9 | 9 | 17 | 78 | 105 | 105 | 104 | 106 | 107 | 107 | 107 | 107 | 108 | 108 |  | 101 | 109 | 109 | 109 | 109 | 108 | 108 | 1998360
| Manikgonj 162MW PP(MPGL) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 30 | 35 | 35 | 35 | 35 | 37 | 144 | 162 |  | 162 | 162 | 162 | 162 | 108 | 17 | 17 | 1340640
77 | Siddhirganj 100 PP(Dutch Bangla) | 30 | 30 | 0 |  |  | 6 | 30 | 30 | 33 | 70 | 71 | 72 | 72 | 72 | 72 | 77 | 77 | 85 |  | 87 | 87 | 87 | 88 | 87 | 87 | 41 | 1267200
78 | Gazipur 52 MW PP | 8 | 0 |  |  |  |  | 26 | 42 | 42 | 42 | 42 | 42 | 49 | 49 | 45 | 49 | 49 | 49 |  | 49 | 49 | 49 | 49 | 8 | 8 | 0 | 692160
79 | Kodda 150MW PP | 16 | 0 |  |  |  |  | 64 | 98 | 115 | 115 | 115 | 115 | 133 | 133 | 133 | 133 | 133 | 133 |  | 100 | 64 | 64 | 64 | 16 | 16 | 16 | 1702080
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 10 | 16 | 16 | 8 | 8 | 8 | 8 | 212563
| Gazipur 100 MW PP | 105 | 17 | 0 |  |  |  | 36 | 105 | 105 | 105 | 105 | 105 | 88 | 88 | 88 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 88 | 105 | 105 | 1952832
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 2 | 3 | 4 | 4 | 4 | 4 | 3 | 2 | 1 | 0 | [9 empty] | 26281
| Jodiac Power | 25 | 17 | 17 | 17 | 17 | 17 | 31 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 |  | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 793353
| Karnaphuli Power Ltd. | 73 | 73 | 73 | 58 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 68 | 87 | 91 |  | 91 | 91 | 91 | 91 | 91 | 53 | 54 | 1639266
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL) | 25 | 0 |  |  |  |  | 3 | 24 | 25 | 28 | 61 | 78 | 89 | 91 | 89 | 91 | 90 | 92 |  | 89 | 92 | 92 | 89 | 50 | 17 | 17 | 1138560
| Meghnaghat 104 MW PP (OPCL) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 20 | 27 | 30 | 17 | 17 | 18 | 25 | 35 | 35 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 491520
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 44 | 44 | 44 |  | 44 | 44 | 44 | 44 | 44 | 44 | 22 | 694440
92 | Fenchuganj 44MW (Energyprima) |  | 32 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 30 | 30 |  |  | 0 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 628488
93 | Ashuganj 51 MW PP (Midland) | [12 empty] | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 217844
94 | Gagnagar 102 MW PP (Digital Power) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 24 | 8 | 8 | 8 | 8 | 16 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 8 | 8 | 372816
95 | Patenga 50MW PP (Baraka) | 37 | 6 | 0 |  |  |  | 4 | 27 | 31 | 31 | 31 | 12 | 12 | 26 | 35 | 37 | 38 | 43 |  | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 654720
96 | Chattogram 108 MW PP (ECPV) | [25 empty] | 0 | 0
97 | katpotti 52 MW
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 45 | 45 | 40 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 45 | 45 | 45 | 45 | 35 | 45 | 45 |  | 45 | 45 | 45 | 45 | 45 | 45 | 35 | 969318
100 | Manikganj 55 MW PP (Northern) | 35 | 0 |  |  |  |  | 17 | 35 | 35 | 35 | 35 | 55 | 55 | 35 | 35 | 35 | 35 | 55 |  | 55 | 55 | 55 | 35 | 35 | 17 | 17 | 732309
101 | Kushiara 163 MW CCPP (KP)
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 1 | 0 | 0 | [9 empty] | 12700
103 | Kamalaghat 54 MW PP(Banco Energy) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 54 |  | 54 | 54 | 54 | 17 | 17 | 17 | 17 | 529920
104 | Keranigonj 300 MW PP (APR) | [9 empty] | 35 | 14 | 132 | 185 | 30 | 0 | 100 | 0 | 66 |  | 15 | 0 |  |  |  |  | 0 | 521665
105 | Bramhangoan 100 MW PP (Aggreko) | [9 empty] | 25 | 25 | 95 | 96 | 25 | 0 | 50 | 0 | 80 |  | 0 | [5 empty] | 0 | 363633
106 | Mymensingh 200 MW PP (United) | 48 | 0 |  |  |  | 35 | 46 | 46 | 46 | 48 | 76 | 77 | 78 | 66 | 67 | 67 | 49 | 87 |  | 88 | 88 | 87 | 88 | 88 | 86 | 48 | 1279200
112 | Aurahati 100MW PP (Aggreko) | [9 empty] | 25 | 25 | 92 | 92 | 25 | 3 | 50 | 0 | 50 |  | 0 | [5 empty] | 0 | 367323
114 | Kodda 149 MW PP Unit-1 (Summit) | 149 | 149 | 113 | 98 | 98 | 104 | 134 | 135 | 136 | 136 | 136 | 135 | 135 | 135 | 136 | 125 | 7 | 92 |  | 95 | 108 | 108 | 111 | 134 | 149 | 149 | 2933712
115 | Juldah 100 MW PP Unit-3 (Acorn) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 30 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 25 | 25 | 756480
116 | Chandpur 200MW (Desh energy) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 25 | 109 | 147 |  | 155 | 120 | 120 | 120 | 120 | 120 | 120 | 1342080
117 | Ashuganj 150MW PP (Midland) | 65 | 10 | 10 | 10 | 10 | 25 | 52 | 75 | 79 | 80 | 79 | 80 | 79 | 80 | 81 | 100 | 118 | 120 |  | 120 | 120 | 120 | 120 | 118 | 86 | 75 | 1873454
118 | Bibiyana-III 400 MW CCPP | 416 | 416 | 416 | 418 | 352 | 418 | 417 | 418 | 417 | 419 | 420 | 422 | 422 | 371 | 419 | 414 | 404 | 391 |  | 333 | 335 | 384 | 351 | 352 | 352 | 417 | 9496000
| Jamalpur 115 MW PP (United) | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 68 | 68 | 68 | 68 | 69 | 69 | 50 | 97 |  | 98 | 98 | 98 | 98 | 98 | 98 | 49 | 1557600
| Anwara 300 MW PP (United) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 200 | 266 | 281 | 283 | 285 | 300 | 300 | 300 |  | 300 | 300 | 232 | 70 | 70 | 70 | 70 | 3078655
| Juldah unit-2 (Acorn) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 42 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 29 | 787200
| Anlima Energy Ltd. | 107 | 107 | 51 | 34 | 34 | 34 | 82 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 |  | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 2347255
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 34 |  | 35 | 35 | 35 | 35 | 35 | 34 | 17 | 550440
| Spectra Solar Plant Ltd. | [6 empty] | 2 | 10 | 19 | 25 | 28 | 27 | 26 | 23 | 15 | 6 | 1 | 0 | [8 empty] | 180625
| Chandpur 115(Doreen) | 28 | 18 | 17 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 68 | 115 | 115 | 30 | 18 | 18 | 57 | 115 |  | 115 | 115 | 115 | 115 | 115 | 56 | 35 | 1290240
| Kanchan Purbachal Power Generation Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 434160
| Mirsharai 150 MW (Oil) | [10 empty] | 13 | 30 | 9 | 7 | 0 | [11 empty] | 58545
Mirsharai 150 MW (Gas)
120 | Eastern Zone Total | 5286 | 4832 | 4634 | 4427 | 4335 | 4458 | 4805 | 5163 | 5210 | 5341 | 5647 | 6106 | 6195 | 5698 | 5678 | 6051 | 6054 | 6840 |  | 6521 | 6424 | 6484 | 6198 | 5929 | 5618 | 5323 | 133476507
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | 32 | 0 | [7 empty] | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 99 |  | 114 | 114 | 114 | 103 | 16 | 16 | 16 | 613440
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [14 empty] | 0 | 5 | 36 | 50 |  | 41 | 0 | [5 empty] | 98880
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 94 | 53 | 17 | 17 | 17 | 17 | 30 | 64 | 70 | 53 | 53 | 53 | 56 | 82 | 94 | 94 | 94 | 94 |  | 94 | 94 | 94 | 94 | 70 | 70 | 70 | 1614240
130 | Mongla Orion 100 MW Solar PP | [6 empty] | 6 | 26 | 48 | 64 | 73 | 77 | 71 | 56 | 38 | 13 | 2 | 0 | [8 empty] | 481680
131 | Rampal 1320 MW (BIFPCL)
132 | United Payra Power Ltd. | [25 empty] | 0 | 0
133 | Bhola Nutan Biddut BD LTD (GAS) | 96 | 109 | 110 | 109 | 109 | 109 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 0 | [9 empty] | 0 | 1704300
Bhola Nutan Biddut BD LTD (OIL)
Barisal 110 MW PP (Summit )
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW | 145 | 144 | 142 | 143 | 147 | 145 | 146 | 198 | 199 | 199 | 200 | 174 | 198 | 199 | 200 | 200 | 248 | 329 |  | 307 | 306 | 305 | 307 | 306 | 306 | 306 | 5136700
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 130 | 115 | 115 | 130 | 130 | 130 | 130 | 130 | 112 | 100 | 85 | 100 | 75 | 100 | 100 | 130 | 130 | 115 |  | 109 | 130 | 130 | 115 | 125 | 125 | 111 | 2852000
140 | Bhola 33 MW PP (Venture) | 20 | 19 | 18 | 17 | 17 | 17 | 16 | 15 | 15 | 13 | 15 | 16 | 16 | 15 | 14 | 14 | 16 | 20 |  | 21 | 21 | 21 | 23 | 23 | 21 | 21 | 421400
141 | Noapara 100 MW PP (Bangla Trac) | 0 | [24 empty] | 0 | 0
142 | Noapara 40 MW PP (Khanjahan Ali) | [9 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 32 |  | 32 | 32 | 32 | 32 |  |  | 0 | 188625
143 | Gopalganj 100 MW Peaking PP | 36 | 0 | [14 empty] | 0 | 50 |  | 85 | 60 | 60 | 5 |  |  |  | 228224
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 660 | 660 | 660 | 660 | 660 | 660 | 660 | 660 | 754 | 801 | 896 | 896 | 896 | 896 | 896 | 897 | 896 | 895 |  | 894 | 894 | 894 | 894 | 894 | 894 | 801 | 19460363
147 | Bheramara 410 MW CCPP | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 175 | 170 | 160 | 155 | 145 | 145 | 145 | 145 | 145 | 145 | 145 |  | 150 | 150 | 150 | 165 | 170 | 170 | 180 | 4077216
148 | Payra 1320 MW | 540 | 550 | 550 | 550 | 550 | 550 | 610 | 690 | 650 | 610 | 590 | 590 | 650 | 660 | 580 | 540 | 550 | 630 |  | 710 | 720 | 720 | 760 | 740 | 680 | 640 | 16658300
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 |  | 160 | 160 | 160 | 160 | 160 | 160 | 159 | 3903900
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [16 empty] | 0 | 24 |  | 24 | 24 | 0 |  |  |  |  | 59088
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 1 | 2 | 3 | 4 | 4 | 4 | 3 | 2 | 0 | 0 | [9 empty] | 27900
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 176 | 175 | 176 | 175 | 175 | 175 | 176 | 174 | 170 | 163 | 161 | 159 | 159 | 159 | 156 | 157 | 157 | 157 |  | 157 | 158 | 159 | 162 | 166 | 170 | 155 | 4189173
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 275 | 240 | 275 | 275 | 270 | 270 | 261 | 249 | 226 | 208 | 200 | 180 | 183 | 186 | 188 | 177 | 183 | 187 |  | 189 | 210 | 223 | 228 | 235 | 225 | 258 | 5337672
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [16 empty] | 0 | 3 |  | 4 | 0 |  |  |  |  | 0 | 3926
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 20 | 21 | 21 | 21 | 20 | 18 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 16 | 17 |  | 21 | 22 | 22 | 22 | 22 | 22 | 22 | 432960
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 225972
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | 25 | 0 |  |  |  |  | 8 | 8 | 24 | 24 | 16 | 16 | 16 | 16 | 16 | 34 | 34 | 34 |  | 34 | 34 | 34 | 8 | 8 | 8 | 8 | 365676
167 | Katakhali 50 MW Peaking PP | [16 empty] | 0 | 37 |  | 40 | 40 | 0 |  |  |  |  | 71420
168 | Santahar 50 MW Peaking PP | [17 empty] | 24 |  | 29 | 29 | 0 |  |  |  |  | 48667
169 | Natore 52 MW PP (Rajlanka) | [6 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 43 |  | 11 | 0 |  |  |  |  | 0 | 139200
170 | Chapainawabganj 100 MW Peaking PP | [16 empty] | 0 | 80 |  | 25 | 25 | 0 |  |  |  |  | 116057
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 35 | 82 | 35 | 35 | 35 | 35 | 35 | 35 | 69 | 70 | 35 | 35 | 57 | 94 | 94 | 94 | 106 | 113 |  | 113 | 113 | 113 | 113 | 70 | 70 | 70 | 1817184
172 | Confidence Power Bogura Unit-1 113 MW | 70 | 70 | 70 | 70 | 70 | 70 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 113 | 95 | 95 |  | 95 | 95 | 95 | 95 | 95 | 37 | 35 | 1531968
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | 56 | 0 |  |  |  | 34 | 65 | 97 | 95 | 70 | 34 | 34 | 90 | 106 | 113 | 113 | 113 | 113 |  | 113 | 113 | 113 | 113 | 34 | 34 | 47 | 1584739
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 3 | 4 | 6 | 6 | 6 | 5 | 4 | 2 | 0 | [9 empty] | 35989
178 | Energypac Power Venture Thakurgaon Ltd. | [6 empty] | 17 | 72 | 56 | 36 | 36 | 36 | 56 | 56 | 45 | 17 | 17 | 115 |  | 115 | 74 | 37 | 37 | 37 | 37 | 37 | 842688
178 | Intraco Solar 30 MW | [6 empty] | 1 | 9 | 16 | 25 | 29 | 32 | 24 | 22 | 15 | 7 | 0 | [9 empty] | 184330