## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2022-11-25 | Friday
|  | Date (day): | 2022-11-25 |  | Friday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 8782.6 | MW |  |  | (b) At Evening Peak Hour : |  | 10688 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2022-11-24 | 2022-11-25 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Line O/L
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 200 | 200 |  | 365 | Machine problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 66 | 71 | 22 | 22 | 86 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 328 | 313 | 320 | 310 | 102 |  | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 275 | 267 | 0 | 0 | 360 |  | DCT of Siddhirganj peaking
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 150 | 225 | 225 |  | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 68 | 83 | 50 | 92 |  | 8 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas line maintenance
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 0 | 0 | 0 | 0 |  | 102 | Under maint
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 30 | 45 | 30 | 45 |  | 10 | Engine problem
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 22 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 100 |  |  | DCT
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 71 | 80 | 80 | 90 |  | 10 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 16 | 40 | 16 | 50 | 52 |  | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 54 | 17 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 48 | 48 | 48 | 133 | 16 |  | Fuel shortage
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 35 | 35 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 35 | 17 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 48 | 51 | 48 | 48 |  | 32 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 30 | 28 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 33 | 49 | 50 | 50
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 97 | 289 | 97 | 275 |  | 25 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 191 | 224 | 100 | 150 | 150 |  | Fuel conservation
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 97 | 95 | 50 | 50 | 50 |  | Fuel conservation
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 94 | 96 | 50 | 50 | 50 |  | Fuel conservation
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 135 | 143 | 135 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 105 | 105 | 105 | 105
37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 17 | 17 | 17 | 17 | 87 |  | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 62 | 162 | 17 | 162
39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 28 | 0 | 30 | 0
40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 17 | 17 | 17 | 38 |  | Fuel shortage
| Dhaka area Total |  |  |  |  | 6263 | 5847 | 2394 | 2807 | 2179 | 2772 | 1937 | 1232
41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 17 | 17 | 17 | 17 |  | 8 | Engine problem
43 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 20 | 0 | 20 | 0
44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 13 | 26 | 19 | 43 |  | 7 | Engine problem
45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 76 | 76 | 46 | 46 | 184 |  | Low Water Level
46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 151 | 151 | 150 | 150 |  | 75 | ST under maint
47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 68 | 68 | 68 | 105
49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 48 | 38 | 22 | 33 | 65 |  | Fuel shortage
50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 17 | 51 | 17 | 51 | 51 |  | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 10 | 10 | 10 | 10 | 90 |  | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 12 | 12 | 12 | 88 |  | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  | 22 | Engine problem
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 3 | 15 | 25
54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 250 | 286 | 300 | 300
57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 54 | 36 | 36 | 36 |  | 18 | Engine problem
58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 53 | 57 | 53 | 91 |  | 19 | Engine problem
59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 12 | 12 | 12 | 88 |  | Fuel shortage
60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 89 | 89 | 89 | 89 |  | 27 | Engine problem
| Mirsharai 150 MW |  | Gas/HSD | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0
| Chattogram area Total |  |  |  |  | 2442 | 2382 | 896 | 932 | 891 | 1020 | 1034 | 326
61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 0 | 0 | 0 | 0 |  | 221 | Under maint.
63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint
64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 230 | 210 | 280 | 280 | 80 |  | Gas shortage
| Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+136*1 | 284 | 284 | 432 | 430 | 400 | 400 |  |  | On test.
65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 44 | 41 | 44 | 44
66 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 55 | 25 | 25 | 25 | 25 | 30 |  | Gas shortae
67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 0 | 0 | 0 | 0 | 195 |  | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 5 | 5 | 5 | 5 | 46 |  | Gas shortage
69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 75 | 120 | 85 | 115 | 35 |  | Fuel shortage
70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 24 | 31 | 0 | 30 |  | 22 | Engine problem
71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 79 | 70 | 78 | 78 | 85 |  | Gas shortage.
72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 51 | 92 | 51 | 200
73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 10 | 10 | 10 | 10
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 112 | 114 | 143 | 166
75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 16 | 22 | 33 | 33
76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 16 | 8 | 8 | 44 |  | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 15 | 15 | 15 | 15 |  | 10 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 70 | 50 | 100 | 100 | 100 |  | Fuel conservation
79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 17 | 17 | 17 | 97 |  | Fuel shortage
80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 98 | 89 | 104 | 104 |  | 9 | Engine problem
81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 34 |  | 20 | Engine problem
82 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 97 | 109 | 115 | 115
| Cumilla Area Total |  |  |  |  | 3193 | 3169 | 1447 | 1505 | 1552 | 1801 | 846 | 642
83 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 34 | 34 | 75 | 105 | 97 |  | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 8 | 8 | 8 | 8 | 14 |  | Gas shortage
85 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0
86 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
87 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 58 | 58 | 58 | 58 | 142 |  | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 58 | 59 | 49 | 59 | 56 |  | Fuel shortage
89 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 39 | 0 | 50 | 0
90 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 12 | 12 |  | 10 | Engine problem
| Mymensingh Area Total |  |  |  |  | 717 | 614 | 211 | 171 | 253.6 | 242 | 111 | 10
91 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 30 | 30 | 30 | 30 |  | 40 | Machine problem.
92 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 43 | 43 | 43 | 43 |  | 47 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 | 163 |  | Gas shortage
94 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 50 | 50 | 50 | 50
96 | Fenchuganj 44MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 37 | 37 | 37 | 37 | 13 |  | Gas shortage
97 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 3 | 3 | 3 | 3 | 8 |  | Gas shortage
98 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 57 | 68 | 66 | 66
99 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 0 | 84 | 0 | 84
100 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
101 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 90 | 90 | 90 | 90 |  | 141 | ST under maint
102 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 19 | 19
103 | Sylhet 50MW PP (EPL) |  | Gas | NENP | 27*2 | 50 | 50 | 26 | 27 | 25 | 25 | 25 |  | Gas shortage
104 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 24 | 22 | 24
105 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 0 | 0 | 0 | 0 |  | 341 | Under maint. |  | 2022-12-23
106 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 415 | 420 | 400 | 400
107 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
108 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 400 | 400 | 400 | 400
| Sylhet Area Total |  |  |  |  | 2522 | 2477 | 1195 | 1304 | 1195 | 1281 | 209 | 999
109 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 895 | 893 | 480 | 720
110 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 10 | 97 | 66 | 115
111 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 50
112 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
113 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 60 | 0 | 75 |  | 34 | Engine problem
114 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 155 | 155 | 160 | 165 | 245 |  | Gas shortage
115 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 32 | 0 | 32 | 8 |  | Fuel shortage
116 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 0 | 50 | 50 |  | Fuel conservation
117 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 17 | 60 | 54 | 94 |  | 11 | Engine problem
118 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Fuel shortage
119 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 75 | 0 | 100 | 0
| Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 2388 | 2384 | 1152 | 1297 | 860 | 1301 | 654 | 45
120 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 0 | 0 |  |  | Line O/L
121 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 13 | 17 | 15 | 20 |  | 20 | Engine problem
122 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 130 | 130 | 130 | 130 |  | 64 | Machine problem
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
123 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 660 | 890 | 850 | 850 |  |  | Line O/L
124 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 0 | 0 | 0 | 0 |  | 220 | Under maint.
125 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 0 | 0 |  |  | Line O/L
| Barisal 307 MW |  | Coal | BCPCL | 0 | 0 | 0 | 251 | 0 | 0 | 0 |  |  | On test.
| Barisal Area Total |  |  |  |  | 1958 | 1958 | 1054 | 1037 | 995 | 1000 | 0 | 304
126 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
127 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 34 |  | 18 | Engine problem
128 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 20 |  | 51 | Engine problem
129 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
130 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 16 | 34 | 34 | 34 |  | 16 | Engine problem
131 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 31 | 0 | 40 | 10 |  | Fuel shortage
132 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 167 | 165 | 165 | 160 | 50 |  | Gas shortage
133 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Fuel shortage
134 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
135 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 201 | 202 | 200 | 200 | 214 |  | Gas shortage
136 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 33 | 0 | 34 |  | 16 | Engine problem
137 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 15 | 16 | 19 | 19 |  | 3 | Engine problem
138 | Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
139 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 11 | 11
140 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 16 | 43 | 35 | 43 |  | 9 | Engine problem
141 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 88 | 0 | 80 |  | 24 | Engine problem
142 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 1 | 0 | 0 | 200 |  | Fuel shortage
143 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 36 | 94 | 70 | 113
144 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 37 | 95 | 35 | 95 |  | 18 | Engine problem
145 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
| Rajshahi Area Total |  |  |  |  | 2199 | 2129 | 501 | 810 | 575 | 883 | 1085 | 155
146 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal shortage
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
147 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 160 | 160 | 160 | 160 |  |  | Machine problem
148 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
149 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
150 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 34 | 84 | 34 | 113
151 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 6 | 0 | 8 | 0
152 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 0 | 0 | 50 | 115
| Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 31 | 0 | 30 | 0
| Rangpur Area Total |  |  |  |  | 830 | 750 | 231 | 244 | 282 | 388 | 125 | 85
| Total |  |  |  |  | 22512 | 21710 | 9081 | 10107 | 8782.6 | 10688 | 6001 | 3798
A. |  | 2022-11-24 | (Yesterday) |  |  |  |  | Thursday
1 | Highest Generation : |  |  | 10107 | MW at | 18:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 18:00 | hrs.
2 | Minimum Generation : |  |  | 6604 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 10107 | MW
3 | Day peak Generation : |  |  | 9081 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 9738.26 | MW
4 | Evening peak Generation : |  |  | 10107 | MW at | 18:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 204.4198 | MKWHr | By Solar | 1.3572 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Gas : | 103.5609 | MKWHr |  | By Oil: | 49.5486 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 26.629 | MKWHr |  | By Hydro: | 1.5378 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 6001 | MW | Dhaka | 3952.82 | 3952.82 |  | 0 |  | 18:00 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 3798 | MW | Chittagong | 1133.2 | 1133.2 |  | 0 |  | 19:00 |  | 0
|  |  | Total = |  |  | 9799 | MW | Khulna | 1048.5 | 1048.5 |  | 0 |  | 19:30 |  | 0
7 | Total Gas Supplied : |  |  | 817.46 | MMCFD |  |  | Rajshahi | 855.7 | 855.7 |  | 0 |  | 20:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 103891004.794 | ii) Oil : | Taka | 673345944.85 | Comilla | 792 | 792 |  | 0 |  | 21:00 |  | 0
|  | iii) Coal : |  | 207103370 | Total | Taka | 984340319.644 | Mymensingh | 703 | 703 |  | 0 |  | 22:00 |  | 0
9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0 | MKWHr. | Sylhet | 373 | 373 |  | 0 |  | 23:00 |  | 0
| ii) During Peak Demand : |  |  | 800 | MW (E to W) at | 18:00 | hrs | Barisal | 227.04 | 227.04 |  | 0 |  | 24:00 |  | 0
| iii) Maximum : |  |  | 684 | MW at | 7:00 | hrs | Rangpur | 653 | 653 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 30.2° C |  |  | Total | 9738.26 | 9738.26 |  | 0
B. |  | 2022-11-25 | (Today) |  |  |  | Friday |  |  | Probable max. temperature in Dhaka |  |  | 29.1° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 10200 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 10688 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 8500 | MW
4 | Reserve(Generation end) |  |  |  | 488 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | 3 | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 206.3008 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 6674 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 19.4458 | MKWHr. | ii) HVDC Flow at Peak Time |  | 893 | MW at | 18:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.3405 | MKWHr. | iii) Maximum HVDC Flow : |  | 895 | MW at | 11:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 90.83 |  | (b) Today: | 90.68 |  | (c) Rule Curve: |  | 106.7
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2022-11-24
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 0 | 71 | 0 | 339 | 292 |  | 0 | 225 | 0 | 25 | 0 | 38 | 0 | 0 | 0 | 30 | 8 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 22 | 22 | 27 | 33 | 33 | 8 | 0 | 46 | 0 | 0 | 0 | 8 | 152 | 0 | 0 | 0 |  | 12 | 55 | 0 | 10 | 0 | 24 | 0 | 13 | 0 | 0 | 0 | 0 | 210 | 0 | 0 | 72 | 45 | 30 | 0 | 5 | 0 | 32 | 8 | 22 | 10 | 33 | 15 | 94 | 110 | 0 | 8 | 0 | 30 | 43 | 53 | 37 | 0 | 0 | 40 | 50 | 0 | 90 | 19 | 26 | 10 | 0 | 22 | 3 | 0 | 98 | 0 | 0 | 48 | 0 | 149 | 0 | 12 | 69 | 73 | 354 | 49 | 105 | 17 | 0 | 16 | 17 | 53 | 17 | 55 | 10 | 400 | 17 | 0 | 17 | 51 | 0 | 17 | 0 | 18 | 17 | 433 | 0 | 0 |  | 658 | 0 | 165 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 237 | 35 | 0 | 70 | 0 | 34 | 0 | 0 | 35 | 710 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 139 |  | 4971 | 2602 | 7573 | 3238 | 658 | 1086 | 0 | 1355 | 1009 | 46 | 0 | 87 | 94 | 0 | 0 | 90.82
2:00 | 0 | 0 | 0 | 180 | 0 | 71 | 0 | 339 | 292 |  | 0 | 225 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 30 | 8 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 22 | 22 | 27 | 33 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 152 | 0 | 0 | 0 |  | 12 | 0 | 0 | 10 | 0 | 24 | 0 | 17 | 0 | 0 | 0 | 0 | 210 | 0 | 0 | 70 | 45 | 30 | 0 | 5 | 0 | 0 | 8 | 22 | 10 | 33 | 15 | 92 | 110 | 0 | 8 | 0 | 30 | 43 | 53 | 37 | 0 | 0 | 40 | 0 | 0 | 90 | 19 | 26 | 10 | 0 | 22 | 3 | 0 | 95 | 0 | 0 | 48 | 0 | 149 | 0 | 12 | 56 | 68 | 354 | 49 | 70 | 17 | 0 | 16 | 17 | 53 | 17 | 55 | 10 | 400 | 17 | 0 | 17 | 51 | 0 | 17 | 0 | 18 | 17 | 433 | 0 | 0 |  | 659 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 700 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142 |  | 4704 | 2444 | 7148 | 3237 | 659 | 1042 | 0 | 1070 | 1002 | 46 | 0 | 0 | 92 | 0 | 0 | 90.82
3:00 | 0 | 0 | 0 | 180 | 0 | 70 | 0 | 340 | 294 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 8 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 17 | 22 | 22 | 27 | 33 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 |  | 12 | 0 | 0 | 10 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 210 | 0 | 0 | 70 | 45 | 30 | 0 | 5 | 0 | 0 | 8 | 22 | 10 | 33 | 15 | 88 | 111 | 0 | 8 | 0 | 30 | 43 | 53 | 37 | 0 | 0 | 40 | 0 | 0 | 90 | 19 | 26 | 10 | 0 | 22 | 3 | 0 | 98 | 0 | 0 | 8 | 0 | 149 | 0 | 12 | 51 | 10 | 354 | 49 | 34 | 17 | 0 | 16 | 17 | 54 | 17 | 8 | 10 | 380 | 17 | 0 | 17 | 51 | 0 | 17 | 0 | 18 | 17 | 433 | 0 | 0 |  | 659 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 700 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 139 |  | 4437 | 2447 | 6884 | 3220 | 659 | 1056 | 0 | 816 | 999 | 46 | 0 | 0 | 88 | 0 | 0 | 90.82
4:00 | 0 | 0 | 0 | 180 | 0 | 70 | 0 | 341 | 297 |  | 0 | 225 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 17 | 22 | 22 | 27 | 33 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 |  | 12 | 0 | 0 | 10 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 210 | 0 | 0 | 70 | 45 | 30 | 0 | 5 | 0 | 0 | 8 | 22 | 10 | 33 | 15 | 80 | 111 | 0 | 8 | 0 | 30 | 43 | 53 | 37 | 0 | 0 | 70 | 0 | 0 | 90 | 19 | 26 | 10 | 0 | 22 | 3 | 0 | 97 | 0 | 0 | 8 | 0 | 82 | 0 | 12 | 17 | 10 | 354 | 49 | 17 | 17 | 0 | 16 | 17 | 54 | 17 | 8 | 10 | 380 | 0 | 0 | 17 | 36 | 0 | 17 | 0 | 17 | 17 | 433 | 0 | 0 |  | 660 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 700 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 139 |  | 4299 | 2450 | 6749 | 3251 | 660 | 1073 | 0 | 640 | 999 | 46 | 0 | 0 | 80 | 0 | 0 | 90.83
5:00 | 0 | 0 | 0 | 180 | 0 | 70 | 0 | 346 | 297 |  | 0 | 225 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 17 | 22 | 22 | 27 | 33 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 |  | 12 | 0 | 0 | 10 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 210 | 0 | 0 | 77 | 45 | 30 | 0 | 5 | 0 | 0 | 8 | 22 | 10 | 33 | 15 | 82 | 111 | 0 | 8 | 0 | 30 | 43 | 53 | 37 | 0 | 0 | 71 | 0 | 0 | 90 | 19 | 26 | 10 | 0 | 21 | 3 | 0 | 97 | 0 | 0 | 8 | 0 | 36 | 0 | 12 | 17 | 10 | 354 | 16 | 17 | 17 | 0 | 16 | 17 | 54 | 17 | 8 | 10 | 380 | 0 | 0 | 17 | 17 | 0 | 17 | 0 | 17 | 17 | 432 | 0 | 0 |  | 659 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 620 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 141 |  | 4238 | 2366 | 6604 | 3281 | 659 | 1076 | 0 | 539 | 921 | 46 | 0 | 0 | 82 | 0 | 0 | 90.83
6:00 | 0 | 0 | 0 | 180 | 0 | 70 | 0 | 354 | 274 |  | 0 | 225 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 1 | 8 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 17 | 22 | 22 | 27 | 33 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 |  | 12 | 0 | 17 | 10 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 77 | 45 | 30 | 0 | 5 | 0 | 0 | 8 | 22 | 10 | 33 | 15 | 84 | 112 | 0 | 8 | 0 | 30 | 43 | 53 | 37 | 0 | 0 | 71 | 0 | 0 | 90 | 19 | 26 | 10 | 0 | 21 | 3 | 0 | 97 | 0 | 0 | 37 | 0 | 41 | 0 | 12 | 23 | 15 | 417 | 47 | 17 | 17 | 0 | 16 | 17 | 54 | 17 | 10 | 10 | 380 | 2 | 0 | 17 | 27 | 0 | 17 | 0 | 18 | 17 | 432 | 0 | 0 |  | 659 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 236 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 35 | 630 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 |  | 4469 | 2371 | 6840 | 3404 | 659 | 1033 | 0 | 667 | 930 | 46 | 0 | 17 | 84 | 0 | 0 | 90.83
7:00 | 0 | 0 | 0 | 180 | 0 | 70 | 0 | 355 | 290 |  | 0 | 225 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 26 | 8 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 17 | 22 | 22 | 27 | 33 | 33 | 4 | 0 | 46 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 |  | 12 | 0 | 17 | 10 | 0 | 12 | 0 | 24 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 77 | 45 | 30 | 0 | 5 | 0 | 0 | 8 | 22 | 0 | 33 | 15 | 78 | 73 | 0 | 8 | 0 | 30 | 43 | 53 | 37 | 0 | 0 | 67 | 0 | 0 | 90 | 19 | 26 | 10 | 0 | 21 | 3 | 0 | 98 | 0 | 0 | 46 | 0 | 108 | 3 | 12 | 51 | 32 | 386 | 47 | 17 | 17 | 0 | 16 | 28 | 54 | 17 | 51 | 12 | 400 | 17 | 3 | 17 | 89 | 0 | 17 | 2 | 18 | 17 | 429 | 0 | 0 |  | 659 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 261 | 18 | 0 | 30 | 0 | 1 | 0 | 0 | 35 | 680 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 1 | 132 |  | 4708 | 2513 | 7221 | 3361 | 659 | 1065 | 0 | 1009 | 972 | 46 | 0 | 17 | 78 | 14 | 0 | 90.81
8:00 | 0 | 0 | 0 | 180 | 0 | 70 | 0 | 353 | 297 |  | 0 | 225 | 0 | 6 | 0 | 30 | 0 | 0 | 0 | 30 | 8 | 100 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 19 | 22 | 23 | 33 | 33 | 15 | 0 | 46 | 0 | 0 | 0 | 8 | 151 | 0 | 0 | 0 |  | 12 | 0 | 17 | 10 | 0 | 16 | 0 | 2 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 79 | 45 | 30 | 0 | 5 | 0 | 0 | 8 | 22 | 10 | 28 | 15 | 92 | 70 | 0 | 8 | 1 | 30 | 43 | 53 | 37 | 0 | 0 | 69 | 0 | 0 | 90 | 19 | 26 | 10 | 0 | 21 | 3 | 0 | 97 | 0 | 0 | 48 | 0 | 134 | 9 | 12 | 51 | 57 | 418 | 49 | 88 | 17 | 1 | 16 | 36 | 53 | 17 | 81 | 12 | 400 | 18 | 17 | 17 | 89 | 0 | 17 | 8 | 18 | 17 | 433 | 0 | 0 |  | 659 | 0 | 180 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 23 | 0 | 19 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 251 | 46 | 0 | 55 | 0 | 26 | 0 | 1 | 35 | 790 | 0 | 0 | 0 | 1 | 26 | 28 | 0 | 0 | 0 | 9 | 130 |  | 5099 | 2861 | 7960 | 3394 | 659 | 1038 | 0 | 1461 | 1080 | 46 | 0 | 117 | 92 | 73 | 0 | 90.8
9:00 | 0 | 0 | 0 | 180 | 0 | 70 | 0 | 350 | 292 |  | 0 | 225 | 0 | 25 | 0 | 30 | 0 | 0 | 0 | 30 | 8 | 114 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 19 | 22 | 28 | 33 | 31 | 24 | 0 | 46 | 0 | 0 | 0 | 17 | 151 | 0 | 0 | 0 |  | 12 | 30 | 17 | 10 | 0 | 19 | 0 | 2 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 77 | 45 | 30 | 0 | 5 | 0 | 0 | 8 | 22 | 10 | 22 | 15 | 94 | 72 | 0 | 8 | 1 | 30 | 43 | 53 | 37 | 0 | 0 | 66 | 0 | 0 | 90 | 19 | 26 | 10 | 0 | 21 | 3 | 0 | 97 | 0 | 0 | 48 | 0 | 149 | 14 | 12 | 51 | 72 | 416 | 49 | 88 | 17 | 3 | 16 | 36 | 53 | 17 | 106 | 12 | 380 | 17 | 31 | 17 | 89 | 0 | 17 | 17 | 18 | 17 | 433 | 0 | 0 |  | 753 | 0 | 180 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 121 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 34 | 0 | 17 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 231 | 56 | 0 | 70 | 0 | 32 | 0 | 3 | 37 | 770 | 0 | 0 | 0 | 3 | 46 | 34 | 0 | 0 | 0 | 15 | 162 |  | 5223 | 3037 | 8260 | 3341 | 753 | 1010 | 0 | 1630 | 1092 | 46 | 0 | 161 | 94 | 133 | 0 | 90.8
10:00 | 0 | 0 | 0 | 180 | 0 | 71 | 0 | 343 | 281 |  | 0 | 225 | 0 | 30 | 0 | 30 | 0 | 0 | 0 | 48 | 8 | 48 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 19 | 22 | 28 | 25 | 30 | 32 | 0 | 46 | 0 | 0 | 0 | 17 | 151 | 0 | 0 | 0 |  | 12 | 45 | 17 | 10 | 0 | 19 | 0 | 2 | 0 | 0 | 0 | 0 | 210 | 0 | 0 | 76 | 45 | 25 | 0 | 5 | 0 | 0 | 8 | 22 | 10 | 21 | 15 | 98 | 68 | 0 | 8 | 2 | 30 | 43 | 50 | 37 | 0 | 0 | 52 | 0 | 0 | 90 | 18 | 26 | 10 | 0 | 16 | 3 | 0 | 97 | 0 | 0 | 48 | 0 | 149 | 18 | 12 | 51 | 78 | 401 | 49 | 88 | 33 | 4 | 16 | 36 | 53 | 17 | 108 | 9 | 395 | 17 | 41 | 17 | 89 | 0 | 17 | 23 | 18 | 15 | 428 | 0 | 0 |  | 801 | 0 | 165 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 34 | 0 | 16 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 212 | 56 | 0 | 70 | 0 | 34 | 0 | 4 | 37 | 720 | 0 | 0 | 0 | 4 | 63 | 0 | 0 | 0 | 0 | 25 | 161 |  | 5123 | 2974 | 8097 | 3225 | 801 | 972 | 0 | 1620 | 1041 | 46 | 0 | 110 | 98 | 184 | 0 | 90.8
11:00 | 0 | 0 | 0 | 180 | 0 | 66 | 0 | 335 | 281 |  | 0 | 225 | 0 | 59 | 0 | 30 | 0 | 0 | 0 | 71 | 16 | 48 | 0 | 0 | 0 | 0 | 17 | 55 | 17 | 19 | 22 | 28 | 25 | 30 | 32 | 0 | 92 | 0 | 0 | 0 | 17 | 151 | 0 | 0 | 0 |  | 12 | 48 | 17 | 10 | 0 | 19 | 0 | 2 | 0 | 0 | 0 | 0 | 210 | 0 | 0 | 78 | 45 | 25 | 0 | 5 | 0 | 22 | 8 | 22 | 10 | 20 | 8 | 102 | 34 | 0 | 8 | 2 | 30 | 43 | 50 | 37 | 0 | 0 | 61 | 0 | 0 | 90 | 18 | 26 | 10 | 0 | 16 | 3 | 20 | 97 | 97 | 50 | 56 | 60 | 135 | 20 | 12 | 51 | 85 | 419 | 58 | 105 | 61 | 4 | 100 | 39 | 53 | 17 | 102 | 12 | 380 | 17 | 46 | 17 | 89 | 0 | 17 | 28 | 52 | 17 | 432 | 0 | 0 |  | 895 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 16 | 0 | 15 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 207 | 17 | 0 | 35 | 0 | 34 | 0 | 5 | 37 | 690 | 0 | 0 | 0 | 3 | 72 | 0 | 0 | 0 | 0 | 27 | 215 |  | 5655 | 2902 | 8557 | 3170 | 895 | 962 | 227 | 1702 | 1065 | 92 | 0 | 135 | 102 | 207 | 0 | #REF!
12:00 | 0 | 0 | 0 | 180 | 0 | 66 | 0 | 328 | 275 |  | 0 | 225 | 0 | 68 | 0 | 30 | 0 | 0 | 0 | 71 | 16 | 48 | 0 | 0 | 0 | 0 | 17 | 55 | 17 | 19 | 22 | 26 | 25 | 30 | 33 | 0 | 76 | 0 | 0 | 0 | 17 | 151 | 0 | 0 | 0 |  | 12 | 48 | 17 | 10 | 0 | 13 | 0 | 2 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 79 | 44 | 25 | 0 | 5 | 0 | 24 | 8 | 22 | 10 | 16 | 15 | 112 | 34 | 0 | 8 | 2 | 30 | 43 | 50 | 37 | 0 | 0 | 57 | 0 | 0 | 90 | 18 | 26 | 10 | 0 | 16 | 3 | 70 | 97 | 191 | 97 | 58 | 94 | 135 | 20 | 12 | 51 | 75 | 415 | 58 | 105 | 68 | 4 | 250 | 54 | 53 | 17 | 98 | 12 | 400 | 17 | 39 | 62 | 89 | 0 | 17 | 28 | 97 | 17 | 432 | 0 | 0 |  | 895 | 0 | 155 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 16 | 0 | 15 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 201 | 17 | 0 | 36 | 0 | 34 | 0 | 6 | 37 | 660 | 0 | 0 | 0 | 5 | 75 | 0 | 0 | 0 | 0 | 31 | 251 |  | 6143 | 2938 | 9081 | 3203 | 895 | 950 | 452 | 1975 | 1071 | 76 | 0 | 137 | 112 | 210 | 0 | 90.79
13:00 | 0 | 0 | 0 | 180 | 0 | 70 | 0 | 329 | 277 |  | 0 | 225 | 0 | 74 | 0 | 37 | 0 | 0 | 0 | 71 | 16 | 48 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 19 | 22 | 26 | 25 | 30 | 37 | 0 | 76 | 0 | 0 | 0 | 17 | 151 | 0 | 0 | 0 |  | 12 | 40 | 17 | 10 | 0 | 12 | 0 | 2 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 70 | 44 | 25 | 0 | 5 | 0 | 28 | 8 | 22 | 10 | 16 | 15 | 110 | 34 | 0 | 8 | 2 | 30 | 43 | 50 | 37 | 0 | 0 | 57 | 0 | 0 | 90 | 18 | 26 | 10 | 0 | 21 | 3 | 100 | 97 | 246 | 97 | 58 | 94 | 135 | 18 | 12 | 51 | 77 | 399 | 58 | 105 | 51 | 4 | 250 | 54 | 53 | 17 | 99 | 12 | 395 | 17 | 39 | 72 | 89 | 0 | 17 | 28 | 83 | 17 | 424 | 0 | 0 |  | 895 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 43 | 0 | 15 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 168 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 199 | 22 | 0 | 55 | 0 | 34 | 0 | 6 | 37 | 690 | 0 | 0 | 0 | 5 | 68 | 0 | 0 | 0 | 0 | 28 | 0 |  | 6210 | 2771 | 8981 | 3167 | 895 | 955 | 547 | 2050 | 850 | 76 | 0 | 133 | 110 | 198 | 0 | 0
14:00 | 0 | 0 | 0 | 180 | 0 | 70 | 0 | 328 | 276 |  | 0 | 225 | 0 | 74 | 0 | 45 | 0 | 0 | 0 | 71 | 16 | 48 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 22 | 26 | 25 | 28 | 44 | 0 | 76 | 0 | 0 | 0 | 6 | 151 | 0 | 0 | 0 |  | 12 | 40 | 17 | 10 | 0 | 12 | 0 | 2 | 0 | 0 | 0 | 0 | 210 | 0 | 0 | 71 | 43 | 25 | 0 | 5 | 0 | 30 | 8 | 22 | 10 | 16 | 15 | 112 | 34 | 0 | 8 | 2 | 30 | 43 | 53 | 37 | 0 | 0 | 57 | 0 | 0 | 90 | 18 | 26 | 10 | 0 | 21 | 3 | 20 | 97 | 30 | 25 | 57 | 40 | 135 | 15 | 12 | 51 | 82 | 422 | 58 | 105 | 51 | 3 | 258 | 36 | 53 | 17 | 100 | 12 | 400 | 17 | 35 | 72 | 89 | 0 | 17 | 22 | 79 | 17 | 430 | 0 | 0 |  | 895 | 0 | 150 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 16 | 123 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 43 | 0 | 15 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 199 | 55 | 0 | 70 | 0 | 34 | 0 | 5 | 37 | 770 | 0 | 0 | 0 | 4 | 54 | 0 | 0 | 0 | 0 | 20 | 0 |  | 5766 | 2920 | 8686 | 3167 | 895 | 957 | 115 | 2139 | 930 | 76 | 0 | 135 | 112 | 160 | 0 | 90.79
15:00 | 0 | 0 | 0 | 180 | 0 | 71 | 0 | 329 | 271 |  | 0 | 225 | 0 | 74 | 0 | 45 | 0 | 0 | 0 | 71 | 16 | 48 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 22 | 26 | 25 | 28 | 49 | 0 | 76 | 0 | 0 | 0 | 17 | 151 | 0 | 0 | 0 |  | 12 | 40 | 17 | 10 | 0 | 12 | 0 | 2 | 0 | 0 | 0 | 0 | 210 | 0 | 0 | 70 | 43 | 25 | 0 | 5 | 0 | 30 | 8 | 22 | 10 | 16 | 15 | 104 | 34 | 0 | 8 | 1 | 30 | 43 | 47 | 37 | 0 | 0 | 57 | 0 | 0 | 90 | 18 | 25 | 10 | 0 | 21 | 3 | 0 | 97 | 15 | 25 | 58 | 0 | 133 | 11 | 12 | 51 | 90 | 422 | 58 | 105 | 51 | 2 | 263 | 36 | 53 | 17 | 99 | 12 | 400 | 17 | 25 | 72 | 89 | 0 | 17 | 15 | 64 | 17 | 430 | 0 | 0 |  | 895 | 0 | 150 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 32 | 130 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 43 | 0 | 15 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 55 | 0 | 70 | 0 | 34 | 0 | 4 | 37 | 840 | 0 | 0 | 0 | 2 | 35 | 0 | 0 | 0 | 0 | 13 | 0 |  | 5661 | 2965 | 8626 | 3175 | 895 | 927 | 40 | 2166 | 1000 | 76 | 0 | 135 | 104 | 108 | 0 | 0
16:00 | 0 | 0 | 0 | 180 | 0 | 71 | 0 | 325 | 266 |  | 0 | 225 | 0 | 82 | 0 | 45 | 0 | 0 | 0 | 71 | 16 | 48 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 22 | 26 | 25 | 28 | 47 | 0 | 76 | 0 | 0 | 0 | 17 | 151 | 0 | 0 | 0 |  | 12 | 40 | 17 | 10 | 0 | 7 | 0 | 2 | 0 | 0 | 0 | 0 | 210 | 0 | 0 | 71 | 44 | 25 | 0 | 5 | 0 | 23 | 8 | 22 | 10 | 22 | 15 | 98 | 34 | 0 | 8 | 0 | 30 | 43 | 50 | 37 | 0 | 0 | 60 | 0 | 0 | 90 | 18 | 25 | 10 | 0 | 21 | 3 | 0 | 104 | 0 | 0 | 58 | 0 | 141 | 5 | 12 | 51 | 100 | 419 | 58 | 105 | 65 | 1 | 268 | 36 | 53 | 17 | 105 | 12 | 400 | 17 | 5 | 73 | 89 | 0 | 17 | 7 | 78 | 17 | 429 | 0 | 0 |  | 895 | 0 | 155 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 24 | 0 | 15 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 56 | 0 | 70 | 0 | 34 | 0 | 4 | 60 | 850 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 6 | 0 |  | 5642 | 2924 | 8566 | 3186 | 895 | 925 | 0 | 2205 | 1010 | 76 | 0 | 128 | 98 | 43 | 0 | 0
17:00 | 0 | 0 | 0 | 180 | 0 | 71 | 0 | 322 | 267 |  | 0 | 225 | 0 | 81 | 0 | 45 | 0 | 0 | 0 | 71 | 16 | 48 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 22 | 26 | 33 | 28 | 49 | 0 | 76 | 0 | 0 | 0 | 17 | 151 | 0 | 0 | 0 |  | 12 | 28 | 17 | 10 | 0 | 22 | 0 | 2 | 0 | 0 | 0 | 0 | 210 | 0 | 0 | 71 | 44 | 25 | 0 | 5 | 0 | 25 | 8 | 22 | 10 | 22 | 15 | 102 | 34 | 0 | 8 | 0 | 30 | 43 | 47 | 37 | 0 | 0 | 60 | 0 | 0 | 90 | 18 | 26 | 10 | 0 | 21 | 3 | 0 | 100 | 98 | 25 | 48 | 25 | 137 | 0 | 12 | 51 | 112 | 416 | 50 | 105 | 68 | 0 | 268 | 36 | 53 | 17 | 104 | 12 | 400 | 17 | 0 | 151 | 89 | 0 | 17 | 1 | 86 | 17 | 427 | 0 | 0 |  | 895 | 0 | 150 | 0 | 65 | 0 | 0 | 0 | 0 | 10 | 16 | 130 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 24 | 14 | 16 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 56 | 0 | 94 | 0 | 49 | 0 | 0 | 95 | 850 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5856 | 3019 | 8875 | 3181 | 895 | 918 | 148 | 2401 | 1010 | 76 | 0 | 142 | 102 | 2 | 0 | 0
18:00 | 0 | 0 | 0 | 180 | 0 | 71 | 0 | 313 | 267 |  | 0 | 225 | 0 | 83 | 0 | 45 | 0 | 0 | 0 | 80 | 40 | 48 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 22 | 25 | 26 | 33 | 28 | 49 | 0 | 76 | 0 | 0 | 0 | 17 | 151 | 0 | 0 | 0 |  | 12 | 38 | 51 | 10 | 0 | 26 | 0 | 3 | 0 | 0 | 0 | 0 | 210 | 0 | 0 | 70 | 41 | 25 | 0 | 5 | 0 | 31 | 16 | 22 | 10 | 22 | 15 | 114 | 34 | 0 | 8 | 0 | 30 | 43 | 50 | 37 | 0 | 0 | 68 | 84 | 0 | 90 | 18 | 27 | 10 | 0 | 24 | 3 | 50 | 289 | 224 | 95 | 58 | 96 | 143 | 0 | 12 | 92 | 120 | 420 | 59 | 105 | 68 | 0 | 286 | 36 | 57 | 17 | 89 | 12 | 400 | 17 | 0 | 162 | 89 | 0 | 17 | 0 | 109 | 17 | 430 | 0 | 0 |  | 893 | 0 | 155 | 0 | 97 | 0 | 0 | 0 | 0 | 60 | 32 | 130 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 0 | 34 | 31 | 43 | 33 | 16 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202 | 60 | 1 | 94 | 0 | 84 | 0 | 0 | 95 | 890 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6719 | 3388 | 10107 | 3194 | 893 | 1039 | 466 | 2895 | 1050 | 76 | 0 | 380 | 114 | 0 | 0 | 0
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 100 | 71 | 0 | 312 | 268 |  | 0 | 225 | 0 | 82 | 0 | 45 | 0 | 0 | 0 | 80 | 40 | 48 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 26 | 33 | 28 | 49 | 0 | 76 | 0 | 0 | 0 | 17 | 151 | 0 | 0 | 0 |  | 12 | 32 | 51 | 10 | 0 | 26 | 0 | 8 | 0 | 0 | 0 | 0 | 210 | 0 | 0 | 71 | 44 | 25 | 0 | 5 | 0 | 22 | 16 | 0 | 10 | 22 | 15 | 108 | 44 | 0 | 8 | 0 | 30 | 43 | 47 | 37 | 0 | 0 | 63 | 84 | 0 | 90 | 18 | 26 | 10 | 0 | 24 | 3 | 0 | 279 | 4 | 40 | 57 | 70 | 133 | 0 | 12 | 120 | 112 | 420 | 59 | 105 | 74 | 0 | 285 | 36 | 75 | 17 | 112 | 12 | 390 | 17 | 0 | 162 | 90 | 0 | 17 | 0 | 116 | 26 | 434 | 0 | 0 |  | 893 | 0 | 155 | 0 | 97 | 0 | 0 | 0 | 0 | 85 | 32 | 113 | 17 | 0 | 0 | 0 | 0 | 24 | 0 | 88 | 0 | 34 | 40 | 39 | 34 | 19 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 199 | 67 | 50 | 94 | 0 | 85 | 0 | 0 | 95 | 940 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6530 | 3532 | 10062 | 3256 | 893 | 1041 | 164 | 3000 | 1100 | 76 | 0 | 424 | 108 | 0 | 0 | 0
19:30 | 0 | 0 | 0 | 180 | 120 | 71 | 0 | 307 | 267 |  | 0 | 225 | 0 | 82 | 0 | 45 | 0 | 0 | 0 | 80 | 41 | 48 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 26 | 33 | 28 | 49 | 0 | 76 | 0 | 0 | 0 | 17 | 151 | 0 | 0 | 0 |  | 12 | 16 | 51 | 10 | 0 | 26 | 0 | 9 | 0 | 0 | 0 | 0 | 210 | 0 | 0 | 71 | 44 | 25 | 0 | 5 | 0 | 22 | 16 | 0 | 10 | 30 | 15 | 108 | 50 | 0 | 8 | 0 | 30 | 43 | 47 | 37 | 0 | 0 | 63 | 84 | 0 | 90 | 18 | 26 | 10 | 0 | 24 | 3 | 0 | 264 | 0 | 25 | 57 | 0 | 143 | 0 | 12 | 101 | 108 | 420 | 59 | 105 | 68 | 0 | 285 | 36 | 91 | 34 | 119 | 12 | 400 | 17 | 0 | 162 | 107 | 0 | 17 | 0 | 115 | 17 | 432 | 0 | 0 |  | 893 | 0 | 155 | 0 | 97 | 0 | 0 | 0 | 0 | 80 | 16 | 130 | 16 | 0 | 0 | 0 | 0 | 24 | 0 | 49 | 0 | 34 | 40 | 25 | 34 | 20 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 204 | 75 | 30 | 94 | 0 | 85 | 0 | 0 | 95 | 970 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6476 | 3498 | 9974 | 3310 | 893 | 1046 | 55 | 2992 | 1130 | 76 | 0 | 364 | 108 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 180 | 150 | 42 | 0 | 309 | 265 |  | 0 | 225 | 0 | 82 | 0 | 45 | 0 | 0 | 0 | 80 | 41 | 42 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 26 | 33 | 28 | 49 | 0 | 76 | 0 | 0 | 0 | 17 | 151 | 0 | 0 | 0 |  | 12 | 38 | 51 | 10 | 0 | 26 | 0 | 8 | 0 | 0 | 0 | 0 | 210 | 0 | 0 | 70 | 45 | 25 | 0 | 5 | 0 | 0 | 16 | 0 | 10 | 33 | 15 | 108 | 51 | 0 | 8 | 0 | 30 | 43 | 47 | 37 | 0 | 0 | 63 | 84 | 0 | 90 | 19 | 26 | 10 | 0 | 24 | 3 | 0 | 266 | 0 | 0 | 58 | 0 | 149 | 0 | 12 | 85 | 108 | 419 | 59 | 105 | 68 | 0 | 285 | 36 | 90 | 17 | 118 | 12 | 400 | 17 | 0 | 162 | 107 | 0 | 17 | 0 | 115 | 24 | 433 | 0 | 0 |  | 894 | 0 | 160 | 0 | 97 | 0 | 0 | 0 | 0 | 80 | 16 | 125 | 18 | 0 | 0 | 0 | 0 | 24 | 0 | 49 | 0 | 34 | 40 | 8 | 34 | 22 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 203 | 75 | 0 | 94 | 0 | 85 | 0 | 0 | 95 | 970 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6431 | 3455 | 9886 | 3347 | 894 | 1017 | 0 | 2956 | 1130 | 76 | 0 | 358 | 108 | 0 | 0 | 0
21:00 | 0 | 0 | 0 | 180 | 190 | 42 | 0 | 307 | 266 |  | 0 | 225 | 0 | 75 | 0 | 45 | 0 | 0 | 0 | 80 | 41 | 32 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 25 | 26 | 33 | 28 | 49 | 0 | 76 | 0 | 0 | 0 | 17 | 151 | 0 | 0 | 0 |  | 12 | 32 | 51 | 10 | 0 | 26 | 0 | 5 | 0 | 0 | 0 | 0 | 210 | 0 | 0 | 71 | 45 | 25 | 0 | 5 | 0 | 0 | 8 | 0 | 10 | 32 | 15 | 112 | 54 | 0 | 8 | 0 | 30 | 43 | 50 | 37 | 0 | 0 | 68 | 84 | 0 | 90 | 19 | 27 | 10 | 0 | 24 | 3 | 0 | 283 | 0 | 0 | 58 | 0 | 149 | 0 | 12 | 85 | 102 | 395 | 59 | 105 | 78 | 0 | 70 | 36 | 91 | 0 | 115 | 12 | 370 | 17 | 0 | 162 | 107 | 0 | 17 | 0 | 115 | 17 | 434 | 0 | 0 |  | 892 | 0 | 160 | 0 | 97 | 0 | 0 | 0 | 0 | 45 | 16 | 130 | 18 | 0 | 0 | 0 | 0 | 24 | 0 | 49 | 0 | 25 | 32 | 43 | 34 | 22 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 217 | 75 | 0 | 94 | 0 | 35 | 0 | 0 | 95 | 990 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 0 | 0 | 0 |  | 6102 | 3498 | 9600 | 3346 | 892 | 1033 | 0 | 2692 | 1150 | 76 | 0 | 299 | 112 | 0 | 0 | 0
22:00 | 0 | 0 | 0 | 180 | 200 | 22 | 0 | 307 | 267 |  | 0 | 225 | 0 | 65 | 0 | 45 | 0 | 0 | 0 | 70 | 41 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 25 | 26 | 33 | 30 | 24 | 0 | 76 | 0 | 0 | 0 | 17 | 151 | 0 | 0 | 0 |  | 12 | 24 | 51 | 10 | 0 | 26 | 0 | 6 | 0 | 0 | 0 | 0 | 210 | 0 | 0 | 71 | 45 | 25 | 0 | 5 | 0 | 0 | 8 | 6 | 10 | 32 | 15 | 102 | 75 | 0 | 8 | 0 | 30 | 43 | 50 | 37 | 0 | 0 | 69 | 84 | 0 | 90 | 19 | 26 | 10 | 0 | 24 | 3 | 0 | 283 | 0 | 0 | 58 | 0 | 84 | 0 | 12 | 85 | 98 | 352 | 59 | 105 | 105 | 0 | 68 | 36 | 90 | 0 | 65 | 12 | 370 | 17 | 0 | 162 | 107 | 0 | 17 | 0 | 115 | 17 | 433 | 0 | 0 |  | 894 | 0 | 165 | 0 | 114 | 0 | 0 | 0 | 0 | 0 | 16 | 130 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 43 | 0 | 22 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 217 | 75 | 0 | 94 | 0 | 35 | 0 | 0 | 90 | 880 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 0 | 0 | 0 |  | 5889 | 3205 | 9094 | 3346 | 894 | 1014 | 0 | 2547 | 1040 | 76 | 0 | 75 | 102 | 0 | 0 | 90.76
23:00 | 0 | 0 | 0 | 180 | 200 | 22 | 0 | 310 | 267 |  | 0 | 225 | 0 | 50 | 0 | 45 | 0 | 0 | 0 | 40 | 41 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 35 | 22 | 25 | 26 | 33 | 30 | 30 | 0 | 76 | 0 | 0 | 0 | 17 | 151 | 0 | 0 | 0 |  | 12 | 24 | 34 | 10 | 0 | 26 | 0 | 8 | 0 | 0 | 0 | 0 | 210 | 0 | 0 | 71 | 45 | 25 | 0 | 5 | 0 | 0 | 8 | 19 | 11 | 32 | 15 | 100 | 105 | 0 | 8 | 0 | 30 | 43 | 50 | 37 | 0 | 0 | 69 | 84 | 0 | 90 | 19 | 26 | 10 | 0 | 22 | 3 | 0 | 260 | 0 | 0 | 58 | 0 | 0 | 0 | 12 | 85 | 85 | 418 | 59 | 105 | 58 | 0 | 68 | 36 | 70 | 17 | 65 | 12 | 400 | 17 | 0 | 144 | 107 | 0 | 17 | 0 | 79 | 17 | 432 | 0 | 0 |  | 894 | 0 | 170 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 16 | 116 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 43 | 0 | 22 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 236 | 75 | 0 | 70 | 0 | 35 | 0 | 0 | 35 | 800 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 0 | 0 | 0 |  | 5731 | 3062 | 8793 | 3479 | 894 | 1035 | 0 | 2191 | 960 | 76 | 0 | 58 | 100 | 0 | 0 | 90.75
24:00 | 0 | 0 | 0 | 180 | 200 | 22 | 0 | 315 | 267 |  | 0 | 225 | 0 | 28 | 0 | 45 | 0 | 0 | 0 | 24 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 25 | 26 | 33 | 31 | 50 | 0 | 76 | 0 | 0 | 0 | 17 | 151 | 0 | 0 | 0 |  | 12 | 24 | 20 | 10 | 0 | 26 | 0 | 8 | 0 | 0 | 0 | 0 | 210 | 0 | 0 | 70 | 45 | 25 | 0 | 5 | 0 | 0 | 8 | 19 | 11 | 33 | 15 | 96 | 104 | 0 | 8 | 0 | 30 | 43 | 50 | 37 | 0 | 0 | 70 | 84 | 0 | 90 | 19 | 26 | 10 | 0 | 22 | 3 | 0 | 143 | 48 | 50 | 48 | 50 | 0 | 0 | 12 | 85 | 73 | 418 | 49 | 105 | 17 | 0 | 67 | 36 | 60 | 17 | 65 | 12 | 400 | 17 | 0 | 17 | 107 | 0 | 17 | 0 | 26 | 17 | 432 | 0 | 0 |  | 801 | 0 | 170 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 116 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 43 | 0 | 21 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 231 | 53 | 0 | 70 | 0 | 34 | 0 | 0 | 35 | 770 | 0 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 0 |  | 5469 | 2919 | 8388 | 3486 | 801 | 1028 | 148 | 1763 | 930 | 76 | 0 | 60 | 96 | 0 | 0 | 90.74
KWH | 0 | 0 | 0 | 4347000 | 928900 | 1492909 | 0 | 8048640 | 6714000 |  | 0 | 5343900 | 0 | 1080960 | 0 | 893650 | 0 | 0 | 0 | 1142400 | 439056 | 782880 | 0 | 0 | 0 | 0 | 528120 | 727422 | 658851 | 478584 | 549000 | 615060 | 802000 | 742700 | 692640 | 0 | 1537820 | 0 | 0 | 0 | 285856 | 3607593 | 0 | 0 | 0 |  | 302400 | 626304 | 524526 | 258960 | 0 | 441120 | 0 | 236640 | 0 | 0 | 0 | 0 | 5543000 | 0 | 0 | 1746170 | 1043136 | 670560 | 0 | 214484 | 0 | 292960 | 225840 | 418644 | 227880 | 627800 | 346660 | 2340480 | 1612800 | 0 | 193500 | 12400 | 716000 | 992520 | 1219200 | 967320 | 0 | 0 | 1441536 | 651840 | 0 | 2155340 | 440000 | 611480 | 244440 | 0 | 524376 | 72215 | 274752 | 3404836 | 985190 | 506630 | 1113600 | 471122 | 2790144 | 133380 | 290880 | 1494720 | 1803200 | 9532000 | 1225200 | 2035104 | 1099818 | 25199 | 2847818 | 829212 | 1487884 | 397860 | 1948800 | 281280 | 9436000 | 382080 | 290500 | 1710720 | 1945800 | 0 | 444240 | 178523 | 1405440 | 446400 | 10302900 | 0 | 0 |  | 19445818 | 0 | 4078944 | 0 | 1079040 | 0 | 0 | 0 | 0 | 262656 | 178500 | 3079000 | 349300 | 0 | 0 | 0 | 0 | 80176 | 0 | 254800 | 0 | 468976 | 121136 | 541440 | 143506 | 429360 | 0 | 192042 | 0 | 0 | 3912700 | 0 | 0 | 4270955 | 0 | 0 | 0 | 0 | 9600 | 0 | 0 | 5302545 | 1002720 | 77364 | 1467168 | 0 | 785040 | 0 | 37515 | 1198656 | 20688700 | 0 | 0 | 0 | 31200 | 468000 | 351168 | 0 | 0 | 0 | 180492 | 2027600 |  | 131903704 | 72516117 | 204419821 | 79112895 | 19445818 | 24447978 | 2324658 | 44135019 | 26629000 | 1537820 | 0 | 3088944 | 2340480 | 1357209 | 0
Fuel Cost | 0 | 0 | 0 | 6477030 | 1040368 | 1985568.97 | 0 | 8451072 | 7251120 |  | 0 | 5824851 | 0 | 12085132.8 | 0 | 11840862.5 | 0 | 0 | 0 | 16701888 | 6177517.92 | 12690484.8 | 0 | 0 | 0 | 0 | 6717686.4 | 9820197 | 8835191.91 | 358938 | 411750 | 0 | 0 | 0 | 11781806.4 | 0 | 415211.4 | 0 | 0 | 0 | 4673745.6 | 3751896.72 | 0 | 0 | 0 |  | 3946320 | 10446750.72 | 8927432.52 | 3498549.6 | 0 | 5103758.4 | 0 | 788011.2 | 0 | 0 | 0 | 0 | 6041870 | 0 | 0 | 2130327.4 | 1178743.68 | 999134.4 | 0 | 358188.28 | 0 | 5059419.2 | 3037548 | 573542.28 | 170910 | 1098650 | 259995 | 16804646.4 | 1757952 | 0 | 263160 | 197656 | 980920 | 1310126.4 | 2121408 | 1673463.6 | 0 | 0 | 2796579.84 | 1486195.2 | 0 | 2176893.4 | 946000 | 911105.2 | 483991.2 | 0 | 393282 | 54883.4 | 5758801.92 | 46476011.4 | 20649582.4 | 10472042.1 | 15011328 | 9738091.74 | 38643494.4 | 1559212.2 | 3001881.6 | 20417875.2 | 23928464 | 8769440 | 14898432 | 29427603.84 | 13912697.7 | 0 | 33433383.32 | 9030118.68 | 15816206.92 | 5398960.2 | 25120032 | 3313478.4 | 8681120 | 4947936 | 4197725 | 21709036.8 | 22143204 | 0 | 5801774.4 | 2133349.85 | 21039436.8 | 5879088 | 0 | 0 | 0 |  | 58337454 | 0 | 4568417.28 | 0 | 11232806.4 | 0 | 0 | 0 | 0 | 4727808 | 2565045 | 3448480 | 677642 | 0 | 0 | 0 | 0 | 1344551.52 | 0 | 3985072 | 0 | 7766242.56 | 2048409.76 | 7379827.2 | 2420946.22 | 888775.2 | 0 | 145375.794 | 0 | 0 | 20698183 | 0 | 0 | 4954307.8 | 0 | 0 | 0 | 0 | 201408 | 0 | 0 | 5249519.55 | 13476556.8 | 1622323.08 | 17356597.44 | 0 | 9970008 | 0 | 414540.75 | 14551683.84 | 186405187 | 0 | 0 | 0 | 352872 | 5489640 | 5383405.44 | 0 | 0 | 0 | 0 | 0 |  | 676579541.61 | 397663085.634 | 1074242627.244 | 73192030.994 | 58337454 | 30698973.8 | 48442249.24 | 573252820.87 | 207103370 | 415211.4 | 0 | 51650874.74 | 16804646.4 | 14344995.8 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 0 | 66 | 0 | 328 | 275 |  | 0 | 225 | 0 | 68 | 0 | 30 | 0 | 0 | 0 | 71 | 16 | 48 | 0 | 0 | 0 | 0 | 17 | 55 | 17 | 19 | 22 | 26 | 25 | 30 | 33 | 0 | 76 | 0 | 0 | 0 | 17 | 151 | 0 | 0 | 0 |  | 12 | 48 | 17 | 10 | 0 | 13 | 0 | 2 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 79 | 44 | 25 | 0 | 5 | 0 | 24 | 8 | 22 | 10 | 16 | 15 | 112 | 34 | 0 | 8 | 2 | 30 | 43 | 50 | 37 | 0 | 0 | 57 | 0 | 0 | 90 | 18 | 26 | 10 | 0 | 16 | 3 | 70 | 97 | 191 | 97 | 58 | 94 | 135 | 20 | 12 | 51 | 75 | 415 | 58 | 105 | 68 | 4 | 250 | 54 | 53 | 17 | 98 | 12 | 400 | 17 | 39 | 62 | 89 | 0 | 17 | 28 | 97 | 17 | 432 | 0 | 0 |  | 895 | 0 | 155 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 16 | 0 | 15 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 201 | 17 | 0 | 36 | 0 | 34 | 0 | 6 | 37 | 660 | 0 | 0 | 0 | 5 | 75 | 0 | 0 | 0 | 0 | 31 | 251 |  | 9081 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 0 | 71 | 0 | 313 | 267 | 0 | 0 | 225 | 0 | 83 | 0 | 45 | 0 | 0 | 0 | 80 | 40 | 48 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 22 | 25 | 26 | 33 | 28 | 49 | 0 | 76 | 0 | 0 | 0 | 17 | 151 | 0 | 0 | 0 | 0 | 12 | 38 | 51 | 10 | 0 | 26 | 0 | 3 | 0 | 0 | 0 | 0 | 210 | 0 | 0 | 70 | 41 | 25 | 0 | 5 | 0 | 31 | 16 | 22 | 10 | 22 | 15 | 114 | 34 | 0 | 8 | 0 | 30 | 43 | 50 | 37 | 0 | 0 | 68 | 84 | 0 | 90 | 18 | 27 | 10 | 0 | 24 | 3 | 50 | 289 | 224 | 95 | 58 | 96 | 143 | 0 | 12 | 92 | 120 | 420 | 59 | 105 | 68 | 0 | 286 | 36 | 57 | 17 | 89 | 12 | 400 | 17 | 0 | 162 | 89 | 0 | 17 | 0 | 109 | 17 | 430 | 0 | 0 |  | 893 | 0 | 155 | 0 | 97 | 0 | 0 | 0 | 0 | 60 | 32 | 130 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 0 | 34 | 31 | 43 | 33 | 16 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202 | 60 | 1 | 94 | 0 | 84 | 0 | 0 | 95 | 890 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 10107 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 200 | 22 | 0 | 310 | 0 | 0 | 0 | 225 | 0 | 92 | 0 | 45 | 0 | 0 | 100 | 90 | 50 | 133 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 22 | 26 | 33 | 33 | 50 | 0 | 46 | 0 | 0 | 0 | 17 | 150 | 0 | 0 | 0 | 0 | 12 | 33 | 51 | 10 | 0 | 43 | 0 | 25 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 78 | 44 | 25 | 0 | 5 | 0 | 30 | 8 | 22 | 10 | 33 | 15 | 166 | 105 | 0 | 8 | 0 | 30 | 43 | 50 | 37 | 0 | 0 | 66 | 84 | 0 | 90 | 19 | 25 | 10 | 0 | 24 | 3 | 100 | 275 | 150 | 50 | 58 | 50 | 149 | 0 | 12 | 200 | 115 | 400 | 59 | 105 | 105 | 0 | 300 | 36 | 91 | 17 | 104 | 12 | 400 | 17 | 0 | 162 | 89 | 0 | 34 |  | 115 | 17 | 400 |  |  |  | 720 | 0 | 165 | 0 | 115 | 0 | 0 | 0 | 50 | 75 | 32 | 130 | 20 | 0 | 0 | 0 | 0 | 34 | 20 | 80 | 0 | 34 | 40 | 43 | 34 | 19 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 160 |  | 0 | 0 | 0 | 50 | 0 | 0 | 200 | 94 | 0 | 113 | 0 | 113 | 0 | 0 | 95 | 850 | 0 |  | 0 |  |  | 115 | 0 |  |  |  | 0
Forecast for Day | 0 | 0 | 0 | 180 | 200 | 22 | 0 | 320 | 0 | 0 | 0 | 150 | 0 | 50 | 0 | 30 | 0 | 0 | 210 | 80 | 16 | 48 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 22 | 22 | 26 | 33 | 33 | 50 | 0 | 46 | 0 | 0 | 0 | 17 | 150 | 0 | 0 | 0 | 0 | 12 | 22 | 17 | 10 | 0 | 19 | 0 | 15 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 78 | 44 | 25 | 0 | 5 | 0 | 0 | 8 | 22 | 10 | 33 | 15 | 143 | 75 | 0 | 8 | 1.6 | 30 | 43 | 50 | 37 | 0 | 0 | 66 | 0 | 0 | 90 | 19 | 25 | 10 | 0 | 22 | 3 | 100 | 97 | 100 | 50 | 58 | 50 | 135 | 20 | 12 | 51 | 85 | 400 | 49 | 105 | 68 | 5 | 300 | 36 | 53 | 17 | 104 | 12 | 400 | 17 | 50 | 17 | 89 | 0 | 17 | 30 | 115 | 17 | 400 |  |  |  | 480 | 0 | 160 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 35 | 0 | 19 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 54 | 0 | 70 | 0 | 34 | 0 | 8 | 35 | 850 | 0 |  | 0 | 6 | 100 | 50 | 0 |  |  | 30 | 0
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 200 | 22 | 0 | 392 | 0 | 0 | 0 | 225 | 0 | 19 | 0 | 0 | 0 | 0 | 72 | 24 | 8 | 48 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 22 | 23 | 18 | 28 | 32 | 24 | 0 | 76 | 0 | 0 | 0 | 10 | 151 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 10 | 0 | 15 | 0 | 37 | 0 | 0 | 0 | 0 | 210 | 0 | 0 | 78 | 44 | 25 | 0 | 5 | 0 | 0 | 8 | 19 | 11 | 33 | 0 | 76 | 75 | 0 | 8 | 1 | 30 | 43 | 50 | 37 | 0 | 0 | 70 | 0 | 0 | 90 | 19 | 26 | 10 | 0 | 22 | 3 | 0 | 95 | 0 | 0 | 46 | 0 | 143 | 10 | 12 | 17 | 48 | 417 | 47 | 70 | 17 | 0 | 69 | 36 | 53 | 17 | 74 | 12 | 245 | 17 | 18 | 17 | 107 | 0 | 17 | 12 | 36 | 13 | 432 | 0 | 0 | 0 | 473 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 43 | 0 | 20 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 244 | 0 | 0 | 70 | 0 | 34 | 0 | 1 | 37 | 430 | 0 | 0 | 0 | 1 | 27 | 69 | 0 | 0 | 284 | 10 | 0 | 0 |  |  |  |  | 49548621 |  | 0
49548621
| Minimum Generation |  | 6604 | 5:00
| Highest Generation |  | 10107 | 18:00
| Day Peak Generation |  | 9081 | 12:00
| Evening Peak Generation |  | 10107 | 18:00
| HVDC Max Flow |  | 895 | 11:00
| HVDC EvPeak Flow |  | 893 | 18:00
| Load factor L.F |  | 84.27% | [161 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2022-11-25
Till now the maximum generation is : - |  |  |  | 14782 | 21:00 | Hrs on | 2022-04-16
The Summary of Yesterday's |  |  | 2022-11-24 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 9081 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 6674
Evening Peak Generation : |  |  | 10107 | MW Hour : | 18:00 | Available Max Generation : |  | 10688
E.P. Demand (at gen end) : |  |  | 10107 | MW Hour : | 18:00 | Max Demand (Evening) : |  | 10200
Maximum Generation : |  |  | 10107 | MW Hour : | 18:00 | Reserve(Generation end) |  | 488
Total Gen. (MKWH) : |  |  | 204.4198 | System Load Factor : | 84.27% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 684 | MW at | 7:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2022-11-25
Actual : |  | 90.68 | Ft.(MSL) , | Rule curve : | 106.7 | Ft.( MSL )
Gas Consumed : |  | Total = | 817.46 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 103891004.794
: |  |  | Coal : | 207103370 | Oil : | 673345944.85 | Total : | 984340319.644
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 0 | 0:00 | 4098.4931 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 1161.0318 |  |  | 0 | 0%
Khulna Area |  | 0 | 0:00 | 1532.4656 |  |  | 0 | 0%
Rajshahi Area |  | 0 | 0:00 | 1359.6786 |  |  | 0 | 0%
Cumilla Area |  | 0 | 0:00 | 1157.4564 |  |  | 0 | 0%
Mymensingh Area |  | 0 | 0:00 | 956.2319 |  |  | 0 | 0%
Sylhet Area |  | 0 | 0:00 | 427.3941 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 348.401 |  |  | 0 | 0%
Rangpur Area |  | 0 | 0:00 | 755.0075 |  |  | 0 | 0%
Total |  | 0 |  | 11796.16 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
[5 empty] | 1) Barapukuria ST: Unit-1, 2 |  | 10) Ashuganj-225 MW
[5 empty] | 2) Ghorasal-3, 4, 7 |  | 11) Bibiana-II 341 MW CCPP (Summit)
3) Ashuganj-5
4) Baghabari-71,100 MW
5) Raozan unit-1 & 2
6) Siddhirganj 210 MW .
7) Shajibazar 330 MW
8) Sirajganj-2
9) Ashuganj(N)-360 MW
Outage Time | Restore Time
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
08:15 | 13:26 | Bogura 230/132kV S/S T-03 LT Forced S/D Due to Emergence.
08:15 | 13:25 | Bogura 230/132kV S/S T-03 HT Forced S/D Due to Emergence.
08:17 | 18:35 | Bibiyana-Kaliakoir 400 kV Ckt-1 Scheduled S/D from Bibiana Due to A/M.
08:17 | 17:25 | Rajshahi 230/132/33kV S/S ATR-01 (704T) LT Scheduled S/D Due to A/M.
08:18 | 17:23 | Rajshahi 230/132/33kV S/S ATR-01 (704T) HT Scheduled S/D Due to A/M.
08:30 | 12:19 | Shahjibazar 132/33kV S/S TR-04 HT Scheduled S/D Due to A/M.
08:30 | 12:44 | Shahjibazar 132/33kV S/S TR-04 LT Scheduled S/D Due to A/M.
08:32 | 14:50 | Tangail 132/33kV S/S Tr-4 HT Scheduled S/D Due to A/M. |  |  |  |  | 7 MW load interruption.
08:32 | 15:52 | Tangail 132/33kV S/S Tr-4 LT Scheduled S/D S/D Due to A/M.
08:39 | 14:48 | Chhatak 132/33kV S/S T-3 HT Scheduled S/D Due to Relay testing, Load transfer from T-1 and T-2 Transformer.
08:50 | 17:04 | Kabirpur - Manikganj 132kV Ckt-1 Scheduled S/D from Manikganj 132/33kV end due to A/M.
08:50 | 17:04 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-4 (50/75 MVA) HT Scheduled S/D Due to A/M.
08:50 | 17:07 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-4 (50/75 MVA) LT Scheduled S/D Due to A/M.
08:51 | 16:52 | Rangpur 132/33kV S/S 132KV Bus A Scheduled S/D Due to A/M.
08:55 | 16:34 | Kabirpur -Tongi 132kV Ckt-1 Scheduled S/D from Kabirpur 132/33kV end Due to A/M.
08:57 | 15:54 | Baroirhat-Hathazari 132 kV Ckt-2 Scheduled S/D from Baroirhat 132/33kV end Due to A/M and from Hathazari
230/132/33kV end Due to Breaker and Bay maintenance.
08:59 | 14:09 | Haripur-Siddirganj 230kV Ckt-2 Scheduled S/D from Haripur 230/132kV end Due to Work on other end.
09:00 | 16:24 | Dohazari-Sikalbaha 132 kV Ckt-1 Scheduled S/D from Dohazari 132/33kV end Due to A/M
and from Shikalbaha 230/132kV end Due to A/M of line.
09:10 | 15:44 | Barapukuria-Rangpur 132 kV Ckt-2 Scheduled S/D from Rangpur 132/33kV end Due to A/M
and from Barapukuria 230/132/33kV end Due to A/M work.
09:11 | 14:35 | Kodda-Rajendrapur 132kV Ckt-1 Scheduled S/D from Rajendrapur 132/33kV end Due to Kodda Substation Scheduled
working and from Kodda 132/33kV end Due to A/M.
09:29 | 10:37 | Aminbazar-Mirpur 132kV Ckt-1 Scheduled S/D from Mirpur 132/33kV end Due to S/D has been taken by Aminbazar
SS and from Aminbazar 230/132kV end Due to A/M Relay Test.
09:39 | 17:02 | Kabirpur - Manikganj 132kV Ckt-1 Scheduled S/D from Kabirpur 132/33kV end Due to Annual maintenance.
09:40 | 16:32 | Kabirpur -Tongi 132kV Ckt-1 Scheduled S/D from Tongi 230/132/33kV end.
09:46 | 16:31 | Narail 132/33kV S/S TR2 (413-T) HT Scheduled S/D Due to A/M.
9:46 | 16:32 | Narail 132/33kV S/S TR2 (413-T) LT Scheduled S/D Due to A/M.
10:43 | 12:09 | Aminbazar-Mirpur 132kV Ckt-2 Scheduled S/D from Aminbazar 230/132kV end Due to A/M Relay Test by SPMD.
10:48 | 11:10 | Tongi 230/132/33kV S/S Tongi-Tongi 80 MW PS Tripped showing Master trip,Backup protection,LBB protection relays.
10:55 | 13:42 | Aminbazar 230/132kV S/S 230 kv Bus 02 Scheduled S/D Due to A/M.
11:33 | 17:16 | New Tongi S/S T1(403T) LT Tripped showing relay relays Due to Showing over voltage trip but actual voltage 127kv
Signal reset then again show over voltage trip.
11:33 | 17:16 | New Tongi S/S T1(403T) HT Tripped showing relay relays Due to 132KV X_former triping due to Over Voltage but actual 127 Kv.
11:34 | 13:01 | Bogura-Sirajganj 230 kV Ckt-1 Tripped from Bogura 230/132kV end showing AR BLOCKED, permit close, earth fault,
DEF.TRIP. relays Due to no reason
12:27 | 16:41 | Tongi 230/132/33kV S/S Tongi-Tongi 80 MW PS Tripped showing Master trip,Backup protection, LBB protection relays.
12:36 |  | Barishal Electric tripped |  |  |  |  | 250 MW Generation interruption.
14:37 | 15:17 | Rajshahi-Rajshahi(New) 132kV Ckt-1 Forced S/D from Rajshahi 132/33kV end Due to Barker Replacement work
and from Rajshahi 230/132/33kV end Due to S/D taken from Rajshahi 132kV SS.
| 15:35 | Bogura(New)-Naogaon 132 kV Ckt-1 is restored.
| 15:46 | Jamalpur-Mymensingh 132kV Ckt-2 is restored.
| 15:48 | Jamalpur-Mymensingh 132kV Ckt-2 is restored.
| 16:33 | Tongi-Kabirpur 132kV Ckt-01 is restored.
| 16:47 | Patuakhali 132/33kV S/S 425T (T-3) HT is restored.
| 16:48 | Patuakhali 132/33kV S/S 425T (T-3) LT is restored.
18:01 |  | Barishal Electric Synch
18:24 |  | Ghorashal Unit-7 GT Synch
18:41 |  | Barishal Electric Tripped
| 19:21 | Bhulta-Ghorasal 230 kV Ckt-1 is restored.
01:26 |  | Payra Unit-1 tripped.
02:30 |  | Rampal Unit-1 sync.
06:00 |  | Bibiyana South ST tripped
06:48 |  | Madangonj -Madangonj 55MW 132KV line tripped showing 67/67N
07:12 |  | Haripur AES 360MW ST SD due
07:15 |  | Chandpur 132/33kV S/S 402T LT S/D Due to 33 KV bus section -1 shutdown Maintenance and changing loop. |  |  |  |  | 7 MW load interruption.
07:20 |  | Chandpur 132/33kV S/S 402T HT S/D Due to 33 KV bus section -1 shutdown Maintenance and changing loop.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2022-11-24 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Line O/L
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4347000
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 928900 | Under maint.
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 71 | 1492909 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 313 | 8048640 | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 267 | 6714000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 5343900 | GT-2 S/D due to Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 83 | 1080960 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 0 | 0 | Under maint.
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 45 | 893650 | Engine problem
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 478584
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 80 | 1142400 | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 40 | 439056 | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 528120
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 48 | 782880 | Fuel shortage
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 35 | 727422 | Engine problem
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 658851 | Engine problem
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 51 | 1164060 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 802000
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 28 | 742700 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 49 | 692640 | 0:00
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 289 | 3404836 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 224 | 985190 | Fuel shortage
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 95 | 506630
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 96 | 471122
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 143 | 2790144 | Engine problem
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 2035104
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 17 | 382080 | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 1710720
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 178523
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 446400 | Fuel shortage
| Dhaka area Total |  |  |  | 5847 | 2807 | 49919421
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Machine problem
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 17 | 285856 | Engine problem
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 133380
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 26 | 441120 | Engine problem
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 76 | 1537820 | Low water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 151 | 3607593 | ST Under maint
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 68 | 1099818 | Engine problem
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 38 | 626304 | Fuel shortage
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 524526 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 10 | 258960 | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 12 | 290880 | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 0 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 3 | 236640
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 25199
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 286 | 2847818 | Engine problem
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 36 | 829212 | Engine problem
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 57 | 1487884 | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 281280
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 89 | 1945800 | Engine problem
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Chattogram area Total |  |  |  | 2382 | 932 | 16460090
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 0 | 0 | Gas shortage
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 0 | 0 | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 210 | 5543000 | Gas shortage
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+136*1 | 284 | 430 | 10302900 | On test.
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 41 | 1043136
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 25 | 670560 | Gas shortage
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 0 | 0 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 5 | 214484 | Gas shortage
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 120 | 1803200 | Fuel shortage
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 31 | 292960 | Engine problem
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 70 | 1746170 | Machine problem
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 92 | 1494720 | High voltage
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 418644
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 10 | 227880
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 114 | 2340480
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 22 | 627800 | Engine problem
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 16 | 225840 | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 15 | 346660 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 50 | 274752 | Fuel conservation
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 17 | 397860 | Fuel shortage
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 89 | 1948800 | Engine problem
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 444240 | Engine problem
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 109 | 1405440 | Engine problem
| Cumilla Area Total |  |  |  | 3169 | 1505 | 31769526
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 34 | 1612800 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 8 | 193500 | Gas shortage
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 12400
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 58 | 1113600 | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 59 | 1225200 | Fuel shortage
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 290500
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 302400 | Engine problem
| Mymensingh Area Total |  |  |  | 614 | 171 | 4750400
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 30 | 716000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 43 | 992520 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Gas shortage
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 50 | 1219200
| Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 37 | 967320 | Gas shortage
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 3 | 72215 | Gas shortage
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 68 | 1441536
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 84 | 651840
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 90 | 2155340 | Gas shortage
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 440000
| Sylhet 50MW PP (EPL) |  | NENP | 27*2 | 50 | 27 | 611480 | Gas shortage
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 524376 | Gas shortage
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 0 | 0 | Under maint.
104 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 420 | 9532000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 244440
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 400 | 9436000
| Sylhet Area Total |  |  |  | 2477 | 1304 | 29004267
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Fuel shortage
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 893 | 19445818
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 97 | 1079040 | Engine problem
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Line O/L
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 60 | 262656 | High voltage
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 155 | 4078944 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 32 | 178500 | Fuel shortage
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 9600 | Fuel conservation
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 60 | 1002720 | Engine problem
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Fuel shortage
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 468000
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 0 | 0 | 0 | On test.
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 0 | 0 | 0 | 0 | On test.
| Khulna Area Total |  |  |  | 2384 | 1297 | 26525278
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Line O/L
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 17 | 349300 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 130 | 3079000 | Gas shortage
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 890 | 20688700 | Line O/L
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 0 | 0 | Under maint.
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Line O/L
| Barisal 307 MW |  | BCPCL | 0 | 0 | 0 | 2027600 | On test.
| Barisal Area Total |  |  |  | 1958 | 1037 | 26144600
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 80176
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contract Expired
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 34 | 468976 | Engine problem
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 31 | 121136 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 165 | 4270955 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 202 | 5302545 | Gas shortage
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 33 | 143506 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 16 | 429360 | Engine problem
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 192042 | Engine problem
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 43 | 541440 | Engine problem
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 88 | 254800 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 1 | 77364 | Fuel conservation
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 94 | 1467168 | Engine problem
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 95 | 1198656 | Engine problem
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 31200
| Rajshahi Area Total |  |  |  | 2129 | 810 | 14579324
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 160 | 3912700 | Machine problem
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 84 | 785040 | Engine problem
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 37515
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 0 | 351168 | Protection work.
| Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 180492
| Rangpur Area Total |  |  |  | 750 | 244 | 5266915
| Total |  |  |  | 21710 | 10107 | 204419821
| Eastern Grid Total |  |  |  | 14489 | 6719 | 131903704
| Western Grid Total |  |  |  | 7221 | 3388 | 72516117
| National Grid Total |  |  |  | 21710 | 10107 | 204419821
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2022-11-24
| (a) ENTIRE EASTERN GRID : |  | 6954.02 | MW | (b) ENTIRE WESTERN GRID : |  | 2784.24 | MW
| i) Dhaka area |  | 3952.82 | MW | i) Khulna area |  | 1048.5 | MW
| ii) Chittagong area |  | 1133.2 | MW | ii) Rajshahi area |  | 855.7 | MW
| iii) Comilla area |  | 792 | MW | iii) Barisal area |  | 227.04 | MW
| iv) Mymensingh area |  | 703 | MW | iv) Rangpur area |  | 653 | MW
| v) Sylhet area |  | 373 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 9738.26 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 23 | 10:00 | Chowmuhani | 128 | 21:00 | Kaptai | 3.5 | 18:00 | Nawabganj | 32.8 | 21:00 | Sholosohor | 25 | 17:00
2 | AKSML | 80 | 07:00 | Chuadanga | 68 | 18:00 | Kazla | 81 | 18:00 | Netrakona | 83 | 18:00 | Shyampur | 168 | 13:00
3 | Aftabnagar | 25.64 | 18:00 | Coxsbazar | 94 | 11:00 | Keranigonj | 66 | 11:00 | New | 61 | 12:00 | Siddhirganj | 70 | 18:00
4 | Agargaon | 57 | 13:00 | Cumilla(N) | 88 | 19:30 | Khagrachori | 22 | 18:00 | Niamatpur | 46 | 18:00 | Sirajganj | 70 | 18:30
5 | Agrabad | 52 | 12:00 | Cumilla(S) | 114 | 18:00 | Khulna | 71 | 18:00 | Noapara | 34.5 | 18:00 | Sonargaon | 82 | 10:00
6 | Amnura | 33 | 18:00 | Daudkandi | 93 | 19:00 | Khulshi | 159 | 12:00 | PHP | 8 | 08:00 | Sreemongol | 40 | 18:00
7 | Ashuganj | 63 | 00:00 | Dhaka | 30 | 13:00 | Kishoreganj | 94 | 19:00 | Pabna | 80 | 18:00 | Srinagar | 27.96 | 20:00
8 | BSRM | 138 | 19:30 | Dhamrai | 96 | 18:00 | Kodda | 254 | 18:00 | Palashbari | 88 | 18:00 | Sunamganj | 32 | 18:00
9 | Bagerhat | 73 | 18:30 | Dhanmondi | 94 | 13:00 | Kulaura | 28 | 18:00 | Panchagarh | 51 | 18:00 | Sylhet | 103 | 18:00
10 | Bakulia | 95 | 18:30 | Dohazari | 70 | 18:00 | Kurigram | 46 | 18:00 | Patuakhali | 70 | 21:00 | TK | 11.2 | 18:00
11 | Banani | 30 | 12:00 | Faridpur | 98 | 18:00 | Kushtia | 92 | 18:30 | Payra | 0.71 | 18:30 | Tangail | 143 | 18:00
12 | Bangabhaban | 11 | 10:00 | Fatullah | 58 | 10:00 | Lalbag | 71 | 18:00 | Postogola | 35 | 13:00 | Thakurgaon | 60 | 18:00
13 | Barapukuria | 42 | 18:30 | Fenchuganj | 32 | 18:00 | Lalmonirhat | 36 | 18:00 | Purbachal | 12 | 12:00 | Tongi | 107 | 11:00
14 | Barguna | 12 | 19:30 | Feni | 83 | 18:30 | Madanganj | 82 | 14:00 | Purbasadipur | 89 | 18:30 | Ullon | 22 | 18:00
15 | Barishal | 68 | 18:00 | GPH | 91 | 01:00 | Madaripur | 59 | 19:30 | Rahanpur_I | 24.2 | 19:30 | Uttara | 58 | 13:00
16 | Barishal-230 | 58 | 23:00 | Ghorashal | 56 | 19:00 | Madartek | 58 | 18:00 | Rahim | 36 | 09:00 | UttaraNew | 15 | 19:00
17 | Baroaulia | 66 | 11:00 | Goalpara | 16 | 13:00 | Madunaghat | 41 | 18:00 | Rajbari | 44 | 18:00 | Zigatola | 36 | 18:00
18 | Baroirhat | 35 | 18:00 | Gollamari | 38 | 13:00 | Magura | 42 | 18:00 | Rajendrapur | 100 | 20:00
19 | Bashundhara | 119 | 18:00 | Gopalganj | 66 | 18:30 | Mahasthangarh | 42 | 18:00 | Rajshahi | 96 | 13:00
20 | BashundharaCement | 8 | 08:00 | Gulshan | 76 | 13:00 | Manikganj | 61 | 18:30 | Rajshahi-230 | 29 | 18:00
21 | Beanibazar | 37 | 18:00 | Halishahar | 95 | 12:00 | Maniknagar | 56 | 13:00 | Ramganj | 64 | 20:00
22 | Benapole | 48 | 18:00 | HaripurSBU | 155 | 17:00 | Matarbari | 121 | 14:00 | Rampur | 21 | 18:30
23 | Bhaluka | 110 | 12:00 | Hasnabad | 55 | 12:00 | Matuail | 53.2 | 17:00 | Rangamati | 10 | 18:00
24 | Bhandaria | 32 | 21:00 | Hathazari | 47 | 18:00 | Millgate | 60 | 12:00 | Rangpur | 106 | 18:30
25 | Bhangura | 20 | 18:00 | Ishurdi | 49 | 18:30 | Mirpur | 93 | 18:00 | Ruppur | 4.2 | 15:00
26 | Bheramara(GK) | 38 | 18:00 | Jaldhaka | 47 | 18:00 | Mirsorai | 1 | 10:00 | SSM | 10 | 11:00
27 | Bhulta | 211 | 12:00 | Jamalpur | 94 | 20:00 | Mithapukur | 25 | 08:00 | Saidpur | 78 | 18:30
28 | Bog-Sherpur | 48 | 18:00 | Jashore | 76 | 18:00 | Modern | 0 | 00:00 | Satkhira | 70 | 18:30
29 | Bogura | 117 | 18:30 | Jhenaidah | 84 | 18:30 | Mogbazar | 101 | 15:00 | Satmasjid | 67 | 14:00
30 | Borhanuddin | 22 | 20:00 | Joydebpur | 143 | 19:30 | Mongla | 32 | 08:00 | Savar | 138 | 15:00
31 | Brahmanbaria | 104 | 21:00 | Joypurhat | 37 | 18:30 | Motijheel | 25 | 12:00 | Shahjadpur | 77 | 19:30
32 | Cantonment | 102 | 18:00 | Juldah | 24 | 00:00 | Munshiganj | 64 | 20:00 | Shahjibazar | 83 | 18:00
33 | Chandpur | 42 | 19:30 | KSRM | 40 | 06:00 | Mymensingh | 140 | 19:00 | Shahmirpur | 35 | 17:00
34 | Chandraghona | 22 | 18:00 | Kabirpur | 247 | 12:00 | Naogaon | 83 | 19:00 | Shariatpur | 46 | 20:00
35 | Chapai | 41 | 08:00 | Kachua | 44 | 18:00 | Narail | 36 | 18:00 | Sherpur | 84 | 20:00
36 | Charsaidpur | 45.5 | 05:00 | Kallyanpur | 66 | 18:00 | Narinda | 54 | 13:00 | Shikalbaha | 20 | 19:30
37 | Chauddagram | 28 | 18:00 | Kalurghat | 6 | 09:00 | Narshingdi | 137 | 20:00 | Shikalbaha-230 | N/A | N/A
38 | Chhatak | 18 | 18:00 | Kamrangirchar | 68 | 13:00 | Natore | 89 | 18:30 | Shitalakhya | 109 | 12:00
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2022-11-24 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Bhulta | 383 | 06:00 | 369 | 14:00 | Kaliakoir | 398 | 01:00 | 369 | 16:00
| Bibiana | 403 | 06:00 | 390 | 12:00 | Payra | 422 | 06:00 | 414 | 18:00
| BIPTC | 407 | 02:00 | 395 | 11:00 | Rahanpur_I | 423 | 19:00 | 380 | 06:00
| Gopalganj_I | 423 | 06:00 | 411 | 12:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 229 | 06:00 | 217 | 10:00 | Hasnabad | 228 | 21:00 | 216 | 09:00
| AKSML | 242 | 20:00 | 217 | 10:00 | Hathazari | 244 | 19:30 | 222 | 10:00
| Aminbazar | 230 | 04:00 | 220 | 10:00 | Ishurdi | 241 | 00:00 | 229 | 12:00
| Ashuganj | 240 | 00:00 | 230 | 07:00 | Jhenaidah | 241 | 00:00 | 226 | 12:00
| Baghabari | 238 | 00:00 | 228 | 11:00 | Kaliakoir | 230 | 00:00 | 216 | 16:00
| Barapukuria | 230 | 00:00 | 219 | 12:00 | Keranigonj | 228 | 06:00 | 217 | 10:00
| Barishal | 246 | 06:00 | 240 | 12:00 | Khulna(S) | 241 | 23:00 | 226 | 12:00
| Bheramara | 239 | 00:00 | 222 | 18:00 | Maniknagar | 229 | 06:00 | 219 | 10:00
| Bhulta | 230 | 00:00 | 220 | 10:00 | Meghnaghat | 233 | 04:00 | 224 | 09:00
| Bibiana | 239 | 19:30 | 230 | 11:00 | Mirsorai | 236 | 20:00 | 221 | 04:00
| BIPTC | 242 | 00:00 | 226 | 12:00 | Rajshahi | 243 | 00:00 | 230 | 12:00
| Bogura | 235 | 00:00 | 222 | 12:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 248 | 06:00 | 243 | 12:00 | Rampura | 227 | 00:00 | 219 | 10:00
| BSRM | 237 | 19:00 | 219 | 04:00 | Shikalbaha | 136 | 19:00 | 128 | 10:00
| Cumilla(N) | 233 | 20:00 | 223 | 10:00 | Shyampur | 241 | 19:30 | 221 | 05:00
| Fenchuganj | 241 | 01:00 | 234 | 10:00 | Siddhirganj | 228 | 06:00 | 217 | 10:00
| Ghorashal | N/A | N/A | N/A | N/A | Sirajgonj | 229 | 01:00 | 221 | 16:00
| GPH | 232 | 03:00 | 222 | 10:00 | Tongi | 234 | 00:00 | 227 | 12:00
| Haripur | 226 | 18:30 | 218 | 10:00 |  | 230 | 00:00 | 213 | 10:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 134 | 06:00 | 125 | 10:00 | Lalbag | 138 | 06:00 | 129 | 10:00
| Agargaon | 133 | 06:00 | 128 | 13:00 | Lalmonirhat | 133 | 01:00 | 126 | 07:00
| Agrabad | 138 | 19:00 | 129 | 10:00 | Madanganj | 135 | 19:00 | 128 | 10:00
| AKS | 138 | 18:30 | 128 | 10:00 | Madaripur | 141 | 06:00 | 136 | 11:00
| Aminbazar | 134 | 18:30 | 124 | 10:00 | Madartek | 132 | 06:00 | 125 | 10:00
| Amnura | 136 | 00:00 | 126 | 12:00 | Madunaghat | 140 | 19:00 | 130 | 05:00
| Ashuganj | 139 | 01:00 | 134 | 16:00 | Magura | 140 | 05:00 | 130 | 12:00
| Bagerhat | 138 | 17:00 | 129 | 12:00 | Mahasthangarh | 138 | 00:00 | 128 | 12:00
| Bakulia | 140 | 19:00 | 128 | 06:00 | Manikganj | 133 | 09:00 | 124 | 12:00
| Banani | 138 | 02:00 | 127 | 12:00 | Maniknagar | 135 | 05:00 | 128 | 10:00
| Bangabhaban | 136 | 22:00 | 129 | 10:00 | Matarbari | 134 | 20:00 | 121 | 01:00
| Barapukuria | 137 | 00:00 | 129 | 12:00 | Matuail | 134 | 19:00 | 128.5 | 10:00
| Barguna | 136 | 06:00 | 131 | 19:30 | Millgate | 139 | 06:00 | 127 | 16:00
| Barishal | 144 | 21:00 | 129 | 12:00 | Mirpur | 133 | 19:00 | 123 | 10:00
| Barishal-230 | 140 | 05:00 | 136 | 12:00 | Mithapukur | 137 | 23:00 | 128 | 12:00
| Baroaulia | 140 | 17:00 | 130 | 10:00 | Modern | 138 | 18:30 | 130 | 09:00
| Baroirhat | 140 | 19:00 | 132 | 04:00 | Mogbazar | 134 | 04:00 | 126 | 10:00
| Bashundhara | 138 | 00:00 | 128 | 12:00 | Mongla | 138 | 23:00 | 128 | 12:00
| BashundharaCement | 135 | 19:00 | 128 | 10:00 | Motijheel | 136 | 22:00 | 129 | 10:00
| Beanibazar | 135 | 01:00 | 131 | 10:00 | Munshiganj | 135 | 20:00 | 129 | 10:00
| Benapole | 138 | 23:00 | 127 | 12:00 | Mymensingh | 134 | 06:00 | 120 | 16:00
| Bhaluka | 133 | 05:00 | 120 | 17:00 | Naogaon | 138 | 06:00 | 124 | 14:00
| Bhandaria | 140 | 05:00 | 135 | 11:00 | Narail | 139 | 01:00 | 129 | 12:00
| Bhangura | 142 | 01:00 | 137 | 10:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bheramara | 138 | 00:00 | 134 | 10:00 | Narshingdi | 132 | 06:00 | 125 | 10:00
| Bheramara(GK) | 140 | 23:00 | 134 | 12:00 | Natore | 137 | 00:00 | 130 | 11:00
| Bhulta | 129 | 01:00 | 122 | 16:00 | Nawabganj | 137 | 01:00 | 130 | 10:00
| Bog-Sherpur | 139 | 00:00 | 130 | 12:00 | Netrakona | 136 | 06:00 | 125 | 17:00
| Bogura | 140 | 00:00 | 130 | 12:00 | New | 137 | 00:00 | 127 | 16:00
| Bogura-230 | 139 | 00:00 | 130 | 12:00 | Niamatpur | 136 | 00:00 | 125 | 12:00
| Brahmanbaria | 134 | 00:00 | 127 | 11:00 | Noapara | 139 | 23:00 | 129 | 12:00
| Cantonment | 132 | 06:00 | 124 | 10:00 | Pabna | 141 | 00:00 | 132 | 12:00
| Chandpur | 144 | 18:00 | 138 | 03:00 | Palashbari | 135 | 00:00 | 127 | 12:00
| Chandraghona | 142 | 20:00 | 130 | 04:00 | Panchagarh | 136 | 23:00 | 119 | 18:00
| Chapai | 137 | 00:00 | 127 | 12:00 | Patuakhali | 137 | 05:00 | 132 | 18:00
| Charsaidpur | 136 | 19:00 | 129 | 10:00 | Payra | 138 | 01:00 | 136 | 19:00
| Chauddagram | 139 | 18:30 | 134 | 03:00 | PHP | 140 | 20:00 | 132 | 04:00
| Chhatak | 134 | 04:00 | 131 | 12:00 | Postogola | 136 | 06:00 | 128 | 10:00
| Chowmuhani | 140 | 17:00 | 136 | 00:00 | Purbachal | 138 | 01:00 | 127 | 12:00
| Chuadanga | 138 | 05:00 | 128 | 12:00 | Purbasadipur | 133 | 00:00 | 123 | 12:00
| Coxsbazar | 135 | 19:30 | 122 | 06:00 | Rahim | 134 | 18:30 | 129 | 10:00
| Cumilla(N) | 140 | 20:00 | 134 | 10:00 | Rajbari | 138 | 06:00 | 131 | 12:00
| Cumilla(S) | 139 | 17:00 | 130 | 10:00 | Rajendrapur | 133 | 02:00 | 120 | 17:00
| Daudkandi | 136 | 18:00 | 131 | 10:00 | Rajshahi | 134 | 01:00 | 126 | 12:00
| Dhaka | 133 | 06:00 | 126 | 12:00 | Rajshahi-230 | 134 | 00:00 | 125 | 12:00
| Dhamrai | 139 | 06:00 | 129 | 16:00 | Ramganj | 142 | 19:00 | 134 | 05:00
| Dhanmondi | 134.5 | 20:00 | 128.5 | 16:00 | Rampur | 137 | 19:30 | 128 | 05:00
| Dohazari | 137 | 21:00 | 127 | 10:00 | Rampura | 132 | 01:00 | 125 | 10:00
| Faridpur | 137 | 06:00 | 131 | 12:00 | Rangamati | 140 | 19:00 | 130 | 04:00
| Fatullah | 136 | 18:00 | 128 | 10:00 | Rangpur | 134 | 23:00 | 124 | 18:00
| Fenchuganj | 140 | 06:00 | 134 | 15:00 | Ruppur | 140 | 00:00 | 134 | 09:00
| Feni | 141 | 19:30 | 136 | 10:00 | Saidpur | 135 | 01:00 | 123 | 18:00
| Ghorashal | 140 | 00:00 | 137 | 01:00 | Satkhira | 138 | 01:00 | 129 | 12:00
| Goalpara | 139 | 06:00 | 128 | 12:00 | Satmasjid | 133 | 06:00 | 125 | 10:00
| Gollamari | 139 | 23:00 | 130 | 12:00 | Savar | 135 | 19:00 | 123 | 10:00
| Gopalganj | 138 | 00:00 | 131 | 12:00 | Shahjadpur | 144 | 00:00 | 139 | 10:00
| Gopalganj_I | 139 | 00:00 | 134 | 12:00 | Shahjibazar | 137 | 23:00 | 130 | 15:00
| Gulshan | 132 | 03:00 | 125 | 10:00 | Shariatpur | 139 | 03:00 | 135 | 12:00
| Halishahar | 140 | 20:00 | 129 | 05:00 | Sherpur | 136 | 06:00 | 125 | 07:00
| Haripur | 134 | 18:30 | 129 | 10:00 | Shikalbaha | 141 | 20:00 | 131 | 02:00
| HaripurSBU | 134 | 18:30 | 129 | 16:00 | Shikalbaha-230 | 140 | 19:30 | 129 | 05:00
| Hasnabad | 136 | 19:00 | 129 | 16:00 | Shitalakhya | 136 | 00:00 | 126 | 10:00
| Hathazari | 143 | 19:30 | 132 | 10:00 | Sholosohor | 140 | 20:00 | 128 | 04:00
| Ishurdi | 140 | 00:00 | 133 | 12:00 | Shyampur | 133 | 08:00 | 127 | 10:00
| Jaldhaka | 134 | 21:00 | 121 | 18:00 | Shyampur-230 | 135 | 19:00 | 128 | 10:00
| Jamalpur | 136 | 01:00 | 126 | 07:00 | Siddhirganj | 134 | 19:00 | 129 | 10:00
| Jashore | 138 | 23:00 | 127 | 12:00 | Sirajganj | 140 | 00:00 | 131 | 12:00
| Jhenaidah | 140 | 00:00 | 135 | 16:00 | Sonargaon | 133 | 13:00 | 128 | 10:00
| Jhenaidah-230 | 140 | 00:00 | 131 | 12:00 | Sreemongol | 139 | 06:00 | 135 | 09:00
| Joydebpur | 140 | 00:00 | 135 | 12:00 | Srinagar | 137 | 18:00 | 129 | 10:00
| Joypurhat | 138 | 01:00 | 126 | 12:00 | SSM | 142 | 19:30 | 131 | 10:00
| Juldah | 138 | 18:30 | 130 | 03:00 | Sunamganj | 134 | 03:00 | 130 | 12:00
| Kabirpur | 137 | 00:00 | 122 | 16:00 | Sylhet | 136 | 00:00 | 133 | 12:00
| Kachua | 140 | 13:00 | 136 | 02:00 | Tangail | 132 | 00:00 | 124 | 15:00
| Kaliakoir | 140 | 02:00 | 123 | 16:00 | Thakurgaon | 137 | 23:00 | 120 | 12:00
| Kallyanpur | 134 | 19:00 | 124 | 10:00 | TK | 141 | 20:00 | 131 | 10:00
| Kalurghat | 142 | 20:00 | 130 | 04:00 | Tongi | 140 | 00:00 | 129 | 11:00
| Kamrangirchar | 137 | 01:00 | 130 | 10:00 | Ullon | 132 | 01:00 | 125 | 10:00
| Kaptai | 135 | 00:00 | 132 | 18:00 | Uttara | 138 | 02:00 | 126 | 12:00
| Kazla | 136 | 06:00 | 128 | 16:00 | UttaraNew | 133 | 23:00 | 123 | 15:00
| Keranigonj | 138 | 19:00 | 130 | 10:00 | Zigatola | 136 | 04:00 | 129 | 16:00
| Khagrachori | 138 | 21:00 | 129 | 04:00
| Khulna | 138 | 06:00 | 129 | 12:00
| Khulna(S) | 140 | 23:00 | 130 | 12:00
| Khulshi | 137 | 19:00 | 127 | 04:00
| Kishoreganj | 136 | 06:00 | 127 | 18:00
| Kodda | 142 | 07:00 | 122 | 16:00
| KSRM | 140 | 19:00 | 130 | 03:00
| Kulaura | 138 | 02:00 | 134 | 16:00
| Kurigram | 132 | 04:00 | 122 | 11:00
| Kushtia | 139 | 00:00 | 132 | 12:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2022-11-24
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 880 | 5469 | 2919 | 8388 |  |  |  | QF-LDC-11
0:30 | 900 | 5220 | 2760.5 | 7980.5 | Date: | 2022-11-24
1:00 | 920 | 4971 | 2602 | 7573
1:30 | 910 | 4837.5 | 2523 | 7360.5
2:00 | 900 | 4704 | 2444 | 7148
2:30 | 940 | 4570.5 | 2445.5 | 7016 | [5 empty] | Gen. at Eve. Peak | 10107 | 10107 MW (18:00 )
3:00 | 980 | 4437 | 2447 | 6884 | [6 empty] | 18:00
3:30 | 960 | 4368 | 2448.5 | 6816.5 | [5 empty] | Gen. at Day Peak | 9081 | 9081 MW (12:00 )
4:00 | 940 | 4299 | 2450 | 6749 | [6 empty] | 12:00
4:30 | 935 | 4268.5 | 2408 | 6676.5 | [5 empty] | Highest Generation | 10107
5:00 | 930 | 4238 | 2366 | 6604 | [6 empty] | 18:00
5:30 | 875 | 4353.5 | 2368.5 | 6722
6:00 | 820 | 4469 | 2371 | 6840
6:30 | 752 | 4588.5 | 2442 | 7030.5
7:00 | 684 | 4708 | 2513 | 7221
7:30 | 780 | 4903.5 | 2687 | 7590.5
8:00 | 876 | 5099 | 2861 | 7960
8:30 | 1043 | 5161 | 2949 | 8110
9:00 | 1210 | 5223 | 3037 | 8260
9:30 | 1355 | 5173 | 3005.5 | 8178.5
10:00 | 1500 | 5123 | 2974 | 8097
10:30 | 1325 | 5389 | 2938 | 8327
11:00 | 1150 | 5655 | 2902 | 8557
11:30 | 1090 | 5899 | 2920 | 8819
12:00 | 1030 | 6143 | 2938 | 9081
12:30 | 990 | 6176.5 | 2854.5 | 9031
13:00 | 950 | 6210 | 2771 | 8981
13:30 | 1115 | 5988 | 2845.5 | 8833.5
14:00 | 1280 | 5766 | 2920 | 8686
14:30 | 1330 | 5713.5 | 2942.5 | 8656
15:00 | 1380 | 5661 | 2965 | 8626
15:30 | 1390 | 5651.5 | 2944.5 | 8596
16:00 | 1400 | 5642 | 2924 | 8566
16:30 | 1245 | 5749 | 2971.5 | 8720.5
17:00 | 1090 | 5856 | 3019 | 8875
17:30 | 945 | 6287.5 | 3203.5 | 9491
18:00 | 800 | 6719 | 3388 | 10107
18:30 | 815 | 6624.5 | 3460 | 10084.5
19:00 | 830 | 6530 | 3532 | 10062
19:30 | 840 | 6476 | 3498 | 9974
20:00 | 800 | 6431 | 3455 | 9886 |  |  |  | Executive Engineer
20:30 | 905 | 6266.5 | 3476.5 | 9743 |  |  |  | Network Operation Division
21:00 | 1010 | 6102 | 3498 | 9600
21:30 | 955 | 5995.5 | 3351.5 | 9347
22:00 | 900 | 5889 | 3205 | 9094 |  |  |  |  | Page 6 of 7
22:30 | 940 | 5810 | 3133.5 | 8943.5
23:00 | 980 | 5731 | 3062 | 8793
23:30 | 930 | 5600 | 2990.5 | 8590.5
24:00 | 880 | 5469 | 2919 | 8388
10107 MW (18:00 )
9081 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2022-11-24 |  | Energy |  | 204419821
[13 empty] | 2022-11-24 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 3486 | 801 | 1028 | 148 | 1763 | 930 | 76 | 0 | 60 | 96 | 0 | 0
0:30 | 3362 | 729.5 | 1057 | 74 | 1559 | 969.5 | 61 | 0 | 73.5 | 95 | 0 | 0 | Date: | 2022-11-24
1:00 | 3238 | 658 | 1086 | 0 | 1355 | 1009 | 46 | 0 | 87 | 94 | 0 | 0
1:30 | 3237.5 | 658.5 | 1064 | 0 | 1212.5 | 1005.5 | 46 | 0 | 43.5 | 93 | 0 | 0 | [8 empty] | Total Energy | 204.4198 | Total Energy Gen 204.420 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 204.420 MKWHr
2:00 | 3237 | 659 | 1042 | 0 | 1070 | 1002 | 46 | 0 | 0 | 92 | 0 | 0 | [8 empty] | Energy not Served | 0
2:30 | 3228.5 | 659 | 1049 | 0 | 943 | 1000.5 | 46 | 0 | 0 | 90 | 0 | 0 | [8 empty] | Energy Requirement | 204.4198
3:00 | 3220 | 659 | 1056 | 0 | 816 | 999 | 46 | 0 | 0 | 88 | 0 | 0
3:30 | 3235.5 | 659.5 | 1064.5 | 0 | 728 | 999 | 46 | 0 | 0 | 84 | 0 | 0 | [6 empty] | Shortage
4:00 | 3251 | 660 | 1073 | 0 | 640 | 999 | 46 | 0 | 0 | 80 | 0 | 0
4:30 | 3266 | 659.5 | 1074.5 | 0 | 589.5 | 960 | 46 | 0 | 0 | 81 | 0 | 0
5:00 | 3281 | 659 | 1076 | 0 | 539 | 921 | 46 | 0 | 0 | 82 | 0 | 0
5:30 | 3342.5 | 659 | 1054.5 | 0 | 603 | 925.5 | 46 | 0 | 8.5 | 83 | 0 | 0
6:00 | 3404 | 659 | 1033 | 0 | 667 | 930 | 46 | 0 | 17 | 84 | 0 | 0
6:30 | 3382.5 | 659 | 1049 | 0 | 838 | 951 | 46 | 0 | 17 | 81 | 7 | 0 |  |  |  |  | Coal
7:00 | 3361 | 659 | 1065 | 0 | 1009 | 972 | 46 | 0 | 17 | 78 | 14 | 0
7:30 | 3377.5 | 659 | 1051.5 | 0 | 1235 | 1026 | 46 | 0 | 67 | 85 | 43.5 | 0 |  |  |  | Oil |  |  |  | ,
8:00 | 3394 | 659 | 1038 | 0 | 1461 | 1080 | 46 | 0 | 117 | 92 | 73 | 0
8:30 | 3367.5 | 706 | 1024 | 0 | 1545.5 | 1086 | 46 | 0 | 139 | 93 | 103 | 0
9:00 | 3341 | 753 | 1010 | 0 | 1630 | 1092 | 46 | 0 | 161 | 94 | 133 | 0
9:30 | 3283 | 777 | 991 | 0 | 1625 | 1066.5 | 46 | 0 | 135.5 | 96 | 158.5 | 0
10:00 | 3225 | 801 | 972 | 0 | 1620 | 1041 | 46 | 0 | 110 | 98 | 184 | 0
10:30 | 3197.5 | 848 | 967 | 113.5 | 1661 | 1053 | 69 | 0 | 122.5 | 100 | 195.5 | 0
11:00 | 3170 | 895 | 962 | 227 | 1702 | 1065 | 92 | 0 | 135 | 102 | 207 | 0
11:30 | 3186.5 | 895 | 956 | 339.5 | 1838.5 | 1068 | 84 | 0 | 136 | 107 | 208.5 | 0
12:00 | 3203 | 895 | 950 | 452 | 1975 | 1071 | 76 | 0 | 137 | 112 | 210 | 0
12:30 | 3185 | 895 | 952.5 | 499.5 | 2012.5 | 960.5 | 76 | 0 | 135 | 111 | 204 | 0
13:00 | 3167 | 895 | 955 | 547 | 2050 | 850 | 76 | 0 | 133 | 110 | 198 | 0
13:30 | 3167 | 895 | 955 | 547 | 2050 | 850 | 76 | 0 | 133 | 110 | 198 | 0
14:00 | 3167 | 895 | 955 | 547 | 2050 | 850 | 76 | 0 | 133 | 110 | 198 | 0
14:30 | 3171 | 895 | 941 | 293.5 | 2108 | 925 | 76 | 0 | 134 | 107 | 153 | 0
15:00 | 3175 | 895 | 927 | 40 | 2166 | 1000 | 76 | 0 | 135 | 104 | 108 | 0
15:30 | 3180.5 | 895 | 926 | 20 | 2185.5 | 1005 | 76 | 0 | 131.5 | 101 | 75.5 | 0
16:00 | 3186 | 895 | 925 | 0 | 2205 | 1010 | 76 | 0 | 128 | 98 | 43 | 0
16:30 | 3181 | 895 | 921.5 | 74 | 2303 | 1010 | 76 | 0 | 135 | 100 | 22.5 | 0
17:00 | 3181 | 895 | 918 | 148 | 2401 | 1010 | 76 | 0 | 142 | 102 | 2 | 0
17:30 | 3187.5 | 894 | 978.5 | 307 | 2648 | 1030 | 76 | 0 | 261 | 108 | 1 | 0
18:00 | 3194 | 893 | 1039 | 466 | 2895 | 1050 | 76 | 0 | 380 | 114 | 0 | 0
18:30 | 3225 | 893 | 1040 | 315 | 2947.5 | 1075 | 76 | 0 | 402 | 111 | 0 | 0
19:00 | 3256 | 893 | 1041 | 164 | 3000 | 1100 | 76 | 0 | 424 | 108 | 0 | 0
19:30 | 3310 | 893 | 1046 | 55 | 2992 | 1130 | 76 | 0 | 364 | 108 | 0 | 0
20:00 | 3347 | 894 | 1017 | 0 | 2956 | 1130 | 76 | 0 | 358 | 108 | 0 | 0
20:30 | 3346.5 | 893 | 1025 | 0 | 2824 | 1140 | 76 | 0 | 328.5 | 110 | 0 | 0
21:00 | 3346 | 892 | 1033 | 0 | 2692 | 1150 | 76 | 0 | 299 | 112 | 0 | 0
21:30 | 3346 | 893 | 1023.5 | 0 | 2619.5 | 1095 | 76 | 0 | 187 | 107 | 0 | 0
22:00 | 3346 | 894 | 1014 | 0 | 2547 | 1040 | 76 | 0 | 75 | 102 | 0 | 0
22:30 | 3412.5 | 894 | 1024.5 | 0 | 2369 | 1000 | 76 | 0 | 66.5 | 101 | 0 | 0
23:00 | 3479 | 894 | 1035 | 0 | 2191 | 960 | 76 | 0 | 58 | 100 | 0 | 0
23:30 | 3482.5 | 847.5 | 1031.5 | 74 | 1977 | 945 | 76 | 0 | 59 | 98 | 0 | 0 | Max Temp. in Dhaka |  | 24.7° C | 30.2° C
24:00 | 3486 | 801 | 1028 | 148 | 1763 | 930 | 76 | 0 | 60 | 96 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 204.420 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 204.420 MKWHr
Note on W13: Author:

## Generation
g | 2022-11-24
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 92 | 76 | 76 | 76 | 76 | 76 | 76 | 76 |  | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 1537820
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 8 | 0 | [5 empty] | 8 | 17 | 17 | 17 | 17 | 17 | 6 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 285856
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 3 | 9 | 14 | 18 | 20 | 20 | 18 | 15 | 11 | 5 | 0 | [9 empty] | 133380
6 | Sikalbaha 225MW CCPP (Gas) | 152 | 152 | 151 | 151 | 151 | 151 | 151 | 151 | 151 | 151 | 151 | 151 | 151 | 151 | 151 | 151 | 151 | 151 |  | 151 | 151 | 151 | 151 | 151 | 151 | 151 | 3607593
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking |  |  |  |  | 0 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 51 |  | 51 | 51 | 51 | 51 | 51 | 34 | 20 | 524526
12 | Hathazari 100 MW peaking PP | 55 | 0 | [6 empty] | 30 | 45 | 48 | 48 | 40 | 40 | 40 | 40 | 28 | 38 |  | 32 | 16 | 38 | 32 | 24 | 24 | 24 | 626304
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 33 | 61 | 68 | 51 | 51 | 51 | 65 | 68 | 68 |  | 74 | 68 | 68 | 78 | 105 | 58 | 17 | 1099818
| Daudkandi 200 MW PP (B.Trac) | [10 empty] | 20 | 70 | 100 | 20 |  |  |  | 50 | [8 empty] | 274752
14 | Titas 50 MW Peaking PP | 32 | 0 | [8 empty] | 22 | 24 | 28 | 30 | 30 | 23 | 25 | 31 |  | 22 | 22 |  |  |  |  | 0 | 292960
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 98 | 95 | 98 | 97 | 97 | 97 | 98 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 104 | 100 | 289 |  | 279 | 264 | 266 | 283 | 283 | 260 | 143 | 3404836
19 | Ashuganj 195MW PP (APSCL-United)
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4347000
24
25 | Ghorasal 365 MW CCPP Unit-7 | [19 empty] | 100 | 120 | 150 | 190 | 200 | 200 | 200 | 928900
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 44 | 44 | 43 | 43 | 44 | 44 | 41 |  | 44 | 44 | 45 | 45 | 45 | 45 | 45 | 1043136
33 | Ashuganj 225 MW CCPP
34 | Ashuganj 450 MW CCPP(South) | 210 | 210 | 210 | 210 | 210 | 280 | 280 | 280 | 270 | 210 | 210 | 230 | 230 | 210 | 210 | 210 | 210 | 210 |  | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 5543000
Ashuganj 450 MW CCPP(North)
| Ashuganj 420 MW CCPP(East) | 433 | 433 | 433 | 433 | 432 | 432 | 429 | 433 | 433 | 428 | 432 | 432 | 424 | 430 | 430 | 429 | 427 | 430 |  | 434 | 432 | 433 | 434 | 433 | 432 | 432 | 10302900
35 | Ashuganj 55 MW PP (Precision) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 670560
36 | Chandpur 150 MW CCPP | 72 | 70 | 70 | 70 | 77 | 77 | 77 | 79 | 77 | 76 | 78 | 79 | 70 | 71 | 70 | 71 | 71 | 70 |  | 71 | 71 | 70 | 71 | 71 | 71 | 70 | 1746170
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 339 | 339 | 340 | 341 | 346 | 354 | 355 | 353 | 350 | 343 | 335 | 328 | 329 | 328 | 329 | 325 | 322 | 313 |  | 312 | 307 | 309 | 307 | 307 | 310 | 315 | 8048640
40 | Meghnaghat 450 MW CCPP(MPL) | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 |  | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 5343900
41 | Haripur 360MW CCPP(HPL) | 292 | 292 | 294 | 297 | 297 | 274 | 290 | 297 | 292 | 281 | 281 | 275 | 277 | 276 | 271 | 266 | 267 | 267 |  | 268 | 267 | 265 | 266 | 267 | 267 | 267 | 6714000
42 | RPCL 210MW CCPP | 110 | 110 | 111 | 111 | 111 | 112 | 73 | 70 | 72 | 68 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 |  | 44 | 50 | 51 | 54 | 75 | 105 | 104 | 1612800
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 0 | 3 | 17 | 31 | 41 | 46 | 39 | 39 | 35 | 25 | 5 | 0 | [9 empty] | 290500
44 | Fenchugonj CCPP Phase-1 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 716000
45 | Fenchugonj CCPP Phase-2 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 992520
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 40 | 40 | 40 | 70 | 71 | 71 | 67 | 69 | 66 | 52 | 61 | 57 | 57 | 57 | 57 | 60 | 60 | 68 |  | 63 | 63 | 63 | 68 | 69 | 69 | 70 | 1441536
48 | Shahjibazar 86MW PP (Shahjibazar) | 50 | 0 | [15 empty] | 84 |  | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 651840
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 2155340
51 | Sylhet 20 MW GTPP | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 19 | 19 | 19 | 19 | 19 | 440000
52 | Sylhet 50MW PP (EPL) | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 25 | 25 | 26 | 27 |  | 26 | 26 | 26 | 27 | 26 | 26 | 26 | 611480
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 244440
54 | Hobiganj 11MW PP Cofidence-E | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 72215
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 50 | 50 | 50 | 50 | 53 | 47 | 50 | 47 | 50 |  | 47 | 47 | 47 | 50 | 50 | 50 | 50 | 1219200
56 | Shahjahanulla 25 MW PP | 22 | 22 | 22 | 22 | 21 | 21 | 21 | 21 | 21 | 16 | 16 | 16 | 21 | 21 | 21 | 21 | 21 | 24 |  | 24 | 24 | 24 | 24 | 24 | 22 | 22 | 524376
57 | Bibiana-II 341 MW CCPP (Summit)
| Bibiyana South 400 MW | 400 | 400 | 380 | 380 | 380 | 380 | 400 | 400 | 380 | 395 | 380 | 400 | 395 | 400 | 400 | 400 | 400 | 400 |  | 390 | 400 | 400 | 370 | 370 | 400 | 400 | 9436000
58 | Nababganj 55 MW PP (Southern power ) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 35 | 35 | 35 | 35 | 35 |  | 55 | 55 | 55 | 35 | 35 | 35 | 35 | 658851
59 | Tangail Palli Power Gen 22 MW | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 302400
60 | Barabkunda 22 MW PP (Regent)
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 478584
62 | Tangail 22 MW PP (Doreen) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 193500
63 | Impoprt (Tripura) | 94 | 92 | 88 | 80 | 82 | 84 | 78 | 92 | 94 | 98 | 102 | 112 | 110 | 112 | 104 | 98 | 102 | 114 |  | 108 | 108 | 108 | 112 | 102 | 100 | 96 | 2340480
64 | Malancha, Ctg. EPZ (United) | 13 | 17 | 26 | 28 | 30 | 31 | 24 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 3 |  | 8 | 9 | 8 | 5 | 6 | 8 | 8 | 236640
65 | Feni 22MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | [5 empty] | 6 | 19 | 19 | 418644
66 | Feni 11 MW PP (Doreen) | 10 | 10 | 10 | 10 | 10 | 10 | 0 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 11 | 11 | 227880
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 28 | 22 | 21 | 20 | 16 | 16 | 16 | 16 | 22 | 22 | 22 |  | 22 | 30 | 33 | 32 | 32 | 32 | 33 | 627800
68 | Cumilla 25 MW PP (Summit) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 8 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 346660
69 | Summit Ashulia | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 549000
70 | Summit Madhabdi | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 23 | 28 | 28 | 28 | 26 | 26 | 26 | 26 | 26 | 26 | 26 |  | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 615060
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 802000
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 31 | 30 | 30 | 30 | 30 | 28 | 28 | 28 | 28 | 28 |  | 28 | 28 | 28 | 28 | 30 | 30 | 31 | 742700
73 | Ghorashal 108MW PP (Regent) | 71 | 71 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 71 | 66 | 66 | 70 | 70 | 71 | 71 | 71 | 71 |  | 71 | 71 | 42 | 42 | 22 | 22 | 22 | 1492909
| Feni Lanka Power | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 34 | 17 |  |  | 17 | 17 | 397860
| Chowmuhani 113 MW | 55 | 55 | 8 | 8 | 8 | 10 | 51 | 81 | 106 | 108 | 102 | 98 | 99 | 100 | 99 | 105 | 104 | 89 |  | 112 | 119 | 118 | 115 | 65 | 65 | 65 | 1948800
| Manikgonj 162MW PP(MPGL) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 62 | 72 | 72 | 72 | 73 | 151 | 162 |  | 162 | 162 | 162 | 162 | 162 | 144 | 17 | 1710720
77 | Siddhirganj 100 PP(Dutch Bangla) | 30 | 30 | 22 | 0 | 0 | 1 | 26 | 30 | 30 | 48 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 80 |  | 80 | 80 | 80 | 80 | 70 | 40 | 24 | 1142400
78 | Gazipur 52 MW PP | 8 | 0 |  |  |  |  | 4 | 15 | 24 | 32 | 32 | 33 | 37 | 44 | 49 | 47 | 49 | 49 |  | 49 | 49 | 49 | 49 | 24 | 30 | 50 | 692640
79 | Kodda 150MW PP | [7 empty] | 100 | 114 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 |  | 48 | 48 | 42 | 32 |  |  | 16 | 782880
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 16 |  | 16 | 16 | 16 | 8 | 8 | 8 | 8 | 225840
| Gazipur 100 MW PP | 105 | 70 | 34 | 17 | 17 | 17 | 17 | 88 | 88 | 88 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2035104
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 0 | 1 | 3 | 4 | 4 | 4 | 4 | 3 | 2 | 1 | [10 empty] | 25199
| Jodiac Power | 17 | 17 | 17 | 17 | 17 | 17 | 28 | 36 | 36 | 36 | 39 | 54 | 54 | 36 | 36 | 36 | 36 | 36 |  | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 829212
| Karnaphuli Power Ltd. | 53 | 53 | 54 | 54 | 54 | 54 | 54 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 57 |  | 75 | 91 | 90 | 91 | 90 | 70 | 60 | 1487884
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL) | 25 | 23 | 0 |  |  |  |  | 6 | 25 | 30 | 59 | 68 | 74 | 74 | 74 | 82 | 81 | 83 |  | 82 | 82 | 82 | 75 | 65 | 50 | 28 | 1080960
| Meghnaghat 104 MW PP (OPCL) | 17 | 17 | 17 | 0 | 0 | 2 | 17 | 18 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 382080
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 258960
92 | Fenchuganj 44MW (Energyprima) | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 |  | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 967320
93 | Ashuganj 51 MW PP (Midland) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 214484
94 | Gagnagar 102 MW PP (Digital Power) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 40 |  | 40 | 41 | 41 | 41 | 41 | 41 | 8 | 439056
95 | Patenga 50MW PP (Baraka) | 24 | 24 | 0 |  |  | 0 | 12 | 16 | 19 | 19 | 19 | 13 | 12 | 12 | 12 | 7 | 22 | 26 |  | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 441120
96 | Chattogram 108 MW PP (ECPV) | [25 empty] | 0 | 0
97 | katpotti 52 MW
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 38 | 0 | 0 | 8 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 37 | 45 | 45 | 45 | 45 | 45 |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 893650
100 | Manikganj 55 MW PP (Northern) | 35 | 17 | 0 |  |  |  |  | 35 | 35 | 35 | 55 | 55 | 55 | 35 | 35 | 35 | 35 | 35 |  | 55 | 55 | 55 | 35 | 35 | 17 | 35 | 727422
101 | Kushiara 163 MW CCPP (KP)
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 1 | 0 | [10 empty] | 12400
103 | Kamalaghat 54 MW PP(Banco Energy) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 54 |  | 54 | 54 | 54 | 17 | 17 | 17 | 17 | 528120
104 | Keranigonj 300 MW PP (APR) | [10 empty] | 97 | 191 | 246 | 30 | 15 |  | 98 | 224 |  | 4 | [5 empty] | 48 | 985190
105 | Bramhangoan 100 MW PP (Aggreko) | [10 empty] | 50 | 97 | 97 | 25 | 25 |  | 25 | 95 |  | 40 | 25 |  |  |  |  | 50 | 506630
106 | Mymensingh 200 MW PP (United) | 48 | 48 | 8 | 8 | 8 | 37 | 46 | 48 | 48 | 48 | 56 | 58 | 58 | 57 | 58 | 58 | 48 | 58 |  | 57 | 57 | 58 | 58 | 58 | 58 | 48 | 1113600
112 | Aurahati 100MW PP (Aggreko) | [10 empty] | 60 | 94 | 94 | 40 |  |  | 25 | 96 |  | 70 | [5 empty] | 50 | 471122
114 | Kodda 149 MW PP Unit-1 (Summit) | 149 | 149 | 149 | 82 | 36 | 41 | 108 | 134 | 149 | 149 | 135 | 135 | 135 | 135 | 133 | 141 | 137 | 143 |  | 133 | 143 | 149 | 149 | 84 |  | 0 | 2790144
115 | Juldah 100 MW PP Unit-3 (Acorn) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 290880
116 | Chandpur 200MW (Desh energy) | 69 | 56 | 51 | 17 | 17 | 23 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 92 |  | 120 | 101 | 85 | 85 | 85 | 85 | 85 | 1494720
117 | Ashuganj 150MW PP (Midland) | 73 | 68 | 10 | 10 | 10 | 15 | 32 | 57 | 72 | 78 | 85 | 75 | 77 | 82 | 90 | 100 | 112 | 120 |  | 112 | 108 | 108 | 102 | 98 | 85 | 73 | 1803200
118 | Bibiyana-III 400 MW CCPP | 354 | 354 | 354 | 354 | 354 | 417 | 386 | 418 | 416 | 401 | 419 | 415 | 399 | 422 | 422 | 419 | 416 | 420 |  | 420 | 420 | 419 | 395 | 352 | 418 | 418 | 9532000
| Jamalpur 115 MW PP (United) | 49 | 49 | 49 | 49 | 16 | 47 | 47 | 49 | 49 | 49 | 58 | 58 | 58 | 58 | 58 | 58 | 50 | 59 |  | 59 | 59 | 59 | 59 | 59 | 59 | 49 | 1225200
| Anwara 300 MW PP (United) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 100 | 250 | 250 | 258 | 263 | 268 | 268 | 286 |  | 285 | 285 | 285 | 70 | 68 | 68 | 67 | 2847818
| Juldah unit-2 (Acorn) | 10 | 10 | 10 | 10 | 10 | 10 | 12 | 12 | 12 | 9 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 281280
| Anlima Energy Ltd. | 51 | 51 | 51 | 36 | 17 | 27 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 |  | 90 | 107 | 107 | 107 | 107 | 107 | 107 | 1945800
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 444240
| Spectra Solar Plant Ltd. | [5 empty] | 0 | 2 | 8 | 17 | 23 | 28 | 28 | 28 | 22 | 15 | 7 | 1 | [9 empty] | 178523
| Chandpur 115(Doreen) | 18 | 18 | 18 | 17 | 17 | 18 | 18 | 18 | 18 | 18 | 52 | 97 | 83 | 79 | 64 | 78 | 86 | 109 |  | 116 | 115 | 115 | 115 | 115 | 79 | 26 | 1405440
| Kanchan Purbachal Power Generation Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 15 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 26 | 17 | 24 | 17 | 17 | 17 | 17 | 446400
| Mirsharai 150 MW (Oil) | [25 empty] | 0 | 0
Mirsharai 150 MW (Gas)
120 | Eastern Zone Total | 4971 | 4704 | 4437 | 4299 | 4238 | 4469 | 4708 | 5099 | 5223 | 5123 | 5655 | 6143 | 6210 | 5766 | 5661 | 5642 | 5856 | 6719 |  | 6530 | 6476 | 6431 | 6102 | 5889 | 5731 | 5469 | 131903704
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | 16 | 0 | [5 empty] | 58 | 83 | 55 |  | 10 |  | 50 | 49 | 49 | 65 | 97 |  | 97 | 97 | 97 | 97 | 114 | 110 | 83 | 1079040
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 35 | 0 |  |  |  |  | 18 | 46 | 56 | 56 | 17 | 17 | 22 | 55 | 55 | 56 | 56 | 60 |  | 67 | 75 | 75 | 75 | 75 | 75 | 53 | 1002720
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 0 | 5 | 26 | 46 | 63 | 72 | 75 | 68 | 54 | 35 | 15 | 1 | [9 empty] | 468000
131 | Rampal 1320 MW (BIFPCL)
132 | United Payra Power Ltd. | [25 empty] | 0 | 0
133 | Bhola Nutan Biddut BD LTD (GAS)
Bhola Nutan Biddut BD LTD (OIL)
Barisal 110 MW PP (Summit )
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW | 139 | 142 | 139 | 139 | 141 | 140 | 132 | 130 | 162 | 161 | 215 | 251 | [14 empty] | 2027600
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 130 | 130 | 130 | 130 | 130 | 110 | 130 | 130 | 121 | 130 | 108 | 130 | 130 | 123 | 130 | 130 | 130 | 130 |  | 113 | 130 | 125 | 130 | 130 | 116 | 116 | 3079000
140 | Bhola 33 MW PP (Venture) | 16 | 16 | 15 | 14 | 14 | 14 | 13 | 13 | 12 | 12 | 13 | 13 | 14 | 14 | 12 | 11 | 15 | 17 |  | 17 | 16 | 18 | 18 | 18 | 18 | 17 | 349300
141 | Noapara 100 MW PP (Bangla Trac) | [9 empty] | 0 |  |  | 10 | [12 empty] | 0 | 9600
142 | Noapara 40 MW PP (Khanjahan Ali) | [13 empty] | 16 | 32 |  | 16 | 32 |  | 32 | 16 | 16 | 16 | 16 | 16 | 0 | 178500
143 | Gopalganj 100 MW Peaking PP | [16 empty] | 10 | 60 |  | 85 | 80 | 80 | 45 |  |  |  | 262656
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 658 | 659 | 659 | 660 | 659 | 659 | 659 | 659 | 753 | 801 | 895 | 895 | 895 | 895 | 895 | 895 | 895 | 893 |  | 893 | 893 | 894 | 892 | 894 | 894 | 801 | 19445818
147 | Bheramara 410 MW CCPP | 165 | 165 | 165 | 165 | 180 | 180 | 180 | 180 | 180 | 165 | 165 | 155 | 150 | 150 | 150 | 155 | 150 | 155 |  | 155 | 155 | 160 | 160 | 165 | 170 | 170 | 4078944
148 | Payra 1320 MW | 710 | 700 | 700 | 700 | 620 | 630 | 680 | 790 | 770 | 720 | 690 | 660 | 690 | 770 | 840 | 850 | 850 | 890 |  | 940 | 970 | 970 | 990 | 880 | 800 | 770 | 20688700
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 |  | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 3912700
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [19 empty] | 24 | 24 | 24 | 24 |  |  |  | 80176
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 0 | 1 | 3 | 4 | 3 | 5 | 5 | 4 | 2 | 0 | 0 | [9 empty] | 31200
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 168 | 169 | 171 | 171 | 175 | 176 | 179 | 179 | 176 | 173 | 169 | 167 | 168 | 164 | 165 | 165 | 165 | 165 |  | 164 | 164 | 164 | 165 | 164 | 166 | 167 | 4270955
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 237 | 238 | 243 | 256 | 257 | 236 | 261 | 251 | 231 | 212 | 207 | 201 | 199 | 199 | 182 | 183 | 172 | 202 |  | 199 | 204 | 203 | 217 | 217 | 236 | 231 | 5302545
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 21 | 22 | 22 | 22 | 22 | 22 | 21 | 19 | 17 | 16 | 15 | 15 | 15 | 15 | 15 | 15 | 16 | 16 |  | 19 | 20 | 22 | 22 | 22 | 22 | 21 | 429360
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 192042
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | [7 empty] | 34 | 34 | 34 | 8 | 16 | 34 | 34 | 34 | 34 | 34 | 34 |  | 34 | 34 | 34 | 25 | 8 | 16 | 25 | 468976
167 | Katakhali 50 MW Peaking PP | [17 empty] | 31 |  | 40 | 40 | 40 | 32 |  |  |  | 121136
168 | Santahar 50 MW Peaking PP | [16 empty] | 14 | 33 |  | 34 | 34 | 34 | 34 |  |  |  | 143506
169 | Natore 52 MW PP (Rajlanka) | [7 empty] | 23 | 34 | 34 | 16 | 16 | 43 | 43 | 43 | 24 | 24 | 43 |  | 39 | 25 | 8 | 43 | 43 | 43 | 43 | 541440
170 | Chapainawabganj 100 MW Peaking PP | [17 empty] | 88 |  | 88 | 49 | 49 | 49 |  |  |  | 254800
171 | Baghabari 200 MW PP (Paramount) | [17 empty] | 1 |  | 50 | 30 |  |  |  |  | 0 | 77364
| Bagura 113 MW PP (Confidence)-2 | 70 | 0 |  |  | 0 | 1 | 30 | 55 | 70 | 70 | 35 | 36 | 55 | 70 | 70 | 70 | 94 | 94 |  | 94 | 94 | 94 | 94 | 94 | 70 | 70 | 1467168
172 | Confidence Power Bogura Unit-1 113 MW | 35 | 35 | 35 | 25 | 0 | 35 | 35 | 35 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 60 | 95 | 95 |  | 95 | 95 | 95 | 95 | 90 | 35 | 35 | 1198656
173 | Rangpur 20 MW GTPP | [5 empty] | 0
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | 34 | 0 |  |  |  |  | 1 | 26 | 32 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 49 | 84 |  | 85 | 85 | 85 | 35 | 35 | 35 | 34 | 785040
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 0 | 1 | 3 | 4 | 5 | 6 | 6 | 5 | 4 | 4 | 0 | [9 empty] | 37515
178 | Energypac Power Venture Thakurgaon Ltd. | [7 empty] | 28 | 34 | [13 empty] | 72 | 72 | 72 | 115 | 351168
178 | Intraco Solar 30 MW | [5 empty] | 0 | 1 | 9 | 15 | 25 | 27 | 31 | 28 | 20 | 13 | 6 | 0 | [9 empty] | 180492