## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2022-12-02 | Friday
|  | Date (day): | 2022-12-02 |  | Friday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 8509.6 | MW |  |  | (b) At Evening Peak Hour : |  | 11321 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2022-12-01 | 2022-12-02 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Line O/L
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 200 | 200 | 200 | 200 |  | 165 | Machine problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 22 | 22 | 22 | 22 | 86 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 269 | 285 | 300 | 290 | 122 |  | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 0 | 0 | 0 | 0 | 360 |  | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 225 | 225 | 225 |  | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 59 | 58 | 80 | 80 |  | 20 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 210 | 215 | 240 | 220 | 115 |  | FGMO
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 0 | 0 | 0 | 0 |  | 102 | Under maint
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 45 | 45 | 45 | 45 |  | 10 | Engine problem
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 22 | 16 | 16 |  | 6 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 65 | 70 | 80 | 80 |  | 20 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 8 | 24 | 40 | 80 | 22 |  | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 54 | 17 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 32 | 32 | 32 | 32 | 117 |  | Fuel shortage
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 35 | 35 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 35 | 35 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 46 | 47 | 46 | 46 |  | 34 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 26 | 26 | 25 | 25 |  | 8 | Engine problem
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 41 | 49 | 50 | 50
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 98 | 247 | 95 | 285 |  | 15 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 300 | 300 | 0 | 150 | 150 |  | Fuel conservation
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 99 | 0 | 0 | 50 | 50 |  | Fuel conservation
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 98 | 100 | 0 | 50 | 50 |  | Fuel conservation
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 43 | 60 | 53 | 64 | 85 |  | Fuel shortage
36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 88 | 105 | 88 | 105
37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 55 | 72 | 55 | 55 | 49 |  | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 90 | 162 | 90 | 162
39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 30 | 0 | 30 | 0
40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 17 | 17 | 17 | 38 |  | Fuel shortage
| Dhaka area Total |  |  |  |  | 6263 | 5847 | 2485 | 2720 | 2129 | 2726 | 2065 | 1060
41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 17 | 17 | 17 | 17 |  | 8 | Engine problem
43 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 16 | 0 | 20 | 0
44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 19 | 28 | 26 | 44 |  | 6 | Engine problem
45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 46 | 46 | 46 | 46 | 184 |  | Low Water Level
46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 148 | 151 | 151 | 151 |  | 74 | ST under maint
47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 17 | 105 | 17 | 105
49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 31 | 39 | 28 | 32 | 66 |  | Fuel shortage
50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 0 | 51 | 51 |  | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 10 | 10 | 10 | 10 | 90 |  | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 12 | 12 | 12 | 88 |  | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  | 22 | Engine problem
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 4 | 20 | 20
54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 230 | 280 | 69 | 290 |  | 10
57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 17 | 36 | 17 | 36 |  | 18 | Engine problem
58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 54 | 73 | 53 | 74 |  | 36 | Engine problem
59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 12 | 12 | 12 | 88 |  | Fuel shortage
60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 89 | 89 | 107 | 107 |  | 9 | Engine problem
| Mirsharai 150 MW |  | Gas/HSD | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0
| Chattogram area Total |  |  |  |  | 2442 | 2382 | 724 | 953 | 610 | 1007 | 1035 | 333
61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 152 | 219 | 170 | 200 | 21 |  | Gas shortage
63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 205 | 305 | 200 | 250 | 110
| Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+136*1 | 284 | 284 | 242 | 119 | 400 | 400 |  |  | On test.
65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 5 | 30 | 0 | 0 | 45 |  | Gas shortage
66 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 55 | 0 | 5 | 0 | 0 | 55 |  | Gas shortae
67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 36 | 0 | 0 | 195 |  | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 5 | 5 | 5 | 5 | 46 |  | Gas shortage
69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 150 | 74 | 75 | 100 |  |  | Fuel shortage
70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 4 | 37 | 21 | 32 |  | 20 | Engine problem
71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 64 | 64 | 80 | 80 | 83 |  | Gas shortage.
72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 17 | 50 | 17 | 200
73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 10 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 112 | 122 | 143 | 165
75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 14 | 16 | 33 | 33
76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 9 | 8 | 16 | 36 |  | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 15 | 15 | 15 | 15 |  | 10 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 160 | 148 | 0 | 100 | 100 |  | Fuel conservation
79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 99 | 17 | 99 | 15 |  | Fuel shortage
80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 97 | 111 | 113 | 113
81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 17 |  | 37 | Engine problem
82 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 111 | 111 | 34 | 115
| Cumilla Area Total |  |  |  |  | 3193 | 3169 | 1436 | 1624 | 1381 | 1973 | 840 | 427
83 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 37 | 33 | 32 | 72 | 130 |  | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 8 | 4 | 8 | 8 | 14 |  | Gas shortage
85 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0
86 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
87 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 58 | 58 | 48 | 57 | 143 |  | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 58 | 58 | 49 | 58 | 57 |  | Fuel shortage
89 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 43 | 0 | 50 | 0
90 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 4 | 12 | 12 |  | 10 | Engine problem
| Mymensingh Area Total |  |  |  |  | 717 | 614 | 218 | 157 | 200.6 | 207 | 144 | 10
91 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 30 | 30 | 30 | 30 |  | 40 | Machine problem.
92 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 |  | 60 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 90 | 90 | 90 | 90 | 78 |  | Gas shortage
94 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 50 | 53 | 51 | 51
96 | Fenchuganj 44MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 40 | 42 | 40 | 40
97 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 8 | 8 | 3 |  | Gas shortage
98 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 62 | 64 | 66 | 66
99 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 0 | 86 | 0 | 86
100 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
101 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 0 | 0 | 0 |  | 231 | Under maint
102 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18
103 | Sylhet 50MW PP (EPL) |  | Gas | NENP | 27*2 | 50 | 50 | 32 | 33 | 32 | 32 | 18 |  | Gas shortage
104 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 22 | 24 | 21 | 24
105 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 0 | 0 | 0 | 0 |  | 341 | Under maint. |  | 2022-12-23
106 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 414 | 422 | 400 | 400
107 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
108 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 394 | 396 | 400 | 400
| Sylhet Area Total |  |  |  |  | 2522 | 2477 | 1200 | 1306 | 1196 | 1285 | 99 | 1102
109 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 891 | 885 | 717 | 910
110 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 49 | 54 | 83 | 114 | 83 |  | Fuel shortage
111 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 43 | 0 | 40
112 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
113 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 76 | 0 | 75 |  | 34 | Engine problem
114 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 155 | 155 | 0 | 0 |  | 410 | Under maint
115 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 0 | 0 | 8 | 32 |  | Fuel shortage
116 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 40 | 0 | 50 | 50 |  | Fuel conservation
117 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 75 | 75 | 55 | 75 |  | 30 | Engine problem
118 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Fuel shortage
119 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 76 | 0 | 100 | 0
| Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 0 | 0 | 0 | 546 | 538 | 150 | 540 |  |  | On test.
| Khulna Area Total |  |  |  |  | 2388 | 2384 | 1792 | 1866 | 1105 | 1812 | 516 | 474
120 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 0 | 0 |  |  | Line O/L
121 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 17 | 18 | 15 | 19 |  | 21 | Engine problem
122 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 178 | 158 | 180 | 180 |  | 14
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
123 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 260 | 280 | 622 | 622 |  | 622 | Unit-1 under maint
124 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 174 | 210 | 200 | 220
125 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 0 | 0 |  |  | Line O/L
| Barisal 307 MW |  | Coal | BCPCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Barisal Area Total |  |  |  |  | 1958 | 1958 | 629 | 666 | 1017 | 1041 | 0 | 657
126 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
127 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 24 | 0 | 34 |  | 18 | Engine problem
128 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 4 | 0 | 29 |  | 42 | Engine problem
129 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
130 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 16 | 34 | 34 | 34 |  | 16 | Engine problem
131 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 40 | 0 | 40 | 10 |  | Fuel shortage
132 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 183 | 188 | 160 | 160 | 50 |  | Gas shortage
133 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Fuel shortage
134 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
135 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 223 | 212 | 280 | 280 | 134 |  | Gas shortage
136 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 30 | 0 | 35 |  | 15 | Engine problem
137 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 16 | 17 | 20 | 22
138 | Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
139 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
140 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 8 | 43 | 43 |  | 9 | Engine problem
141 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 75 | 0 | 85 |  | 15 | Engine problem
142 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel shortage
143 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 35 | 92 | 35 | 95 |  | 18 | Engine problem
144 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 35 | 35 | 50 | 95 |  | 18 | Engine problem
145 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
| Adani Power Jharkhanda Ltd |  | Coal | Import | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Rajshahi Area Total |  |  |  |  | 2199 | 2129 | 532 | 770 | 639 | 963 | 1005 | 151
146 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal shortage
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
147 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 160 | 160 | 160 | 160 |  |  | Machine problem
148 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
149 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
150 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 34 | 49 | 34 | 34 |  | 79 | Engine problem
151 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 6 | 0 | 8 | 0
152 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 0 | 75 | 0 | 113
| Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 30 | 0 | 30 | 0
| Rangpur Area Total |  |  |  |  | 830 | 750 | 230 | 284 | 232 | 307 | 125 | 164
| Total |  |  |  |  | 22512 | 21710 | 9246 | 10346 | 8509.6 | 11321 | 5829 | 4378
A. |  | 2022-12-01 | (Yesterday) |  |  |  |  | Thursday
1 | Highest Generation : |  |  | 10346 | MW at | 18:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 18:00 | hrs.
2 | Minimum Generation : |  |  | 7382 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 10550 | MW
3 | Day peak Generation : |  |  | 9246 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 10109.51 | MW
4 | Evening peak Generation : |  |  | 10346 | MW at | 18:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 188 | MW
5 | Total Energy Generation : |  | 209.9611 | MKWHr | By Solar | 1.343 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Gas : | 109.0488 | MKWHr |  | By Oil: | 53.0219 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 22.9287 | MKWHr |  | By Hydro: | 1.1085 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 5829 | MW | Dhaka | 3864.24 | 3752.24 |  | 112 |  | 18:00 |  | 188.0013
|  |  | For Plants S/D or M/C prob = |  |  | 4378 | MW | Chittagong | 1186.1 | 1186.1 |  | 0 |  | 19:00 |  | 82.0202
|  |  | Total = |  |  | 10207 | MW | Khulna | 1130 | 1130 |  | 0 |  | 19:30 |  | 63.5887
7 | Total Gas Supplied : |  |  | 888.48 | MMCFD |  |  | Rajshahi | 956.1 | 956.1 |  | 0 |  | 20:00 |  | 45.1572
8 | Fuel Cost : | i) Gas : | Taka | 117942063.714 | ii) Oil : | Taka | 743502555.66 | Comilla | 888 | 888 |  | 0 |  | 21:00 |  | 0
|  | iii) Coal : |  | 94373123 | Total | Taka | 955817742.374 | Mymensingh | 773 | 697 |  | 76 |  | 22:00 |  | 0
9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0 | MKWHr. | Sylhet | 406 | 406 |  | 0 |  | 23:00 |  | 0
| ii) During Peak Demand : |  |  | 900 | MW (E to W) at | 18:00 | hrs | Barisal | 251.07 | 251.07 |  | 0 |  | 24:00 |  | 0
| iii) Maximum : |  |  | 850 | MW at | 22:00 | hrs | Rangpur | 655 | 655 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 30.4° C |  |  | Total | 10109.51 | 9921.51 |  | 188
B. |  | 2022-12-02 | (Today) |  |  |  | Friday |  |  | Probable max. temperature in Dhaka |  |  | 28.3° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 10000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 11321 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 8200 | MW
4 | Reserve(Generation end) |  |  |  | 1321 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 202.9394 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 6923 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 19.92 | MKWHr. | ii) HVDC Flow at Peak Time |  | 885 | MW at | 18:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.5901 | MKWHr. | iii) Maximum HVDC Flow : |  | 893 | MW at | 20:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 89.75 |  | (b) Today: | 89.68 |  | (c) Rule Curve: |  | 106
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2022-12-01
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 200 | 22 | 0 | 295 | 0 |  | 0 | 225 | 210 | 25 | 0 | 45 | 0 | 0 | 0 | 30 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 19 | 22 | 27 | 33 | 30 | 48 | 0 | 46 | 0 | 0 | 0 | 17 | 151 | 0 | 0 | 0 |  | 12 | 32 | 51 | 10 | 0 | 19 | 0 | 18 | 0 | 0 | 0 | 260 | 270 | 173 | 8 | 71 | 5 | 5 | 0 | 5 | 0 | 0 | 8 | 22 | 11 | 33 | 15 | 110 | 106 | 0 | 8 | 0 | 30 | 21 | 53 | 43 | 100 | 0 | 66 | 0 | 0 | 0 | 19 | 33 | 10 | 0 | 24 | 8 | 0 | 98 | 60 | 100 | 48 | 70 | 45 | 0 | 12 | 17 | 92 | 421 | 49 | 105 | 17 | 1 | 16 | 17 | 54 | 17 | 110 | 12 | 400 | 55 | 0 | 17 | 107 | 0 | 17 | 0 | 35 | 17 | 0 | 0 | 0 |  | 701 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 157 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 258 | 75 | 0 | 55 | 0 | 34 | 0 | 0 | 35 | 410 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 465 | 0 | 0 | 0 |  | 5386 | 2942 | 8328 | 3442 | 701 | 1209 | 230 | 1455 | 1035 | 46 | 0 | 99 | 110 | 1 | 0 | 89.75
2:00 | 0 | 0 | 0 | 180 | 200 | 22 | 0 | 292 | 0 |  | 0 | 225 | 200 | 24 | 0 | 45 | 0 | 0 | 0 | 30 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 19 | 22 | 27 | 33 | 30 | 49 | 0 | 46 | 0 | 0 | 0 | 17 | 150 | 0 | 0 | 0 |  | 12 | 32 | 51 | 10 | 0 | 19 | 0 | 30 | 0 | 0 | 0 | 250 | 280 | 173 | 8 | 71 | 5 | 5 | 0 | 5 | 0 | 0 | 8 | 22 | 11 | 33 | 15 | 110 | 106 | 0 | 8 | 0 | 30 | 21 | 53 | 43 | 100 | 0 | 67 | 0 | 0 | 0 | 19 | 33 | 10 | 0 | 23 | 8 | 0 | 98 | 0 | 0 | 48 | 0 | 42 | 0 | 12 | 17 | 119 | 421 | 49 | 105 | 17 | 0 | 16 | 17 | 54 | 17 | 109 | 12 | 400 | 55 | 0 | 17 | 107 | 0 | 17 | 0 | 35 | 17 | 0 | 0 | 0 |  | 654 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 254 | 75 | 0 | 55 | 0 | 34 | 0 | 0 | 35 | 380 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 466 | 0 | 0 | 0 |  | 5176 | 2865 | 8041 | 3442 | 654 | 1206 | 0 | 1478 | 1006 | 46 | 0 | 99 | 110 | 0 | 0 | 89.75
3:00 | 0 | 0 | 0 | 180 | 200 | 22 | 0 | 285 | 0 |  | 0 | 225 | 200 | 24 | 0 | 45 | 0 | 0 | 0 | 30 | 8 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 19 | 22 | 27 | 33 | 30 | 25 | 0 | 46 | 0 | 0 | 0 | 17 | 150 | 0 | 0 | 0 |  | 12 | 0 | 0 | 10 | 0 | 19 | 0 | 30 | 0 | 0 | 0 | 260 | 250 | 152 | 8 | 70 | 5 | 5 | 0 | 5 | 0 | 0 | 8 | 22 | 11 | 33 | 15 | 100 | 106 | 0 | 8 | 0 | 30 | 21 | 53 | 43 | 100 | 0 | 67 | 0 | 0 | 0 | 19 | 33 | 10 | 0 | 23 | 8 | 0 | 98 | 0 | 0 | 48 | 0 | 43 | 0 | 12 | 17 | 145 | 352 | 49 | 105 | 17 | 0 | 16 | 17 | 54 | 17 | 105 | 12 | 370 | 55 | 0 | 17 | 107 | 0 | 17 | 0 | 35 | 17 | 22 | 0 | 0 |  | 654 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 17 | 0 | 35 | 0 | 10 | 0 | 0 | 35 | 360 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 466 | 0 | 0 | 0 |  | 4940 | 2758 | 7698 | 3316 | 654 | 1221 | 0 | 1375 | 986 | 46 | 0 | 0 | 100 | 0 | 0 | 89.75
4:00 | 0 | 0 | 0 | 180 | 200 | 22 | 0 | 285 | 0 |  | 0 | 225 | 200 | 0 | 0 | 45 | 0 | 0 | 0 | 30 | 8 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 19 | 22 | 27 | 33 | 30 | 0 | 0 | 46 | 0 | 0 | 0 | 17 | 151 | 0 | 0 | 0 |  | 12 | 0 | 0 | 10 | 0 | 19 | 0 | 33 | 0 | 0 | 0 | 0 | 270 | 185 | 8 | 72 | 5 | 5 | 0 | 5 | 0 | 0 | 8 | 22 | 11 | 33 | 15 | 98 | 108 | 0 | 8 | 0 | 30 | 21 | 53 | 43 | 100 | 0 | 67 | 0 | 0 | 0 | 19 | 32 | 10 | 0 | 22 | 8 | 0 | 98 | 0 | 0 | 24 | 0 | 43 | 0 | 12 | 17 | 150 | 358 | 49 | 70 | 17 | 0 | 16 | 17 | 54 | 17 | 108 | 12 | 370 | 55 | 0 | 17 | 107 | 0 | 17 | 0 | 35 | 17 | 130 | 0 | 0 |  | 654 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 274 | 17 | 0 | 35 | 0 | 0 | 0 | 0 | 35 | 330 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 466 | 0 | 0 | 0 |  | 4733 | 2722 | 7455 | 3228 | 654 | 1226 | 0 | 1247 | 956 | 46 | 0 | 0 | 98 | 0 | 0 | 89.75
5:00 | 0 | 0 | 0 | 180 | 200 | 22 | 0 | 285 | 0 |  | 0 | 225 | 200 | 0 | 0 | 45 | 0 | 0 | 0 | 30 | 8 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 16 | 22 | 27 | 33 | 30 | 0 | 0 | 46 | 0 | 0 | 0 | 17 | 151 | 0 | 0 | 0 |  | 12 | 0 | 0 | 10 | 0 | 19 | 0 | 33 | 0 | 0 | 0 | 0 | 270 | 185 | 8 | 71 | 5 | 5 | 0 | 5 | 0 | 0 | 4 | 22 | 11 | 33 | 15 | 104 | 108 | 0 | 8 | 0 | 30 | 21 | 22 | 20 | 100 | 0 | 40 | 0 | 0 | 0 | 19 | 32 | 10 | 0 | 21 | 8 | 0 | 98 | 0 | 0 | 24 | 0 | 43 | 0 | 12 | 17 | 150 | 358 | 49 | 70 | 17 | 0 | 16 | 17 | 54 | 17 | 65 | 12 | 360 | 55 | 0 | 17 | 107 | 0 | 17 | 0 | 35 | 17 | 220 | 0 | 0 |  | 654 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 139 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 320 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 516 | 0 | 0 | 0 |  | 4686 | 2696 | 7382 | 3270 | 654 | 1172 | 0 | 1140 | 996 | 46 | 0 | 0 | 104 | 0 | 0 | 89.75
6:00 | 0 | 0 | 0 | 180 | 200 | 22 | 0 | 286 | 0 |  | 0 | 225 | 200 | 2 | 0 | 45 | 0 | 0 | 0 | 30 | 8 | 10 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 16 | 22 | 27 | 33 | 30 | 2 | 0 | 46 | 0 | 0 | 0 | 17 | 151 | 0 | 0 | 0 |  | 12 | 0 | 0 | 10 | 0 | 19 | 0 | 36 | 0 | 0 | 0 | 0 | 270 | 184 | 8 | 71 | 5 | 5 | 0 | 5 | 0 | 0 | 8 | 22 | 11 | 33 | 15 | 72 | 108 | 0 | 8 | 0 | 30 | 21 | 22 | 20 | 100 | 0 | 40 | 0 | 0 | 0 | 19 | 32 | 10 | 0 | 21 | 8 | 0 | 98 | 0 | 0 | 24 | 0 | 43 | 0 | 12 | 17 | 150 | 341 | 49 | 80 | 17 | 0 | 16 | 17 | 54 | 17 | 73 | 12 | 340 | 55 | 0 | 17 | 98 | 0 | 17 | 0 | 34 | 17 | 275 | 0 | 0 |  | 654 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 300 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 555 | 0 | 0 | 0 |  | 4719 | 2731 | 7450 | 3302 | 654 | 1177 | 0 | 1174 | 1015 | 46 | 0 | 10 | 72 | 0 | 0 | 89.75
7:00 | 0 | 0 | 0 | 180 | 200 | 22 | 0 | 280 | 0 |  | 0 | 225 | 196 | 21 | 0 | 45 | 0 | 0 | 0 | 30 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 16 | 22 | 27 | 33 | 30 | 36 | 0 | 46 | 0 | 0 | 0 | 17 | 151 | 0 | 0 | 0 |  | 12 | 0 | 0 | 10 | 0 | 19 | 0 | 31 | 0 | 0 | 0 | 0 | 230 | 170 | 8 | 71 | 5 | 5 | 0 | 5 | 0 | 0 | 8 | 22 | 11 | 33 | 15 | 86 | 97 | 0 | 8 | 0 | 30 | 21 | 22 | 20 | 100 | 0 | 40 | 0 | 0 | 0 | 18 | 33 | 10 | 0 | 21 | 8 | 0 | 95 | 0 | 0 | 46 | 0 | 44 | 2 | 12 | 17 | 150 | 416 | 49 | 88 | 17 | 0 | 16 | 17 | 54 | 17 | 95 | 12 | 400 | 55 | 3 | 17 | 89 | 0 | 17 | 2 | 35 | 17 | 269 | 0 | 0 |  | 793 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 157 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 11 | 0 | 14 | 0 | 33 | 0 | 0 | 35 | 320 | 180 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 527 | 1 | 0 | 0 |  | 4890 | 2914 | 7804 | 3353 | 793 | 1163 | 0 | 1327 | 1007 | 46 | 0 | 16 | 86 | 13 | 0 | 89.74
8:00 | 0 | 0 | 0 | 180 | 200 | 22 | 0 | 278 | 0 |  | 0 | 225 | 200 | 25 | 0 | 45 | 0 | 0 | 0 | 30 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 16 | 22 | 27 | 33 | 17 | 41 | 0 | 46 | 0 | 0 | 0 | 17 | 151 | 0 | 0 | 0 |  | 12 | 0 | 0 | 10 | 0 | 19 | 0 | 13 | 0 | 0 | 0 | 0 | 230 | 150 | 8 | 72 | 5 | 5 | 0 | 5 | 0 | 0 | 8 | 19 | 11 | 19 | 15 | 96 | 72 | 0 | 8 | 1 | 30 | 21 | 51 | 20 | 100 | 0 | 69 | 0 | 0 | 0 | 18 | 32 | 10 | 0 | 21 | 8 | 0 | 98 | 0 | 0 | 46 | 0 | 43 | 6 | 12 | 17 | 150 | 355 | 49 | 88 | 17 | 1 | 16 | 17 | 54 | 17 | 98 | 12 | 348 | 55 | 14 | 17 | 89 | 0 | 17 | 11 | 35 | 17 | 269 | 0 | 0 |  | 892 | 0 | 180 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 135 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 8 | 0 | 20 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 265 | 53 | 0 | 34 | 0 | 33 | 0 | 1 | 35 | 370 | 170 | 0 | 0 | 1 | 26 | 0 | 0 | 0 | 527 | 6 | 0 | 0 |  | 4794 | 3154 | 7948 | 3180 | 892 | 1159 | 0 | 1435 | 1057 | 46 | 0 | 16 | 96 | 67 | 309.6492 | 89.74
9:00 | 0 | 0 | 0 | 180 | 200 | 22 | 0 | 275 | 0 |  | 0 | 225 | 210 | 25 | 0 | 45 | 0 | 0 | 0 | 30 | 8 | 32 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 16 | 22 | 27 | 33 | 30 | 41 | 0 | 46 | 0 | 0 | 0 | 17 | 151 | 0 | 0 | 0 |  | 12 | 18 | 0 | 10 | 0 | 19 | 0 | 6 | 0 | 0 | 0 | 0 | 210 | 151 | 8 | 71 | 5 | 0 | 0 | 5 | 0 | 0 | 8 | 19 | 11 | 15 | 15 | 96 | 73 | 0 | 8 | 1 | 30 | 21 | 51 | 20 | 100 | 0 | 67 | 0 | 0 | 0 | 18 | 32 | 10 | 0 | 16 | 8 | 0 | 98 | 0 | 0 | 48 | 0 | 43 | 12 | 12 | 17 | 150 | 373 | 49 | 88 | 17 | 2 | 16 | 17 | 54 | 17 | 98 | 12 | 400 | 55 | 30 | 17 | 89 | 0 | 17 | 20 | 35 | 17 | 292 | 0 | 0 |  | 891 | 0 | 175 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 158 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 8 | 0 | 19 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 248 | 75 | 0 | 35 | 0 | 33 | 0 | 2 | 35 | 310 | 175 | 0 | 0 | 3 | 48 | 0 | 0 | 0 | 534 | 16 | 0 | 0 |  | 4951 | 3197 | 8148 | 3276 | 891 | 1143 | 0 | 1508 | 1004 | 46 | 0 | 50 | 96 | 134 | 254.3547 | 89.74
10:00 | 0 | 0 | 0 | 180 | 200 | 22 | 0 | 271 | 0 |  | 0 | 225 | 205 | 33 | 0 | 45 | 0 | 0 | 0 | 40 | 8 | 32 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 16 | 22 | 27 | 33 | 16 | 41 | 0 | 46 | 0 | 0 | 0 | 17 | 151 | 0 | 0 | 0 |  | 12 | 23 | 0 | 10 | 0 | 19 | 0 | 2 | 0 | 0 | 0 | 0 | 200 | 151 | 8 | 63 | 5 | 0 | 0 | 5 | 0 | 0 | 8 | 22 | 11 | 14 | 15 | 100 | 41 | 0 | 8 | 2 | 30 | 21 | 50 | 40 | 100 | 0 | 66 | 0 | 0 | 0 | 18 | 32 | 10 | 0 | 16 | 8 | 0 | 98 | 0 | 0 | 48 | 0 | 43 | 18 | 12 | 17 | 150 | 421 | 49 | 88 | 17 | 3 | 16 | 17 | 54 | 17 | 98 | 12 | 400 | 55 | 39 | 17 | 89 | 0 | 17 | 26 | 35 | 17 | 292 | 0 | 0 |  | 890 | 0 | 170 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 117 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 8 | 0 | 17 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 241 | 75 | 0 | 35 | 0 | 35 | 0 | 4 | 35 | 290 | 175 | 0 | 0 | 4 | 65 | 0 | 0 | 0 | 534 | 22 | 0 | 0 |  | 4992 | 3154 | 8146 | 3210 | 890 | 1147 | 0 | 1531 | 984 | 46 | 0 | 55 | 100 | 183 | 306.8845 | 89.74
11:00 | 0 | 0 | 0 | 180 | 200 | 22 | 0 | 267 | 0 |  | 0 | 225 | 210 | 55 | 0 | 45 | 0 | 0 | 0 | 60 | 8 | 32 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 16 | 23 | 26 | 33 | 21 | 41 | 0 | 46 | 0 | 0 | 0 | 17 | 151 | 0 | 0 | 0 |  | 12 | 32 | 0 | 10 | 0 | 19 | 0 | 2 | 0 | 0 | 0 | 0 | 200 | 152 | 8 | 64 | 5 | 0 | 0 | 5 | 0 | 0 | 8 | 22 | 11 | 14 | 15 | 106 | 36 | 0 | 8 | 2 | 30 | 21 | 50 | 40 | 90 | 0 | 63 | 0 | 0 | 0 | 18 | 32 | 10 | 0 | 22 | 8 | 90 | 98 | 300 | 100 | 48 | 99 | 43 | 18 | 12 | 17 | 150 | 414 | 49 | 88 | 17 | 4 | 208 | 17 | 54 | 17 | 105 | 12 | 397 | 55 | 45 | 84 | 89 | 0 | 17 | 30 | 44 | 17 | 292 | 0 | 0 |  | 891 | 0 | 160 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 8 | 0 | 16 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 224 | 75 | 0 | 35 | 0 | 34 | 0 | 5 | 35 | 260 | 174 | 0 | 0 | 5 | 75 | 0 | 0 | 0 | 539 | 29 | 0 | 0 |  | 5910 | 3114 | 9024 | 3185 | 891 | 1124 | 589 | 1847 | 959 | 46 | 0 | 64 | 106 | 213 | 4.6079 | 89.74
12:00 | 0 | 0 | 0 | 180 | 200 | 22 | 0 | 269 | 0 |  | 0 | 225 | 210 | 59 | 0 | 45 | 0 | 0 | 0 | 65 | 8 | 32 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 23 | 23 | 33 | 26 | 41 | 0 | 46 | 0 | 0 | 0 | 17 | 148 | 0 | 0 | 0 |  | 12 | 31 | 0 | 10 | 0 | 19 | 0 | 2 | 0 | 0 | 0 | 0 | 205 | 152 | 8 | 64 | 5 | 0 | 0 | 5 | 0 | 4 | 8 | 22 | 11 | 14 | 15 | 112 | 37 | 0 | 8 | 2 | 30 | 30 | 50 | 40 | 90 | 0 | 62 | 0 | 0 | 0 | 18 | 32 | 10 | 0 | 22 | 8 | 160 | 98 | 300 | 99 | 58 | 98 | 43 | 16 | 12 | 17 | 150 | 414 | 58 | 88 | 17 | 4 | 230 | 17 | 54 | 17 | 97 | 12 | 394 | 55 | 43 | 90 | 89 | 0 | 17 | 30 | 111 | 17 | 242 | 0 | 0 |  | 891 | 0 | 155 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 8 | 0 | 16 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 223 | 75 | 0 | 35 | 0 | 34 | 0 | 6 | 35 | 260 | 174 | 0 | 0 | 5 | 76 | 0 | 0 | 0 | 546 | 30 | 0 | 0 |  | 6063 | 3183 | 9246 | 3201 | 891 | 1124 | 657 | 1970 | 966 | 46 | 0 | 67 | 112 | 212 | 51.6082 | 89.73
13:00 | 0 | 0 | 0 | 180 | 200 | 22 | 0 | 295 | 0 |  | 0 | 225 | 240 | 68 | 0 | 34 | 0 | 0 | 0 | 70 | 8 | 48 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 23 | 24 | 33 | 26 | 41 | 0 | 46 | 0 | 0 | 0 | 17 | 150 | 0 | 0 | 0 |  | 12 | 31 | 0 | 10 | 0 | 19 | 0 | 2 | 0 | 0 | 0 | 0 | 320 | 152 | 8 | 64 | 5 | 3 | 0 | 5 | 0 | 12 | 8 | 22 | 11 | 14 | 15 | 114 | 35 | 0 | 8 | 2 | 29 | 30 | 53 | 40 | 90 | 0 | 65 | 0 | 0 | 0 | 18 | 32 | 10 | 0 | 22 | 8 | 160 | 98 | 298 | 98 | 58 | 99 | 43 | 16 | 12 | 17 | 150 | 414 | 59 | 88 | 17 | 2 | 220 | 17 | 54 | 17 | 104 | 12 | 394 | 55 | 42 | 90 | 89 | 0 | 17 | 29 | 115 | 17 | 218 | 0 | 0 |  | 891 | 0 | 155 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 8 | 0 | 15 | 0 | 11 | 0 | 0 | 143 | 0 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219 | 75 | 0 | 35 | 0 | 34 | 0 | 6 | 35 | 260 | 174 | 0 | 0 | 5 | 71 | 0 | 0 | 0 | 576 | 27 | 0 | 0 |  | 6244 | 3207 | 9451 | 3327 | 891 | 1155 | 655 | 1993 | 979 | 46 | 0 | 91 | 114 | 200 | 0 | 89.73
14:00 | 0 | 0 | 0 | 180 | 200 | 22 | 0 | 306 | 0 |  | 0 | 225 | 235 | 65 | 0 | 45 | 0 | 0 | 0 | 78 | 8 | 32 | 0 | 0 | 0 | 0 | 17 | 17 | 35 | 19 | 23 | 24 | 33 | 26 | 41 | 0 | 46 | 0 | 0 | 0 | 17 | 150 | 0 | 0 | 0 |  | 12 | 31 | 0 | 10 | 0 | 19 | 0 | 3 | 0 | 0 | 0 | 0 | 320 | 151 | 8 | 65 | 5 | 5 | 0 | 5 | 0 | 28 | 8 | 22 | 5 | 15 | 15 | 118 | 32 | 0 | 8 | 2 | 29 | 30 | 50 | 40 | 90 | 0 | 63 | 0 | 0 | 0 | 18 | 32 | 10 | 0 | 22 | 8 | 160 | 98 | 156 | 0 | 58 | 100 | 45 | 12 | 12 | 17 | 150 | 414 | 52 | 88 | 17 | 1 | 230 | 17 | 54 | 17 | 106 | 12 | 400 | 55 | 35 | 108 | 89 | 0 | 17 | 25 | 67 | 17 | 217 | 0 | 0 |  | 892 | 0 | 155 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 8 | 0 | 15 | 0 | 11 | 0 | 0 | 163 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 56 | 0 | 35 | 0 | 34 | 0 | 5 | 35 | 260 | 174 | 0 | 0 | 4 | 57 | 0 | 0 | 0 | 553 | 20 | 0 | 0 |  | 5969 | 3171 | 9140 | 3336 | 892 | 1155 | 416 | 1949 | 976 | 46 | 0 | 91 | 118 | 161 | 0 | 89.74
15:00 | 0 | 0 | 0 | 180 | 200 | 22 | 0 | 308 | 0 |  | 0 | 225 | 245 | 60 | 0 | 45 | 0 | 0 | 0 | 78 | 8 | 32 | 0 | 0 | 0 | 0 | 17 | 17 | 35 | 19 | 23 | 24 | 33 | 26 | 41 | 0 | 46 | 0 | 0 | 0 | 17 | 151 | 0 | 0 | 0 |  | 12 | 31 | 0 | 10 | 0 | 18 | 0 | 2 | 0 | 0 | 0 | 0 | 305 | 216 | 8 | 64 | 5 | 5 | 0 | 5 | 0 | 32 | 8 | 22 | 8 | 16 | 15 | 116 | 31 | 0 | 7 | 1 | 30 | 30 | 50 | 40 | 90 | 0 | 61 | 0 | 0 | 0 | 18 | 32 | 10 | 0 | 22 | 8 | 162 | 98 | 253 | 0 | 58 | 100 | 44 | 9 | 12 | 17 | 119 | 421 | 58 | 88 | 17 | 1 | 230 | 22 | 60 | 17 | 100 | 12 | 400 | 55 | 25 | 108 | 89 | 0 | 17 | 17 | 18 | 17 | 144 | 0 | 0 |  | 891 | 0 | 155 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 8 | 0 | 15 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 215 | 35 | 0 | 35 | 0 | 34 | 0 | 4 | 35 | 260 | 164 | 0 | 0 | 2 | 40 | 0 | 0 | 0 | 574 | 14 | 0 | 0 |  | 5968 | 3088 | 9056 | 3325 | 891 | 1142 | 515 | 1819 | 994 | 46 | 0 | 95 | 116 | 113 | 0 | 89.73
16:00 | 0 | 0 | 0 | 180 | 200 | 22 | 0 | 298 | 0 |  | 0 | 225 | 235 | 57 | 0 | 45 | 0 | 0 | 0 | 70 | 8 | 32 | 0 | 0 | 0 | 0 | 17 | 17 | 35 | 19 | 23 | 24 | 33 | 26 | 41 | 0 | 46 | 0 | 0 | 0 | 17 | 151 | 0 | 0 | 0 |  | 12 | 33 | 0 | 10 | 0 | 18 | 0 | 2 | 0 | 0 | 0 | 0 | 320 | 214 | 8 | 64 | 5 | 5 | 0 | 5 | 0 | 37 | 8 | 22 | 8 | 16 | 15 | 110 | 33 | 0 | 7 | 0 | 30 | 30 | 50 | 40 | 90 | 0 | 64 | 0 | 0 | 0 | 18 | 32 | 10 | 0 | 22 | 8 | 0 | 98 | 0 | 0 | 58 | 0 | 44 | 3 | 12 | 17 | 79 | 412 | 49 | 88 | 27 | 0 | 230 | 36 | 73 | 17 | 107 | 15 | 398 | 59 | 8 | 162 | 89 | 0 | 17 | 7 | 17 | 17 | 144 | 18 | 0 |  | 885 | 0 | 155 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 8 | 0 | 16 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 206 | 35 | 0 | 35 | 0 | 34 | 0 | 1 | 35 | 250 | 162 | 0 | 0 | 0 | 17 | 30 | 0 | 0 | 503 | 5 | 0 | 0 |  | 5468 | 2984 | 8452 | 3323 | 885 | 1121 | 0 | 1893 | 913 | 46 | 18 | 102 | 110 | 41 | 228.5506 | 89.72
17:00 | 0 | 0 | 0 | 180 | 200 | 22 | 0 | 290 | 0 |  | 0 | 225 | 230 | 51 | 0 | 45 | 0 | 0 | 0 | 70 | 8 | 32 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 23 | 24 | 33 | 26 | 41 | 0 | 46 | 0 | 0 | 0 | 17 | 151 | 0 | 0 | 0 |  | 9 | 39 | 19 | 10 | 0 | 18 | 0 | 2 | 0 | 0 | 0 | 0 | 305 | 220 | 8 | 64 | 23 | 5 | 0 | 5 | 0 | 37 | 8 | 22 | 8 | 16 | 15 | 112 | 33 | 0 | 7 | 0 | 30 | 30 | 53 | 40 | 90 | 0 | 40 | 40 | 0 | 0 | 18 | 32 | 10 | 0 | 23 | 8 | 0 | 230 | 0 | 0 | 48 | 0 | 45 | 0 | 12 | 28 | 72 | 364 | 50 | 88 | 105 | 0 | 230 | 36 | 73 | 34 | 111 | 12 | 335 | 72 | 0 | 162 | 89 | 0 | 17 | 1 | 37 | 17 | 117 | 0 | 0 |  | 885 | 0 | 155 | 0 | 45 | 0 | 0 | 0 | 3 | 20 | 0 | 160 | 16 | 0 | 0 | 0 | 0 | 0 | 4 | 25 | 0 | 34 | 10 | 8 | 0 | 16 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 212 | 25 | 0 | 45 | 0 | 49 | 0 | 0 | 35 | 250 | 142 | 0 | 0 | 0 | 1 | 72 | 0 | 0 | 504 | 0 | 0 | 0 |  | 5607 | 3076 | 8683 | 3142 | 885 | 1148 | 0 | 2245 | 914 | 46 | 0 | 189 | 112 | 2 | 292.1393 | 89.72
18:00 | 0 | 0 | 0 | 180 | 200 | 22 | 0 | 285 | 0 |  | 0 | 225 | 215 | 58 | 0 | 45 | 0 | 0 | 0 | 70 | 24 | 32 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 22 | 23 | 24 | 33 | 26 | 49 | 0 | 46 | 0 | 0 | 0 | 17 | 151 | 0 | 0 | 0 |  | 4 | 39 | 51 | 10 | 0 | 28 | 0 | 4 | 0 | 0 | 0 | 0 | 305 | 219 | 36 | 64 | 30 | 5 | 0 | 5 | 0 | 37 | 9 | 22 | 10 | 16 | 15 | 122 | 33 | 0 | 4 | 0 | 30 | 30 | 53 | 42 | 90 | 0 | 64 | 86 | 0 | 0 | 18 | 33 | 10 | 0 | 24 | 8 | 148 | 247 | 300 | 0 | 58 | 100 | 60 | 0 | 12 | 50 | 74 | 422 | 58 | 105 | 105 | 0 | 280 | 36 | 73 | 99 | 111 | 12 | 396 | 72 | 0 | 162 | 89 | 0 | 17 | 0 | 111 | 17 | 119 | 0 | 0 |  | 885 | 0 | 155 | 0 | 54 | 0 | 0 | 0 | 43 | 76 | 0 | 158 | 18 | 0 | 0 | 0 | 0 | 24 | 4 | 75 | 0 | 34 | 40 | 8 | 30 | 17 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 188 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 212 | 75 | 0 | 92 | 0 | 49 | 0 | 0 | 35 | 280 | 210 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 538 | 0 | 0 | 0 |  | 6760 | 3586 | 10346 | 3285 | 885 | 1283 | 588 | 2708 | 978 | 46 | 0 | 451 | 122 | 0 | 188.0013 | 89.72
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 200 | 22 | 0 | 287 | 0 |  | 0 | 225 | 220 | 59 | 0 | 45 | 0 | 0 | 0 | 78 | 33 | 32 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 23 | 24 | 33 | 26 | 49 | 0 | 46 | 0 | 0 | 0 | 17 | 151 | 0 | 0 | 0 |  | 12 | 46 | 51 | 10 | 0 | 44 | 0 | 4 | 0 | 0 | 0 | 0 | 305 | 220 | 36 | 64 | 30 | 5 | 0 | 5 | 0 | 37 | 11 | 19 | 10 | 25 | 15 | 120 | 48 | 0 | 7 | 0 | 30 | 30 | 53 | 42 | 90 | 0 | 62 | 86 | 0 | 0 | 18 | 33 | 10 | 0 | 24 | 8 | 10 | 247 | 50 | 0 | 58 | 100 | 63 | 0 | 12 | 100 | 74 | 420 | 59 | 105 | 105 | 0 | 281 | 36 | 73 | 99 | 115 | 12 | 400 | 63 | 0 | 162 | 105 | 0 | 17 | 0 | 115 | 17 | 20 | 0 | 0 |  | 885 | 0 | 155 | 0 | 82 | 0 | 0 | 0 | 33 | 40 | 0 | 168 | 18 | 0 | 0 | 0 | 0 | 33 | 17 | 84 | 0 | 34 | 40 | 8 | 34 | 19 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219 | 75 | 0 | 94 | 0 | 49 | 0 | 0 | 35 | 380 | 211 | 0 | 0 | 0 | 0 | 113 | 0 | 0 | 550 | 0 | 0 | 0 |  | 6441 | 3735 | 10176 | 3220 | 885 | 1298 | 160 | 2910 | 1090 | 46 | 0 | 447 | 120 | 0 | 82.0202 | 89.71
19:30 | 0 | 0 | 0 | 180 | 200 | 22 | 0 | 292 | 0 |  | 0 | 225 | 216 | 66 | 0 | 45 | 0 | 0 | 0 | 78 | 33 | 32 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 23 | 24 | 33 | 26 | 49 | 0 | 46 | 0 | 0 | 0 | 17 | 151 | 0 | 0 | 0 |  | 12 | 46 | 51 | 10 | 0 | 44 | 0 | 5 | 0 | 0 | 0 | 0 | 305 | 218 | 36 | 63 | 40 | 5 | 0 | 5 | 0 | 37 | 16 | 19 | 10 | 25 | 15 | 122 | 58 | 0 | 7 | 0 | 30 | 30 | 53 | 42 | 90 | 0 | 62 | 86 | 0 | 0 | 18 | 32 | 10 | 0 | 16 | 8 | 10 | 247 | 110 | 0 | 58 | 75 | 70 | 0 | 12 | 196 | 74 | 422 | 59 | 105 | 105 | 0 | 122 | 36 | 73 | 99 | 75 | 12 | 400 | 55 | 0 | 162 | 107 | 0 | 17 | 0 | 115 | 17 | 16 | 0 | 0 |  | 886 | 0 | 160 | 0 | 57 | 0 | 0 | 0 | 33 | 40 | 0 | 183 | 19 | 0 | 0 | 0 | 0 | 33 | 19 | 84 | 0 | 34 | 40 | 8 | 35 | 22 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219 | 75 | 0 | 94 | 0 | 49 | 0 | 0 | 35 | 390 | 221 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 556 | 0 | 0 | 0 |  | 6396 | 3766 | 10162 | 3252 | 886 | 1308 | 195 | 2797 | 1106 | 46 | 0 | 450 | 122 | 0 | 63.5887 | 0
20:00 | 0 | 0 | 0 | 180 | 200 | 22 | 0 | 290 | 0 |  | 0 | 225 | 215 | 67 | 0 | 45 | 0 | 0 | 0 | 78 | 33 | 32 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 23 | 24 | 33 | 26 | 49 | 0 | 46 | 0 | 0 | 0 | 17 | 151 | 0 | 0 | 0 |  | 12 | 40 | 51 | 10 | 0 | 44 | 0 | 10 | 0 | 0 | 0 | 0 | 305 | 220 | 63 | 66 | 44 | 5 | 0 | 5 | 0 | 37 | 16 | 22 | 10 | 30 | 15 | 116 | 63 | 0 | 7 | 0 | 30 | 30 | 53 | 42 | 90 | 0 | 62 | 86 | 0 | 0 | 18 | 33 | 10 | 0 | 16 | 8 | 10 | 247 | 103 | 0 | 58 | 75 | 72 | 0 | 12 | 195 | 74 | 421 | 59 | 105 | 105 | 0 | 51 | 36 | 73 | 99 | 75 | 12 | 400 | 55 | 0 | 162 | 107 | 0 | 17 | 0 | 115 | 17 | 2 | 0 | 0 |  | 893 | 0 | 160 | 0 | 16 | 0 | 0 | 0 | 31 | 40 | 0 | 184 | 19 | 0 | 0 | 0 | 0 | 33 | 20 | 43 | 0 | 34 | 40 | 8 | 34 | 22 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 226 | 35 | 0 | 94 | 0 | 49 | 0 | 0 | 35 | 390 | 221 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 561 | 0 | 0 | 0 |  | 6365 | 3661 | 10026 | 3257 | 893 | 1347 | 188 | 2667 | 1111 | 46 | 0 | 401 | 116 | 0 | 45.1572 | 89.71
21:00 | 0 | 0 | 0 | 180 | 200 | 22 | 0 | 293 | 0 |  | 0 | 225 | 220 | 65 | 0 | 45 | 0 | 0 | 0 | 78 | 33 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 55 | 19 | 23 | 24 | 33 | 26 | 49 | 0 | 46 | 0 | 0 | 0 | 17 | 151 | 0 | 0 | 0 |  | 12 | 39 | 51 | 10 | 0 | 44 | 0 | 17 | 0 | 0 | 0 | 0 | 305 | 220 | 110 | 71 | 44 | 5 | 0 | 5 | 0 | 37 | 8 | 22 | 10 | 33 | 15 | 118 | 104 | 0 | 8 | 0 | 30 | 30 | 53 | 42 | 90 | 0 | 64 | 86 | 0 | 0 | 18 | 32 | 10 | 0 | 24 | 8 | 10 | 246 | 230 | 0 | 58 | 56 | 72 | 0 | 12 | 87 | 75 | 421 | 59 | 105 | 105 | 0 | 51 | 36 | 73 | 24 | 75 | 12 | 400 | 55 | 0 | 162 | 107 | 0 | 17 | 0 | 115 | 17 | 13 | 0 | 0 |  | 893 | 0 | 160 | 0 | 16 | 0 | 0 | 0 | 31 | 40 | 0 | 183 | 19 | 0 | 0 | 0 | 0 | 33 | 20 | 43 | 0 | 34 | 32 | 8 | 0 | 22 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 35 | 0 | 94 | 0 | 34 | 0 | 0 | 35 | 400 | 217 | 0 | 0 | 0 | 0 | 95 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6340 | 3028 | 9368 | 3331 | 893 | 1400 | 296 | 2382 | 560 | 46 | 0 | 342 | 118 | 0 | 0 | 89.71
22:00 | 0 | 0 | 0 | 180 | 200 | 22 | 0 | 298 | 0 |  | 0 | 225 | 220 | 74 | 0 | 45 | 0 | 0 | 0 | 78 | 33 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 23 | 24 | 33 | 28 | 49 | 0 | 46 | 0 | 0 | 0 | 17 | 151 | 0 | 0 | 0 |  | 12 | 39 | 51 | 10 | 0 | 35 | 0 | 21 | 0 | 0 | 0 | 0 | 310 | 222 | 110 | 70 | 44 | 5 | 0 | 5 | 0 | 37 | 8 | 22 | 10 | 33 | 15 | 112 | 110 | 0 | 8 | 0 | 30 | 30 | 53 | 42 | 90 | 0 | 64 | 86 | 0 | 0 | 18 | 32 | 10 | 0 | 24 | 8 | 10 | 246 | 101 | 0 | 58 | 52 | 72 | 0 | 12 | 51 | 75 | 419 | 59 | 105 | 105 | 0 | 51 | 36 | 73 | 17 | 75 | 12 | 400 | 55 | 0 | 162 | 107 | 0 | 17 | 0 | 115 | 17 | 11 | 0 | 0 |  | 893 | 0 | 170 | 0 | 87 | 0 | 0 | 0 | 31 | 40 | 0 | 183 | 19 | 0 | 0 | 0 | 0 | 33 | 20 | 8 | 0 | 34 | 16 | 8 | 0 | 22 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 85 | 0 | 0 | 235 | 36 | 0 | 94 | 0 | 34 | 0 | 0 | 35 | 380 | 221 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6157 | 3117 | 9274 | 3355 | 893 | 1418 | 248 | 2371 | 540 | 46 | 0 | 291 | 112 | 0 | 0 | 89.7
23:00 | 0 | 0 | 0 | 180 | 200 | 22 | 0 | 299 | 0 |  | 0 | 225 | 235 | 73 | 0 | 45 | 0 | 0 | 0 | 78 | 33 | 16 | 0 | 0 | 0 | 0 | 17 | 17 | 35 | 19 | 23 | 0 | 33 | 30 | 50 | 0 | 46 | 0 | 0 | 0 | 17 | 151 | 0 | 0 | 0 |  | 12 | 39 | 51 | 10 | 0 | 20 | 0 | 24 | 0 | 0 | 0 | 0 | 310 | 202 | 112 | 71 | 44 | 5 | 0 | 5 | 0 | 37 | 8 | 22 | 10 | 33 | 15 | 114 | 113 | 0 | 8 | 0 | 30 | 30 | 53 | 42 | 90 | 0 | 68 | 86 | 0 | 0 | 18 | 32 | 10 | 0 | 24 | 8 | 10 | 158 | 67 | 0 | 58 | 50 | 59 | 0 | 12 | 51 | 73 | 419 | 59 | 105 | 51 | 0 | 68 | 36 | 63 | 17 | 75 | 12 | 400 | 55 | 0 | 140 | 107 | 0 | 17 | 0 | 48 | 17 | 9 | 0 | 0 |  | 893 | 0 | 180 | 0 | 96 | 0 | 0 | 0 | 31 | 40 | 0 | 183 | 18 | 0 | 0 | 0 | 0 | 33 | 19 | 0 | 0 | 34 | 16 | 8 | 0 | 22 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 86 | 0 | 0 | 247 | 66 | 0 | 50 | 0 | 34 | 0 | 0 | 35 | 390 | 221 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5836 | 3135 | 8971 | 3330 | 893 | 1449 | 213 | 2094 | 550 | 46 | 0 | 282 | 114 | 0 | 0 | 89.7
24:00 | 0 | 0 | 0 | 180 | 200 | 22 | 0 | 305 | 0 |  | 0 | 225 | 235 | 72 | 0 | 45 | 0 | 0 | 0 | 42 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 17 | 35 | 19 | 25 | 24 | 33 | 30 | 49 | 0 | 46 | 0 | 0 | 0 | 17 | 151 | 0 | 0 | 0 |  | 12 | 39 | 51 | 10 | 0 | 19 | 0 | 25 | 0 | 0 | 0 | 0 | 310 | 168 | 112 | 71 | 44 | 5 | 0 | 5 | 0 | 37 | 8 | 22 | 10 | 33 | 15 | 108 | 113 | 0 | 8 | 0 | 30 | 30 | 53 | 42 | 90 | 0 | 68 | 86 | 0 | 0 | 18 | 32 | 10 | 0 | 24 | 8 | 10 | 88 | 60 | 0 | 48 | 50 | 54 | 0 | 12 | 24 | 68 | 419 | 49 | 105 | 17 | 0 | 69 | 36 | 60 | 17 | 75 | 12 | 400 | 55 | 0 | 72 | 107 | 0 | 17 | 0 | 34 | 17 | 12 | 0 | 0 |  | 784 | 0 | 180 | 0 | 99 | 0 | 0 | 0 | 31 | 40 | 0 | 183 | 17 | 0 | 0 | 0 | 0 | 32 | 19 | 0 | 0 | 34 | 16 | 8 | 0 | 21 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 188 | 0 | 0 | 0 | 0 | 87 | 0 | 0 | 248 | 76 | 0 | 50 | 0 | 34 | 0 | 0 | 35 | 390 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5516 | 2963 | 8479 | 3332 | 784 | 1448 | 207 | 1723 | 550 | 46 | 0 | 281 | 108 | 0 | 0 | 89.7
KWH | 0 | 0 | 0 | 4362750 | 4780500 | 559318 | 0 | 7053310 | 0 |  | 0 | 4925300 | 5164044 | 1055040 | 0 | 1094250 | 0 | 0 | 0 | 1257629 | 330624 | 544800 | 0 | 0 | 0 | 0 | 515124 | 731649 | 741451 | 428616 | 600000 | 572940 | 806760 | 645400 | 931771 | 0 | 1108500 | 0 | 0 | 0 | 419279 | 3565403 | 0 | 0 | 0 |  | 286320 | 626544 | 471763 | 265800 | 0 | 563520 | 0 | 314880 | 0 | 0 | 0 | 922700 | 6768000 | 4454000 | 669090 | 1631530 | 388584 | 126720 | 0 | 16869 | 0 | 391584 | 211656 | 501017 | 232020 | 595000 | 355470 | 2590080 | 1677120 | 0 | 176256 | 13200 | 716000 | 562440 | 1155000 | 1002672 | 2203609 | 0 | 1471392 | 645120 | 0 | 0 | 425000 | 763840 | 244080 | 0 | 529992 | 192384 | 1022016 | 3163964 | 2270301 | 386279 | 1202400 | 1118701 | 1220256 | 98820 | 295680 | 863520 | 2868727 | 9654000 | 1257600 | 2174400 | 992763 | 19320 | 2545473 | 632596 | 1484539 | 706800 | 2341920 | 306240 | 9302500 | 1401600 | 283910 | 1926720 | 2351018 | 0 | 444600 | 198930 | 1421760 | 433440 | 3310200 | 18400 | 0 |  | 19920000 | 0 | 4456512 | 0 | 773760 | 0 | 0 | 0 | 202080 | 308480 | 0 | 3992438 | 383384 | 0 | 0 | 0 | 0 | 212577 | 99731 | 233424 | 0 | 471366 | 206265 | 133291 | 103396 | 439680 | 0 | 237492 | 0 | 0 | 3895700 | 0 | 0 | 4698691 | 0 | 0 | 0 | 0 | 271680 | 0 | 0 | 5801018 | 1226208 | 0 | 1206048 | 0 | 761136 | 0 | 35123 | 907968 | 8187000 | 4567800 | 0 | 0 | 33600 | 486720 | 614016 | 0 | 0 | 10846000 | 173397 | 0 | 0 |  | 134075103 | 75885981 | 209961084 | 80066417 | 19920000 | 28982424 | 5068977 | 44533922 | 22928700 | 1108500 | 18400 | 3400644 | 2590080 | 1343020 | 0
Fuel Cost | 0 | 0 | 0 | 6500497.5 | 5354160 | 743892.94 | 0 | 7405975.5 | 0 |  | 0 | 5368577 | 5732088.84 | 11795347.2 | 0 | 14498812.5 | 0 | 0 | 0 | 18386535.98 | 4651879.68 | 8831208 | 0 | 0 | 0 | 0 | 6552377.28 | 9877261.5 | 9942857.91 | 321462 | 450000 | 0 | 0 | 0 | 15849424.71 | 0 | 299295 | 0 | 0 | 0 | 6855211.65 | 3708019.12 | 0 | 0 | 0 |  | 3736476 | 10450753.92 | 8029406.26 | 3590958 | 0 | 6519926.4 | 0 | 1048550.4 | 0 | 0 | 0 | 1024197 | 7377120 | 5166640 | 863126.1 | 1990466.6 | 439099.92 | 188812.8 | 0 | 28171.23 | 0 | 6762655.68 | 2846773.2 | 686393.29 | 174015 | 1041250 | 266602.5 | 18596774.4 | 1828060.8 | 0 | 239708.16 | 210408 | 980920 | 742420.8 | 2009700 | 1734622.56 | 2534150.35 | 0 | 2854500.48 | 1470873.6 | 0 | 0 | 913750 | 1138121.6 | 483278.4 | 0 | 397494 | 146211.84 | 21421455.36 | 43188108.6 | 47585508.96 | 7984386.93 | 16208352 | 23123549.67 | 16900545.6 | 1155205.8 | 3051417.6 | 11795683.2 | 38068007.29 | 8881680 | 15292416 | 31441824 | 12558451.95 | 0 | 29883853.02 | 6888970.44 | 15780649.57 | 9591276 | 30187348.8 | 3607507.2 | 8558300 | 18150720 | 4102499.5 | 24450076.8 | 26754584.84 | 0 | 5806476 | 2377213.5 | 21283747.2 | 5708404.8 | 0 | 0 | 0 |  | 59760000 | 0 | 4991293.44 | 0 | 8054841.6 | 0 | 0 | 0 | 3639460.8 | 5552640 | 0 | 4471530.56 | 743764.96 | 0 | 0 | 0 | 0 | 3564916.29 | 1744295.19 | 3650751.36 | 0 | 7805820.96 | 3487941.15 | 1816756.33 | 1744290.52 | 910137.6 | 0 | 179781.444 | 0 | 0 | 20608253 | 0 | 0 | 5450481.56 | 0 | 0 | 0 | 0 | 5699846.4 | 0 | 0 | 5743007.82 | 16480235.52 | 0 | 14267547.84 | 0 | 9666427.2 | 0 | 388109.15 | 11022731.52 | 73764870 | 4659156 | 0 | 0 | 380016 | 5709225.6 | 9412865.28 | 0 | 0 | 0 | 0 | 0 | 0 |  | 753425494.23 | 295370995.094 | 1048796489.324 | 82542031.514 | 59760000 | 35400032.2 | 105814747.32 | 580229489.17 | 94373123 | 299295 | 0 | 57458319.17 | 18596774.4 | 14322677.55 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 200 | 22 | 0 | 269 | 0 |  | 0 | 225 | 210 | 59 | 0 | 45 | 0 | 0 | 0 | 65 | 8 | 32 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 23 | 23 | 33 | 26 | 41 | 0 | 46 | 0 | 0 | 0 | 17 | 148 | 0 | 0 | 0 |  | 12 | 31 | 0 | 10 | 0 | 19 | 0 | 2 | 0 | 0 | 0 | 0 | 205 | 152 | 8 | 64 | 5 | 0 | 0 | 5 | 0 | 4 | 8 | 22 | 11 | 14 | 15 | 112 | 37 | 0 | 8 | 2 | 30 | 30 | 50 | 40 | 90 | 0 | 62 | 0 | 0 | 0 | 18 | 32 | 10 | 0 | 22 | 8 | 160 | 98 | 300 | 99 | 58 | 98 | 43 | 16 | 12 | 17 | 150 | 414 | 58 | 88 | 17 | 4 | 230 | 17 | 54 | 17 | 97 | 12 | 394 | 55 | 43 | 90 | 89 | 0 | 17 | 30 | 111 | 17 | 242 | 0 | 0 |  | 891 | 0 | 155 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 8 | 0 | 16 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 223 | 75 | 0 | 35 | 0 | 34 | 0 | 6 | 35 | 260 | 174 | 0 | 0 | 5 | 76 | 0 | 0 | 0 | 546 | 30 | 0 | 0 |  | 9246 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 200 | 22 | 0 | 285 | 0 | 0 | 0 | 225 | 215 | 58 | 0 | 45 | 0 | 0 | 0 | 70 | 24 | 32 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 22 | 23 | 24 | 33 | 26 | 49 | 0 | 46 | 0 | 0 | 0 | 17 | 151 | 0 | 0 | 0 | 0 | 4 | 39 | 51 | 10 | 0 | 28 | 0 | 4 | 0 | 0 | 0 | 0 | 305 | 219 | 36 | 64 | 30 | 5 | 0 | 5 | 0 | 37 | 9 | 22 | 10 | 16 | 15 | 122 | 33 | 0 | 4 | 0 | 30 | 30 | 53 | 42 | 90 | 0 | 64 | 86 | 0 | 0 | 18 | 33 | 10 | 0 | 24 | 8 | 148 | 247 | 300 | 0 | 58 | 100 | 60 | 0 | 12 | 50 | 74 | 422 | 58 | 105 | 105 | 0 | 280 | 36 | 73 | 99 | 111 | 12 | 396 | 72 | 0 | 162 | 89 | 0 | 17 | 0 | 111 | 17 | 119 | 0 | 0 |  | 885 | 0 | 155 | 0 | 54 | 0 | 0 | 0 | 43 | 76 | 0 | 158 | 18 | 0 | 0 | 0 | 0 | 24 | 4 | 75 | 0 | 34 | 40 | 8 | 30 | 17 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 188 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 212 | 75 | 0 | 92 | 0 | 49 | 0 | 0 | 35 | 280 | 210 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 538 | 0 | 0 | 0 |  | 10346 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 200 | 22 | 0 | 290 | 0 | 0 | 0 | 225 | 220 | 80 | 0 | 45 | 0 | 0 | 0 | 80 | 80 | 32 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 16 | 22 | 24 | 33 | 25 | 50 | 0 | 46 | 0 | 0 | 0 | 17 | 151 | 0 | 0 | 0 | 0 | 12 | 32 | 51 | 10 | 0 | 44 | 0 | 20 | 0 | 0 | 0 | 0 | 250 | 200 | 0 | 80 | 0 | 0 | 0 | 5 | 0 | 32 | 16 | 22 | 11 | 33 | 15 | 165 | 72 | 0 | 8 | 0 | 30 | 30 | 51 | 40 | 90 | 0 | 66 | 86 | 0 | 0 | 18 | 32 | 10 | 0 | 24 | 8 | 100 | 285 | 150 | 50 | 57 | 50 | 64 | 0 | 12 | 200 | 100 | 400 | 58 | 105 | 105 | 0 | 290 | 36 | 74 | 99 | 113 | 12 | 400 | 55 | 0 | 162 | 107 | 0 | 17 |  | 115 | 17 | 400 |  |  |  | 910 | 0 | 0 | 0 | 114 | 0 | 0 | 0 | 40 | 75 | 8 | 180 | 19 | 0 | 0 | 0 | 0 | 34 | 29 | 85 | 0 | 34 | 40 | 43 | 35 | 22 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 160 |  | 0 | 0 | 0 | 50 | 0 | 0 | 280 | 75 | 0 | 95 | 0 | 34 | 0 | 0 | 95 | 622 | 220 |  | 0 |  |  | 113 | 0 |  | 540 |  | 0
Forecast for Day | 0 | 0 | 0 | 180 | 200 | 22 | 0 | 300 | 0 | 0 | 0 | 225 | 240 | 80 | 0 | 45 | 0 | 0 | 0 | 80 | 40 | 32 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 16 | 22 | 24 | 33 | 25 | 50 | 0 | 46 | 0 | 0 | 0 | 17 | 151 | 0 | 0 | 0 | 0 | 12 | 28 | 0 | 10 | 0 | 26 | 0 | 20 | 0 | 0 | 0 | 0 | 200 | 170 | 0 | 80 | 0 | 0 | 0 | 5 | 0 | 21 | 8 | 22 | 11 | 33 | 15 | 143 | 32 | 0 | 8 | 1.6 | 30 | 30 | 51 | 40 | 90 | 0 | 66 | 0 | 0 | 0 | 18 | 32 | 10 | 0 | 21 | 8 | 0 | 95 | 0 | 0 | 48 | 0 | 53 | 20 | 12 | 17 | 75 | 400 | 49 | 88 | 17 | 5 | 69 | 17 | 53 | 17 | 113 | 12 | 400 | 55 | 50 | 90 | 107 | 0 | 17 | 30 | 34 | 17 | 400 |  |  |  | 717 | 0 | 0 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 43 | 0 | 20 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 55 | 0 | 35 | 0 | 34 | 0 | 8 | 50 | 622 | 200 |  | 0 | 6 | 100 | 0 | 0 |  | 150 | 30 | 0 | [5 empty] | g | h | o | c | h | t | s
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 200 | 22 | 0 | 323 | 0 | 0 | 0 | 225 | 260 | 13 | 0 | 45 | 0 | 0 | 0 | 30 | 8 | 32 | 0 | 0 | 0 | 0 | 17 | 18 | 17 | 19 | 23 | 27 | 25 | 31 | 19 | 0 | 46 | 0 | 0 | 0 | 8 | 151 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 10 | 0 | 19 | 0 | 36 | 0 | 0 | 0 | 0 | 230 | 219 | 8 | 83 | 44 | 5 | 0 | 5 | 0 | 0 | 8 | 22 | 8 | 33 | 15 | 80 | 74 | 0 | 8 | 1 | 30 | 30 | 53 | 42 | 90 | 0 | 70 | 0 | 0 | 0 | 18 | 33 | 0 | 0 | 21 | 8 | 0 | 97 | 0 | 0 | 47 | 0 | 53 | 8 | 12 | 17 | 46 | 411 | 49 | 34 | 17 | 1 | 69 | 17 | 54 | 17 | 50 | 12 | 400 | 54 | 15 | 17 | 107 | 0 | 17 | 11 | 35 | 17 | 323 | 0 | 0 | 0 | 656 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 16 | 0 | 20 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 291 | 74 | 0 | 34 | 0 | 34 | 0 | 1 | 0 | 300 | 180 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 |  |  |  | 109.0488 | 19.92 | 53.0219 | 22.9287 | 1.1085 | 2.5901 | 1.343
209.9611
| Minimum Generation |  | 7382 | 5:00
| Highest Generation |  | 10346 | 18:00
| Day Peak Generation |  | 9246 | 12:00
| Evening Peak Generation |  | 10346 | 18:00
| HVDC Max Flow |  | 893 | 20:00
| HVDC EvPeak Flow |  | 885 | 18:00
| Load factor L.F |  | 84.56% | [161 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2022-12-02
Till now the maximum generation is : - |  |  |  | 14782 | 21:00 | Hrs on | 2022-04-16
The Summary of Yesterday's |  |  | 2022-12-01 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 9246 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 6923
Evening Peak Generation : |  |  | 10346 | MW Hour : | 18:00 | Available Max Generation : |  | 11321
E.P. Demand (at gen end) : |  |  | 10550 | MW Hour : | 18:00 | Max Demand (Evening) : |  | 10000
Maximum Generation : |  |  | 10346 | MW Hour : | 18:00 | Reserve(Generation end) |  | 1321
Total Gen. (MKWH) : |  |  | 209.9611 | System Load Factor : | 84.56% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 850 | MW at | 22:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2022-12-02
Actual : |  | 89.68 | Ft.(MSL) , | Rule curve : | 106 | Ft.( MSL )
Gas Consumed : |  | Total = | 888.48 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 117942063.714
: |  |  | Coal : | 94373123 | Oil : | 743502555.66 | Total : | 955817742.374
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 112 | 2688:00 | 3362.0451 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 952.4089 |  |  | 0 | 0%
Khulna Area |  | 0 | 0:00 | 1257.1007 |  |  | 0 | 0%
Rajshahi Area |  | 0 | 0:00 | 1115.3614 |  |  | 0 | 0%
Cumilla Area |  | 0 | 0:00 | 949.4759 |  |  | 0 | 0%
Mymensingh Area |  | 76 | 1824:00 | 784.409 |  |  | 0 | 0%
Sylhet Area |  | 0 | 0:00 | 350.5967 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 285.7977 |  |  | 0 | 0%
Rangpur Area |  | 0 | 0:00 | 619.3421 |  |  | 0 | 0%
Total |  | 188 |  | 9676.5375 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1, 2
2) Ghorasal-3, 4
3) Ashuganj-5
4) Baghabari-71,100 MW
5) Raozan unit-1 & 2
6) Siddhirganj 210 MW .
7) Shajibazar 330 MW
8) Sirajganj-2
9) Bibiana-II 341 MW CCPP (Summit)
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
08:10 | 13:15 | Rajshahi 230/132/33kV S/S T-01 (406T) HT Scheduled S/D
08:17 | 15:45 | Noapara 132/33kV S/S BUS-B Scheduled S/D Due to Bus-B S/D Due To Annual Maintenance.
08:18 | 10:18 | Chattak-Sylhet 132 kV Ckt-2 Scheduled S/D from Chhatak 132/33kV end Due to Annual Maintenance.
08:30 | 12:54 | Juldah 132/33kV S/S 133/33 KV T-2 416T HT Scheduled S/D Due to Annual Maintenance.
08:31 | 10:22 | Chattak-Sylhet 132 kV Ckt-2 Scheduled S/D from Sylhet 132/33kV end Due to Annual Maintenance.
08:38 | 15:57 | Haripur-Sonargaon 132kV Ckt-1 Scheduled S/D from Sonargaon 132/33kV end Due to Annual maintenance
sonargaon-haripur ckt-01 and from Haripur 230/132kV end Due to Annual Maintenance.
08:46 | 16:33 | Chauddagram-Feni 132 kV Ckt-1 Scheduled S/D from Feni 132/33kV end Due to Chowddagram S/S Annual maintenance.
and from Chauddagram 132/33kV end Due to Annual Maintenance.
08:54 | 15:11 | Ashuganj-Kishoreganj 132kV Ckt-2 Scheduled S/D from Kishoreganj 132/33kV end Due toAnnual Maintenance.
09:02 |  | Postogola 132/33KV GT2 close.
09:09 | 16:23 | Dhamrai 132/33kV S/S Transformer-2 LT Scheduled S/D Due to 132/33 kV Transformer-2 OLTC Oil changing. | [5 empty] | 15 MW load interruption.
09:09 | 16:24 | Dhamrai 132/33kV S/S Transformer-2 HT Scheduled S/D Due to 132/33 kV Transformer-2 OLTC Oil changing.
09:10 | 16:16 | Dohazari-Sikalbaha 132 kV Ckt-2 Scheduled S/D from Shikalbaha 230/132kV end Due to Annual Maintanance and from
Dohazari 132/33kV end Due to Annual Maintenance.
09:15 |  | Uttara 132/33KV T1 SD for Annual Maintenance.
09:24 | 16:31 | Ashuganj-Brahmanbaria 132kV Ckt-2 Scheduled S/D from Brahmanbaria 132/33kV end Due to Annual Maintenance.
09:32 | 11:50 | Kaliakoir-Tongi 230kV Ckt-2 Scheduled S/D from Kaliakoir 400/230/132kV end Due to Relay Test and from Tongi 230/132/33kV end.
10:14 | 14:55 | Daudkandi 132/33kV S/S Titas 50 MW Power Plant Line Scheduled S/D Due to Annual Maintenance.
10:30 | 13:01 | Chattak-Sylhet 132 kV Ckt-1 Scheduled S/D from Chhatak 132/33kV end Due to Annual Maintenance(BUS-B) , and from
Sylhet 132/33kV end Due to Annual Maintenance.
10:36 | 13:12 | Bagerhat-Bhandaria 132 kV Ckt-1 Forced S/D from Bagerhat 132/33kV end Due to Tree trimming work.
10:54 |  | Ashugonj(N) ST sync.
11:07 | 13:22 | Sylhet 132/33kV S/S 150MW GT PS Scheduled S/D Due to IED Installation & Replacement.
11:40 | 12:36 | Haripur-Haripur (360MW) 230kV Ckt-1 Scheduled S/D from Haripur 230/132kV end Due to From Other End.
11:41 | 12:37 | Haripur-Haripur (360MW) 230kV Ckt-2 Scheduled S/D from Haripur 230/132kV end Due to From Other End.
12:01 | 13:36 | Bakulia-Sikalbaha 132 kV Ckt-1 Tripped from Shikalbaha 230/132kV end showing REL 670 relays and from Bakulia 132/33kV end.
12:15 | 13:25 | Kaliakoir-Kodda(300MW) 230kV Ckt-1 Scheduled S/D from Kaliakoir 400/230/132kV end Due to Relay test.
12:24 | 12:58 | Sylhet 132/33kV S/S 20 MW PP Scheduled S/D Due to IED Change . | [5 empty] | 16 MW load interruption.
12:24 | 13:07 | Halishahar 132/33kV S/S 403T(TR-1) LT Forced S/D Due to PDB work . | [5 empty] | 15 MW load interruption.
12:25 | 13:06 | Halishahar 132/33kV S/S 403T(TR-1) HT Forced S/D Due to PDB work .
13:14 | 13:37 | Siddhirganj 132/33kV S/S 120MW EGCB GT1 Forced S/D Due to Off Load Tap Change for EGCB .
13:32 |  | Rangpur-Tista Solar 132KV-1
13:45 |  | Rangpur-Tista Solar 132KV-2
| 14:31 | Hathazari 230/132/33kV S/S Shikolbaha-02 is restored.
| 14:41 | Shikalbaha 230/132kV S/S Hathazari-02 is restored.
14:44 | 15:48 | Naogaon 132/33kV S/S T-3 LT Forced S/D Due to Emergency maintenance work of arji noagaon 33 kv bus isolator on T3 33 kv bus. | [5 empty] | 20 MW load interruption.
14:45 | 15:45 | Naogaon 132/33kV S/S T-3 HT Forced S/D Due to Emergency maintenance work of arji noagaon 33 kv bus isolator on T3 33 kv bus.
14:49 | 16:38 | Tangail 132/33kV S/S Kaliakair-1 Scheduled S/D Due to Relay testing by SPMD . | [5 empty] | 40 MW load interruption.
14:54 | 16:37 | Kaliakoir-Tangail 132kV Ckt-1 Scheduled S/D from Kaliakoir 400/230/132kV end Due to Relay Test .
| 17:08 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-2(35/50 MVA) HT is restored.
| 17:08 | Kabirpur - Manikganj 132kV Ckt-2 is restored.
| 17:15 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-2(35/50 MVA) LT is restored.
17:24 | 18:08 | Beanibazar 132/33kV S/S 132KV Transformer TR-02 LT Tripped showing relay relays Due to 33 kV Beanibazar feeder trip | [5 empty] | 19 MW load interruption.
due to cat climbing on the feeder.
17:24 | 18:07 | Beanibazar 132/33kV S/S 132 KV Transformer TR-01 LT Tripped showing relay relays Due to 33 kV Beanibazar feeder trip
due to cat climbing on the feeder.
17:24 | 18:07 | Beanibazar 132/33kV S/S 132 KV Transformer TR-01 LT Tripped showing relay relays Due to 33 kV Beanibazar feeder trip
due to cat climbing on the feeder.
17:27 |  | Coxsbazar 132/33kV S/S T3 LT Tripped showing relay relays Due to Over Load. | [5 empty] | 60 MW load interruption.
17:58 | 18:02 | Shahjibazar 132/33kV S/S TR-02 LT Forced S/D Due to Load ontrol Purpose. | [5 empty] | 24 MW load interruption.
03:44 |  | Ashugonj North 360MW was shutdown.
06:00 | 06:23 | Cumilla(S) 132/33kV S/S TR-2 LT Tripped Due to 33 KV Kasba feeder fault. | [5 empty] | 22 MW load interruption.
07:28 |  | Khulna 225MW-Khulna central 132kV Ckt-1 & 2 was S/D for corrective maintenance.
07:48 |  | Kabirpur - Manikganj 132kV Ckt-2 Scheduled S/D from Manikganj 132/33kV end Due to Annual Maintenance and from
Kabirpur 132/33kV end.
07:48 |  | Manikganj 132/33kV S/S 132/33 kV Transformer GT-2(35/50 MVA) HT Scheduled S/D Due to Annual Maintenance .
7:48 |  | Manikganj 132/33kV S/S 132/33 kV Transformer GT-2(35/50 MVA) LT Scheduled S/D Due to Annual Maintenance .
07:56 |  | Naogaon 132/33kV S/S T-2 LT Scheduled S/D Due to Annual Maintenance.
07:58 |  | Naogaon 132/33kV S/S T-2 HT Scheduled S/D Due to Annual Maintenance.
| 2:46 | Ashuganj 420 MW CCPP(East) GT was sync.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2022-12-01 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Line O/L
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4362750
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 200 | 4780500 | GBC problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 22 | 559318 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 285 | 7053310 | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 0 | 0 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 4925300 | GT-2 S/D due to Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 58 | 1055040 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 215 | 5164044 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 0 | 0 | Under maint.
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 45 | 1094250 | Engine problem
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 428616
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 70 | 1257629 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 24 | 330624 | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 515124
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 32 | 544800 | Fuel shortage
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 35 | 731649 | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 741451 | Fuel shortage
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 47 | 1172940 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 806760
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 26 | 645400 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 49 | 931771 | 0:00
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 247 | 3163964 | Fuel shortage
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 300 | 2270301 | Fuel conservation
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 0 | 386279 | Fuel conservation
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 100 | 1118701 | Fuel conservation
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 60 | 1220256 | Fuel shortage
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 2174400
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 72 | 1401600 | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 1926720
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 198930
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 433440 | Fuel shortage
| Dhaka area Total |  |  |  | 5847 | 2720 | 51395867
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Machine problem
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 17 | 419279 | Engine problem
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 98820
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 28 | 563520 | Engine problem
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 46 | 1108500 | Low water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 151 | 3565403 | ST Under maint
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 105 | 992763
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 39 | 626544 | Fuel shortage
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 471763 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 10 | 265800 | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 12 | 295680 | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 0 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 4 | 314880
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 19320
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 280 | 2545473 | Fuel shortage
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 36 | 632596 | Engine problem
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 73 | 1484539 | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 306240
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 89 | 2351018 | Engine problem
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 18400 | On test.
| Chattogram area Total |  |  |  | 2382 | 953 | 16080538
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 219 | 4454000 | Gas shortage
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 0 | 922700 | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 305 | 6768000 | Gas shortage
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+136*1 | 284 | 119 | 3310200 | On test.
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 30 | 388584 | Gas shortage
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 5 | 126720 | Gas shortage
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 36 | 669090 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 5 | 16869 | Gas shortage
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 74 | 2868727 | Fuel shortage
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 37 | 391584 | Engine problem
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 64 | 1631530 | Machine problem
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 50 | 863520 | High voltage
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 501017
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 10 | 232020
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 122 | 2590080
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 16 | 595000 | Engine problem
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 9 | 211656 | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 15 | 355470 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 148 | 1022016 | Fuel conservation
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 99 | 706800 | Fuel shortage
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 111 | 2341920
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 444600 | Engine problem
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 111 | 1421760
| Cumilla Area Total |  |  |  | 3169 | 1624 | 32833863
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 33 | 1677120 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 4 | 176256 | Gas shortage
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 13200
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 58 | 1202400 | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 58 | 1257600 | Fuel shortage
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 283910
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 4 | 286320 | Engine problem
| Mymensingh Area Total |  |  |  | 614 | 157 | 4896806
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 30 | 716000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 562440 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 90 | 2203609 | ST Under shut down
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 1155000
| Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 42 | 1002672
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 8 | 192384 | Gas shortage
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 64 | 1471392
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 86 | 645120
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 0 | 0 | Under maint.
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 425000
| Sylhet 50MW PP (EPL) |  | NENP | 27*2 | 50 | 33 | 763840 | Gas shortage
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 529992
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 0 | 0 | Under maint.
104 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 422 | 9654000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 244080
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 396 | 9302500
| Sylhet Area Total |  |  |  | 2477 | 1306 | 28868029
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Fuel shortage
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 885 | 19920000
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 54 | 773760 | Engine problem
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 43 | 202080 | Line O/L
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 76 | 308480 | Engine problem
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 155 | 4456512 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 0 | 0 | Fuel shortage
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 40 | 271680 | Fuel conservation
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 75 | 1226208 | Engine problem
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Fuel shortage
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 486720
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 0 | 0 | 0 | On test.
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 0 | 0 | 538 | 10846000 | On test.
| Khulna Area Total |  |  |  | 2384 | 1866 | 38491440
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Line O/L
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 18 | 383384 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 158 | 3992438 | Gas shortage
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 280 | 8187000 | Line O/L
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 210 | 4567800
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Line O/L
| Barisal 307 MW |  | BCPCL | 0 | 0 | 0 | 0 | On test.
| Barisal Area Total |  |  |  | 1958 | 666 | 17130622
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 24 | 212577 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 4 | 99731 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contract Expired
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 34 | 471366
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 40 | 206265 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 188 | 4698691 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 212 | 5801018 | Gas shortage
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 30 | 103396 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 17 | 439680
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 237492
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 8 | 133291 | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 75 | 233424 | High voltage
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Fuel conservation
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 92 | 1206048 | Engine problem
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 35 | 907968 | Engine problem
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 33600
| Adani Power Jharkhanda Ltd |  | Import | 0 | 0 | 0 | 0
| Rajshahi Area Total |  |  |  | 2129 | 770 | 14784547
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 160 | 3895700 | Machine problem
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 49 | 761136 | Engine problem
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 35123
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 75 | 614016 | Engine problem
| Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 173397
| Rangpur Area Total |  |  |  | 750 | 284 | 5479372
| Total |  |  |  | 21710 | 10346 | 209961084
| Eastern Grid Total |  |  |  | 14489 | 6760 | 134075103
| Western Grid Total |  |  |  | 7221 | 3586 | 75885981
| National Grid Total |  |  |  | 21710 | 10346 | 209961084
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2022-12-01
| (a) ENTIRE EASTERN GRID : |  | 6929.34 | MW | (b) ENTIRE WESTERN GRID : |  | 2992.17 | MW
| i) Dhaka area |  | 3752.24 | MW | i) Khulna area |  | 1130 | MW
| ii) Chittagong area |  | 1186.1 | MW | ii) Rajshahi area |  | 956.1 | MW
| iii) Comilla area |  | 888 | MW | iii) Barisal area |  | 251.07 | MW
| iv) Mymensingh area |  | 697 | MW | iv) Rangpur area |  | 655 | MW
| v) Sylhet area |  | 406 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 9921.51 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 10 | 00:00 | Chowmuhani | 134 | 19:00 | Kaptai | 3.8 | 18:00 | Nawabganj | 27.6 | 21:00 | Sholosohor | 29 | 18:00
2 | AKSML | 84 | 11:00 | Chuadanga | 69 | 18:00 | Kazla | 82 | 13:00 | Netrakona | 88 | 18:30 | Shyampur | 170 | 11:00
3 | Aftabnagar | 26.6 | 18:00 | Coxsbazar | 100 | 18:00 | Keranigonj | 40 | 13:00 | New | 62 | 12:00 | Siddhirganj | 78 | 18:00
4 | Agargaon | 60 | 13:00 | Cumilla(N) | 101 | 18:00 | Khagrachori | 22 | 18:00 | Niamatpur | 48 | 18:00 | Sirajganj | 68 | 18:30
5 | Agrabad | 62 | 18:00 | Cumilla(S) | 122 | 18:00 | Khulna | 73 | 19:00 | Noapara | 35 | 18:00 | Sonargaon | 101 | 14:00
6 | Amnura | 33 | 18:30 | Daudkandi | 110 | 18:00 | Khulshi | 168 | 15:00 | PHP | 10 | 11:00 | Sreemongol | 42 | 18:30
7 | Ashuganj | 48 | 00:00 | Dhaka | 30 | 12:00 | Kishoreganj | 96 | 19:30 | Pabna | 80 | 18:00 | Srinagar | 29 | 20:00
8 | BSRM | 165 | 03:00 | Dhamrai | 90 | 18:30 | Kodda | 250 | 14:00 | Palashbari | 88 | 18:30 | Sunamganj | 35 | 19:00
9 | Bagerhat | 76 | 18:00 | Dhanmondi | 108 | 13:00 | Kulaura | 36 | 18:00 | Panchagarh | 53 | 18:00 | Sylhet | 123 | 18:00
10 | Bakulia | 108 | 18:00 | Dohazari | 68 | 18:00 | Kurigram | 44 | 18:00 | Patuakhali | 75 | 20:00 | TK | 22.6 | 18:00
11 | Banani | 32 | 12:00 | Faridpur | 98 | 18:00 | Kushtia | 98 | 18:00 | Payra | 1.17 | 19:00 | Tangail | 131 | 19:00
12 | Bangabhaban | 13 | 10:00 | Fatullah | 59 | 12:00 | Lalbag | 69 | 17:00 | Postogola | 33 | 13:00 | Thakurgaon | 64 | 18:00
13 | Barapukuria | 41 | 18:00 | Fenchuganj | 35 | 18:00 | Lalmonirhat | 33 | 18:00 | Purbachal | 11 | 18:00 | Tongi | 106 | 11:00
14 | Barguna | 12 | 19:30 | Feni | 91 | 18:00 | Madanganj | 42 | 12:00 | Purbasadipur | 93 | 18:00 | Ullon | 37 | 13:00
15 | Barishal | 71 | 18:00 | GPH | 14 | 11:00 | Madaripur | 60 | 20:00 | Rahanpur_I | 11.1 | 01:00 | Uttara | 64 | 13:00
16 | Barishal-230 | 52 | 18:00 | Ghorashal | 50 | 20:00 | Madartek | 56 | 18:00 | Rahim | 33 | 01:00 | UttaraNew | 13 | 11:00
17 | Baroaulia | 70 | 17:00 | Goalpara | 18 | 19:30 | Madunaghat | 46 | 18:00 | Rajbari | 42 | 18:00 | Zigatola | 36 | 18:30
18 | Baroirhat | 37 | 18:00 | Gollamari | 36 | 13:00 | Magura | 42 | 18:00 | Rajendrapur | 98 | 19:00
19 | Bashundhara | 123 | 18:00 | Gopalganj | 72 | 18:00 | Mahasthangarh | 44 | 18:00 | Rajshahi | 100 | 13:00
20 | BashundharaCement | 6 | 01:00 | Gulshan | 84 | 12:00 | Manikganj | 64 | 19:30 | Rajshahi-230 | 21 | 18:30
21 | Beanibazar | 43 | 18:00 | Halishahar | 97 | 15:00 | Maniknagar | 47 | 17:00 | Ramganj | 64 | 18:00
22 | Benapole | 42 | 08:00 | HaripurSBU | 147 | 23:00 | Matarbari | 34 | 18:00 | Rampur | 24 | 00:00
23 | Bhaluka | 106 | 00:00 | Hasnabad | 72 | 14:00 | Matuail | 52 | 12:00 | Rangamati | 10 | 12:00
24 | Bhandaria | 33 | 21:00 | Hathazari | 51 | 18:00 | Millgate | 60 | 13:00 | Rangpur | 102 | 18:30
25 | Bhangura | 21 | 18:00 | Ishurdi | 50 | 18:00 | Mirpur | 104 | 13:00 | Ruppur | 4 | 16:00
26 | Bheramara(GK) | 38 | 18:00 | Jaldhaka | 46 | 18:00 | Mirsorai | 3 | 18:00 | SSM | 3 | 01:00
27 | Bhulta | 205 | 18:30 | Jamalpur | 97 | 20:00 | Mithapukur | 23 | 08:00 | Saidpur | 79 | 18:00
28 | Bog-Sherpur | 48 | 18:00 | Jashore | 90 | 18:00 | Modern | 0 | 00:00 | Satkhira | 79 | 18:00
29 | Bogura | 124 | 18:30 | Jhenaidah | 89 | 18:00 | Mogbazar | 99 | 15:00 | Satmasjid | 71 | 18:00
30 | Borhanuddin | 24 | 22:00 | Joydebpur | 141 | 19:30 | Mongla | 24 | 08:00 | Savar | 140 | 11:00
31 | Brahmanbaria | 106 | 21:00 | Joypurhat | 42 | 18:00 | Motijheel | 30 | 13:00 | Shahjadpur | 75 | 18:00
32 | Cantonment | 107 | 18:00 | Juldah | 26 | 01:00 | Munshiganj | 65 | 00:00 | Shahjibazar | 89 | 18:00
33 | Chandpur | 41 | 19:30 | KSRM | 36 | 00:00 | Mymensingh | 151 | 19:30 | Shahmirpur | 40 | 00:00
34 | Chandraghona | 26 | 18:00 | Kabirpur | 245 | 18:30 | Naogaon | 85 | 18:00 | Shariatpur | 44 | 20:00
35 | Chapai | 41 | 12:00 | Kachua | 46 | 18:00 | Narail | 36 | 18:00 | Sherpur | 82 | 20:00
36 | Charsaidpur | 42.8 | 16:00 | Kallyanpur | 66 | 18:00 | Narinda | 54 | 13:00 | Shikalbaha | 32 | 05:00
37 | Chauddagram | 31 | 18:00 | Kalurghat | 8 | 12:00 | Narshingdi | 139 | 18:30 | Shikalbaha-230 | N/A | N/A
38 | Chhatak | 19 | 18:00 | Kamrangirchar | 69 | 18:00 | Natore | 91 | 18:00 | Shitalakhya | 103 | 15:00
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2022-12-01 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Bhulta | 396 | 22:00 | 377 | 12:00 | Kaliakoir | 402 | 21:00 | 384 | 14:00
| Bibiana | 407 | 21:00 | 390 | 15:00 | Payra | 421 | 04:00 | 417 | 07:00
| BIPTC | 409 | 04:00 | 394 | 12:00 | Rahanpur_I | 421 | 18:00 | 390 | 12:00
| Gopalganj_I | 423 | 17:00 | 412 | 21:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 237 | 21:00 | 223 | 11:00 | Hasnabad | 236 | 22:00 | 224 | 10:00
| AKSML | 241 | 19:00 | 215 | 10:00 | Hathazari | 240 | 19:00 | 217 | 10:00
| Aminbazar | 237 | 21:00 | 225 | 12:00 | Ishurdi | 245 | 21:00 | 231 | 12:00
| Ashuganj | 245 | 22:00 | 235 | 00:00 | Jhenaidah | 243 | 21:00 | 232 | 07:00
| Baghabari | 240 | 22:00 | 229 | 12:00 | Kaliakoir | 236 | 21:00 | 222 | 14:00
| Barapukuria | 232 | 21:00 | 220 | 09:00 | Keranigonj | 236 | 21:00 | 215 | 13:00
| Barishal | 248 | 17:00 | 242 | 22:00 | Khulna(S) | 252 | 21:00 | 232 | 00:00
| Bheramara | 243 | 21:00 | 227 | 09:00 | Maniknagar | 235 | 21:00 | 221 | 11:00
| Bhulta | 237 | 21:00 | 223 | 12:00 | Meghnaghat | 242 | 22:00 | 230 | 10:00
| Bibiana | 240 | 17:00 | 231 | 12:00 | Mirsorai | 235 | 19:00 | 216 | 10:00
| BIPTC | 245 | 21:00 | 228 | 17:00 | Rajshahi | 246 | 21:00 | 232 | 09:00
| Bogura | 237 | 22:00 | 226 | 09:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 251 | 08:00 | 248 | 00:00 | Rampura | 235 | 22:00 | 222 | 15:00
| BSRM | 237 | 18:30 | 217 | 10:00 | Shikalbaha | 230 | 19:00 | 221 | 10:00
| Cumilla(N) | 237 | 21:00 | 226 | 10:00 | Shyampur | 241 | 19:00 | 217 | 10:00
| Fenchuganj | 242 | 17:00 | 234 | 11:00 | Siddhirganj | 237 | 21:00 | 224 | 10:00
| Ghorashal | N/A | N/A | N/A | N/A | Sirajgonj | 237 | 21:00 | 226 | 10:00
| GPH | 238 | 18:30 | 214 | 10:00 | Tongi | 238 | 21:00 | 229 | 09:00
| Haripur | 235 | 22:00 | 224 | 10:00 |  | 235 | 21:00 | 216 | 11:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 136 | 21:00 | 126 | 12:00 | Lalbag | 139 | 22:00 | 131 | 10:00
| Agargaon | 137 | 21:00 | 128 | 11:00 | Lalmonirhat | 135 | 21:00 | 123 | 07:00
| Agrabad | 138 | 19:00 | 125 | 09:00 | Madanganj | 138 | 18:00 | 130 | 12:00
| AKS | 138 | 18:30 | 122 | 10:00 | Madaripur | 138 | 04:00 | 136 | 00:00
| Aminbazar | 136 | 18:00 | 128 | 19:00 | Madartek | 135 | 21:00 | 126 | 12:00
| Amnura | 137 | 19:00 | 125 | 12:00 | Madunaghat | 140 | 19:00 | 126 | 10:00
| Ashuganj | 140 | 03:00 | 135 | 12:00 | Magura | 141 | 21:00 | 132 | 12:00
| Bagerhat | 139 | 21:00 | 134 | 00:00 | Mahasthangarh | 140 | 21:00 | 130 | 12:00
| Bakulia | 137 | 18:30 | 124 | 10:00 | Manikganj | 135 | 06:00 | 124 | 14:00
| Banani | 138 | 21:00 | 128 | 11:00 | Maniknagar | 138 | 22:00 | 129 | 12:00
| Bangabhaban | 138 | 22:00 | 129 | 12:00 | Matarbari | 131 | 21:00 | 112 | 13:00
| Barapukuria | 137 | 21:00 | 128 | 09:00 | Matuail | 136 | 21:00 | 126 | 12:00
| Barguna | 135 | 05:00 | 131 | 14:00 | Millgate | 139 | 21:00 | 127 | 11:00
| Barishal | 140 | 07:00 | 128 | 14:00 | Mirpur | 138 | 21:00 | 128 | 10:00
| Barishal-230 | 142 | 17:00 | 137 | 00:00 | Mithapukur | 137 | 21:00 | 128 | 12:00
| Baroaulia | 138 | 21:00 | 127 | 02:00 | Modern | 137 | 18:30 | 126 | 05:00
| Baroirhat | 139 | 18:00 | 131 | 00:00 | Mogbazar | 137 | 22:00 | 127 | 14:00
| Bashundhara | 140 | 21:00 | 128 | 11:00 | Mongla | 139 | 21:00 | 130 | 07:00
| BashundharaCement | 138 | 18:00 | 130 | 12:00 | Motijheel | 138 | 22:00 | 127 | 18:30
| Beanibazar | 135 | 04:00 | 130 | 14:00 | Munshiganj | 138 | 18:00 | 131 | 11:00
| Benapole | 139 | 21:00 | 132 | 12:00 | Mymensingh | 134 | 05:00 | 123 | 14:00
| Bhaluka | 133 | 06:00 | 123 | 18:30 | Naogaon | 138 | 22:00 | 127 | 09:00
| Bhandaria | 140 | 02:00 | 137 | 13:00 | Narail | 140 | 21:00 | 131 | 13:00
| Bhangura | 144 | 21:00 | 137 | 09:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bheramara | 140 | 21:00 | 134 | 09:00 | Narshingdi | 134 | 04:00 | 126 | 11:00
| Bheramara(GK) | 141 | 21:00 | 136 | 12:00 | Natore | 138 | 22:00 | 130 | 09:00
| Bhulta | 133 | 08:00 | 125 | 11:00 | Nawabganj | 140 | 21:00 | 131 | 10:00
| Bog-Sherpur | 141 | 21:00 | 131 | 12:00 | Netrakona | 134 | 04:00 | 125 | 09:00
| Bogura | 140 | 22:00 | 131 | 12:00 | New | 140 | 21:00 | 129 | 12:00
| Bogura-230 | 141 | 22:00 | 132 | 09:00 | Niamatpur | 136 | 21:00 | 127 | 08:00
| Brahmanbaria | 137 | 21:00 | 130 | 12:00 | Noapara | 141 | 21:00 | 132 | 07:00
| Cantonment | 136 | 21:00 | 127 | 10:00 | Pabna | 142 | 21:00 | 133 | 12:00
| Chandpur | 143 | 18:30 | 136 | 00:00 | Palashbari | 136 | 21:00 | 127 | 12:00
| Chandraghona | 140 | 19:00 | 126 | 09:00 | Panchagarh | 138 | 21:00 | 120 | 09:00
| Chapai | 139 | 21:00 | 128 | 09:00 | Patuakhali | 135 | 03:00 | 133 | 12:00
| Charsaidpur | 139 | 21:00 | 131 | 12:00 | Payra | 139 | 05:00 | 136 | 19:30
| Chauddagram | 140 | 21:00 | 133 | 00:00 | PHP | 139 | 17:00 | 131 | 00:00
| Chhatak | 134 | 03:00 | 129 | 14:00 | Postogola | 141 | 21:00 | 132 | 10:00
| Chowmuhani | 140 | 18:00 | 134 | 00:00 | Purbachal | 140 | 21:00 | 128 | 12:00
| Chuadanga | 138 | 21:00 | 131 | 07:00 | Purbasadipur | 137 | 20:00 | 121 | 09:00
| Coxsbazar | 127 | 20:00 | 114 | 00:00 | Rahim | 138 | 21:00 | 132 | 10:00
| Cumilla(N) | 142 | 21:00 | 135 | 11:00 | Rajbari | 137 | 05:00 | 133 | 07:00
| Cumilla(S) | 141 | 17:00 | 128 | 13:00 | Rajendrapur | 131 | 03:00 | 123 | 12:00
| Daudkandi | 141 | 18:00 | 132 | 00:00 | Rajshahi | 136 | 22:00 | 127 | 12:00
| Dhaka | 136 | 22:00 | 127 | 10:00 | Rajshahi-230 | 135 | 21:00 | 126 | 09:00
| Dhamrai | 136 | 21:00 | 127 | 11:00 | Ramganj | 140 | 08:00 | 133 | 00:00
| Dhanmondi | 138 | 21:00 | 131 | 12:00 | Rampur | 136 | 19:00 | 125 | 10:00
| Dohazari | 137 | 19:00 | 120 | 10:00 | Rampura | 135 | 22:00 | 124 | 05:00
| Faridpur | 136 | 22:00 | 132 | 07:00 | Rangamati | 139 | 19:00 | 124 | 10:00
| Fatullah | 138 | 21:00 | 129 | 10:00 | Rangpur | 137 | 21:00 | 125 | 09:00
| Fenchuganj | 138 | 06:00 | 134 | 15:00 | Ruppur | 141 | 21:00 | 134 | 14:00
| Feni | 140 | 15:00 | 133 | 14:00 | Saidpur | 136 | 21:00 | 122 | 09:00
| Ghorashal | 142 | 22:00 | 128 | 01:00 | Satkhira | 136 | 17:00 | 131 | 07:00
| Goalpara | 139 | 18:00 | 134 | 06:00 | Satmasjid | 137 | 21:00 | 128 | 11:00
| Gollamari | 140 | 21:00 | 130 | 07:00 | Savar | 139 | 21:00 | 127 | 11:00
| Gopalganj | 138 | 21:00 | 133 | 07:00 | Shahjadpur | 145 | 22:00 | 137 | 12:00
| Gopalganj_I | 138 | 05:00 | 134 | 07:00 | Shahjibazar | 138 | 23:00 | 133 | 11:00
| Gulshan | 135 | 21:00 | 126 | 12:00 | Shariatpur | 138 | 04:00 | 134 | 12:00
| Halishahar | 137 | 18:00 | 124 | 10:00 | Sherpur | 135 | 06:00 | 123 | 07:00
| Haripur | 138 | 21:00 | 132 | 10:00 | Shikalbaha | 139 | 19:00 | 127 | 00:00
| HaripurSBU | 137 | 21:00 | 131 | 13:00 | Shikalbaha-230 | 140 | 19:00 | 126 | 10:00
| Hasnabad | 141 | 22:00 | 132 | 09:00 | Shitalakhya | 140 | 21:00 | 129 | 11:00
| Hathazari | 141 | 19:00 | 129 | 10:00 | Sholosohor | 138 | 19:00 | 123 | 10:00
| Ishurdi | 142 | 21:00 | 134 | 12:00 | Shyampur | 134 | 19:30 | 129 | 14:00
| Jaldhaka | 133 | 20:00 | 120 | 12:00 | Shyampur-230 | 137 | 21:00 | 129 | 10:00
| Jamalpur | 137 | 05:00 | 128 | 18:00 | Siddhirganj | 138 | 22:00 | 131 | 12:00
| Jashore | 139 | 21:00 | 128 | 06:00 | Sirajganj | 141 | 21:00 | 132 | 12:00
| Jhenaidah | 140 | 22:00 | 133 | 06:00 | Sonargaon | 139 | 18:00 | 133 | 10:00
| Jhenaidah-230 | 142 | 21:00 | 134 | 12:00 | Sreemongol | 140 | 22:00 | 134 | 14:00
| Joydebpur | 144 | 06:00 | 132 | 13:00 | Srinagar | 141 | 21:00 | 130 | 10:00
| Joypurhat | 138 | 21:00 | 127 | 09:00 | SSM | 139 | 21:00 | 122 | 04:00
| Juldah | 138 | 19:00 | 124 | 10:00 | Sunamganj | 134 | 05:00 | 128 | 14:00
| Kabirpur | 137 | 21:00 | 124 | 12:00 | Sylhet | 136 | 06:00 | 131 | 14:00
| Kachua | 142 | 18:30 | 134 | 14:00 | Tangail | 135 | 21:00 | 125 | 11:00
| Kaliakoir | 137 | 21:00 | 128 | 11:00 | Thakurgaon | 139 | 21:00 | 117 | 13:00
| Kallyanpur | 137 | 21:00 | 128 | 12:00 | TK | 138 | 21:00 | 127 | 03:00
| Kalurghat | 141 | 19:00 | 126 | 10:00 | Tongi | 140 | 21:00 | 130 | 11:00
| Kamrangirchar | 140 | 21:00 | 130 | 10:00 | Ullon | 135 | 21:00 | 126 | 12:00
| Kaptai | 137 | 21:00 | 127 | 09:00 | Uttara | 139 | 21:00 | 127 | 11:00
| Kazla | 138 | 22:00 | 129 | 13:00 | UttaraNew | 137 | 21:00 | 128 | 11:00
| Keranigonj | 139 | 21:00 | 131 | 10:00 | Zigatola | 139 | 21:00 | 130 | 10:00
| Khagrachori | 136 | 18:00 | 123 | 10:00
| Khulna | 138 | 21:00 | 130 | 18:00
| Khulna(S) | 141 | 21:00 | 131 | 07:00
| Khulshi | 137 | 19:00 | 123 | 09:00
| Kishoreganj | 136 | 06:00 | 127 | 12:00
| Kodda | 146 | 21:00 | 124 | 12:00
| KSRM | 138 | 19:00 | 127 | 00:00
| Kulaura | 138 | 22:00 | 134 | 12:00
| Kurigram | 133 | 21:00 | 123 | 12:00
| Kushtia | 140 | 21:00 | 132 | 12:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2022-12-01
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 954 | 5516 | 2963 | 8479 |  |  |  | QF-LDC-11
0:30 | 1092 | 5451 | 2952.5 | 8403.5 | Date: | 2022-12-01
1:00 | 1230 | 5386 | 2942 | 8328
1:30 | 1230 | 5281 | 2903.5 | 8184.5
2:00 | 1230 | 5176 | 2865 | 8041
2:30 | 1235 | 5058 | 2811.5 | 7869.5 | [5 empty] | Gen. at Eve. Peak | 10346 | 10346 MW (18:00 )
3:00 | 1240 | 4940 | 2758 | 7698 | [6 empty] | 18:00
3:30 | 1235 | 4836.5 | 2740 | 7576.5 | [5 empty] | Gen. at Day Peak | 9246 | 9246 MW (12:00 )
4:00 | 1230 | 4733 | 2722 | 7455 | [6 empty] | 12:00
4:30 | 1225 | 4709.5 | 2709 | 7418.5 | [5 empty] | Highest Generation | 10346
5:00 | 1220 | 4686 | 2696 | 7382 | [6 empty] | 18:00
5:30 | 1195 | 4702.5 | 2713.5 | 7416
6:00 | 1170 | 4719 | 2731 | 7450
6:30 | 1125 | 4804.5 | 2822.5 | 7627
7:00 | 1080 | 4890 | 2914 | 7804
7:30 | 1210 | 4842 | 3034 | 7876
8:00 | 1340 | 4794 | 3154 | 7948
8:30 | 1390 | 4872.5 | 3175.5 | 8048
9:00 | 1440 | 4951 | 3197 | 8148
9:30 | 1490 | 4971.5 | 3175.5 | 8147
10:00 | 1540 | 4992 | 3154 | 8146
10:30 | 1460 | 5451 | 3134 | 8585
11:00 | 1380 | 5910 | 3114 | 9024
11:30 | 1345 | 5986.5 | 3148.5 | 9135
12:00 | 1310 | 6063 | 3183 | 9246
12:30 | 1285 | 6153.5 | 3195 | 9348.5
13:00 | 1260 | 6244 | 3207 | 9451
13:30 | 1320 | 6106.5 | 3189 | 9295.5
14:00 | 1380 | 5969 | 3171 | 9140
14:30 | 1420 | 5968.5 | 3129.5 | 9098
15:00 | 1460 | 5968 | 3088 | 9056
15:30 | 1405 | 5718 | 3036 | 8754
16:00 | 1350 | 5468 | 2984 | 8452
16:30 | 1310 | 5537.5 | 3030 | 8567.5
17:00 | 1270 | 5607 | 3076 | 8683
17:30 | 1085 | 6183.5 | 3331 | 9514.5
18:00 | 900 | 6760 | 3586 | 10346
18:30 | 1040 | 6600.5 | 3660.5 | 10261
19:00 | 1180 | 6441 | 3735 | 10176
19:30 | 1200 | 6396 | 3766 | 10162
20:00 | 1160 | 6365 | 3661 | 10026 |  |  |  | Executive Engineer
20:30 | 1050 | 6352.5 | 3344.5 | 9697 |  |  |  | Network Operation Division
21:00 | 940 | 6340 | 3028 | 9368
21:30 | 895 | 6248.5 | 3072.5 | 9321
22:00 | 850 | 6157 | 3117 | 9274 |  |  |  |  | Page 6 of 7
22:30 | 983 | 5996.5 | 3126 | 9122.5
23:00 | 1116 | 5836 | 3135 | 8971
23:30 | 1035 | 5676 | 3049 | 8725
24:00 | 954 | 5516 | 2963 | 8479
10346 MW (18:00 )
9246 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2022-12-01 |  | Energy |  | 209961084
[13 empty] | 2022-12-01 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 3332 | 784 | 1448 | 207 | 1723 | 550 | 46 | 0 | 281 | 108 | 0 | 0
0:30 | 3387 | 742.5 | 1328.5 | 218.5 | 1589 | 792.5 | 46 | 0 | 190 | 109 | 0.5 | 0 | Date: | 2022-12-01
1:00 | 3442 | 701 | 1209 | 230 | 1455 | 1035 | 46 | 0 | 99 | 110 | 1 | 0
1:30 | 3442 | 677.5 | 1207.5 | 115 | 1466.5 | 1020.5 | 46 | 0 | 99 | 110 | 0.5 | 0 | [8 empty] | Total Energy | 209.9611 | Total Energy Gen 180.187 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 180.187 MKWHr
2:00 | 3442 | 654 | 1206 | 0 | 1478 | 1006 | 46 | 0 | 99 | 110 | 0 | 0 | [8 empty] | Energy not Served | 1.6925
2:30 | 3379 | 654 | 1213.5 | 0 | 1426.5 | 996 | 46 | 0 | 49.5 | 105 | 0 | 0 | [8 empty] | Energy Requirement | 211.6535
3:00 | 3316 | 654 | 1221 | 0 | 1375 | 986 | 46 | 0 | 0 | 100 | 0 | 0
3:30 | 3272 | 654 | 1223.5 | 0 | 1311 | 971 | 46 | 0 | 0 | 99 | 0 | 0 | [6 empty] | Shortage
4:00 | 3228 | 654 | 1226 | 0 | 1247 | 956 | 46 | 0 | 0 | 98 | 0 | 0
4:30 | 3249 | 654 | 1199 | 0 | 1193.5 | 976 | 46 | 0 | 0 | 101 | 0 | 0
5:00 | 3270 | 654 | 1172 | 0 | 1140 | 996 | 46 | 0 | 0 | 104 | 0 | 0
5:30 | 3286 | 654 | 1174.5 | 0 | 1157 | 1005.5 | 46 | 0 | 5 | 88 | 0 | 0
6:00 | 3302 | 654 | 1177 | 0 | 1174 | 1015 | 46 | 0 | 10 | 72 | 0 | 0
6:30 | 3327.5 | 723.5 | 1170 | 0 | 1250.5 | 1011 | 46 | 0 | 13 | 79 | 6.5 | 0 |  |  |  |  | Coal
7:00 | 3353 | 793 | 1163 | 0 | 1327 | 1007 | 46 | 0 | 16 | 86 | 13 | 0
7:30 | 3266.5 | 842.5 | 1161 | 0 | 1381 | 1032 | 46 | 0 | 16 | 91 | 40 | 154.8246 |  |  |  | Oil |  |  |  | ,
8:00 | 3180 | 892 | 1159 | 0 | 1435 | 1057 | 46 | 0 | 16 | 96 | 67 | 309.6492
8:30 | 3228 | 891.5 | 1151 | 0 | 1471.5 | 1030.5 | 46 | 0 | 33 | 96 | 100.5 | 282.0019
9:00 | 3276 | 891 | 1143 | 0 | 1508 | 1004 | 46 | 0 | 50 | 96 | 134 | 254.3547
9:30 | 3243 | 890.5 | 1145 | 0 | 1519.5 | 994 | 46 | 0 | 52.5 | 98 | 158.5 | 280.6196
10:00 | 3210 | 890 | 1147 | 0 | 1531 | 984 | 46 | 0 | 55 | 100 | 183 | 306.8845
10:30 | 3197.5 | 890.5 | 1135.5 | 294.5 | 1689 | 971.5 | 46 | 0 | 59.5 | 103 | 198 | 155.7462
11:00 | 3185 | 891 | 1124 | 589 | 1847 | 959 | 46 | 0 | 64 | 106 | 213 | 4.6079
11:30 | 3193 | 891 | 1124 | 623 | 1908.5 | 962.5 | 46 | 0 | 65.5 | 109 | 212.5 | 28.108
12:00 | 3201 | 891 | 1124 | 657 | 1970 | 966 | 46 | 0 | 67 | 112 | 212 | 51.6082
12:30 | 3264 | 891 | 1139.5 | 656 | 1981.5 | 972.5 | 46 | 0 | 79 | 113 | 206 | 25.8041
13:00 | 3327 | 891 | 1155 | 655 | 1993 | 979 | 46 | 0 | 91 | 114 | 200 | 0
13:30 | 3327 | 891 | 1155 | 655 | 1993 | 979 | 46 | 0 | 91 | 114 | 200 | 0
14:00 | 3327 | 891 | 1155 | 655 | 1993 | 979 | 46 | 0 | 91 | 114 | 200 | 0
14:30 | 3326 | 891 | 1148.5 | 585 | 1906 | 986.5 | 46 | 0 | 93 | 115 | 156.5 | 0
15:00 | 3325 | 891 | 1142 | 515 | 1819 | 994 | 46 | 0 | 95 | 116 | 113 | 0
15:30 | 3324 | 888 | 1131.5 | 257.5 | 1856 | 953.5 | 46 | 9 | 98.5 | 113 | 77 | 114.2753
16:00 | 3323 | 885 | 1121 | 0 | 1893 | 913 | 46 | 18 | 102 | 110 | 41 | 228.5506
16:30 | 3232.5 | 885 | 1134.5 | 0 | 2069 | 913.5 | 46 | 9 | 145.5 | 111 | 21.5 | 260.3449
17:00 | 3142 | 885 | 1148 | 0 | 2245 | 914 | 46 | 0 | 189 | 112 | 2 | 292.1393
17:30 | 3213.5 | 885 | 1215.5 | 294 | 2476.5 | 946 | 46 | 0 | 320 | 117 | 1 | 240.0703
18:00 | 3285 | 885 | 1283 | 588 | 2708 | 978 | 46 | 0 | 451 | 122 | 0 | 188.0013
18:30 | 3252.5 | 885 | 1290.5 | 374 | 2809 | 1034 | 46 | 0 | 449 | 121 | 0 | 135.0107
19:00 | 3220 | 885 | 1298 | 160 | 2910 | 1090 | 46 | 0 | 447 | 120 | 0 | 82.0202
19:30 | 3252 | 886 | 1308 | 195 | 2797 | 1106 | 46 | 0 | 450 | 122 | 0 | 63.5887
20:00 | 3257 | 893 | 1347 | 188 | 2667 | 1111 | 46 | 0 | 401 | 116 | 0 | 45.1572
20:30 | 3294 | 893 | 1373.5 | 242 | 2524.5 | 835.5 | 46 | 0 | 371.5 | 117 | 0 | 22.5786
21:00 | 3331 | 893 | 1400 | 296 | 2382 | 560 | 46 | 0 | 342 | 118 | 0 | 0
21:30 | 3343 | 893 | 1409 | 272 | 2376.5 | 550 | 46 | 0 | 316.5 | 115 | 0 | 0
22:00 | 3355 | 893 | 1418 | 248 | 2371 | 540 | 46 | 0 | 291 | 112 | 0 | 0
22:30 | 3342.5 | 893 | 1433.5 | 230.5 | 2232.5 | 545 | 46 | 0 | 286.5 | 113 | 0 | 0
23:00 | 3330 | 893 | 1449 | 213 | 2094 | 550 | 46 | 0 | 282 | 114 | 0 | 0
23:30 | 3331 | 838.5 | 1448.5 | 210 | 1908.5 | 550 | 46 | 0 | 281.5 | 111 | 0 | 0 | Max Temp. in Dhaka |  | 24.7° C | 30.4° C
24:00 | 3332 | 784 | 1448 | 207 | 1723 | 550 | 46 | 0 | 281 | 108 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 180.187 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 180.187 MKWHr
Note on W13: Author:

## Generation
g | 2022-12-01
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 |  | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 1108500
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 419279
| Teknaf 20MW PP (Solartech) | [6 empty] | 2 | 6 | 12 | 18 | 18 | 16 | 16 | 12 | 9 | 3 | 0 | [9 empty] | 98820
6 | Sikalbaha 225MW CCPP (Gas) | 151 | 150 | 150 | 151 | 151 | 151 | 151 | 151 | 151 | 151 | 151 | 148 | 150 | 150 | 151 | 151 | 151 | 151 |  | 151 | 151 | 151 | 151 | 151 | 151 | 151 | 3565403
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 51 | 51 | [14 empty] | 19 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 471763
12 | Hathazari 100 MW peaking PP | 32 | 32 | [5 empty] | 0 | 18 | 23 | 32 | 31 | 31 | 31 | 31 | 33 | 39 | 39 |  | 46 | 46 | 40 | 39 | 39 | 39 | 39 | 626544
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 27 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 51 | 17 | 992763
| Daudkandi 200 MW PP (B.Trac) | [9 empty] | 0 | 90 | 160 | 160 | 160 | 162 |  |  | 148 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 1022016
14 | Titas 50 MW Peaking PP | [10 empty] | 0 | 4 | 12 | 28 | 32 | 37 | 37 | 37 |  | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 391584
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 98 | 98 | 98 | 98 | 98 | 98 | 95 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 230 | 247 |  | 247 | 247 | 247 | 246 | 246 | 158 | 88 | 3163964
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 36 |  | 36 | 36 | 63 | 110 | 110 | 112 | 112 | 669090
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4362750
24
25 | Ghorasal 365 MW CCPP Unit-7 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4780500
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 23 | 30 |  | 30 | 40 | 44 | 44 | 44 | 44 | 44 | 388584
33 | Ashuganj 225 MW CCPP | 173 | 173 | 152 | 185 | 185 | 184 | 170 | 150 | 151 | 151 | 152 | 152 | 152 | 151 | 216 | 214 | 220 | 219 |  | 220 | 218 | 220 | 220 | 222 | 202 | 168 | 4454000
34 | Ashuganj 450 MW CCPP(South) | 270 | 280 | 250 | 270 | 270 | 270 | 230 | 230 | 210 | 200 | 200 | 205 | 320 | 320 | 305 | 320 | 305 | 305 |  | 305 | 305 | 305 | 305 | 310 | 310 | 310 | 6768000
| Ashuganj 450 MW CCPP(North) | 260 | 250 | 260 | 0 | [21 empty] | 0 | 922700
| Ashuganj 420 MW CCPP(East) |  |  | 22 | 130 | 220 | 275 | 269 | 269 | 292 | 292 | 292 | 242 | 218 | 217 | 144 | 144 | 117 | 119 |  | 20 | 16 | 2 | 13 | 11 | 9 | 12 | 3310200
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 0 |  |  | 0 | 3 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 126720
36 | Chandpur 150 MW CCPP | 71 | 71 | 70 | 72 | 71 | 71 | 71 | 72 | 71 | 63 | 64 | 64 | 64 | 65 | 64 | 64 | 64 | 64 |  | 64 | 63 | 66 | 71 | 70 | 71 | 71 | 1631530
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 295 | 292 | 285 | 285 | 285 | 286 | 280 | 278 | 275 | 271 | 267 | 269 | 295 | 306 | 308 | 298 | 290 | 285 |  | 287 | 292 | 290 | 293 | 298 | 299 | 305 | 7053310
40 | Meghnaghat 450 MW CCPP(MPL) | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 |  | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 4925300
41 | Haripur 360MW CCPP(HPL)
42 | RPCL 210MW CCPP | 106 | 106 | 106 | 108 | 108 | 108 | 97 | 72 | 73 | 41 | 36 | 37 | 35 | 32 | 31 | 33 | 33 | 33 |  | 48 | 58 | 63 | 104 | 110 | 113 | 113 | 1677120
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 3 | 14 | 30 | 39 | 45 | 43 | 42 | 35 | 25 | 8 | 0 | [9 empty] | 283910
44 | Fenchugonj CCPP Phase-1 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 29 | 29 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 716000
45 | Fenchugonj CCPP Phase-2 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 562440
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 66 | 67 | 67 | 67 | 40 | 40 | 40 | 69 | 67 | 66 | 63 | 62 | 65 | 63 | 61 | 64 | 40 | 64 |  | 62 | 62 | 62 | 64 | 64 | 68 | 68 | 1471392
48 | Shahjibazar 86MW PP (Shahjibazar) | [16 empty] | 40 | 86 |  | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 645120
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP
51 | Sylhet 20 MW GTPP | 19 | 19 | 19 | 19 | 19 | 19 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 425000
52 | Sylhet 50MW PP (EPL) | 33 | 33 | 33 | 32 | 32 | 32 | 33 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 33 |  | 33 | 32 | 33 | 32 | 32 | 32 | 32 | 763840
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 244080
54 | Hobiganj 11MW PP Cofidence-E | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 192384
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 53 | 53 | 53 | 22 | 22 | 22 | 51 | 51 | 50 | 50 | 50 | 53 | 50 | 50 | 50 | 53 | 53 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 1155000
56 | Shahjahanulla 25 MW PP | 24 | 23 | 23 | 22 | 21 | 21 | 21 | 21 | 16 | 16 | 22 | 22 | 22 | 22 | 22 | 22 | 23 | 24 |  | 24 | 16 | 16 | 24 | 24 | 24 | 24 | 529992
57 | Bibiana-II 341 MW CCPP (Summit)
| Bibiyana South 400 MW | 400 | 400 | 370 | 370 | 360 | 340 | 400 | 348 | 400 | 400 | 397 | 394 | 394 | 400 | 400 | 398 | 335 | 396 |  | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 9302500
58 | Nababganj 55 MW PP (Southern power ) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 55 | 55 | 35 | 35 | 35 | 741451
59 | Tangail Palli Power Gen 22 MW | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 9 | 4 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 286320
60 | Barabkunda 22 MW PP (Regent)
61 | Narshingdi 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 19 | 19 | 19 | 19 | 19 | 22 | 22 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 428616
62 | Tangail 22 MW PP (Doreen) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 7 | 7 | 7 | 4 |  | 7 | 7 | 7 | 8 | 8 | 8 | 8 | 176256
63 | Impoprt (Tripura) | 110 | 110 | 100 | 98 | 104 | 72 | 86 | 96 | 96 | 100 | 106 | 112 | 114 | 118 | 116 | 110 | 112 | 122 |  | 120 | 122 | 116 | 118 | 112 | 114 | 108 | 2590080
64 | Malancha, Ctg. EPZ (United) | 18 | 30 | 30 | 33 | 33 | 36 | 31 | 13 | 6 | 2 | 2 | 2 | 2 | 3 | 2 | 2 | 2 | 4 |  | 4 | 5 | 10 | 17 | 21 | 24 | 25 | 314880
65 | Feni 22MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 19 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 19 | 19 | 22 | 22 | 22 | 22 | 22 | 501017
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 5 | 8 | 8 | 8 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 232020
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 19 | 15 | 14 | 14 | 14 | 14 | 15 | 16 | 16 | 16 | 16 |  | 25 | 25 | 30 | 33 | 33 | 33 | 33 | 595000
68 | Cumilla 25 MW PP (Summit) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 355470
69 | Summit Ashulia | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 |  | 23 | 23 | 23 | 23 | 23 | 23 | 25 | 600000
70 | Summit Madhabdi | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 26 | 23 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 0 | 24 | 572940
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 806760
72 | Rupganj 33 MW PP(Summit) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 17 | 30 | 16 | 21 | 26 | 26 | 26 | 26 | 26 | 26 | 26 |  | 26 | 26 | 26 | 26 | 28 | 30 | 30 | 645400
73 | Ghorashal 108MW PP (Regent) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 559318
| Feni Lanka Power | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 34 | 99 |  | 99 | 99 | 99 | 24 | 17 | 17 | 17 | 706800
| Chowmuhani 113 MW | 110 | 109 | 105 | 108 | 65 | 73 | 95 | 98 | 98 | 98 | 105 | 97 | 104 | 106 | 100 | 107 | 111 | 111 |  | 115 | 75 | 75 | 75 | 75 | 75 | 75 | 2341920
| Manikgonj 162MW PP(MPGL) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 84 | 90 | 90 | 108 | 108 | 162 | 162 | 162 |  | 162 | 162 | 162 | 162 | 162 | 140 | 72 | 1926720
77 | Siddhirganj 100 PP(Dutch Bangla) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 40 | 60 | 65 | 70 | 78 | 78 | 70 | 70 | 70 |  | 78 | 78 | 78 | 78 | 78 | 78 | 42 | 1257629
78 | Gazipur 52 MW PP | 48 | 49 | 25 |  |  | 2 | 36 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 49 |  | 49 | 49 | 49 | 49 | 49 | 50 | 49 | 931771
79 | Kodda 150MW PP | 16 | 16 |  |  |  | 10 | 16 | 16 | 32 | 32 | 32 | 32 | 48 | 32 | 32 | 32 | 32 | 32 |  | 32 | 32 | 32 | 16 | 16 | 16 | 16 | 544800
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 8 | 8 | 8 | 8 | 4 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 9 |  | 11 | 16 | 16 | 8 | 8 | 8 | 8 | 211656
| Gazipur 100 MW PP | 105 | 105 | 105 | 70 | 70 | 80 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2174400
| Kaptai 7 MW Solar PP | 1 | [5 empty] | 0 | 1 | 2 | 3 | 4 | 4 | 2 | 1 | 1 | 0 | [10 empty] | 19320
| Jodiac Power | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 22 | 36 | 36 | 36 |  | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 632596
| Karnaphuli Power Ltd. | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 60 | 73 | 73 | 73 |  | 73 | 73 | 73 | 73 | 73 | 63 | 60 | 1484539
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP ( Summit) | 210 | 200 | 200 | 200 | 200 | 200 | 196 | 200 | 210 | 205 | 210 | 210 | 240 | 235 | 245 | 235 | 230 | 215 |  | 220 | 216 | 215 | 220 | 220 | 235 | 235 | 5164044
87 | Meghnaghat 100 MW(IEL) | 25 | 24 | 24 |  |  | 2 | 21 | 25 | 25 | 33 | 55 | 59 | 68 | 65 | 60 | 57 | 51 | 58 |  | 59 | 66 | 67 | 65 | 74 | 73 | 72 | 1055040
| Meghnaghat 104 MW PP (OPCL) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 59 | 72 | 72 |  | 63 | 55 | 55 | 55 | 55 | 55 | 55 | 1401600
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 265800
92 | Fenchuganj 44MW (Energyprima) | 43 | 43 | 43 | 43 | 20 | 20 | 20 | 20 | 20 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 1002672
93 | Ashuganj 51 MW PP (Midland) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 16869
94 | Gagnagar 102 MW PP (Digital Power) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 24 |  | 33 | 33 | 33 | 33 | 33 | 33 | 8 | 330624
95 | Patenga 50MW PP (Baraka) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 18 | 18 | 18 | 28 |  | 44 | 44 | 44 | 44 | 35 | 20 | 19 | 563520
96 | Chattogram 108 MW PP (ECPV) | [19 empty] | 0 | [6 empty] | 0
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 34 | 45 | 45 | 45 | 45 | 45 |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 1094250
100 | Manikganj 55 MW PP (Northern) | 35 | 35 | 35 | 17 | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 17 | 17 | 17 | 35 | 35 |  | 55 | 55 | 55 | 35 | 35 | 17 | 17 | 731649
101 | Kushiara 163 MW CCPP (KP) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 2203609
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 1 | 0 | [10 empty] | 13200
103 | Kamalaghat 54 MW PP(Banco Energy) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 54 |  | 54 | 54 | 54 | 17 | 17 | 17 | 17 | 515124
104 | Keranigonj 300 MW PP (APR) | 60 | [8 empty] | 0 | 300 | 300 | 298 | 156 | 253 |  |  | 300 |  | 50 | 110 | 103 | 230 | 101 | 67 | 60 | 2270301
105 | Bramhangoan 100 MW PP (Aggreko) | 100 | [8 empty] | 0 | 100 | 99 | 98 | [12 empty] | 0 | 386279
106 | Mymensingh 200 MW PP (United) | 48 | 48 | 48 | 24 | 24 | 24 | 46 | 46 | 48 | 48 | 48 | 58 | 58 | 58 | 58 | 58 | 48 | 58 |  | 58 | 58 | 58 | 58 | 58 | 58 | 48 | 1202400
112 | Aurahati 100MW PP (Aggreko) | 70 | [8 empty] | 0 | 99 | 98 | 99 | 100 | 100 |  |  | 100 |  | 100 | 75 | 75 | 56 | 52 | 50 | 50 | 1118701
114 | Kodda 149 MW PP Unit-1 (Summit) | 45 | 42 | 43 | 43 | 43 | 43 | 44 | 43 | 43 | 43 | 43 | 43 | 43 | 45 | 44 | 44 | 45 | 60 |  | 63 | 70 | 72 | 72 | 72 | 59 | 54 | 1220256
115 | Juldah 100 MW PP Unit-3 (Acorn) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 295680
116 | Chandpur 200MW (Desh energy) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 28 | 50 |  | 100 | 196 | 195 | 87 | 51 | 51 | 24 | 863520
117 | Ashuganj 150MW PP (Midland) | 92 | 119 | 145 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 119 | 79 | 72 | 74 |  | 74 | 74 | 74 | 75 | 75 | 73 | 68 | 2868727
118 | Bibiyana-III 400 MW CCPP | 421 | 421 | 352 | 358 | 358 | 341 | 416 | 355 | 373 | 421 | 414 | 414 | 414 | 414 | 421 | 412 | 364 | 422 |  | 420 | 422 | 421 | 421 | 419 | 419 | 419 | 9654000
| Jamalpur 115 MW PP (United) | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 58 | 59 | 52 | 58 | 49 | 50 | 58 |  | 59 | 59 | 59 | 59 | 59 | 59 | 49 | 1257600
| Anwara 300 MW PP (United) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 208 | 230 | 220 | 230 | 230 | 230 | 230 | 280 |  | 281 | 122 | 51 | 51 | 51 | 68 | 69 | 2545473
| Juldah unit-2 (Acorn) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 15 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 306240
| Anlima Energy Ltd. | 107 | 107 | 107 | 107 | 107 | 98 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 |  | 105 | 107 | 107 | 107 | 107 | 107 | 107 | 2351018
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 444600
| Spectra Solar Plant Ltd. | [6 empty] | 2 | 11 | 20 | 26 | 30 | 30 | 29 | 25 | 17 | 7 | 1 | [9 empty] | 198930
| Chandpur 115(Doreen) | 35 | 35 | 35 | 35 | 35 | 34 | 35 | 35 | 35 | 35 | 44 | 111 | 115 | 67 | 18 | 17 | 37 | 111 |  | 115 | 115 | 115 | 115 | 115 | 48 | 34 | 1421760
| Kanchan Purbachal Power Generation Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 433440
| Mirsharai 150 MW (Oil) | [15 empty] | 18 | [9 empty] | 0 | 18400
Mirsharai 150 MW (Gas)
120 | Eastern Zone Total | 5386 | 5176 | 4940 | 4733 | 4686 | 4719 | 4890 | 4794 | 4951 | 4992 | 5910 | 6063 | 6244 | 5969 | 5968 | 5468 | 5607 | 6760 |  | 6441 | 6396 | 6365 | 6340 | 6157 | 5836 | 5516 | 134075103
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | [6 empty] | 0 | 16 | 46 | 49 | 49 | 49 | 49 | 49 | 16 | 16 | 45 | 54 |  | 82 | 57 | 16 | 16 | 87 | 96 | 99 | 773760
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [16 empty] | 3 | 43 |  | 33 | 33 | 31 | 31 | 31 | 31 | 31 | 202080
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 75 | 75 | 17 | 17 |  |  | 11 | 53 | 75 | 75 | 75 | 75 | 75 | 56 | 35 | 35 | 25 | 75 |  | 75 | 75 | 35 | 35 | 36 | 66 | 76 | 1226208
130 | Mongla Orion 100 MW Solar PP | [6 empty] | 5 | 26 | 48 | 65 | 75 | 76 | 71 | 57 | 40 | 17 | 1 | [9 empty] | 486720
131 | Rampal 1320 MW (BIFPCL) | 465 | 466 | 466 | 466 | 516 | 555 | 527 | 527 | 534 | 534 | 539 | 546 | 576 | 553 | 574 | 503 | 504 | 538 |  | 550 | 556 | 561 |  |  |  |  | 10846000
132 | United Payra Power Ltd. | [25 empty] | 0 | 0
133 | Bhola Nutan Biddut BD LTD (GAS) | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 170 | 175 | 175 | 174 | 174 | 174 | 174 | 164 | 162 | 142 | 210 |  | 211 | 221 | 221 | 217 | 221 | 221 | 220 | 4567800
Bhola Nutan Biddut BD LTD (OIL)
Barisal 110 MW PP (Summit )
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 157 | 159 | 159 | 159 | 139 | 159 | 157 | 135 | 158 | 117 | 115 | 178 | 182 | 183 | 184 | 184 | 160 | 158 |  | 168 | 183 | 184 | 183 | 183 | 183 | 183 | 3992438
140 | Bhola 33 MW PP (Venture) | 17 | 16 | 15 | 14 | 14 | 15 | 14 | 13 | 12 | 15 | 16 | 17 | 17 | 16 | 14 | 13 | 16 | 18 |  | 18 | 19 | 19 | 19 | 19 | 18 | 17 | 383384
141 | Noapara 100 MW PP (Bangla Trac) | [17 empty] | 40 | [5 empty] | 85 | 86 | 87 | 271680
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP | [16 empty] | 20 | 76 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 308480
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 701 | 654 | 654 | 654 | 654 | 654 | 793 | 892 | 891 | 890 | 891 | 891 | 891 | 892 | 891 | 885 | 885 | 885 |  | 885 | 886 | 893 | 893 | 893 | 893 | 784 | 19920000
147 | Bheramara 410 MW CCPP | 180 | 180 | 180 | 180 | 190 | 185 | 180 | 180 | 175 | 170 | 160 | 155 | 155 | 155 | 155 | 155 | 155 | 155 |  | 155 | 160 | 160 | 160 | 170 | 180 | 180 | 4456512
148 | Payra 1320 MW | 410 | 380 | 360 | 330 | 320 | 300 | 320 | 370 | 310 | 290 | 260 | 260 | 260 | 260 | 260 | 250 | 250 | 280 |  | 380 | 390 | 390 | 400 | 380 | 390 | 390 | 8187000
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 143 | 163 | 160 | 160 | 160 | 160 |  | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 3895700
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [17 empty] | 24 |  | 33 | 33 | 33 | 33 | 33 | 33 | 32 | 212577
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 1 | 3 | 4 | 5 | 5 | 5 | 4 | 2 | 0 | 0 | [9 empty] | 33600
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 177 | 179 | 179 | 180 | 184 | 183 | 184 | 190 | 195 | 194 | 190 | 183 | 185 | 187 | 188 | 189 | 189 | 188 |  | 188 | 188 | 187 | 188 | 187 | 187 | 188 | 4698691
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 258 | 254 | 270 | 274 | 274 | 275 | 270 | 265 | 248 | 241 | 224 | 223 | 219 | 225 | 215 | 206 | 212 | 212 |  | 219 | 219 | 226 | 225 | 235 | 247 | 248 | 5801018
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [16 empty] | 4 | 4 |  | 17 | 19 | 20 | 20 | 20 | 19 | 19 | 99731
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 19 | 17 | 16 | 16 | 15 | 15 | 15 | 16 | 16 | 17 |  | 19 | 22 | 22 | 22 | 22 | 22 | 21 | 439680
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 237492
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | 8 | 8 | 8 | 8 |  |  | 0 | 8 | 8 | 8 | 8 | 16 | 34 | 34 | 34 | 34 | 34 | 34 |  | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 471366
167 | Katakhali 50 MW Peaking PP | [16 empty] | 10 | 40 |  | 40 | 40 | 40 | 32 | 16 | 16 | 16 | 206265
168 | Santahar 50 MW Peaking PP | [17 empty] | 30 |  | 34 | 35 | 34 |  |  |  |  | 103396
169 | Natore 52 MW PP (Rajlanka) | [6 empty] | 0 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 133291
170 | Chapainawabganj 100 MW Peaking PP | [16 empty] | 25 | 75 |  | 84 | 84 | 43 | 43 | 8 |  |  | 233424
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 55 | 55 | 35 | 35 |  |  | 14 | 34 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 45 | 92 |  | 94 | 94 | 94 | 94 | 94 | 50 | 50 | 1206048
172 | Confidence Power Bogura Unit-1 113 MW | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 907968
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | 34 | 34 | 10 |  |  |  | 33 | 33 | 33 | 35 | 34 | 34 | 34 | 34 | 34 | 34 | 49 | 49 |  | 49 | 49 | 49 | 34 | 34 | 34 | 34 | 761136
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 2 | 4 | 5 | 6 | 6 | 5 | 4 | 1 | 0 | [9 empty] | 35123
178 | Energypac Power Venture Thakurgaon Ltd. | [15 empty] | 30 | 72 | 75 |  | 113 | 115 | 115 | 95 | 75 | 75 | 0 | 614016
| Intraco Solar 30 MW | [6 empty] | 1 | 6 | 16 | 22 | 29 | 30 | 27 | 20 | 14 | 5 | 0 | [9 empty] | 173397
178 | Adani Power Jharkhanda Ltd