## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID COMPANY OF BANGLADESH LTD.
SYSTEM OPERATION DATA
Month:October 2022
Sl. | Items | Current Month |  | Previous Month |  | This Month Last Year |  | Max. Till-to-date
|  | 2022-10-10 |  | 2022-09-01 |  | 2021-09-01
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 12901 | 2022-10-10 | 13761 | 2022-09-07 | 13509 | 2021-09-11 | 14782 | 2022-04-16
|  |  | 20:00 |  | 22:00 |  | 20:00 |  | 21:00
2 | Minimum Generation (MW) | 2828 | 2022-10-25 | 8864 | 2022-09-15 | 8491 | 2021-09-17 | - | -
|  |  | 6:00 |  | 6:00 |  | 1:00 |  | -
3 | Maximum Evening Peak Generation (MW) | 12901 | 2022-10-10 | 13712 | 2022-09-01 | 13509 | 2021-09-11 | 14782 | 2022-04-16
|  |  | 20:00 |  | 22:00 |  | 20:00 |  | 21:00
4 | Maximum Day Peak Generation (MW) | 11274 | 2022-10-01 | 11999 | 2022-09-08 | 11723 | 2021-09-05 | 12895 | 2022-04-26
|  |  | 12:00 |  | 12:00 |  | 12:00 |  | 12:00
5 | Maximum Evening Peak Demand (MW) Estimated | 14300 | 2022-10-31 | 14695 | 2022-09-01 | 13509 | 2021-09-11 | 14782 | 2022-04-16
|  |  | 20:00 |  | 20:00 |  | 20:00 |  | 12:00
6 | Average Generation (MW) at Evening Peak | 11594.5161 |  | 13055.1 |  | 12742.1667 |  | 13536.33 | 2022-04-27
7 | Average Generation (MW) at Day Peak | 9760.6774 |  | 11203.2667 |  | 10804.6667 |  | 11233.4 | 2022-04-27
8 | Maximum Power Import from India, BIPTC (MW) | 975 | 2022-10-04 | 919 | 2022-09-30 | 907 | 2021-07-01 | 956 | 27/3/2019
|  |  | 14:30 |  | 11:00 |  | 0:30 |  | 19:00
9 | Maximum Power Import from Tripura, India (MW) | 172 | 2022-10-10 | 184 | 2022-09-10 | 172 | 2021-07-10 | 194 | 12/06/19
|  |  | 19:00 |  | 18:30 |  | 23:00 |  | 19:00
10 | Maximum Load Shed (MW) at Evening Peak | 4395 | 2022-10-04 | 1471 | 2022-09-28 | 0 | - | 1459 | 04/05/2010
|  |  | 21:00 |  | 21:00 |  | - |  | 20:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | 8431 | 2022-10-04 | 12904 | 2022-09-28 | - | - | 13792 | 2021-04-27
|  | - | 21:00 | - | 21:00 | - | - |  | 20:00
12 | Minimum Load Shed (MW) at Evening Peak | 0 | 2022-10-24 | 0 | 2022-09-13 | 0 | -
|  |  | 21:00 |  | 19:00
13 | Generation During Min. Load Shed (MW) at Evening Peak | 5652 | 2022-10-24 | 11790 | 2022-09-13 | - | -
|  |  | 21:00 |  | 19:00
14 | Maximum Load Shed (MW) at Day Peak | 1937 | 2022-10-10 | 1235 | 2022-09-06 | - | -
|  |  | 12:00 |  | 12:00
15 | Generation During Max. Load Shed (MW) at Day Peak | 10256 | 2022-10-10 | 10112 | 2022-09-06 | - | -
|  |  | 10:00 |  | 12:00
16 | Minimum Load Shed (MW) at Day Peak | 0 | 2022-10-24 | 0 | 2022-09-02 | - | -
|  |  | 9:00 |  | 12:00
17 | Generation During Min. Load Shed (MW) at Day Peak | 8146 | 2022-10-24 | 11272 | 2022-09-02 | - | -
|  |  | 9:00 |  | 12:00
18 | Nos. of Days Load Shed at Evening Peak | 25 |  | 29 |  | 0
19 | Nos. of Days Load Shed at Day Peak | 27 |  | 20 |  | -
20 | Gross Generation of BPDB (MKWH) | 1483.1714 |  | 1767.5579 |  | 1586.2039 |  | 3805.72 | 2019-09-19
21 | Station Use of BPDB (MKWH) | 135.2896 |  | 88.5941 |  | 134.2992
22 | Net Generation of BPDB (MKWH) | 1347.8818 |  | 1678.9638 |  | 1451.9047
23 | Net Generation of IPP (MKWH) | 4808.0999 |  | 5416.8526 |  | 5324.0599
24 | Net Generation of REB (MKWH) | 114.4586 |  | 111.5457 |  | 141.3247
24 | Net Generation of Rental Power Plant (MKWH) | 308.6068 |  | 401.8248 |  | 490.1064
25 | Total Net Generation (MKHWh) (BPDB, IPP, RPP & REB) | 6579.047 |  | 7609.1868 |  | 7407.3956 |  | 7842.9924 | April'22
26 | Energy Generation by Gas (MKWH) | 3736.515 |  | 4050.2118 |  | 4494.9287 |  | 4756.96 | Sep-19
27 | Energy Generation by Diesel (MKWH) | 205.5598 |  | 582.493 |  | 614.1861 |  | 771.52 | July-18
28 | Energy Generation by Furnace Oil (MKWH) | 1900.5833 |  | 1974.4688 |  | 1887.4763 |  | 2365.7466 | April'22
29 | Energy Generation by Hydro (MKWH) | 110.3709 |  | 104.6574 |  | 104.8774 |  | 104.66 | Sep-22
30 | Energy Generation by Solar (MKWH) | 41.0067 |  | 34.9866 |  | 23.2163 |  | 40.58 | March-22
31 | Energy Generation by Coal (MKWH) | 720.3009 |  | 950.9634 |  | 417.01 |  | 950.96 | Sep'22
32 | Enegry Import from India (BIPTC & AC) (MKWH) | 755.5794 |  | 744.831 |  | 600.369 |  | 776.67 | August-22
33 | Monthly Load Factor (%) | 86.4057 |  | 91.3054 |  | 81.01 |  | 92.62 | August-22

## QF-LDC-22
Page: 1/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month:July 2022
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quantity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 12901 | 2022-10-10 | 20:00
Generation Period
| Dhaka | MW | 4484.12
| Chattogram | MW | 1261.51
| Cumilla | MW | 1107.5
| Mymensingh | MW | 930
| Sylhet | MW | 499
a) | Total supply in East zone | MW | 8282.13
| Khulna | MW | 1611.8
| Barisal | MW | 368.97
| Rajshahi | MW | 1371
| Rangpur | MW | 782
b) | Total supply in West zone | MW | 4133.77
c) | Total supply in both zone ( a+b) | MW | 12415.9
Ref: | 27.21.0000.603.16.087.20.574 | Date: 20/11/2022
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
Page: 2/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month:October 2022
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Daily Maximum power Export through EWI/ NO-1
| a) Ghorashal end | AMPS | 300 | 2022-10-23 | 18:00
| b) Ishurdi end | MW | 516 | 2022-10-03 | 16:00
18 | Daily Maximum power Import through EWI/ NO-1
| a) Ghorashal end | AMPS | 1500 | 2022-10-01 | 8:00
| b) Ishurdi end | MW | 56 | 2022-10-14 | 18:00
19 | Daily Maximum Energy Export through EWI/NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
20 | Daily Maximum Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
21 | Total Energy Export through EWI/ NO-1
| a) Ghorashal end | MKWH | 0.161
| b) Ishurdi end | MKWH | 195.22
22 | Total Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | -
| b) Ishurdi end | MKWH | -
23 | Transmission loss of EWI/ NO-1 | % | 3
24 | Daily Maximum power Export through EWI/ NO-2
| a) Ashuganj end | MW | 200 | 2022-10-11 | 10:00
| b)Serajganj end | MW | 632 | 2022-10-03 | 16:00
25 | Daily Maximum power Import through EWI/ NO-2
| a) Ashuganj end | MW | 560 | 2022-10-03 | 13:00
| b)Sirajganj end | MW | 180 | 2022-10-23 | 18:00
26 | Daily Maximum Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 0.112 | 2022-10-25 | 18:00
| b)Sirajganj end | MKWH | 0.114 | 2022-10-25 | 18:00
27 | Daily Maximum Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | - | -
| b)Sirajganj end | MKWH
28 | Total Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 0.94
| b)Sirajganj end | MKWH | 100
29 | Total Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | 174.11
| b)Sirajganj end | MKWH | 0.95
30 | Transmission loss of EWI /NO-2 | % | 3.245%
* Total energy export from Ghorasal end and import from Ishurdi end and the transmission loss of EWI/NO-1 is taken
from the calculation of GMD, PGCB, Ishwardi.
* *Total energy export from Ashuganj end and import from Sirajganj end and the transmission loss of EWI/NO-2 is taken
from the calculation of Sirajganj switching sub station.
* **The energy meter of Ghorasal end is out of order.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-23
QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: October2022
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Mymensingh | 132/33 kV transformers T-1 & T-2 | 2022-10-01 02:10 | 2022-10-01 02:34 | 0:24 | T | Due to 33 kV feeder fault | 140 | 56 | Power interruption
Mirpur | 132/33 kV transformer T-2 | 2022-10-01 06:36 | 2022-10-01 07:49 | 1:13 | T | Due to red-hot maint of 132 kV B-phase bushing | 15 | 18.25 | Power interruption
Joydevpur | 132/33 kV transformer T-2 | 2022-10-02 01:16 | 2022-10-02 01:40 | 0:24 | T | Due to Sherpur-2 feeder fault | 35 | 14 | Power interruption
Aminbazar | 132 kV Bus-1 | 2022-10-04 14:04 | 2022-10-04 17:14 | 3:10 | T | Eastern Zone got blackout. | 0 | 0 | No interruption
| 230 kV Bus-1 | 2022-10-04 14:04 | 2022-10-04 17:54 | 3:50 | T |  | 0 | 0 | No interruption
| 230/132 kV transformer T-2 | 2022-10-04 14:04 | 2022-10-04 17:55 | 3:51 | T |  | 0 | 0 | No interruption
Savar | 132/33 kV transformers T-1, T2 & T3 | 2022-10-16 10:57 | 2022-10-16 11:44 | 0:47 | E/O | Due to man injured | 103 | 80.6833 | Power interruption
Sonargaon | 132/33 kV transformer T-1 with 33 kV Bus | 2022-10-20 21:53 | 2022-10-21 04:39 | 6:46 | E/O | Due to red-hot maint.at 33 kV side | 25 | 169.1667 | Power interruption
Kabirpur | 132/33 kV transformer T-2 | 2022-10-21 20:15 | 2022-10-21 21:35 | 1:20 | E/O | Due to red-hot maint.at 33 kV side | 95 | 126.6667 | Power interruption
Joydevpur | 132/33 kV transformer T-3 | 2022-10-23 18:10 | 2022-10-23 18:10 | 0:00 | T | Tripped showing diff.relay
| 132/33 kV transformer T-4 | 2022-10-24 15:49 | 2022-10-24 17:01 | 1:12 | T | Due to 33 kV feeder fault | 21 | 25.2 | Power interruption
Kallyanpur | 132/33 kV transformer T-2 | 2022-10-24 22:02 | 2022-10-25 11:38 | 13:36 | T | Tripped showing diff.relay | 0 | 0 | No interruption
Savar | 132 kV Bus-A | 2022-10-26 00:07 | 2022-10-26 01:36 | 1:29 | E/O | Due to red-hot maint.by PBS | 0 | 0 | No interruption
Mymensingh | 132/33 kV transformer T-3 with 33 kV Bus | 2022-10-27 22:20 | 2022-10-27 23:25 | 1:05 | E/O | Due to red-hot maint.at 33 kV side | 20 | 21.6667 | Power interruption
|  |  | Total : | 39:07 |  | Unserved Energy: |  | 511.6333
Dhaka (South) Grid Circle :
Siddhirganj | 230 kV Bus-1 & 2 | 2022-10-04 14:04 | 2022-10-04 17:19 | 3:15 | T | Eastern Zone got blackout. | 0 | 0 | No interruption
Hasnabad | 132/33 kV transformer T-2 | 2022-10-20 09:12 | 2022-10-20 09:19 | 0:07 | T | Due to 33 kV feeder fault | 14 | 1.6333 | Power interruption
Sreenagar | 132/33 kV transformers T-1 & T2 | 2022-10-20 15:44 | 2022-10-20 16:17 | 0:33 | T | Due to 33 kV feeder fault | 25 | 13.75 | Power interruption
Narsinghdi | 132/33 kV transformer T1 | 2022-10-21 05:57 | 2022-10-21 06:48 | 0:51 | T | Tripped showing 87T at high side and inter trip at low | 17 | 14.45 | Power interruption
| 132/33 kV transformer T3 | 2022-10-21 06:48 | 2022-10-21 06:55 | 0:07 | T |  | 25 | 2.9167 | Power interruption
Hasnabad | 132/33 kV transformers T-1 & T5 | 2022-10-24 14:23 | 2022-10-24 14:40 | 0:17 | T | Due to 33 kV feeder fault | 40 | 11.3333 | Power interruption
Bhulta | 132/33 kV transformer T1 | 2022-10-24 16:36 | 2022-10-24 16:37 | 0:01 | T | Tripped showing diff. relay | 0 | 0 | No interruption
|  |  | Total : | 5:11 |  | Unserved Energy: |  | 44.0833
Chattogram Grid Circle :
Hathazari | 132 kV Bus-1 | 2022-10-04 14:04 | 2022-10-04 17:15 | 3:11 | T | Eastern Zone got blackout. | 0 | 0 | No interruption
| 230 kV Bus-1 | 2022-10-04 14:04 | 2022-10-04 18:19 | 4:15 | T |  | 0 | 0 | No interruption
Ramganj | 132/33 kV transformer T2 | 2022-10-06 19:14 | 2022-10-06 20:08 | 0:54 | E/O | Due to red-hot maint. | 20 | 18 | Power interruption
Cox'sbazar | 132/33 kV transformer T3 | 2022-10-07 08:38 | 2022-10-07 08:49 | 0:11 | T | Tripped showing E/F. relay at 33 kV side | 0 | 0 | No interruption
Dohazari | 132/33 kV transformers T-1 & T2 | 2022-10-08 23:25 | 2022-10-08 23:44 | 0:19 | T | Tripped showing O/C. relay | 58 | 18.3667 | Power interruption
Sikalbaha | 132/33 kV transformer T4 | 2022-10-12 04:15 | 2022-10-12 08:54 | 4:39 | T | Tripped showing O/C. relay | 0 | 0 | No interruption
Dohazari | 132/33 kV transformer T1 | 2022-10-13 13:44 | 2022-10-13 14:34 | 0:50 | E/O | Due to red-hot maint. | 0 | 0 | No interruption
|  |  | Total : | 14:19 |  | Unserved Energy: |  | 36.3667
Cumilla Grid Circle :
Ashuganj | 230 kV Bus-1 | 2022-10-04 14:04 | 2022-10-04 14:39 | 0:35 | T | Eastern Zone got blackout. | 0 | 0 | No interruption
Cumilla(N) | 231 kV Bus-2 | 2022-10-04 14:04 | 2022-10-04 16:00 | 1:56 | T |  | 0 | 0 | No interruption
Cumilla(S) | 132/33 kV transformer T3 | 2022-10-06 06:02 | 2022-10-06 06:35 | 0:33 | T | Tripped showing O/C relay | 74 | 40.7 | Power interruption
| 132/33 kV transformer T4 | 2022-10-06 06:02 | 2022-10-06 06:33 | 0:31 | T | Due to 33 kV feeder fault | 0 | 0 | No interruption
Sylhet | 132/33 kV transformer T2 with 33 kV Bus | 2022-10-10 21:15 | 2022-10-10 22:15 | 1:00 | E/O | Due to red-hot maint.work | 10 | 10 | Power interruption
Feni | 132/33 kV transformer T1 | 2022-10-10 20:43 | 2022-10-10 22:21 | 1:38 | E/O | Due to flashing at 132 kV DS Bus | 0 | 0 | No interruption
Shahjibazar | 132/33 kV transformer T2 | 2022-10-11 11:23 | 2022-10-11 11:35 | 0:12 | T | Due to 33 kV feeder fault | 25 | 5 | Power interruption
Sreemongal | 132/33 kV transformer T1 with 33 kV Bus-1 | 2022-10-14 10:49 | 2022-10-14 12:12 | 1:23 | E/O | Due to red-hot maint.work | 20 | 27.6667 | Power interruption
B.Baria | 132/33 kV transformers T1 & T2 | 2022-10-14 20:49 | 2022-10-14 21:14 | 0:25 | T | Due to 33 kV feeder fault | 125 | 52.0833 | Power interruption
Ashuganj | 132/33 kV transformer T3 | 2022-10-16 17:54 | 2022-10-16 18:26 | 0:32 | E/O | Due to red-hot maint.work | 0 | 0 | No interruption
Cumilla(N) | 230/132 kV transformer T02 | 2022-10-17 01:14 | 2022-10-17 05:59 | 4:45 | T | Tripped showing protection trip | 0 | 0 | No interruption
| 230/132 kV transformer T02 | 2022-10-17 22:54 | 2022-10-18 07:29 | 8:35 | T | Tripped showing Lockout relay | 0 | 0 | No interruption
Shahjibazar | 132/33 kV transformer T2 | 2022-10-24 08:46 | 2022-10-24 08:56 | 0:10 | T | Due to 33 kV feeder fault | 9 | 1.5 | Power interruption
Daudkandi | 132/33 kV transformers T1 & T2 | 2022-10-24 10:45 | 2022-10-24 10:57 | 0:12 | T | Due to 33 kV feeder fault | 72 | 14.4 | Power interruption
Cumilla(S) | 132/33 kV transformer T1 | 2022-10-24 16:04 | 2022-10-24 16:23 | 0:19 | T | Tripped showing Lockout relay | 0 | 0 | No interruption
Cumilla(N) | 132/33 kV transformers T3 & T4 | 2022-10-24 19:40 | 2022-10-24 19:58 | 0:18 | T | Tripped showing Lockout relay | 0 | 0 | No interruption
Ramganj | 132/33 kV transformer T1 | 2022-10-30 08:58 | 2022-10-30 09:58 | 1:00 | E/O | Due to red-hot maint.work | 0 | 0 | No interruption
Sylhet | 132/33 kV transformer T4 | 2022-10-31 19:20 | 2022-10-31 20:08 | 0:48 | T | Tripped showing O/C relay | 10 | 8 | Power interruption
|  |  | Total : | 24:52 |  |  |  | 159.35
Khulna Grid Circle :
Faridpur | 132/33 kV transformers T1 & T2 | 2022-10-02 07:44 | 2022-10-02 08:14 | 0:30 | T | Due to 33 kV feeder fault | 20 | 10 | Power interruption
Barisal(S) | 132/33 kV transformer T1 | 2022-10-07 19:16 | 2022-10-07 20:19 | 1:03 | E/O | Due to red-hot maint at 33 kV side | 20 | 21 | Power interruption
Narail | 132/33 kV transformer T1 | 2022-10-12 20:08 | 2022-10-12 21:45 | 1:37 | E/O | Due to red-hot maint at 33 kV side | 26 | 42.0333 | Power interruption
Patuakhali | 132/33 kV transformers T1 & T2 | 2022-10-14 15:28 | 2022-10-14 16:00 | 0:32 | T | Tripped showing O/C & E/F relay at 33 kV side | 60 | 32 | Power interruption
Gallamari | 132/33 kV transformer T2 | 2022-10-18 06:23 | 2022-10-18 07:18 | 0:55 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Madaripur | 132/33 kV transformers T1 | 2022-10-20 15:38 | 2022-10-20 15:57 | 0:19 | T | Due to 33 kV feeder fault | 48 | 15.2 | Power interruption
| 132/33 kV transformers T2 | 2022-10-20 15:38 | 2022-10-21 00:27 | 8:49 | T
Bhandaria | 132/33 kV transformer T1 | 2022-10-23 08:17 | 2022-10-23 09:19 | 1:02 | E/O | Due to red-hot maint at 33 kV side | 6 | 6.2 | Power interruption
Gopalganj | 132/33 kV transformers T1 & T2 | 2022-10-24 08:56 | 2022-10-24 09:23 | 0:27 | E/O | Due to bursting of CB at 33 kV side | 0 | 0 | No interruption
Faridpur | 132/33 kV transformers T1 & T2 | 2022-10-24 09:47 | 2022-10-24 10:03 | 0:16 | T | Due to 33 kV feeder fault | 50 | 13.3333 | Power interruption
Patuakhali | 132/33 kV transformer T2 | 2022-10-25 16:01 | 2022-10-25 16:54 | 0:53 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Faridpur | 132/33 kV transformer T1 | 2022-10-29 08:40 | 2022-10-29 10:16 | 1:36 | E/O | Due to red-hot maint | 20 | 32 | Power interruption
|  |  | Total : | 17:59 |  | Unserved Energy: |  | 171.7667
HVDC Grid Circle :
Shahjadpur | 132/33 kV transformer T3 | 2022-10-10 11:40 | 2022-10-10 15:57 | 4:17 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Jashore | 132/33 kV transformer T1 | 2022-10-20 20:44 | 2022-10-20 21:52 | 1:08 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Bottail | 132/33 kV transformer T2 | 2022-10-27 07:26 | 2022-10-27 08:41 | 1:15 | E/O | Due to red-hot maint at 33 kV side | 20 | 25 | Power interruption
|  |  | Total : | 6:40 |  |  |  | 25
Bogura Grid Circle:
Mohasthangar | 132/33 kV transformer T2 with 33 kV Bus | 2022-10-03 09:17 | 2022-10-03 11:21 | 2:04 | E/O | Due to red-hot maint at 33 kV side | 25 | 51.6667 | Power interruption
Barapukuria | 132/33 kV transformer T5 | 2022-10-08 00:48 | 2022-10-08 00:48 | 0:00 | E/O | Due to bursting of HT Bushing | 0 | 0 | No interruption
| 230/132 kV transformer T01 | 2022-10-08 00:48 | 2022-10-09 01:38 | 24:50 | E/O | Due to Oil leakage | 0 | 0 | No interruption
| 132/33 kV transformer T3 | 2022-10-09 09:55 | 2022-10-09 11:47 | 1:52 | E/O | Due to red-hot maint at 33 kV side | 12 | 22.4 | Power interruption
Purbasadipur | 132/33 kV transformer T3 | 2022-10-11 06:40 | 2022-10-11 07:10 | 0:30 | T | Tripped showing E/F. relay at 33 kV side | 0 | 0 | No interruption
| 132/33 kV transformer T3 | 2022-10-12 08:05 | 2022-10-12 08:27 | 0:22 | T |  | 0 | 0 | No interruption
Bogura | 132/33 kV transformer T1 | 2022-10-13 20:42 | 2022-10-13 23:37 | 2:55 | T | Tripped showing lockout. relay | 0 | 0 | No interruption
Kurigram | 132/33 kV transformer T1 | 2022-10-14 15:37 |  |  | T | Tripped showing over voltage | 0 | 0 | No interruption
Purbasadipur | 132/33 kV transformers T1 | 2022-10-15 18:23 | 2022-10-15 18:59 | 0:36 | T | Due to 33 kV feeder fault | 74 | 44.4 | Power interruption
| 132/33 kV transformers T3 | 2022-10-15 18:23 | 2022-10-15 20:28 | 2:05 | T
Saidpur | 132/33 kV transformers T1 | 2022-10-15 21:05 | 2022-10-15 21:52 | 0:47 | E/O | Due to red-hot maint at 33 kV side | 20 | 15.6667 | Power interruption
Naogaon | 132/33 kV all transformers | 2022-10-21 19:55 | 2022-10-21 20:32 | 0:37 | E/O | Due to 33 kV breaker burst | 104 | 64.1333 | Power interruption
Mithapukur | 132/33 kV transformer T2 | 2022-10-29 21:15 | 2022-10-30 11:56 | 14:41 | E/O | Due to red-hot maint at 33 kV side | 0 | 0 | No interruption
Sherpur(Bogura) | 132/33 kV transformer T2 | 2022-10-31 01:03 |  |  | E/O | Due to bursting of PT | 0 | 0 | No interruption
|  |  | Total : | 51:19 |  |  |  | 198.2667
Others :
Ashuganj | 230/132 kV transformer OAT12 | 2022-08-02 12:02 | 2022-08-02 12:23 | 0:21 | T | Tripped showing O/C. relay | 0 | 0 | No interruption
| 230/132 kV transformer T01 | 2022-08-08 09:21 | 2022-08-08 15:21 | 6:00 | T | Tripped showing O/C. relay | 0 | 0 | No interruption
| 132/33 kV transformer OAT12 | 2022-08-10 13:17 | 2022-08-10 13:31 | 0:14 | T | Tripped showing O/C. relay | 0 | 0 | No interruption
| 132/33 kV transformer OAT12 | 2022-08-14 13:17 | 2022-08-14 15:04 | 1:47 | T | Tripped showing O/C. relay | 0 | 0 | No interruption
| 132/33 kV transformer OAT12 | 2022-08-18 06:04 | 2022-08-18 10:33 | 4:29 | T | Tripped showing O/C. relay | 0 | 0 | No interruption
| 230/132 kV transformer OAT12 | 2022-08-21 11:15 | 2022-08-21 11:28 | 0:13 | T | Tripped showing O/C. relay | 0 | 0 | No interruption
| 230/132 kV transformer OAT12 | 2022-08-23 08:27 | 2022-08-23 08:36 | 0:09 | T | Tripped showing O/C. relay at 33 kV side | 0 | 0 | No interruption
| 230/132 kV transformer OAT12 | 2022-08-23 23:07 | 2022-08-23 23:23 | 0:16 | T | Tripped showing O/C. relay | 0 | 0 | No interruption
|  |  | Total : | 13:29 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 172:56 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-24
Page: 1/2 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month:October2022
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Mirpur | Mirpur-Aminbazar 132 kV Ckt-2 | 2022-10-01 05:44 | 2022-10-01 06:37 | 0:53 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Aminbazar | Aminbazar-Mirpur 132 kV Ckt-1 | 2022-10-04 14:04 | 2022-10-04 17:14 | 3:10 | T | Eastern Zone got blackout. | 0 | 0 | No interruption
| Aminbazar-Kallyanpur 132 kV Ckt-1 | 2022-10-04 14:04 | 2022-10-04 17:15 | 3:11 | T |  | 0 | 0 | No interruption
| Aminbazar-Manikganj 162 MW P.P 132 kV Ckt-1 | 2022-10-04 14:04 | 2022-10-04 17:21 | 3:17 | T |  | 0 | 0 | No interruption
| Aminbazar-Kallyanpur 132 kV Ckt-1 | 2022-10-04 14:04 | 2022-10-04 17:54 | 3:50 | T |  | 0 | 0 | No interruption
| Aminbazar-Kallyanpur 132 kV Ckt-2 | 2022-10-04 14:04 | 2022-10-04 17:57 | 3:53 | T |  | 0 | 0 | No interruption
| Aminbazar-Agargaon 230 kV Ckt-1 | 2022-10-04 14:04 | 2022-10-04 18:56 | 4:52 | T |  | 0 | 0 | No interruption
| Aminbazar-Meghnaghat 230 kV Ckt-1 | 2022-10-04 14:04 | 2022-10-04 19:15 | 5:11 | T |  | 0 | 0 | No interruption
Kishoreganj | Kishoreganj-Mymensingh 132 kV Ckt-1 | 2022-10-04 14:04 | 2022-10-04 14:57 | 0:53 | T |  | 0 | 0 | No interruption
Ghonobhaban |  |  | 2022-10-04 17:22 |  | T | at kallyanpur S/S | 0 | 0 | No interruption
Banghobhaban |  |  | 2022-10-04 17:40 |  |  |  | 0 | 0 | No interruption
Kabirpur | Kabirpur-Manikganj 132 kV Ckt-2 | 2022-10-06 07:12 | 2022-10-06 07:39 | 0:27 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Kodda 132 kV Ckt-1 | 2022-10-09 08:51 | 2022-10-09 09:05 | 0:14 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
| Kaliakoir-Kodda 132 kV Ckt-2 | 2022-10-09 08:51 | 2022-10-09 14:43 | 5:52 | T | Tripped showing Dist.& E/F relay | 0 | 0 | No interruption
| Kaliakoir-Tangail 132 kV Ckt-1 & 2 | 2022-10-11 17:05 | 2022-10-11 17:20 | 0:15 | T | Tripped showing Dist. relay | 507 | 126.75 | Power interruption
Mymensingh | Mymensingh-Mymensingh RPCL 132 kV Ckt-1 | 2022-10-12 12:22 | 2022-10-12 12:32 | 0:10 | E/O | Due to Mymensingh RPCL bus coupler got tripped | 385 | 64.1667 | Power interruption
Tongi | Tongi-Uttara 132 kV Ckt | 2022-10-15 05:19 | 2022-10-15 05:29 | 0:10 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Kabirpur | Kabirpur-Tongi 132 kV Ck-2 | 2022-10-20 08:55 | 2022-10-20 09:03 | 0:08 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Kodda | Kodda-Rajendrapur 132 kV Ckt-2 | 2022-10-24 09:56 | 2022-10-24 10:29 | 0:33 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Tongi | Tongi-Bashundhara 132 kV Ckt-1 | 2022-10-24 16:21 | 2022-10-24 16:31 | 0:10 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
| Tongi-Kabirpur 132 kV Ckt-2 | 2022-10-24 22:52 | 2022-10-24 23:04 | 0:12 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
|  |  | Total : | 37:21 |  | Unserved Energy: |  | 190.9167
Dhaka (South) Grid Circle :
Ghorashal GIS | Ghorashal GIS-Ghorashal AIS 230 kV Ckt-1 | 2022-10-04 14:04 | 2022-10-04 14:43 | 0:39 | T | Eastern Zone got blackout. | 0 | 0 | No interruption
| Ghorashal GIS-Ghorashal AIS 230 kV Ckt-2 | 2022-10-04 14:04 | 2022-10-04 14:04 | 0:00 | T |  | 0 | 0 | No interruption
Rampura | Rampura-Gulshan 132 kV Ckt-2 | 2022-10-04 14:04 | 2022-10-04 18:31 | 4:27 | T |  |  | 0 | No interruption
| Rampura-Bashundhara 132 kV Ckt-1 | 2022-10-04 14:04 | 2022-10-04 18:39 | 4:35 | T
| Rampura-Madertek 132 kV Ckt-1 | 2022-10-04 14:04 | 2022-10-04 19:28 | 5:24 | T
| Rampura-Aftabagar 132 kV Ckt-1 | 2022-10-04 14:04 | 2022-10-04 19:06 | 5:02 | T |  | 0 | 0 | No interruption
| Rampura-Dhaka University 132 kV Ckt-1 &,2 | 2022-10-04 14:04 | 2022-10-04 20:38 | 6:34 | T
| Rampura-Ullon 132 kV Ckt | 2022-10-04 14:04 | 2022-10-04 19:57 | 5:53 | T
| Rampura-Moghbazar 132 kV Ckt-1 | 2022-10-04 14:04 | 2022-10-04 19:57 | 5:53 | T
Siddhirganj | Siddhirganj-Haripur 132 kV Ckt-1 | 2022-10-04 14:04 | 2022-10-04 16:58 | 2:54 | T
Haripur | Haripur-Bhulta 230 kV Ckt-1 | 2022-10-08 12:15 | 2022-10-08 13:19 | 1:04 | T | Due to red-hot maint. | 0 | 0 | No interruption
Fatulla | Fatulla-Haripur 132 kV Ckt | 2022-10-18 11:52 | 2022-10-18 11:52 | 0:00 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Maniknagar | Maniknagar-Matijheel 132 kV Ckt-2 | 2022-10-19 10:54 | 2022-10-19 17:41 | 6:47 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
| Maniknagar-Matuail 132 kV Ckt | 2022-10-20 19:23 | 2022-10-20 23:37 | 4:14 | T | Due to red-hot maint. | 0 | 0 | No interruption
Shyampur | Shyampur-Fatullah 132 kV Ckt-2 | 2022-10-24 18:57 | 2022-10-25 10:37 | 15:40 | T | Due to bad weather | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Matuail 132 kV Ckt | 2022-10-24 23:40 | 2022-10-24 23:57 | 0:17 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Ghorashal GIS | Ghorashal GIS-Ashuganj (S) 230 kV Ckt | 2022-10-24 21:24 | 2022-10-25 12:35 | 15:11 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Rampura | Rampura-Bashundhara 132 kV Ckt-1 & 2 | 2022-10-25 01:13 | 2022-10-25 01:27 | 0:14 | T | Tripped showing Dist. relay | 35 | 8.1667 | Power interruption
Hasnabad | Hasnabad-Shitalakyha 132 kV Ckt | 2022-10-25 02:10 | 2022-10-25 02:31 | 0:21 | T | Tripped showing Dist. relay | 72 | 25.2 | Power interruption
| Hasnabad-Brahmangaon 132 kV Ckt | 2022-10-25 02:10 | 2022-10-25 02:10 | 0:00 | T | Tripped showing main pro. relay | 0 | 0 | No interruption
|  |  | Total : | 85:09 |  | Unserved Energy: |  | 33.3667
Chattogram Grid Circle :
Hathazari | Hathazari-Kaptai 132 kV Ckt-1 | 2022-10-02 14:40 | 2022-10-02 14:40 | 0:00 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Hathazari | Hathazari-Baroierhat 132 kV Ckt-1 | 2022-10-04 14:04 | 2022-10-04 17:15 | 3:11 | T | Eastern Zone got blackout. | 0 | 0 | No interruption
| Hathazari-AKSML 230 kV Ckt | 2022-10-04 14:04 | 2022-10-04 18:24 | 4:20 | T |  | 0 | 0 | No interruption
| Hathazari-GPS 230 kV Ckt | 2022-10-04 14:04 | 2022-10-04 20:47 | 6:43 | T |  | 0 | 0 | No interruption
| Hathazari-Raozan 230 kV Ckt-1 | 2022-10-04 14:04 | 2022-10-04 18:26 | 4:22 | T |  |  | 0 | No interruption
| Hathazari-Kaptai 132 kV Ckt-1 | 2022-10-13 08:19 | 2022-10-13 09:30 | 1:11 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Rangamati | Rangamati-Chandraghona 132 kV Ckt-2 | 2022-10-17 18:01 | 2022-10-17 18:09 | 0:08 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
| Rangamati-Chandraghona 132 kV Ckt-2 | 2022-10-18 17:16 | 2022-10-18 17:28 | 0:12 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Hathazari | Hathazari-Kaptai 132 kV Ckt-2 | 2022-10-29 11:34 | 2022-10-29 12:05 | 0:31 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
|  |  | Total : | 20:38 |  | Unserved Energy: |  | 0
Cumilla Grid Circle :
Cumilla(S) | Cumilla(S)-Tripur 132 kV both Ckts | 2022-10-02 02:45 | 2022-10-02 03:32 | 0:47 | T | Due to over load | 76 | 59.5333 | Power interruption
| Cumilla(S)-Tripur 132 kV both Ckts | 2022-10-02 02:45 | 2022-10-02 05:42 | 2:57 | T
Ashuganj | Ashuganj(S)-Ghorashal 230 kV Ckt-1 | 2022-10-03 08:39 | 2022-10-03 09:17 | 0:38 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
| Ashuganj-Sirajganj 230 kV Ckt-1 | 2022-10-04 14:04 | 2022-10-04 14:39 | 0:35 | T | Eastern Zone got blackout. | 0 | 0 | No interruption
| Ashuganj-Sirajganj 230 kV Ckt-2 | 2022-10-04 14:04 | 2022-10-04 15:21 | 1:17 | T |  | 0 | 0 | No interruption
| Ashuganj-Cumilla(N) 230 kV Ckt-1 | 2022-10-04 14:04 | 2022-10-04 15:33 | 1:29 | T |  | 0 | 0 | No interruption
| Ashuganj-Cumilla(N) 230 kV Ckt-2 | 2022-10-04 14:04 | 2022-10-04 16:00 | 1:56 | T |  | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Meghnaghat 230 kV Ckt-1 | 2022-10-04 14:04 | 2022-10-04 18:02 | 3:58 | T |  | 0 | 0 | No interruption
| Cumilla(N)-Bibiyana 230 kV Ckt-1 | 2022-10-04 14:04 | 2022-10-04 20:35 | 6:31 | T |  | 0 | 0 | No interruption
| Cumilla(N)-Bibiyana 230 kV Ckt-2 | 2022-10-04 14:04 | 2022-10-04 20:38 | 6:34 | T |  | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV Ckt-1 | 2022-10-04 14:04 | 2022-10-04 14:54 | 0:50 | T |  | 0 | 0 | No interruption
| Ashuganj-B.baria 132 kV Ckt-1 | 2022-10-04 14:04 | 2022-10-04 15:28 | 1:24 | T |  | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Sylhet 132 kV Ckt | 2022-10-04 14:04 | 2022-10-04 18:23 | 4:19 | T |  | 0 | 0 | No interruption
Bibiyana | Bibiyana-Kaliakoir 400 kV Ckt-1 | 2022-10-06 10:24 | 2022-10-06 11:26 | 1:02 | T | Tripped showing O/C. relay | 0 | 0 | No interruption
Feni | Feni-Chowmuhani 132 kV Ckt-1 | 2022-10-10 07:46 | 2022-10-10 07:53 | 0:07 | T | Tripped showing Oil leakage | 0 | 0 | No interruption
Sreemongal | Sreemongal-Shahjibazar 132 kV Ckt-1 | 2022-10-11 19:30 | 2022-10-11 20:30 | 1:00 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-BSRM 230 kV Ckt-1 | 2022-10-14 12:31 | 2022-10-14 15:00 | 2:29 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Ashuganj | Ashuganj-B.baria 132 kV Ckt-1 & 2 | 2022-10-14 20:49 | 2022-10-14 21:17 | 0:28 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Ashuganj 230 kV Ckt-2 | 2022-10-22 07:23 | 2022-10-22 07:39 | 0:16 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Daudkandi | Daudkandi-Cumilla(N) 132 kV Ckt-1 | 2022-10-24 09:28 | 2022-10-24 15:17 | 5:49 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Bibiyana | Bibiyana-Kaliakoir 400 kV Ckt-2 | 2022-10-24 22:02 | 2022-10-24 23:57 | 1:55 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV Ckt-2 | 2022-10-24 23:06 |  |  | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Daudkandi | Daudkandi-Cumilla(N) 132 kV Ckt-1 | 2022-10-24 22:21 | 2022-10-25 04:09 | 5:48 | T | Due to tree fall in the line | 0 | 0 | No interruption
| Daudkandi-Cumilla(N) 132 kV Ckt-2 | 2022-10-24 22:21 | 2022-10-25 04:15 | 5:54 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Feni | Feni-Chowmuhani 132 kV Ckt-1 | 2022-10-24 21:16 |  |  | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Chandpur | Chandpur-Chowmuhani 132 kV Ckt-1 | 2022-10-24 21:16 |  |  | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
| Chandpur-Kachua 132 kV Ckt-1 | 2022-10-24 21:35 | 2022-10-25 06:50 | 9:15 | T | Due to tree broken on this line | 0 | 0 | No interruption
Sylhet | Sylhet-Chattak 132 kV Ckt-1 | 2022-10-25 02:34 | 2022-10-25 02:44 | 0:10 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Meghnaghat 230 kV Ckt-1 | 2022-10-28 06:19 | 2022-10-28 08:44 | 2:25 | T | Due to red-hot maint. | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Sylhet 132 kV Ckt | 2022-10-30 07:40 | 2022-10-30 08:17 | 0:37 | T | Tripped showing E/F. relay. | 135 | 83.25 | Power interruption
|  |  | Total : | 70:30 |  | Unserved Energy: |  | 142.7833
Khulna Grid Circle :
Bagerhat | Bagerhat-Bhandaria 132 kV Ckt | 2022-10-24 15:40 | 2022-10-24 18:29 | 2:49 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Khulna(S) | Khulna(S)-Satkhira 132 kV Ckt-2 | 2022-10-30 03:22 | 2022-10-30 07:59 | 4:37 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
|  |  | Total : | 7:26 |  | Unserved Energy: |  | 0
HVDC Grid Circle :
Pabna | Pabna-Shahjadpur 132 kV Ckt | 2022-10-28 08:29 | 2022-10-28 11:50 | 3:21 | E/O | Due to Breaker maint.work | 0 | 0 | No interruption
Ishurdi | Ishurdi-Ghorashal 230 kV Ckt-2 | 2022-10-30 12:05 | 2022-10-30 12:05 | 0:00 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
|  |  | Total : | 3:21 |  | Unserved Energy: |  | 0
Bogura Grid Circle:
Amnura | Amnura-Chapai 132 kV Ckt | 2022-10-03 15:49 | 2022-10-03 18:50 | 3:01 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
| Amnura-Rajshahi 132 kV Ckt | 2022-10-03 15:49 | 2022-10-03 16:19 | 0:30 | T | Tripped showing O/C . relay. | 12 | 6 | Power interruption
Rajshahi | Rajshahi-HVDC 230 kV Ckt-1 | 2022-10-05 11:38 | 2022-10-05 11:45 | 0:07 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Godda | Godda-Rohanpur 400 kV Ckt | 2022-10-11 13:03 | 2022-10-11 14:02 | 0:59 | T | Tripped showing high voltage | 0 | 0 | No interruption
Naogaon | Naogaon-Joypurhat 132 kV Ckt | 2022-10-15 07:15 | 2022-10-15 07:42 | 0:27 | T | Tripped showing Dist. relay. | 30 | 13.5 | Power interruption
Bogura | Bogura-Natore 132 kV Ckt-2 | 2022-10-15 09:38 | 2022-10-15 14:24 | 4:46 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Rangpur | Rangpur-Rangpur confi.132 kV Ckt-2 | 2022-10-22 12:31 | 2022-10-22 12:46 | 0:15 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Naogaon | Naogaon-Joypurhat 132 kV Ckt | 2022-10-22 23:04 | 2022-10-22 23:15 | 0:11 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
|  |  | Total : | 10:16 |  | Unserved Energy: |  | 19.5
Others :
Maniknagar | Maniknagar-Matuail 132 kV Ckt | 2022-10-20 19:23 | 2022-10-20 23:37 | 4:14 | T | Due to red-hot maint.
| Maniknagar-Matuail 132 kV Ckt-2 | 2022-10-24 19:57 | 2022-10-24 19:57 | 0:00 | T | Due to bad weather | 0 | 0 | No interruption
4:14
|  |  | Total : |  |  | Unserved Energy: |  | 386.5667
Total outage period of Sub-station Equipment : |  |  |  | 238:55 | Hours
T = Tripping | [7 empty] | Executive Engineer
E/O = Emergency Outage | [7 empty] | Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-25
Page: 1/4 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: October 2022
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Mymensingh | 132 kV Bus-A | 2022-10-01 07:41 | 2022-10-01 07:41 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-1 | 2022-10-01 07:55 | 2022-10-01 07:55 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-2 | 2022-10-01 09:51 | 2022-10-01 11:04 | 1:13 | S/O | Due to C/M work | 0 | 0 | No interruption
Sherpur | 132/33 kV transformer T-1 | 2022-10-02 10:54 | 2022-10-02 17:03 | 6:09 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | 132/33 kV transformer T-1 | 2022-10-06 06:48 | 2022-10-06 09:49 | 3:01 | S/O | Due to loop miant. | 20 | 60.3333 | Power interruption
Manikganj | 132/33 kV transformer T-4 | 2022-10-06 13:09 | 2022-10-06 14:17 | 1:08 | S/O | Due to C/M work | 0 | 0 | No interruption
Tangail | 132/33 kV transformer T-3 | 2022-10-07 08:06 | 2022-10-07 09:37 | 1:31 | S/O | Due to C/M work | 25 | 37.9167 | Power interruption
Jamalpur | 132/33 kV transformer T-1 | 2022-10-07 11:24 | 2022-10-07 12:58 | 1:34 | S/O | Due to 33 kV feeder fault | 0 | 0 | No interruption
| 132/33 kV transformer T-2 | 2022-10-07 12:03 | 2022-10-07 12:58 | 0:55 | S/O |  | 20 | 18.3333 | Power interruption
| 132/33 kV transformers T-1 & T2 | 2022-10-08 12:20 | 2022-10-08 14:51 | 2:31 | S/O | Due to C/M work | 40 | 100.6667 | Power interruption
Netrakona | 132/33 kV transformer T-2 | 2022-10-11 08:30 | 2022-10-11 11:16 | 2:46 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-3 | 2022-10-11 11:41 | 2022-10-11 14:12 | 2:31 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | 132/33 kV transformer T-1 | 2022-10-12 07:35 |  |  | S/O | Due to D/W work | 0 | 0 | No interruption
Manikganj | 132/33 kV transformer T-4 | 2022-10-12 09:48 | 2022-10-12 10:35 | 0:47 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | 230/132 kV transformer T01 | 2022-10-12 15:16 | 2022-10-12 16:40 | 1:24 | S/O | Due to C/M work | 0 | 0 | No interruption
Joydevpur | 132/33 kV transformer T-4 | 2022-10-12 17:56 | 2022-10-12 18:10 | 0:14 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | 132/33 kV transformer T-3 | 2022-10-12 15:50 | 2022-10-12 18:38 | 2:48 | S/O | Due to C/M work | 20 | 56 | Power interruption
Joydevpur | 132/33 kV transformer T-4 | 2022-10-13 02:47 | 2022-10-13 02:47 | 0:00 |  | Due to for safety due to fire at BOF feeder | 0 | 0 | No interruption
Aminbazar | 230/132 kV transformer T01 | 2022-10-13 06:04 | 2022-10-13 06:04 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | 132/33 kV transformer T-2 | 2022-10-13 09:10 | 2022-10-13 13:20 | 4:10 | S/O | Due to D/W work | 0 | 0 | No interruption
Kishoreganj | 132/33 kV transformer T-3 | 2022-10-16 09:09 | 2022-10-16 16:23 | 7:14 | S/O | Due to A/M work | 0 | 0 | No interruption
Sherpur | 132/33 kV transformer T-1 | 2022-10-17 08:12 | 2022-10-17 16:01 | 7:49 | S/O | Due to A/M work | 0 | 0 | No interruption
Kallyanpur | 132 kV Bus-1 | 2022-10-18 08:57 | 2022-10-18 17:06 | 8:09 | S/O | Due to A/M work | 0 | 0 | No interruption
Sherpur | 132/33 kV transformer T-2 | 2022-10-18 08:40 | 2022-10-18 16:13 | 7:33 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | 230/132 kV transformer T03 | 2022-10-18 15:02 | 2022-10-18 17:50 | 2:48 | S/O | Due to C/M work | 0 | 0 | No interruption
Sherpur | 132/33 kV transformer T-2 | 2022-10-19 08:25 | 2022-10-19 16:19 | 7:54 | S/O | Due to A/M work | 0 | 0 | No interruption
Kishoreganj | 132/33 kV transformer T-1 | 2022-10-19 08:46 | 2022-10-19 11:48 | 3:02 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-3 | 2022-10-19 08:46 | 2022-10-19 10:10 | 1:24 | S/O | Due to A/M work | 20 | 28 | Power interruption
Metro Rail | 132/33 kV transformer T-1 | 2022-10-19 12:09 | 2022-10-19 12:09 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Sherpur | 132/33 kV transformer T-2 | 2022-10-20 08:16 | 2022-10-20 16:47 | 8:31 | S/O | Due to A/M work | 0 | 0 | No interruption
Kallyanpur | 132 kV Bus-1 | 2022-10-20 09:15 | 2022-10-20 15:16 | 6:01 | S/O | Due to A/M work | 0 | 0 | No interruption
Mirpur | 132 kV reserve Bus | 2022-10-20 09:27 | 2022-10-20 17:30 | 8:03 | S/O | Due to A/M work | 0 | 0 | No interruption
Sherpur | 132/33 kV transformer T-3 | 2022-10-22 08:20 | 2022-10-22 16:34 | 8:14 | S/O | Due to C/M work | 0 | 0 | No interruption
Kallyanpur | 132 kV Bus-2 | 2022-10-22 11:35 | 2022-10-22 16:38 | 5:03 | S/O | Due to A/M work | 0 | 0 | No interruption
Dhamrai | 132/33 kV transformer T-1 | 2022-10-22 15:18 | 2022-10-22 17:28 | 2:10 | S/O | Due to C/M work | 20 | 43.3333 | Power interruption
Sherpur | 132/33 kV transformer T-3 | 2022-10-23 08:33 | 2022-10-23 16:35 | 8:02 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132 kV Bus coupler | 2022-10-26 08:56 | 2022-10-26 15:52 | 6:56 | S/O | Due to A/M work | 0 | 0 | No interruption
Joydevpur | 132/33 kV transformer T-3 | 2022-10-26 15:57 | 2022-10-26 17:40 | 1:43 | S/O | Due to C/M work | 90 | 154.5 | Power interruption
Sherpur | 132 kV Bus-A | 2022-10-27 08:49 | 2022-10-27 12:08 | 3:19 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | 132 kV Bus-1 | 2022-10-27 09:52 | 2022-10-27 17:10 | 7:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Savar | 132 kV Bus-A | 2022-10-29 11:11 | 2022-10-29 15:21 | 4:10 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-2 | 2022-10-29 11:20 | 2022-10-29 17:17 | 5:57 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132 kV Bus-B | 2022-10-29 16:10 | 2022-10-29 18:11 | 2:01 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-1 | 2022-10-29 17:20 | 2022-10-29 18:07 | 0:47 | S/O | Due to C/M work | 0 | 0
Mymensingh | 132/33 kV transformer T-3 | 2022-10-30 16:40 | 2022-10-30 18:05 | 1:25 | S/O | Due to C/M work | 10 | 14.1667 | Power interruption
|  |  | Total : | 158:15 |  | Unserved Energy: |  | 513.25 |  |  | 54 | 634.8
Dhaka (South) Grid Circle : | [11 empty] | 39.3333
Rampura | 132/33 kV transformer T-1 | 2022-10-02 13:33 | 2022-10-02 13:33 | 0:00 | S/O | Due to SAS work | 0 | 0 | No interruption |  |  | 674.1333
| 132/33 kV transformer T-2 | 2022-10-02 15:13 | 2022-10-02 18:07 | 2:54 | S/O |  | 0 | 0 | No interruption
Sonargaon | 132/33 kV transformer T-1 with 33 kV Bus | 2022-10-03 06:40 | 2022-10-03 06:40 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Ghorashal | 230/132 kV transformer T01 | 2022-10-09 14:16 | 2022-10-09 15:15 | 0:59 | S/O | Due to C/M work | 0 | 0 | No interruption
Ghorashal AIS | 230/132 kV transformer T01 | 2022-10-14 06:11 | 2022-10-14 06:11 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Narsingdi | 132/33 kV transformer T-1 | 2022-10-16 06:02 | 2022-10-16 08:01 | 1:59 | S/O | Due to C/M work | 0 | 0 | No interruption
Savar | 33 kV Bus-B | 2022-10-16 09:38 | 2022-10-16 20:08 | 10:30 | S/O | Due to C/M work | 0 | 0 | No interruption
Fatulla | 132/33 kV transformer GT-2 | 2022-10-16 09:43 | 2022-10-16 17:32 | 7:49 | S/O | Due to C/M work | 0 | 0 | No interruption
Kamangirchar | 132/33 kV transformer T-2 | 2022-10-18 09:57 | 2022-10-18 18:37 | 8:40 | S/O | Due to A/M work | 0 | 0 | No interruption
Keraniganj | 132/33 kV transformer T-3 | 2022-10-18 08:14 | 2022-10-18 15:24 | 7:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Kamangirchar | 132/33 kV transformer T-3 | 2022-10-19 09:30 | 2022-10-19 16:28 | 6:58 | S/O | Due to A/M work | 0 | 0 | No interruption
Haripur | 132 kV Bus | 2022-10-19 14:39 | 2022-10-19 17:08 | 2:29 | S/O | Due to C/M work | 0 | 0 | No interruption
Sreenagar | 132/33 kV transformer T-2 | 2022-10-20 10:41 | 2022-10-20 14:15 | 3:34 | S/O | Due to C/M work | 0 | 0 | No interruption
Sonargaon | 132/33 kV transformer T-2 | 2022-10-22 08:21 | 2022-10-22 10:00 | 1:39 | S/O | Due to C/M work | 0 | 0 | No interruption
Bhulta | 132/33 kV transformer T-1 | 2022-10-26 08:10 | 2022-10-26 11:51 | 3:41 | S/O | Due to C/M work | 0 | 0 | No interruption
Tongi | 132 kV Bus -2 | 2022-10-29 09:40 | 2022-10-29 16:57 | 7:17 | S/O | Due to A/M work | 0 | 0 | No interruption
Kazla | 132/33 kV transformer T-2 | 2022-10-30 09:21 | 2022-10-30 16:48 | 7:27 | S/O | Due to A/M work | 0 | 0 | No interruption
Shyampur | 132/33 kV transformer T-1 | 2022-10-31 09:05 | 2022-10-31 20:02 | 10:57 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 84:03 |  | Unserved Energy: |  | 0
Chattogram Grid Circle :
Halishahar | 132/33 kV transformer T2 | 2022-10-02 07:01 | 2022-10-02 07:01 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Rampur | 230/132 kV transformer T-R2 | 2022-10-03 10:11 | 2022-10-03 12:17 | 2:06 | S/O | Due to SAS work | 0 | 0 | No interruption
| 230/132 kV transformer T-R1 | 2022-10-03 12:25 | 2022-10-03 13:14 | 0:49 | S/O | Due to SAS work | 0 | 0 | No interruption
Baroierhat | 132/33 kV transformer T2 | 2022-10-06 07:19 | 2022-10-06 09:02 | 1:43 | S/O | Due to C/M work | 16 | 27.4667 | Power interruption
| 132/33 kV transformer T1 | 2022-10-06 09:30 | 2022-10-06 11:04 | 1:34 | S/O | Due to C/M work | 0 | 0 | No interruption
Halishahar | 132/33 kV transformer T3 | 2022-10-06 13:04 | 2022-10-06 13:57 | 0:53 | S/O | Due to C/M work | 0 | 0 | No interruption
Cox'sbazar | 132/33 kV transformer T1 | 2022-10-07 07:05 | 2022-10-07 07:33 | 0:28 | S/O | Due to C/M work | 12 | 5.6 | Power interruption
Hathazari | 132/33 kV transformer T1 | 2022-10-11 08:17 | 2022-10-11 18:43 | 10:26 | S/O | Due to A/M work | 0 | 0 | No interruption
Madunaghat | 132/33 kV transformer T2 | 2022-10-14 07:42 | 2022-10-14 11:00 | 3:18 | S/O | Due to replacement work | 30 | 99 | Power interruption
Halishahar | 132/33 kV transformer T1 | 2022-10-14 09:54 | 2022-10-14 12:10 | 2:16 | S/O | Due to C/M work | 0 | 0 | No interruption | 120.3333
Rampur | 132/33 kV transformer T2 | 2022-10-15 06:40 | 2022-10-15 06:40 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption | 557.9167
Madunaghat | 132/33 kV transformer T2 | 2022-10-15 09:13 | 2022-10-15 10:15 | 1:02 | S/O | Due to D/W work | 30 | 31 | Power interruption
Sholoshahar | 132/33 kV transformer T2 | 2022-10-15 10:53 | 2022-10-15 12:27 | 1:34 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer T1 | 2022-10-15 12:42 | 2022-10-15 13:28 | 0:46 | S/O | Due to A/M work | 0 | 0 | No interruption
Dohazari | 132/33 kV transformer T2 | 2022-10-16 08:34 | 2022-10-16 08:34 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Halishahar | 132/33 kV transformer T1 | 2022-10-17 10:48 | 2022-10-17 11:07 | 0:19 | S/O | Due to C/M work | 0 | 0 | No interruption
Hathazari | 230/132 kV transformer MT-3 | 2022-10-18 10:16 | 2022-10-18 11:20 | 1:04 | S/O | Due to D/W work | 0 | 0 | No interruption
Agrabad | 132/33 kV transformer T1 | 2022-10-19 09:35 | 2022-10-19 09:50 | 0:15 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV transformer T2 | 2022-10-19 10:00 | 2022-10-19 10:15 | 0:15 | S/O | Due to D/W work | 0 | 0 | No interruption | 678.25
Dohazari | 33 kV Bus | 2022-10-20 07:10 | 2022-10-20 09:06 | 1:56 | S/O | Due to C/M work | 25 | 48.3333 | Power interruption
Kalurghat | 132/33 kV transformer T2 | 2022-10-20 10:20 | 2022-10-20 14:35 | 4:15 | S/O | Due to D/W work | 0 | 0 | No interruption
Rampur | 132/33 kV transformer T1 | 2022-10-20 10:30 | 2022-10-20 11:04 | 0:34 | S/O | Due to C/M work | 0 | 0 | No interruption
| 230/132 kV transformer T-01 | 2022-10-20 11:14 | 2022-10-20 12:16 | 1:02 | S/O | Due to C/M work | 0 | 0 | No interruption
| 230/132 kV transformer T-02 | 2022-10-20 11:44 | 2022-10-20 12:13 | 0:29 | S/O | Due to C/M work | 0 | 0 | No interruption
Khulshi | 132/33 kV transformer T2 | 2022-10-21 07:45 | 2022-10-21 08:48 | 1:03 | S/O | Due to 33 Bus maint. | 0 | 0 | No interruption
Cox'sbazar | 132/33 kV transformer T3 | 2022-10-26 15:13 | 2022-10-26 16:29 | 1:16 | S/O | Due to C/M work | 35 | 44.3333 | Power interruption
Halishahar | 132/33 kV transformer T1 | 2022-10-29 07:12 | 2022-10-29 07:12 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 39:23 |  | Unserved Energy : |  | 255.7333
Cumilla Grid Circle :
Kachua | 132/33 kV transformer T2 | 2022-10-01 22:12 | 2022-10-01 23:46 | 1:34 | S/O | Due to C/M work | 0 | 0 | No interruption
Chandpur | 132/33 kV transformer T2 | 2022-10-02 09:50 | 2022-10-02 21:32 | 11:42 | S/O | Due to C/M work | 0 | 0 | No interruption
Bibiyana | 400/230 kV transformer T01 | 2022-10-07 09:49 | 2022-10-07 21:24 | 11:35 | S/O | Due to C/M work | 0 | 0 | No interruption
Feni | 132/33 kV transformer T2 | 2022-10-10 07:18 | 2022-10-10 07:18 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Cumilla(N) | 132/33 kV transformer T5 | 2022-10-22 09:11 | 2022-10-22 10:23 | 1:12 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformers T3 & T4 | 2022-10-22 16:25 | 2022-10-22 16:45 | 0:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Sunamganj | 132/33 kV transformer T1 | 2022-10-23 08:36 | 2022-10-23 14:52 | 6:16 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T2 | 2022-10-23 14:59 | 2022-10-23 19:26 | 4:27 | S/O | Due to A/M work | 0 | 0 | No interruption
Ramganj | 132/33 kV transformer T1 | 2022-10-26 08:22 | 2022-10-26 09:22 | 1:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Cumilla(N) | 132/33 kV transformer T4 | 2022-10-26 09:25 | 2022-10-26 13:43 | 4:18 | S/O | Due to C/M work | 0 | 0 | No interruption
Chowddagram | 132/33 kV transformer T1 | 2022-10-27 10:06 | 2022-10-27 13:45 | 3:39 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer T2 | 2022-10-27 13:48 | 2022-10-27 15:50 | 2:02 | S/O | Due to C/M work | 0 | 0 | No interruption
Chattak | 132/33 kV transformer T1 | 2022-10-29 09:11 | 2022-10-29 13:19 | 4:08 | S/O | Due to C/M work | 20 | 82.6667 | Power interruption
Ashuganj | 132/33 kV transformer T3 | 2022-10-29 11:17 | 2022-10-29 18:03 | 6:46 | S/O | Due to C/M work | 0 | 0 | No interruption
Chattak | 132/33 kV transformer T3 | 2022-10-29 16:14 | 2022-10-29 18:00 | 1:46 | S/O | Due to C/M work | 0 | 0 | No interruption
Fenchuganj | 132/33 kV transformer T2 | 2022-10-30 08:47 | 2022-10-30 15:10 | 6:23 | S/O | Due to A/M work | 0 | 0 | No interruption
Sylhet | 132/33 kV transformer T2 | 2022-10-30 10:34 | 2022-10-30 11:55 | 1:21 | S/O | Due to 33 kV feeder maint.work | 0 | 0 | No interruption
Fenchuganj | 132/33 kV transformer T1 | 2022-10-30 15:26 | 2022-10-30 17:20 | 1:54 | S/O | Due to C/M work | 0 | 0 | No interruption
Sylhet | 33 kV Bus-2 | 2022-10-31 07:27 |  |  | S/O | Due to C/M work by PDB | 0 | 0 | No interruption
|  |  | Total : | 70:23 |  | Unserved Energy : |  | 82.6667
Khulna Grid Circle : | [10 empty] | 251.2167
Sariatpur | 132/33 kV transformer T1 | 2022-10-01 07:11 | 2022-10-01 07:11 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption |  | 113.55
Khulna(S) | 230/132 kV Transformer T01 | 2022-10-01 09:18 | 2022-10-01 16:58 | 7:40 | S/O | Due to A/M work | 0 | 0 | No interruption
| 230/132 kV Transformer T01 | 2022-10-03 09:20 | 2022-10-03 15:02 | 5:42 | S/O | Due to A/M work | 0 | 0 | No interruption
Shariatpur | 132/33 kV transformer T2 | 2022-10-03 11:43 | 2022-10-03 17:27 | 5:44 | S/O | Due to A/M work | 10 | 57.3333 | Power interruption
Shariatpur | 132/33 kV transformer T2 | 2022-10-04 07:12 |  |  | S/O | Due to A/M work | 0 | 0
Khulna(S) | 230/132 kV Transformer T01 | 2022-10-05 09:20 | 2022-10-05 22:30 | 13:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Shariatpur | 132 kV Bay | 2022-10-06 07:06 | 2022-10-06 07:06 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulna(C) | 132/33 kV transformer T2 | 2022-10-09 09:32 | 2022-10-09 11:40 | 2:08 | S/O | Due to C/M work | 0 | 0 | No interruption
Rajbari | 132/33 kV transformers T1 | 2022-10-10 08:34 | 2022-10-10 15:10 | 6:36 | S/O | Due to A/M work | 0 | 0 | No interruption |  | 364.7667
Khulna(S) | 230/132 kV Transformer T01 | 2022-10-10 13:04 | 2022-10-10 13:55 | 0:51 | S/O | Due to maint.work | 0 | 0 | No interruption
Rajbari | 132/33 kV transformer T1 | 2022-10-11 08:06 | 2022-10-11 15:47 | 7:41 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulna(C) | 132/33 kV transformer T1 | 2022-10-12 08:12 | 2022-10-12 17:08 | 8:56 | S/O | Due to A/M work | 0 | 0 | No interruption
Rajbari | 132/33 kV transformer T2 | 2022-10-12 08:11 | 2022-10-12 15:46 | 7:35 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulna(S) | 230/132 kV Transformer T02 | 2022-10-12 09:09 | 2022-10-12 14:35 | 5:26 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulna(C) | 132/33 kV transformer T1 | 2022-10-13 07:58 | 2022-10-13 15:24 | 7:26 | S/O | Due to A/M work | 0 | 0 | No interruption
Rajbari | 132/33 kV transformer T2 | 2022-10-13 08:11 | 2022-10-13 15:44 | 7:33 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulna(C) | 132/33 kV transformer T2 | 2022-10-13 09:15 | 2022-10-13 15:55 | 6:40 | S/O | Due to A/M work | 0 | 0 | No interruption
Gopalganj | 400/132 kV Transformers T1 | 2022-10-14 07:34 | 2022-10-14 07:34 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
| 400/132 kV Transformers T2 | 2022-10-14 07:41 | 2022-10-14 07:41 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Rajbari | 132 kV Bus | 2022-10-15 08:55 | 2022-10-15 15:09 | 6:14 | S/O | Due to C/M work | 0 | 0 | No interruption
Khulna(C) | 230/132 kV Transformer T03 | 2022-10-15 09:31 | 2022-10-15 15:15 | 5:44 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T2 | 2022-10-15 07:59 | 2022-10-15 15:15 | 7:16 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T2 | 2022-10-16 07:45 | 2022-10-16 15:46 | 8:01 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulna(S) | 230/132 kV Transformer T03 | 2022-10-16 09:16 | 2022-10-16 16:50 | 7:34 | S/O | Due to A/M work | 0 | 0 | No interruption
Rajbari | 33/04 kV auxiliary transformer T2 | 2022-10-16 10:58 | 2022-10-16 13:35 | 2:37 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulna(C) | 132/33 kV transformer T2 | 2022-10-17 08:08 | 2022-10-17 15:16 | 7:08 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulna(S) | 230/132 kV Transformer T03 | 2022-10-17 08:32 | 2022-10-17 14:09 | 5:37 | S/O | Due to A/M work | 0 | 0 | No interruption
Gopalganj | 132/33 kV transformer T1 | 2022-10-18 07:17 | 2022-10-18 07:17 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulna(C) | 132/33 kV transformer T3 | 2022-10-18 08:01 | 2022-10-18 16:16 | 8:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Noapara | 132 kV main Bus | 2022-10-19 07:25 | 2022-10-19 10:00 | 2:35 | S/O | Due to A/M work | 0 | 0 | No interruption
Gopalganj(O) | 132/33 kV transformer T1 | 2022-10-19 07:15 | 2022-10-19 07:15 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulna(C) | 132/33 kV transformer T3 | 2022-10-19 08:06 | 2022-10-19 15:37 | 7:31 | S/O | Due to A/M work | 0 | 0 | No interruption
Bagerhat | 132/33 kV transformer T1 | 2022-10-19 09:04 | 2022-10-19 16:19 | 7:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Payra | 400/132 kV Transformer T02 | 2022-10-19 09:35 | 2022-10-19 09:35 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Rajbari | 132/33 kV transformer T1 | 2022-10-20 07:08 | 2022-10-20 08:25 | 1:17 | S/O | Due to C/M work | 14 | 17.9667 | Power interruption
Bagerhat | 132/33 kV transformer T2 | 2022-10-20 09:14 | 2022-10-20 16:44 | 7:30 | S/O | Due to A/M work | 0 | 0 | No interruption
Patuakhali | 132/33 kV transformers T3 |  | 2022-10-20 20:25 |  | S/O | After maint.work | 0 | 0 | No interruption
Faridpur | 132/33 kV transformer T1 | 2022-10-21 07:37 | 2022-10-21 09:04 | 1:27 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer T3 | 2022-10-21 07:35 | 2022-10-21 09:08 | 1:33 | S/O | Due to C/M work | 0 | 0 | No interruption
Bagerhat | 132/33 kV transformer T1 | 2022-10-21 09:11 | 2022-10-21 13:06 | 3:55 | S/O | Due to C/M work | 0 | 0 | No interruption
Madaripur | 132/33 kV transformer T3 | 2022-10-21 11:18 | 2022-10-21 11:25 | 0:07 | S/O | Due to C/M work | 10 | 1.1667 | Power interruption
Gopalganj(O) | 132/33 kV transformer T2 | 2022-10-22 07:28 | 2022-10-22 07:28 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Bagerhat | 132/33 kV transformer T2 | 2022-10-22 09:10 | 2022-10-22 16:32 | 7:22 | S/O | Due to A/M work | 0 | 0 | No interruption
Gopalganj(O) | 132/33 kV transformer T2 | 2022-10-23 07:30 |  |  | S/O | Due to A/M work | 0 | 0 | No interruption
Bagerhat | 132/33 kV transformer T2 | 2022-10-23 09:14 | 2022-10-23 14:58 | 5:44 | S/O | Due to A/M work | 0 | 0 | No interruption
Madaripur | 132/33 kV transformer T3 | 2022-10-23 11:00 | 2022-10-23 12:32 | 1:32 | S/O | Due to 33 kV loop maint.work | 0 | 0 | No interruption
Goalpara | 132/33 kV transformer T5 | 2022-10-26 08:24 | 2022-10-26 18:08 | 9:44 | S/O | Due to A/M work | 0 | 0 | No interruption
Noapara | 132 kV Bus-B | 2022-10-27 09:10 | 2022-10-27 11:04 | 1:54 | S/O | Due to D/W work | 0 | 0 | No interruption
Madaripur | 132/33 kV transformer T1 | 2022-10-27 07:48 | 2022-10-27 07:48 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Noapara | 132 kV Bus-B | 2022-10-27 09:10 | 2022-10-27 11:04 | 1:54 | S/O | Due to A/M work | 0 | 0 | No interruption
Mongla | 132/33 kV transformer T1 | 2022-10-28 08:35 | 2022-10-28 08:35 | 0:00 | S/O |  | 0 | 0 | No interruption
Narail | 132/33 kV transformer T2 | 2022-10-29 07:07 | 2022-10-29 09:05 | 1:58 | S/O | Due to C/M work | 20 | 39.3333 | Power interruption
Madaripur | 132/33 kV transformer T2 | 2022-10-29 08:29 | 2022-10-29 16:12 | 7:43 | S/O | Due to A/M work | 0 | 0 | No interruption
Goalpara | 132/33 kV transformer T6 | 2022-10-29 08:25 | 2022-10-29 16:32 | 8:07 | S/O | Due to A/M work | 0 | 0 | No interruption
Payra | 132 kV Bus-A | 2022-10-29 10:24 | 2022-10-29 10:24 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Madaripur | 132/33 kV transformer T2 | 2022-10-30 07:33 | 2022-10-30 07:33 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Goalpara | 132/33 kV transformer T6 | 2022-10-30 08:36 | 2022-10-30 16:19 | 7:43 | S/O | Due to A/M work | 0 | 0 | No interruption
Mongla | 132/33 kV transformer T1 |  | 2022-10-30 08:48 |  | S/O | After maint.work | 0 | 0 | No interruption
| 132/33 kV transformer T2 | 2022-10-30 09:58 | 2022-10-30 09:58 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Satkhira | 132/33 kV transformer T1 | 2022-10-30 19:56 | 2022-10-30 20:57 | 1:01 | S/O | Due to C/M work by PBS | 40 | 40.6667 | Power interruption
Madaripur | 132/33 kV transformer T3 | 2022-10-31 08:02 | 2022-10-31 16:02 | 8:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Goalpara | 132/33 kV transformer T6 | 2022-10-31 08:32 | 2022-10-31 15:04 | 6:32 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 253:58 |  | Unserved Energy : |  | 156.4667
HVDC Grid Circle
Benapole | 132/33 kV transformer T1 | 2022-10-01 15:13 | 2022-10-01 16:00 | 0:47 | S/O | Due to D/W work | 20 | 15.6667 | Power interruption
Pabna | 132/33 kV transformer T2 with 33 kV Bus | 2022-10-02 06:40 | 2022-10-02 07:50 | 1:10 | S/O | Due to C/M work by PBS | 25 | 29.1667 | Power interruption
Jhenaidah | 132/33 kV transformer T1 | 2022-10-20 07:13 | 2022-10-20 11:19 | 4:06 | S/O | Due to C/M work by PBS | 15 | 61.5 | Power interruption
Ishurdi | 230/132 kV Transformer T01 | 2022-10-20 09:18 | 2022-10-20 13:05 | 3:47 | S/O | Due to C/M work | 0 | 0 | No interruption
| 230/132 kV Transformer T03 | 2022-10-20 13:10 | 2022-10-20 17:03 | 3:53 | S/O | Due to C/M work | 0 | 0 | No interruption
Shahjadpur | 132/33 kV transformer T2 | 2022-10-23 12:03 | 2022-10-23 13:04 | 1:01 | S/O | Due to C/M work | 0 | 0 | No interruption
Pabna | 132/33 kV transformer T3 | 2022-10-24 10:13 | 2022-10-24 11:11 | 0:58 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer T2 | 2022-10-24 11:11 | 2022-10-24 15:56 | 4:45 | S/O | Due to C/M work | 0 | 0 | No interruption
Shahjadpur | 132/33 kV transformer T1 | 2022-10-26 10:10 | 2022-10-26 13:45 | 3:35 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer T4 | 2022-10-27 08:44 | 2022-10-27 13:24 | 4:40 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 28:42 |  | Unserved Energy : |  | 106.3333
Bogura Grid Circle:
Palshbari | 132/33 kV transformers T3 & T4 | 2022-10-02 20:40 | 2022-10-02 22:04 | 1:24 | S/O | Due to 33 kV Bus coupler DS Y-phase loop out | 40 | 56 | Power interruption
Bogura(O) | 132 kV Bus-1 | 2022-10-03 12:47 |  |  | S/O | Due to C/M work | 0 | 0 | No interruption
Jaldhaka | 132/33 kV transformer T2 | 2022-10-05 10:45 | 2022-10-05 12:15 | 1:30 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer T1 | 2022-10-06 10:58 | 2022-10-06 12:47 | 1:49 | S/O | Due to C/M work | 0 | 0 | No interruption
Naogaon | 132/33 kV transformer T3 | 2022-10-08 19:58 | 2022-10-08 21:10 | 1:12 | S/O | Due to C/M work | 0 | 0 | No interruption | 2205.7833
Sherpur | 132/33 kV transformer T1 | 2022-10-15 08:12 | 2022-10-15 16:11 | 7:59 | S/O | Due to A/M work | 0 | 0 | No interruption | 177.8167
| 132/33 kV transformer T1 | 2022-10-16 08:12 | 2022-10-16 17:07 | 8:55 | S/O | Due to A/M work | 0 | 0 | No interruption | 0
Palshbari | 132/33 kV transformer T2 | 2022-10-17 08:40 | 2022-10-17 15:28 | 6:48 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T2 | 2022-10-18 08:50 | 2022-10-18 15:27 | 6:37 | S/O | Due to A/M work | 0 | 0 | No interruption
Charsayedpur | 132/33 kV transformer T1 | 2022-10-18 10:24 | 2022-10-18 17:46 | 7:22 | S/O | Due to A/M work | 0 | 0 | No interruption
Thakurgaon | 132/33 kV transformer T1 | 2022-10-19 08:20 | 2022-10-19 16:56 | 8:36 | S/O | Due to A/M work | 0 | 0 | No interruption
Saidpur | 132/33 kV transformer T2 | 2022-10-19 08:18 | 2022-10-19 15:45 | 7:27 | S/O | Due to A/M work | 0 | 0 | No interruption
Palashbari | 132/33 kV transformer T1 | 2022-10-19 08:30 | 2022-10-19 15:33 | 7:03 | S/O | Due to A/M work | 0 | 0 | No interruption
Charsayedpur | 132/33 kV transformer GT2 | 2022-10-20 09:47 | 2022-10-20 16:51 | 7:04 | S/O | Due to A/M work | 0 | 0 | No interruption
Thakurgaon | 132/33 kV transformer T1 | 2022-10-20 08:08 | 2022-10-20 15:38 | 7:30 | S/O | Due to A/M work | 0 | 0 | No interruption
Saidpur | 132/33 kV transformer T2 | 2022-10-20 08:25 | 2022-10-20 15:55 | 7:30 | S/O | Due to A/M work | 0 | 0 | No interruption
Palashbari | 132/33 kV transformer T1 | 2022-10-20 08:40 | 2022-10-20 15:20 | 6:40 | S/O | Due to A/M work | 0 | 0 | No interruption
Natore | 132/33 kV transformer T3 | 2022-10-21 07:06 | 2022-10-21 11:54 | 4:48 | S/O | Due to C/M work | 7 | 33.6 | Power interruption
| 132/33 kV transformer T1 | 2022-10-22 07:04 |  |  | S/O | Due to C/M work | 0 | 0 | No interruption
Thakurgaon | 132/33 kV transformer T2 | 2022-10-22 08:17 | 2022-10-22 14:14 | 5:57 | S/O | Due to A/M work | 0 | 0 | No interruption
Kurigram | 132/33 kV transformer T1 | 2022-10-22 08:44 | 2022-10-22 11:31 | 2:47 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T2 | 2022-10-22 11:34 | 2022-10-22 13:40 | 2:06 | S/O | Due to A/M work | 0 | 0 | No interruption
Thakurgaon | 132/33 kV transformer T1 | 2022-10-22 14:35 | 2022-10-22 22:18 | 7:43 | S/O | Due to C/M work | 0 | 0 | No interruption
Niamatpur | 132/33 kV transformerT1 | 2022-10-22 15:51 | 2022-10-22 17:00 | 1:09 | S/O | Due to C/M work | 20 | 23 | Power interruption
Rangpur | 132/33 kV transformerT1 | 2022-10-23 08:15 | 2022-10-23 15:45 | 7:30 | S/O | Due to A/M work | 10 | 75 | Power interruption
Thakurgaon | 132/33 kV transformer T2 | 2022-10-23 10:25 | 2022-10-23 15:37 | 5:12 | S/O | Due to A/M work | 0 | 0 | No interruption
Rangpur | 132/33 kV transformerT2 | 2022-10-24 08:42 | 2022-10-24 14:28 | 5:46 | S/O | Due to A/M work | 10 | 57.6667 | Power interruption
Saidpur | 132/33 kV transformerT3 | 2022-10-24 08:25 | 2022-10-24 16:09 | 7:44 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformerT4 | 2022-10-26 08:27 | 2022-10-26 18:27 | 10:00 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformerT2 | 2022-10-26 08:30 | 2022-10-26 15:50 | 7:20 | S/O | Due to A/M work | 20 | 146.6667 | Power interruption
Panchugarh | 132/33 kV transformerT1 | 2022-10-27 08:10 | 2022-10-27 15:10 | 7:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Rangpur | 132/33 kV transformerT3 | 2022-10-27 08:20 | 2022-10-27 16:54 | 8:34 | S/O | Due to A/M work | 0 | 0 | No interruption
Mohastangarh | 132 kV Bus coupler | 2022-10-27 09:13 | 2022-10-27 13:28 | 4:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Sherpur(Bogura) | 132 kV Bus-1 | 2022-10-28 09:11 | 2022-10-28 17:33 | 8:22 | S/O | Due to A/M work | 0 | 0 | No interruption
Panchugarh | 132/33 kV transformerT1 | 2022-10-29 08:06 | 2022-10-29 15:45 | 7:39 | S/O | Due to A/M work | 0 | 0 | No interruption
Sherpur(Bogura) | 132 kVmain Bus-2 | 2022-10-29 09:56 | 2022-10-29 13:24 | 3:28 | S/O | Due to A/M work | 0 | 0 | No interruption
Saidpur | 132/33 kV transformerT5 | 2022-10-29 08:23 | 2022-10-29 15:08 | 6:45 | S/O | Due to A/M work | 0 | 0 | No interruption
Rangpur | 132 kV Bus coupler | 2022-10-29 10:15 | 2022-10-29 12:40 | 2:25 | S/O | Due to A/M work | 0 | 0 | No interruption
Panchugarh | 132/33 kV transformerT2 | 2022-10-30 08:10 | 2022-10-30 15:30 | 7:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Saidpur | 132/33 kV transformerT5 | 2022-10-30 08:10 | 2022-10-30 15:30 | 7:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Palashbari | 132/33 kV transformer T3 | 2022-10-30 08:52 | 2022-10-30 15:55 | 7:03 | S/O | Due to A/M work | 0 | 0 | No interruption
Panchugarh | 132/33 kV transformerT2 | 2022-10-31 08:14 | 2022-10-31 15:32 | 7:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Palashbari | 132/33 kV transformer T3 | 2022-10-31 09:20 | 2022-10-31 14:22 | 5:02 | S/O | Due to A/M work | 0 | 0 | No interruption
Saidpur | 132 kV Bus coupler | 2022-10-31 09:28 | 2022-10-31 13:20 | 3:52 | S/O | Due to A/M work | 0 | 0 | No interruption
Joypurhat | 132 kV Bus coupler | 2022-10-31 10:20 | 2022-10-31 13:21 | 3:01 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 252:52 |  | Unserved Energy : |  | 391.9333
Others :
Ashuganj | 230/132 kV transformer OAT-12 | 2022-10-22 08:18 | 2022-10-22 10:36 | 2:18 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformerTr1 | 2022-10-29 08:33 | 2022-10-29 08:33 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformerT4 | 2022-10-30 10:19 | 2022-10-30 19:01 | 8:42 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformerT4 | 2022-10-31 10:37 | 2022-10-31 18:13 | 7:36 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total | 18:36 |  | Unserved Energy : |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 906:12 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-26
Page: 1/5 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: October2022
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Mymensingh | Mymensingh-Solar 132 kV Ckt | 2022-10-01 07:28 | 2022-10-01 07:28 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
| Mymensingh-Kishoreganj 132 kV Ckt-1 | 2022-10-03 09:30 | 2022-10-03 23:56 | 14:26 | S/O | Due to A/M work | 0 | 0 | No interruption
Kallyanpur | Kallyanpur-Lalbagh 132 kV Ckt-2 | 2022-10-04 07:07 | 2022-10-04 07:07 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
| Kallyanpur-Lalbagh 132 kV Ckt-2 | 2022-10-06 07:40 | 2022-10-06 07:40 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Meghnaghat 230 kV Ckt-2 | 2022-10-08 10:47 | 2022-10-08 18:15 | 7:28 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | Tongi-Ghorashal 230 kV Ckt-1 | 2022-10-09 06:19 | 2022-10-09 06:19 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
| Tongi-Ghorashal 230 kV Ckt-1 | 2022-10-09 14:59 | 2022-10-09 14:59 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Keraniganj 230 kV Ckt-2 | 2022-10-10 09:36 | 2022-10-10 16:56 | 7:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Netrakona 132 kV Ckt-1 | 2022-10-10 16:30 | 2022-10-10 17:58 | 1:28 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Keraniganj 230 kV Ckt-2 | 2022-10-11 09:44 | 2022-10-11 17:27 | 7:43 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | Tongi-Uttara 132 kV Ckt | 2022-10-11 09:06 | 2022-10-11 16:25 | 7:19 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Netrakona 132 kV Ckt-2 | 2022-10-11 09:31 | 2022-10-11 13:04 | 3:33 | S/O | Due to A/M work | 0 | 0 | No interruption
Mirpur | Mirpur-Uttara 3rd 132 kV Ckt | 2022-10-11 09:35 | 2022-10-11 17:33 | 7:58 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Mymensingh RPCL 132 kV Ckt-1 | 2022-10-12 10:22 | 2022-10-12 12:18 | 1:56 | S/O | Due to A/M work | 0 | 0 | No interruption
| Mymensingh-Mymensingh RPCL 132 kV Ckt-2 | 2022-10-12 12:20 | 2022-10-12 12:41 | 0:21 | S/O | Due to A/M work | 0 | 0 | No interruption
| Mymensingh-Mymensingh RPCL 132 kV Ckt-2 | 2022-10-12 15:15 | 2022-10-12 16:14 | 0:59 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Bhaluka 132 kV Ckt-1 | 2022-10-13 12:10 | 2022-10-13 13:10 | 1:00 | S/O | Due to A/M work | 0 | 0 | No interruption
| Mymensingh-Bhaluka 132 kV Ckt-2 | 2022-10-13 13:24 | 2022-10-13 14:41 | 1:17 | S/O | Due to A/M work | 0 | 0 | No interruption
| Mymensingh-Netrakona 132 kV Ckt-1 | 2022-10-15 08:29 | 2022-10-15 15:26 | 6:57 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Bashundhara 132 kV Ckt-1 | 2022-10-15 09:37 | 2022-10-15 16:37 | 7:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Netrakona 132 kV Ckt-1 | 2022-10-16 08:35 | 2022-10-16 15:32 | 6:57 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | Tongi-Bashundhara 132 kV Ckt-1 | 2022-10-16 09:13 | 2022-10-16 16:59 | 7:46 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Kishoreganj 132 kV Ckt-2 | 2022-10-16 11:27 | 2022-10-16 12:19 | 0:52 | S/O | Due to C/M work | 0 | 0 | No interruption
| Mymensingh-Netrakona 132 kV Ckt-1 | 2022-10-17 08:39 | 2022-10-17 16:05 | 7:26 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | Tongi-Bashundhara 132 kV Ckt-1 | 2022-10-17 11:10 | 2022-10-17 16:48 | 5:38 | S/O | Due to D/W work | 0 | 0 | No interruption
Netrakona | Netrakona-Mymensingh 132 kV Ckt-1 | 2022-10-18 08:48 | 2022-10-18 16:30 | 7:42 | S/O | Due to A/M work | 0 | 0 | No interruption
Kodda | Kodda-Joydevpur 132 kV Ckt-1 | 2022-10-18 09:03 | 2022-10-18 16:42 | 7:39 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | Tongi-Bashundhara 132 kV Ckt-1 | 2022-10-18 09:40 | 2022-10-18 18:19 | 8:39 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Netrakona 132 kV Ckt-1 | 2022-10-19 08:23 | 2022-10-19 16:25 | 8:02 | S/O | Due to A/M work | 0 | 0 | No interruption
Joydevpur | Joydevpur-Kodda 132 kV Ckt-2 | 2022-10-19 08:42 | 2022-10-19 17:28 | 8:46 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Netrakona 132 kV Ckt-1 | 2022-10-20 08:26 | 2022-10-20 16:55 | 8:29 | S/O | Due to A/M work | 0 | 0 | No interruption
Mirpur | Mirpur-Uttara 3rd 132 kV Ckt | 2022-10-20 08:44 | 2022-10-20 21:03 | 12:19 | S/O | Due to A/M work | 0 | 0 | No interruption
Joydevpur | Joydevpur-Kodda 132 kV Ckt-2 | 2022-10-20 09:07 | 2022-10-20 16:01 | 6:54 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | Tongi-Bashundhara 132 kV Ckt-2 | 2022-10-20 09:20 | 2022-10-20 13:43 | 4:23 | S/O | Due to C/M work | 0 | 0 | No interruption | No interruption
Mymensingh | Mymensingh-Netrakona 132 kV Ckt-2 | 2022-10-22 09:12 | 2022-10-22 17:36 | 8:24 | S/O | Due to A/M work | 0 | 0 | No interruption
| Mymensingh-Netrakona 132 kV Ckt-2 | 2022-10-23 08:44 | 2022-10-23 15:37 | 6:53 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | Tongi-Bashundhara 132 kV Ckt-2 | 2022-10-23 08:47 | 2022-10-23 16:44 | 7:57 | S/O | Due to A/M work | 0 | 0 | No interruption
Joydevpur | Joydevpur-Ghorashal 132 kV Ckt-1 | 2022-10-23 09:08 | 2022-10-23 17:21 | 8:13 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | Tongi-Bashundhara 132 kV Ckt |  | 2022-10-25 16:14 |  | S/O | Due to A/M work | 0 | 0 | No interruption
Ghorashal | Ghorashal-Joydevpur 132 kV Ckt-2 | 2022-10-26 07:35 | 2022-10-26 07:35 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Netrakona 132 kV Ckt-2 | 2022-10-26 08:39 | 2022-10-26 16:05 | 7:26 | S/O | Due to A/M work | 0 | 0 | No interruption
| Mymensingh-Netrakona 132 kV Ckt-2 | 2022-10-27 08:53 | 2022-10-27 14:55 | 6:02 | S/O | Due to A/M work | 0 | 0 | No interruption
| Mymensingh-Kishoreganj 132 kV Ckt-1 | 2022-10-29 08:55 | 2022-10-29 16:35 | 7:40 | S/O | Due to A/M work | 0 | 0 | No interruption
| Mymensingh-Kishoreganj 132 kV Ckt-1 | 2022-10-30 08:38 | 2022-10-30 17:22 | 8:44 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | Tongi-Tongi(N) 132 kV Ckt-1 | 2022-10-30 09:07 | 2022-10-30 13:12 | 4:05 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Kabirpur 132 kV Ckt-2 | 2022-10-30 09:21 | 2022-10-30 13:57 | 4:36 | S/O | Due to A/M work | 0 | 0 | No interruption
Keraniganj | Keraniganj-Nawabganj 132 kV Ckt-2 | 2022-10-30 09:06 | 2022-10-30 17:08 | 8:02 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Agargaon 230 kV Ckt-2 | 2022-10-30 09:50 | 2022-10-30 16:36 | 6:46 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Kishoreganj 132 kV Ckt-2 | 2022-10-31 08:46 | 2022-10-31 16:56 | 8:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | Tongi-Tongi(N) 132 kV Ckt-1 | 2022-10-31 13:10 | 2022-10-31 15:13 | 2:03 | S/O | Due to A/M work | 0 | 0 | No interruption
| Tongi-Tongi(N) 132 kV Ckt-2 | 2022-10-31 15:15 | 2022-10-31 16:37 | 1:22 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 274:40 |  | Unserved Energy: |  | 0 |  | 0:00
Dhaka (South) Grid Circle : | [9 empty] | 0:00
Bhulta | Bhulta-Haripur 230 kV Ckt-2 | 2022-10-02 10:38 | 2022-10-02 12:06 | 1:28 | S/O | Due to C/M work | 0 | 0 | No interruption
Ghorashal AIS | Ghorashal AIS-Ghorashal GIS 230 kV Ckt-1 | 2022-10-09 06:41 | 2022-10-09 06:41 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption |  | 21
Maniknagar | Maniknagar-Siddhirganj 230 kV Ckt-1 |  | 2022-10-09 13:55 |  |  | After maint.work | 0 | 0 | No interruption
Ghorashal AIS | Ghorashal AIS-Ghorashal GIS 230 kV Ckt-2 | 2022-10-14 07:10 | 2022-10-14 07:10 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
| Ghorashal AIS-Tongi 230 kV Ckt-2 | 2022-10-14 06:17 | 2022-10-14 06:17 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
| Ghorashal AIS-Ghorashal GIS 230 kV Ckt-1 | 2022-10-14 12:15 | 2022-10-14 17:57 | 5:42 | S/O | Due to C/M work | 0 | 0 | No interruption
| Ghorashal AIS-Ghorashal GIS 230 kV Ckt-1 | 2022-10-14 06:03 | 2022-10-14 06:03 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Cumilla(N) 230 kV Ckt-2 | 2022-10-15 08:41 | 2022-10-15 15:59 | 7:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Rampura | Rampura-Gulshan 132 kV cable Ckt-1 | 2022-10-16 05:46 | 2022-10-16 08:41 | 2:55 | S/O | Due to C/M work | 0 | 0 | No interruption
Haripur | Haripur-Rahim steel 132 kV cable Ckt | 2022-10-16 06:45 | 2022-10-16 06:45 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
| Haripur-Rahim steel 132 kV cable Ckt | 2022-10-17 07:00 | 2022-10-17 11:57 | 4:57 | S/O | Due to D/W work | 0 | 0 | No interruption
Ullon | Ullon-Haripur 132 kV Ckt | 2022-10-19 10:54 | 2022-10-19 10:54 |  |  | Due to Ct Change | 0 | 0 | No interruption
Shyampur | Shyampur-Fatullah 132 kV Ckt-2 | 2022-10-20 10:08 | 2022-10-20 20:24 | 10:16 | S/O | Due to A/M work | 0 | 0 | No interruption
| Shyampur-Fatullah 132 kV Ckt-1 | 2022-10-21 08:22 | 2022-10-21 16:05 | 7:43 | S/O | Due to C/M work | 0 | 0 | No interruption
Ullon | Ullon-Haripur 132 kV Ckt |  | 2022-10-21 13:22 |  | S/O | After maint.work | 0 | 0 | No interruption
Siddhirganj | Siddhirganj -Dutch Bangla P/S 132 kV Ckt | 2022-10-22 06:20 |  |  | S/O | Due to D/W work | 0 | 0 | No interruption
Sonargaon | Sonargaon-Daudkandi 132 kV Ckt-1 | 2022-10-23 09:18 | 2022-10-23 14:14 | 4:56 | S/O | Due to C/M work | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Haripur 132 kV Ckt-2 | 2022-10-23 09:33 | 2022-10-23 17:59 | 8:26 | S/O | Due to C/M work | 0 | 0 | No interruption
Ghorashal | Ghorashal -Bhulta 230 kV Ckt-2 |  | 2022-10-25 09:58 |  |  | After maint.work | 0 | 0 | No interruption
| Ghorashal -Joydevpur 132 kV Ckt-1 |  | 2022-10-25 11:02 |  |  |  | 0 | 0 | No interruption
| Ghorashal -Joydevpur 132 kV Ckt-1 | 2022-10-25 14:27 | 2022-10-25 15:15 | 0:48 | S/O | Due to relay testing | 0 | 0 | No interruption
| Ghorashal -Joydevpur 132 kV Ckt-2 | 2022-10-25 15:20 | 2022-10-25 15:20 | 0:00 | S/O |  | 0 | 0 | No interruption
Keraniganj | Keraniganj-Nawabganj 132 kV Ckt-1 | 2022-10-26 09:41 | 2022-10-26 16:53 | 7:12 | S/O | Due to A/M work | 0 | 0 | No interruption
Rampura | Rampura-Bashundhara 132 kV Ckt-2 | 2022-10-26 11:32 | 2022-10-26 14:24 | 2:52 | S/O | Due to C/M work | 0 | 0 | No interruption
Keraniganj | Keraniganj-Nawabganj 132 kV Ckt-1 | 2022-10-27 08:19 | 2022-10-27 17:08 | 8:49 | S/O | Due to A/M work | 0 | 0 | No interruption
Ghorashal | Ghorashal -Bhulta 230 kV Ckt-1 | 2022-10-27 11:37 | 2022-10-27 16:45 | 5:08 | S/O | Due to C/M work | 0 | 0 | No interruption
Sonargaon S/S | Sonargaon S/S-Orion P.P 132 kV Ckt | 2022-10-29 07:12 | 2022-10-29 07:12 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Keraniganj | Keraniganj-Nawabganj 132 kV Ckt-2 | 2022-10-31 08:37 | 2022-10-31 16:54 | 8:17 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 86:47 |  | Unserved Energy: |  | 0
Chattogram Grid Circle :
Khagrachari | Khagrachari-Rangamati 132 kV Ckt-1 | 2022-10-01 08:29 | 2022-10-01 17:02 | 8:33 | S/O | Due to A/M work | 0 | 0 | No interruption
| Khagrachari-Rangamati 132 kV Ckt-1 | 2022-10-02 08:17 | 2022-10-02 17:14 | 8:57 | S/O | Due to A/M work | 0 | 0 | No interruption
Juldah | Juldah-Sikalbaha 132 kV Ckt | 2022-10-02 08:51 | 2022-10-02 18:10 | 9:19 | S/O | Due to A/M work | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'sbazar 132 kV Ckt-2 | 2022-10-02 09:53 | 2022-10-02 12:11 | 2:18 | S/O | Due to C/M work | 0 | 0 | No interruption
Rampur | Rampur-Hathazari 132 kV Ckt-1 | 2022-10-02 12:10 | 2022-10-02 13:04 | 0:54 | S/O | Due to C/M work | 0 | 0 | No interruption
Khagrachari | Khagrachari-Rangamati 132 kV Ckt-2 | 2022-10-03 08:43 | 2022-10-03 17:10 | 8:27 | S/O | Due to C/M work | 0 | 0 | No interruption
| Khagrachari-Rangamati 132 kV Ckt-1 | 2022-10-07 08:45 | 2022-10-07 17:19 | 8:34 | S/O | Due to A/M work | 0 | 0 | No interruption
| Khagrachari-Rangamati 132 kV Ckt-2 | 2022-10-08 08:20 | 2022-10-08 17:15 | 8:55 | S/O | Due to A/M work | 0 | 0 | No interruption
Sikalbaha(N) | Sikalbaha(N)-Shahmirpur 132 kV Ckt-1 | 2022-10-08 10:40 | 2022-10-08 15:32 | 4:52 | S/O | Due to maint.work | 0 | 0 | No interruption
Khagrachari | Khagrachari-Rangamati 132 kV Ckt-2 | 2022-10-09 08:29 | 2022-10-09 17:01 | 8:32 | S/O | Due to A/M work | 0 | 0 | No interruption
| Khagrachari-Rangamati 132 kV Ckt-1 | 2022-10-10 09:20 | 2022-10-10 16:38 | 7:18 | S/O | Due to C/M work | 0 | 0 | No interruption
| Khagrachari-Rangamati 132 kV Ckt-2 | 2022-10-11 08:48 | 2022-10-11 16:38 | 7:50 | S/O | Due to C/M work | 0 | 0 | No interruption
Kaptai | Kaptai-Chandraghona 132 kV Ckt-1 | 2022-10-12 08:20 | 2022-10-12 08:20 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Khagrachari | Khagrachari-Rangamati 132 kV Ckt-2 | 2022-10-12 08:50 | 2022-10-12 19:00 | 10:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaptai | Kaptai-Chandraghona 132 kV Ckt-1 | 2022-10-13 08:17 | 2022-10-13 16:48 | 8:31 | S/O | Due to A/M work | 0 | 0 | No interruption
Rangamati | Rangamati -Khagrachari 132 kV Ckt-2 | 2022-10-13 09:00 | 2022-10-13 16:51 | 7:51 | S/O | Due to A/M work | 0 | 0 | No interruption
Rampur | Rampur-Agrabad 132 kV Ckt-1 | 2022-10-13 12:29 | 2022-10-13 13:14 | 0:45 | S/O | Due to protection test | 0 | 0 | No interruption
| Rampur-Agrabad 132 kV Ckt-2 | 2022-10-13 13:17 | 2022-10-13 13:50 | 0:33 | S/O
Hathazari | Hathazari-Baroierhat 132 kV Ckt-1 | 2022-10-15 08:10 | 2022-10-15 16:20 | 8:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaptai | Kaptai-Chandraghona 132 kV Ckt-1 | 2022-10-15 08:46 | 2022-10-15 16:08 | 7:22 | S/O | Due to A/M work | 0 | 0 | No interruption
Sikalbaha(O) | Sikalbaha(O)-Sikalbaha (N) 132 kV Ckt-1 |  | 2022-10-15 11:23 |  | S/O | After maint.work | 0 | 0 | No interruption
Hathazari | Hathazari-Baroierhat 132 kV Ckt-1 | 2022-10-16 08:10 | 2022-10-16 17:06 | 8:56 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaptai | Kaptai-Chandraghona 132 kV Ckt-2 | 2022-10-16 08:35 | 2022-10-16 16:38 | 8:03 | S/O | Due to A/M work | 0 | 0 | No interruption
Chandraghona | Chandraghona-Kaptai 132 kV Ckt-2 | 2022-10-18 08:45 | 2022-10-18 17:39 | 8:54 | S/O | Due to A/M work | 0 | 0 | No interruption
Madunaghat | Madunaghat-Chandraghona 132 kV Ckt-1 | 2022-10-19 08:17 | 2022-10-19 16:22 | 8:05 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Raozan 230 kV Ckt-2 | 2022-10-19 09:33 | 2022-10-19 16:05 | 6:32 | S/O | Due to A/M work | 0 | 0 | No interruption
Madunaghat | Madunaghat-Chandraghona 132 kV Ckt-1 | 2022-10-20 07:28 | 2022-10-20 07:28 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Raozan 230 kV Ckt-2 | 2022-10-20 09:13 | 2022-10-20 16:59 | 7:46 | S/O | Due to A/M work | 0 | 0 | No interruption
| Hathazari-Baroierhat 132 kV Ckt-1 | 2022-10-21 09:17 | 2022-10-21 16:02 | 6:45 | S/O | Due to C/M work | 0 | 0 | No interruption
Khulshi | Khulshi-Baraulia 132 kV Ckt-2 | 2022-10-22 07:39 | 2022-10-22 07:39 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Chandraghona | Chandraghona-Madunaghat 132 kV Ckt-1 | 2022-10-22 07:45 | 2022-10-22 15:59 | 8:14 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Raozan 230 kV Ckt-1 | 2022-10-22 09:20 | 2022-10-22 16:45 | 7:25 | S/O | Due to A/M work | 0 | 0 | No interruption
Chandraghona | Chandraghona-Madunaghat 132 kV Ckt-1 | 2022-10-23 07:37 | 2022-10-23 07:37 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Raozan 230 kV Ckt-2 | 2022-10-23 09:28 | 2022-10-23 16:13 | 6:45 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulshi | Khulshi-Halishahar 132 kV Ckt | 2022-10-23 20:25 | 2022-10-23 21:33 | 1:08 | S/O | Due to A/M work | 0 | 0 | No interruption
Madunaghat | Madunaghat-Chandraghona 132 kV Ckt-1 & 2 | 2022-10-24 09:30 | 2022-10-24 11:41 | 2:11 | S/O | Due to project work | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'sbazar 132 kV Ckt-2 | 2022-10-25 14:20 | 2022-10-25 15:14 | 0:54 | S/O | Due to tree trimming | 0 | 0 | No interruption
Madunaghat | Madunaghat-Chandraghona 132 kV Ckt-2 | 2022-10-26 07:26 | 2022-10-26 07:26 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Raozan 230 kV Ckt-2 | 2022-10-26 08:22 | 2022-10-26 11:43 | 3:21 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Baroierhat 132 kV Ckt | 2022-10-26 09:03 | 2022-10-26 15:22 | 6:19 | S/O | Due to A/M work | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-Intermediate 230 kV Ckt-1 | 2022-10-26 10:08 | 2022-10-26 10:10 | 0:02 | S/O | Due to SAS work | 0 | 0 | No interruption
| Sikalbaha-Intermediate 230 kV Ckt-2 | 2022-10-26 11:12 | 2022-10-26 12:19 | 1:07 | S/O | Due to SAS work | 0 | 0 | No interruption
Madunaghat | Madunaghat-Chandraghona 132 kV Ckt-2 | 2022-10-27 07:09 | 2022-10-27 07:09 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Baroierhat 132 kV Ckt-2 | 2022-10-27 09:08 | 2022-10-27 16:27 | 7:19 | S/O | Due to A/M work | 0 | 0 | No interruption
Madunaghat | Madunaghat-Chandraghona 132 kV Ckt-2 | 2022-10-29 07:42 | 2022-10-29 07:42 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Baroierhat 132 kV Ckt-2 | 2022-10-29 08:47 | 2022-10-29 16:06 | 7:19 | S/O | Due to A/M work | 0 | 0 | No interruption
Madunaghat | Madunaghat-Chandraghona 132 kV Ckt-2 | 2022-10-30 07:33 | 2022-10-30 07:33 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Baroierhat 132 kV Ckt-2 | 2022-10-30 08:55 | 2022-10-30 16:10 | 7:15 | S/O | Due to C/M work | 0 | 0 | No interruption
Madunaghat | Madunaghat-Sikalbaha 132 kV Ckt | 2022-10-31 07:33 | 2022-10-31 07:33 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Baroierhat 132 kV Ckt-2 | 2022-10-31 09:16 | 2022-10-31 16:04 | 6:48 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 248:59 |  | Unserved Energy: |  | 0
Cumilla Grid Circle : | [9 empty] | 0:00
Ashuganj | Ashuganj-Shahjibazar 132 kV Ckt | 2022-10-02 10:29 | 2022-10-02 17:47 | 7:18 | S/O | Due to C/M work | 0 | 0 | No interruption | 0:00
Cumilla(N) | Cumilla(N)-Daudkandi 132 kV Ckt-1 | 2022-10-10 08:49 | 2022-10-10 13:31 | 4:42 | S/O | Due to C/M work | 0 | 0 | No interruption
| Cumilla(N)-Meghnaghat 230 kV Ckt-1 | 2022-10-11 08:34 | 2022-10-11 16:06 | 7:32 | S/O | Due to A/M work | 0 | 0 | No interruption
| Cumilla(N)-kachua kV Ckt | 2022-10-11 09:10 | 2022-10-11 16:55 | 7:45 | S/O | Due to C/M work | 0 | 0 | No interruption
| Cumilla(N)-Meghnaghat 230 kV Ckt-1 | 2022-10-12 08:10 | 2022-10-12 16:10 | 8:00 | S/O | Due to A/M work | 0 | 0 | No interruption
| Cumilla(N)-Cumilla(S) 132 kV Ckt-2 | 2022-10-12 08:24 | 2022-10-12 13:14 | 4:50 | S/O | Due to C/M work | 0 | 0 | No interruption
| Cumilla(N)-Meghnaghat 230 kV Ckt-1 | 2022-10-13 08:34 | 2022-10-13 16:31 | 7:57 | S/O | Due to A/M work | 0 | 0 | No interruption
Sylhet | Sylhet-Fenchuganj 132 kV Ckt | 2022-10-14 06:13 |  |  | S/O | Due to A/M work | 0 | 0 | No interruption
| Cumilla(N)-Meghnaghat 230 kV Ckt-2 | 2022-10-16 08:31 | 2022-10-16 17:00 | 8:29 | S/O | Due to A/M work | 0 | 0 | No interruption
| Cumilla(N)-Meghnaghat 230 kV Ckt-2 | 2022-10-17 08:13 | 2022-10-17 16:37 | 8:24 | S/O | Due to A/M work | 0 | 0 | No interruption
Daudkandi | Daudkandi-Cumilla(N) 132 kV Ckt-1 | 2022-10-18 08:36 | 2022-10-18 16:24 | 7:48 | S/O | Due to A/M work | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Daudkandi 132 kV Ckt-1 | 2022-10-19 08:58 | 2022-10-19 16:10 | 7:12 | S/O | Due to A/M work | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Bibiyana 132 kV Ckt | 2022-10-20 06:04 | 2022-10-20 08:36 | 2:32 | S/O | Due to D/W work | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Daudkandi 132 kV Ckt-1 | 2022-10-20 08:50 | 2022-10-20 16:24 | 7:34 | S/O | Due to A/M work | 0 | 0 | No interruption
Sylhet | Sylhet-Fenchuganj P/S132 kV Ckt-1 | 2022-10-21 06:17 |  |  | S/O | Due to D/W work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishireganj 132 kV Ckt-2 | 2022-10-22 08:39 | 2022-10-22 16:40 | 8:01 | S/O | Due to A/M work | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Daudkandi 132 kV Ckt-2 | 2022-10-22 08:28 | 2022-10-22 17:06 | 8:38 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishireganj 132 kV Ckt-2 | 2022-10-23 08:39 | 2022-10-23 16:40 | 8:01 | S/O | Due to A/M work | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Daudkandi 132 kV Ckt-2 | 2022-10-23 08:34 | 2022-10-23 17:05 | 8:31 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Comilla(N) 230 kV Ckt-2 | 2022-10-23 17:00 | 2022-10-23 17:54 | 0:54 | S/O | for trimming bamboo | 0 | 0 | No interruption
| Ashuganj-Kishoreganj 132 kV Ckt-1 | 2022-10-25 12:30 | 2022-10-25 13:01 | 0:31 | S/O | Due to tree trimming | 0 | 0 | No interruption
Sylhet | Sylhet-Fenchuganj P/S 132 kV Ckt | 2022-10-26 06:36 |  |  | S/O | Due to D/W work | 0 | 0 | No interruption
Chaddagram | Chaddagram-Feni 132 kV Ckt-1 | 2022-10-26 08:26 | 2022-10-26 16:49 | 8:23 | S/O | Due to A/M work | 0 | 0 | No interruption
Feni | Feni-Chaddagram 132 kV Ckt-2 | 2022-10-29 09:26 | 2022-10-29 13:08 | 3:42 | S/O | Due to C/M work | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Bibiyana 230 kV Ckt-1 | 2022-10-30 10:23 | 2022-10-30 18:42 | 8:19 | S/O | Due to A/M work | 0 | 0 | No interruption
| Cumilla(N)-Daudkandi 132 kV Ckt-2 | 2022-10-31 08:49 | 2022-10-31 15:52 | 7:03 | S/O | Due to A/M work | 0 | 0 | No interruption
| Cumilla(N)-Bibiyana 230 kV Ckt-2 | 2022-10-31 09:37 |  |  | S/O | Due to A/M work | 0 | 0 | No interruption
Ramganj | Ramganj-Chandpur Desh 132 kV Ckt-1 | 2022-10-31 08:28 | 2022-10-31 11:31 | 3:03 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 155:09 |  | Unserved Energy: |  | 0
Khulna Grid Circle :
Madaripur | Madaripur-Gopalganj 132 kV Ckt-1 & 2 | 2022-10-08 08:17 | 2022-10-08 17:12 | 8:55 | S/O | Due to A/M work | 0 | 0 | No interruption
Gopalganj | Gopalganj-Madaripur 132 kV Ckt-1 & 2 | 2022-10-10 07:19 | 2022-10-10 07:19 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulna (S) | Khulna (S)-Noapara 132 kV Ckt-1 | 2022-10-12 07:28 | 2022-10-12 11:06 | 3:38 | S/O | Due to C/M work | 0 | 0 | No interruption
Madaripur | Madaripur-Gopalganj 132 kV Ckt-1 & 2 | 2022-10-12 08:14 | 2022-10-12 17:00 | 8:46 | S/O | Due to A/M work | 0 | 0 | No interruption
| Madaripur-Gopalganj 132 kV Ckt-1 & 2 | 2022-10-13 08:10 | 2022-10-13 16:46 | 8:36 | S/O | Due to A/M work | 0 | 0 | No interruption
Gopalganj | Gopalganj-Payra 400 kV Ckt-2 | 2022-10-14 07:05 |  |  | S/O | Due to D/W work | 0 | 0 | No interruption
Madaripur | Madaripur-Shariatpur 132 kV Ckt-2 | 2022-10-16 15:28 | 2022-10-16 17:35 |  | S/O | Due to DC fault | 0 | 0 | No interruption
Noapara | Noapara-Jashore 132 kV Ckt-1 | 2022-10-17 10:59 | 2022-10-17 17:45 | 6:46 | S/O | Due to C/M work | 0 | 0 | No interruption
Barisal(N) | Barisal(N)-Bhola 230 kV Ckt-2 |  | 2022-10-25 19:23 |  | S/O | After maint.work | 0 | 0 | No interruption
Madaripur | Madaripur-Shariatpur 132 kV Ckt-1 |  | 2022-10-25 19:28 |  | S/O |  | 0 | 0 | No interruption
| Madaripur-Barisal(N) 132 kV Ckt-1 |  | 2022-10-25 17:14 |  | S/O |  | 0 | 0 | No interruption
Patuakhali | Patuakhali-Payra 132 kV Ckt-1 | 2022-10-26 09:42 | 2022-10-26 20:59 | 11:17 | S/O | Due to C/M work | 0 | 0 | No interruption
Khulna (S) | Khulna (S)-Satkhira 132 kV Ckt-1 | 2022-10-27 11:06 | 2022-10-27 12:49 | 1:43 | S/O | Due to C/M work | 0 | 0 | No interruption
| Khulna (S)-Satkhira 132 kV Ckt-2 | 2022-10-27 12:50 | 2022-10-27 15:40 | 2:50 | S/O | Due to C/M work | 0 | 0 | No interruption
Payra | Payra-Patuakhali 132 kV Ckt-1 | 2022-10-28 09:26 | 2022-10-28 15:48 | 6:22 | S/O | Due to C/M work | 0 | 0 | No interruption
Patuakhali | Patuakhali-Payra 132 kV Ckt-2 | 2022-10-29 10:21 | 2022-10-29 16:54 | 6:33 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 65:26 |  | Unserved Energy: |  | 0
HVDC Grid Circle :
Ishurdi | Ishurdi-Bheramara 230 kV both Ckts | 2022-10-21 08:52 | 2022-10-21 17:54 | 9:02 | S/O | Due to C/M work | 0 | 0 | No interruption
| Ishurdi-Ruppur 132 kV Ckt-1 | 2022-10-23 08:19 | 2022-10-23 16:15 | 7:56 | S/O | Due to A/M work | 0 | 0 | No interruption
Ruppur | Ruppur-Ishurdi 132 kV Ckt-2 | 2022-10-26 08:15 | 2022-10-26 17:40 | 9:25 | S/O | Due to A/M work | 0 | 0 | No interruption
Ishurdi | Ishurdi-Pabna 132 kV Ckt | 2022-10-30 08:44 | 2022-10-30 16:54 | 8:10 | S/O | Due to A/M work | 0 | 0 | No interruption
| Ishurdi-Pabna 132 kV Ckt | 2022-10-31 08:23 | 2022-10-31 15:45 | 7:22 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 41:55 |  | Unserved Energy: |  | 0
Bogura Grid Circle :
Bogura | Bogura-Naogaon 132 kV Ckt-2 | 2022-10-01 07:45 | 2022-10-01 07:45 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Rohanpur | Rohanpur-Godda 400 kV Ckt-1 |  | 2022-10-07 11:15 |  |  | new connection | 0 | 0 | No interruption
Bogura(N) | Bogura(N)-Naogaon 132 kV Ckt-2 | 2022-10-07 07:48 | 2022-10-07 18:12 | 10:24 | S/O | Due to C/M work | 0 | 0 | No interruption
Naogaon | Naogaon-Santahar 132 kV Ckt | 2022-10-07 07:40 | 2022-10-07 18:17 | 10:37 | S/O | Due to C/M work | 0 | 0 | No interruption
Bogura | Bogura-Naogaon 132 kV Ckt-2 | 2022-10-08 07:12 | 2022-10-08 07:12 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
| Bogura-Naogaon 132 kV Ckt-1 | 2022-10-12 08:01 | 2022-10-12 17:13 | 9:12 | S/O | Due to C/M work | 0 | 0 | No interruption
| Bogura-Naogaon 132 kV Ckt-1 | 2022-10-14 07:21 | 2022-10-14 07:21 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Naogaon | Naogaon-Santahar 132 kV Ckt | 2022-10-14 14:48 | 2022-10-14 15:30 | 0:42 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 30:55 |  | Unserved Energy: |  | 0
Others :
Matuail | Matuail-Maniknagar 132 kV Ckt | 2022-10-05 13:05 | 2022-10-05 13:22 | 0:17 | S/O | Due to C/M work | 0 | 0 | No interruption
Ullon | Ullon-Dhanmondi 132 kV Ckt-2 | 2022-10-19 10:50 | 2022-10-21 13:22 | 50:32 | S/O | Due to CT change | 0 | 0 | No interruption
Matuail | Matuail-Siddhirganj 132 kV Ckt | 2022-10-20 09:39 | 2022-10-20 19:03 | 9:24 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 60:13 |  | Unserved Energy: |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 964:04 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month:October 2022
| Area | Previous Month (September' 2022) |  |  |  | Current Month (October '2022)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 15 | 6 | 37 | 58 | 29 | 6 | 95 | 130
2 | Dhaka (South) Grid Circle. | 9 | 7 | 34 | 50 | 27 |  | 42 | 69
3 | Chattogram Grid Circle. | 30 | 4 | 38 | 72 | 14 | 2 | 77 | 93
4 | Cumilla Grid Circle. | 23 | 8 | 33 | 64 | 43 | 5 | 47 | 95
5 | Khulna Grid Circle. | 22 | 10 | 47 | 79 | 7 | 7 | 78 | 92
6 | HVDC Grid Circle | 10 | 6 | 16 | 32 | 1 | 4 | 15 | 20
7 | Bogura Grid Circle. | 24 | 10 | 57 | 91 | 14 | 9 | 52 | 75
8 | Others | 8 |  | 2 | 10 | 10 |  | 7 | 17
9 | Total | 141 | 51 | 264 | 456 | 145 | 33 | 413 | 591
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month:October 2022
| Area | Previous Month (September' 2022) |  |  |  | Current Month (October '2022)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 620.73 | 248 | 345.73 | 1214.46 | 240.2 | 462.36 | 513.25 | 1215.81
2 | Dhaka (South) Grid Circle. | 588.37 | 382.08 | 138.3 | 1108.75 | 77.45 | 0 | 0 | 77.45
3 | Chattogram Grid Circle. | 609.76 | 9.75 | 231.7 | 851.21 | 18.37 | 18 | 255.73 | 292.1
4 | Cumilla Grid Circle. | 118.67 | 374.42 | 352.9 | 845.99 | 264.46 | 37.67 | 82.67 | 384.8
5 | Khulna Grid Circle. | 254.52 | 247.28 | 146 | 647.8 | 70.53 | 101.23 | 156.46 | 328.22
6 | HVDC Grid Circle |  | 182.75 | 342.82 | 525.57 |  | 25 | 106.33 | 131.33
7 | Bogura Grid Circle. | 537.53 | 258.8 | 1707.42 | 2503.75 | 63.9 | 153.87 | 391.94 | 609.71
8 | Others | Energy unserved ( MWH ) due to Total: 0; Energy unserved ( MWH ) due to Total: 0
9 | Total | 2729.58 | 1703.08 | 3264.87 | 7697.53 | 734.91 | 798.13 | 1506.38 | 3039.42
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-29
Page: 1/1 | [9 empty] | QF-LDC-29
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month:August 2022
A) Power Interruption
SL. | Name of | Total Capacity | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of the Sub-Station |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Dhaka (North) | 8801.6 | 10 | 1 | 11 | 7 | 1 | 3 | 343.37
2 | Dhaka (South) | 5031.6 | 4 |  | 4 | 2 | 1 | 1 | 186.0333
3 | Chattogram | 2042 | 6 | 2 | 8 | 2 | 1 | 5 | 429.72
4 | Khulna | 2434 | 8 | 9 | 17 | 3 | 5 | 9 | 869.11
5 | HVDC | 5954.3 | 3 | 1 | 4 | 1 | 2 | 1 | 110.4
6 | Bogura | 3145.6 | 12 | 11 | 23 | 4 | 2 | 17 | 844.1
7 | Cumilla | 2981 | 7 | 9 | 16 | 4 | 3 | 9 | 517.45
8 | Others | - | - | - | - | - | - | - | 0
| Total | 30390.1 | [6 empty] | 3300.1833
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 99.99%
2 | Dhaka (South) | 99.95%
3 | Chattogram | 99.9%
4 | Khulna | 99.87%
5 | HVDC | 99.98% | [6 empty] | Executive Engineer
6 | Bogura | 99.89% | [6 empty] | Information Management Division
7 | Cumilla | 99.94% | [6 empty] | LDC, PGCB, Dhaka.

## QF-LDC-30
Page: 1/1 | [10 empty] | QF-LDC-30
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month:October 2022
A) Power Interruption
SL. | Name of | Total length | No. of Section in | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of Transmission line | the Transmission |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | (Ckt-KM) | Line | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 2254.4715 | - | 2 |  | 2 | 2 | - | - | - | 190.92
2 | Dhaka (South) | 990.29 |  | 2 |  | 2 | 2 | - | - | - | 33.37
3 | Chattogram | 917 | - | - | - | - | - | - | - | - | -
4 | Khulna | 1238.4 | - | - | - | - | - | - | - | - | -
5 | HVDC | 1325 | - | - | - | - | - | - | - | - | -
6 | Bogura | 1803.3 | - | 1 |  | 1 | - | - | - | - | 19.5
7 | Cumilla | 1648.16 | - | 2 |  | 2 |  | 2 | - | - | 142.78
8 | Others | - |  |  | - | - | - | - | - | - | -
| Total | 10176.6215 | [8 empty] | 386.57
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 99.99%
2 | Dhaka (South) | 99.93%
3 | Chattogram | 99.95%
4 | Khulna | 99.98%
5 | Bheramara (HVDC) | 99.98% | [7 empty] | Executive Engineer
6 | Bogura | 98.77% | [7 empty] | Information Management Division
7 | Cumilla | 99.9% | [7 empty] | LDC, PGCB, Dhaka.

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month:October 2022
Type of | Power failure due to | [7 empty] | Partial |  | Total Grid failure
fault | Trouble In |  | Trouble In Grid S/S |  | Trouble In |  | Lightning in |  | Grid failure |  |  |  | Remarks
| Generation |  | Equipment |  | Transmission Line |  | Transmission Line/Thunder Storm
Period | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration
| No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min.
2022-10-01 | 19 | - | 3 | 02hr54 min | 1 | 10 min | - | - | 1 | 07Hr | - | - | Eastern Region Blackout on 04.10.2022
* Tripping of a generator is accounted in the category "Trouble in Generation ". Not all tripping cause power interruption.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-32
Page: 1/2 |  |  |  |  | QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the Systems
Month:October 2022
| Total Nos.of | Total | Unserved | Total | Remarks
Sub-station | Interruption | Duration of | Load | Unserved
|  | Interruption | (MW) | Energy
|  | Hrs./Mins. |  | (MWH)
Mymensingh | 1 | 0:24 | 140 | 56 | Due to 33 kV feeder fault
Mirpur | 1 | 1:13 | 15 | 18.25 | Due to red-hot maint 132/33 kV Transformer T2
Joydevpur | 1 | 0:24 | 35 | 14 | Due to 33 kV feeder fault
Savar | 1 | 0:47 | 103 | 80.6833 | Due to man injured
Sonargaon | 1 | 6:46 | 25 | 169.1667 | Due to red-hot maint.at 33 kV side
Kabirpur | 1 | 1:20 | 95 | 126.6667
Joydevpur | 1 | 1:12 | 21 | 25.2 | Due to 33 kV feeder fault
Mymensingh | 2 | 1:05 | 20 | 21.6667 | Due to red-hot maint.at 33 kV side
Kaliakoir |  | 0:15 | 507 | 126.75 | Due to tripping Kaliakoir-Tangail 132 kV Ckt-1 & 2
Mymensingh | 1 | 0:10 | 385 | 64.1667 | Due to tripping of Mymensingh RPCL bus coupler got tripped
| 1 | 3:01 | 20 | 60.3333 | Due to S/D of 132/33 kV transformer T1
Tangail | 1 | 1:31 | 25 | 37.9167 | Due to S/D of 132/33 kV transformer T3
Jamalpur | 1 | 0:55 | 20 | 18.3333 | Due to S/D of 132/33 kV transformer T2
| 1 | 2:31 | 40 | 100.6667 | Due to S/D of 132/33 kV transformers T1 & T2
Mymensingh | 1 | 2:48 | 20 | 56 | Due to S/D of 132/33 kV transformer T3
Kishoreganj | 1 | 1:24 | 20 | 28 | Due to S/D of 132/33 kV transformer T3
Dhamrai | 1 | 2:10 | 20 | 43.3333 | Due to S/D of 132/33 kV transformer T1
Joydevpur | 1 | 1:43 | 90 | 154.5 | Due to S/D of 132/33 kV transformer T3
Mymensingh | 1 | 1:25 | 10 | 14.1667
Hasnabad |  | 0:07 | 14 | 1.6333 | Due to 33 kV feeder fault
Sreenagar | 1 | 0:33 | 25 | 13.75
Narsinghdi | 1 | 0:51 | 17 | 14.45 | Due to tripping of 132/33 kV transformers T1 & T3
| 1 | 0:07 | 25 | 2.9167
Hasnabad | 1 | 0:17 | 40 | 11.3333 | Due to tripping of 132/33 kV transformers T-1 & T5
Rampura | 1 | 0:14 | 35 | 8.1667 | Due to trippng of Rampura-Bashundhara 132 kV Ckt-1 & 2
Hasnabad | 1 | 0:21 | 72 | 25.2 | Due to tripping of Hasnabad-Shitalakyha 132 kV Ckt
Ramganj | 1 | 0:54 | 20 | 18 | Due to red-hot maint.of 132/33 kV Transformer T2
Dohazari | 1 | 0:19 | 58 | 18.3667 | Due to tripping of 132/33 kV transformers T-1 & T2
Baroierhat | 1 | 1:43 | 16 | 27.4667 | Due to S/D of 132/33 kV transformer T2
Cox'sbazar |  | 0:28 | 12 | 5.6 | Due to S/D of 132/33 kV transformer T1
Madunaghat | 2 | 3:18 | 30 | 99 | Due to S/D of 132/33 kV transformer T2
|  | 1:02 | 30 | 31
Dohazari |  | 1:56 | 25 | 48.3333 | Due to S/D of 33 kV Bus
Cox'sbazar |  | 1:16 | 35 | 44.3333 | Due to S/D of 132/33 kV transformer T3
Cumilla(S) | 1 | 0:33 | 74 | 40.7 | Due to S/d of 132/33 kV transformer T3
Sylhet | 1 | 1:00 | 10 | 10 | Due to red-hot maint. Of 132/32 kV Transformer T2 with 33 kV Bus
Shahjibazar | 1 | 0:12 | 25 | 5 | Due to 33 kV feeder fault
Sreemongal | 1 | 1:23 | 20 | 27.6667 | Due to red-hot maint.of 132/33 kV trasnformerT2 & 33 kV Bus
B.Baria | 2 | 0:25 | 125 | 52.0833 | Due to 33 kV feeder fault
Shahjibazar |  | 0:10 | 9 | 1.5 | Due to 33 kV feeder fault
Daudkandi | 1 | 0:12 | 72 | 14.4
Sylhet | 1 | 0:48 | 10 | 8 | Due to tripping of 132/33 kV transformer T4
Cumilla(S) | 2 | 0:47 | 76 | 59.5333 | Due to tripping of Cumilla(S)-Tripur 132 kV both Ckts
Fenchuganj |  | 0:37 | 135 | 83.25 | Due to tripping of Fenchuganj-Sylhet 132 kV Ckt
Chattak | 1 | 4:08 | 20 | 82.6667 | Due to S/D of 132/33 kV transformer T1
Faridpur | 1 | 0:30 | 20 | 10 | Due to 33 kV feeder fault
Barisal(S) | 1 | 1:03 | 20 | 21 | Due to red-hot maint of132/33 kV Transformer T1
Narail | 1 | 1:37 | 26 | 42.0333 | Due to red-hot maint 132/33 kV Transformer T1 with 33 kV Bus
Patuakhali | 1 | 0:32 | 60 | 32 | Due to tripping of 132/33 kV Transformer T1 & T2
Madaripur | 1 | 0:19 | 48 | 15.2 | Due to 33 kV feeder fault
Bhandaria | 1 | 1:02 | 6 | 6.2 | Due to red-hot maint.of 132/33 kV Transformer T1
Faridpur | 2 | 0:16 | 50 | 13.3333 | Due to 33 kV feeder fault
|  | 1:36 | 20 | 32 | Due to red-hot manit.of 132/33 kV transformer T-1
Shariatpur | 1 | 1:10 | 10 | 57.3333 | Due to S/D of 132/33 kV transformer T2
Rajbari | 1 | 1:17 | 14 | 17.9667 | Due to S/D of 132/33 kV transformer T1
Madaripur | 1 | 0:07 | 10 | 1.1667 | Due to S/D 132/33 kV transformer T3
Narail |  | 1:58 | 20 | 39.3333 | Due to S/D of 132/33 kV transformer T2
Satkhira | 1 | 1:01 | 40 | 40.6667 | Due to S/D of 132/33 kV transformer T-1
Bottail | 1 | 1:15 | 20 | 25 | Due to red-hot maint.of 132/33 kV Transformer T2 | 4068.5833
Benapole | 1 | 0:47 | 20 | 15.6667 | Due to S/D of 132/33 kV transformer T1
Pabna | 1 | 1:10 | 25 | 29.1667 | Due to S/D of132/33 kV transformer T2 with 33 kV Bus
Jhenaidah | 1 | 4:06 | 15 | 61.5 | Due to S/D of132/33 kV transformer T1 By PBS
Mohasthangar | 1 | 2:04 | 25 | 51.6667 | Due to red-hot maint.of 132/33 kV Transformer T2
Page: 2/2 |  |  |  |  | QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the Systems
Month:October 2022
| Total Nos.of | Total | Unserved | Total | Remarks
Sub-station | Interruption | Duration of | Load | Unserved
|  | Interruption | (MW) | Energy
|  | Hrs./Mins. |  | (MWH)
Barapukuria | 1 | 1:52 | 12 | 22.4 | Due to red-hot maint.of 132/33 kV Transformer T3
Purbasadipur | 1 | 0:36 | 74 | 44.4 | Due to 33 kV feeder fault
Saidpur | 1 | 0:47 | 20 | 15.6667 | Due to red-hot maint at 33 kV side
Naogaon | 1 | 0:37 | 104 | 64.1333 | Due to 33 kV breaker burst
Amnura | 1 | 0:30 | 12 | 6 | Due to tripping of Amnura-Rajshahi 132 kV Ckt
Naogaon | 1 | 0:27 | 30 | 13.5 | Due to tripping of Naogaon-Joypurhat 132 kV Ckt
Palashbari | 1 | 1:24 | 40 | 56 | Due to S/D of 132/33 kV transformersT3 & T4
Natore | 1 | 4:48 | 7 | 33.6 | Due to S/D of 132/33 kV transformer T3
Niamatpur |  | 1:09 | 20 | 23 | Due to S/D of 132/33 kV transformerT1
Rangpur |  | 7:30 | 10 | 75
Rangpur | 1 | 5:46 | 10 | 57.6667 | Due to S/D of 132/33 kV transformer T2
Saidpur |  | 7:20 | 20 | 146.6667
| Total Unserved energy : |  |  | 3039.4167 | MWH
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-33
Page: 1/3 |  |  | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month: October '2022
Sl. No | Sub-station | Load (MW) | Time
1 | AKS | 25 | 2022-10-20 15:00
2 | AKSML | 178 | 2022-10-09 06:00
3 | Aftabnagar | 34.98 | 2022-10-18 18:00
4 | Agargaon | 89 | 2022-10-13 13:00
5 | Agrabad | 80 | 2022-10-16 15:00
6 | Amnura | 64 | 2022-10-01 19:00
7 | Ashuganj | 84.5 | 2022-10-18 01:00
8 | BSRM | 166 | 2022-10-03 18:30
9 | Bagerhat | 103 | 2022-10-10 18:30
10 | Bakulia | 138 | 2022-10-22 19:30
11 | Banani | 44 | 2022-10-11 14:00
12 | Bangabhaban | 22 | 2022-10-10 10:00
13 | Barapukuria | 55 | 2022-10-19 18:00
14 | Barguna | 20 | 2022-10-01 00:00
15 | Barishal | 106 | 2022-10-04 18:00
16 | Barishal-230 | 86 | 2022-10-07 20:00
17 | Baroaulia | 82 | 2022-10-14 14:00
18 | Baroirhat | 58 | 2022-10-01 20:00
19 | Bashundhara | 170 | 2022-10-01 18:00
20 | BashundharaCement | 14 | 2022-10-18 08:00
21 | Beanibazar | 65 | 2022-10-05 01:00
22 | Benapole | 56 | 2022-10-08 20:00
23 | Bhaluka | 154 | 2022-10-15 16:00
24 | Bhandaria | 50 | 2022-10-01 22:00
25 | Bhangura | 34 | 2022-10-08 19:30
26 | Bheramara(GK) | 63 | 2022-10-09 20:00
27 | Bhulta | 243 | 2022-10-22 21:00
28 | Bog-Sherpur | 62 | 2022-10-08 19:30
29 | Bogura | 170 | 2022-10-17 18:00
30 | Borhanuddin | 45 | 2022-10-13 21:00
31 | Brahmanbaria | 170 | 2022-10-08 20:00
32 | Cantonment | 160 | 2022-10-15 18:30
33 | Chandpur | 75 | 2022-10-08 20:00
34 | Chandraghona | 36 | 2022-10-22 18:30
35 | Chapai | 67 | 2022-10-26 20:00
36 | Charsaidpur | 52.5 | 2022-10-31 17:00
37 | Chauddagram | 63 | 2022-10-08 20:00
38 | Chhatak | 33 | 2022-10-07 19:30
39 | Chowmuhani | 225 | 2022-10-08 21:00
40 | Chuadanga | 104 | 2022-10-09 20:00
41 | Coxsbazar | 124 | 2022-10-11 18:00
42 | Cumilla(N) | 180 | 2022-10-04 18:30
43 | Cumilla(S) | 172 | 2022-10-07 22:00
44 | Daudkandi | 151 | 2022-10-08 20:00
45 | Dhaka | 44 | 2022-10-02 12:00
46 | Dhamrai | 118 | 2022-10-26 18:00
47 | Dhanmondi | 160 | 2022-10-13 13:00
48 | Dohazari | 102 | 2022-10-15 19:30
49 | Faridpur | 151 | 2022-10-09 21:00
50 | Fatullah | 76 | 2022-10-13 11:00
51 | Fenchuganj | 46 | 2022-10-01 03:00
52 | Feni | 112 | 2022-10-08 20:00
53 | GPH | 97 | 2022-10-04 10:00
Page: 2/3 |  |  | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month: October '2022
Sl. No | Sub-station | Load (MW) | Time
54 | Ghorashal | 152 | 2022-10-11 00:00
56 | Goalpara | 35 | 2022-10-12 13:00
57 | Gollamari | 57 | 2022-10-30 18:00
58 | Gopalganj | 105.6 | 2022-10-01 22:00
59 | Gulshan | 118 | 2022-10-13 15:00
60 | Halishahar | 104 | 2022-10-11 14:00
61 | HaripurSBU | 164 | 2022-10-10 10:00
62 | Hasnabad | 107 | 2022-10-04 19:30
63 | Hathazari | 77 | 2022-10-01 18:30
64 | Ishurdi | 78 | 2022-10-08 18:00
65 | Jaldhaka | 55 | 2022-10-07 20:00
66 | Jamalpur | 139 | 2022-10-02 05:00
67 | Jashore | 144 | 2022-10-09 18:30
68 | Jhenaidah | 128 | 2022-10-09 18:30
69 | Joydebpur | 186 | 2022-10-09 20:00
70 | Joypurhat | 64 | 2022-10-08 21:00
71 | Juldah | 32 | 2022-10-30 12:00
72 | KSRM | 44.5 | 2022-10-24 22:00
73 | Kabirpur | 369 | 2022-10-20 05:00
74 | Kachua | 78 | 2022-10-14 20:00
75 | Kallyanpur | 114 | 2022-10-04 20:00
76 | Kalurghat | 22 | 2022-10-25 09:00
77 | Kamrangirchar | 82 | 2022-10-19 13:00
78 | Kaptai | 5 | 2022-10-01 18:00
79 | Kazla | 96 | 2022-10-20 20:00
80 | Keranigonj | 72 | 2022-10-26 18:30
81 | Khagrachori | 32 | 2022-10-01 18:30
82 | Khulna | 95 | 2022-10-10 18:30
83 | Khulshi | 193 | 2022-10-11 09:00
84 | Kishoreganj | 144 | 2022-10-11 20:00
85 | Kodda | 301 | 2022-10-13 19:30
86 | Kulaura | 50 | 2022-10-07 20:00
87 | Kurigram | 59 | 2022-10-02 07:00
88 | Kushtia | 146 | 2022-10-01 19:00
89 | Lalbag | 102 | 2022-10-19 13:00
90 | Lalmonirhat | 44 | 2022-10-07 20:00
91 | Madanganj | 98 | 2022-10-17 20:00
92 | Madaripur | 106 | 2022-10-01 21:00
93 | Madartek | 101 | 2022-10-04 22:00
94 | Madunaghat | 65 | 2022-10-22 21:00
95 | Magura | 64 | 2022-10-08 18:30
96 | Mahasthangarh | 70 | 2022-10-08 20:00
97 | Manikganj | 92 | 2022-10-14 20:00
98 | Maniknagar | 80 | 2022-10-18 13:00
99 | Matarbari | 43 | 2022-10-05 20:00
100 | Matuail | 68 | 2022-10-02 12:00
101 | Millgate | 72 | 2022-10-01 11:00
101 | Mirpur | 144 | 2022-10-04 19:00
102 | Mirsorai | 5 | 2022-10-05 18:30
Page: 3/3 |  |  | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month: October '2022
Sl. No | Sub-station | Load (MW) | Time
103 | Mithapukur | 46 | 2022-10-09 23:00
104 | Modern | 0 | 2022-10-01 00:00
105 | Mogbazar | 134 | 2022-10-18 12:00
106 | Mongla | 38 | 2022-10-13 12:00
107 | Motijheel | 40 | 2022-10-19 13:00
108 | Munshiganj | 108 | 2022-10-17 19:30
109 | Mymensingh | 232 | 2022-10-01 20:00
110 | Naogaon | 120 | 2022-10-10 21:00
111 | Narail | 54 | 2022-10-18 19:00
112 | Narinda | 70 | 2022-10-02 13:00
113 | Narshingdi | 179 | 2022-10-23 21:00
114 | Natore | 139 | 2022-10-10 18:30
115 | Nawabganj | 52.6 | 2022-10-10 19:00
116 | Netrakona | 130 | 2022-10-17 19:30
117 | New | 80 | 2022-10-10 16:00
118 | Niamatpur | 73 | 2022-10-29 13:00
119 | Noapara | 46 | 2022-10-15 18:30
120 | PHP | 11 | 2022-10-12 19:30
121 | Pabna | 114 | 2022-10-08 20:00
122 | Palashbari | 128 | 2022-10-10 21:00
123 | Panchagarh | 61 | 2022-10-08 19:30
124 | Patuakhali | 124 | 2022-10-01 00:00
125 | Payra | 1.13 | 2022-10-02 20:00
126 | Postogola | 47 | 2022-10-01 00:00
127 | Purbachal | 20 | 2022-10-04 22:00
128 | Purbasadipur | 107 | 2022-10-10 20:00
129 | Rahanpur_I | 18.4 | 2022-10-29 20:00
130 | Rahim | 38 | 2022-10-22 16:00
131 | Rajbari | 70 | 2022-10-08 19:00
132 | Rajendrapur | 122 | 2022-10-22 21:00
133 | Rajshahi | 151 | 2022-10-01 18:30
134 | Rajshahi-230 | 82.5 | 2022-10-24 09:00
135 | Ramganj | 120 | 2022-10-05 00:00
136 | Rampur | 40 | 2022-10-22 21:00
137 | Rangamati | 16 | 2022-10-16 18:00
138 | Rangpur | 139 | 2022-10-17 18:00
139 | Ruppur | 5.2 | 2022-10-04 11:00
140 | SSM | 23 | 2022-10-11 00:00
141 | Saidpur | 97 | 2022-10-02 08:00
142 | Satkhira | 122 | 2022-10-01 20:00
143 | Satmasjid | 99 | 2022-10-04 22:00
144 | Savar | 175 | 2022-10-03 21:00
145 | Shahjadpur | 112 | 2022-10-01 19:30
146 | Shahjibazar | 128 | 2022-10-23 19:00
147 | Shahmirpur | 59.4 | 2022-10-16 19:00
148 | Shariatpur | 78 | 2022-10-01 21:00
149 | Sherpur | 118 | 2022-10-01 23:00
150 | Shikalbaha | 39 | 2022-10-11 05:00
151 | Shikalbaha-230 | N/A | N/A
152 | Shitalakhya | 129 | 2022-10-31 15:00
153 | Sholosohor | 37 | 2022-10-01 20:00
154 | Shyampur | 188 | 2022-10-13 13:00
155 | Siddhirganj | 118 | 2022-10-01 16:00
156 | Sirajganj | 114 | 2022-10-08 21:00
157 | Sonargaon | 112 | 2022-10-23 20:00
158 | Sreemongol | 57 | 2022-10-05 22:00
159 | Srinagar | 49.1 | 2022-10-04 20:00
160 | Sunamganj | 50 | 2022-10-13 20:00
161 | Sylhet | 166 | 2022-10-01 19:30
162 | TK | 32.5 | 2022-10-16 18:00
163 | Tangail | 229 | 2022-10-01 21:00
164 | Thakurgaon | 80 | 2022-10-02 20:00
165 | Tongi | 120 | 2022-10-18 19:30
166 | Ullon | 51 | 2022-10-04 23:00
167 | Uttara | 95 | 2022-10-10 18:30
168 | UttaraNew | 34 | 2022-10-04 21:00
169 | Zigatola | 68 | 2022-10-04 23:00
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID COMPANY OF BANGLADESH LTD. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month:October 2022
Area | MW | Date | Hour | Remarks
Dhaka | 4769.52 | 18/10/2022 | 19:00
Chattogram | 1421.5 | 2022-12-10 | 18:00
Cumilla | 1360.5 | 2022-08-10 | 20:00
Mymensingh | 1042 | 2022-01-10 | 21:00
Sylhet | 528 | 2022-01-10 | 18:00
Khulna | 1640 | 2022-10-10 | 18:30
Barishal | 408.71 | 2022-01-10 | 0:00
Rajshahi | 1379 | 2022-08-10 | 20:00
Rangpur | 793 | 2022-10-10 | 19:30
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-35
| Page: 1/3 | [5 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: October '2022
SL. | 400 KV Substation | Rated | Maxm |  | Minm | Date and Time
No. |  | Voltage | Voltage | Date and Time | Voltage |  | Remarks
|  | kV | kV |  | kV
1 | Bhulta | 400 | 407 | 2022-10-24 22:00 | 373 | 2022-10-04 14:00
2 | Bibiana | 400 | 414 | 2022-10-04 20:00 | 385 | 2022-10-05 04:00
3 | BIPTC | 400 | 412 | 2022-10-25 02:00 | 393 | 2022-10-27 18:00
4 | Gopalganj_I | 400 | 435 | 2022-10-25 04:00 | 395 | 2022-10-09 03:00
5 | Kaliakoir | 400 | 406 | 2022-10-25 07:00 | 275 | 2022-10-04 09:00
6 | Payra | 400 | 428 | 2022-10-25 02:00 | 401 | 2022-10-10 21:00
7 | Rahanpur_I | 400 | 424 | 2022-10-31 17:00 | 364 | 2022-10-05 11:00
|  | Rated | Maxm |  | Minm | Date and Time
SL. | Substation | Voltage | Voltage | Date and Time | Voltage |  | Remarks
No. | 230 KV Substation | kV | kV |  | kV
1 | Agargaon | 230 | 242 | 2022-10-24 22:00 | 209 | 2022-10-04 12:00
2 | AKSML | 230 | 257 | 2022-10-04 17:00 | 211 | 2022-10-04 16:00
3 | Aminbazar | 230 | 243 | 2022-10-24 22:00 | 208 | 2022-10-30 19:00
4 | Ashuganj | 230 | 252 | 2022-10-04 18:30 | 238 | 2022-10-30 09:00
5 | Baghabari | 230 | 240 | 2022-10-25 02:00 | 218 | 2022-10-04 14:00
6 | Barapukuria | 230 | 227 | 2022-10-22 04:00 | 201 | 2022-10-05 23:00
7 | Barishal | 230 | 258 | 2022-10-25 04:00 | 230 | 2022-10-04 16:00
8 | Bheramara | 230 | 255 | 2022-10-27 06:00 | 223 | 2022-10-20 20:00
9 | Bhulta | 230 | 241 | 2022-10-24 22:00 | 234 | 2022-10-04 14:00
10 | Bibiana | 230 | 243 | 2022-10-25 02:00 | 219 | 2022-10-04 03:00
11 | BIPTC | 230 | 246 | 2022-10-25 02:00 | 222 | 2022-10-05 14:00
12 | Bogura | 230 | 233 | 2022-10-25 04:00 | 222 | 2022-10-01 11:00
13 | Borhanuddin | 230 | 264 | 2022-10-25 04:00 | 230 | 2022-10-04 15:00
14 | BSRM | 230 | 254 | 2022-10-04 17:00 | 222 | 2022-10-02 12:00
15 | Cumilla(N) | 230 | 245 | 2022-10-04 16:00 | 219 | 2022-10-02 14:00
16 | Fenchuganj | 230 | 246 | 2022-10-04 19:30 | 227 | 2022-10-10 19:30
17 | Ghorashal | 230 | N/A | N/A | N/A | N/A
18 | GPH | 230 | 239 | 2022-10-26 20:00 | 220 | 2022-10-30 03:00
19 | Haripur | 230 | 239 | 2022-10-24 22:00 | 212 | 2022-10-04 12:00
20 | Hasnabad | 230 | 245 | 2022-10-04 18:00 | 211 | 2022-10-02 23:00
21 | Hathazari | 230 | 240 | 2022-10-14 17:00 | 235 | 2022-10-06 07:00
22 | Ishurdi | 230 | 246 | 2022-10-25 02:00 | 224 | 2022-10-02 01:00
23 | Jhenaidah | 230 | 247 | 2022-10-25 04:00 | 216 | 2022-10-09 03:00
24 | Kaliakoir | 230 | 231 | 2022-10-25 09:00 | 222 | 2022-10-21 03:00
25 | Keranigonj | 230 | 245 | 2022-10-04 18:30 | 222 | 2022-10-02 02:00
26 | Khulna(S) | 230 | 250 | 2022-10-25 04:00 | 222 | 2022-10-16 19:00
27 | Maniknagar | 230 | 242 | 2022-10-24 22:00 | 225 | 2022-10-07 17:00
28 | Meghnaghat | 230 | 250 | 2022-10-04 17:00 | 223 | 2022-10-27 02:00
29 | Mirsorai | 230 | 238 | 2022-10-14 01:00 | 223 | 2022-10-09 17:00
30 | Rajshahi | 230 | 251 | 2022-10-25 01:00 | 223 | 2022-10-18 04:00
31 | Rampur | 230 | N/A | N/A | N/A | N/A
32 | Rampura | 230 | 240 | 2022-10-24 22:00 | 214 | 2022-10-04 12:00
33 | Shahmirpur | 230 | 140 | 2022-10-23 18:00 | 213 | 2022-10-22 18:30
34 | Shikalbaha | 230 | 241 | 2022-10-31 18:00 | 235 | 2022-10-14 02:00
35 | Shyampur | 230 | 245 | 2022-10-04 18:30 | 222 | 2022-10-05 04:00
36 | Siddhirganj | 230 | 242 | 2022-10-04 18:00 | 222 | 2022-10-10 20:00
37 | Sirajgonj | 230 | 259 | 2022-10-12 06:00 | 229 | 2022-10-04 12:00
38 | Tongi | 230 | 243 | 2022-10-24 22:00 | 238 | 2022-10-15 04:00
QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: October '2022
|  | Rated | Maxm |  | Minm | Date and Time
SL. | Substation | Voltage | Voltage | Date and Time | Voltage |  | Remarks
No. | 132 KV Substation | kV | kV |  | kV
1 | Aftabnagar | 132 | 146 | 2022-10-04 20:00 | 124 | 2022-10-27 10:00
2 | Agargaon | 132 | 140 | 2022-10-02 06:00 | 119 | 2022-10-27 00:00
3 | Agrabad | 132 | 140 | 2022-10-23 18:00 | 134 | 2022-10-12 04:00
4 | AKS | 132 | 138 | 2022-10-06 00:00 | 126 | 2022-10-23 05:00
5 | Aminbazar | 132 | 142 | 2022-10-06 18:00 | 107 | 2022-10-17 07:00
6 | Amnura | 132 | 157 | 2022-10-14 12:00 | 112 | 2022-10-26 01:00
7 | Ashuganj | 132 | 145 | 2022-10-04 17:00 | 133 | 2022-10-02 01:00
8 | Bagerhat | 132 | 145 | 2022-10-25 04:00 | 121 | 2022-10-16 19:00
9 | Bakulia | 132 | 140 | 2022-10-04 18:30 | 129 | 2022-10-20 18:00
10 | Banani | 132 | 145 | 2022-10-24 22:00 | 124 | 2022-10-27 10:00
11 | Bangabhaban | 132 | 147 | 2022-10-04 18:00 | 122 | 2022-10-27 10:00
12 | Barapukuria | 132 | 139 | 2022-10-27 23:00 | 120 | 2022-10-05 23:00
13 | Barguna | 132 | 140 | 2022-10-24 17:00 | 126 | 2022-10-01 23:00
14 | Barishal | 132 | 148 | 2022-10-25 04:00 | 123 | 2022-10-02 11:00
15 | Barishal-230 | 132 | 147 | 2022-10-25 04:00 | 130 | 2022-10-01 00:00
16 | Baroaulia | 132 | 141 | 2022-10-06 00:00 | 114 | 2022-10-04 18:00
17 | Baroirhat | 132 | 142 | 2022-10-24 23:00 | 122 | 2022-10-11 14:00
18 | Bashundhara | 132 | 146 | 2022-10-04 19:00 | 120 | 2022-10-04 19:30
19 | BashundharaCement | 132 | 142 | 2022-10-24 22:00 | 121 | 2022-10-04 10:00
20 | Beanibazar | 132 | 141 | 2022-10-04 18:30 | 118 | 2022-10-05 01:00
21 | Benapole | 132 | 141 | 2022-10-24 19:30 | 123 | 2022-10-16 18:30
22 | Bhaluka | 132 | 139 | 2022-10-04 17:00 | 112 | 2022-10-12 21:00
23 | Bhandaria | 132 | 147 | 2022-10-24 17:00 | 108 | 2022-10-16 02:00
24 | Bhangura | 132 | 146 | 2022-10-25 02:00 | 126 | 2022-10-14 06:00
25 | Bheramara | 132 | 141 | 2022-10-25 02:00 | 130 | 2022-10-08 19:30
26 | Bheramara(GK) | 132 | 140 | 2022-10-24 22:00 | 135 | 2022-10-29 19:00
27 | Bhulta | 132 | 141 | 2022-10-24 22:00 | 118 | 2022-10-12 07:00
28 | Bog-Sherpur | 132 | 144 | 2022-10-25 02:00 | 127 | 2022-10-07 20:00
29 | Bogura | 132 | 143 | 2022-10-25 04:00 | 126 | 2022-10-24 07:00
30 | Bogura-230 | 132 | 143 | 2022-10-25 04:00 | 116 | 2022-10-24 14:00
31 | Brahmanbaria | 132 | 140 | 2022-10-04 16:00 | 113 | 2022-10-03 12:00
32 | Cantonment | 132 | 140 | 2022-10-24 21:00 | 121 | 2022-10-17 10:00
33 | Chandpur | 132 | 144 | 2022-10-24 23:00 | 123 | 2022-10-11 15:00
34 | Chandraghona | 132 | 140 | 2022-10-18 18:30 | 117 | 2022-10-22 20:00
35 | Chapai | 132 | 138 | 2022-10-04 17:00 | 122 | 2022-10-13 04:00
36 | Charsaidpur | 132 | 143 | 2022-10-24 22:00 | 119 | 2022-10-04 14:00
37 | Chauddagram | 132 | 141 | 2022-10-25 05:00 | 130 | 2022-10-15 13:00
38 | Chhatak | 132 | 139 | 2022-10-04 19:30 | 118 | 2022-10-05 01:00
39 | Chowmuhani | 132 | 141 | 2022-10-01 06:00 | 112 | 2022-10-22 00:00
40 | Chuadanga | 132 | 141 | 2022-10-25 04:00 | 119 | 2022-10-10 22:00
41 | Coxsbazar | 132 | 139 | 2022-10-24 18:00 | 108 | 2022-10-02 11:00
42 | Cumilla(N) | 132 | 143 | 2022-10-04 16:00 | 128 | 2022-10-12 01:00
43 | Cumilla(S) | 132 | 143 | 2022-10-24 22:00 | 120 | 2022-10-26 04:00
44 | Daudkandi | 132 | 145 | 2022-10-04 19:00 | 122 | 2022-10-12 05:00
45 | Dhaka | 132 | 140 | 2022-10-02 05:00 | 125 | 2022-10-27 10:00
46 | Dhamrai | 132 | 147 | 2022-10-04 20:00 | 120 | 2022-10-27 10:00
47 | Dhanmondi | 132 | 143 | 2022-10-24 22:00 | 122 | 2022-10-04 12:00
48 | Dohazari | 132 | 141 | 2022-10-04 19:30 | 122 | 2022-10-25 13:00
49 | Faridpur | 132 | 142 | 2022-10-25 04:00 | 113 | 2022-10-04 04:00
50 | Fatullah | 132 | 143 | 2022-10-24 21:00 | 124 | 2022-10-27 10:00
51 | Fenchuganj | 132 | 141 | 2022-10-04 19:30 | 128 | 2022-10-13 20:00
52 | Feni | 132 | 142 | 2022-10-24 22:00 | 126 | 2022-10-20 18:00
53 | Ghorashal | 132 | 148 | 2022-10-30 01:00 | 126 | 2022-10-20 03:00
54 | Goalpara | 132 | 143 | 2022-10-25 04:00 | 115 | 2022-10-05 08:00
55 | Gollamari | 132 | 144 | 2022-10-25 04:00 | 126 | 2022-10-16 18:00
56 | Gopalganj | 132 | 145 | 2022-10-25 04:00 | 127 | 2022-10-09 01:00
57 | Gopalganj_I | 132 | 144 | 2022-10-24 20:00 | 127 | 2022-10-09 01:00
58 | Gulshan | 132 | 146 | 2022-10-04 20:00 | 138 | 2022-10-16 15:00
59 | Halishahar | 132 | 140 | 2022-10-04 19:00 | 114 | 2022-10-19 01:00
60 | Haripur | 132 | 142 | 2022-10-24 22:00 | 123 | 2022-10-04 12:00
61 | HaripurSBU | 132 | 141 | 2022-10-25 00:00 | 120 | 2022-10-02 01:00
| Page: 3/3 | [5 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: October '2022
Rated
SL. | Substation | Rated | Maxm |  | Minm | Date and Time
No. | 132 KV Substation | Voltage | Voltage | Date and Time | Voltage |  | Remarks
|  | kV | kV |  | kV
62 | Hasnabad | 132 | 142 | 2022-10-02 06:00 | 125 | 2022-10-08 11:00
63 | Hathazari | 132 | 140 | 2022-10-04 18:30 | 131 | 2022-10-24 15:00
64 | Ishurdi | 132 | 142 | 2022-10-25 02:00 | 113 | 2022-10-05 01:00
65 | Jaldhaka | 132 | 136 | 2022-10-27 23:00 | 112 | 2022-10-05 23:00
66 | Jamalpur | 132 | 141 | 2022-10-04 16:00 | 117 | 2022-10-12 14:00
67 | Jashore | 132 | 140 | 2022-10-24 22:00 | 112 | 2022-10-16 19:00
68 | Jhenaidah | 132 | 142 | 2022-10-25 01:00 | 125 | 2022-10-13 15:00
69 | Jhenaidah-230 | 132 | 143 | 2022-10-25 04:00 | 128 | 2022-10-10 19:30
70 | Joydebpur | 132 | 146 | 2022-10-24 22:00 | 129 | 2022-10-29 10:00
71 | Joypurhat | 132 | 139 | 2022-10-24 22:00 | 112 | 2022-10-09 02:00
72 | Juldah | 132 | 139 | 2022-10-11 00:00 | 128 | 2022-10-30 10:00
73 | Kabirpur | 132 | 155 | 2022-10-22 14:00 | 114 | 2022-10-16 23:00
74 | Kachua | 132 | 141 | 2022-10-04 21:00 | 124 | 2022-10-11 15:00
75 | Kaliakoir | 132 | 142 | 2022-10-06 18:00 | 135 | 2022-10-17 19:30
76 | Kallyanpur | 132 | 142 | 2022-10-04 20:00 | 112 | 2022-10-26 11:00
77 | Kalurghat | 132 | 140 | 2022-10-15 18:30 | 130 | 2022-10-02 11:00
78 | Kamrangirchar | 132 | 147 | 2022-10-04 18:00 | 126 | 2022-10-27 10:00
79 | Kaptai | 132 | 140 | 2022-10-04 19:30 | 132 | 2022-10-02 07:00
80 | Kazla | 132 | 143 | 2022-10-04 20:00 | 122 | 2022-10-27 11:00
81 | Keranigonj | 132 | 145 | 2022-10-04 18:00 | 117 | 2022-10-14 09:00
82 | Khagrachori | 132 | 139 | 2022-10-26 21:00 | 130 | 2022-10-01 12:00
83 | Khulna | 132 | 143 | 2022-10-25 05:00 | 126 | 2022-10-16 18:30
84 | Khulna(S) | 132 | 145 | 2022-10-25 04:00 | 132 | 2022-10-12 04:00
85 | Khulshi | 132 | 140 | 2022-10-04 18:30 | 127 | 2022-10-24 15:00
86 | Kishoreganj | 132 | 140 | 2022-10-04 17:00 | 118 | 2022-10-01 21:00
87 | Kodda | 132 | 148 | 2022-10-24 22:00 | 120 | 2022-10-28 11:00
88 | KSRM | 132 | 140 | 2022-10-04 19:30 | 128 | 2022-10-23 06:00
89 | Kulaura | 132 | 141 | 2022-10-04 20:00 | 126 | 2022-10-05 01:00
90 | Kurigram | 132 | 137 | 2022-10-24 23:00 | 112 | 2022-10-05 23:00
91 | Kushtia | 132 | 140 | 2022-10-24 22:00 | 128 | 2022-10-13 04:00
92 | Lalbag | 132 | 148 | 2022-10-04 18:30 | 125 | 2022-10-27 10:00
93 | Lalmonirhat | 132 | 157 | 2022-10-28 16:00 | 118 | 2022-10-02 23:00
94 | Madanganj | 132 | 142 | 2022-10-24 22:00 | 121 | 2022-10-04 10:00
95 | Madaripur | 132 | 146 | 2022-10-25 02:00 | 108 | 2022-10-04 00:00
96 | Madartek | 132 | 147 | 2022-10-04 20:00 | 124 | 2022-10-27 10:00
97 | Madunaghat | 132 | 140 | 2022-10-06 00:00 | 130 | 2022-10-23 06:00
98 | Magura | 132 | 143 | 2022-10-25 02:00 | 126 | 2022-10-08 19:30
99 | Mahasthangarh | 132 | 141 | 2022-10-25 02:00 | 124 | 2022-10-07 20:00
100 | Manikganj | 132 | 140 | 2022-10-04 18:00 | 117 | 2022-10-30 07:00
101 | Maniknagar | 132 | 146 | 2022-10-04 18:00 | 117 | 2022-10-27 10:00
102 | Matarbari | 132 | 1254 | 2022-10-19 09:00 | 110 | 2022-10-15 19:30
103 | Matuail | 132 | 142.6 | 2022-10-24 22:00 | 122.5 | 2022-10-04 12:00
104 | Millgate | 132 | 142 | 2022-10-24 21:00 | 123 | 2022-10-27 10:00
105 | Mirpur | 132 | 141 | 2022-10-04 19:30 | 126 | 2022-10-26 16:00
106 | Mithapukur | 132 | 140 | 2022-10-24 22:00 | 122 | 2022-10-18 01:00
107 | Modern | 132 | 139 | 2022-10-06 00:00 | 129 | 2022-10-03 16:00
108 | Mogbazar | 132 | 148 | 2022-10-04 20:00 | 126 | 2022-10-18 19:00
109 | Mongla | 132 | 145 | 2022-10-25 04:00 | 122 | 2022-10-16 18:30
110 | Motijheel | 132 | 147 | 2022-10-04 18:00 | 122 | 2022-10-27 10:00
111 | Munshiganj | 132 | 142 | 2022-10-24 22:00 | 122 | 2022-10-04 12:00
112 | Mymensingh | 132 | 139 | 2022-10-04 16:00 | 110 | 2022-10-01 21:00
113 | Naogaon | 132 | 140 | 2022-10-25 02:00 | 113 | 2022-10-31 21:00
114 | Narail | 132 | 142 | 2022-10-25 02:00 | 124 | 2022-10-08 21:00
115 | Narinda | 132 | 0 | 2022-10-01 00:00 | N/A | N/A
116 | Narshingdi | 132 | 140 | 2022-10-24 21:00 | 117 | 2022-10-12 06:00
117 | Natore | 132 | 139 | 2022-10-25 02:00 | 132 | 2022-10-11 20:00
118 | Nawabganj | 132 | 142 | 2022-10-05 20:00 | 113 | 2022-10-04 05:00
119 | Netrakona | 132 | 139 | 2022-10-25 00:00 | 126 | 2022-10-22 08:00
120 | New | 132 | 144 | 2022-10-24 22:00 | 124 | 2022-10-27 10:00
121 | Niamatpur | 132 | 140 | 2022-10-25 02:00 | 117 | 2022-10-08 20:00
122 | Noapara | 132 | 143 | 2022-10-25 03:00 | 126 | 2022-10-16 18:00
123 | Pabna | 132 | 140 | 2022-10-24 22:00 | 127 | 2022-10-30 12:00
124 | Palashbari | 132 | 138 | 2022-10-24 22:00 | 119 | 2022-10-08 01:00
125 | Panchagarh | 132 | 138 | 2022-10-20 03:00 | 108 | 2022-10-05 23:00
126 | Patuakhali | 132 | 138 | 2022-10-24 17:00 | 118 | 2022-10-11 21:00
127 | Payra | 132 | 140 | 2022-10-24 20:00 | 113 | 2022-10-16 19:30
128 | PHP | 132 | 141 | 2022-10-24 22:00 | 120 | 2022-10-11 15:00
129 | Postogola | 132 | 145 | 2022-10-24 21:00 | 124 | 2022-10-08 11:00
130 | Purbachal | 132 | 149 | 2022-10-24 22:00 | 124 | 2022-10-27 10:00
131 | Purbasadipur | 132 | 137 | 2022-10-27 23:00 | 110 | 2022-10-05 23:00
132 | Rahim | 132 | 138 | 2022-10-24 20:00 | 123 | 2022-10-04 12:00
133 | Rajbari | 132 | 144 | 2022-10-25 04:00 | 123 | 2022-10-03 18:00
134 | Rajendrapur | 132 | 143 | 2022-10-04 18:30 | 120 | 2022-10-29 09:00
135 | Rajshahi | 132 | 136 | 2022-10-04 17:00 | 121 | 2022-10-10 19:30
136 | Rajshahi-230 | 132 | 136 | 2022-10-04 16:00 | 120 | 2022-10-18 09:00
137 | Ramganj | 132 | 142 | 2022-10-25 07:00 | 114 | 2022-10-13 03:00
138 | Rampur | 132 | 139 | 2022-10-24 19:00 | 131 | 2022-10-22 16:00
139 | Rampura | 132 | 145 | 2022-10-04 19:30 | 111 | 2022-10-30 21:00
140 | Rangamati | 132 | 139 | 2022-10-06 00:00 | 113 | 2022-10-23 06:00
141 | Rangpur | 132 | 138 | 2022-10-13 15:00 | 115 | 2022-10-05 23:00
142 | Ruppur | 132 | 140 | 2022-10-04 18:00 | 130 | 2022-10-15 18:30
143 | Saidpur | 132 | 137 | 2022-10-28 00:00 | 116 | 2022-10-07 20:00
144 | Satkhira | 132 | 142 | 2022-10-25 03:00 | 120 | 2022-10-16 18:30
145 | Satmasjid | 132 | 140 | 2022-10-24 21:00 | 112 | 2022-10-10 16:00
146 | Savar | 132 | 142 | 2022-10-06 18:00 | 126 | 2022-10-25 12:00
147 | Shahjadpur | 132 | 148 | 2022-10-25 01:00 | 134 | 2022-10-09 20:00
148 | Shahjibazar | 132 | 145 | 2022-10-04 17:00 | 132 | 2022-10-16 10:00
149 | Shariatpur | 132 | 145 | 2022-10-25 02:00 | 121 | 2022-10-13 18:00
150 | Sherpur | 132 | 155 | 2022-10-23 13:00 | 113 | 2022-10-23 18:00
151 | Shikalbaha | 132 | 141 | 2022-10-26 22:00 | 122 | 2022-10-30 00:00
152 | Shikalbaha-230 | 132 | 140 | 2022-10-18 18:30 | 113 | 2022-10-09 04:00
153 | Shitalakhya | 132 | 144 | 2022-10-24 21:00 | 112 | 2022-10-11 15:00
154 | Sholosohor | 132 | 139 | 2022-10-06 00:00 | 128 | 2022-10-24 15:00
155 | Shyampur | 132 | 141 | 2022-10-04 18:00 | 123 | 2022-10-27 10:00
156 | Shyampur-230 | 132 | 141 | 2022-10-24 21:00 | 113 | 2022-10-09 07:00
157 | Siddhirganj | 132 | 142 | 2022-10-24 22:00 | 123 | 2022-10-04 12:00
158 | Sirajganj | 132 | 142 | 2022-10-24 23:00 | 127 | 2022-10-08 20:00
159 | Sonargaon | 132 | 143 | 2022-10-24 22:00 | 112 | 2022-10-06 06:00
160 | Sreemongol | 132 | 144 | 2022-10-04 17:00 | 128 | 2022-10-05 01:00
161 | Srinagar | 132 | 165 | 2022-10-18 07:00 | 125 | 2022-10-27 10:00
162 | SSM | 132 | 1440 | 2022-10-10 21:00 | 129 | 2022-10-02 06:00
163 | Sunamganj | 132 | 139 | 2022-10-04 19:00 | 113 | 2022-10-07 22:00
164 | Sylhet | 132 | 142 | 2022-10-04 18:30 | 121 | 2022-10-07 21:00
165 | Tangail | 132 | 140 | 2022-10-24 22:00 | 121 | 2022-10-01 13:00
166 | Thakurgaon | 132 | 140 | 2022-10-20 04:00 | 118 | 2022-10-11 02:00
167 | TK | 132 | 140 | 2022-10-26 21:00 | 111 | 2022-10-25 18:00
168 | Tongi | 132 | 144 | 2022-10-04 18:30 | 127 | 2022-10-27 09:00
169 | Ullon | 132 | 145 | 2022-10-04 20:00 | 124 | 2022-10-27 10:00
170 | Uttara | 132 | 142 | 2022-10-04 20:00 | 125 | 2022-10-04 11:00
171 | UttaraNew | 132 | 140 | 2022-10-04 19:30 | 126 | 2022-10-26 11:00
172 | Zigatola | 132 | 149 | 2022-10-04 18:00 | 126 | 2022-10-27 10:00

## QF-LDC-36
Page: 1/2 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
Month: October 2022
Name of the | Auto transformer |  | Recorded maximum load
sub-station | Name | Capacity ( MVA ) | MW | Amps ( 230kV side ) | Date | Time | Remarks
| TR1 | 225 | 55 | 205
Hasnabad | TR2 | 225 | 55 | 205 | 08.10.2022 | 12:00
| TR3 | 225 | 55 | 205
| TR1 | 225 | 160 | 550
Tongi | TR2 | 225 | 160 | 550 | 08.10.2022 | 19:00
| TR3 | 225 | 160 | 550
Haripur | TR1 | 225 | 144 | 450
| TR2 | 225 | 144 | 450 | 01.10.2022 | 24:00
| TR3 | 225 | 144 | 450
| TR1 | 225 | 185 | 540
Rampura | TR2 | 225 | 185 | 504 | 18.10.2022 | 18:30
| TR3 | 225 | 185 | 540
Keraniganj | ATR1 | 300 | 104 | 298
| ATR2 | 300 | 104 | 298 | 10.10.22 | 20:00
| ATR3 | 300 | 104 | 298
| TR1 | 225 | 140 | 657
Aminbazar | TR2 | 225 | 140 | 657 | 01.10.2022 | 23:00
| TR3 | 225 | 164 | 682
Agargaon | TR1 | 300 | 165 | 473
| TR2 | 300 | 165 | 473 | 19.10.22 | 13:00
Maniknagar | TR1 | 300 | 160 | 480 | 20.10.2022 | 18:30
| TR2 | 300 | 160 | 480
Cumilla (N) | TR1 | 225 | 156 | 422 | 02.10.22 | 6:00
| TR2 | 225 | 154 | 410
Fenchuganj | AT2 | 300 | 257 | 727 | 07.10.22 | 22:00
| MT1 | 150 | 97 | 265
Hathazari | MT2 | 150 | 97 | 265
| MT3 | 150 | 97 | 265 | 01.10.22 | 18:00
| MT4 | 150 | 97 | 265
| TR1 | 225 | 86 | 219
Ishurdi | TR2 | 225 | 86 | 219 | 23.10.22 | 17:56
| TR3 | 225 | 86 | 219
Khulna(S) | TR1 | 225 | 83 | 218
| TR2 | 225 | 83 | 218 | 09.10.22 | 13:00
| TR3 | 300 | 105 | 279
Bogura | TR1 | 225 | 100 | 298
| TR2 | 225 | 100 | 298 | 08.10.22 | 18:00
| TR3 | 225 | 134 | 403
Baghabari | TR1 | 300 | 168 | 470 | 08.10.22 | 20:00
| TR2 | 225 | 125 | 350
Rajshahi | ATR-01 | 300 | 116 | 302
| ATR-02 | 300 | 116 | 302 | 02.10.22 | 6:00
Barapukuria | TR1 | 225 | 144 | 674 |  |  | Due to unavailability of 230 kV side meters
| TR2 | 225 | 134 | 620 | 01.10.2022 | 19:30 | 132 kV current is being provided
| TR6 | 300 | 174 | 793
Bheramara | Transformer-1 | 225 | 73 | 191
| Transformer-2 | 225 | 73 | 191 | 10.10.2022 | 18:30
Shyampur | ATR-01 | 300 | 122 | 380
| ATR-02 | 300 | 122 | 380 | 02.10.22 | 24:00
Kaliakoir | TR1 | 300 | 118 | 540 | 29.10.22 | 17:30
Sikalbaha | ATR-1 | 300 | 189 | 547
| ATR-2 | 300 | 189 | 547 | 12.10.22 | 19:00
Jhenaidah | T1(230/132 kV) | 300 | 168 | 510 | 10.10.2022 | 18:30
| T2(230/132 kV) | 300 | 168 | 510
Page: 2/2 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 400/230 & 400/132 kV Transformer
Month:October 2022
Name of the | Transformer |  | Recorded maximum load |  |  |  | Remarks
sub-station | Name | Capacity ( MVA ) | MW | Amps (400 kV side) | Date | Time
Kaliakoir | TR1(400/230 kV) | 520 | 243.1 | 370 | 07.10.2022 | 11:30
| TR2(400/230 kV) | 520 | 245.6 | 371
| TR1(400/132 kV) | 325 | 320.7 | 509 | 13.10.2022 | 22:30
| TR2(400/132 kV) | 325 | 320.6 | 523
Bibiyana | ICT1(400/230 kV) | 520 | 206 | 308 | 31.10.2022 | 21:00
| ICT2(400/230kV) | 520 | 201 | 304
Bhulta | ATR1(400/230 kV) | 520 | 342 | 590 | 13.09.2022 | 13:15
| ATR2(400/230kV) | 520 | 342 | 590
Ashuganj(N) | GSUT1(400/230 kV) | 567 | 370 | 604 | 02.10.2022 | 22:16
Gopalganj | ATR1(400/138 kV) | 325 | 287 | 427 | 01.10.22 | 24:00
| ATR2(400/138kV) | 325 | 287 | 427
Payra | GSUT1 | 270 | 625 | 911 | 18.10.2022 | 21:22
| GSUT2 | 270 | 590 | 866 | 02.10.2022 | 24:14
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-37
Page: 1/2 |  |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
[6 empty] | Report on load shedding | [13 empty] | Report on load shedding
Month: October 2022 | [6 empty] | (For Evening Peak) | [7 empty] | Month: October 2022 | [6 empty] | (For Day Peak)
| Peak Hour |  | Total load shed (SS end) | [12 empty] | Peak Hour |  | Total load shed (SS end)
Date | Generation (Gen End) | Demand (Gen End) |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks | Date | Generation | Demand (Gen End) |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur
2022-10-01 | 12773 | 14300 | 1407 | 21:00 | 490 | 0 | 237 | 167 | 89 | 119 | 144 | 0 | 161 | - | 2022-10-01 | 11274 | 12497 | 1127 | 12:00 | 447 | 187 | 90 | 74 | 60 | 157 | 54 | 0 | 58 | -
2022-10-02 | 12369 | 13372 | 924 | 21:00 | 248 | 0 | 158 | 142 | 64 | 116 | 106 | 0 | 90 | - | 2022-10-02 | 10572 | 11100 | 487 | 12:00 | 262 | 168 | 0 | 0 | 0 | 23 | 34 | 0 | 0 | -
2022-10-03 | 12087 | 12683 | 549 | 21:00 | 20 | 0 | 161 | 126 | 65 | 138 | 0 | 0 | 39 |  | 2022-10-03 | 10146 | 10975 | 764 | 12:00 | 629 | 73 | 0 | 0 | 9 | 22 | 31 | 0 | 0 | -
2022-10-04 | 8431 | 13200 | 4395 | 21:00 | 2002 | 500 | 12 | 185 | 440 | 665 | 350 | 0 | 241 | - | 2022-10-04 | 10161 | 10975 | 1419 | 12:00 | 709 | 235 | 0 | 0 | 162 | 227 | 86 | 0 | 0 | -
2022-10-05 | 11790 | 13282 | 1375 | 20:00 | 712 | 0 | 0 | 0 | 200 | 230 | 99 | 0 | 134 | - | 2022-10-05 | 9390 | 11134 | 1607 | 12:00 | 997 | 254 | 0 | 0 | 178 | 92 | 86 | 0 | 0 | -
2022-10-06 | 11990 | 13275 | 1184 | 20:00 | 429 | 36 | 0 | 0 | 264 | 293 | 162 | 0 | 0 | - | 2022-10-06 | 9821 | 11654 | 1689 | 10:00 | 978 | 209 | 0 | 0 | 198 | 229 | 75 | 0 | 0 | -
2022-10-07 | 11904 | 12950 | 964 | 20:00 | 207 | 88 | 50 | 0 | 253 | 246 | 110 | 0 | 10 | - | 2022-10-07 | 9241 | 10600 | 1252 | 9:00 | 330 | 200 | 0 | 0 | 250 | 355 | 117 | 0 | 0 | -
2022-10-08 | 12289 | 13872 | 1459 | 19:30 | 600 | 278 | 0 | 18 | 41 | 355 | 167 | 0 | 0 | - | 2022-10-08 | 9737 | 11688 | 1798 | 12:00 | 962 | 249 | 0 | 0 | 197 | 282 | 108 | 0 | 0 | -
2022-10-09 | 12383 | 13452 | 985 | 21:00 | 356 | 0 | 0 | 0 | 256 | 262 | 111 | 0 | 0 | - | 2022-10-09 | 9703 | 11550 | 1702 | 12:00 | 876 | 299 | 0 | 0 | 215 | 268 | 44 | 0 | 0 | -
2022-10-10 | 12901 | 13923 | 942 | 20:00 | 382 | 0 | 0 | 0 | 232 | 209 | 50 | 0 | 69 | - | 2022-10-10 | 10256 | 12358 | 1937 | 12:00 | 1081 | 273 | 0 | 0 | 225 | 297 | 61 | 0 | 0 | -
2022-10-11 | 12388 | 13003 | 567 | 20:00 | 214 | 0 | 0 | 0 | 231 | 122 | 0 | 0 | 0 | - | 2022-10-11 | 10233 | 12019 | 1646 | 12:00 | 1041 | 138 | 0 | 0 | 211 | 228 | 28 | 0 | 0 | -
2022-10-12 | 12281 | 12758 | 440 | 19:30 | 144 | 0 | 0 | 0 | 111 | 185 | 0 | 0 | 0 | - | 2022-10-12 | 10559 | 11070 | 471 | 12:00 | 277 | 0 | 0 | 0 | 64 | 130 | 0 | 0 | 0 | -
2022-10-13 | 12747 | 12856 | 100 | 20:00 | 0 | 0 | 0 | 0 | 20 | 80 | 0 | 0 | 0 | - | 2022-10-13 | 10656 | 11307 | 600 | 12:00 | 402 | 144 | 0 | 0 | 0 | 36 | 18 | 0 | 0 | -
2022-10-14 | 12363 | 12596 | 215 | 20:00 | 7 | 0 | 0 | 0 | 30 | 169 | 9 | 0 | 0 | - | 2022-10-14 | 9778 | 10393 | 567 | 12:00 | 363 | 95 | 0 | 0 | 68 | 41 | 0 | 0 | 0 | -
2022-10-15 | 12348 | 13354 | 927 | 19:30 | 374 | 0 | 0 | 0 | 189 | 211 | 102 | 0 | 51 | - | 2022-10-15 | 10119 | 10987 | 800 | 12:00 | 601 | 132 | 0 | 0 | 46 | 0 | 21 | 0 | 0 | -
2022-10-16 | 12309 | 13177 | 800 | 20:00 | 344 | 0 | 0 | 0 | 170 | 160 | 104 | 0 | 22 | - | 2022-10-16 | 10481 | 11280 | 736 | 12:00 | 557 | 135 | 0 | 0 | 0 | 10 | 34 | 0 | 0 | -
2022-10-17 | 12385 | 13593 | 1113 | 21:00 | 368 | 151 | 0 | 95 | 188 | 161 | 76 | 0 | 74 | - | 2022-10-17 | 9896 | 11740 | 1699 | 12:00 | 1142 | 280 | 0 | 0 | 73 | 131 | 73 | 0 | 0 | -
2022-10-18 | 12255 | 13660 | 1295 | 20:00 | 208 | 216 | 0 | 162 | 210 | 260 | 125 | 0 | 114 | - | 2022-10-18 | 10351 | 12043 | 1559 | 12:00 | 842 | 233 | 0 | 0 | 229 | 188 | 67 | 0 | 0 | -
2022-10-19 | 12314 | 13019 | 650 | 21:00 | 145 | 107 | 0 | 0 | 189 | 131 | 78 | 0 | 0 | - | 2022-10-19 | 10144 | 11224 | 995 | 12:00 | 598 | 144 | 0 | 0 | 109 | 130 | 14 | 0 | 0 | -
2022-10-20 | 12286 | 13150 | 796 | 20:00 | 330 | 0 | 0 | 0 | 192 | 170 | 104 | 0 | 0 | - | 2022-10-20 | 10122 | 11856 | 796 | 12:00 | 989 | 294 | 0 | 0 | 156 | 96 | 63 | 0 | 0 | -
2022-10-21 | 12276 | 12500 | 206 | 19:30 | 10 | 0 | 0 | 0 | 80 | 116 | 0 | 0 | 0 | - | 2022-10-21 | 9451 | 9499 | 44 | 10:00 | 19 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | -
2022-10-22 | 12318 | 12952 | 584 | 21:00 | 160 | 0 | 0 | 0 | 121 | 200 | 103 | 0 | 0 | - | 2022-10-22 | 9750 | 10449 | 1062 | 12:00 | 903 | 100 | 0 | 0 | 34 | 25 | 0 | 0 | 0 | -
2022-10-23 | 11939 | 13060 | 1033 | 21:00 | 168 | 193 | 110 | 140 | 129 | 222 | 23 | 0 | 48 | - | 2022-10-23 | 9817 | 11440 | 1496 | 12:00 | 863 | 208 | 0 | 0 | 180 | 158 | 71 | 0 | 16 | -
2022-10-24 | 5652 | 5652 | 0 | 18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2022-10-24 | 8146 | 8146 | 0 | 9:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2022-10-25 | 9032 | 9032 | 0 | 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2022-10-25 | 6655 | 6655 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2022-10-26 | 10800 | 10800 | 0 | 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2022-10-26 | 9263 | 9350 | 80 | 12:00 | 0 | 0 | 0 | 0 | 71 | 0 | 9 | 0 | 0 | -
2022-10-27 | 11028 | 11028 | 0 | 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2022-10-27 | 9524 | 9860 | 310 | 12:00 | 0 | 150 | 0 | 0 | 0 | 77 | 83 | 0 | 0 | -
2022-10-28 | 10071 | 10071 | 0 | 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2022-10-28 | 8594 | 8594 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2022-10-29 | 11060 | 11060 | 0 | 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2022-10-29 | 9040 | 9040 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-10-30 | 11230 | 11300 | 65 | 19:30 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2022-10-30 | 9865 | 10112 | 228 | 12:00 | 0 | 163 | 0 | 0 | 0 | 6 | 59 | 0 | 0
2022-10-31 | 11431 | 11815 | 354 | 20:00 | 169 | 75 | 0 | 0 | 70 | 30 | 10 | 0 | 0 |  | 2022-10-31 | 9836 | 10250 | 382 | 12:00 | 176 | 100 | 0 | 0 | 84 | 0 | 22 | 0 | 0
23329
| Max. L/S | - | 4395 | - | [10 empty] | Max. L/S | - |  | 1937
| Min. L/S | - | 54 | - | [10 empty] | Min. L/S | - |  | 0
| No. of Days | - | 31 | - | [10 empty] | No. of Days | - | 31
| Average L/S |  | 21566 | [11 empty] | Average L/S |  | 19669
|  | - | - | - | [11 empty] | - | -
|  |  | - | -
[15 empty] | -477 | 511 | 12
[15 empty] | -109 | 651 | 13
[15 empty] | -233 | 615 | 14
[15 empty] | -1006 | 868 | 15
[15 empty] | -868 | 799 | 16
[15 empty] | -1208 | 1844 | 17
[15 empty] | -1405 | 1692 | 18
[15 empty] | -705 | 1080 | 19
[15 empty] | -864 | 1734 | 20
[15 empty] | -224 | 48 | 21
[15 empty] | -634 | 699 | 22
[15 empty] | -1121 | 1623 | 23
[15 empty] | 0 | 0 | 24
[15 empty] | 0 | 0 | 25
[15 empty] | 0 | 87 | 26
[15 empty] | 0 | 336 | 27
[15 empty] | 0 | 0 | 28
[15 empty] | #REF! | #REF! | 29
[15 empty] | #REF! | #REF! | 30
[15 empty] | #REF! | #REF! | 31

## QF-LDC-38
Page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month:October 2022
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 12901 | 2022-10-10 | 20:00
2 | Maximum Day Peak Genaration | MW | 11274 | 2022-10-01 | 12:00
3 | Maximum Evening Peak Demand | MW | 14300 | 2022-10-31 | 20:00
4 | Minimum Generation | MW | 2828 | 2022-10-25 | 6:00
5 | Average of the daily evening peak Genaration | MW | 11594.5161 | - | -
6 | Average of the daily day peak Genaration | MW | 9760.6774 | - | -
7 | Maximum load shed | MW | 4395 | 2022-10-04 | 21:00
8 | Minimum load shed | MW | 0 | 2022-10-24 | 21:00
9 | Total nos. of load shed days | Day | 25 | - | -
10 | Average load shed ( Avg. of the 31 days in the month) | MW/Day | 752.5484 | - | -
11 | Total Generation | MkWh | 7469.9161 | - | -
12 | Total Generation by BPDB | MkWh | 1483.1714 | % of total Gen. | 19.86%
13 | Total Generation by IPP | MkWh | 2463.4808 | '' | 32.98%
14 | A) Total Generation by Generation Companies | MkWh | 2344.6191 | '' | 31.39%
| B) Total Generation by REB | MkWh | 114.4586 | " | 1.532%
| C) Total Generation by RENTAL | MkWh | 308.6068 | " | 4.131%
| D) Total Imported from India (BIPTC) | MkWh | 658.9362 | " | 8.821%
| E) Total Imported from Tripura, India (A.C) | MkWh | 96.6432 | " | 1.294%
15 | Fuel wise Generation.
| A) Gas | MkWh | 3736.515 | % of total Gen. | 50.02%
| B) Oil | MkWh | 2106.1432 | '' | 28.2%
| C) Hydro | MkWh | 110.3709 | '' | 1.478%
| D) Solar | MkWh | 41.0067 | '' | 0.549%
| E) Coal | MkWh | 720.3009 | '' | 9.643%
| F) BIPTC (Import from India) | MkWh | 658.9362 | '' | 8.821%
| G) A.C (Import from Tripura, India) | MkWh | 96.6432 | '' | 1.294%
16 | Maximun of the daily total Generation . | MkWh | 280.1182 | 2022-10-01
17 | Monthly Load factor | % | 86.4057 | - | -
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 39473.6233 | - | -
| A) Gas | M.Taka | 3983.4903 | - | -
| B) Liquid fuel | M.Taka | 26371.2014 | - | -
| C) Coal | M.Taka | 5644.3225 | - | -
| D) BIPTC (Import from India) | M.Taka | 2780.711 | - | -
| E) Tripura(Import from India) | M.Taka | 693.8982 | - | -
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 1682.8656 | 2022-10-23
| A) Gas | M.Taka | 148.4167 | 2022-10-05
| B) Liquid fuel | M.Taka | 1268.9181 | 2022-10-23
| C) Coal | M.Taka | 266.2557 | 2022-10-23
| D) BIPTC (Import from India) | M.Taka | 1682.8656 | 2022-10-02
20 | Average fuel cost of per unit Generation
| A) Including Hydro & Solar | Taka/kWhR | 6.7855
| B) Excluding Hydro & Solar | Taka/kWhR | 6.9251
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 108.9 | 31/10/2022 | 06:00
b) | Actual | FT (MSL) | 95.9 | 31/10/2022 | 06:00
22 | Peak Genaration of October2021 | MW | 13482 | 2021-10-11 | 21:00
23 | Peak Demand of October 2021 | MW | 13482 | 2021-10-11 | 21:00
24 | Maximum peak Generation recorded upto 31/10/2022 | MW | 14782 | 16/04/2022 | 21:00
25 | Maximum peak Demand recorded upto 31/10/2022 | MW | 14782 | 16/04/2022 | 21:00
26 | Maximum load shed recorded upto 31/10/2022 | MW | 1459 | 04/05/2010 | 20:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## FGMO
Power Grid Company Of Bangladesh Ltd.
NLDC, Aftabnagar, Dhaka.
Monthly status of Free Governor Mode of Operation (FGMO) Power Plants
SL | Plant Name | Owner | Installed capacity | FGMO Status
|  |  | (MW) | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
1 | Bibiana-II 341 MW CCPP (Summit) | IPP | 341 | √ | √ | √ | √ |  |  |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
2 | Shahjibazar GTPP Unit 8 & 9 | BPDB | 70
3 | Sirajgonj 400 MW CCPP Unit-4 | IPP | 414
4 | Sirajgonj 225MW CCPP Unit-3 | NWPGCL | 220
5 | Sirajgonj 225MW CCPP Unit-2 | NWPGCL | 220
6 | Meghnaghat CCPP(Summit) | IPP | 335
7 | Ashuganj 450 MW CCPP(North) | APSCL | 360 | [12 empty] | √ | √ | √ | √ | √ | √
8 | Ashuganj 225 MW CCPP | APSCL | 221
9 | Bheramara 410 MW CCPP | NWPGCL | 410
10 | Haripur 412 MW CCPP | EGCB | 412
11 | Fenchugonj CCPP Phase-1 | BPDB | 97
12 | Chandpur 150 MW CCPP | BPDB | 163
13 | Siddhirganj 2x120 MW GTPP | EGCB | 210
14 | Shikalbaha 225 MW CCPP | BPDB | 225
15 | Shikalbaha Peaking GT | BPDB | 150
16 | Shahjibazar 330 MW CCPP | BPDB | 330
17 | Ashuganj 450 MW CCPP(South) | APSCL | 360 | [12 empty] | √ | √ | √ | √ | √ | √ | √
18 | Fenchugonj CCPP Phase-2 | BPDB | 104
19 | Bhola 225 MW CCPP | BPDB | 194
20 | Ghorasal 365 MW CCPP Unit-7 | BPDB | 365
21 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | 210
22 | Siddhirganj 335 MW CCPP | EGCB | 335
23 | Bibiyana-III 400 MW CCPP | BPDB | 400
24 | Sylhet 225 MW CCPP | BPDB | 231
25 | RPCL 210 MW CCPP | IPP | 210
26 | Khulna 225 MW CCPP | NWPGCL | 230
27 | a) Baghabari 71 MW GTPP | BPDB | 71
| b) Baghabari 100 MW GTPP | BPDB | 100
28 | Karnaphuli Hydro PP Unit: 1 | BPDB | 40
| Karnaphuli Hydro PP Unit: 2 | BPDB | 40
| Karnaphuli Hydro PP Unit: 3 | BPDB | 50
| Karnaphuli Hydro PP Unit: 4 | BPDB | 50
| Karnaphuli Hydro PP Unit: 5 | BPDB | 50
29 | a) Ghorasal Repowered CCPP Unit-3 | BPDB | 416
| b) Ghorasal Repowered CCPP Unit-4 | BPDB | 410
30 | Bibiyana South 400 MW CCPP | BPDB | 383
31 | Barapukuria 275 MW TPP Unit-3 | BPDB | 274
32 | Shajibazar 100 MW PP | BPDB | 100
33 | Payra 1320 MW Unit-1 | BCPCL | 622
34 | Kushiara 163 MW CCPP (KP) | IPP | 163
35 | Haripur 360MW CCPP(HPL) | IPP | 360
36 | Meghnaghat 450 MW CCPP(MPL) | IPP | 450
due to gas shortage