## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2022-12-17 | Saturday
|  | Date (day): | 2022-12-17 |  | Saturday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 8560.6 | MW |  |  | (b) At Evening Peak Hour : |  | 10962 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2022-12-16 | 2022-12-17 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Line O/L
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 | 365 |  | Gas shortage
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 69 | 70 | 70 | 70 | 38 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 394 | 361 | 400 | 400 | 12 |  | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 352 | 282 | 350 | 350 | 10 |  | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 225 | 225 | 225 |  | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 1 | 0 | 35 | 50 | 50 |  | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 0 | 0 | 34 | 34 | 68 |  | Fuel shortage
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 0 | 0 | 15 | 15 | 40 |  | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 10 | 22 | 22 |  |  | Machine problem
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 0 | 0 | 50 | 85 |  | 15 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 16 | 50 | 94 | 50 | 52 |  | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 54 | 17 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 16 | 0 | 32 | 32 | 117 |  | Fuel shortage
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 55 | 17 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 55 | 17 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 43 | 45 | 49 | 49 |  | 31 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 22 | 22 | 22 | 25 |  | 8 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 0 | 0 | 50 | 50
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 15 | 95 | 65 | 195 | 105 |  | Fuel shortage
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 150 | 150 |  | Fuel conservation
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 0 | 0 | 0 | 50 | 50 |  | Fuel conservation
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 50 | 50 |  | Fuel conservation
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 17 | 35 | 35 | 35 | 114 |  | Fuel shortage
36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 17 | 17 | 70 | 105
37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 55 | 54 | 55 | 55 | 49 |  | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 17 | 162 | 17 | 162
39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 25 | 0 | 30 | 0
40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 5 | 21 | 18 | 18 | 37 |  | Fuel shortage
| Dhaka area Total |  |  |  |  | 6263 | 5847 | 1545 | 1826 | 2002 | 2654 | 2463 | 734
41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 1 | 0 | 17 | 25
43 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 16 | 0 | 20 | 0
44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 1 | 19 | 20 | 20 |  | 30 | Engine problem
45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 46 | 46 | 46 | 46 | 184 |  | Low Water Level
46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | Under maint
47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 17 | 34 | 20 | 51 | 54 |  | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 22 | 33 | 65 |  | Fuel shortage
50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 17 | 51 | 17 | 50 | 52 |  | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 10 | 10 | 10 | 10 | 90 |  | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 12 | 12 | 12 | 88 |  | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 22 |  | Gas shortage
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 35 | 28 | 7 | 15
54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 1 | 0 | 0 | 108 |  | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 51 | 141 | 50 | 300
57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 17 | 36 | 17 | 36 |  | 18 | Engine problem
58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 54 | 90 | 54 | 92 |  | 18 | Engine problem
59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 12 | 12 | 12 | 88 |  | Fuel shortage
60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 107 | 107 | 107 | 107 |  | 9 | Engine problem
| Mirsharai 150 MW |  | Gas/HSD | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0
| Chattogram area Total |  |  |  |  | 2442 | 2382 | 400 | 587 | 436 | 809 | 1111 | 450
61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 118 | 161 | 200 | 220 |  |  | FGMO
63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 | 360 |  | S/D due to Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 280 | 275 | 310 | 320 | 40 |  | FGMO
65 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 318 | 318 | 353 | 353 |  |  | On test.
66 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 10 | 10 | 10 | 10 | 35 |  | Gas shortage
67 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 55 | 5 | 5 | 5 | 5 | 50 |  | Gas shortae
68 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
69 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 20 | 51 | 51 | 51
70 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 105 | 15 | 108 | 42 |  | Fuel shortage
71 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 20 | 40 |  | 12 | Engine problem
72 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 | 163 |  | Under Maint.
73 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 17 | 72 | 34 | 200
74 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 21 | 21 | 21
75 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 10 | 10 | 10 | 10
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 84 | 96 | 135 | 153
76 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 22 | 33 | 33 | 33
77 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 8 | 8 | 44 |  | Fuel shortage
78 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 15 | 15 | 15 | 15 |  | 10 | Engine problem
79 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 100 | 100 |  | Fuel conservation
80 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 0 | 17 | 17 | 97 |  | Fuel shortage
81 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 1 | 8 | 65 | 113
82 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 17 |  | 37 | Engine problem
83 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 42 | 52 | 34 | 52 |  | 63 | Engine problem
| Cumilla Area Total |  |  |  |  | 3309 | 3285 | 1003 | 1257 | 1361 | 1854 | 1252 | 122
84 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 106 | 216 | 109 | 150 | 52 |  | Gas shortage
85 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 19 | 19 | 3 |  | Gas shortage
86 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0
87 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
88 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 33 | 56 | 50 | 57 | 143 |  | Fuel shortage
89 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 33 | 57 | 47 | 59 | 56 |  | Fuel shortage
90 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 34 | 0 | 50 | 0
91 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 12 | 12 |  | 10 | Engine problem
| Mymensingh Area Total |  |  |  |  | 717 | 614 | 239 | 360 | 288.6 | 297 | 55 | 10
92 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 30 | 30 | 30 | 30 |  | 40 | Machine problem.
93 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 42 | 42 | 42 | 42 |  | 48 | Machine problem
94 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 | 78 |  | Gas shortage
95 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
96 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 22 | 22 | 22 | 22
97 | Fenchuganj 44MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 10 | 10 | 20 | 20 | 30 |  | Gas Shortage
98 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 8 | 8 | 3 |  | Gas shortage
99 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 51 | 32 | 30 | 30 | 36 |  | Gas Shortage
100 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 30 | 30 | 50 | 86
101 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
102 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 218 | 178 | 218 | 218
103 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 19 | 19 | 19
104 | Sylhet 50MW PP (EPL) |  | Gas | NENP | 27*2 | 50 | 50 | 11 | 11 | 11 | 11 | 39 |  | Gas shortage
105 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 21 | 22 | 22 | 22
106 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 0 | 0 | 0 | 0 |  | 341 | Under maint. |  | 2022-12-23
107 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 387 | 418 | 400 | 400
108 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
109 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 260 | 220 | 260 | 260 |  | 123 | Machine problem
| Sylhet Area Total |  |  |  |  | 2522 | 2477 | 1118 | 1052 | 1142 | 1178 | 186 | 982
110 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 682 | 873 | 952 | 952
111 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 0 | 16 | 16 | 49 |  |  | Line O/L
112 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 45 |  | 9 | Engine problem
113 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
114 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 85 |  | 24 | Engine problem
115 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 | 410 |  | Gas shortage.
116 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 0 | 0 | 40
117 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 0 | 50 | 50 |  | Fuel conservation
118 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 17 | 94 | 15 | 94 |  | 11 | Engine problem
119 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Fuel shortage
120 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 78 | 0 | 100 | 0
| Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 0 | 0 | 0 | 406 | 405 | 500 | 500 |  |  | On test.
| Khulna Area Total |  |  |  |  | 2388 | 2384 | 1183 | 1388 | 1583 | 1815 | 811 | 44
121 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 0 | 0 |  |  | Line O/L
122 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 18 | 22 | 18 | 25 |  | 15 | Engine problem
123 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 182 | 184 | 187 | 187 |  | 7
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
124 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 290 | 260 | 330 | 350 |  | 894 | Unit-1 U/M &Rampal Test
125 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 190 | 160 | 220 | 220
126 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 0 | 35 |  |  | Line O/L
| Barisal 307 MW |  | Coal | BCPCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Barisal Area Total |  |  |  |  | 1958 | 1958 | 680 | 626 | 755 | 817 | 0 | 916
127 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
128 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 32 |  | 20 | Engine problem
129 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 25 |  | 46 | Engine problem
130 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
131 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 25 | 16 | 16 | 50
132 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 41 | 0 | 40 | 10 |  | Fuel shortage
133 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 189 | 160 | 200 | 210
134 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Fuel shortage
135 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
136 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 397 | 276 | 400 | 410
137 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 35 | 0 | 35 |  | 15 | Engine problem
138 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 0 | 18 | 15 | 15 |  |  | Machine problem
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
139 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
140 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 8 | 8 | 8 |  | 44 | Engine problem
141 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 0 | 90 |  | 14 | Engine problem
142 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel shortage
143 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 35 | 111 | 35 | 113
144 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 35 | 35 | 35 | 113
145 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 3 | 0 | 6 | 0
| Adani Power Jharkhanda Ltd |  | Coal | Import | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Rajshahi Area Total |  |  |  |  | 2179 | 2129 | 703 | 711 | 726 | 1152 | 821 | 139
146 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal shortage
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
147 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 160 | 160 | 160 | 160 |  |  | Machine problem
148 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
149 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
150 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 34 | 107 | 34 | 113
151 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 3 | 0 | 8 | 0
152 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 17 | 34 | 35 | 113
153 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 17 | 0 | 30 | 0
| Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 0 | 0 | 70 | 0 | 0 | 0
| Rangpur Area Total |  |  |  |  | 830 | 750 | 301 | 301 | 267 | 386 | 125 | 85
| Total |  |  |  |  | 22608 | 21826 | 7172 | 8108 | 8560.6 | 10962 | 6824 | 3482
A. |  | 2022-12-16 | (Yesterday) |  |  |  |  | Friday
1 | Highest Generation : |  |  | 8108 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
2 | Minimum Generation : |  |  | 6158 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 8108 | MW
3 | Day peak Generation : |  |  | 7172 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 7633.72 | MW
4 | Evening peak Generation : |  |  | 8108 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 169.1588 | MKWHr | By Solar | 1.4396 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Gas : | 103.4012 | MKWHr |  | By Oil: | 21.9835 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 22.4093 | MKWHr |  | By Hydro: | 1.1256 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 6824 | MW | Dhaka | 2520.53 | 2520.53 |  | 0 |  | 18:00 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 3482 | MW | Chittagong | 854 | 854 |  | 0 |  | 19:00 |  | 0
|  |  | Total = |  |  | 10306 | MW | Khulna | 986.8 | 986.8 |  | 0 |  | 19:30 |  | 0
7 | Total Gas Supplied : |  |  | 768.17 | MMCFD |  |  | Rajshahi | 837.4 | 837.4 |  | 0 |  | 20:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 107244768.458 | ii) Oil : | Taka | 280349281.72 | Comilla | 646 | 646 |  | 0 |  | 21:00 |  | 0
|  | iii) Coal : |  | 91893776 | Total | Taka | 479487826.178 | Mymensingh | 674 | 674 |  | 0 |  | 22:00 |  | 0
9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0 | MKWHr. | Sylhet | 326 | 326 |  | 0 |  | 23:00 |  | 0
| ii) During Peak Demand : |  |  | 936 | MW (E to W) at | 19:00 | hrs | Barisal | 216.99 | 216.99 |  | 0 |  | 24:00 |  | 0
| iii) Maximum : |  |  | 664 | MW at | 6:00 | hrs | Rangpur | 572 | 572 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 25.4° C |  |  | Total | 7633.72 | 7633.72 |  | 0
B. |  | 2022-12-17 | (Today) |  |  |  | Saturday |  |  | Probable max. temperature in Dhaka |  |  | 26.4° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 9900 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 10962 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 7800 | MW
4 | Reserve(Generation end) |  |  |  | 1062 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 206.5457 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5506 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 16.8269 | MKWHr. | ii) HVDC Flow at Peak Time |  | 873 | MW at | 19:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.9728 | MKWHr. | iii) Maximum HVDC Flow : |  | 873 | MW at | 19:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 88.15 |  | (b) Today: | 88.03 |  | (c) Rule Curve: |  | 104.5
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2022-12-16
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 0 | 72 | 0 | 396 | 327 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 22 | 22 | 27 | 22 | 28 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 152 | 0 | 0 | 0 |  | 12 | 0 | 17 | 10 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 305 | 182 | 8 | 0 | 10 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 10 | 33 | 15 | 82 | 109 | 0 | 19 | 0 | 30 | 42 | 11 | 30 | 0 | 0 | 40 | 70 | 0 | 217 | 19 | 11 | 10 | 0 | 22 | 8 | 0 | 30 | 0 | 0 | 48 | 0 | 17 | 0 | 12 | 17 | 0 | 405 | 24 | 0 | 17 | 0 | 51 | 17 | 54 | 0 | 8 | 12 | 171 | 17 | 0 | 17 | 107 | 0 | 17 | 0 | 17 | 17 | 353 | 0 | 0 |  | 728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 327 | 17 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 320 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 489 | 0 | 0 | 0 | 0 |  | 4437 | 2739 | 7176 | 3279 | 728 | 1426 | 0 | 629 | 969 | 46 | 0 | 17 | 82 | 0 | 0 | 88.17
2:00 | 0 | 0 | 0 | 180 | 0 | 72 | 0 | 395 | 301 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 22 | 27 | 22 | 15 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 152 | 0 | 0 | 0 |  | 12 | 0 | 17 | 10 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 305 | 182 | 8 | 0 | 10 | 5 | 0 | 51 | 0 | 0 | 0 | 16 | 10 | 33 | 15 | 78 | 109 | 0 | 19 | 0 | 30 | 42 | 11 | 10 | 0 | 0 | 40 | 70 | 0 | 218 | 19 | 11 | 10 | 0 | 21 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 12 | 17 | 0 | 399 | 8 | 0 | 0 | 0 | 51 | 17 | 54 | 0 | 0 | 12 | 200 | 17 | 0 | 17 | 107 | 0 | 17 | 0 | 17 | 17 | 321 | 0 | 0 |  | 611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 483 | 0 | 0 | 0 | 0 |  | 4203 | 2497 | 6700 | 3210 | 611 | 1379 | 0 | 426 | 933 | 46 | 0 | 17 | 78 | 0 | 0 | 88.17
3:00 | 0 | 0 | 0 | 180 | 0 | 72 | 0 | 395 | 308 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 22 | 27 | 22 | 24 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12 | 0 | 17 | 10 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 275 | 182 | 8 | 0 | 10 | 5 | 0 | 10 | 0 | 0 | 0 | 16 | 10 | 33 | 15 | 72 | 109 | 0 | 19 | 0 | 30 | 42 | 11 | 10 | 0 | 0 | 40 | 30 | 0 | 218 | 19 | 11 | 10 | 0 | 21 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 12 | 17 | 0 | 399 | 8 | 0 | 4 | 0 | 51 | 17 | 54 | 0 | 0 | 12 | 200 | 17 | 0 | 17 | 107 | 0 | 17 | 0 | 17 | 17 | 319 | 0 | 0 |  | 611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 490 | 0 | 0 | 0 | 0 |  | 3957 | 2473 | 6430 | 3022 | 611 | 1292 | 0 | 430 | 940 | 46 | 0 | 17 | 72 | 0 | 0 | 88.16
4:00 | 0 | 0 | 0 | 180 | 0 | 72 | 0 | 348 | 269 |  | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 22 | 27 | 22 | 30 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12 | 0 | 17 | 10 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 275 | 181 | 8 | 0 | 10 | 5 | 0 | 10 | 0 | 0 | 0 | 16 | 10 | 33 | 15 | 72 | 109 | 0 | 19 | 0 | 30 | 42 | 11 | 10 | 0 | 0 | 40 | 30 | 0 | 217 | 19 | 11 | 10 | 0 | 21 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 12 | 17 | 0 | 385 | 8 | 0 | 17 | 0 | 51 | 17 | 54 | 0 | 0 | 12 | 256 | 17 | 0 | 17 | 107 | 0 | 17 | 0 | 17 | 17 | 318 | 0 | 0 |  | 611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 484 | 0 | 0 | 0 | 0 |  | 3884 | 2464 | 6348 | 3019 | 611 | 1206 | 0 | 443 | 934 | 46 | 0 | 17 | 72 | 0 | 0 | 88.16
5:00 | 0 | 0 | 0 | 180 | 0 | 32 | 0 | 331 | 268 |  | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 22 | 27 | 22 | 30 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12 | 0 | 17 | 10 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 275 | 151 | 8 | 0 | 10 | 5 | 0 | 10 | 0 | 0 | 0 | 16 | 10 | 33 | 15 | 70 | 109 | 0 | 19 | 0 | 30 | 42 | 11 | 10 | 0 | 0 | 40 | 10 | 0 | 217 | 19 | 11 | 10 | 0 | 21 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 12 | 17 | 0 | 363 | 8 | 0 | 17 | 0 | 51 | 17 | 54 | 0 | 0 | 12 | 260 | 17 | 0 | 17 | 107 | 0 | 17 | 0 | 17 | 0 | 318 | 0 | 0 |  | 610 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 490 | 0 | 0 | 0 | 0 |  | 3739 | 2419 | 6158 | 2954 | 610 | 1105 | 0 | 426 | 930 | 46 | 0 | 17 | 70 | 0 | 0 | 88.15
6:00 | 0 | 0 | 0 | 180 | 0 | 32 | 0 | 340 | 267 |  | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 22 | 27 | 22 | 31 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12 | 0 | 17 | 10 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 275 | 151 | 8 | 0 | 10 | 5 | 0 | 10 | 0 | 0 | 0 | 16 | 10 | 33 | 15 | 72 | 109 | 0 | 19 | 0 | 30 | 42 | 11 | 10 | 0 | 0 | 40 | 10 | 0 | 217 | 19 | 11 | 10 | 0 | 21 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 12 | 17 | 0 | 352 | 8 | 0 | 17 | 0 | 51 | 17 | 54 | 0 | 0 | 12 | 260 | 17 | 0 | 17 | 107 | 0 | 17 | 0 | 17 | 0 | 318 | 0 | 0 |  | 611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 490 | 0 | 0 | 0 | 0 |  | 3739 | 2461 | 6200 | 2953 | 611 | 1135 | 0 | 426 | 940 | 46 | 0 | 17 | 72 | 0 | 0 | 88.15
7:00 | 0 | 0 | 0 | 180 | 0 | 32 | 0 | 375 | 269 |  | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 22 | 27 | 22 | 31 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12 | 0 | 17 | 10 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 295 | 148 | 8 | 0 | 10 | 5 | 0 | 10 | 0 | 0 | 0 | 16 | 10 | 33 | 15 | 76 | 109 | 0 | 19 | 0 | 30 | 42 | 11 | 10 | 0 | 0 | 40 | 10 | 0 | 217 | 19 | 11 | 10 | 0 | 21 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 1 | 12 | 17 | 0 | 352 | 8 | 0 | 17 | 0 | 51 | 17 | 54 | 0 | 0 | 12 | 260 | 17 | 1 | 17 | 107 | 0 | 17 | 1 | 17 | 0 | 331 | 0 | 0 |  | 611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 170 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 495 | 0 | 0 | 0 | 0 |  | 3814 | 2473 | 6287 | 3018 | 611 | 1142 | 0 | 426 | 945 | 46 | 0 | 17 | 76 | 6 | 0 | 88.15
8:00 | 0 | 0 | 0 | 180 | 0 | 58 | 0 | 396 | 356 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 22 | 22 | 27 | 22 | 31 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12 | 0 | 17 | 10 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 310 | 136 | 8 | 0 | 10 | 5 | 0 | 10 | 0 | 0 | 0 | 18 | 10 | 33 | 15 | 72 | 109 | 0 | 19 | 0 | 30 | 42 | 22 | 10 | 0 | 0 | 59 | 20 | 0 | 217 | 18 | 11 | 10 | 0 | 8 | 8 | 0 | 1 | 0 | 0 | 10 | 0 | 0 | 5 | 12 | 17 | 0 | 372 | 15 | 0 | 17 | 0 | 51 | 17 | 54 | 0 | 1 | 12 | 260 | 17 | 4 | 17 | 107 | 0 | 17 | 7 | 18 | 0 | 353 | 0 | 0 |  | 611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 5 | 0 | 2 | 0 | 2 | 0 | 0 | 20 | 300 | 177 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 502 | 3 | 0 | 0 | 16 |  | 4110 | 2638 | 6748 | 3100 | 611 | 1400 | 0 | 484 | 962 | 46 | 0 | 17 | 72 | 56 | 0 | 88.14
9:00 | 0 | 0 | 0 | 180 | 0 | 66 | 0 | 393 | 292 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 13 | 22 | 27 | 22 | 31 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12 | 0 | 17 | 10 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 0 | 280 | 128 | 8 | 0 | 10 | 5 | 0 | 10 | 0 | 0 | 0 | 18 | 10 | 26 | 15 | 74 | 109 | 0 | 16 | 1 | 30 | 42 | 22 | 10 | 0 | 0 | 60 | 30 | 0 | 218 | 18 | 11 | 10 | 0 | 21 | 8 | 0 | 12 | 0 | 0 | 48 | 0 | 15 | 10 | 12 | 17 | 0 | 352 | 24 | 0 | 17 | 1 | 51 | 17 | 54 | 0 | 8 | 12 | 230 | 17 | 5 | 17 | 107 | 0 | 17 | 15 | 33 | 0 | 353 | 0 | 0 |  | 610 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 8 | 0 | 15 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 338 | 17 | 0 | 33 | 0 | 34 | 0 | 1 | 35 | 290 | 178 | 0 | 0 | 1 | 44 | 17 | 0 | 0 | 502 | 8 | 0 | 0 | 38 |  | 4096 | 2750 | 6846 | 3011 | 610 | 1276 | 0 | 736 | 952 | 46 | 0 | 17 | 74 | 124 | 0 | 88.13
10:00 | 0 | 0 | 0 | 180 | 0 | 69 | 0 | 376 | 309 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 13 | 22 | 19 | 22 | 25 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12 | 0 | 17 | 10 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 0 | 280 | 121 | 8 | 0 | 10 | 5 | 0 | 10 | 0 | 0 | 0 | 19 | 10 | 22 | 15 | 76 | 109 | 0 | 16 | 1 | 30 | 42 | 22 | 10 | 0 | 0 | 40 | 30 | 0 | 206 | 18 | 11 | 10 | 0 | 21 | 8 | 0 | 15 | 0 | 0 | 24 | 0 | 17 | 14 | 12 | 17 | 0 | 345 | 24 | 0 | 17 | 2 | 51 | 17 | 54 | 0 | 0 | 12 | 200 | 40 | 6 | 17 | 107 | 0 | 17 | 21 | 35 | 0 | 319 | 0 | 0 |  | 611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 8 | 0 | 15 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 17 | 0 | 35 | 0 | 34 | 0 | 2 | 35 | 270 | 178 | 0 | 0 | 2 | 62 | 17 | 0 | 0 | 435 | 12 | 0 | 0 | 57 |  | 3984 | 2663 | 6647 | 2853 | 611 | 1264 | 0 | 736 | 865 | 46 | 0 | 17 | 76 | 179 | 0 | 88.13
11:00 | 0 | 0 | 0 | 180 | 0 | 70 | 0 | 377 | 302 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 0 | 22 | 25 | 22 | 25 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12 | 0 | 17 | 10 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 0 | 280 | 121 | 8 | 0 | 10 | 5 | 0 | 10 | 0 | 0 | 0 | 19 | 10 | 22 | 15 | 82 | 108 | 0 | 19 | 1 | 30 | 42 | 22 | 10 | 0 | 0 | 47 | 30 | 0 | 178 | 18 | 11 | 10 | 0 | 21 | 8 | 0 | 15 | 0 | 0 | 24 | 0 | 17 | 16 | 12 | 17 | 0 | 378 | 24 | 0 | 17 | 4 | 51 | 17 | 54 | 0 | 0 | 12 | 220 | 52 | 11 | 17 | 107 | 0 | 17 | 24 | 37 | 0 | 318 | 0 | 0 |  | 611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 8 | 0 | 0 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 329 | 17 | 0 | 35 | 0 | 34 | 0 | 2 | 35 | 270 | 178 | 0 | 0 | 2 | 73 | 17 | 0 | 0 | 406 | 15 | 0 | 0 | 71 |  | 4037 | 2669 | 6706 | 2880 | 611 | 1265 | 0 | 750 | 836 | 46 | 0 | 17 | 82 | 219 | 0 | 88.12
12:00 | 0 | 0 | 0 | 180 | 0 | 69 | 0 | 394 | 352 |  | 0 | 225 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 16 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 0 | 22 | 21 | 22 | 25 | 0 | 0 | 46 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 |  | 12 | 0 | 17 | 10 | 0 | 1 | 0 | 35 | 0 | 0 | 0 | 0 | 280 | 118 | 8 | 0 | 10 | 5 | 0 | 20 | 0 | 0 | 0 | 19 | 10 | 22 | 15 | 84 | 106 | 0 | 19 | 2 | 30 | 42 | 22 | 10 | 0 | 0 | 51 | 30 | 0 | 218 | 18 | 11 | 10 | 0 | 21 | 8 | 0 | 15 | 0 | 0 | 33 | 0 | 17 | 16 | 12 | 17 | 0 | 387 | 33 | 17 | 17 | 4 | 51 | 17 | 54 | 17 | 1 | 12 | 260 | 55 | 34 | 17 | 107 | 0 | 17 | 25 | 42 | 5 | 318 | 0 | 0 |  | 682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 8 | 0 | 0 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 397 | 17 | 0 | 35 | 0 | 34 | 0 | 3 | 35 | 290 | 190 | 0 | 0 | 3 | 78 | 17 | 0 | 0 | 406 | 17 | 0 | 0 | 70 |  | 4305 | 2867 | 7172 | 2998 | 682 | 1402 | 0 | 819 | 856 | 46 | 0 | 33 | 84 | 252 | 0 | 88.12
13:00 | 0 | 0 | 0 | 180 | 0 | 69 | 0 | 408 | 344 |  | 0 | 225 | 0 | 21 | 4 | 5 | 0 | 0 | 0 | 7 | 16 | 32 | 0 | 0 | 0 | 0 | 17 | 35 | 22 | 0 | 22 | 13 | 22 | 29 | 8 | 0 | 46 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 |  | 12 | 24 | 17 | 10 | 0 | 15 | 0 | 22 | 0 | 0 | 0 | 0 | 310 | 118 | 8 | 0 | 10 | 5 | 0 | 43 | 0 | 2 | 8 | 19 | 10 | 22 | 15 | 96 | 105 | 0 | 19 | 1 | 30 | 42 | 22 | 20 | 0 | 0 | 60 | 30 | 0 | 219 | 18 | 11 | 10 | 0 | 21 | 8 | 0 | 50 | 0 | 0 | 53 | 0 | 26 | 16 | 12 | 17 | 10 | 405 | 47 | 50 | 17 | 4 | 51 | 17 | 54 | 17 | 43 | 12 | 243 | 55 | 32 | 17 | 107 | 0 | 17 | 23 | 35 | 17 | 352 | 0 | 0 |  | 682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 8 | 0 | 18 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 345 | 17 | 0 | 40 | 0 | 35 | 0 | 3 | 70 | 320 | 190 | 0 | 0 | 3 | 72 | 26 | 0 | 0 | 408 | 14 | 0 | 0 | 67 |  | 4719 | 2939 | 7658 | 3115 | 682 | 1383 | 0 | 1138 | 888 | 46 | 0 | 75 | 96 | 235 | 0 | 88.11
14:00 | 0 | 0 | 0 | 180 | 0 | 69 | 0 | 351 | 287 |  | 0 | 180 | 0 | 0 | 22 | 15 | 0 | 0 | 0 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 0 | 22 | 12 | 22 | 0 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12 | 0 | 17 | 10 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 275 | 131 | 8 | 0 | 10 | 5 | 0 | 43 | 0 | 0 | 8 | 21 | 10 | 25 | 15 | 84 | 105 | 0 | 17 | 1 | 30 | 42 | 22 | 10 | 0 | 0 | 32 | 30 | 0 | 178 | 18 | 11 | 10 | 0 | 21 | 8 | 0 | 15 | 0 | 0 | 53 | 0 | 34 | 13 | 12 | 17 | 13 | 328 | 47 | 0 | 17 | 3 | 51 | 17 | 54 | 3 | 26 | 12 | 150 | 55 | 23 | 17 | 107 | 0 | 17 | 19 | 22 | 17 | 321 | 0 | 0 |  | 660 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 18 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 232 | 17 | 0 | 35 | 0 | 35 | 0 | 4 | 35 | 280 | 184 | 0 | 0 | 2 | 58 | 0 | 0 | 0 | 405 | 12 | 0 | 0 | 51 |  | 4019 | 2548 | 6567 | 2660 | 660 | 1147 | 0 | 922 | 845 | 46 | 0 | 17 | 84 | 186 | 0 | 88.12
15:00 | 0 | 0 | 0 | 180 | 0 | 69 | 0 | 332 | 300 |  | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 0 | 22 | 12 | 22 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12 | 0 | 17 | 10 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 290 | 125 | 8 | 0 | 10 | 5 | 0 | 43 | 0 | 0 | 0 | 19 | 10 | 33 | 12 | 80 | 105 | 0 | 17 | 1 | 30 | 42 | 22 | 10 | 0 | 0 | 32 | 30 | 0 | 178 | 18 | 11 | 10 | 0 | 21 | 8 | 0 | 15 | 0 | 0 | 16 | 0 | 17 | 9 | 12 | 17 | 0 | 338 | 16 | 0 | 0 | 2 | 51 | 36 | 17 | 0 | 8 | 12 | 150 | 55 | 16 | 17 | 107 | 0 | 17 | 13 | 28 | 17 | 328 | 0 | 0 |  | 660 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 157 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 231 | 0 | 0 | 0 | 0 | 35 | 0 | 2 | 0 | 260 | 183 | 0 | 0 | 1 | 37 | 0 | 0 | 0 | 409 | 8 | 0 | 0 | 29 |  | 3844 | 2372 | 6216 | 2695 | 660 | 1153 | 0 | 618 | 829 | 46 | 0 | 17 | 80 | 118 | 0 | 88.1
16:00 | 0 | 0 | 0 | 180 | 0 | 66 | 0 | 332 | 294 |  | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 35 | 0 | 22 | 12 | 22 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12 | 0 | 17 | 10 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 275 | 195 | 8 | 0 | 10 | 5 | 0 | 43 | 0 | 0 | 0 | 19 | 10 | 33 | 12 | 78 | 140 | 0 | 17 | 0 | 30 | 42 | 22 | 10 | 0 | 0 | 32 | 30 | 0 | 178 | 18 | 11 | 10 | 0 | 21 | 8 | 0 | 15 | 0 | 0 | 8 | 0 | 17 | 4 | 12 | 24 | 0 | 328 | 8 | 0 | 0 | 1 | 65 | 36 | 17 | 0 | 8 | 12 | 150 | 57 | 5 | 17 | 34 | 0 | 17 | 6 | 17 | 17 | 318 | 0 | 0 |  | 660 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 157 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 34 | 0 | 1 | 0 | 290 | 180 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 404 | 3 | 0 | 0 | 11 |  | 3791 | 2348 | 6139 | 2765 | 660 | 1150 | 0 | 522 | 854 | 46 | 0 | 17 | 78 | 47 | 0 | 88.1
17:00 | 0 | 0 | 0 | 180 | 0 | 70 | 0 | 336 | 292 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 35 | 0 | 22 | 12 | 22 | 25 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12 | 0 | 44 | 10 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 275 | 168 | 8 | 0 | 10 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 10 | 33 | 12 | 86 | 161 | 0 | 19 | 0 | 30 | 42 | 22 | 10 | 0 | 0 | 32 | 30 | 0 | 178 | 18 | 11 | 10 | 0 | 21 | 8 | 0 | 35 | 0 | 0 | 12 | 0 | 17 | 0 | 12 | 19 | 0 | 338 | 15 | 1 | 0 | 0 | 125 | 36 | 23 | 0 | 8 | 12 | 135 | 63 | 0 | 140 | 47 | 0 | 17 | 1 | 20 | 17 | 319 | 0 | 0 |  | 660 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 158 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 23 | 18 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 237 | 1 | 0 | 1 | 0 | 50 | 0 | 0 | 35 | 260 | 180 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 406 | 0 | 0 | 0 | 0 |  | 4085 | 2395 | 6480 | 2754 | 660 | 1208 | 0 | 821 | 826 | 46 | 0 | 76 | 86 | 3 | 0 | 88.09
18:00 | 0 | 0 | 0 | 180 | 0 | 70 | 0 | 337 | 283 |  | 0 | 225 | 0 | 19 | 0 | 10 | 0 | 0 | 0 | 10 | 50 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 0 | 22 | 12 | 22 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12 | 0 | 51 | 10 | 0 | 2 | 0 | 33 | 0 | 0 | 0 | 0 | 300 | 161 | 8 | 0 | 10 | 5 | 0 | 51 | 0 | 0 | 0 | 20 | 10 | 33 | 15 | 96 | 170 | 0 | 19 | 0 | 30 | 42 | 22 | 10 | 0 | 0 | 32 | 30 | 0 | 178 | 18 | 11 | 10 | 0 | 21 | 8 | 0 | 175 | 0 | 0 | 56 | 0 | 35 | 0 | 12 | 20 | 45 | 397 | 57 | 17 | 32 | 0 | 135 | 36 | 81 | 0 | 8 | 12 | 210 | 57 | 0 | 162 | 100 | 0 | 17 | 0 | 52 | 17 | 346 | 0 | 0 |  | 872 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 41 | 0 | 35 | 18 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 239 | 60 | 0 | 52 | 0 | 107 | 0 | 0 | 35 | 260 | 164 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 405 | 0 | 0 | 0 | 0 |  | 4960 | 2889 | 7849 | 2981 | 872 | 1199 | 0 | 1703 | 825 | 46 | 0 | 127 | 96 | 0 | 0 | 88.09
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 0 | 70 | 0 | 361 | 282 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 10 | 22 | 23 | 22 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12 | 0 | 51 | 10 | 1 | 19 | 0 | 28 | 0 | 0 | 0 | 0 | 275 | 161 | 8 | 0 | 10 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 10 | 33 | 15 | 96 | 216 | 0 | 19 | 0 | 30 | 42 | 22 | 10 | 0 | 0 | 32 | 30 | 0 | 178 | 19 | 11 | 10 | 0 | 22 | 8 | 0 | 95 | 0 | 0 | 56 | 0 | 35 | 0 | 12 | 72 | 105 | 418 | 57 | 17 | 34 | 0 | 141 | 36 | 90 | 0 | 8 | 12 | 220 | 54 | 0 | 162 | 107 | 0 | 17 | 0 | 52 | 21 | 318 | 0 | 0 |  | 873 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 41 | 8 | 35 | 18 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 94 | 0 | 111 | 0 | 107 | 0 | 0 | 35 | 260 | 160 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 405 | 0 | 0 | 0 | 0 |  | 5082 | 3026 | 8108 | 3053 | 873 | 1228 | 0 | 1860 | 825 | 46 | 0 | 127 | 96 | 0 | 0 | 88.07
19:30 | 0 | 0 | 0 | 180 | 0 | 70 | 0 | 404 | 281 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 35 | 10 | 22 | 23 | 22 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12 | 0 | 17 | 0 | 0 | 19 | 0 | 28 | 0 | 0 | 0 | 0 | 320 | 153 | 8 | 0 | 10 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 10 | 33 | 15 | 98 | 212 | 0 | 19 | 0 | 30 | 42 | 22 | 10 | 0 | 0 | 32 | 30 | 0 | 178 | 19 | 11 | 10 | 0 | 22 | 8 | 0 | 45 | 0 | 0 | 56 | 0 | 35 | 0 | 0 | 146 | 40 | 420 | 16 | 0 | 17 | 0 | 141 | 0 | 54 | 0 | 8 | 0 | 220 | 54 | 0 | 162 | 107 | 0 | 17 | 0 | 17 | 35 | 373 | 0 | 0 |  | 871 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 39 | 8 | 35 | 18 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 94 | 0 | 113 | 0 | 107 | 0 | 0 | 35 | 260 | 160 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 405 | 0 | 0 | 0 | 0 |  | 4880 | 3116 | 7996 | 3186 | 871 | 1317 | 0 | 1562 | 825 | 46 | 0 | 91 | 98 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 180 | 0 | 70 | 0 | 395 | 284 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 35 | 10 | 22 | 23 | 22 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12 | 0 | 0 | 0 | 0 | 19 | 0 | 42 | 0 | 0 | 0 | 0 | 300 | 170 | 8 | 0 | 10 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 10 | 33 | 15 | 100 | 212 | 0 | 19 | 0 | 30 | 42 | 22 | 10 | 0 | 0 | 32 | 30 | 0 | 178 | 19 | 11 | 10 | 0 | 22 | 8 | 0 | 45 | 0 | 0 | 56 | 0 | 35 | 0 | 0 | 140 | 40 | 420 | 16 | 0 | 17 | 0 | 135 | 0 | 60 | 0 | 8 | 0 | 260 | 55 | 0 | 162 | 107 | 0 | 17 | 0 | 17 | 35 | 336 | 0 | 0 |  | 872 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 40 | 43 | 27 | 18 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 373 | 94 | 0 | 113 | 0 | 107 | 0 | 0 | 35 | 260 | 160 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 406 | 0 | 0 | 0 | 0 |  | 4868 | 3154 | 8022 | 3177 | 872 | 1342 | 0 | 1592 | 826 | 46 | 0 | 67 | 100 | 0 | 0 | 88.08
21:00 | 0 | 0 | 0 | 180 | 0 | 70 | 0 | 403 | 320 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 35 | 10 | 22 | 23 | 22 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12 | 0 | 0 | 0 | 0 | 19 | 0 | 42 | 0 | 0 | 0 | 0 | 275 | 216 | 8 | 0 | 10 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 10 | 33 | 15 | 94 | 216 | 0 | 19 | 0 | 30 | 42 | 22 | 10 | 0 | 0 | 32 | 30 | 0 | 178 | 19 | 11 | 10 | 0 | 22 | 8 | 0 | 45 | 0 | 0 | 56 | 0 | 35 | 0 | 0 | 93 | 40 | 418 | 16 | 0 | 17 | 0 | 135 | 0 | 54 | 0 | 8 | 0 | 260 | 55 | 0 | 162 | 107 | 0 | 17 | 0 | 17 | 17 | 318 | 0 | 0 |  | 872 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 43 | 27 | 18 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 415 | 94 | 0 | 113 | 0 | 107 | 0 | 0 | 35 | 280 | 160 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 406 | 0 | 0 | 0 | 0 |  | 4803 | 3231 | 8034 | 3244 | 872 | 1421 | 0 | 1484 | 846 | 46 | 0 | 27 | 94 | 0 | 0 | 88.07
22:00 | 0 | 0 | 0 | 180 | 0 | 68 | 0 | 397 | 309 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 35 | 10 | 22 | 23 | 22 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 275 | 212 | 8 | 0 | 10 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 10 | 33 | 15 | 96 | 211 | 0 | 19 | 0 | 30 | 42 | 22 | 10 | 0 | 0 | 32 | 30 | 0 | 178 | 19 | 11 | 10 | 0 | 14 | 8 | 0 | 0 | 0 | 0 | 56 | 0 | 35 | 0 | 0 | 51 | 0 | 419 | 16 | 0 | 0 | 0 | 135 | 0 | 54 | 0 | 8 | 0 | 260 | 55 | 0 | 134 | 107 | 0 | 17 | 0 | 17 | 17 | 318 | 0 | 0 |  | 872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 94 | 0 | 70 | 0 | 34 | 0 | 0 | 35 | 340 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 0 | 0 |  | 4579 | 3035 | 7614 | 3223 | 872 | 1406 | 0 | 1066 | 905 | 46 | 0 | 0 | 96 | 0 | 0 | 88.07
23:00 | 0 | 0 | 0 | 180 | 0 | 68 | 0 | 398 | 304 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 35 | 10 | 22 | 23 | 22 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 275 | 183 | 8 | 0 | 10 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 10 | 33 | 15 | 90 | 216 | 0 | 19 | 0 | 30 | 42 | 22 | 10 | 0 | 0 | 32 | 30 | 0 | 179 | 19 | 11 | 10 | 0 | 22 | 8 | 0 | 0 | 0 | 0 | 56 | 0 | 25 | 0 | 0 | 51 | 0 | 417 | 16 | 0 | 0 | 0 | 135 | 0 | 54 | 0 | 8 | 0 | 200 | 54 | 0 | 17 | 107 | 0 | 17 | 0 | 17 | 17 | 320 | 0 | 0 |  | 776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 391 | 55 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 340 | 164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 0 | 0 |  | 4366 | 2825 | 7191 | 3132 | 776 | 1381 | 0 | 864 | 902 | 46 | 0 | 0 | 90 | 0 | 0 | 88.06
24:00 | 0 | 0 | 0 | 180 | 0 | 70 | 0 | 398 | 303 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 35 | 10 | 22 | 23 | 22 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 300 | 183 | 8 | 0 | 10 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 10 | 33 | 15 | 86 | 216 | 0 | 19 | 0 | 30 | 42 | 22 | 15 | 0 | 0 | 32 | 50 | 0 | 218 | 19 | 11 | 10 | 0 | 22 | 8 | 0 | 0 | 0 | 0 | 47 | 0 | 17 | 0 | 0 | 24 | 0 | 417 | 16 | 0 | 0 | 0 | 135 | 0 | 51 | 0 | 8 | 0 | 15 | 17 | 0 | 17 | 107 | 0 | 17 | 0 | 17 | 17 | 318 | 0 | 0 |  | 730 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 361 | 17 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 320 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 0 | 0 |  | 4147 | 2668 | 6815 | 2992 | 730 | 1371 | 0 | 708 | 882 | 46 | 0 | 0 | 86 | 0 | 0 | 88.06
KWH | 0 | 0 | 0 | 4347000 | 0 | 1505454 | 0 | 9095160 | 7228000 |  | 0 | 5226500 | 0 | 76800 | 23297 | 55000 | 0 | 0 | 0 | 26880 | 586800 | 30240 | 0 | 0 | 0 | 0 | 394920 | 450461 | 636150 | 273564 | 528000 | 520920 | 568800 | 706500 | 12000 | 0 | 1125600 | 0 | 0 | 0 | 32941 | 361629 | 0 | 0 | 0 |  | 300000 | 30432 | 404618 | 209040 | 0 | 100800 | 0 | 819360 | 0 | 0 | 0 | 0 | 7004000 | 3880000 | 200727 | 0 | 284616 | 150240 | 0 | 866432 | 0 | 9232 | 16834 | 450324 | 246240 | 754900 | 332670 | 1972800 | 3210240 | 0 | 438984 | 8300 | 716000 | 964800 | 448200 | 351792 | 0 | 0 | 931392 | 801600 | 0 | 4026660 | 440000 | 306260 | 248220 | 0 | 506856 | 192384 | 0 | 745200 | 0 | 0 | 818400 | 0 | 439776 | 102600 | 230400 | 767040 | 309454 | 9072000 | 578400 | 130800 | 340399 | 20520 | 1911927 | 469388 | 1328976 | 37620 | 255360 | 242880 | 5141300 | 956160 | 135090 | 1157760 | 2471455 | 0 | 445320 | 156866 | 632640 | 322920 | 7941300 | 0 | 0 |  | 16826909 | 0 | 0 | 0 | 63360 | 0 | 0 | 0 | 0 | 0 | 0 | 4312973 | 448000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184810 | 111298 | 127162 | 137485 | 342240 | 0 | 232074 | 0 | 0 | 3901700 | 0 | 0 | 4640336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7961345 | 703200 | 0 | 897504 | 0 | 899769 | 0 | 20466 | 568512 | 7908300 | 4375227 | 0 | 0 | 18840 | 472320 | 301632 | 0 | 0 | 10599300 | 93434 | 0 | 0 | 411120 |  | 102599520 | 66559316 | 169158836 | 72121622 | 16826909 | 31279597 | 0 | 21260147 | 22409300 | 1125600 | 0 | 723305 | 1972800 | 1439556 | 0
Fuel Cost | 0 | 0 | 0 | 6477030 | 0 | 2002253.82 | 0 | 9549918 | 7806240 |  | 0 | 5696885 | 0 | 858624 | 308685.25 | 728750 | 0 | 0 | 0 | 392985.6 | 8256276 | 490190.4 | 0 | 0 | 0 | 0 | 5023382.4 | 6081223.5 | 8530771.5 | 205173 | 396000 | 0 | 0 | 0 | 204120 | 0 | 303912 | 0 | 0 | 0 | 538585.35 | 376094.16 | 0 | 0 | 0 |  | 3915000 | 507605.76 | 6886598.36 | 2824130.4 | 0 | 1166256 | 0 | 2728468.8 | 0 | 0 | 0 | 0 | 7634360 | 4500800 | 258937.83 | 0 | 321616.08 | 223857.6 | 0 | 1446941.44 | 0 | 159436.64 | 226417.3 | 616943.88 | 184680 | 1321075 | 249502.5 | 14164704 | 3499161.6 | 0 | 597018.24 | 132302 | 980920 | 1273536 | 779868 | 608600.16 | 0 | 0 | 1806900.48 | 1827648 | 0 | 4066926.6 | 946000 | 456327.4 | 491475.6 | 0 | 380142 | 146211.84 | 0 | 10171980 | 0 | 0 | 11032032 | 0 | 6090897.6 | 1199394 | 2377728 | 10477766.4 | 4106454.58 | 8346240 | 7033344 | 1891368 | 4306047.35 | 0 | 22446022.98 | 5111635.32 | 14127014.88 | 510503.4 | 3291590.4 | 2861126.4 | 4729996 | 12382272 | 1952050.5 | 14691974.4 | 28125157.9 | 0 | 5815879.2 | 1874548.7 | 9470620.8 | 4252856.4 | 0 | 0 | 0 |  | 50480727 | 0 | 0 | 0 | 659577.6 | 0 | 0 | 0 | 0 | 0 | 0 | 4830529.76 | 869120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3060453.6 | 1882049.18 | 1733218.06 | 2319371.95 | 708436.8 | 0 | 175680.018 | 0 | 0 | 20639993 | 0 | 0 | 5382789.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7881731.55 | 9451008 | 0 | 10617472.32 | 0 | 11427066.3 | 0 | 226149.3 | 6901735.68 | 71253783 | 4462731.54 | 0 | 0 | 213080.4 | 5540313.6 | 4624018.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 330233970.7 | 225341036.978 | 555575007.678 | 68995244.918 | 50480727 | 38249523.54 | 0 | 268104029.43 | 91893776 | 303912 | 0 | 12245252.29 | 14164704 | 11137838.5 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 0 | 69 | 0 | 394 | 352 |  | 0 | 225 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 16 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 0 | 22 | 21 | 22 | 25 | 0 | 0 | 46 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 |  | 12 | 0 | 17 | 10 | 0 | 1 | 0 | 35 | 0 | 0 | 0 | 0 | 280 | 118 | 8 | 0 | 10 | 5 | 0 | 20 | 0 | 0 | 0 | 19 | 10 | 22 | 15 | 84 | 106 | 0 | 19 | 2 | 30 | 42 | 22 | 10 | 0 | 0 | 51 | 30 | 0 | 218 | 18 | 11 | 10 | 0 | 21 | 8 | 0 | 15 | 0 | 0 | 33 | 0 | 17 | 16 | 12 | 17 | 0 | 387 | 33 | 17 | 17 | 4 | 51 | 17 | 54 | 17 | 1 | 12 | 260 | 55 | 34 | 17 | 107 | 0 | 17 | 25 | 42 | 5 | 318 | 0 | 0 |  | 682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 8 | 0 | 0 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 397 | 17 | 0 | 35 | 0 | 34 | 0 | 3 | 35 | 290 | 190 | 0 | 0 | 3 | 78 | 17 | 0 | 0 | 406 | 17 | 0 | 0 | 70 |  | 7172 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 0 | 70 | 0 | 361 | 282 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 10 | 22 | 23 | 22 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 51 | 10 | 1 | 19 | 0 | 28 | 0 | 0 | 0 | 0 | 275 | 161 | 8 | 0 | 10 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 10 | 33 | 15 | 96 | 216 | 0 | 19 | 0 | 30 | 42 | 22 | 10 | 0 | 0 | 32 | 30 | 0 | 178 | 19 | 11 | 10 | 0 | 22 | 8 | 0 | 95 | 0 | 0 | 56 | 0 | 35 | 0 | 12 | 72 | 105 | 418 | 57 | 17 | 34 | 0 | 141 | 36 | 90 | 0 | 8 | 12 | 220 | 54 | 0 | 162 | 107 | 0 | 17 | 0 | 52 | 21 | 318 | 0 | 0 |  | 873 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 41 | 8 | 35 | 18 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 94 | 0 | 111 | 0 | 107 | 0 | 0 | 35 | 260 | 160 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 405 | 0 | 0 | 0 | 0 |  | 8108 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 0 | 70 | 0 | 400 | 350 | 0 | 0 | 225 | 0 | 50 | 34 | 15 | 0 | 0 | 0 | 85 | 50 | 32 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 22 | 27 | 25 | 33 | 50 | 0 | 46 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 12 | 33 | 50 | 10 | 0 | 20 | 0 | 15 | 0 | 0 | 0 | 0 | 320 | 220 | 8 | 0 | 10 | 5 | 0 | 51 | 0 | 40 | 8 | 21 | 10 | 33 | 15 | 153 | 150 | 0 | 19 | 0 | 30 | 42 | 22 | 20 | 0 | 0 | 30 | 86 | 0 | 218 | 19 | 11 | 10 | 0 | 22 | 8 | 100 | 195 | 150 | 50 | 57 | 50 | 35 | 0 | 12 | 200 | 108 | 400 | 59 | 105 | 51 | 0 | 300 | 36 | 92 | 17 | 113 | 12 | 260 | 55 | 0 | 162 | 107 | 0 | 17 |  | 52 | 18 | 353 |  |  |  | 952 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 45 | 85 | 40 | 187 | 25 |  | 0 | 0 | 0 | 32 | 25 | 90 | 0 | 50 | 40 | 8 | 35 | 15 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 210 |  | 0 | 0 | 0 | 50 | 0 | 0 | 410 | 94 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 350 | 220 |  | 35 |  |  | 113 | 0 |  | 500 |  | 0 | 0
Forecast for Day | 0 | 0 | 0 | 180 | 0 | 70 | 0 | 400 | 350 | 0 | 0 | 225 | 0 | 35 | 34 | 15 | 0 | 0 | 0 | 50 | 94 | 32 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 22 | 22 | 27 | 22 | 33 | 50 | 0 | 46 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 12 | 22 | 17 | 10 | 0 | 20 | 0 | 7 | 0 | 0 | 0 | 0 | 310 | 200 | 8 | 0 | 10 | 5 | 0 | 51 | 0 | 20 | 8 | 21 | 10 | 33 | 15 | 135 | 109 | 0 | 19 | 1.6 | 30 | 42 | 22 | 20 | 0 | 0 | 30 | 50 | 0 | 218 | 19 | 11 | 10 | 0 | 22 | 8 | 0 | 65 |  | 0 | 50 | 0 | 35 | 20 | 12 | 34 | 15 | 400 | 47 | 70 | 20 | 5 | 50 | 17 | 54 | 17 | 65 | 12 | 260 | 55 | 50 | 17 | 107 | 0 | 17 | 30 | 34 | 18 | 353 |  |  |  | 952 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 8 | 0 | 15 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 15 | 0 | 35 | 0 | 34 | 0 | 8 | 35 | 330 | 220 |  | 0 | 6 | 100 | 35 | 0 |  | 500 | 30 | 0 | 0 | [5 empty] | g | h | o | c | h | t | s
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 0 | 69 | 0 | 396 | 290 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 10 | 22 | 24 | 20 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 10 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 330 | 190 | 8 | 0 | 10 | 5 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 33 | 12 | 82 | 220 | 0 | 19 | 0 | 30 | 42 | 22 | 20 | 0 | 0 | 30 | 50 | 0 | 218 | 18 | 11 | 10 | 0 | 16 | 8 | 0 | 15 | 0 | 0 | 47 | 0 | 0 | 7 | 12 | 17 | 3 | 364 | 47 | 6 | 7 | 1 | 51 | 17 | 17 | 0 | 10 | 12 | 50 | 17 | 7 | 17 | 107 | 0 | 17 | 4 | 36 | 0 | 357 | 0 | 0 | 0 | 612 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 158 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 8 | 0 | 15 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 425 | 9 | 0 | 15 | 0 | 5 | 0 | 0 | 35 | 300 | 162 | 0 | 0 | 0 | 16 | 17 | 0 | 0 | 407 | 3 | 0 | 0 |  | 0 |  |  |  | 103.4012 | 16.8269 | 21.9835 | 22.4093 | 1.1256 | 1.9728 | 1.4396
169.1588
| Minimum Generation |  | 6158 | 5:00
| Highest Generation |  | 8108 | 19:00
| Day Peak Generation |  | 7172 | 12:00
| Evening Peak Generation |  | 8108 | 19:00
| HVDC Max Flow |  | 873 | 19:00
| HVDC EvPeak Flow |  | 873 | 19:00
| Load factor L.F |  | 86.93% | [161 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2022-12-17
Till now the maximum generation is : - |  |  |  | 14782 | 21:00 | Hrs on | 2022-04-16
The Summary of Yesterday's |  |  | 2022-12-16 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 7172 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 5506
Evening Peak Generation : |  |  | 8108 | MW Hour : | 19:00 | Available Max Generation : |  | 10962
E.P. Demand (at gen end) : |  |  | 8108 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 9900
Maximum Generation : |  |  | 8108 | MW Hour : | 19:00 | Reserve(Generation end) |  | 1062
Total Gen. (MKWH) : |  |  | 169.1588 | System Load Factor : | 86.93% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 664 | MW at | 6:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2022-12-17
Actual : |  | 88.03 | Ft.(MSL) , | Rule curve : | 104.5 | Ft.( MSL )
Gas Consumed : |  | Total = | 768.17 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 107244768.458
: |  |  | Coal : | 91893776 | Oil : | 280349281.72 | Total : | 479487826.178
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 0 | 0:00 | 3362.0451 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 952.4089 |  |  | 0 | 0%
Khulna Area |  | 0 | 0:00 | 1257.1007 |  |  | 0 | 0%
Rajshahi Area |  | 0 | 0:00 | 1115.3614 |  |  | 0 | 0%
Cumilla Area |  | 0 | 0:00 | 949.4759 |  |  | 0 | 0%
Mymensingh Area |  | 0 | 0:00 | 784.409 |  |  | 0 | 0%
Sylhet Area |  | 0 | 0:00 | 350.5967 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 285.7977 |  |  | 0 | 0%
Rangpur Area |  | 0 | 0:00 | 619.3421 |  |  | 0 | 0%
Total |  | 0 |  | 9676.5375 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1, 2
2) Ghorasal-3, 4, 7
3) Ashuganj-5
4) Baghabari-100 MW
5) Raozan unit-1 & 2
6) Siddhirganj 210 MW .
7) Shajibazar 330 MW
8) Sirajganj-2
9) Bibiana-II 341 MW CCPP (Summit)
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
9:06 | 9:27 | Baroirhat-Feni 132 kV Ckt-2 Tripped from Baroirhat 132/33kV end showing Distance relay.
12:21 | 17:50 | Moghbazar-Rampura 132kV Ckt-2 Tripped from Rampura 230/132kV end showing Distance Protection - 21/1 Z2 ABN Master trip - 86 T1
relays Due to Unknown.
12:57 | 17:50 | Moghbazar-Rampura 132kV Ckt-2 Forced S/D from Rampura 230/132kV end Due to Work in Moghbazar 132 kv S/S , According to NLDC
instruction.
- | 13:35 | Natore 132/33kV S/S TR-3 (425 T) HT is restored.
7:13 | - | Mymensingh 132/33kV S/S Transformer-2 (414T) HT Scheduled S/D Due to Annual Maintenance work. | [5 empty] | 40.0MW load interrup.
7:20 | - | Mymensingh 132/33kV S/S T-2 Bus Scheduled S/D Due to Annual Maintenance work. | [5 empty] | 40.0MW load interrup.
7:22 | - | Kallyanpur-Lalbag 132kV Ckt-2 Scheduled S/D from Kallyanpur 132/33kV end Due to dead line checking.
7:39 | - | Kaliakoir 400/230/132kV S/S 400kV Bus 2 Scheduled S/D Due to annual maintenance.
7:40 | - | Feni 132/33kV S/S T-1(405T) HT Forced S/D Due to 33KV Bus isolator & Red hot maintenance by bpdb. | [5 empty] | 30.0MW load interrup.
7:40 | - | Feni 132/33kV S/S T-1(405T) LT Forced S/D Due to 33KV Bus isolator & Red hot maintenance by bpdb. | [5 empty] | 30.0MW load interrup.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2022-12-16 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Line O/L
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4347000
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 70 | 1505454 | Machine problem
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 361 | 9095160 | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 282 | 7228000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 5226500 | GT-2 S/D due to Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 0 | 76800 | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 0 | 23297 | Line O/L
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 0 | 55000 | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 10 | 273564 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 0 | 26880 | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 50 | 586800 | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 394920
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 0 | 30240 | Fuel shortage
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 450461 | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 636150 | Fuel shortage
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 45 | 1048920 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 22 | 568800 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 706500 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 0 | 12000 | reserve.
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 95 | 745200 | Fuel shortage
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Fuel conservation
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 0 | 0 | Fuel conservation
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Fuel conservation
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 35 | 439776 | Fuel shortage
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 17 | 130800 | Low demand
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 54 | 956160 | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 1157760
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 156866
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 21 | 322920 | Fuel shortage
| Dhaka area Total |  |  |  | 5847 | 1826 | 36201928
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Machine problem
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 0 | 32941
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 102600
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 100800 | Engine problem
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 46 | 1125600 | Low water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 361629 | ST Under maint
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 34 | 340399 | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 30432 | Fuel shortage
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 404618 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 10 | 209040 | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 12 | 230400 | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 0 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 28 | 819360
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 1 | 0 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 20520
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 141 | 1911927 | Fuel shortage
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 36 | 469388 | Engine problem
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 90 | 1328976 | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 242880 | reserve.
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 107 | 2471455
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Chattogram area Total |  |  |  | 2382 | 587 | 10202965
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 161 | 3880000 | FGMO
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 0 | 0 | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 275 | 7004000 | FGMO
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 318 | 7941300 | FGMO
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 10 | 284616 | Gas shortage
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 5 | 150240 | Gas shortage
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 200727 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 866432 | Gas shortage
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 105 | 309454 | Fuel shortage
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 9232 | Engine problem
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Machine problem
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 72 | 767040 | Fuel shortage
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 450324
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 10 | 246240
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 96 | 1972800
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 754900 | Engine problem
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 16834 | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 15 | 332670 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Fuel conservation
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 37620 | Fuel shortage
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 8 | 255360 | Low demand
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 445320 | Engine problem
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 52 | 632640 | Fuel shortage
| Cumilla Area Total |  |  |  | 3285 | 1257 | 26557749
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 216 | 3210240 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 438984 | Gas shortage
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 8300
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 56 | 818400 | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 57 | 578400 | Fuel shortage
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 135090
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 300000 | Engine problem
| Mymensingh Area Total |  |  |  | 614 | 360 | 5489414
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 30 | 716000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 42 | 964800 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Gas shortage
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 22 | 448200 | Gas shortage
| Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 10 | 351792 | Gas shortage
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 8 | 192384 | Engine problem
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 32 | 931392 | GT-9 S/D due to maintenance work.
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 30 | 801600 | Gas shortage
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 178 | 4026660 | Gas shortage
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 19 | 440000
| Sylhet 50MW PP (EPL) |  | NENP | 27*2 | 50 | 11 | 306260 | Gas shortage
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 22 | 506856
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 0 | 0 | Under maint.
104 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 418 | 9072000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 248220
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 220 | 5141300 | ST Under maint
| Sylhet Area Total |  |  |  | 2477 | 1052 | 24147464
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Fuel shortage
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 873 | 16826909
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 16 | 63360 | Fuel shortage
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Line O/L
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Line O/L
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Under maint.
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 0 | 0 | Fuel shortage
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Fuel conservation
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 94 | 703200 | Fuel shortage
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Fuel shortage
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 472320
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 0 | 0 | 0 | On test.
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 0 | 0 | 405 | 10599300 | On test.
| Khulna Area Total |  |  |  | 2384 | 1388 | 28665089
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Line O/L
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 22 | 448000 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 184 | 4312973
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 260 | 7908300 | Line O/L & Unit-1 Under maint.
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 160 | 4375227
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Line O/L
| Barisal 307 MW |  | BCPCL | 0 | 0 | 0 | 0 | On test.
| Barisal Area Total |  |  |  | 1958 | 626 | 17044500
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Low demand
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Low demand
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contract Expired
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 16 | 184810
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 41 | 111298 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 160 | 4640336 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 276 | 7961345 | FGMO
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 35 | 137485 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 18 | 342240 | Gas shortage
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 232074
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 8 | 127162 | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Line O/L
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Fuel conservation
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 111 | 897504
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 35 | 568512 | Low demand
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 18840
| Adani Power Jharkhanda Ltd |  | Import | 0 | 0 | 0 | 0 | On test.
| Rajshahi Area Total |  |  |  | 2129 | 711 | 15221606
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 160 | 3901700 | Machine problem
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 107 | 899769 | Engine problem
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 20466
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 34 | 301632 | Low demand
| Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 93434
| Teesta Solar Limited |  | BPCL | 16*12.5 | 0 | 0 | 411120
| Rangpur Area Total |  |  |  | 750 | 301 | 5628121
| Total |  |  |  | 21826 | 8108 | 169158836
| Eastern Grid Total |  |  |  | 14605 | 5082 | 102599520
| Western Grid Total |  |  |  | 7221 | 3026 | 66559316
| National Grid Total |  |  |  | 21826 | 8108 | 169158836
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2022-12-16
| (a) ENTIRE EASTERN GRID : |  | 5020.53 | MW | (b) ENTIRE WESTERN GRID : |  | 2613.19 | MW
| i) Dhaka area |  | 2520.53 | MW | i) Khulna area |  | 986.8 | MW
| ii) Chittagong area |  | 854 | MW | ii) Rajshahi area |  | 837.4 | MW
| iii) Comilla area |  | 646 | MW | iii) Barisal area |  | 216.99 | MW
| iv) Mymensingh area |  | 674 | MW | iv) Rangpur area |  | 572 | MW
| v) Sylhet area |  | 326 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 7633.72 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 8 | 08:00 | Chhatak | 13 | 18:00 | Kamrangirchar | 46 | 00:00 | Natore | 79 | 18:00 | Shitalakhya | 70 | 00:00
2 | AKSML | 84 | 23:00 | Chowmuhani | 119 | 19:00 | Kaptai | 3.2 | 18:00 | Nawabganj | 26.2 | 21:00 | Sholosohor | 17 | 13:00
3 | Aftabnagar | 20 | 12:00 | Chuadanga | 64 | 18:00 | Kazla | 66 | 19:30 | Netrakona | 82 | 18:00 | Shyampur | 140 | 00:00
4 | Agargaon | 47 | 13:00 | Coxsbazar | 78 | 13:00 | Keranigonj | 30 | 00:00 | New | 36 | 00:00 | Siddhirganj | 66 | 00:00
5 | Agrabad | 36 | 18:30 | Cumilla(N) | 85 | 19:30 | Khagrachori | 22 | 18:00 | Niamatpur | 48 | 18:00 | Sirajganj | 56 | 18:30
6 | Amnura | 33 | 07:00 | Cumilla(S) | 100 | 20:00 | Khulna | 62 | 13:00 | Noapara | 34 | 18:00 | Sonargaon | 79 | 00:00
7 | Ashuganj | 41 | 00:00 | Daudkandi | 82 | 19:30 | Khulshi | 119 | 23:00 | PHP | 3 | 16:00 | Sreemongol | 35 | 19:00
8 | BIPTC | N/A | N/A | Dhaka | 14 | 13:00 | Kishoreganj | 92 | 19:00 | Pabna | 65 | 18:00 | Srinagar | 28.85 | 13:00
9 | BSRM | 155 | 05:00 | Dhamrai | 60 | 00:00 | Kodda | 152 | 00:00 | Palashbari | 84 | 18:00 | Sunamganj | 31 | 18:30
10 | Bagerhat | 71 | 18:00 | Dhanmondi | 63 | 13:00 | Kulaura | 24 | 18:00 | Panchagarh | 50 | 18:00 | Sylhet | 91 | 21:00
11 | Bakulia | 61 | 18:00 | Dohazari | 68 | 19:00 | Kurigram | 50 | 18:00 | Patuakhali | 78 | 21:00 | TK | N/A | N/A
12 | Banani | 18 | 13:00 | Faridpur | 88 | 20:00 | Kushtia | 73 | 18:00 | Payra | 1.01 | 20:00 | Tangail | 124 | 18:00
13 | Bangabhaban | 2 | 00:00 | Fatullah | 42 | 00:00 | Lalbag | 54 | 00:00 | Postogola | 24 | 13:00 | Thakurgaon | 60 | 18:00
14 | Barapukuria | 36 | 18:00 | Fenchuganj | 27 | 19:00 | Lalmonirhat | 26 | 18:00 | Purbachal | 11 | 13:00 | Tongi | 70 | 00:00
15 | Barguna | 12 | 19:30 | Feni | 72 | 18:00 | Madanganj | 24 | 00:00 | Purbasadipur | 89 | 11:00 | Ullon | 29 | 13:00
16 | Barishal | 58 | 13:00 | GPH | 86 | 06:00 | Madaripur | 58 | 19:30 | Rahanpur_I | 19.2 | 17:00 | Uttara | 50 | 13:00
17 | Barishal-230 | 48 | 19:00 | Ghorashal | 46 | 00:00 | Madartek | 51 | 13:00 | Rahim | 20 | 00:00 | UttaraNew | 10 | 12:00
18 | Baroaulia | 50 | 00:00 | Goalpara | 20 | 13:00 | Madunaghat | 35 | 19:00 | Rajbari | 42 | 18:00 | Zigatola | 30 | 13:00
19 | Baroirhat | 30 | 18:00 | Gollamari | 32 | 13:00 | Magura | 38 | 18:00 | Rajendrapur | 68 | 00:00
20 | Bashundhara | 92 | 13:00 | Gopalganj | 66 | 19:30 | Mahasthangarh | 40 | 18:00 | Rajshahi | 87 | 19:30
21 | BashundharaCement | 1 | 00:00 | Gulshan | 50 | 12:00 | Manikganj | 45 | 00:00 | Rajshahi-230 | 19 | 18:30
22 | Beanibazar | 36 | 18:00 | Halishahar | 47.5 | 20:00 | Maniknagar | 39 | 13:00 | Ramganj | 64 | 13:00
23 | Benapole | 32 | 18:00 | HaripurSBU | 136 | 00:00 | Matarbari | 26 | 18:00 | Rampur | 16 | 00:00
24 | Bhaluka | 90 | 00:00 | Hasnabad | 56 | 13:00 | Matuail | 40 | 00:00 | Rangamati | 10 | 18:00
25 | Bhandaria | 33 | 21:00 | Hathazari | 38 | 18:30 | Millgate | 38 | 00:00 | Rangpur | 93 | 13:00
26 | Bhangura | 20 | 18:00 | Ishurdi | 45 | 18:30 | Mirpur | 76.5 | 13:00 | Ruppur | 2.4 | 00:00
27 | Bheramara(GK) | 34 | 18:00 | Jaldhaka | 44 | 18:00 | Mirsorai | 2.5 | 18:00 | SSM | 0 | 00:00
28 | Bhulta | 187 | 00:00 | Jamalpur | 99 | 18:30 | Mithapukur | 24 | 08:00 | Saidpur | 67 | 18:00
29 | Bog-Sherpur | 42 | 18:00 | Jashore | 84 | 18:30 | Modern | 0 | 00:00 | Satkhira | 74 | 18:30
30 | Bogura | 96 | 19:00 | Jhenaidah | 82 | 18:00 | Mogbazar | 69 | 21:00 | Satmasjid | 67 | 13:00
31 | Borhanuddin | 0 | 00:00 | Joydebpur | 78 | 00:00 | Mongla | 24 | 00:00 | Savar | 82 | 00:00
32 | Brahmanbaria | 94 | 20:00 | Joypurhat | 38 | 18:00 | Motijheel | 18 | 12:00 | Shahjadpur | 66 | 18:00
33 | Cantonment | 85 | 13:00 | Juldah | 18 | 00:00 | Munshiganj | 60 | 18:00 | Shahjibazar | 74 | 18:00
34 | Chandpur | 37 | 19:30 | KSRM | 31 | 00:00 | Mymensingh | 138 | 13:00 | Shahmirpur | 32.5 | 01:00
35 | Chandraghona | 22 | 18:30 | Kabirpur | 133 | 00:00 | Naogaon | 77 | 20:00 | Shariatpur | 46 | 21:00
36 | Chapai | 44 | 12:00 | Kachua | 42 | 18:00 | Narail | 29 | 18:00 | Sherpur | 90 | 20:00
37 | Charsaidpur | 37.71 | 02:00 | Kallyanpur | 58 | 13:00 | Narinda | 31 | 12:00 | Shikalbaha | 23 | 00:00
38 | Chauddagram | 27 | 13:00 | Kalurghat | 4 | 00:00 | Narshingdi | 121 | 20:00 | Shikalbaha-230 | N/A | N/A
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2022-12-16 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Bhulta | 393 | 18:30 | 383 | 00:00 | Gopalganj_I | 425 | 19:00 | 417 | 02:00
| Bibiana | 407 | 17:00 | 394 | 01:00 | Kaliakoir | 405 | 13:00 | 305 | 17:00
| BIPTC | 409 | 03:00 | 394 | 11:00 | Payra | 424 | 17:00 | 418 | 15:00
| Gopalganj | N/A | N/A | N/A | N/A | Rahanpur_I | 414 | 21:00 | 388 | 07:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 241 | 19:00 | 231 | 00:00 | Hasnabad | 238 | 18:30 | 230 | 00:00
| AKSML | 243 | 19:00 | 228 | 22:00 | Hathazari | 241 | 19:00 | 226 | 12:00
| Aminbazar | 242 | 19:00 | 232 | 00:00 | Ishurdi | 242 | 19:00 | 232 | 08:00
| Ashuganj | 245 | 17:00 | 237 | 00:00 | Jhenaidah | 242 | 21:00 | 231 | 08:00
| Baghabari | 238 | 20:00 | 233 | 07:00 | Kaliakoir | 237 | 13:00 | 230 | 02:00
| Barapukuria | 232 | 13:00 | 224 | 01:00 | Keranigonj | 239 | 19:00 | 229 | 00:00
| Barishal | 248 | 17:00 | 242 | 02:00 | Khulna(S) | 243 | 21:00 | 234 | 08:00
| Bheramara | 239 | 19:00 | 230 | 08:00 | Maniknagar | 238 | 19:00 | 224 | 08:00
| Bhulta | 238 | 17:00 | 230 | 00:00 | Meghnaghat | 241 | 17:00 | 233 | 07:00
| Bibiana | 242 | 17:00 | 234 | 00:00 | Mirsorai | 239 | 19:00 | 225 | 16:00
| BIPTC | 242 | 19:00 | 230 | 08:00 | Rajshahi | 244 | 13:00 | 235 | 09:00
| Bogura | 237 | 13:00 | 229 | 08:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 250 | 02:00 | 248 | 00:00 | Rampura | 236 | 17:00 | 230 | 00:00
| BSRM | 240 | 17:00 | 225 | 12:00 | Shikalbaha | 245 | 19:00 | 226 | 16:00
| Cumilla(N) | 237 | 17:00 | 230 | 11:00 | Shyampur | 239 | 19:00 | 229 | 00:00
| Fenchuganj | 244 | 17:00 | 237 | 00:00 | Siddhirganj | 238 | 17:00 | 232 | 01:00
| Ghorashal | N/A | N/A | N/A | N/A | Sirajgonj | 267 | 01:00 | 230 | 15:00
| GPH | 242 | 17:00 | 225 | 12:00 | Tongi | 238 | 18:00 | 227 | 01:00
| Haripur | 236 | 19:00 | 228 | 00:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 137 | 17:00 | 133 | 00:00 | Kushtia | 140 | 21:00 | 134 | 08:00
| Agargaon | 140 | 17:00 | 134 | 12:00 | Lalbag | 140 | 17:00 | 134 | 22:00
| Agrabad | 141 | 19:00 | 130 | 11:00 | Lalmonirhat | 135 | 13:00 | 127 | 07:00
| AKS | 143 | 17:00 | 131 | 11:00 | Madanganj | 139 | 18:00 | 131 | 00:00
| Aminbazar | 141 | 18:30 | 133 | 00:00 | Madaripur | 138 | 05:00 | 136 | 00:00
| Amnura | 133 | 19:30 | 127 | 07:00 | Madartek | 137 | 17:00 | 133 | 00:00
| Ashuganj | 140 | 14:00 | 137 | 00:00 | Madunaghat | 142 | 19:00 | 131 | 07:00
| Bagerhat | 138 | 21:00 | 130 | 07:00 | Magura | 138 | 01:00 | 134 | 08:00
| Bakulia | 141 | 17:00 | 131 | 00:00 | Mahasthangarh | 139 | 13:00 | 132 | 07:00
| Banani | 145 | 17:00 | 137 | 01:00 | Manikganj | 135 | 13:00 | 128 | 00:00
| Bangabhaban | 138 | 19:00 | 132 | 00:00 | Maniknagar | 137 | 17:00 | 132 | 00:00
| Barapukuria | 137 | 13:00 | 132 | 00:00 | Matarbari | 136 | 17:00 | 125 | 12:00
| Barguna | 138 | 05:00 | 134 | 00:00 | Matuail | 139 | 17:00 | 133.8 | 00:00
| Barishal | 142 | 17:00 | 132 | 00:00 | Millgate | 142 | 17:00 | 136 | 00:00
| Barishal-230 | 142 | 17:00 | 137 | 02:00 | Mirpur | 139 | 19:00 | 132 | 00:00
| Baroaulia | 143 | 19:00 | 134 | 02:00 | Mithapukur | 137 | 13:00 | 132 | 02:00
| Baroirhat | 139 | 14:00 | 132 | 12:00 | Modern | 141 | 19:00 | 134 | 00:00
| Bashundhara | 145 | 19:00 | 137 | 00:00 | Mogbazar | 137 | 13:00 | 134 | 00:00
| BashundharaCement | 139 | 18:00 | 131 | 00:00 | Mongla | 137 | 19:00 | 130 | 08:00
| Beanibazar | 135 | 03:00 | 134 | 00:00 | Motijheel | 138 | 19:00 | 132 | 00:00
| Benapole | 137 | 21:00 | 131 | 07:00 | Munshiganj | 140 | 19:00 | 133 | 00:00
| Bhaluka | 136 | 13:00 | 126 | 02:00 | Mymensingh | 139 | 14:00 | 120 | 12:00
| Bhandaria | 142 | 05:00 | 139 | 00:00 | Naogaon | 139 | 13:00 | 131 | 07:00
| Bhangura | 142 | 19:30 | 138 | 07:00 | Narail | 138 | 19:00 | 132 | 08:00
| Bheramara | 138 | 19:00 | 133 | 07:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bheramara(GK) | 139 | 17:00 | 134 | 09:00 | Narshingdi | 138 | 17:00 | 130 | 00:00
| Bhulta | 133 | 17:00 | 127 | 00:00 | Natore | 138 | 21:00 | 132 | 07:00
| Bog-Sherpur | 141 | 13:00 | 133 | 07:00 | Nawabganj | 140 | 17:00 | 134 | 22:00
| Bogura | 141 | 21:00 | 134 | 08:00 | Netrakona | 137 | 12:00 | 130 | 03:00
| Bogura-230 | 141 | 13:00 | 134 | 08:00 | New | 144 | 19:00 | 138 | 00:00
| Brahmanbaria | 135 | 13:00 | 132 | 11:00 | Niamatpur | 138 | 13:00 | 130 | 16:00
| Cantonment | 139 | 19:00 | 133 | 12:00 | Noapara | 137 | 21:00 | 131 | 08:00
| Chandpur | 142 | 19:00 | 134 | 01:00 | Pabna | 140 | 19:00 | 134 | 08:00
| Chandraghona | 141 | 13:00 | 133 | 11:00 | Palashbari | 137 | 13:00 | 129 | 08:00
| Chapai | 136 | 13:00 | 129 | 08:00 | Panchagarh | 134 | 13:00 | 125 | 18:00
| Charsaidpur | 140 | 18:00 | 133 | 00:00 | Patuakhali | 137 | 16:00 | 134 | 12:00
| Chauddagram | 140 | 13:00 | 134 | 22:00 | Payra | 139 | 01:00 | 137 | 12:00
| Chhatak | 134 | 04:00 | 133 | 00:00 | PHP | 140 | 14:00 | 132 | 12:00
| Chowmuhani | 137 | 19:00 | 121 | 22:00 | Postogola | 143 | 19:00 | 136 | 00:00
| Chuadanga | 137 | 17:00 | 131 | 08:00 | Purbachal | 146 | 17:00 | 136 | 07:00
| Coxsbazar | 133 | 19:00 | 126 | 19:30 | Purbasadipur | 133 | 17:00 | 125 | 07:00
| Cumilla(N) | 141 | 13:00 | 136 | 00:00 | Rahim | 140 | 18:00 | 134 | 00:00
| Cumilla(S) | 141 | 17:00 | 130 | 10:00 | Rajbari | 137 | 19:00 | 132 | 08:00
| Daudkandi | 140 | 17:00 | 134 | 00:00 | Rajendrapur | 136 | 14:00 | 128 | 03:00
| Dhaka | 138 | 19:00 | 133 | 00:00 | Rajshahi | 135 | 13:00 | 127 | 15:00
| Dhamrai | 139 | 17:00 | 132 | 00:00 | Rajshahi-230 | 134 | 19:00 | 128 | 09:00
| Dhanmondi | 140 | 19:00 | 134 | 00:00 | Ramganj | 140 | 08:00 | 132 | 00:00
| Dohazari | 140 | 05:00 | 129 | 11:00 | Rampur | 138 | 06:00 | 133 | 00:00
| Faridpur | 136 | 19:00 | 132 | 00:00 | Rampura | 136 | 17:00 | 133 | 00:00
| Fatullah | 139 | 19:00 | 133 | 00:00 | Rangamati | 142 | 17:00 | 133 | 12:00
| Fenchuganj | 138 | 14:00 | 135 | 20:00 | Rangpur | 136 | 13:00 | 130 | 08:00
| Feni | 140 | 13:00 | 134 | 12:00 | Ruppur | 140 | 13:00 | 135 | 01:00
| Ghorashal | 143 | 18:00 | 137 | 00:00 | Saidpur | 136 | 13:00 | 127 | 22:00
| Goalpara | 138 | 18:30 | 130 | 08:00 | Satkhira | 136 | 21:00 | 130 | 07:00
| Gollamari | 137 | 19:00 | 132 | 09:00 | Satmasjid | 139 | 17:00 | 134 | 12:00
| Gopalganj | 138 | 19:00 | 133 | 07:00 | Savar | 141 | 19:00 | 132 | 11:00
| Gopalganj-400 | N/A | N/A | N/A | N/A | Shahjadpur | 145 | 05:00 | 140 | 07:00
| Gopalganj_I | 139 | 13:00 | 135 | 03:00 | Shahjibazar | 138 | 17:00 | 135 | 00:00
| Gulshan | 137 | 19:00 | 133 | 00:00 | Shahmirpur | 139 | 17:00 | 128 | 03:00
| Halishahar | 141 | 19:00 | 132 | 12:00 | Shariatpur | 139 | 01:00 | 135 | 00:00
| Haripur | 140 | 18:00 | 134 | 00:00 | Sherpur | 138 | 19:00 | 126 | 03:00
| HaripurSBU | 140 | 18:00 | 133 | 01:00 | Shikalbaha | 142 | 17:00 | 134 | 00:00
| Hasnabad | 141 | 15:00 | 137 | 11:00 | Shikalbaha-230 | 142 | 19:00 | 133 | 12:00
| Hathazari | 142 | 17:00 | 134 | 12:00 | Shitalakhya | 141 | 18:00 | 135 | 00:00
| Ishurdi | 140 | 19:00 | 134 | 09:00 | Sholosohor | 142 | 17:00 | 132 | 12:00
| Jaldhaka | 134 | 17:00 | 126 | 07:00 | Shyampur | 136 | 18:30 | 114 | 17:00
| Jamalpur | 140 | 19:00 | 126 | 08:00 | Shyampur-230 | 138 | 17:00 | 138 | 18:30
| Jashore | 137 | 21:00 | 130 | 08:00 | Siddhirganj | 139 | 17:00 | 134 | 00:00
| Jhenaidah | 140 | 21:00 | 133 | 08:00 | Sirajganj | 141 | 21:00 | 136 | 11:00
| Jhenaidah-230 | 140 | 21:00 | 133 | 08:00 | Sonargaon | 136 | 18:00 | 131 | 00:00
| Joydebpur | 143 | 13:00 | 137 | 00:00 | Sreemongol | 140 | 19:00 | 136 | 08:00
| Joypurhat | 138 | 19:00 | 131 | 15:00 | Srinagar | 140 | 17:00 | 134 | 00:00
| Juldah | 137 | 17:00 | 131 | 10:00 | SSM | 145 | 19:00 | 136 | 13:00
| Kabirpur | 142 | 17:00 | 129 | 00:00 | Sunamganj | 133 | 00:00 | 132 | 08:00
| Kachua | 140 | 13:00 | 133 | 23:00 | Sylhet | 135 | 09:00 | 134 | 00:00
| Kaliakoir | 135 | 14:00 | 131 | 02:00 | Tangail | 136 | 13:00 | 131 | 01:00
| Kallyanpur | 139 | 17:00 | 133 | 00:00 | Thakurgaon | 136 | 13:00 | 124 | 22:00
| Kalurghat | 142 | 17:00 | 133 | 12:00 | TK | N/A | N/A | N/A | N/A
| Kamrangirchar | 140 | 17:00 | 135 | 20:00 | Tongi | 145 | 17:00 | 135 | 01:00
| Kaptai | 138 | 00:00 | 128 | 06:00 | Ullon | 137 | 19:00 | 133 | 00:00
| Kazla | 137 | 18:00 | 132 | 00:00 | Uttara | 139 | 19:00 | 133 | 00:00
| Keranigonj | 140 | 17:00 | 133 | 22:00 | UttaraNew | 140 | 19:00 | 132 | 00:00
| Khagrachori | 139 | 06:00 | 133 | 12:00 | Zigatola | 140 | 18:00 | 134 | 23:00
| Khulna | 137 | 17:00 | 132 | 07:00
| Khulna(S) | 138 | 21:00 | 131 | 08:00
| Khulshi | 141 | 19:00 | 131 | 12:00
| Kishoreganj | 133 | 05:00 | 128 | 22:00
| Kodda | 142 | 13:00 | 127 | 02:00
| KSRM | 143 | 19:00 | 131 | 02:00
| Kulaura | 137 | 09:00 | 135 | 00:00
| Kurigram | 133 | 11:00 | 128 | 22:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2022-12-16
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 1302 | 4147 | 2668 | 6815 |  |  |  | QF-LDC-11
0:30 | 1171 | 4292 | 2703.5 | 6995.5 | Date: | 2022-12-16
1:00 | 1040 | 4437 | 2739 | 7176
1:30 | 960 | 4320 | 2618 | 6938
2:00 | 880 | 4203 | 2497 | 6700
2:30 | 840 | 4080 | 2485 | 6565 | [5 empty] | Gen. at Eve. Peak | 8108 | 8108 MW (19:00 )
3:00 | 800 | 3957 | 2473 | 6430 | [6 empty] | 19:00
3:30 | 790 | 3920.5 | 2468.5 | 6389 | [5 empty] | Gen. at Day Peak | 7172 | 7172 MW (12:00 )
4:00 | 780 | 3884 | 2464 | 6348 | [6 empty] | 12:00
4:30 | 750 | 3811.5 | 2441.5 | 6253 | [5 empty] | Highest Generation | 8108
5:00 | 720 | 3739 | 2419 | 6158 | [6 empty] | 19:00
5:30 | 692 | 3739 | 2440 | 6179
6:00 | 664 | 3739 | 2461 | 6200
6:30 | 697 | 3776.5 | 2467 | 6243.5
7:00 | 730 | 3814 | 2473 | 6287
7:30 | 718 | 3962 | 2555.5 | 6517.5
8:00 | 706 | 4110 | 2638 | 6748
8:30 | 868 | 4103 | 2694 | 6797
9:00 | 1030 | 4096 | 2750 | 6846
9:30 | 1185 | 4040 | 2706.5 | 6746.5
10:00 | 1340 | 3984 | 2663 | 6647
10:30 | 1368 | 4010.5 | 2666 | 6676.5
11:00 | 1396 | 4037 | 2669 | 6706
11:30 | 1388 | 4171 | 2768 | 6939
12:00 | 1380 | 4305 | 2867 | 7172
12:30 | 1260 | 4512 | 2903 | 7415
13:00 | 1140 | 4719 | 2939 | 7658
13:30 | 1137 | 4369 | 2743.5 | 7112.5
14:00 | 1134 | 4019 | 2548 | 6567
14:30 | 1207 | 3931.5 | 2460 | 6391.5
15:00 | 1280 | 3844 | 2372 | 6216
15:30 | 1230 | 3817.5 | 2360 | 6177.5
16:00 | 1180 | 3791 | 2348 | 6139
16:30 | 1166 | 3938 | 2371.5 | 6309.5
17:00 | 1152 | 4085 | 2395 | 6480
17:30 | 1076 | 4522.5 | 2642 | 7164.5
18:00 | 1000 | 4960 | 2889 | 7849
18:30 | 968 | 5021 | 2957.5 | 7978.5
19:00 | 936 | 5082 | 3026 | 8108
19:30 | 840 | 4880 | 3116 | 7996
20:00 | 730 | 4868 | 3154 | 8022 |  |  |  | Executive Engineer
20:30 | 930 | 4835.5 | 3192.5 | 8028 |  |  |  | Network Operation Division
21:00 | 1130 | 4803 | 3231 | 8034
21:30 | 1175 | 4691 | 3133 | 7824
22:00 | 1220 | 4579 | 3035 | 7614 |  |  |  |  | Page 6 of 7
22:30 | 1268 | 4472.5 | 2930 | 7402.5
23:00 | 1316 | 4366 | 2825 | 7191
23:30 | 1309 | 4256.5 | 2746.5 | 7003
24:00 | 1302 | 4147 | 2668 | 6815
8108 MW (19:00 )
7172 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2022-12-16 |  | Energy |  | 169158836
[13 empty] | 2022-12-16 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 2992 | 730 | 1371 | 0 | 708 | 882 | 46 | 0 | 0 | 86 | 0 | 0
0:30 | 3135.5 | 729 | 1398.5 | 0 | 668.5 | 925.5 | 46 | 0 | 8.5 | 84 | 0 | 0 | Date: | 2022-12-16
1:00 | 3279 | 728 | 1426 | 0 | 629 | 969 | 46 | 0 | 17 | 82 | 0 | 0
1:30 | 3244.5 | 669.5 | 1402.5 | 0 | 527.5 | 951 | 46 | 0 | 17 | 80 | 0 | 0 | [8 empty] | Total Energy | 169.1588 | Total Energy Gen 169.159 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 169.159 MKWHr
2:00 | 3210 | 611 | 1379 | 0 | 426 | 933 | 46 | 0 | 17 | 78 | 0 | 0 | [8 empty] | Energy not Served | 0
2:30 | 3116 | 611 | 1335.5 | 0 | 428 | 936.5 | 46 | 0 | 17 | 75 | 0 | 0 | [8 empty] | Energy Requirement | 169.1588
3:00 | 3022 | 611 | 1292 | 0 | 430 | 940 | 46 | 0 | 17 | 72 | 0 | 0
3:30 | 3020.5 | 611 | 1249 | 0 | 436.5 | 937 | 46 | 0 | 17 | 72 | 0 | 0 | [6 empty] | Shortage
4:00 | 3019 | 611 | 1206 | 0 | 443 | 934 | 46 | 0 | 17 | 72 | 0 | 0
4:30 | 2986.5 | 610.5 | 1155.5 | 0 | 434.5 | 932 | 46 | 0 | 17 | 71 | 0 | 0
5:00 | 2954 | 610 | 1105 | 0 | 426 | 930 | 46 | 0 | 17 | 70 | 0 | 0
5:30 | 2953.5 | 610.5 | 1120 | 0 | 426 | 935 | 46 | 0 | 17 | 71 | 0 | 0
6:00 | 2953 | 611 | 1135 | 0 | 426 | 940 | 46 | 0 | 17 | 72 | 0 | 0
6:30 | 2985.5 | 611 | 1138.5 | 0 | 426 | 942.5 | 46 | 0 | 17 | 74 | 3 | 0 |  |  |  |  | Coal
7:00 | 3018 | 611 | 1142 | 0 | 426 | 945 | 46 | 0 | 17 | 76 | 6 | 0
7:30 | 3059 | 611 | 1271 | 0 | 455 | 953.5 | 46 | 0 | 17 | 74 | 31 | 0 |  |  |  | Oil |  |  |  | ,
8:00 | 3100 | 611 | 1400 | 0 | 484 | 962 | 46 | 0 | 17 | 72 | 56 | 0
8:30 | 3055.5 | 610.5 | 1338 | 0 | 610 | 957 | 46 | 0 | 17 | 73 | 90 | 0
9:00 | 3011 | 610 | 1276 | 0 | 736 | 952 | 46 | 0 | 17 | 74 | 124 | 0
9:30 | 2932 | 610.5 | 1270 | 0 | 736 | 908.5 | 46 | 0 | 17 | 75 | 151.5 | 0
10:00 | 2853 | 611 | 1264 | 0 | 736 | 865 | 46 | 0 | 17 | 76 | 179 | 0
10:30 | 2866.5 | 611 | 1264.5 | 0 | 743 | 850.5 | 46 | 0 | 17 | 79 | 199 | 0
11:00 | 2880 | 611 | 1265 | 0 | 750 | 836 | 46 | 0 | 17 | 82 | 219 | 0
11:30 | 2939 | 646.5 | 1333.5 | 0 | 784.5 | 846 | 46 | 0 | 25 | 83 | 235.5 | 0
12:00 | 2998 | 682 | 1402 | 0 | 819 | 856 | 46 | 0 | 33 | 84 | 252 | 0
12:30 | 3056.5 | 682 | 1392.5 | 0 | 978.5 | 872 | 46 | 0 | 54 | 90 | 243.5 | 0
13:00 | 3115 | 682 | 1383 | 0 | 1138 | 888 | 46 | 0 | 75 | 96 | 235 | 0
13:30 | 3115 | 682 | 1383 | 0 | 1138 | 888 | 46 | 0 | 75 | 96 | 235 | 0
14:00 | 3115 | 682 | 1383 | 0 | 1138 | 888 | 46 | 0 | 75 | 96 | 235 | 0
14:30 | 2905 | 671 | 1268 | 0 | 878 | 858.5 | 46 | 0 | 46 | 88 | 176.5 | 0
15:00 | 2695 | 660 | 1153 | 0 | 618 | 829 | 46 | 0 | 17 | 80 | 118 | 0
15:30 | 2730 | 660 | 1151.5 | 0 | 570 | 841.5 | 46 | 0 | 17 | 79 | 82.5 | 0
16:00 | 2765 | 660 | 1150 | 0 | 522 | 854 | 46 | 0 | 17 | 78 | 47 | 0
16:30 | 2759.5 | 660 | 1179 | 0 | 671.5 | 840 | 46 | 0 | 46.5 | 82 | 25 | 0
17:00 | 2754 | 660 | 1208 | 0 | 821 | 826 | 46 | 0 | 76 | 86 | 3 | 0
17:30 | 2867.5 | 766 | 1203.5 | 0 | 1262 | 825.5 | 46 | 0 | 101.5 | 91 | 1.5 | 0
18:00 | 2981 | 872 | 1199 | 0 | 1703 | 825 | 46 | 0 | 127 | 96 | 0 | 0
18:30 | 3017 | 872.5 | 1213.5 | 0 | 1781.5 | 825 | 46 | 0 | 127 | 96 | 0 | 0
19:00 | 3053 | 873 | 1228 | 0 | 1860 | 825 | 46 | 0 | 127 | 96 | 0 | 0
19:30 | 3186 | 871 | 1317 | 0 | 1562 | 825 | 46 | 0 | 91 | 98 | 0 | 0
20:00 | 3177 | 872 | 1342 | 0 | 1592 | 826 | 46 | 0 | 67 | 100 | 0 | 0
20:30 | 3210.5 | 872 | 1381.5 | 0 | 1538 | 836 | 46 | 0 | 47 | 97 | 0 | 0
21:00 | 3244 | 872 | 1421 | 0 | 1484 | 846 | 46 | 0 | 27 | 94 | 0 | 0
21:30 | 3233.5 | 872 | 1413.5 | 0 | 1275 | 875.5 | 46 | 0 | 13.5 | 95 | 0 | 0
22:00 | 3223 | 872 | 1406 | 0 | 1066 | 905 | 46 | 0 | 0 | 96 | 0 | 0
22:30 | 3177.5 | 824 | 1393.5 | 0 | 965 | 903.5 | 46 | 0 | 0 | 93 | 0 | 0
23:00 | 3132 | 776 | 1381 | 0 | 864 | 902 | 46 | 0 | 0 | 90 | 0 | 0
23:30 | 3062 | 753 | 1376 | 0 | 786 | 892 | 46 | 0 | 0 | 88 | 0 | 0 | Max Temp. in Dhaka |  | 24.7° C | 25.4° C
24:00 | 2992 | 730 | 1371 | 0 | 708 | 882 | 46 | 0 | 0 | 86 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 169.159 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 169.159 MKWHr
Note on W13: Author:

## Generation
g | 2022-12-16
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 |  | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 1125600
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [10 empty] | 0 | 1 | 13 | 0 | [11 empty] | 0 | 32941
| Teknaf 20MW PP (Solartech) | [6 empty] | 1 | 5 | 10 | 14 | 16 | 16 | 16 | 13 | 9 | 4 | 0 | [9 empty] | 102600
6 | Sikalbaha 225MW CCPP (Gas) | 152 | 152 | [23 empty] | 0 | 361629
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 44 | 51 |  | 51 | 17 | [5 empty] | 404618
12 | Hathazari 100 MW peaking PP | [11 empty] | 0 | 24 | [13 empty] | 30432
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 17 |  | 4 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  |  |  | 32 |  | 34 | 17 | 17 | 17 |  |  | 0 | 340399
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP | [11 empty] | 0 | 2 | [12 empty] | 0 | 9232
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 30 | 0 | [5 empty] | 1 | 12 | 15 | 15 | 15 | 50 | 15 | 15 | 15 | 35 | 175 |  | 95 | 45 | 45 | 45 |  |  | 0 | 745200
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 200727
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4347000
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 284616
33 | Ashuganj 225 MW CCPP | 182 | 182 | 182 | 181 | 151 | 151 | 148 | 136 | 128 | 121 | 121 | 118 | 118 | 131 | 125 | 195 | 168 | 161 |  | 161 | 153 | 170 | 216 | 212 | 183 | 183 | 3880000
34 | Ashuganj 450 MW CCPP(South) | 305 | 305 | 275 | 275 | 275 | 275 | 295 | 310 | 280 | 280 | 280 | 280 | 310 | 275 | 290 | 275 | 275 | 300 |  | 275 | 320 | 300 | 275 | 275 | 275 | 300 | 7004000
Ashuganj 450 MW CCPP(North)
| Ashuganj 420 MW CCPP(East) | 353 | 321 | 319 | 318 | 318 | 318 | 331 | 353 | 353 | 319 | 318 | 318 | 352 | 321 | 328 | 318 | 319 | 346 |  | 318 | 373 | 336 | 318 | 318 | 320 | 318 | 7941300
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 150240
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 396 | 395 | 395 | 348 | 331 | 340 | 375 | 396 | 393 | 376 | 377 | 394 | 408 | 351 | 332 | 332 | 336 | 337 |  | 361 | 404 | 395 | 403 | 397 | 398 | 398 | 9095160
40 | Meghnaghat 450 MW CCPP(MPL) | 225 | 225 | 225 | 180 | 180 | 180 | 180 | 225 | 225 | 225 | 225 | 225 | 225 | 180 | 180 | 180 | 225 | 225 |  | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 5226500
41 | Haripur 360MW CCPP(HPL) | 327 | 301 | 308 | 269 | 268 | 267 | 269 | 356 | 292 | 309 | 302 | 352 | 344 | 287 | 300 | 294 | 292 | 283 |  | 282 | 281 | 284 | 320 | 309 | 304 | 303 | 7228000
42 | RPCL 210MW CCPP | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 108 | 106 | 105 | 105 | 105 | 140 | 161 | 170 |  | 216 | 212 | 212 | 216 | 211 | 216 | 216 | 3210240
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 1 | 4 | 5 | 6 | 11 | 34 | 32 | 23 | 16 | 5 | 0 | [9 empty] | 135090
44 | Fenchugonj CCPP Phase-1 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 716000
45 | Fenchugonj CCPP Phase-2 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 964800
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 59 | 60 | 40 | 47 | 51 | 60 | 32 | 32 | 32 | 32 | 32 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 931392
48 | Shahjibazar 86MW PP (Shahjibazar) | 70 | 70 | 30 | 30 | 10 | 10 | 10 | 20 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 50 | 801600
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 217 | 218 | 218 | 217 | 217 | 217 | 217 | 217 | 218 | 206 | 178 | 218 | 219 | 178 | 178 | 178 | 178 | 178 |  | 178 | 178 | 178 | 178 | 178 | 179 | 218 | 4026660
51 | Sylhet 20 MW GTPP | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 440000
52 | Sylhet 50MW PP (EPL) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 306260
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 248220
54 | Hobiganj 11MW PP Cofidence-E | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 192384
55 | Fenchugonj 51 MW PP (Barakatullah) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 448200
56 | Shahjahanulla 25 MW PP | 22 | 21 | 21 | 21 | 21 | 21 | 21 | 8 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 22 | 22 | 22 | 22 | 14 | 22 | 22 | 506856
57 | Bibiana-II 341 MW CCPP (Summit)
| Bibiyana South 400 MW | 171 | 200 | 200 | 256 | 260 | 260 | 260 | 260 | 230 | 200 | 220 | 260 | 243 | 150 | 150 | 150 | 135 | 210 |  | 220 | 220 | 260 | 260 | 260 | 200 | 15 | 5141300
58 | Nababganj 55 MW PP (Southern power ) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 22 | 35 | 35 | 35 | 35 | 35 |  | 55 | 35 | 35 | 35 | 35 | 35 | 35 | 636150
59 | Tangail Palli Power Gen 22 MW | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 300000
60 | Barabkunda 22 MW PP (Regent)
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 13 | 13 | 0 | [8 empty] | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 273564
62 | Tangail 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 16 | 16 | 19 | 19 | 19 | 17 | 17 | 17 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 438984
63 | Impoprt (Tripura) | 82 | 78 | 72 | 72 | 70 | 72 | 76 | 72 | 74 | 76 | 82 | 84 | 96 | 84 | 80 | 78 | 86 | 96 |  | 96 | 98 | 100 | 94 | 96 | 90 | 86 | 1972800
64 | Malancha, Ctg. EPZ (United) | 23 | 30 | 35 | 35 | 35 | 35 | 36 | 42 | 39 | 39 | 39 | 35 | 22 | 22 | 22 | 30 | 23 | 33 |  | 28 | 28 | 42 | 42 | 42 | 42 | 42 | 819360
65 | Feni 22MW PP (Doreen) | 21 | 16 | 16 | 16 | 16 | 16 | 16 | 18 | 18 | 19 | 19 | 19 | 19 | 21 | 19 | 19 | 19 | 20 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 450324
66 | Feni 11 MW PP (Doreen) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 246240
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 26 | 22 | 22 | 22 | 22 | 25 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 754900
68 | Cumilla 25 MW PP (Summit) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 12 | 12 | 12 | 15 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 332670
69 | Summit Ashulia | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 528000
70 | Summit Madhabdi | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 19 | 25 | 21 | 13 | 12 | 12 | 12 | 12 | 12 |  | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 520920
71 | Maona 33 MW PP(Summit) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 568800
72 | Rupganj 33 MW PP(Summit) | 28 | 15 | 24 | 30 | 30 | 31 | 31 | 31 | 31 | 25 | 25 | 25 | 29 | 0 | 33 | 33 | 25 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 706500
73 | Ghorashal 108MW PP (Regent) | 72 | 72 | 72 | 72 | 32 | 32 | 32 | 58 | 66 | 69 | 70 | 69 | 69 | 69 | 69 | 66 | 70 | 70 |  | 70 | 70 | 70 | 70 | 68 | 68 | 70 | 1505454
| Feni Lanka Power | [10 empty] | 0 | 17 | 17 | 3 | [11 empty] | 0 | 37620
| Chowmuhani 113 MW | 8 | 0 | [5 empty] | 1 | 8 | 0 | 0 | 1 | 43 | 26 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 255360
| Manikgonj 162MW PP(MPGL) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 140 | 162 |  | 162 | 162 | 162 | 162 | 134 | 17 | 17 | 1157760
77 | Siddhirganj 100 PP(Dutch Bangla) | [11 empty] | 0 | 7 | 16 |  |  |  | 10 | [7 empty] | 0 | 26880
78 | Gazipur 52 MW PP | [11 empty] | 0 | 8 | [12 empty] | 0 | 12000
79 | Kodda 150MW PP | [10 empty] | 0 | 16 | 32 | [12 empty] | 0 | 30240
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 8 | 8 | [12 empty] | 16834
| Gazipur 100 MW PP | [10 empty] | 0 | 17 | 50 |  |  |  | 1 | 17 |  | 17 | [5 empty] | 0 | 130800
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 0 | 1 | 2 | 4 | 4 | 4 | 3 | 2 | 1 | [10 empty] | 20520
| Jodiac Power | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 36 | 36 | 36 | 36 |  | 36 | [5 empty] | 0 | 469388
| Karnaphuli Power Ltd. | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 17 | 17 | 23 | 81 |  | 90 | 54 | 60 | 54 | 54 | 54 | 51 | 1328976
82 | Madanganj 102 PP(Summit) | [11 empty] | 0 | 4 | 22 | [11 empty] | 0 | 23297
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL) | [10 empty] | 0 | 1 | 21 |  |  |  |  | 19 | [8 empty] | 76800
| Meghnaghat 104 MW PP (OPCL) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 40 | 52 | 55 | 55 | 55 | 55 | 57 | 63 | 57 |  | 54 | 54 | 55 | 55 | 55 | 54 | 17 | 956160
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | [5 empty] | 0 | 209040
92 | Fenchuganj 44MW (Energyprima) | 30 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 20 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 15 | 351792
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 20 | 43 | 43 | 43 | 43 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 866432
94 | Gagnagar 102 MW PP (Digital Power) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 16 | 586800
95 | Patenga 50MW PP (Baraka) | [10 empty] | 0 | 1 | 15 |  |  |  |  | 2 |  | 19 | 19 | 19 | 19 |  |  | 0 | 100800
96 | Chattogram 108 MW PP (ECPV) | [19 empty] | 1 | [6 empty] | 0
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [11 empty] | 0 | 5 | 15 |  |  |  | 10 | [7 empty] | 0 | 55000
100 | Manikganj 55 MW PP (Northern) | 35 | 0 | [5 empty] | 17 | 17 | 17 | 17 | 17 | 35 | 35 | 35 | 17 | 17 | 55 |  | 55 | 17 | 17 | 17 | 17 | 17 | 17 | 450461
101 | Kushiara 163 MW CCPP (KP)
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 | 1 | 1 | 1 | 2 | 1 | 1 | 1 | 0 | [10 empty] | 8300
103 | Kamalaghat 54 MW PP(Banco Energy) | 0 | [6 empty] | 0 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 54 |  | 54 | 54 | 54 | 17 | 17 | 17 | 17 | 394920
104 | Keranigonj 300 MW PP (APR) | [25 empty] | 0 | 0
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 48 | 8 | 8 | 8 | 8 | 8 | 8 | 10 | 48 | 24 | 24 | 33 | 53 | 53 | 16 | 8 | 12 | 56 |  | 56 | 56 | 56 | 56 | 56 | 56 | 47 | 818400
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 17 | 0 | [5 empty] | 0 | 15 | 17 | 17 | 17 | 26 | 34 | 17 | 17 | 17 | 35 |  | 35 | 35 | 35 | 35 | 35 | 25 | 17 | 439776
115 | Juldah 100 MW PP Unit-3 (Acorn) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | [5 empty] | 0 | 230400
116 | Chandpur 200MW (Desh energy) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 24 | 19 | 20 |  | 72 | 146 | 140 | 93 | 51 | 51 | 24 | 767040
117 | Ashuganj 150MW PP (Midland) | 0 | [10 empty] | 0 | 10 | 13 |  |  |  | 45 |  | 105 | 40 | 40 | 40 |  |  | 0 | 309454
118 | Bibiyana-III 400 MW CCPP | 405 | 399 | 399 | 385 | 363 | 352 | 352 | 372 | 352 | 345 | 378 | 387 | 405 | 328 | 338 | 328 | 338 | 397 |  | 418 | 420 | 420 | 418 | 419 | 417 | 417 | 9072000
| Jamalpur 115 MW PP (United) | 24 | 8 | 8 | 8 | 8 | 8 | 8 | 15 | 24 | 24 | 24 | 33 | 47 | 47 | 16 | 8 | 15 | 57 |  | 57 | 16 | 16 | 16 | 16 | 16 | 16 | 578400
| Anwara 300 MW PP (United) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 65 | 125 | 135 |  | 141 | 141 | 135 | 135 | 135 | 135 | 135 | 1911927
| Juldah unit-2 (Acorn) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | [5 empty] | 0 | 242880
| Anlima Energy Ltd. | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 34 | 47 | 100 |  | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 2471455
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 445320
| Spectra Solar Plant Ltd. | [6 empty] | 1 | 7 | 15 | 21 | 24 | 25 | 23 | 19 | 13 | 6 | 1 | [9 empty] | 156866
| Chandpur 115(Doreen) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 18 | 33 | 35 | 37 | 42 | 35 | 22 | 28 | 17 | 20 | 52 |  | 52 | 17 | 17 | 17 | 17 | 17 | 17 | 632640
| Kanchan Purbachal Power Generation Ltd. | 17 | 17 | 17 | 17 | 0 | [5 empty] | 0 | 5 | 17 | 17 | 17 | 17 | 17 | 17 |  | 21 | 35 | 35 | 17 | 17 | 17 | 17 | 322920
Mirsharai 150 MW (Oil)
Mirsharai 150 MW (Gas)
120 | Eastern Zone Total | 4437 | 4203 | 3957 | 3884 | 3739 | 3739 | 3814 | 4110 | 4096 | 3984 | 4037 | 4305 | 4719 | 4019 | 3844 | 3791 | 4085 | 4960 |  | 5082 | 4880 | 4868 | 4803 | 4579 | 4366 | 4147 | 102599520
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | [16 empty] | 8 | 16 |  | 16 | 16 | 16 | 16 |  |  | 0 | 63360
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 17 | [6 empty] | 5 | 17 | 17 | 17 | 17 | 17 | 17 |  |  | 1 | 60 |  | 94 | 94 | 94 | 94 | 94 | 55 | 17 | 703200
130 | Mongla Orion 100 MW Solar PP | [6 empty] | 3 | 21 | 44 | 62 | 73 | 78 | 72 | 58 | 37 | 16 | 2 | [9 empty] | 472320
131 | Rampal 1320 MW (BIFPCL) | 489 | 483 | 490 | 484 | 490 | 490 | 495 | 502 | 502 | 435 | 406 | 406 | 408 | 405 | 409 | 404 | 406 | 405 |  | 405 | 405 | 406 | 406 | 405 | 402 | 402 | 10599300
132 | United Payra Power Ltd. | [25 empty] | 0 | 0
133 | Bhola Nutan Biddut BD LTD (GAS) | 220 | 220 | 220 | 220 | 170 | 170 | 170 | 177 | 178 | 178 | 178 | 190 | 190 | 184 | 183 | 180 | 180 | 164 |  | 160 | 160 | 160 | 160 | 160 | 164 | 160 | 4375227
Bhola Nutan Biddut BD LTD (OIL)
Barisal 110 MW PP (Summit )
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 184 | 184 | 182 | 183 | 150 | 157 | 157 | 158 | 184 |  | 184 | 184 | 184 | 184 | 184 | 180 | 178 | 4312973
140 | Bhola 33 MW PP (Venture) | 21 | 20 | 18 | 18 | 17 | 19 | 17 | 17 | 17 | 16 | 16 | 18 | 21 | 16 | 14 | 14 | 16 | 20 |  | 22 | 23 | 23 | 24 | 23 | 22 | 20 | 448000
141 | Noapara 100 MW PP (Bangla Trac) | [25 empty] | 0 | 0
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 728 | 611 | 611 | 611 | 610 | 611 | 611 | 611 | 610 | 611 | 611 | 682 | 682 | 660 | 660 | 660 | 660 | 872 |  | 873 | 871 | 872 | 872 | 872 | 776 | 730 | 16826909
147 | Bheramara 410 MW CCPP
148 | Payra 1320 MW | 320 | 290 | 290 | 290 | 280 | 290 | 290 | 300 | 290 | 270 | 270 | 290 | 320 | 280 | 260 | 290 | 260 | 260 |  | 260 | 260 | 260 | 280 | 340 | 340 | 320 | 7908300
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 |  | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 3901700
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [26 empty] | 0
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 0 | 1 | 2 | 2 | 3 | 3 | 2 | 1 | 0 | 0 | [9 empty] | 18840
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 228 | 187 | 174 | 173 | 173 | 173 | 173 | 179 | 185 | 170 | 170 | 189 | 221 | 175 | 160 | 160 | 160 | 160 |  | 160 | 160 | 160 | 214 | 215 | 205 | 190 | 4640336
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 327 | 320 | 304 | 302 | 313 | 342 | 348 | 414 | 338 | 307 | 329 | 397 | 345 | 232 | 231 | 230 | 237 | 239 |  | 276 | 365 | 373 | 415 | 414 | 391 | 361 | 7961345
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 0 | 0 | 18 | 18 | 15 | 17 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 342240
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 232074
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | [7 empty] | 0 | 25 | 25 | 25 | 25 | 25 |  |  |  |  | 16 |  | 16 | 16 | 16 | 16 |  |  | 0 | 184810
167 | Katakhali 50 MW Peaking PP | [16 empty] | 9 | 41 |  | 41 | 39 | 40 |  |  |  |  | 111298
168 | Santahar 50 MW Peaking PP | [16 empty] | 23 | 35 |  | 35 | 35 | 27 | 27 |  |  |  | 137485
169 | Natore 52 MW PP (Rajlanka) | 0 | [6 empty] | 0 | 8 | 8 | 8 | 8 | 8 | 8 | [5 empty] | 8 | 8 | 43 | 43 |  |  | 0 | 127162
170 | Chapainawabganj 100 MW Peaking PP | [25 empty] | 0 | 0
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 0 | [6 empty] | 2 | 33 | 35 | 35 | 35 | 40 | 35 |  |  | 1 | 52 |  | 111 | 113 | 113 | 113 | 70 | 35 | 35 | 897504
172 | Confidence Power Bogura Unit-1 113 MW | 0 | [6 empty] | 20 | 35 | 35 | 35 | 35 | 70 | 35 |  |  | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 568512
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | 23 | 0 | [5 empty] | 2 | 34 | 34 | 34 | 34 | 35 | 35 | 35 | 34 | 50 | 107 |  | 107 | 107 | 107 | 107 | 34 | 34 | 34 | 899769
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 0 | 1 | 2 | 2 | 3 | 3 | 4 | 2 | 1 | 0 | [9 empty] | 20466
178 | Energypac Power Venture Thakurgaon Ltd. | [7 empty] | 0 | 17 | 17 | 17 | 17 | 26 |  |  |  |  | 34 |  | 34 | 36 | 36 | 36 |  |  | 0 | 301632
| Intraco Solar 30 MW | [6 empty] | 0 | 3 | 8 | 12 | 15 | 17 | 14 | 12 | 8 | 3 | 0 | [9 empty] | 93434
Adani Power Jharkhanda Ltd
178 | Teesta Solar Limited | [7 empty] | 16 | 38 | 57 | 71 | 70 | 67 | 51 | 29 | 11 | [10 empty] | 411120