## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2022-12-24 | Saturday
|  | Date (day): | 2022-12-24 |  | Saturday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 7999.6 | MW |  |  | (b) At Evening Peak Hour : |  | 10209 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2022-12-23 | 2022-12-24 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Line O/L
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  |  | Machine problem
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 120 | 200 | 200 | 200 | 165 |  | Gas shortage
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 69 | 71 | 70 | 70 | 38 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 399 | 378 | 400 | 400
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 280 | 320 | 330 | 330 | 30
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 225 | 225 | 225 |  | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 31 | 32 | 33 | 34 | 66 |  | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 17 | 27 | 34 | 34 | 68 |  | Fuel shortage
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 0 | 15 | 0 | 15 | 40 |  | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 11 | 0 | 13 | 13 |  | 9 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 32 | 30 | 33 | 38 | 50 |  | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 16 | 33 | 16 | 33 | 69 |  | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 54 | 17 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 16 | 32 | 32 | 32 | 117 |  | Fuel shortage
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 35 | 35 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 35 | 35 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 39 | 49 | 49 | 49 |  | 31 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25 |  | 8 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 8 | 8 | 50 | 50
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 30 | 32 | 30 | 97 | 203 |  | Fuel shortage
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 150 | 150 |  | Fuel conservation
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 0 | 0 | 0 | 50 | 50 |  | Fuel conservation
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 50 | 50 |  | Fuel conservation
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 36 | 35 | 35 | 35 | 114 |  | Fuel shortage
36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 70 | 35 | 90 | 100
37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 17 | 17 | 17 | 17 | 87 |  | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 17 | 162 | 17 | 162
39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 30 | 0 | 30 | 0
40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 17 | 17 | 17 | 38 |  | Fuel shortage
| Dhaka area Total |  |  |  |  | 6263 | 5847 | 1607 | 1900 | 1866 | 2423 | 2491 | 728
41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 13 | 17 | 8 | 25
43 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 19 | 0 | 20 | 0
44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 13 | 43 | 32 | 44 |  | 6 | Engine problem
45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 30 | 30 | 76 | 76 | 154 |  | Low Water Level
46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 151 | 151 | 150 | 150 |  | 75 | ST Under maint
47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 17 | 17 | 17 | 85 | 20 |  | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 32 | 24 | 24 | 74 |  | Fuel shortage
50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 39 | 0 | 50 | 52 |  | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 10 | 10 | 10 | 10 | 90 |  | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 12 | 12 | 12 | 88 |  | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 22 |  | Gas shortage
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 23 | 33 | 5 | 30
54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 32 | 0 | 0 | 0 | 108 |  | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 51 | 135 | 51 | 275 |  | 25
57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 32 | 17 | 35 | 35 |  | 19 | Engine problem
58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 47 | 17 | 51 | 68 |  | 42 | Engine problem
59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 12 | 12 | 12 | 88 |  | Fuel shortage
60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 91 | 89 | 107 | 107 |  | 9 | Engine problem
| Mirsharai 150 MW |  | Gas/HSD | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0
| Chattogram area Total |  |  |  |  | 2442 | 2382 | 557 | 654 | 615 | 1003 | 1056 | 326
61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 203 | 196 | 180 | 185 |  |  | Gas shortage
63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 | 360 |  | S/D due to Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 300 | 290 | 300 | 300 |  |  | FGMO
65 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 342 | 333 | 320 | 320 |  |  | On test.
66 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 5 | 35 | 35 | 35 | 10 |  | Gas shortage
67 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 55 | 0 | 5 | 5 | 5 | 50 |  | Gas shortage
68 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 0 | 8 | 8 | 8 | 187 |  | Gas shortage
69 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
70 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 6 | 72 | 6 | 70 | 80 |  | Fuel shortage
71 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 25 | 30 |  | 22 | Engine problem
72 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under Maint.
73 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 17 | 51 | 17 | 50 | 150 |  | Fuel shortage
74 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 20 | 21 | 21
75 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 76 | 82 | 135 | 152
76 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 24 | 33 | 33 | 33
77 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 8 | 8 | 8 | 44 |  | Fuel shortage
78 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 15 | 15 | 15 | 15 |  | 10 | Engine problem
79 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 100 | 100 |  | Fuel conservation
80 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 0 | 0 | 0 | 114 |  | Fuel shortage
81 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 63 | 8 | 9 | 9 | 104 |  | Fuel shortage
82 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 36 | 17 | 17 | 17 |  | 37 | Engine problem
83 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 35 | 53 | 24 | 66 | 49 |  | Fuel shortage
| Cumilla Area Total |  |  |  |  | 3309 | 3285 | 1226 | 1288 | 1220 | 1486 | 1382 | 232
84 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 70 | 100 | 70 | 100 | 102 |  | Gas shortage
85 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 22 | 22 | 22
86 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0
87 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
88 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 49 | 46 | 46 | 48 | 152 |  | Fuel shortage
89 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 28 | 47 | 17 | 47 | 68 |  | Fuel shortage
90 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 37 | 0 | 50 | 0
91 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 12 | 12 |  | 10 | Engine problem
| Mymensingh Area Total |  |  |  |  | 717 | 614 | 217 | 227 | 218.6 | 229 | 102 | 10
92 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 30 | 30 | 30 | 30 |  | 40 | Machine problem.
93 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 31 | 31 | 31 |  | 59 | Machine problem
94 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 110 | 110 | 163 |  | ST Under maint
95 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
96 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 22 | 53 | 10 | 50 | 1
97 | Fenchuganj 44MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 44 | 46 | 20 | 40 | 10
98 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 8 | 8 |  | 3 | Engine problem
99 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 64 | 64 | 65 | 66
100 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 0 | 0 | 50 | 86
101 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
102 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 218 | 0 | 0 | 0 |  | 231 | Under maint
103 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18
104 | Sylhet 50MW PP (EPL) |  | Gas | NENP | 27*2 | 50 | 50 | 15 | 26 | 15 | 15 | 35 |  | Gas shortage
105 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 22 | 22 | 22 | 24
106 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 0 | 0 | 0 | 0 |  | 341 | Under maint.
107 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 414 | 420 | 400 | 400
108 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
109 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 400 | 400 | 400 | 400
| Sylhet Area Total |  |  |  |  | 2522 | 2477 | 1257 | 1120 | 1189 | 1288 | 209 | 1104
110 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 681 | 870 | 831 | 926
111 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 0 | 16 | 0 | 16 | 99 |  | Fuel shortage
112 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 40 |  | 14 | Engine problem
113 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
114 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 70 |  | 39 | Engine problem
115 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 | 410 |  | Gas shortage.
116 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 40 | 0 | 40
117 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 0 | 50 | 50 |  | Fuel conservation
118 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 17 | 17 | 17 | 88 |  | Fuel shortage
119 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Fuel shortage
120 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 69 | 0 | 100 | 0
| Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 0 | 0 | 0 | 410 | 511 | 400 | 400 |  |  | On test.
| Khulna Area Total |  |  |  |  | 2388 | 2384 | 1160 | 1454 | 1348 | 1559 | 998 | 53
121 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 0 | 0 |  |  | Line O/L
122 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 17 | 20 | 19 | 24 |  | 16 | Engine problem
123 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 178 | 184 | 90 | 90 |  |  | machine problem
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
124 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 270 | 430 | 400 | 520 |  | 724 | Unit-2 U/M &Rampal Test
125 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 162 | 220 | 110 | 110
126 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 0 | 35 |  |  | Line O/L
| Barisal 307 MW |  | Coal | BCPCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Barisal Area Total |  |  |  |  | 1958 | 1958 | 627 | 854 | 619 | 779 | 0 | 740
127 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
128 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 20 |  | 32 | Engine problem
129 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 25 |  | 46 | Engine problem
130 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
131 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 34 | 50 | 25 | 42 |  | 8 | Engine problem
132 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 40 |  | 10 | Engine problem
133 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 145 | 180 | 170 | 170 | 40 |  | Gas shortage
134 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 34 | 0 | 0 | 0 | 220 |  | Fuel shortage
135 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
136 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 306 | 278 | 350 | 350 | 64 |  | Gas shortage
137 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 24 | 0 | 30 |  | 20 | Engine problem
138 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 16 | 17 | 20 | 20 |  | 2 | Machine problem
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
139 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 8 | 8 |  | 3 | Engine problem
140 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 8 | 8 | 8 | 44 | 44 | Fuel shortage
141 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 0 | 35 | 69 |  | Fuel shortage
142 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 0 | 100 | 100 |  | Fuel conservation
143 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 35 | 94 | 35 | 95 |  | 18 | Engine problem
144 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 95 | 75 | 35 | 113
145 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 4 | 0 | 6 | 0
| Adani Power Jharkhanda Ltd |  | Coal | Import | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Rajshahi Area Total |  |  |  |  | 2179 | 2129 | 685 | 734 | 657 | 1056 | 928 | 183
146 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal shortage
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
147 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 160 | 160 | 160 | 160 |  |  | Machine problem
148 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
149 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
150 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 49 | 113 | 34 | 113
151 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 4 | 0 | 8 | 0
152 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 90 | 115 | 35 | 113
153 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 6 | 0 | 30 | 0
| Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 0 | 0 | 103 | 0 | 0 | 0
| Rangpur Area Total |  |  |  |  | 830 | 750 | 412 | 388 | 267 | 386 | 125 | 85
| Total |  |  |  |  | 22608 | 21826 | 7748 | 8619 | 7999.6 | 10209 | 7291 | 3461
A. |  | 2022-12-23 | (Yesterday) |  |  |  |  | Friday
1 | Highest Generation : |  |  | 8619 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
2 | Minimum Generation : |  |  | 6203 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 8619 | MW
3 | Day peak Generation : |  |  | 7748 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 8175.14 | MW
4 | Evening peak Generation : |  |  | 8619 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 177.4442 | MKWHr | By Solar | 1.623 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Gas : | 106.7326 | MKWHr |  | By Oil: | 25.6929 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 23.9035 | MKWHr |  | By Hydro: | 0.9168 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 7291 | MW | Dhaka | 2785.35 | 2785.35 |  | 0 |  | 18:00 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 3461 | MW | Chittagong | 924.1 | 924.1 |  | 0 |  | 19:00 |  | 0
|  |  | Total = |  |  | 10752 | MW | Khulna | 1019.8 | 1019.8 |  | 0 |  | 19:30 |  | 0
7 | Total Gas Supplied : |  |  | 797.34 | MMCFD |  |  | Rajshahi | 853.1 | 853.1 |  | 0 |  | 20:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 108702525.74 | ii) Oil : | Taka | 331754305.47 | Comilla | 718 | 718 |  | 0 |  | 21:00 |  | 0
|  | iii) Coal : |  | 94552272 | Total | Taka | 535009103.21 | Mymensingh | 694 | 694 |  | 0 |  | 22:00 |  | 0
9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0 | MKWHr. | Sylhet | 339 | 339 |  | 0 |  | 23:00 |  | 0
| ii) During Peak Demand : |  |  | 500 | MW (E to W) at | 19:00 | hrs | Barisal | 239.79 | 239.79 |  | 0 |  | 24:00 |  | 0
| iii) Maximum : |  |  | 346 | MW at | 20:00 | hrs | Rangpur | 602 | 602 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 27° C |  |  | Total | 8175.14 | 8175.14 |  | 0
B. |  | 2022-12-24 | (Today) |  |  |  | Saturday |  |  | Probable max. temperature in Dhaka |  |  | 26.3° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 9500 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 10209 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 7500 | MW
4 | Reserve(Generation end) |  |  |  | 709 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 195.5818 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5766 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 16.8771 | MKWHr. | ii) HVDC Flow at Peak Time |  | 870 | MW at | 19:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.6982 | MKWHr. | iii) Maximum HVDC Flow : |  | 870 | MW at | 19:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 87.35 |  | (b) Today: | 87.15 |  | (c) Rule Curve: |  | 103.9
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2022-12-23
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 0 | 170 | 70 | 0 | 396 | 339 |  | 0 | 225 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 13 | 23 | 27 | 25 | 30 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 |  | 8 | 0 | 0 | 10 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 290 | 183 | 0 | 0 | 5 | 0 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 15 | 68 | 103 | 0 | 21 | 0 | 30 | 42 | 11 | 30 | 0 | 0 | 62 | 86 | 0 | 218 | 19 | 15 | 10 | 0 | 22 | 8 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 12 | 17 | 5 | 375 | 28 | 0 | 36 | 0 | 51 | 17 | 72 | 0 | 3 | 12 | 400 | 17 | 0 | 17 | 107 | 0 | 17 | 0 | 34 | 17 | 365 | 0 | 0 |  | 729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 8 | 0 | 0 | 159 | 0 | 0 | 157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 311 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 280 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 626 | 0 | 0 | 0 | 0 |  | 4630 | 2720 | 7350 | 3406 | 729 | 1430 | 0 | 606 | 1065 | 46 | 0 | 0 | 68 | 0 | 0 | 87.37
2:00 | 0 | 0 | 0 | 0 | 170 | 70 | 0 | 390 | 341 |  | 0 | 225 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 27 | 25 | 30 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 152 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 290 | 184 | 0 | 0 | 5 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 33 | 15 | 64 | 104 | 0 | 21 | 0 | 30 | 42 | 11 | 10 | 0 | 0 | 64 | 50 | 0 | 218 | 19 | 15 | 10 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 12 | 0 | 0 | 375 | 8 | 0 | 0 | 0 | 51 | 17 | 72 | 0 | 0 | 12 | 400 | 0 | 0 | 0 | 107 | 0 | 17 | 0 | 0 | 17 | 365 | 0 | 0 |  | 609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 634 | 0 | 0 | 0 | 0 |  | 4271 | 2562 | 6833 | 3337 | 609 | 1329 | 0 | 404 | 1044 | 46 | 0 | 0 | 64 | 0 | 0 | 87.37
3:00 | 0 | 0 | 0 | 0 | 170 | 32 | 0 | 361 | 304 |  | 0 | 225 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 27 | 25 | 30 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 290 | 187 | 0 | 0 | 5 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 33 | 15 | 58 | 109 | 0 | 21 | 0 | 30 | 42 | 11 | 10 | 0 | 0 | 64 | 20 | 0 | 218 | 19 | 15 | 10 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 12 | 0 | 0 | 375 | 8 | 0 | 0 | 0 | 51 | 17 | 72 | 0 | 0 | 12 | 370 | 0 | 0 | 0 | 107 | 0 | 17 | 0 | 0 | 17 | 318 | 0 | 0 |  | 608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 159 | 0 | 0 | 156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 631 | 0 | 0 | 0 | 0 |  | 4024 | 2538 | 6562 | 3238 | 608 | 1208 | 0 | 364 | 1040 | 46 | 0 | 0 | 58 | 0 | 0 | 87.36
4:00 | 0 | 0 | 0 | 0 | 160 | 32 | 0 | 361 | 269 |  | 0 | 225 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 27 | 25 | 32 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 290 | 183 | 0 | 0 | 5 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 11 | 8 | 15 | 60 | 110 | 0 | 21 | 0 | 30 | 42 | 11 | 10 | 0 | 0 | 40 | 20 | 0 | 218 | 19 | 15 | 10 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 12 | 0 | 0 | 352 | 8 | 0 | 0 | 0 | 51 | 17 | 34 | 0 | 0 | 12 | 340 | 0 | 0 | 0 | 107 | 0 | 17 | 0 | 0 | 17 | 318 | 0 | 0 |  | 608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 159 | 0 | 0 | 157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 626 | 0 | 0 | 0 | 0 |  | 3853 | 2493 | 6346 | 3137 | 608 | 1134 | 0 | 326 | 1035 | 46 | 0 | 0 | 60 | 0 | 0 | 87.36
5:00 | 0 | 0 | 0 | 0 | 160 | 32 | 0 | 361 | 275 |  | 0 | 225 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 27 | 25 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 290 | 184 | 0 | 0 | 5 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 11 | 8 | 15 | 62 | 110 | 0 | 21 | 0 | 30 | 42 | 11 | 10 | 0 | 0 | 40 | 20 | 0 | 221 | 19 | 15 | 10 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 12 | 0 | 0 | 360 | 8 | 0 | 0 | 0 | 51 | 17 | 34 | 0 | 0 | 12 | 370 | 0 | 0 | 0 | 107 | 0 | 17 | 0 | 0 | 17 | 318 | 0 | 0 |  | 608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 159 | 0 | 0 | 159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 434 | 0 | 0 | 0 | 0 |  | 3907 | 2296 | 6203 | 3182 | 608 | 1136 | 0 | 326 | 843 | 46 | 0 | 0 | 62 | 0 | 0 | 87.35
6:00 | 0 | 0 | 0 | 0 | 150 | 32 | 0 | 380 | 361 |  | 0 | 225 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 22 | 27 | 25 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 |  | 1 | 0 | 0 | 10 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 290 | 183 | 0 | 0 | 5 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 11 | 8 | 15 | 58 | 111 | 0 | 21 | 0 | 30 | 42 | 11 | 10 | 0 | 0 | 40 | 0 | 0 | 222 | 19 | 15 | 10 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 12 | 1 | 1 | 363 | 8 | 0 | 0 | 0 | 51 | 17 | 50 | 0 | 5 | 12 | 400 | 6 | 0 | 17 | 107 | 0 | 17 | 0 | 11 | 17 | 348 | 0 | 0 |  | 609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 157 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 159 | 0 | 0 | 162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 385 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 20 | 250 | 160 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 412 | 0 | 0 | 0 | 0 |  | 4115 | 2357 | 6472 | 3231 | 609 | 1275 | 0 | 432 | 821 | 46 | 0 | 0 | 58 | 0 | 0 | 87.35
7:00 | 0 | 0 | 0 | 0 | 150 | 57 | 0 | 378 | 280 |  | 0 | 225 | 0 | 6 | 17 | 0 | 0 | 0 | 0 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 22 | 27 | 25 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 7 | 151 | 0 | 0 | 0 |  | 10 | 0 | 0 | 10 | 0 | 14 | 0 | 42 | 0 | 0 | 0 | 0 | 290 | 197 | 0 | 0 | 5 | 0 | 0 | 10 | 0 | 0 | 8 | 0 | 11 | 8 | 15 | 56 | 73 | 0 | 21 | 0 | 30 | 0 | 11 | 30 | 0 | 0 | 64 | 0 | 0 | 221 | 19 | 15 | 10 | 0 | 0 | 8 | 0 | 18 | 0 | 0 | 47 | 0 | 10 | 1 | 12 | 17 | 5 | 360 | 8 | 14 | 12 | 0 | 51 | 17 | 68 | 0 | 44 | 12 | 400 | 17 | 1 | 17 | 95 | 0 | 17 | 1 | 35 | 17 | 370 | 0 | 0 |  | 609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 8 | 0 | 13 | 0 | 8 | 0 | 0 | 159 | 0 | 0 | 166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 266 | 0 | 0 | 25 | 0 | 33 | 0 | 0 | 35 | 250 | 160 | 0 | 0 | 1 | 2 | 35 | 0 | 0 | 404 | 0 | 0 | 0 | 0 |  | 4338 | 2383 | 6721 | 3236 | 609 | 1136 | 0 | 819 | 813 | 46 | 0 | 0 | 56 | 6 | 0 | 87.34
8:00 | 0 | 0 | 0 | 0 | 140 | 67 | 0 | 384 | 361 |  | 0 | 225 | 0 | 17 | 17 | 0 | 0 | 0 | 0 | 25 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 22 | 22 | 27 | 25 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 8 | 151 | 0 | 0 | 0 |  | 11 | 0 | 0 | 10 | 0 | 12 | 0 | 36 | 0 | 0 | 0 | 0 | 310 | 198 | 0 | 0 | 5 | 0 | 0 | 51 | 0 | 0 | 8 | 0 | 11 | 21 | 15 | 66 | 73 | 0 | 18 | 1 | 30 | 0 | 22 | 46 | 0 | 0 | 65 | 0 | 0 | 218 | 18 | 15 | 10 | 0 | 21 | 0 | 0 | 32 | 0 | 0 | 47 | 0 | 34 | 7 | 12 | 17 | 6 | 369 | 16 | 34 | 17 | 0 | 51 | 17 | 17 | 0 | 56 | 12 | 400 | 17 | 8 | 17 | 102 | 0 | 17 | 8 | 35 | 17 | 360 | 0 | 0 |  | 609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 8 | 0 | 18 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 397 | 0 | 0 | 35 | 0 | 33 | 0 | 0 | 35 | 250 | 163 | 0 | 0 | 1 | 16 | 35 | 0 | 0 | 421 | 1 | 0 | 0 | 14 |  | 4636 | 2583 | 7219 | 3299 | 609 | 1427 | 0 | 885 | 831 | 46 | 0 | 0 | 66 | 56 | 0 | 87.34
9:00 | 0 | 0 | 0 | 0 | 120 | 70 | 0 | 409 | 343 |  | 0 | 225 | 0 | 18 | 17 | 0 | 0 | 0 | 0 | 25 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 22 | 22 | 27 | 25 | 33 | 8 | 0 | 46 | 0 | 0 | 0 | 8 | 151 | 0 | 0 | 0 |  | 12 | 0 | 0 | 10 | 0 | 21 | 0 | 28 | 0 | 0 | 0 | 0 | 295 | 183 | 0 | 0 | 5 | 0 | 0 | 51 | 0 | 0 | 8 | 0 | 11 | 19 | 15 | 62 | 73 | 0 | 18 | 1 | 30 | 0 | 22 | 43 | 0 | 0 | 70 | 0 | 0 | 218 | 18 | 15 | 10 | 0 | 16 | 0 | 0 | 33 | 0 | 0 | 46 | 0 | 36 | 13 | 12 | 17 | 5 | 338 | 28 | 60 | 17 | 2 | 51 | 17 | 17 | 0 | 56 | 12 | 400 | 17 | 19 | 17 | 107 | 0 | 17 | 17 | 35 | 17 | 347 | 0 | 0 |  | 608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 8 | 0 | 18 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 0 | 35 | 0 | 100 | 0 | 0 | 90 | 260 | 165 | 0 | 0 | 3 | 36 | 36 | 0 | 0 | 404 | 2 | 0 | 0 | 29 |  | 4661 | 2695 | 7356 | 3212 | 608 | 1376 | 0 | 1106 | 824 | 46 | 0 | 0 | 62 | 122 | 0 | 87.33
10:00 | 0 | 0 | 0 | 0 | 120 | 70 | 0 | 374 | 280 |  | 0 | 225 | 0 | 17 | 17 | 0 | 0 | 0 | 0 | 27 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 0 | 22 | 27 | 25 | 33 | 8 | 0 | 46 | 0 | 0 | 0 | 8 | 151 | 0 | 0 | 0 |  | 12 | 0 | 0 | 10 | 9 | 14 | 0 | 23 | 0 | 0 | 0 | 0 | 280 | 183 | 0 | 0 | 5 | 0 | 0 | 51 | 0 | 0 | 8 | 7 | 11 | 16 | 15 | 60 | 72 | 0 | 19 | 0 | 30 | 0 | 22 | 43 | 0 | 0 | 69 | 0 | 0 | 218 | 18 | 15 | 10 | 0 | 16 | 0 | 0 | 32 | 0 | 0 | 48 | 0 | 36 | 17 | 12 | 17 | 6 | 339 | 28 | 70 | 17 | 3 | 51 | 17 | 17 | 0 | 57 | 12 | 382 | 17 | 31 | 17 | 107 | 0 | 21 | 24 | 35 | 17 | 317 | 0 | 0 |  | 608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 8 | 0 | 17 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 35 | 0 | 107 | 0 | 1 | 95 | 270 | 167 | 0 | 0 | 4 | 55 | 36 | 0 | 0 | 410 | 4 | 0 | 0 | 40 |  | 4518 | 2726 | 7244 | 3090 | 608 | 1283 | 0 | 1138 | 840 | 46 | 0 | 0 | 60 | 179 | 0 | 87.33
11:00 | 0 | 0 | 0 | 0 | 120 | 67 | 0 | 359 | 280 |  | 0 | 225 | 0 | 21 | 17 | 0 | 0 | 0 | 0 | 32 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 19 | 22 | 14 | 25 | 33 | 8 | 0 | 19 | 0 | 0 | 0 | 8 | 151 | 0 | 0 | 0 |  | 12 | 0 | 0 | 10 | 32 | 12 | 0 | 23 | 0 | 0 | 0 | 0 | 295 | 191 | 0 | 0 | 5 | 0 | 0 | 51 | 0 | 0 | 8 | 18 | 11 | 17 | 15 | 66 | 71 | 0 | 19 | 2 | 30 | 0 | 22 | 46 | 0 | 0 | 66 | 0 | 0 | 218 | 18 | 15 | 10 | 0 | 16 | 0 | 0 | 32 | 0 | 0 | 49 | 0 | 36 | 19 | 12 | 17 | 6 | 403 | 28 | 70 | 17 | 4 | 51 | 17 | 17 | 0 | 57 | 12 | 400 | 17 | 37 | 17 | 107 | 0 | 35 | 29 | 35 | 17 | 330 | 0 | 0 |  | 608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 8 | 0 | 17 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 321 | 0 | 0 | 35 | 0 | 70 | 0 | 2 | 95 | 270 | 163 | 0 | 0 | 4 | 65 | 37 | 0 | 0 | 368 | 5 | 0 | 0 | 60 |  | 4675 | 2660 | 7335 | 3215 | 608 | 1255 | 0 | 1147 | 798 | 19 | 0 | 0 | 66 | 227 | 0 | 87.32
12:00 | 0 | 0 | 0 | 0 | 120 | 69 | 0 | 399 | 280 |  | 0 | 225 | 0 | 31 | 17 | 0 | 0 | 0 | 0 | 32 | 16 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 11 | 22 | 17 | 25 | 33 | 8 | 0 | 0 | 30 | 0 | 0 | 13 | 151 | 0 | 0 | 0 |  | 12 | 0 | 0 | 10 | 32 | 13 | 0 | 23 | 0 | 0 | 0 | 0 | 300 | 203 | 0 | 0 | 5 | 0 | 0 | 51 | 0 | 0 | 8 | 17 | 11 | 24 | 15 | 76 | 70 | 0 | 19 | 2 | 30 | 0 | 22 | 44 | 0 | 0 | 64 | 0 | 0 | 218 | 18 | 15 | 10 | 0 | 22 | 0 | 0 | 30 | 0 | 0 | 49 | 0 | 36 | 19 | 12 | 17 | 6 | 414 | 28 | 70 | 17 | 4 | 51 | 32 | 47 | 17 | 63 | 12 | 400 | 17 | 37 | 17 | 91 | 0 | 36 | 30 | 35 | 17 | 342 | 0 | 0 |  | 681 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 8 | 0 | 16 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 145 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 306 | 0 | 0 | 35 | 0 | 49 | 0 | 4 | 95 | 270 | 162 | 0 | 0 | 4 | 69 | 90 | 0 | 0 | 410 | 6 | 0 | 0 | 103 |  | 4864 | 2884 | 7748 | 3281 | 681 | 1240 | 0 | 1272 | 840 | 30 | 34 | 50 | 76 | 278 | 0 | 87.32
13:00 | 0 | 0 | 0 | 0 | 120 | 69 | 0 | 402 | 280 |  | 0 | 225 | 0 | 33 | 26 | 0 | 0 | 0 | 0 | 32 | 16 | 32 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 0 | 22 | 11 | 25 | 33 | 39 | 0 | 0 | 30 | 0 | 0 | 17 | 151 | 0 | 0 | 0 |  | 7 | 0 | 0 | 10 | 32 | 32 | 0 | 25 | 0 | 0 | 0 | 0 | 300 | 184 | 8 | 0 | 5 | 0 | 0 | 51 | 0 | 0 | 8 | 19 | 11 | 23 | 15 | 80 | 71 | 0 | 0 | 2 | 30 | 20 | 22 | 45 | 0 | 0 | 66 | 0 | 0 | 218 | 18 | 15 | 10 | 0 | 22 | 0 | 0 | 32 | 30 | 25 | 49 | 0 | 36 | 19 | 12 | 17 | 5 | 352 | 28 | 70 | 17 | 3 | 51 | 34 | 70 | 17 | 62 | 12 | 380 | 17 | 29 | 17 | 89 | 0 | 36 | 27 | 33 | 17 | 351 | 18 | 0 |  | 681 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 170 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 8 | 0 | 16 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 130 | 0 | 68 | 0 | 0 | 0 | 0 | 0 | 268 | 3 | 0 | 35 | 0 | 49 | 0 | 5 | 95 | 340 | 210 | 0 | 0 | 4 | 68 | 115 | 0 | 0 | 410 | 7 | 0 | 0 | 104 |  | 4954 | 3021 | 7975 | 3225 | 681 | 1261 | 55 | 1415 | 910 | 30 | 18 | 32 | 80 | 268 | 0 | 87.31
14:00 | 0 | 0 | 0 | 0 | 190 | 69 | 0 | 361 | 280 |  | 0 | 225 | 0 | 25 | 30 | 0 | 0 | 0 | 0 | 22 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 0 | 22 | 11 | 25 | 33 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 151 | 0 | 0 | 0 |  | 12 | 0 | 0 | 10 | 31 | 37 | 0 | 27 | 0 | 0 | 0 | 0 | 270 | 184 | 8 | 0 | 20 | 0 | 0 | 51 | 0 | 0 | 8 | 19 | 11 | 24 | 15 | 78 | 70 | 0 | 16 | 2 | 30 | 20 | 22 | 45 | 0 | 0 | 40 | 0 | 0 | 0 | 18 | 15 | 10 | 0 | 22 | 0 | 0 | 32 | 0 | 0 | 49 | 0 | 36 | 15 | 12 | 17 | 6 | 352 | 28 | 17 | 17 | 3 | 51 | 17 | 34 | 0 | 8 | 12 | 370 | 17 | 24 | 17 | 89 | 0 | 36 | 24 | 35 | 17 | 318 | 0 | 0 |  | 657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 8 | 0 | 16 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 130 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 244 | 17 | 0 | 35 | 0 | 34 | 0 | 4 | 35 | 350 | 179 | 0 | 0 | 2 | 60 | 35 | 0 | 0 | 410 | 16 | 0 | 0 | 88 |  | 4345 | 2728 | 7073 | 2948 | 657 | 1205 | 0 | 997 | 920 | 30 | 0 | 0 | 78 | 238 | 0 | 87.32
15:00 | 0 | 0 | 0 | 0 | 200 | 69 | 0 | 334 | 250 |  | 0 | 225 | 0 | 8 | 17 | 0 | 0 | 0 | 0 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 0 | 22 | 11 | 25 | 33 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 151 | 0 | 0 | 0 |  | 12 | 0 | 0 | 10 | 31 | 38 | 0 | 29 | 0 | 0 | 0 | 0 | 300 | 183 | 8 | 0 | 20 | 0 | 0 | 51 | 0 | 0 | 8 | 19 | 11 | 33 | 15 | 76 | 70 | 0 | 16 | 1 | 30 | 30 | 11 | 45 | 0 | 0 | 61 | 0 | 0 | 0 | 18 | 18 | 10 | 0 | 22 | 0 | 0 | 32 | 0 | 0 | 24 | 0 | 36 | 12 | 12 | 17 | 6 | 374 | 16 | 17 | 17 | 2 | 51 | 17 | 34 | 0 | 8 | 12 | 367 | 17 | 10 | 17 | 89 | 0 | 36 | 16 | 39 | 17 | 348 | 0 | 0 |  | 655 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 16 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 265 | 0 | 0 | 35 | 0 | 34 | 0 | 4 | 35 | 260 | 162 | 0 | 0 | 2 | 40 | 35 | 0 | 0 | 410 | 10 | 0 | 0 | 65 |  | 4305 | 2512 | 6817 | 2996 | 655 | 1172 | 0 | 896 | 830 | 30 | 0 | 0 | 76 | 162 | 0 | 87.3
16:00 | 0 | 0 | 0 | 0 | 200 | 33 | 0 | 346 | 250 |  | 0 | 225 | 0 | 8 | 5 | 1 | 0 | 0 | 0 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 0 | 22 | 11 | 25 | 33 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 151 | 0 | 0 | 0 |  | 12 | 0 | 0 | 10 | 31 | 34 | 0 | 34 | 0 | 0 | 0 | 0 | 300 | 204 | 8 | 0 | 20 | 0 | 0 | 15 | 0 | 0 | 8 | 19 | 11 | 33 | 15 | 76 | 84 | 0 | 16 | 1 | 30 | 20 | 48 | 45 | 0 | 0 | 61 | 0 | 0 | 0 | 18 | 24 | 10 | 0 | 22 | 0 | 0 | 32 | 0 | 0 | 8 | 0 | 35 | 5 | 12 | 17 | 10 | 377 | 8 | 17 | 17 | 1 | 30 | 17 | 28 | 0 | 8 | 12 | 380 | 17 | 7 | 32 | 88 | 0 | 36 | 8 | 53 | 17 | 376 | 0 | 0 |  | 656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 17 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 259 | 0 | 0 | 35 | 0 | 34 | 0 | 2 | 0 | 260 | 160 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 410 | 5 | 0 | 0 | 33 |  | 4272 | 2370 | 6642 | 3074 | 656 | 1141 | 0 | 755 | 830 | 30 | 0 | 0 | 76 | 80 | 0 | 87.29
17:00 | 0 | 0 | 0 | 0 | 150 | 70 | 0 | 396 | 320 |  | 0 | 225 | 0 | 9 | 17 | 15 | 0 | 0 | 0 | 8 | 16 | 16 | 0 | 0 | 0 | 0 | 17 | 20 | 35 | 0 | 22 | 11 | 25 | 33 | 8 | 0 | 0 | 30 | 0 | 0 | 6 | 130 | 0 | 0 | 0 |  | 12 | 21 | 3 | 10 | 0 | 19 | 0 | 35 | 0 | 0 | 0 | 0 | 270 | 183 | 8 | 0 | 32 | 2 | 0 | 20 | 0 | 0 | 8 | 19 | 11 | 33 | 15 | 80 | 96 | 0 | 22 | 0 | 30 | 20 | 50 | 45 | 0 | 0 | 40 | 0 | 0 | 0 | 18 | 26 | 10 | 0 | 22 | 0 | 0 | 32 | 0 | 0 | 24 | 0 | 35 | 0 | 12 | 17 | 25 | 364 | 20 | 25 | 20 | 0 | 100 | 17 | 25 | 17 | 9 | 12 | 320 | 17 | 1 | 122 | 87 | 0 | 24 | 1 | 52 | 17 | 318 | 0 | 0 |  | 656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 8 | 15 | 17 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 265 | 1 | 0 | 42 | 0 | 50 | 0 | 0 | 25 | 290 | 155 | 0 | 0 | 0 | 1 | 35 | 0 | 0 | 417 | 0 | 0 | 0 | 2 |  | 4452 | 2503 | 6955 | 2913 | 656 | 1263 | 0 | 1086 | 867 | 30 | 0 | 55 | 80 | 5 | 0 | 87.28
18:00 | 0 | 0 | 0 | 0 | 200 | 71 | 0 | 404 | 350 |  | 0 | 225 | 0 | 9 | 17 | 15 | 0 | 0 | 0 | 10 | 33 | 32 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 0 | 22 | 14 | 25 | 33 | 8 | 0 | 0 | 30 | 0 | 0 | 8 | 150 | 0 | 0 | 0 |  | 12 | 32 | 51 | 10 | 0 | 19 | 0 | 32 | 0 | 0 | 0 | 0 | 330 | 206 | 8 | 0 | 32 | 5 | 0 | 51 | 0 | 13 | 8 | 19 | 11 | 33 | 15 | 82 | 96 | 0 | 22 | 0 | 30 | 31 | 53 | 42 | 0 | 0 | 64 | 0 | 0 | 0 | 18 | 26 | 10 | 0 | 22 | 0 | 0 | 32 | 0 | 0 | 46 | 0 | 35 | 0 | 12 | 22 | 63 | 420 | 47 | 35 | 17 | 0 | 210 | 17 | 44 | 17 | 9 | 12 | 400 | 17 | 0 | 162 | 89 | 0 | 17 | 0 | 53 | 17 | 378 | 0 | 0 |  | 869 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 8 | 25 | 17 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 17 | 0 | 74 | 0 | 113 | 0 | 0 | 75 | 350 | 220 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 450 | 0 | 0 | 0 | 0 |  | 5354 | 3144 | 8498 | 3339 | 869 | 1408 | 0 | 1657 | 960 | 30 | 0 | 153 | 82 | 0 | 0 | 87.28
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 0 | 200 | 71 | 0 | 378 | 320 |  | 0 | 225 | 0 | 32 | 27 | 15 | 0 | 0 | 0 | 30 | 33 | 32 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 0 | 22 | 27 | 25 | 33 | 8 | 0 | 0 | 30 | 0 | 0 | 17 | 151 | 0 | 0 | 0 |  | 12 | 32 | 39 | 10 | 0 | 43 | 0 | 33 | 0 | 0 | 0 | 0 | 290 | 196 | 8 | 0 | 35 | 5 | 0 | 51 | 0 | 0 | 8 | 20 | 11 | 33 | 15 | 82 | 100 | 0 | 22 | 0 | 30 | 31 | 53 | 46 | 0 | 0 | 64 | 0 | 0 | 0 | 18 | 26 | 10 | 0 | 22 | 0 | 0 | 32 | 0 | 0 | 46 | 0 | 35 | 0 | 12 | 51 | 72 | 420 | 47 | 35 | 17 | 0 | 135 | 17 | 17 | 0 | 8 | 12 | 400 | 17 | 0 | 162 | 89 | 0 | 17 | 0 | 53 | 17 | 333 | 0 | 0 |  | 870 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 40 | 184 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 8 | 24 | 17 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 17 | 0 | 94 | 0 | 113 | 0 | 0 | 75 | 430 | 220 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 511 | 0 | 0 | 0 | 0 |  | 5189 | 3430 | 8619 | 3248 | 870 | 1383 | 0 | 1778 | 1101 | 30 | 0 | 127 | 82 | 0 | 0 | 87.24
19:30 | 0 | 0 | 0 | 0 | 200 | 71 | 0 | 397 | 350 |  | 0 | 225 | 0 | 34 | 34 | 15 | 0 | 0 | 0 | 32 | 33 | 32 | 0 | 0 | 0 | 0 | 54 | 17 | 35 | 0 | 22 | 27 | 25 | 33 | 8 | 0 | 0 | 30 | 0 | 0 | 17 | 151 | 0 | 0 | 0 |  | 12 | 32 | 17 | 10 | 0 | 44 | 0 | 29 | 0 | 0 | 0 | 0 | 285 | 195 | 8 | 0 | 35 | 5 | 0 | 51 | 0 | 0 | 8 | 20 | 11 | 33 | 15 | 82 | 103 | 0 | 22 | 0 | 30 | 31 | 53 | 46 | 0 | 0 | 64 | 0 | 0 | 0 | 18 | 27 | 10 | 0 | 22 | 0 | 0 | 32 | 0 | 0 | 56 | 0 | 35 | 0 | 12 | 17 | 72 | 420 | 47 | 35 | 17 | 0 | 135 | 17 | 17 | 0 | 8 | 12 | 400 | 17 | 0 | 162 | 89 | 0 | 17 | 0 | 53 | 17 | 334 | 0 | 0 |  | 870 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 40 | 183 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 8 | 0 | 17 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 283 | 17 | 0 | 94 | 0 | 113 | 0 | 0 | 75 | 430 | 220 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 524 | 0 | 10 | 0 | 0 |  | 5181 | 3434 | 8615 | 3264 | 870 | 1416 | 0 | 1748 | 1124 | 30 | 0 | 81 | 82 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 0 | 200 | 72 | 0 | 386 | 353 |  | 0 | 225 | 0 | 34 | 34 | 15 | 0 | 0 | 0 | 33 | 33 | 32 | 0 | 0 | 0 | 0 | 54 | 17 | 45 | 0 | 22 | 27 | 25 | 33 | 8 | 0 | 0 | 30 | 0 | 0 | 17 | 150 | 0 | 0 | 0 |  | 12 | 32 | 17 | 10 | 0 | 44 | 0 | 33 | 0 | 0 | 0 | 0 | 270 | 184 | 8 | 0 | 35 | 5 | 0 | 51 | 0 | 0 | 8 | 20 | 11 | 33 | 15 | 80 | 104 | 0 | 22 | 0 | 30 | 31 | 53 | 46 | 0 | 0 | 65 | 0 | 0 | 0 | 18 | 26 | 10 | 0 | 22 | 0 | 0 | 32 | 0 | 0 | 46 | 0 | 35 | 0 | 12 | 24 | 73 | 420 | 47 | 17 | 17 | 0 | 135 | 17 | 17 | 0 | 8 | 12 | 400 | 17 | 0 | 162 | 89 | 0 | 17 | 0 | 52 | 17 | 320 | 0 | 0 |  | 869 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 32 | 184 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 8 | 0 | 17 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 301 | 17 | 0 | 94 | 0 | 113 | 0 | 0 | 75 | 430 | 220 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 524 | 0 | 34 | 0 | 0 |  | 5126 | 3469 | 8595 | 3215 | 869 | 1442 | 0 | 1730 | 1148 | 30 | 0 | 81 | 80 | 0 | 0 | 87.25
21:00 | 0 | 0 | 0 | 0 | 200 | 72 | 0 | 394 | 358 |  | 0 | 225 | 0 | 34 | 34 | 15 | 0 | 0 | 0 | 34 | 33 | 32 | 0 | 0 | 0 | 0 | 54 | 17 | 55 | 22 | 22 | 27 | 25 | 33 | 8 | 0 | 0 | 30 | 0 | 0 | 17 | 151 | 0 | 0 | 0 |  | 12 | 32 | 17 | 10 | 0 | 44 | 0 | 33 | 0 | 0 | 0 | 0 | 270 | 183 | 8 | 0 | 35 | 5 | 0 | 51 | 0 | 0 | 8 | 21 | 11 | 33 | 15 | 82 | 110 | 0 | 22 | 0 | 30 | 31 | 53 | 46 | 0 | 0 | 64 | 40 | 0 | 0 | 18 | 26 | 10 | 0 | 22 | 0 | 0 | 32 | 0 | 0 | 46 | 0 | 35 | 0 | 12 | 17 | 73 | 418 | 47 | 17 | 17 | 0 | 135 | 17 | 17 | 0 | 8 | 12 | 400 | 17 | 0 | 162 | 107 | 0 | 17 | 0 | 51 | 17 | 320 | 0 | 0 |  | 870 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 162 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 8 | 0 | 18 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 304 | 17 | 0 | 94 | 0 | 113 | 0 | 0 | 75 | 400 | 160 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 477 | 0 | 57 | 0 | 0 |  | 5228 | 3323 | 8551 | 3228 | 870 | 1431 | 0 | 1735 | 1094 | 30 | 0 | 81 | 82 | 0 | 0 | 87.24
22:00 | 0 | 0 | 0 | 0 | 200 | 72 | 0 | 396 | 305 |  | 0 | 225 | 0 | 29 | 19 | 15 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 55 | 22 | 22 | 27 | 20 | 33 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 151 | 0 | 0 | 0 |  | 12 | 0 | 0 | 10 | 0 | 44 | 0 | 36 | 0 | 0 | 0 | 0 | 270 | 183 | 8 | 0 | 35 | 5 | 0 | 51 | 0 | 0 | 8 | 20 | 11 | 33 | 15 | 80 | 109 | 0 | 22 | 0 | 30 | 31 | 53 | 46 | 0 | 0 | 65 | 84 | 0 | 0 | 18 | 26 | 10 | 0 | 22 | 8 | 0 | 32 | 0 | 0 | 46 | 0 | 35 | 0 | 12 | 17 | 65 | 403 | 47 | 0 | 17 | 0 | 135 | 17 | 17 | 0 | 8 | 12 | 370 | 17 | 0 | 108 | 107 | 0 | 17 | 0 | 53 | 17 | 321 | 0 | 0 |  | 869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 8 | 0 | 20 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 17 | 0 | 94 | 0 | 113 | 0 | 0 | 75 | 340 | 160 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 464 | 0 | 102 | 0 | 0 |  | 4906 | 3119 | 8025 | 3119 | 869 | 1433 | 0 | 1428 | 1066 | 30 | 0 | 0 | 80 | 0 | 0 | 87.23
23:00 | 0 | 0 | 0 | 0 | 200 | 72 | 0 | 380 | 357 |  | 0 | 225 | 0 | 0 | 12 | 9 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 35 | 22 | 22 | 27 | 20 | 33 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 151 | 0 | 0 | 0 |  | 12 | 0 | 0 | 10 | 0 | 19 | 0 | 39 | 0 | 0 | 0 | 0 | 265 | 183 | 8 | 0 | 35 | 5 | 0 | 51 | 0 | 0 | 8 | 20 | 11 | 33 | 15 | 76 | 110 | 0 | 22 | 0 | 30 | 31 | 53 | 46 | 70 | 0 | 40 | 84 | 0 | 0 | 19 | 26 | 10 | 0 | 22 | 8 | 0 | 32 | 0 | 0 | 46 | 0 | 35 | 0 | 12 | 17 | 16 | 362 | 47 | 0 | 17 | 0 | 135 | 17 | 17 | 0 | 8 | 12 | 400 | 17 | 0 | 17 | 107 | 0 | 17 | 0 | 49 | 17 | 321 | 0 | 0 |  | 776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 20 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 258 | 17 | 0 | 94 | 0 | 105 | 0 | 0 | 35 | 340 | 160 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 470 | 0 | 121 | 0 | 0 |  | 4741 | 2905 | 7646 | 3066 | 776 | 1505 | 0 | 1102 | 1091 | 30 | 0 | 0 | 76 | 0 | 0 | 87.22
24:00 | 0 | 0 | 0 | 0 | 200 | 72 | 0 | 361 | 336 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 35 | 22 | 22 | 27 | 21 | 33 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 151 | 0 | 0 | 0 |  | 12 | 0 | 0 | 10 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 270 | 183 | 8 | 0 | 35 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 15 | 70 | 110 | 0 | 22 | 0 | 30 | 31 | 53 | 46 | 70 | 0 | 40 | 84 | 0 | 0 | 19 | 26 | 10 | 0 | 22 | 8 | 0 | 0 | 0 | 0 | 41 | 0 | 35 | 0 | 12 | 17 | 0 | 363 | 37 | 0 | 0 | 0 | 51 | 17 | 17 | 0 | 0 | 12 | 400 | 17 | 0 | 17 | 107 | 0 | 17 | 0 | 34 | 15 | 321 | 0 | 0 |  | 729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 35 | 0 | 12 | 0 | 0 | 0 | 340 | 164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 463 | 0 | 153 | 0 | 0 |  | 4450 | 2638 | 7088 | 3055 | 729 | 1488 | 0 | 600 | 1116 | 30 | 0 | 0 | 70 | 0 | 0 | 87.21
KWH | 0 | 0 | 0 | 0 | 3990000 | 1479318 | 0 | 9267200 | 7552000 |  | 0 | 4670000 | 0 | 330240 | 402633 | 109905 | 0 | 0 | 0 | 338880 | 495936 | 205440 | 0 | 0 | 0 | 0 | 396360 | 539674 | 572666 | 178416 | 528000 | 518760 | 597960 | 820400 | 118560 | 0 | 532800 | 384000 | 0 | 0 | 159440 | 3523723 | 0 | 0 | 0 |  | 227760 | 134880 | 127513 | 263400 | 200640 | 488640 | 0 | 753120 | 0 | 0 | 0 | 0 | 7059000 | 4549000 | 100363 | 0 | 400176 | 45120 | 0 | 1006644 | 0 | 18800 | 146875 | 298332 | 231480 | 644400 | 344540 | 1698240 | 2124480 | 0 | 454140 | 11750 | 716000 | 536160 | 700800 | 891000 | 92209 | 0 | 1394400 | 528960 | 0 | 2016840 | 442000 | 481300 | 247320 | 0 | 375072 | 76920 | 0 | 584618 | 51617 | 14913 | 900000 | 0 | 642672 | 122310 | 304320 | 397920 | 480072 | 9052000 | 631200 | 619200 | 388909 | 22078 | 1891855 | 499856 | 975196 | 83220 | 540120 | 303360 | 9160300 | 336960 | 201110 | 1080000 | 2402455 | 0 | 566640 | 184267 | 834240 | 429840 | 8110000 | 18400 | 0 |  | 16877090 | 0 | 0 | 0 | 44160 | 0 | 0 | 0 | 0 | 0 | 132000 | 4037940 | 419300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 324487 | 0 | 138638 | 42928 | 296880 | 0 | 187560 | 0 | 0 | 3900100 | 0 | 0 | 4082918 | 0 | 123877 | 40323 | 0 | 0 | 0 | 0 | 7265490 | 135360 | 0 | 1054560 | 0 | 1357248 | 0 | 25445 | 1071648 | 8204300 | 4360800 | 0 | 0 | 29040 | 434880 | 1095744 | 0 | 0 | 11363950 | 57133 | 435200 | 0 | 534960 |  | 109370233 | 68073959 | 177444192 | 75841994 | 16877090 | 30890624 | 66530 | 25038107 | 23903550 | 916800 | 58723 | 529561 | 1698240 | 1622973 | 0
Fuel Cost | 0 | 0 | 0 | 0 | 4468800 | 1967492.94 | 0 | 9730560 | 8156160 |  | 0 | 5090300 | 0 | 3692083.2 | 5334887.25 | 1456241.25 | 0 | 0 | 0 | 4954425.6 | 6977819.52 | 3330182.4 | 0 | 0 | 0 | 0 | 5041699.2 | 7285599 | 7679451.06 | 133812 | 396000 | 0 | 0 | 0 | 2016705.6 | 0 | 143856 | 103680 | 0 | 0 | 2606844 | 3664671.92 | 0 | 0 | 0 |  | 2972268 | 2249798.4 | 2170271.26 | 3558534 | 2544115.2 | 5653564.8 | 0 | 2507889.6 | 0 | 0 | 0 | 0 | 7694310 | 5276840 | 129468.27 | 0 | 452198.88 | 67228.8 | 0 | 1681095.48 | 0 | 324676 | 1975468.75 | 408714.84 | 173610 | 1127700 | 258405 | 12193363.2 | 2315683.2 | 0 | 617630.4 | 187295 | 980920 | 707731.2 | 1219392 | 1541430 | 106040.35 | 0 | 2705136 | 1206028.8 | 0 | 2037008.4 | 950300 | 717137 | 489693.6 | 0 | 281304 | 58459.2 | 0 | 7980035.7 | 1081892.32 | 308251.71 | 12132000 | 0 | 8901007.2 | 1429803.9 | 3140582.4 | 5435587.2 | 6370555.44 | 8327840 | 7675392 | 8953632 | 4919698.85 | 0 | 22210377.7 | 5443431.84 | 10366333.48 | 1129295.4 | 6962146.8 | 3573580.8 | 8427476 | 4363632 | 2906039.5 | 13705200 | 27339937.9 | 0 | 7400318.4 | 2201990.65 | 12488572.8 | 5660992.8 | 0 | 0 | 0 |  | 50631270 | 0 | 0 | 0 | 459705.6 | 0 | 0 | 0 | 0 | 0 | 1896840 | 4522492.8 | 813442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5373504.72 | 0 | 1889635.94 | 724195.36 | 614541.6 | 0 | 141982.92 | 0 | 0 | 20631529 | 0 | 0 | 4736184.88 | 0 | 158562.56 | 704039.58 | 0 | 0 | 0 | 0 | 7192835.1 | 1819238.4 | 0 | 12475444.8 | 0 | 17237049.6 | 0 | 281167.25 | 13009806.72 | 73920743 | 4448016 | 0 | 0 | 328442.4 | 5101142.4 | 16797755.52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 364607585.36 | 245909568.15 | 610517153.51 | 70754334.2 | 50631270 | 37948191.54 | 1390144.03 | 320860998.44 | 94552272 | 247536 | 704039.58 | 8799123.42 | 12193363.2 | 12435881.1 | 0
Yesterday Day Peak | 0 | 0 | 0 | 0 | 120 | 69 | 0 | 399 | 280 |  | 0 | 225 | 0 | 31 | 17 | 0 | 0 | 0 | 0 | 32 | 16 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 11 | 22 | 17 | 25 | 33 | 8 | 0 | 0 | 30 | 0 | 0 | 13 | 151 | 0 | 0 | 0 |  | 12 | 0 | 0 | 10 | 32 | 13 | 0 | 23 | 0 | 0 | 0 | 0 | 300 | 203 | 0 | 0 | 5 | 0 | 0 | 51 | 0 | 0 | 8 | 17 | 11 | 24 | 15 | 76 | 70 | 0 | 19 | 2 | 30 | 0 | 22 | 44 | 0 | 0 | 64 | 0 | 0 | 218 | 18 | 15 | 10 | 0 | 22 | 0 | 0 | 30 | 0 | 0 | 49 | 0 | 36 | 19 | 12 | 17 | 6 | 414 | 28 | 70 | 17 | 4 | 51 | 32 | 47 | 17 | 63 | 12 | 400 | 17 | 37 | 17 | 91 | 0 | 36 | 30 | 35 | 17 | 342 | 0 | 0 |  | 681 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 8 | 0 | 16 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 145 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 306 | 0 | 0 | 35 | 0 | 49 | 0 | 4 | 95 | 270 | 162 | 0 | 0 | 4 | 69 | 90 | 0 | 0 | 410 | 6 | 0 | 0 | 103 |  | 7748 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 0 | 200 | 71 | 0 | 378 | 320 | 0 | 0 | 225 | 0 | 32 | 27 | 15 | 0 | 0 | 0 | 30 | 33 | 32 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 0 | 22 | 27 | 25 | 33 | 8 | 0 | 0 | 30 | 0 | 0 | 17 | 151 | 0 | 0 | 0 | 0 | 12 | 32 | 39 | 10 | 0 | 43 | 0 | 33 | 0 | 0 | 0 | 0 | 290 | 196 | 8 | 0 | 35 | 5 | 0 | 51 | 0 | 0 | 8 | 20 | 11 | 33 | 15 | 82 | 100 | 0 | 22 | 0 | 30 | 31 | 53 | 46 | 0 | 0 | 64 | 0 | 0 | 0 | 18 | 26 | 10 | 0 | 22 | 0 | 0 | 32 | 0 | 0 | 46 | 0 | 35 | 0 | 12 | 51 | 72 | 420 | 47 | 35 | 17 | 0 | 135 | 17 | 17 | 0 | 8 | 12 | 400 | 17 | 0 | 162 | 89 | 0 | 17 | 0 | 53 | 17 | 333 | 0 | 0 |  | 870 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 40 | 184 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 8 | 24 | 17 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 17 | 0 | 94 | 0 | 113 | 0 | 0 | 75 | 430 | 220 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 511 | 0 | 0 | 0 | 0 |  | 8619 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 0 | 200 | 70 | 0 | 400 | 330 | 0 | 0 | 225 | 0 | 34 | 34 | 15 | 0 | 0 | 0 | 38 | 33 | 32 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 13 | 22 | 27 | 25 | 33 | 50 | 0 | 46 | 30 | 0 | 0 | 25 | 150 | 0 | 0 | 0 | 0 | 12 | 24 | 50 | 10 | 0 | 44 | 0 | 30 | 0 | 0 | 0 | 0 | 300 | 185 | 8 | 0 | 35 | 5 | 0 | 51 | 0 | 30 | 8 | 21 | 11 | 33 | 15 | 152 | 100 | 0 | 22 | 0 | 30 | 31 | 50 | 40 | 110 | 0 | 66 | 86 | 0 | 0 | 18 | 15 | 10 | 0 | 24 | 8 | 100 | 97 | 150 | 50 | 48 | 50 | 35 | 0 | 12 | 50 | 70 | 400 | 47 | 100 | 85 | 0 | 275 | 35 | 68 | 0 | 9 | 12 | 400 | 17 | 0 | 162 | 107 | 0 | 17 |  | 66 | 17 | 320 |  |  |  | 926 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 40 | 70 | 40 | 90 | 24 |  | 0 | 0 | 0 | 20 | 25 | 35 | 0 | 42 | 40 | 8 | 30 | 20 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 170 |  | 0 | 0 | 0 | 50 | 0 | 0 | 350 | 17 | 100 | 95 | 0 | 113 | 0 | 0 | 113 | 520 | 110 |  | 35 |  |  | 113 | 0 |  | 400 |  | 0 | 0
Forecast for Day | 0 | 0 | 0 | 0 | 200 | 70 | 0 | 400 | 330 | 0 | 0 | 225 | 0 | 33 | 34 | 0 | 0 | 0 | 0 | 33 | 16 | 32 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 13 | 22 | 27 | 25 | 33 | 50 | 0 | 46 | 30 | 0 | 0 | 8 | 150 | 0 | 0 | 0 | 0 | 12 | 24 | 0 | 10 | 0 | 32 | 0 | 5 | 0 | 0 | 0 | 0 | 300 | 180 | 8 | 0 | 35 | 5 | 0 | 51 | 0 | 25 | 8 | 21 | 11 | 33 | 15 | 135 | 70 | 0 | 22 | 1.6 | 30 | 31 | 10 | 20 | 110 | 0 | 65 | 50 | 0 | 0 | 18 | 15 | 10 | 0 | 22 | 8 | 0 | 30 |  | 0 | 46 | 0 | 35 | 20 | 12 | 17 | 6 | 400 | 17 | 90 | 17 | 5 | 51 | 35 | 51 | 0 | 9 | 12 | 400 | 17 | 50 | 17 | 107 | 0 | 17 | 30 | 24 | 17 | 320 |  |  |  | 831 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 8 | 0 | 20 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 17 | 0 | 35 | 0 | 34 | 0 | 8 | 35 | 400 | 110 |  | 0 | 6 | 100 | 35 | 0 |  | 400 | 30 | 0 | 0 | [5 empty] | g | h | o | c | h | t | s
Generation at 08:00(Today) | 0 | 0 | 0 | 0 | 200 | 65 | 0 | 400 | 356 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 22 | 27 | 21 | 33 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 10 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 340 | 224 | 8 | 0 | 32 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 15 | 72 | 111 | 0 | 22 | 0 | 30 | 31 | 53 | 45 | 112 | 0 | 64 | 50 | 0 | 0 | 19 | 18 | 10 | 0 | 21 | 8 | 0 | 0 | 0 | 0 | 45 | 0 | 31 | 6 | 12 | 17 | 0 | 369 | 17 | 0 | 0 | 1 | 50 | 18 | 34 | 0 | 0 | 12 | 400 | 17 | 9 | 17 | 107 | 0 | 1 | 8 | 25 | 0 | 380 | 0 | 0 | 0 | 611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 393 | 0 | 0 | 2 | 0 | 34 | 0 | 1 | 20 | 260 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 401 | 2 | 200 | 0 |  | 0 |  |  |  | 106.7326 | 16.8771 | 25.6929 | 23.9035 | 0.9168 | 1.6982 | 1.623
177.4442
| Minimum Generation |  | 6203 | 5:00
| Highest Generation |  | 8619 | 19:00
| Day Peak Generation |  | 7748 | 12:00
| Evening Peak Generation |  | 8619 | 19:00
| HVDC Max Flow |  | 870 | 19:00
| HVDC EvPeak Flow |  | 870 | 19:00
| Load factor L.F |  | 85.78% | [161 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2022-12-24
Till now the maximum generation is : - |  |  |  | 14782 | 21:00 | Hrs on | 2022-04-16
The Summary of Yesterday's |  |  | 2022-12-23 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 7748 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 5766
Evening Peak Generation : |  |  | 8619 | MW Hour : | 19:00 | Available Max Generation : |  | 10209
E.P. Demand (at gen end) : |  |  | 8619 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 9500
Maximum Generation : |  |  | 8619 | MW Hour : | 19:00 | Reserve(Generation end) |  | 709
Total Gen. (MKWH) : |  |  | 177.4442 | System Load Factor : | 85.78% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 346 | MW at | 20:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2022-12-24
Actual : |  | 87.15 | Ft.(MSL) , | Rule curve : | 103.9 | Ft.( MSL )
Gas Consumed : |  | Total = | 797.34 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 108702525.74
: |  |  | Coal : | 94552272 | Oil : | 331754305.47 | Total : | 535009103.21
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 0 | 0:00 | 3362.0451 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 952.4089 |  |  | 0 | 0%
Khulna Area |  | 0 | 0:00 | 1257.1007 |  |  | 0 | 0%
Rajshahi Area |  | 0 | 0:00 | 1115.3614 |  |  | 0 | 0%
Cumilla Area |  | 0 | 0:00 | 949.4759 |  |  | 0 | 0%
Mymensingh Area |  | 0 | 0:00 | 784.409 |  |  | 0 | 0%
Sylhet Area |  | 0 | 0:00 | 350.5967 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 285.7977 |  |  | 0 | 0%
Rangpur Area |  | 0 | 0:00 | 619.3421 |  |  | 0 | 0%
Total |  | 0 |  | 9676.5375 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1, 2
2) Ghorasal-3, 4
3) Ashuganj-5
4) Baghabari-70,100 MW
5) Raozan unit-1 & 2
6) Siddhirganj 210 MW .
7) Shajibazar 330 MW
8) Sirajganj-2
9) Bibiana-II 341 MW CCPP (Summit)
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
08:17 |  | Maniknagar 230/132kV S/S Auto Transformer-02 (715T) LT Scheduled S/D Due to Oil leakage maintenance & Oil
centrifuging work.
08:18 |  | Maniknagar 230/132kV S/S Auto Transformer-02 (715T) HT Scheduled S/D Due to Oil leakage maintenance & Oil
centrifuging work.
08:20 |  | Maniknagar-Siddhirganj 230kV Ckt-2 Scheduled S/D from Maniknagar 230/132kV end Due to Oil leakage maintenance
& Oil centrifuging work.
08:21 | 16:37 | Rampura 230/132kV S/S Auto Transformer - 03 LT Scheduled S/D Due to Annual Maintenance.
08:21 | 16:37 | Rampura 230/132kV S/S Auto Transformer - 03 HT Scheduled S/D Due to Annual Maintenance.
08:22 | 16:09 | Savar 132/33kV S/S 132kV Manikganj PS-Savar Ckt-2 Scheduled S/D Due to For CB site DS dismantling,
PI Installation and loop connection of MPGL-2 due to double bus conversion.
08:27 | 15:57 | Jamalpur United (20MW)- Sherpur 132kV Ckt-2 Scheduled S/D from Sherpur 132/33kV end Due to Annual Maintenance.
08:32 | 16:32 | Purbasadipur-Saidpur 132kV Ckt-2 Scheduled S/D from Purbasadipur 132/33kV end Due to Annual Maintenance and
from Saidpur 132/33kVend.
08:33 | 15:53 | Pabna 132/33kV S/S T-1 LT Scheduled S/D Due to Annual maintenance. |  |  |  |  | 23 MW load interrup.
08:34 | 15:52 | Pabna 132/33kV S/S T-1 HT Scheduled S/D Due to Annual maintenance.
08:48 |  | Ashuganj-Ghorasal 132kV ckt-1 SD for A/M work by Narsingdi S/S.
08:49 | 15:52 | Mahasthangar-Palashbari 132kV Ckt-1 Scheduled S/D from Mahasthangarh 132/33kV end Due to Annual
Maintenance work and from Palashbari 132/33kV end Due to Annual maintenance.
08:50 | 13:55 | Agargaon 230/132kV S/S 132kV Transformer-1 (405T1) LT Scheduled S/D Due to Relay Testing.
08:56 | 16:34 | Kodda 132/33kV S/S Tr-2 (416T) HT Scheduled S/D Due to Annual maintenance.
08:56 | 16:36 | Kodda 132/33kV S/S Tr-2 (416T) LT Scheduled S/D Due to Annual maintenance.
09:04 | 14:36 | Jashore-Noapara 132kV Ckt-2 Scheduled S/D from Noapara 132/33kV end Due to Annual Maintenance work.
09:05 | 13:55 | Agargaon 230/132kV S/S 132kV Transformer-1 (405T1) HT Scheduled S/D Due to Relay Testing.
09:08 | 12:43 | Chattak-Sylhet 132 kV Ckt-2 Scheduled S/D from Chhatak 132/33kV end Due to annual maintenance and from Sylhet
132/33kV end Due to Annual Maintenance purpose.
09:10 | 14:38 | Shahjibazar 132/33kV S/S TR-02 HT Scheduled S/D Due to S/D taken by SPMD for relay testing.
09:10 | 15:27 | Shahjibazar 132/33kV S/S TR-02 LT Scheduled S/D Due to S/D taken by SPMD for relay testing.
09:10 | 14:58 | Bog-Sherpur 132/33kV S/S Transformer-1 (404T) HT Scheduled S/D.
09:10 | 15:00 | Bog-Sherpur 132/33kV S/S Transformer-1 (404T) LT Scheduled S/D.
09:49 | 15:31 | Mymensingh 132/33kV S/S Transformer-3 (424T) LT Scheduled S/D Due to S/D due to annual Maintenance work purposes.
09:49 | 15:30 | Mymensingh 132/33kV S/S Transformer-3 (424T) HT Scheduled S/D Due to S/D due to annual Maintenance work purposes.
10:16 |  | Joydebpur 132/33kV S/S GT-3 LT Tripped showing Protection Trip GIS MCB Trip relays. |  |  |  |  | 14 MW load interrup.
10:49 | 14:58 | Tongi 230/132/33kV S/S Tongi-Mill Gate Ckt-2 Project Work S/D Due to Relay Testing Work by G2G project.
10:50 | 11:08 | Gollamari 132/33kV S/S Tr-1 LT Scheduled S/D Due to SAS commission check.
10:51 | 11:07 | Gollamari 132/33kV S/S Tr-1 HT Scheduled S/D Due to SAS commission check.
11:18 | 11:31 | Gollamari 132/33kV S/S Tr-2 LT Scheduled S/D Due to SAS commission check.
11:19 | 11:31 | Gollamari 132/33kV S/S Tr-2 HT Scheduled S/D Due to SAS commission check.
11:50 | 17:50 | Ghorasal- Ishwardi 230 kV Ckt-1 Scheduled S/D from Ishurdi 230/132kV end Due to A/m work.
12:49 | 15:28 | Savar 132/33kV S/S Main Bus Scheduled S/D Due to For CB site DS dismantling, PI Installation and loop connection of
MPGL-2 due to double bus conversion.
| 13:55 | Agargaon 230/132kV S/S 132kV Transformer-1 (405T1) HT is restored.
| 13:55 | Agargaon 230/132kV S/S 132kV Transformer-1 (405T1) LT is restored.
13:56 | 18:03 | Agargaon 230/132kV S/S 132kV Transformer-2 (415T2) LT Scheduled S/D Due to Tandelta test by SPMD.
13:58 | 18:00 | Agargaon 230/132kV S/S 132kV Transformer-2 (415T2) HT Scheduled S/D Due to Tandelta test by SPMD.
14:54 | 15:43 | Jashore-Noapara 132kV Ckt-2 Tripped from Jashore 132/33kV end showing distance relay relays Due to PT MCB trip.
| 15:02 | Bibiana 400/230kV S/S Summit GTG is restored.
| 15:36 | Aminbazar-Airport(Old) 230kV Ckt-2 is restored.
| 17:55 | Barapukuria S/S-P/S 230 kV Ckt-2 is restored.
| 17:58 | Sirajganj unit-2 GT sync.
| 18:50 | Barishal 132/33kV S/S 132 kv GTPS is restored.
20:10 |  | Sirajganj unit-2 GT SD.
07:11 |  | Shahmirpur 132/33kV S/S 416T LT Scheduled S/D Due to Annual Maintenance.
7:12 |  | Shahmirpur 132/33kV S/S 416T HT Scheduled S/D Due to Annual Maintenance.
07:38 |  | Shikalbaha 230/132kV S/S Hathazari-02 Project Work S/D.
07:48 |  | Hathazari 230/132/33kV S/S Shikolbaha-02 Project Work S/D Due to Development Work.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2022-12-23 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Line O/L
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 200 | 3990000 | Machine problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 71 | 1479318 | Machine problem
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 378 | 9267200 | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 320 | 7552000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 4670000 | GT-2 S/D due to Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 32 | 330240 | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 27 | 402633 | Fuel shortage
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 15 | 109905 | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 178416 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 30 | 338880 | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 33 | 495936 | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 396360
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 32 | 205440 | High Voltage
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 35 | 539674 | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 572666 | Fuel shortage
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 49 | 1046760 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 597960 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 820400
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 8 | 118560 | High Voltage
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 32 | 584618 | Fuel shortage
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 51617 | Fuel conservation
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 0 | 14913 | Fuel conservation
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Fuel conservation
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 35 | 642672 | Fuel shortage
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 35 | 619200 | High Voltage
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 17 | 336960 | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 1080000
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 184267
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 429840 | Fuel shortage
| Dhaka area Total |  |  |  | 5847 | 1900 | 37056435
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Machine problem
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 17 | 159440 | Machine problem
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 122310
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 43 | 488640 | Engine problem
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 30 | 916800 | Low water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 151 | 3523723
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 17 | 388909 | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 32 | 134880 | Fuel shortage
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 39 | 127513 | High Voltage
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 10 | 263400 | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 12 | 304320 | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 0 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 33 | 753120
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 200640 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 22078
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 135 | 1891855 | Transformer O/L
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 17 | 499856 | Fuel shortage
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 17 | 975196 | Transformer O/L
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 303360 | High Voltage
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 89 | 2402455 | Fuel shortage
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 18400 | On test.
| Chattogram area Total |  |  |  | 2382 | 654 | 13496895
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 196 | 4549000 | FGMO
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 0 | 0 | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 290 | 7059000 | FGMO
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 333 | 8110000 | FGMO
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 35 | 400176 | Gas shortage
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 5 | 45120 | Gas shortage
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 100363 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1006644
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 72 | 480072 | Fuel shortage
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 18800 | Engine problem
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Machine problem
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 51 | 397920 | Fuel shortage
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 298332 | Engine problem
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 231480
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 82 | 1698240
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 644400
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 8 | 146875 | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 15 | 344540 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Fuel conservation
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 83220 | Fuel shortage
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 8 | 540120 | Fuel shortage
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 566640 | Engine problem
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 53 | 834240 | Fuel shortage
| Cumilla Area Total |  |  |  | 3285 | 1288 | 27555182
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 100 | 2124480 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 454140 | Gas shortage
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 11750
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 46 | 900000 | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 47 | 631200 | Fuel shortage
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 201110
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 227760 | Engine problem
| Mymensingh Area Total |  |  |  | 614 | 227 | 4550440
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 30 | 716000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 31 | 536160 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 92209 | Gas shortage
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 700800
| Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 46 | 891000
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 0 | 76920 | Engine problem
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 64 | 1394400
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 0 | 528960 | Gas line Maint.
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 0 | 2016840 | Under maint.
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 442000
| Sylhet 50MW PP (EPL) |  | NENP | 27*2 | 50 | 26 | 481300 | Gas shortage
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 22 | 375072
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 0 | 0 | Under maint.
104 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 420 | 9052000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 247320
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 400 | 9160300
| Sylhet Area Total |  |  |  | 2477 | 1120 | 26711281
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Fuel shortage
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 870 | 16877090
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 16 | 44160 | Fuel shortage
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Under maint.
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 40 | 132000
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Fuel conservation
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 135360 | Fuel shortage
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Fuel shortage
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 434880
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 0 | 0 | 0 | On test.
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 0 | 0 | 511 | 11363950 | On test.
| Khulna Area Total |  |  |  | 2384 | 1454 | 28987440
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Line O/L
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 20 | 419300 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 184 | 4037940
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 430 | 8204300 | Line O/L & Unit-2 Under maint.
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 4360800
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Line O/L
| Barisal 307 MW |  | BCPCL | 0 | 0 | 0 | 435200 | On test.
| Barisal Area Total |  |  |  | 1958 | 854 | 17457540
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Fuel shortage
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contract Expired
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 50 | 324487
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | High Voltage
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 180 | 4082918 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 164200
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 278 | 7265490 | Gas shortage
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 24 | 42928 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 17 | 296880 | Engine problem
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 187560 | Engine problem
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 8 | 138638 | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Line O/L
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Fuel conservation
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 94 | 1054560 | High Voltage
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 75 | 1071648 | High Voltage
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 29040
| Adani Power Jharkhanda Ltd |  | Import | 0 | 0 | 0 | 0 | On test.
| Rajshahi Area Total |  |  |  | 2129 | 734 | 14658349
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 160 | 3900100 | Machine problem
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 1357248
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 25445
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 115 | 1095744
| Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 57133
| Teesta Solar Limited |  | BPCL | 16*12.5 | 0 | 0 | 534960
| Rangpur Area Total |  |  |  | 750 | 388 | 6970630
| Total |  |  |  | 21826 | 8619 | 177444192
| Eastern Grid Total |  |  |  | 14605 | 5189 | 109370233
| Western Grid Total |  |  |  | 7221 | 3430 | 68073959
| National Grid Total |  |  |  | 21826 | 8619 | 177444192
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2022-12-23
| (a) ENTIRE EASTERN GRID : |  | 5460.45 | MW | (b) ENTIRE WESTERN GRID : |  | 2714.69 | MW
| i) Dhaka area |  | 2785.35 | MW | i) Khulna area |  | 1019.8 | MW
| ii) Chittagong area |  | 924.1 | MW | ii) Rajshahi area |  | 853.1 | MW
| iii) Comilla area |  | 718 | MW | iii) Barisal area |  | 239.79 | MW
| iv) Mymensingh area |  | 694 | MW | iv) Rangpur area |  | 602 | MW
| v) Sylhet area |  | 339 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 8175.14 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | Chhatak | 19 | 19:00 | Kamrangirchar | 54 | 12:00 | Natore | 86 | 18:00 | Shitalakhya | 78 | 00:00
2 | AKSML | 91 | 03:00 | Chowmuhani | 122 | 19:30 | Kaptai | 3.2 | 18:00 | Nawabganj | 26.8 | 21:00 | Sholosohor | 18 | 12:00
3 | Aftabnagar | 22 | 13:00 | Chuadanga | 65 | 18:00 | Kazla | 70 | 12:00 | Netrakona | 88 | 18:30 | Shyampur | 156 | 11:00
4 | Agargaon | 48 | 13:00 | Coxsbazar | 84 | 18:00 | Keranigonj | 24 | 12:00 | New | 43.4 | 12:00 | Siddhirganj | 64 | 00:00
5 | Agrabad | 36 | 18:00 | Cumilla(N) | 101 | 20:00 | Khagrachori | 22 | 18:00 | Niamatpur | 59 | 18:00 | Sirajganj | 65 | 18:30
6 | Amnura | 47 | 10:00 | Cumilla(S) | 82 | 18:00 | Khulna | 71 | 19:30 | Noapara | 29 | 19:30 | Sonargaon | 63 | 00:00
7 | Ashuganj | 53 | 17:00 | Daudkandi | 84 | 20:00 | Khulshi | 132 | 21:00 | PHP | 2 | 03:00 | Sreemongol | 37 | 18:00
8 | BIPTC | N/A | N/A | Dhaka | 14 | 12:00 | Kishoreganj | 92 | 21:00 | Pabna | 66 | 18:30 | Srinagar | 25.85 | 13:00
9 | BSRM | 154 | 03:00 | Dhamrai | 62 | 00:00 | Kodda | 172 | 12:00 | Palashbari | 80 | 18:00 | Sunamganj | 31 | 19:00
10 | Bagerhat | 70 | 20:00 | Dhanmondi | 70 | 12:00 | Kulaura | 26 | 18:00 | Panchagarh | 53 | 18:30 | Sylhet | 85 | 12:00
11 | Bakulia | 56 | 18:00 | Dohazari | 56 | 18:00 | Kurigram | 60 | 18:00 | Patuakhali | 75 | 21:00 | TK | 18.5 | 18:30
12 | Banani | 23 | 13:00 | Faridpur | 88 | 21:00 | Kushtia | 90 | 18:30 | Payra | 0.86 | 18:30 | Tangail | 127 | 18:30
13 | Bangabhaban | 3 | 11:00 | Fatullah | 42 | 00:00 | Lalbag | 56 | 00:00 | Postogola | 29 | 13:00 | Thakurgaon | 64 | 18:30
14 | Barapukuria | 40 | 00:00 | Fenchuganj | 27 | 18:30 | Lalmonirhat | 19 | 18:00 | Purbachal | 11 | 13:00 | Tongi | 84 | 12:00
15 | Barguna | 12 | 19:30 | Feni | 77 | 13:00 | Madanganj | 30 | 00:00 | Purbasadipur | 99 | 18:30 | Ullon | 31 | 13:00
16 | Barishal | 66 | 13:00 | GPH | 90 | 07:00 | Madaripur | 56 | 18:30 | Rahanpur_I | 3.6 | 06:00 | Uttara | 48 | 12:00
17 | Barishal-230 | 48 | 19:30 | Ghorashal | 50 | 20:00 | Madartek | 52 | 13:00 | Rahim | 24 | 00:00 | UttaraNew | 11 | 12:00
18 | Baroaulia | 57 | 00:00 | Goalpara | 19 | 13:00 | Madunaghat | 39 | 22:00 | Rajbari | 40 | 18:00 | Zigatola | 31 | 13:00
19 | Baroirhat | 31 | 18:00 | Gollamari | 26 | 00:00 | Magura | 40 | 18:00 | Rajendrapur | 78 | 18:30
20 | Bashundhara | 99 | 13:00 | Gopalganj | 70.8 | 18:00 | Mahasthangarh | 40 | 18:30 | Rajshahi | 89 | 20:00
21 | BashundharaCement | 0 | 00:00 | Gulshan | 54 | 13:00 | Manikganj | 59 | 19:00 | Rajshahi-230 | 19 | 13:00
22 | Beanibazar | 37 | 18:00 | Halishahar | 49.5 | 16:00 | Maniknagar | 35 | 13:00 | Ramganj | 60 | 18:30
23 | Benapole | 36 | 08:00 | HaripurSBU | 128 | 00:00 | Matarbari | 26 | 18:30 | Rampur | 15 | 00:00
24 | Bhaluka | 88 | 00:00 | Hasnabad | 62 | 20:00 | Matuail | 40 | 00:00 | Rangamati | 8 | 12:00
25 | Bhandaria | 32 | 19:30 | Hathazari | 41 | 19:30 | Millgate | 44 | 12:00 | Rangpur | 94 | 19:00
26 | Bhangura | 21 | 18:00 | Ishurdi | 46 | 21:00 | Mirpur | 81 | 12:00 | Ruppur | 3.2 | 15:00
27 | Bheramara(GK) | 35 | 18:30 | Jaldhaka | 45 | 18:00 | Mirsorai | 2 | 00:00 | SSM | 12 | 03:00
28 | Bhulta | 178 | 00:00 | Jamalpur | 98 | 18:30 | Mithapukur | 23 | 18:00 | Saidpur | 67 | 12:00
29 | Bog-Sherpur | 44 | 18:00 | Jashore | 87 | 13:00 | Modern | 0 | 00:00 | Satkhira | 79 | 18:30
30 | Bogura | 91 | 19:00 | Jhenaidah | 84 | 18:00 | Mogbazar | 75 | 12:00 | Satmasjid | 66 | 13:00
31 | Borhanuddin | 33 | 00:00 | Joydebpur | 88 | 19:00 | Mongla | 20 | 00:00 | Savar | 116 | 11:00
32 | Brahmanbaria | 98 | 20:00 | Joypurhat | 36 | 13:00 | Motijheel | 18 | 12:00 | Shahjadpur | 63 | 18:00
33 | Cantonment | 82 | 13:00 | Juldah | 14.9 | 11:00 | Munshiganj | 56 | 00:00 | Shahjibazar | 88 | 18:30
34 | Chandpur | 39 | 20:00 | KSRM | 23 | 10:00 | Mymensingh | 142 | 13:00 | Shahmirpur | 22.3 | 23:00
35 | Chandraghona | 22 | 18:00 | Kabirpur | 149 | 18:30 | Naogaon | 78 | 18:30 | Shariatpur | 46 | 21:00
36 | Chapai | 49 | 12:00 | Kachua | 42 | 18:30 | Narail | 36 | 18:00 | Sherpur | 92 | 18:00
37 | Charsaidpur | 41.5 | 12:00 | Kallyanpur | 60 | 13:00 | Narinda | 30 | 12:00 | Shikalbaha | 20 | 12:00
38 | Chauddagram | 28 | 13:00 | Kalurghat | 14 | 00:00 | Narshingdi | 121 | 21:00 | Shikalbaha-230 | N/A | N/A
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2022-12-23 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 418 | 17:00 | 406 | 12:00 | Gopalganj_I | 429 | 22:00 | 418 | 08:00
| Bhulta | 394 | 18:30 | 386 | 12:00 | Kaliakoir | 398 | 06:00 | 393 | 00:00
| Bibiana | 401 | 07:00 | 393 | 23:00 | Payra | 424 | 01:00 | 418 | 13:00
| BIPTC | 406 | 02:00 | 393 | 18:00 | Rahanpur_I | 418 | 18:30 | 386 | 08:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 241 | 17:00 | 234 | 12:00 | Hasnabad | 239 | 18:30 | 234 | 07:00
| AKSML | 235 | 01:00 | 225 | 11:00 | Hathazari | 236 | 06:00 | 225 | 11:00
| Aminbazar | 241 | 18:30 | 237 | 01:00 | Ishurdi | 243 | 15:00 | 234 | 08:00
| Ashuganj | 245 | 17:00 | 240 | 00:00 | Jhenaidah | 242 | 17:00 | 233 | 08:00
| Baghabari | 240 | 14:00 | 235 | 09:00 | Kaliakoir | 237 | 05:00 | 234 | 00:00
| Barapukuria | 235 | 13:00 | 227 | 00:00 | Keranigonj | 239 | 17:00 | 233 | 03:00
| Barishal | 249 | 23:00 | 244 | 18:00 | Khulna(S) | 244 | 22:00 | 237 | 18:00
| Bheramara | 242 | 17:00 | 232 | 08:00 | Maniknagar | 236 | 17:00 | 231 | 12:00
| Bhulta | 239 | 18:30 | 233 | 12:00 | Meghnaghat | 242 | 14:00 | 237 | 08:00
| Bibiana | 242 | 17:00 | 234 | 05:00 | Mirsorai | 237 | 18:30 | 226 | 11:00
| BIPTC | 244 | 17:00 | 231 | 08:00 | Rajshahi | 245 | 15:00 | 236 | 11:00
| Bogura | 238 | 14:00 | 231 | 08:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 251 | 15:00 | 248 | 00:00 | Rampura | 237 | 17:00 | 232 | 12:00
| BSRM | 237 | 17:00 | 228 | 11:00 | Shikalbaha | 241 | 18:30 | 231 | 05:00
| Cumilla(N) | 238 | 18:30 | 232 | 11:00 | Shyampur | 238 | 17:00 | 232 | 11:00
| Fenchuganj | 242 | 14:00 | 237 | 04:00 | Siddhirganj | 239 | 13:00 | 234 | 03:00
| Ghorashal | N/A | N/A | N/A | N/A | Sirajgonj | 238 | 17:00 | 231 | 09:00
| GPH | 236 | 17:00 | 226 | 11:00 | Tongi | 238 | 17:00 | 233 | 04:00
| Haripur | 236 | 14:00 | 231 | 12:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 137 | 17:00 | 133 | 12:00 | Kushtia | 139 | 06:00 | 133 | 11:00
| Agargaon | 140 | 17:00 | 135 | 12:00 | Lalbag | 137 | 06:00 | 134 | 03:00
| Agrabad | 139 | 06:00 | 133 | 09:00 | Lalmonirhat | 137 | 21:00 | 130 | 08:00
| AKS | 138 | 05:00 | 131 | 09:00 | Madanganj | 141 | 18:30 | 135 | 00:00
| Aminbazar | 140 | 18:30 | 135 | 12:00 | Madaripur | 139 | 06:00 | 136 | 00:00
| Amnura | 135 | 00:00 | 128 | 12:00 | Madartek | 137 | 18:30 | 133 | 12:00
| Ashuganj | 140 | 17:00 | 137 | 01:00 | Madunaghat | 138 | 00:00 | 132 | 10:00
| Bagerhat | 139 | 06:00 | 133 | 08:00 | Magura | 139 | 04:00 | 134 | 08:00
| Bakulia | 139 | 07:00 | 134 | 11:00 | Mahasthangarh | 140 | 17:00 | 133 | 08:00
| Banani | 141 | 18:30 | 136 | 12:00 | Manikganj | 133 | 14:00 | 129 | 06:00
| Bangabhaban | 136 | 18:30 | 131 | 12:00 | Maniknagar | 135 | 06:00 | 132 | 11:00
| Barapukuria | 138 | 13:00 | 133 | 00:00 | Matarbari | 131 | 10:00 | 126 | 13:00
| Barguna | 137 | 05:00 | 134 | 12:00 | Matuail | 139.5 | 18:30 | 135 | 00:00
| Barishal | 141 | 04:00 | 131 | 12:00 | Millgate | 141 | 14:00 | 135 | 12:00
| Barishal-230 | 143 | 23:00 | 138 | 18:00 | Mirpur | 139 | 18:30 | 132 | 00:00
| Baroaulia | 140 | 06:00 | 133 | 16:00 | Mithapukur | 140 | 21:00 | 133 | 01:00
| Baroirhat | 139 | 17:00 | 132 | 03:00 | Modern | 137 | 05:00 | 133 | 16:00
| Bashundhara | 141 | 17:00 | 136 | 12:00 | Mogbazar | 138 | 03:00 | 135 | 11:00
| BashundharaCement | 141 | 18:30 | 135 | 00:00 | Mongla | 138 | 06:00 | 133 | 18:00
| Beanibazar | 137 | 17:00 | 133 | 08:00 | Motijheel | 136 | 18:30 | 131 | 12:00
| Benapole | 138 | 04:00 | 132 | 08:00 | Munshiganj | 139 | 18:30 | 135 | 00:00
| Bhaluka | 136 | 00:00 | 128 | 16:00 | Mymensingh | 138 | 05:00 | 119 | 18:00
| Bhandaria | 142 | 06:00 | 138 | 18:00 | Naogaon | 139 | 14:00 | 131 | 08:00
| Bhangura | 142 | 21:00 | 140 | 01:00 | Narail | 138 | 01:00 | 133 | 08:00
| Bheramara | 140 | 17:00 | 132 | 11:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bheramara(GK) | 140 | 17:00 | 133 | 10:00 | Narshingdi | 138 | 14:00 | 133 | 00:00
| Bhulta | 133 | 14:00 | 129 | 00:00 | Natore | 138 | 14:00 | 132 | 08:00
| Bog-Sherpur | 141 | 14:00 | 130 | 10:00 | Nawabganj | 137 | 18:30 | 134 | 02:00
| Bogura | 141 | 19:00 | 136 | 01:00 | Netrakona | 137 | 14:00 | 128 | 16:00
| Bogura-230 | 141 | 14:00 | 136 | 08:00 | New | 141 | 21:00 | 135 | 12:00
| Brahmanbaria | 135 | 13:00 | 132 | 12:00 | Niamatpur | 135 | 00:00 | 129 | 08:00
| Cantonment | 140 | 17:00 | 135 | 12:00 | Noapara | 139 | 06:00 | 134 | 07:00
| Chandpur | 140 | 08:00 | 135 | 14:00 | Pabna | 142 | 14:00 | 136 | 08:00
| Chandraghona | 139 | 07:00 | 133 | 12:00 | Palashbari | 138 | 22:00 | 133 | 18:00
| Chapai | 137 | 21:00 | 130 | 10:00 | Panchagarh | 139 | 21:00 | 125 | 16:00
| Charsaidpur | 141 | 18:30 | 136 | 00:00 | Patuakhali | 137 | 01:00 | 134 | 12:00
| Chauddagram | 140 | 18:30 | 133 | 02:00 | Payra | 140 | 06:00 | 137 | 18:00
| Chhatak | 137 | 22:00 | 133 | 00:00 | PHP | 139 | 07:00 | 132 | 03:00
| Chowmuhani | 138 | 07:00 | 132 | 19:30 | Postogola | 137 | 17:00 | 133 | 02:00
| Chuadanga | 137 | 06:00 | 132 | 08:00 | Purbachal | 142 | 17:00 | 136 | 12:00
| Coxsbazar | 131 | 07:00 | 126 | 12:00 | Purbasadipur | 136 | 13:00 | 126 | 02:00
| Cumilla(N) | 141 | 06:00 | 138 | 00:00 | Rahim | 140 | 18:00 | 136 | 00:00
| Cumilla(S) | 141 | 15:00 | 131 | 12:00 | Rajbari | 136 | 06:00 | 128 | 12:00
| Daudkandi | 139 | 18:30 | 134 | 02:00 | Rajendrapur | 133 | 14:00 | 129 | 00:00
| Dhaka | 137 | 06:00 | 134 | 12:00 | Rajshahi | 136 | 17:00 | 129 | 08:00
| Dhamrai | 139 | 14:00 | 135 | 12:00 | Rajshahi-230 | 136 | 17:00 | 129 | 11:00
| Dhanmondi | 139 | 18:00 | 136 | 12:00 | Ramganj | 139 | 10:00 | 134 | 00:00
| Dohazari | 137 | 18:30 | 130 | 00:00 | Rampur | 137 | 07:00 | 133 | 11:00
| Faridpur | 135 | 06:00 | 128 | 12:00 | Rampura | 137 | 17:00 | 133 | 12:00
| Fatullah | 139 | 18:30 | 135 | 03:00 | Rangamati | 138 | 07:00 | 132 | 11:00
| Fenchuganj | 140 | 18:30 | 135 | 05:00 | Rangpur | 139 | 18:00 | 131 | 08:00
| Feni | 140 | 06:00 | 135 | 02:00 | Ruppur | 140 | 06:00 | 135 | 08:00
| Ghorashal | 141 | 07:00 | 140 | 00:00 | Saidpur | 136 | 05:00 | 130 | 11:00
| Goalpara | 141 | 17:00 | 135 | 08:00 | Satkhira | 138 | 01:00 | 132 | 08:00
| Gollamari | 140 | 14:00 | 134 | 00:00 | Satmasjid | 139 | 17:00 | 135 | 12:00
| Gopalganj | 138 | 06:00 | 134 | 00:00 | Savar | 141 | 18:30 | 133 | 08:00
| Gopalganj-400 | N/A | N/A | N/A | N/A | Shahjadpur | 147 | 13:00 | 141 | 08:00
| Gopalganj_I | 140 | 00:00 | 135 | 02:00 | Shahjibazar | 137 | 00:00 | 134 | 10:00
| Gulshan | 137 | 17:00 | 133 | 11:00 | Shahmirpur | 139 | 18:30 | 132 | 15:00
| Halishahar | 138 | 06:00 | 132 | 11:00 | Shariatpur | 139 | 10:00 | 135 | 00:00
| Haripur | 140 | 18:00 | 136 | 00:00 | Sherpur | 137 | 23:00 | 123 | 16:00
| HaripurSBU | 139 | 17:00 | 136 | 00:00 | Shikalbaha | 140 | 18:30 | 134 | 11:00
| Hasnabad | 137 | 21:00 | 133 | 11:00 | Shikalbaha-230 | 139 | 18:30 | 134 | 11:00
| Hathazari | 140 | 06:00 | 134 | 00:00 | Shitalakhya | 138 | 19:30 | 132 | 11:00
| Ishurdi | 142 | 14:00 | 135 | 08:00 | Sholosohor | 138 | 06:00 | 133 | 11:00
| Jaldhaka | 136 | 21:00 | 128 | 00:00 | Shyampur | 136 | 17:00 | 133 | 01:00
| Jamalpur | 139 | 23:00 | 128 | 16:00 | Shyampur-230 | 138 | 17:00 | 134 | 11:00
| Jashore | 138 | 05:00 | 132 | 12:00 | Siddhirganj | 139 | 13:00 | 136 | 00:00
| Jhenaidah | 140 | 17:00 | 134 | 11:00 | Sirajganj | 141 | 14:00 | 137 | 07:00
| Jhenaidah-230 | 140 | 06:00 | 135 | 08:00 | Sonargaon | 136 | 07:00 | 133 | 04:00
| Joydebpur | 143 | 18:30 | 137 | 01:00 | Sreemongol | 140 | 23:00 | 135 | 11:00
| Joypurhat | 138 | 06:00 | 131 | 08:00 | Srinagar | 136 | 06:00 | 134 | 00:00
| Juldah | 137 | 17:00 | 133 | 04:00 | SSM | 140 | 05:00 | 134 | 13:00
| Kabirpur | 140 | 14:00 | 129 | 04:00 | Sunamganj | 136 | 17:00 | 132 | 10:00
| Kachua | 142 | 18:30 | 132 | 02:00 | Sylhet | 137 | 14:00 | 134 | 12:00
| Kaliakoir | 138 | 06:00 | 132 | 00:00 | Tangail | 136 | 14:00 | 130 | 07:00
| Kallyanpur | 140 | 21:00 | 135 | 01:00 | Thakurgaon | 141 | 21:00 | 126 | 00:00
| Kalurghat | 138 | 07:00 | 133 | 16:00 | TK | 139 | 06:00 | 134 | 11:00
| Kamrangirchar | 138 | 21:00 | 133 | 12:00 | Tongi | 142 | 17:00 | 137 | 04:00
| Kaptai | 136 | 00:00 | 134 | 01:00 | Ullon | 137 | 18:30 | 133 | 12:00
| Kazla | 135 | 07:00 | 132 | 00:00 | Uttara | 140 | 22:00 | 134 | 12:00
| Keranigonj | 137 | 17:00 | 133 | 11:00 | UttaraNew | 140 | 21:00 | 133 | 12:00
| Khagrachori | 137 | 21:00 | 132 | 13:00 | Zigatola | 137 | 06:00 | 133 | 12:00
| Khulna | 140 | 06:00 | 135 | 12:00
| Khulna(S) | 141 | 06:00 | 135 | 18:00
| Khulshi | 137 | 06:00 | 131 | 11:00
| Kishoreganj | 133 | 06:00 | 126 | 18:00
| Kodda | 141 | 13:00 | 128 | 02:00
| KSRM | 137 | 17:00 | 133 | 11:00
| Kulaura | 139 | 21:00 | 136 | 00:00
| Kurigram | 135 | 18:30 | 129 | 00:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2022-12-23
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 414 | 4450 | 2638 | 7088 |  |  |  | QF-LDC-11
0:30 | 442 | 4540 | 2679 | 7219 | Date: | 2022-12-23
1:00 | 470 | 4630 | 2720 | 7350
1:30 | 465 | 4450.5 | 2641 | 7091.5
2:00 | 460 | 4271 | 2562 | 6833
2:30 | 432 | 4147.5 | 2550 | 6697.5 | [5 empty] | Gen. at Eve. Peak | 8619 | 13631 MW (21:00 )
3:00 | 404 | 4024 | 2538 | 6562 | [6 empty] | 19:00
3:30 | 402 | 3938.5 | 2515.5 | 6454 | [5 empty] | Gen. at Day Peak | 7748 | 11805 MW (10:00 )
4:00 | 400 | 3853 | 2493 | 6346 | [6 empty] | 12:00
4:30 | 415 | 3880 | 2394.5 | 6274.5 | [5 empty] | Highest Generation | 8619
5:00 | 430 | 3907 | 2296 | 6203 | [6 empty] | 19:00
5:30 | 438 | 4011 | 2326.5 | 6337.5
6:00 | 446 | 4115 | 2357 | 6472
6:30 | 433 | 4226.5 | 2370 | 6596.5
7:00 | 420 | 4338 | 2383 | 6721
7:30 | 405 | 4487 | 2483 | 6970
8:00 | 390 | 4636 | 2583 | 7219
8:30 | 538 | 4648.5 | 2639 | 7287.5
9:00 | 686 | 4661 | 2695 | 7356
9:30 | 763 | 4589.5 | 2710.5 | 7300
10:00 | 840 | 4518 | 2726 | 7244
10:30 | 740 | 4596.5 | 2693 | 7289.5
11:00 | 640 | 4675 | 2660 | 7335
11:30 | 638 | 4769.5 | 2772 | 7541.5
12:00 | 636 | 4864 | 2884 | 7748
12:30 | 588 | 4909 | 2952.5 | 7861.5
13:00 | 540 | 4954 | 3021 | 7975
13:30 | 510 | 4649.5 | 2874.5 | 7524
14:00 | 480 | 4345 | 2728 | 7073
14:30 | 535 | 4325 | 2620 | 6945
15:00 | 590 | 4305 | 2512 | 6817
15:30 | 590 | 4288.5 | 2441 | 6729.5
16:00 | 590 | 4272 | 2370 | 6642
16:30 | 548 | 4362 | 2436.5 | 6798.5
17:00 | 506 | 4452 | 2503 | 6955
17:30 | 435 | 4903 | 2823.5 | 7726.5
18:00 | 364 | 5354 | 3144 | 8498
18:30 | 432 | 5271.5 | 3287 | 8558.5
19:00 | 500 | 5189 | 3430 | 8619
19:30 | 470 | 5181 | 3434 | 8615
20:00 | 346 | 5126 | 3469 | 8595 |  |  |  | Executive Engineer
20:30 | 391 | 5177 | 3396 | 8573 |  |  |  | Network Operation Division
21:00 | 436 | 5228 | 3323 | 8551
21:30 | 428 | 5067 | 3221 | 8288
22:00 | 420 | 4906 | 3119 | 8025 |  |  |  |  | Page 6 of 7
22:30 | 450 | 4823.5 | 3012 | 7835.5
23:00 | 480 | 4741 | 2905 | 7646
23:30 | 447 | 4595.5 | 2771.5 | 7367
24:00 | 414 | 4450 | 2638 | 7088
13631 MW (21:00 )
11805 MW (10:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2022-12-23 |  | Energy |  | 177444192
[13 empty] | 2022-12-23 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 3055 | 729 | 1488 | 0 | 600 | 1116 | 30 | 0 | 0 | 70 | 0 | 0
0:30 | 3230.5 | 729 | 1459 | 0 | 603 | 1090.5 | 38 | 0 | 0 | 69 | 0 | 0 | Date: | 2022-12-23
1:00 | 3406 | 729 | 1430 | 0 | 606 | 1065 | 46 | 0 | 0 | 68 | 0 | 0
1:30 | 3371.5 | 669 | 1379.5 | 0 | 505 | 1054.5 | 46 | 0 | 0 | 66 | 0 | 0 | [8 empty] | Total Energy | 177.4442 | Total Energy Gen 180.187 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 180.187 MKWHr
2:00 | 3337 | 609 | 1329 | 0 | 404 | 1044 | 46 | 0 | 0 | 64 | 0 | 0 | [8 empty] | Energy not Served | 0
2:30 | 3287.5 | 608.5 | 1268.5 | 0 | 384 | 1042 | 46 | 0 | 0 | 61 | 0 | 0 | [8 empty] | Energy Requirement | 177.4442
3:00 | 3238 | 608 | 1208 | 0 | 364 | 1040 | 46 | 0 | 0 | 58 | 0 | 0
3:30 | 3187.5 | 608 | 1171 | 0 | 345 | 1037.5 | 46 | 0 | 0 | 59 | 0 | 0 | [6 empty] | Shortage
4:00 | 3137 | 608 | 1134 | 0 | 326 | 1035 | 46 | 0 | 0 | 60 | 0 | 0
4:30 | 3159.5 | 608 | 1135 | 0 | 326 | 939 | 46 | 0 | 0 | 61 | 0 | 0
5:00 | 3182 | 608 | 1136 | 0 | 326 | 843 | 46 | 0 | 0 | 62 | 0 | 0
5:30 | 3206.5 | 608.5 | 1205.5 | 0 | 379 | 832 | 46 | 0 | 0 | 60 | 0 | 0
6:00 | 3231 | 609 | 1275 | 0 | 432 | 821 | 46 | 0 | 0 | 58 | 0 | 0
6:30 | 3233.5 | 609 | 1205.5 | 0 | 625.5 | 817 | 46 | 0 | 0 | 57 | 3 | 0 |  |  |  |  | Coal
7:00 | 3236 | 609 | 1136 | 0 | 819 | 813 | 46 | 0 | 0 | 56 | 6 | 0
7:30 | 3267.5 | 609 | 1281.5 | 0 | 852 | 822 | 46 | 0 | 0 | 61 | 31 | 0 |  |  |  | Oil |  |  |  | ,
8:00 | 3299 | 609 | 1427 | 0 | 885 | 831 | 46 | 0 | 0 | 66 | 56 | 0
8:30 | 3255.5 | 608.5 | 1401.5 | 0 | 995.5 | 827.5 | 46 | 0 | 0 | 64 | 89 | 0
9:00 | 3212 | 608 | 1376 | 0 | 1106 | 824 | 46 | 0 | 0 | 62 | 122 | 0
9:30 | 3151 | 608 | 1329.5 | 0 | 1122 | 832 | 46 | 0 | 0 | 61 | 150.5 | 0
10:00 | 3090 | 608 | 1283 | 0 | 1138 | 840 | 46 | 0 | 0 | 60 | 179 | 0
10:30 | 3152.5 | 608 | 1269 | 0 | 1142.5 | 819 | 32.5 | 0 | 0 | 63 | 203 | 0
11:00 | 3215 | 608 | 1255 | 0 | 1147 | 798 | 19 | 0 | 0 | 66 | 227 | 0
11:30 | 3248 | 644.5 | 1247.5 | 0 | 1209.5 | 819 | 24.5 | 17 | 25 | 71 | 252.5 | 0
12:00 | 3281 | 681 | 1240 | 0 | 1272 | 840 | 30 | 34 | 50 | 76 | 278 | 0
12:30 | 3253 | 681 | 1250.5 | 27.5 | 1343.5 | 875 | 30 | 26 | 41 | 78 | 273 | 0
13:00 | 3225 | 681 | 1261 | 55 | 1415 | 910 | 30 | 18 | 32 | 80 | 268 | 0
13:30 | 3225 | 681 | 1261 | 55 | 1415 | 910 | 30 | 18 | 32 | 80 | 268 | 0
14:00 | 3225 | 681 | 1261 | 55 | 1415 | 910 | 30 | 18 | 32 | 80 | 268 | 0
14:30 | 3110.5 | 668 | 1216.5 | 27.5 | 1155.5 | 870 | 30 | 9 | 16 | 78 | 215 | 0
15:00 | 2996 | 655 | 1172 | 0 | 896 | 830 | 30 | 0 | 0 | 76 | 162 | 0
15:30 | 3035 | 655.5 | 1156.5 | 0 | 825.5 | 830 | 30 | 0 | 0 | 76 | 121 | 0
16:00 | 3074 | 656 | 1141 | 0 | 755 | 830 | 30 | 0 | 0 | 76 | 80 | 0
16:30 | 2993.5 | 656 | 1202 | 0 | 920.5 | 848.5 | 30 | 0 | 27.5 | 78 | 42.5 | 0
17:00 | 2913 | 656 | 1263 | 0 | 1086 | 867 | 30 | 0 | 55 | 80 | 5 | 0
17:30 | 3126 | 762.5 | 1335.5 | 0 | 1371.5 | 913.5 | 30 | 0 | 104 | 81 | 2.5 | 0
18:00 | 3339 | 869 | 1408 | 0 | 1657 | 960 | 30 | 0 | 153 | 82 | 0 | 0
18:30 | 3293.5 | 869.5 | 1395.5 | 0 | 1717.5 | 1030.5 | 30 | 0 | 140 | 82 | 0 | 0
19:00 | 3248 | 870 | 1383 | 0 | 1778 | 1101 | 30 | 0 | 127 | 82 | 0 | 0
19:30 | 3264 | 870 | 1416 | 0 | 1748 | 1124 | 30 | 0 | 81 | 82 | 0 | 0
20:00 | 3215 | 869 | 1442 | 0 | 1730 | 1148 | 30 | 0 | 81 | 80 | 0 | 0
20:30 | 3221.5 | 869.5 | 1436.5 | 0 | 1732.5 | 1121 | 30 | 0 | 81 | 81 | 0 | 0
21:00 | 3228 | 870 | 1431 | 0 | 1735 | 1094 | 30 | 0 | 81 | 82 | 0 | 0
21:30 | 3173.5 | 869.5 | 1432 | 0 | 1581.5 | 1080 | 30 | 0 | 40.5 | 81 | 0 | 0
22:00 | 3119 | 869 | 1433 | 0 | 1428 | 1066 | 30 | 0 | 0 | 80 | 0 | 0
22:30 | 3092.5 | 822.5 | 1469 | 0 | 1265 | 1078.5 | 30 | 0 | 0 | 78 | 0 | 0
23:00 | 3066 | 776 | 1505 | 0 | 1102 | 1091 | 30 | 0 | 0 | 76 | 0 | 0
23:30 | 3060.5 | 752.5 | 1496.5 | 0 | 851 | 1103.5 | 30 | 0 | 0 | 73 | 0 | 0 | Max Temp. in Dhaka |  | 24.7° C | 27° C
24:00 | 3055 | 729 | 1488 | 0 | 600 | 1116 | 30 | 0 | 0 | 70 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 180.187 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 180.187 MKWHr
Note on W13: Author:

## Generation
g | 2022-12-23
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 19 | 0 | 0 | [13 empty] | 532800
2 | Karnaphuli Hydro PP Unit-4 & 5 | [10 empty] | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 384000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [6 empty] | 7 | 8 | 8 | 8 | 8 | 13 | 17 |  |  |  | 6 | 8 |  | 17 | 17 | 17 | 17 |  |  | 0 | 159440
| Teknaf 20MW PP (Solartech) | [6 empty] | 1 | 7 | 13 | 17 | 19 | 19 | 19 | 15 | 12 | 5 | 0 | [9 empty] | 122310
6 | Sikalbaha 225MW CCPP (Gas) | 151 | 152 | 151 | 151 | 151 | 151 | 151 | 151 | 151 | 151 | 151 | 151 | 151 | 151 | 151 | 151 | 130 | 150 |  | 151 | 151 | 150 | 151 | 151 | 151 | 151 | 3523723
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [16 empty] | 3 | 51 |  | 39 | 17 | 17 | 17 |  |  | 0 | 127513
12 | Hathazari 100 MW peaking PP | [16 empty] | 21 | 32 |  | 32 | 32 | 32 | 32 |  |  |  | 134880
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 36 | [5 empty] | 12 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 20 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 0 | 388909
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP | [17 empty] | 13 |  | 0 | [5 empty] | 0 | 18800
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | [6 empty] | 18 | 32 | 33 | 32 | 32 | 30 | 32 | 32 | 32 | 32 | 32 | 32 |  | 32 | 32 | 32 | 32 | 32 | 32 | 0 | 584618
19 | Ashuganj 195MW PP (APSCL-United) | [12 empty] | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 100363
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 170 | 170 | 170 | 160 | 160 | 150 | 150 | 140 | 120 | 120 | 120 | 120 | 120 | 190 | 200 | 200 | 150 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 3990000
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 20 | 20 | 20 | 32 | 32 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 400176
33 | Ashuganj 225 MW CCPP | 183 | 184 | 187 | 183 | 184 | 183 | 197 | 198 | 183 | 183 | 191 | 203 | 184 | 184 | 183 | 204 | 183 | 206 |  | 196 | 195 | 184 | 183 | 183 | 183 | 183 | 4549000
34 | Ashuganj 450 MW CCPP(South) | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 310 | 295 | 280 | 295 | 300 | 300 | 270 | 300 | 300 | 270 | 330 |  | 290 | 285 | 270 | 270 | 270 | 265 | 270 | 7059000
Ashuganj 450 MW CCPP(North)
| Ashuganj 420 MW CCPP(East) | 365 | 365 | 318 | 318 | 318 | 348 | 370 | 360 | 347 | 317 | 330 | 342 | 351 | 318 | 348 | 376 | 318 | 378 |  | 333 | 334 | 320 | 320 | 321 | 321 | 321 | 8110000
35 | Ashuganj 55 MW PP (Precision) | [16 empty] | 2 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 45120
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 396 | 390 | 361 | 361 | 361 | 380 | 378 | 384 | 409 | 374 | 359 | 399 | 402 | 361 | 334 | 346 | 396 | 404 |  | 378 | 397 | 386 | 394 | 396 | 380 | 361 | 9267200
40 | Meghnaghat 450 MW CCPP(MPL) | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 |  | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 4670000
41 | Haripur 360MW CCPP(HPL) | 339 | 341 | 304 | 269 | 275 | 361 | 280 | 361 | 343 | 280 | 280 | 280 | 280 | 280 | 250 | 250 | 320 | 350 |  | 320 | 350 | 353 | 358 | 305 | 357 | 336 | 7552000
42 | RPCL 210MW CCPP | 103 | 104 | 109 | 110 | 110 | 111 | 73 | 73 | 73 | 72 | 71 | 70 | 71 | 70 | 70 | 84 | 96 | 96 |  | 100 | 103 | 104 | 110 | 109 | 110 | 110 | 2124480
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 1 | 8 | 19 | 31 | 37 | 37 | 29 | 24 | 10 | 7 | 1 | [9 empty] | 201110
44 | Fenchugonj CCPP Phase-1 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 716000
45 | Fenchugonj CCPP Phase-2 | 42 | 42 | 42 | 42 | 42 | 42 | 0 | 0 | 0 | 0 |  |  | 20 | 20 | 30 | 20 | 20 | 31 |  | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 536160
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 62 | 64 | 64 | 40 | 40 | 40 | 64 | 65 | 70 | 69 | 66 | 64 | 66 | 40 | 61 | 61 | 40 | 64 |  | 64 | 64 | 65 | 64 | 65 | 40 | 40 | 1394400
48 | Shahjibazar 86MW PP (Shahjibazar) | 86 | 50 | 20 | 20 | 20 | [17 empty] | 40 | 84 | 84 | 84 | 528960
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 218 | 218 | 218 | 218 | 221 | 222 | 221 | 218 | 218 | 218 | 218 | 218 | 218 | [12 empty] | 0 | 2016840
51 | Sylhet 20 MW GTPP | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 19 | 19 | 442000
52 | Sylhet 50MW PP (EPL) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 18 | 24 | 26 | 26 |  | 26 | 27 | 26 | 26 | 26 | 26 | 26 | 481300
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 247320
54 | Hobiganj 11MW PP Cofidence-E | 8 | 8 | 8 | 8 | 8 | 8 | 8 | [16 empty] | 8 | 8 | 8 | 76920
55 | Fenchugonj 51 MW PP (Barakatullah) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 11 | 48 | 50 | 53 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 700800
56 | Shahjahanulla 25 MW PP | 22 | [6 empty] | 21 | 16 | 16 | 16 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 375072
57 | Bibiana-II 341 MW CCPP (Summit)
| Bibiyana South 400 MW | 400 | 400 | 370 | 340 | 370 | 400 | 400 | 400 | 400 | 382 | 400 | 400 | 380 | 370 | 367 | 380 | 320 | 400 |  | 400 | 400 | 400 | 400 | 370 | 400 | 400 | 9160300
58 | Nababganj 55 MW PP (Southern power ) | 17 |  |  |  |  | 5 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 35 | 35 | 17 | 35 | 35 |  | 35 | 35 | 45 | 55 | 55 | 35 | 35 | 572666
59 | Tangail Palli Power Gen 22 MW | 8 |  |  |  |  | 1 | 10 | 11 | 12 | 12 | 12 | 12 | 7 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 227760
60 | Barabkunda 22 MW PP (Regent)
61 | Narshingdi 22 MW PP (Doreen) | 13 | [6 empty] | 22 | 22 |  | 19 | 11 | [10 empty] | 22 | 22 | 22 | 22 | 178416
62 | Tangail 22 MW PP (Doreen) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 18 | 18 | 19 | 19 | 19 |  | 16 | 16 | 16 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 454140
63 | Impoprt (Tripura) | 68 | 64 | 58 | 60 | 62 | 58 | 56 | 66 | 62 | 60 | 66 | 76 | 80 | 78 | 76 | 76 | 80 | 82 |  | 82 | 82 | 80 | 82 | 80 | 76 | 70 | 1698240
64 | Malancha, Ctg. EPZ (United) | 25 | 26 | 29 | 31 | 34 | 38 | 42 | 36 | 28 | 23 | 23 | 23 | 25 | 27 | 29 | 34 | 35 | 32 |  | 33 | 29 | 33 | 33 | 36 | 39 | 40 | 753120
65 | Feni 22MW PP (Doreen) | 21 | [8 empty] | 7 | 18 | 17 | 19 | 19 | 19 | 19 | 19 | 19 |  | 20 | 20 | 20 | 21 | 20 | 20 | 21 | 298332
66 | Feni 11 MW PP (Doreen) | 11 |  |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 231480
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 8 | 8 | 8 | 8 | 21 | 19 | 16 | 17 | 24 | 23 | 24 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 644400
68 | Cumilla 25 MW PP (Summit) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 344540
69 | Summit Ashulia | 23 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 528000
70 | Summit Madhabdi | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 14 | 17 | 11 | 11 | 11 | 11 | 11 | 14 |  | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 518760
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 20 | 20 | 21 | 597960
72 | Rupganj 33 MW PP(Summit) | 30 | 30 | 30 | 32 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 820400
73 | Ghorashal 108MW PP (Regent) | 70 | 70 | 32 | 32 | 32 | 32 | 57 | 67 | 70 | 70 | 67 | 69 | 69 | 69 | 69 | 33 | 70 | 71 |  | 71 | 71 | 72 | 72 | 72 | 72 | 72 | 1479318
| Feni Lanka Power | [11 empty] | 17 | 17 |  |  |  | 17 | 17 | [8 empty] | 83220
| Chowmuhani 113 MW | 3 |  |  |  |  | 5 | 44 | 56 | 56 | 57 | 57 | 63 | 62 | 8 | 8 | 8 | 9 | 9 |  | 8 | 8 | 8 | 8 | 8 | 8 | 0 | 540120
| Manikgonj 162MW PP(MPGL) | 17 |  |  |  |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 32 | 122 | 162 |  | 162 | 162 | 162 | 162 | 108 | 17 | 17 | 1080000
77 | Siddhirganj 100 PP(Dutch Bangla) | [6 empty] | 20 | 25 | 25 | 27 | 32 | 32 | 32 | 22 | 8 | 8 | 8 | 10 |  | 30 | 32 | 33 | 34 |  |  | 0 | 338880
78 | Gazipur 52 MW PP | [8 empty] | 8 | 8 | 8 | 8 | 39 |  |  |  | 8 | 8 |  | 8 | 8 | 8 | 8 |  |  | 0 | 118560
79 | Kodda 150MW PP | [11 empty] | 16 | 32 |  |  |  | 16 | 32 |  | 32 | 32 | 32 | 32 |  |  | 0 | 205440
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | [6 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 0 | 146875
| Gazipur 100 MW PP | [6 empty] | 14 | 34 | 60 | 70 | 70 | 70 | 70 | 17 | 17 | 17 | 25 | 35 |  | 35 | 35 | 17 | 17 |  |  | 0 | 619200
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 0 | 2 | 3 | 4 | 4 | 3 | 3 | 2 | 1 | [10 empty] | 22078
| Jodiac Power | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 32 | 34 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 499856
| Karnaphuli Power Ltd. | 72 | 72 | 72 | 34 | 34 | 50 | 68 | 17 | 17 | 17 | 17 | 47 | 70 | 34 | 34 | 28 | 25 | 44 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 975196
82 | Madanganj 102 PP(Summit) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 26 | 30 | 17 | 5 | 17 | 17 |  | 27 | 34 | 34 | 34 | 19 | 12 | 0 | 402633
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL) | [6 empty] | 6 | 17 | 18 | 17 | 21 | 31 | 33 | 25 | 8 | 8 | 9 | 9 |  | 32 | 34 | 34 | 34 | 29 |  | 0 | 330240
| Meghnaghat 104 MW PP (OPCL) | 17 |  |  |  |  | 6 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 336960
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 263400
92 | Fenchuganj 44MW (Energyprima) | 30 | 10 | 10 | 10 | 10 | 10 | 30 | 46 | 43 | 43 | 46 | 44 | 45 | 45 | 45 | 45 | 45 | 42 |  | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 891000
93 | Ashuganj 51 MW PP (Midland) | 51 | 10 | 10 | 10 | 10 | 10 | 10 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 15 | 20 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1006644
94 | Gagnagar 102 MW PP (Digital Power) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 16 | 495936
95 | Patenga 50MW PP (Baraka) | [6 empty] | 14 | 12 | 21 | 14 | 12 | 13 | 32 | 37 | 38 | 34 | 19 | 19 |  | 43 | 44 | 44 | 44 | 44 | 19 | 0 | 488640
96 | Chattogram 108 MW PP (ECPV) | [9 empty] | 9 | 32 | 32 | 32 | 31 | 31 | 31 | [9 empty] | 0 | 200640
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [15 empty] | 1 | 15 | 15 |  | 15 | 15 | 15 | 15 | 15 | 9 | 0 | 109905
100 | Manikganj 55 MW PP (Northern) | 17 | [5 empty] | 17 | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 17 | 20 | 55 |  | 35 | 17 | 17 | 17 | 17 | 17 | 17 | 539674
101 | Kushiara 163 MW CCPP (KP) | [24 empty] | 70 | 70 | 92209
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 1 |  | 2 | 2 | 2 | 2 | 1 | 1 | [10 empty] | 11750
103 | Kamalaghat 54 MW PP(Banco Energy) | [8 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 54 |  | 54 | 54 | 54 | 54 | 17 | 17 | 17 | 396360
104 | Keranigonj 300 MW PP (APR) | [12 empty] | 30 | [12 empty] | 0 | 51617
105 | Bramhangoan 100 MW PP (Aggreko) | [12 empty] | 25 | [12 empty] | 0 | 14913
106 | Mymensingh 200 MW PP (United) | 49 | 48 | 8 | 8 | 8 | 14 | 47 | 47 | 46 | 48 | 49 | 49 | 49 | 49 | 24 | 8 | 24 | 46 |  | 46 | 56 | 46 | 46 | 46 | 46 | 41 | 900000
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [6 empty] | 10 | 34 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 642672
115 | Juldah 100 MW PP Unit-3 (Acorn) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 304320
116 | Chandpur 200MW (Desh energy) | 17 |  |  |  |  | 1 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 22 |  | 51 | 17 | 24 | 17 | 17 | 17 | 17 | 397920
117 | Ashuganj 150MW PP (Midland) | 5 |  |  |  |  | 1 | 5 | 6 | 5 | 6 | 6 | 6 | 5 | 6 | 6 | 10 | 25 | 63 |  | 72 | 72 | 73 | 73 | 65 | 16 | 0 | 480072
118 | Bibiyana-III 400 MW CCPP | 375 | 375 | 375 | 352 | 360 | 363 | 360 | 369 | 338 | 339 | 403 | 414 | 352 | 352 | 374 | 377 | 364 | 420 |  | 420 | 420 | 420 | 418 | 403 | 362 | 363 | 9052000
| Jamalpur 115 MW PP (United) | 28 | 8 | 8 | 8 | 8 | 8 | 8 | 16 | 28 | 28 | 28 | 28 | 28 | 28 | 16 | 8 | 20 | 47 |  | 47 | 47 | 47 | 47 | 47 | 47 | 37 | 631200
| Anwara 300 MW PP (United) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 30 | 100 | 210 |  | 135 | 135 | 135 | 135 | 135 | 135 | 51 | 1891855
| Juldah unit-2 (Acorn) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 303360
| Anlima Energy Ltd. | 107 | 107 | 107 | 107 | 107 | 107 | 95 | 102 | 107 | 107 | 107 | 91 | 89 | 89 | 89 | 88 | 87 | 89 |  | 89 | 89 | 89 | 107 | 107 | 107 | 107 | 2402455
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 21 | 35 | 36 | 36 | 36 | 36 | 36 | 24 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 566640
| Spectra Solar Plant Ltd. | [6 empty] | 1 | 8 | 17 | 24 | 29 | 30 | 27 | 24 | 16 | 8 | 1 | [9 empty] | 184267
| Chandpur 115(Doreen) | 34 |  |  |  |  | 11 | 35 | 35 | 35 | 35 | 35 | 35 | 33 | 35 | 39 | 53 | 52 | 53 |  | 53 | 53 | 52 | 51 | 53 | 49 | 34 | 834240
| Kanchan Purbachal Power Generation Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 15 | 429840
| Mirsharai 150 MW (Oil) | [12 empty] | 18 | [12 empty] | 0 | 18400
Mirsharai 150 MW (Gas)
120 | Eastern Zone Total | 4630 | 4271 | 4024 | 3853 | 3907 | 4115 | 4338 | 4636 | 4661 | 4518 | 4675 | 4864 | 4954 | 4345 | 4305 | 4272 | 4452 | 5354 |  | 5189 | 5181 | 5126 | 5228 | 4906 | 4741 | 4450 | 109370233
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | [17 empty] | 16 |  | 16 | 16 | 16 |  |  |  | 0 | 44160
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | [12 empty] | 3 | 17 |  |  | 1 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 0 | 135360
130 | Mongla Orion 100 MW Solar PP | [6 empty] | 2 | 16 | 36 | 55 | 65 | 69 | 68 | 60 | 40 | 18 | 1 | [9 empty] | 434880
131 | Rampal 1320 MW (BIFPCL) | 626 | 634 | 631 | 626 | 434 | 412 | 404 | 421 | 404 | 410 | 368 | 410 | 410 | 410 | 410 | 410 | 417 | 450 |  | 511 | 524 | 524 | 477 | 464 | 470 | 463 | 11363950
132 | United Payra Power Ltd. | [25 empty] | 0 | 0
133 | Bhola Nutan Biddut BD LTD (GAS) | 220 | 220 | 190 | 178 | 170 | 160 | 160 | 163 | 165 | 167 | 163 | 162 | 210 | 179 | 162 | 160 | 155 | 220 |  | 220 | 220 | 220 | 160 | 160 | 160 | 164 | 4360800
Bhola Nutan Biddut BD LTD (OIL)
Barisal 110 MW PP (Summit )
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW | [20 empty] | 10 | 34 | 57 | 102 | 121 | 153 | 435200
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 183 | 183 | 184 | 184 | 184 | 157 | 184 | 184 | 168 | 168 | 181 | 178 | 170 | 172 | 162 | 162 | 184 | 184 |  | 184 | 183 | 184 | 162 | 91 | 91 | 91 | 4037940
140 | Bhola 33 MW PP (Venture) | 20 | 19 | 18 | 17 | 17 | 18 | 17 | 16 | 15 | 15 | 15 | 17 | 17 | 14 | 13 | 13 | 15 | 20 |  | 20 | 21 | 22 | 22 | 22 | 21 | 19 | 419300
141 | Noapara 100 MW PP (Bangla Trac) | [25 empty] | 0 | 0
142 | Noapara 40 MW PP (Khanjahan Ali) | [12 empty] | 16 | [6 empty] | 40 | 40 | 32 | 40 |  |  | 0 | 132000
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 729 | 609 | 608 | 608 | 608 | 609 | 609 | 609 | 608 | 608 | 608 | 681 | 681 | 657 | 655 | 656 | 656 | 869 |  | 870 | 870 | 869 | 870 | 869 | 776 | 729 | 16877090
147 | Bheramara 410 MW CCPP
148 | Payra 1320 MW | 280 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 260 | 270 | 270 | 270 | 340 | 350 | 260 | 260 | 290 | 350 |  | 430 | 430 | 430 | 400 | 340 | 340 | 340 | 8204300
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 159 | 160 | 159 | 159 | 159 | 159 | 159 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 |  | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 3900100
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [26 empty] | 0
| Sirajgonj 6.55 MW Solar | [6 empty] | 1 | 1 | 3 | 4 | 4 | 4 | 4 | 2 | 2 | 0 | 0 | [9 empty] | 29040
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 157 | 157 | 156 | 157 | 159 | 162 | 166 | 171 | 171 | 165 | 160 | 145 | 130 | 130 | 133 | 130 | 141 | 172 |  | 180 | 180 | 180 | 181 | 183 | 185 | 185 | 4082918
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | [12 empty] | 68 | 46 | [12 empty] | 123877
| Sirajgonj 225 MW CCPP Unit-2 (Oil) | [11 empty] | 34 | [14 empty] | 40323
159 | Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 311 | 322 | 334 | 306 | 307 | 385 | 266 | 397 | 371 | 345 | 321 | 306 | 268 | 244 | 265 | 259 | 265 | 278 |  | 278 | 283 | 301 | 304 | 310 | 258 | 260 | 7265490
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 17 | [5 empty] | 13 | 18 | 18 | 17 | 17 | 16 | 16 | 16 | 16 | 17 | 17 | 17 |  | 17 | 17 | 17 | 18 | 20 | 20 | 19 | 296880
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 187560
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | [6 empty] | 8 | 8 | 8 | 8 | 8 | 34 | 34 | 8 |  |  | 16 | 34 |  | 50 | 50 | 50 | 42 | 8 |  |  | 324487
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP | [16 empty] | 15 | 25 |  | 24 | [6 empty] | 42928
169 | Natore 52 MW PP (Rajlanka) | [6 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 0 | 138638
170 | Chapainawabganj 100 MW Peaking PP
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [6 empty] | 25 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 42 | 74 |  | 94 | 94 | 94 | 94 | 94 | 94 | 35 | 1054560
172 | Confidence Power Bogura Unit-1 113 MW | [5 empty] | 20 | 35 | 35 | 90 | 95 | 95 | 95 | 95 | 35 | 35 |  | 25 | 75 |  | 75 | 75 | 75 | 75 | 75 | 35 | 0 | 1071648
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | 10 |  |  |  |  | 12 | 33 | 33 | 100 | 107 | 70 | 49 | 49 | 34 | 34 | 34 | 50 | 113 |  | 113 | 113 | 113 | 113 | 113 | 105 | 12 | 1357248
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 0 | 0 | 1 | 2 | 4 | 5 | 4 | 4 | 2 | 0 | [9 empty] | 25445
178 | Energypac Power Venture Thakurgaon Ltd. | [5 empty] | 5 | 35 | 35 | 36 | 36 | 37 | 90 | 115 | 35 | 35 |  | 35 | 54 |  | 115 | 115 | 115 | 115 | 75 | 36 | 0 | 1095744
| Intraco Solar 30 MW | [6 empty] | 0 | 1 | 2 | 4 | 5 | 6 | 7 | 16 | 10 | 5 | 0 | [9 empty] | 57133
Adani Power Jharkhanda Ltd
178 | Teesta Solar Limited | [7 empty] | 14 | 29 | 40 | 60 | 103 | 104 | 88 | 65 | 33 | 2 | [9 empty] | 534960