## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2022-12-27 | Tuesday
|  | Date (day): | 2022-12-27 |  | Tuesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 8179.6 | MW |  |  | (b) At Evening Peak Hour : |  | 10484 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2022-12-26 | 2022-12-27 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Line O/L
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  |  | Machine problem
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 200 | 200 | 200 | 200 | 165 |  | Gas shortage
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 70 | 73 | 70 | 70 | 38 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 403 | 402 | 400 | 400
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 346 | 333 | 330 | 330 | 30 |  | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 225 | 225 | 225 |  | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 0 | 17 | 17 | 17 | 83 |  | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 34 | 34 | 34 | 34 | 68 |  | Fuel shortage
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 0 | 20 | 0 | 20 | 35 |  | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 16 | 16 | 16 | 16 | 50 |  | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 16 | 16 | 16 | 16 | 86 |  | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 54 | 17 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 32 | 32 | 32 | 32 | 117 |  | Fuel shortage
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 35 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 55 | 35 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 52 | 52 | 52 | 52 |  | 28 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 30 | 25 | 30 |  | 3 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 28 | 28 | 28 | 28
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 49 | 48 | 50 | 50
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 32 | 95 | 32 | 95 | 205 |  | Fuel shortage
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 204 | 44 | 0 | 150 | 150 |  | Fuel conservation
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 92 | 50 | 0 | 50 | 50 |  | Fuel conservation
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 87 | 70 | 0 | 50 | 50 |  | Fuel conservation
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 35 | 35 | 35 | 35 | 114 |  | Fuel shortage
36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 105 | 105 | 90 | 105
37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 18 | 17 | 17 | 17 | 87 |  | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 17 | 162 | 17 | 162
39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 22 | 0 | 30 | 0
40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 17 | 17 | 17 | 38 |  | Fuel shortage
| Dhaka area Total |  |  |  |  | 6263 | 5847 | 2216 | 2307 | 1842 | 2387 | 2522 | 711
41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 10 | 17 | 17 | 17
43 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 18 | 0 | 20 | 0
44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 0 | 0 |  | 6 | Fuel shortage
45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 30 | 30 | 30 | 30 | 200 |  | Low Water Level
46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 40 | 152 | 150 | 150 |  | 75 | ST Under maint
47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 17 | 51 | 17 | 51 | 54 |  | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 40 | 0 | 40 | 58 |  | Fuel shortage
50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 36 | 0 | 50 | 52 |  | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 10 | 10 | 10 | 10 | 90 |  | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 12 | 12 | 12 | 88 |  | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 22 |  | Gas shortage
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 14 | 5 | 15
54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 10 | 0 | 10 | 98 |  | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 51 | 290 | 51 | 290 |  | 10 | Engine problem
57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 17 | 17 | 17 | 35 |  | 19 | Engine problem
58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 60 | 72 | 72 | 72 |  | 38 | Engine problem
59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 12 | 12 | 12 | 88 |  | Fuel shortage
60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 107 | 107 | 107 | 107 |  | 9 | Engine problem
| Mirsharai 150 MW |  | Gas/HSD | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0
| Chattogram area Total |  |  |  |  | 2442 | 2382 | 390 | 870 | 525 | 901 | 1110 | 307
61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 218 | 131 | 150 | 150 |  |  | Gas shortage
63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 10 | 330 | 330 | 30 |  | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 345 | 270 | 0 | 0
65 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 297 | 258 | 330 | 330
66 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 5 | 0 | 5 | 5 | 40 |  | Gas shortage
67 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 55 | 0 | 0 | 5 | 5 | 50 |  | Gas shortage
68 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 0 | 8 | 8 | 187 |  | Gas shortage
69 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
70 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 6 | 72 | 3 | 70 | 80 |  | Fuel shortage
71 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 30 | 21 | 25 | 30 |  | 22 | Engine problem
72 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under Maint.
73 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 17 | 51 | 17 | 51 | 149 |  | Fuel shortage
74 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 21 | 21 | 21
75 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 10 | 10 | 10 | 10
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 108 | 112 | 135 | 152
76 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 28 | 33 | 30 | 33
77 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 8 | 8 | 8 | 44 |  | Fuel shortage
78 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 9 | 20 | 20 | 20 |  | 5 | Engine problem
79 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 85 | 10 | 0 | 100 | 100 |  | Fuel conservation
80 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 100 | 17 | 17 | 97 |  | Fuel shortage
81 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 9 | 8 | 9 | 104 |  | Fuel shortage
82 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 17 |  | 37 | Engine problem
83 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 36 | 54 | 0 | 0 | 115 |  | Fuel shortage
| Cumilla Area Total |  |  |  |  | 3309 | 3285 | 1317 | 1258 | 1190 | 1417 | 1130 | 227
84 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 33 | 53 | 70 | 100 | 102 |  | Gas shortage
85 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 20 | 19 | 19
86 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0
87 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1 | 0 | 1.6 | 0
88 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 48 | 48 | 46 | 48 | 152 |  | Fuel shortage
89 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 28 | 47 | 28 | 47 | 68 |  | Fuel shortage
90 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 35 | 0 | 50 | 0
91 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 6 | 12 | 12 |  | 10 | Engine problem
| Mymensingh Area Total |  |  |  |  | 717 | 614 | 164 | 174 | 226.6 | 226 | 102 | 10
92 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 30 | 30 | 30 | 30 |  | 40 | Machine problem.
93 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 31 | 43 | 43 |  | 47 | Machine problem
94 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 | 163 |  | ST Under maint
95 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
96 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 51 | 53 | 53 | 53 | -2
97 | Fenchuganj 44MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 44 | 47 | 30 | 40 | 10
98 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 8 | 8 |  | 3 | Engine problem
99 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 60 | 63 | 65 | 66
100 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 30 | 86 | 40 | 86
101 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
102 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 130 | 130 | 130 | 130 |  | 101 | Engine problem
103 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 19 | 19 | 19 | 19
104 | Sylhet 50MW PP (EPL) |  | Gas | NENP | 27*2 | 50 | 50 | 24 | 24 | 24 | 24 | 26 |  | Gas shortage
105 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 0 | 16 | 16 | 16
106 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 0 | 0 | 0 | 0 |  | 341 | Under maint.
107 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 384 | 396 | 400 | 400
108 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
109 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 400 | 400 | 400 | 400
| Sylhet Area Total |  |  |  |  | 2522 | 2477 | 1190 | 1313 | 1268 | 1325 | 197 | 962
110 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 785 | 904 | 838 | 934
111 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 0 | 66 | 0 | 99 | 16 |  | Fuel shortage
112 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 13 | 0 | 40 |  | 14 | Engine problem
113 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
114 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 70 | 0 | 70 |  | 39 | Engine problem
115 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 | 410 |  | Gas shortage.
116 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 32 | 0 | 40
117 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 10 | 0 | 50 | 50 |  | Fuel conservation
118 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 12 | 18 | 18 | 87 |  | Fuel shortage
119 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Fuel shortage
120 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 73 | 0 | 100 | 0
| Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 0 | 0 | 243 | 0 | 0 | 0 |  |  | On test.
| Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 0 | 0 | 0 | 468 | 522 | 420 | 520 |  |  | On test.
| Khulna Area Total |  |  |  |  | 2388 | 2384 | 1569 | 1629 | 1376 | 1771 | 914 | 53
121 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 0 | 0 |  |  | Line O/L
122 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 18 | 24 | 18 | 24 |  | 16 | Engine problem
123 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 156 | 180 | 150 | 180 |  |  | Machine problem
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
124 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 300 | 380 | 300 | 400 |  | 844 | Unit-2 U/M & Rampal Test
125 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 108 | 140 | 110 | 110 |  | 110 | Engine problem
126 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 0 | 35 |  |  | Line O/L
| Barisal 307 MW |  | Coal | BCPCL | 0 | 0 | 0 | 200 | 253 | 230 | 250 |  |  | On test.
| Barisal Area Total |  |  |  |  | 1958 | 1958 | 782 | 977 | 808 | 999 | 0 | 970
127 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
128 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 32 | 0 | 34 |  | 18 | Engine problem
129 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 6 | 0 | 25 |  | 46 | Engine problem
130 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
131 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 42 | 50 | 50 | 50
132 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 16 | 40 | 0 | 40 |  | 10 | Engine problem
133 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 170 | 136 | 150 | 150 | 60 |  | Gas shortage
134 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 43 | 15 | 43 |  | 177 | Machine problem
135 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
136 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 290 | 154 | 350 | 350 | 64 |  | Gas shortage
137 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 32 | 0 | 32 |  | 18 | Engine problem
138 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 16 | 18 | 20 | 20 |  | 2 | Machine problem
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
139 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 8 | 8 |  | 3 | Engine problem
140 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 8 | 8 | 8 | 44 |  | Fuel shortage
141 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 67 | 0 | 67 | 37 |  | Fuel shortage
142 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 10 | 0 | 100 | 100 |  | Fuel conservation
143 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 35 | 70 | 35 | 70 |  | 18 | Fuel shortage
144 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 35 | 75 | 35 | 75 |  |  | Fuel shortage
145 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 4 | 0 | 6 | 0
| Adani Power Jharkhanda Ltd |  | Coal | Import | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Rajshahi Area Total |  |  |  |  | 2179 | 2129 | 624 | 749 | 677 | 1072 | 696 | 292
146 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal shortage
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
147 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 159 | 159 | 160 | 160 |  |  | Machine problem
148 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
149 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
150 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 103 | 113 | 34 | 113
151 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5 | 0 | 8 | 0
152 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 115 | 115 | 35 | 113
153 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 17 | 0 | 30 | 0
| Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 0 | 0 | 66 | 0 | 0 | 0
| Rangpur Area Total |  |  |  |  | 830 | 750 | 465 | 387 | 267 | 386 | 125 | 85
| Total |  |  |  |  | 22608 | 21826 | 8717 | 9664 | 8179.6 | 10484 | 6796 | 3617
A. |  | 2022-12-26 | (Yesterday) |  |  |  |  | Monday
1 | Highest Generation : |  |  | 9664 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
2 | Minimum Generation : |  |  | 6243 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 9664 | MW
3 | Day peak Generation : |  |  | 8717 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 9329.96 | MW
4 | Evening peak Generation : |  |  | 9664 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 193.0802 | MKWHr | By Solar | 1.353 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Gas : | 106.8642 | MKWHr |  | By Oil: | 35.4602 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 28.1039 | MKWHr |  | By Hydro: | 0.72 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 6796 | MW | Dhaka | 3469.88 | 3469.88 |  | 0 |  | 18:00 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 3617 | MW | Chittagong | 1044.7 | 1044.7 |  | 0 |  | 19:00 |  | 0
|  |  | Total = |  |  | 10413 | MW | Khulna | 1118 | 1118 |  | 0 |  | 19:30 |  | 0
7 | Total Gas Supplied : |  |  | 834.57 | MMCFD |  |  | Rajshahi | 920.8 | 920.8 |  | 0 |  | 20:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 109728541.658 | ii) Oil : | Taka | 495336232.61 | Comilla | 810 | 810 |  | 0 |  | 21:00 |  | 0
|  | iii) Coal : |  | 95587801 | Total | Taka | 700652575.268 | Mymensingh | 741 | 741 |  | 0 |  | 22:00 |  | 0
9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0 | MKWHr. | Sylhet | 331 | 331 |  | 0 |  | 23:00 |  | 0
| ii) During Peak Demand : |  |  | 106 | MW (E to W) at | 19:00 | hrs | Barisal | 251.58 | 251.58 |  | 0 |  | 24:00 |  | 0
| iii) Maximum : |  |  | 34 | MW at | 18:30 | hrs | Rangpur | 643 | 643 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 28.9° C |  |  | Total | 9329.96 | 9329.96 |  | 0
B. |  | 2022-12-27 | (Today) |  |  |  | Tuesday |  |  | Probable max. temperature in Dhaka |  |  | 28.0° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 9800 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 10484 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 8700 | MW
4 | Reserve(Generation end) |  |  |  | 684 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 195.7974 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5809 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 18.3796 | MKWHr. | ii) HVDC Flow at Peak Time |  | 904 | MW at | 19:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.1994 | MKWHr. | iii) Maximum HVDC Flow : |  | 909 | MW at | 21:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 86.95 |  | (b) Today: | 86.89 |  | (c) Rule Curve: |  | 103.3
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2022-12-26
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 0 | 200 | 72 | 0 | 405 | 356 |  | 0 | 225 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 22 | 25 | 26 | 25 | 30 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 151 | 0 | 0 | 0 |  | 9 | 0 | 0 | 10 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 280 | 182 | 8 | 0 | 5 | 0 | 0 | 51 | 0 | 0 | 0 | 21 | 10 | 33 | 15 | 80 | 103 | 0 | 22 | 0 | 30 | 43 | 31 | 43 | 0 | 0 | 40 | 40 | 0 | 130 | 19 | 26 | 10 | 0 | 21 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 12 | 17 | 0 | 412 | 8 | 0 | 0 | 0 | 51 | 17 | 72 | 0 | 0 | 12 | 400 | 17 | 0 | 17 | 107 | 0 | 17 | 0 | 36 | 0 | 350 | 0 | 0 |  | 723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 269 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 260 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 392 | 0 | 202 | 0 | 0 |  | 4471 | 2548 | 7019 | 3372 | 723 | 1296 | 0 | 504 | 1014 | 30 | 0 | 0 | 80 | 0 | 0 | 86.97
2:00 | 0 | 0 | 0 | 0 | 200 | 69 | 0 | 405 | 356 |  | 0 | 225 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 26 | 25 | 30 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 151 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 290 | 183 | 8 | 0 | 5 | 0 | 0 | 51 | 0 | 0 | 0 | 18 | 10 | 33 | 15 | 74 | 101 | 0 | 22 | 0 | 30 | 43 | 31 | 46 | 0 | 0 | 40 | 10 | 0 | 130 | 19 | 26 | 10 | 0 | 21 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 12 | 0 | 0 | 405 | 0 | 0 | 0 | 0 | 51 | 17 | 72 | 0 | 0 | 12 | 400 | 17 | 0 | 0 | 107 | 0 | 17 | 0 | 34 | 0 | 350 | 0 | 0 |  | 611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 156 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 202 | 0 | 0 |  | 4350 | 2314 | 6664 | 3326 | 611 | 1222 | 0 | 374 | 1027 | 30 | 0 | 0 | 74 | 0 | 0 | 86.96
3:00 | 0 | 0 | 0 | 0 | 200 | 24 | 0 | 404 | 307 |  | 0 | 225 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 26 | 25 | 32 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 151 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 295 | 187 | 8 | 0 | 5 | 0 | 0 | 10 | 0 | 0 | 0 | 18 | 10 | 33 | 15 | 72 | 113 | 0 | 22 | 0 | 30 | 43 | 11 | 10 | 0 | 0 | 40 | 10 | 0 | 130 | 19 | 11 | 10 | 0 | 21 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 368 | 0 | 0 | 0 | 0 | 51 | 17 | 72 | 0 | 0 | 12 | 385 | 0 | 0 | 0 | 107 | 0 | 17 | 0 | 0 | 0 | 350 | 0 | 0 |  | 611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 157 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 186 | 0 | 0 |  | 4060 | 2292 | 6352 | 3282 | 611 | 1031 | 0 | 315 | 1011 | 30 | 0 | 0 | 72 | 0 | 0 | 86.96
4:00 | 0 | 0 | 0 | 0 | 200 | 12 | 0 | 391 | 306 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 26 | 25 | 32 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 151 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 280 | 185 | 8 | 0 | 5 | 0 | 0 | 10 | 0 | 0 | 0 | 18 | 10 | 33 | 15 | 70 | 113 | 0 | 22 | 0 | 30 | 43 | 11 | 10 | 0 | 0 | 40 | 10 | 0 | 130 | 19 | 11 | 10 | 0 | 21 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 376 | 0 | 0 | 0 | 0 | 51 | 17 | 72 | 0 | 0 | 12 | 370 | 0 | 0 | 0 | 107 | 0 | 17 | 0 | 0 | 0 | 350 | 0 | 0 |  | 624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 157 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 170 | 0 | 0 |  | 3993 | 2287 | 6280 | 3245 | 624 | 1018 | 0 | 298 | 995 | 30 | 0 | 0 | 70 | 0 | 0 | 86.96
5:00 | 0 | 0 | 0 | 0 | 200 | 12 | 0 | 372 | 307 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 26 | 25 | 33 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 151 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 280 | 182 | 8 | 0 | 5 | 0 | 0 | 10 | 0 | 0 | 0 | 18 | 10 | 33 | 15 | 70 | 113 | 0 | 22 | 0 | 30 | 43 | 11 | 10 | 0 | 0 | 40 | 10 | 0 | 130 | 19 | 11 | 10 | 0 | 21 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 363 | 0 | 0 | 0 | 0 | 51 | 17 | 72 | 0 | 0 | 12 | 370 | 0 | 0 | 0 | 107 | 0 | 17 | 0 | 0 | 0 | 350 | 0 | 0 |  | 611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 157 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 171 | 0 | 0 |  | 3960 | 2283 | 6243 | 3211 | 611 | 1027 | 0 | 298 | 996 | 30 | 0 | 0 | 70 | 0 | 0 | 86.96
6:00 | 0 | 0 | 0 | 0 | 200 | 57 | 0 | 372 | 310 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 22 | 25 | 26 | 25 | 33 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 125 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 315 | 202 | 8 | 0 | 5 | 0 | 0 | 10 | 0 | 0 | 0 | 18 | 10 | 33 | 15 | 74 | 112 | 0 | 22 | 0 | 30 | 0 | 11 | 25 | 0 | 0 | 40 | 10 | 0 | 130 | 19 | 11 | 10 | 0 | 21 | 8 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 12 | 2 | 0 | 363 | 2 | 0 | 0 | 0 | 51 | 17 | 72 | 0 | 0 | 12 | 370 | 5 | 0 | 2 | 95 | 0 | 17 | 0 | 8 | 0 | 382 | 0 | 0 |  | 611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 157 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 323 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 260 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 171 | 0 | 0 |  | 4061 | 2375 | 6436 | 3228 | 611 | 1186 | 0 | 316 | 991 | 30 | 0 | 0 | 74 | 0 | 0 | 86.95
7:00 | 0 | 0 | 0 | 0 | 200 | 65 | 0 | 376 | 311 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 22 | 25 | 26 | 25 | 33 | 8 | 0 | 0 | 30 | 0 | 0 | 0 | 30 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 325 | 218 | 8 | 0 | 5 | 0 | 0 | 10 | 0 | 0 | 0 | 18 | 10 | 33 | 15 | 76 | 71 | 0 | 0 | 0 | 30 | 0 | 51 | 40 | 0 | 0 | 64 | 30 | 0 | 130 | 19 | 20 | 10 | 0 | 21 | 8 | 0 | 12 | 0 | 0 | 19 | 0 | 7 | 1 | 12 | 17 | 0 | 387 | 17 | 17 | 11 | 0 | 51 | 17 | 72 | 0 | 0 | 12 | 370 | 17 | 0 | 17 | 107 | 0 | 17 | 0 | 31 | 9 | 408 | 0 | 0 |  | 611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 157 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 18 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 0 | 24 | 0 | 33 | 0 | 0 | 0 | 260 | 102 | 0 | 0 | 0 | 2 | 20 | 0 | 0 | 406 | 0 | 171 | 0 | 1 |  | 4310 | 2512 | 6822 | 3186 | 611 | 1311 | 0 | 607 | 997 | 30 | 0 | 0 | 76 | 4 | 0 | 86.95
8:00 | 0 | 0 | 0 | 0 | 200 | 68 | 0 | 399 | 356 |  | 0 | 225 | 0 | 9 | 6 | 0 | 0 | 0 | 0 | 15 | 8 | 32 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 22 | 25 | 26 | 25 | 32 | 16 | 0 | 0 | 30 | 0 | 0 | 8 | 30 | 0 | 0 | 0 |  | 0 | 4 | 0 | 10 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 345 | 224 | 8 | 0 | 5 | 0 | 0 | 18 | 0 | 0 | 0 | 21 | 10 | 25 | 15 | 84 | 97 | 0 | 19 | 0 | 30 | 0 | 53 | 40 | 0 | 0 | 64 | 30 | 0 | 130 | 19 | 0 | 0 | 0 | 0 | 8 | 0 | 15 | 0 | 0 | 46 | 0 | 32 | 6 | 12 | 17 | 3 | 385 | 28 | 40 | 17 | 1 | 51 | 17 | 72 | 17 | 8 | 12 | 400 | 17 | 3 | 17 | 107 | 0 | 17 | 2 | 36 | 17 | 406 | 0 | 0 |  | 610 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 157 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 8 | 0 | 18 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 413 | 0 | 0 | 35 | 0 | 113 | 0 | 1 | 0 | 290 | 108 | 0 | 0 | 0 | 18 | 95 | 0 | 0 | 395 | 3 | 172 | 0 | 6 |  | 4633 | 2860 | 7493 | 3317 | 610 | 1362 | 0 | 997 | 1017 | 30 | 0 | 36 | 84 | 40 | 0 | 86.95
9:00 | 0 | 0 | 0 | 0 | 200 | 70 | 0 | 399 | 364 |  | 0 | 225 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 16 | 8 | 32 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 22 | 25 | 26 | 25 | 32 | 36 | 0 | 0 | 30 | 0 | 0 | 8 | 31 | 0 | 0 | 0 |  | 0 | 2 | 0 | 10 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 325 | 192 | 8 | 0 | 5 | 0 | 0 | 51 | 0 | 0 | 0 | 21 | 10 | 17 | 15 | 84 | 62 | 0 | 19 | 0 | 30 | 0 | 51 | 46 | 0 | 0 | 62 | 30 | 0 | 130 | 18 | 24 | 10 | 0 | 0 | 8 | 0 | 32 | 0 | 0 | 46 | 0 | 35 | 12 | 12 | 17 | 6 | 384 | 28 | 95 | 17 | 2 | 51 | 17 | 72 | 17 | 9 | 12 | 400 | 17 | 10 | 17 | 107 | 0 | 17 | 12 | 36 | 17 | 377 | 0 | 0 |  | 803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 157 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 8 | 0 | 18 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 35 | 0 | 109 | 0 | 2 | 0 | 340 | 108 | 0 | 0 | 2 | 38 | 112 | 0 | 0 | 402 | 4 | 173 | 0 | 7 |  | 4765 | 3096 | 7861 | 3195 | 803 | 1394 | 0 | 1157 | 1075 | 30 | 0 | 34 | 84 | 89 | 0 | 86.95
10:00 | 0 | 0 | 0 | 0 | 200 | 70 | 0 | 401 | 351 |  | 0 | 225 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 16 | 8 | 32 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 22 | 25 | 27 | 25 | 32 | 42 | 0 | 0 | 30 | 0 | 0 | 8 | 31 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 295 | 187 | 8 | 0 | 5 | 0 | 0 | 51 | 0 | 0 | 0 | 21 | 10 | 25 | 15 | 84 | 33 | 0 | 19 | 1 | 30 | 0 | 51 | 46 | 0 | 0 | 62 | 30 | 0 | 130 | 18 | 24 | 10 | 0 | 0 | 8 | 0 | 32 | 0 | 0 | 46 | 0 | 35 | 16 | 12 | 17 | 6 | 388 | 28 | 105 | 17 | 3 | 51 | 17 | 72 | 17 | 9 | 12 | 400 | 17 | 28 | 17 | 107 | 0 | 17 | 20 | 36 | 17 | 348 | 0 | 0 |  | 804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 156 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 8 | 0 | 17 | 0 | 8 | 0 | 0 | 159 | 0 | 0 | 194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 35 | 0 | 105 | 0 | 3 | 0 | 300 | 108 | 0 | 0 | 2 | 55 | 115 | 25 | 0 | 402 | 10 | 173 | 0 | 66 |  | 4722 | 3144 | 7866 | 3115 | 804 | 1359 | 0 | 1179 | 1034 | 30 | 25 | 32 | 84 | 204 | 0 | 86.84
11:00 | 0 | 0 | 0 | 0 | 200 | 70 | 0 | 403 | 351 |  | 0 | 225 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 16 | 16 | 32 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 22 | 25 | 27 | 25 | 30 | 49 | 0 | 0 | 30 | 0 | 0 | 8 | 31 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 345 | 207 | 8 | 0 | 5 | 0 | 0 | 51 | 0 | 23 | 0 | 21 | 10 | 29 | 15 | 94 | 33 | 0 | 19 | 2 | 30 | 0 | 51 | 48 | 0 | 0 | 61 | 30 | 0 | 130 | 20 | 24 | 10 | 0 | 0 | 8 | 50 | 30 | 108 | 74 | 51 | 74 | 35 | 18 | 12 | 17 | 6 | 385 | 28 | 105 | 17 | 3 | 51 | 17 | 72 | 17 | 9 | 12 | 400 | 17 | 24 | 17 | 107 | 0 | 17 | 22 | 36 | 17 | 297 | 0 | 0 |  | 803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 156 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 8 | 0 | 17 | 0 | 8 | 0 | 0 | 159 | 0 | 0 | 191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 313 | 0 | 0 | 35 | 0 | 107 | 0 | 4 | 35 | 300 | 108 | 0 | 0 | 3 | 68 | 115 | 101 | 0 | 377 | 15 | 201 | 0 | 7 |  | 5096 | 3190 | 8286 | 3133 | 803 | 1327 | 306 | 1234 | 1037 | 30 | 101 | 55 | 94 | 166 | 0 | 86.94
12:00 | 0 | 0 | 0 | 0 | 200 | 70 | 0 | 403 | 346 |  | 0 | 225 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 16 | 16 | 32 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 22 | 25 | 27 | 25 | 28 | 49 | 0 | 0 | 30 | 0 | 0 | 10 | 40 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 345 | 218 | 8 | 0 | 5 | 0 | 0 | 51 | 0 | 30 | 0 | 21 | 10 | 28 | 9 | 108 | 33 | 0 | 19 | 1 | 30 | 0 | 51 | 44 | 0 | 0 | 60 | 30 | 0 | 130 | 19 | 24 | 10 | 0 | 0 | 8 | 85 | 32 | 204 | 92 | 48 | 87 | 35 | 18 | 12 | 17 | 6 | 384 | 28 | 105 | 17 | 4 | 51 | 17 | 60 | 17 | 9 | 12 | 400 | 18 | 35 | 17 | 107 | 0 | 17 | 22 | 36 | 17 | 297 | 0 | 0 |  | 785 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 156 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 16 | 8 | 0 | 16 | 0 | 8 | 0 | 0 | 159 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 35 | 0 | 103 | 0 | 5 | 35 | 300 | 108 | 0 | 0 | 4 | 73 | 115 | 243 | 0 | 468 | 17 | 200 | 0 | 66 |  | 5277 | 3440 | 8717 | 3120 | 785 | 1293 | 468 | 1220 | 1127 | 30 | 243 | 78 | 108 | 245 | 0 | 86.94
13:00 | 0 | 0 | 0 | 0 | 200 | 68 | 0 | 405 | 348 |  | 0 | 225 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 16 | 16 | 32 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 25 | 9 | 30 | 28 | 49 | 0 | 0 | 30 | 0 | 0 | 17 | 42 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 320 | 189 | 8 | 0 | 5 | 0 | 0 | 51 | 0 | 28 | 0 | 21 | 10 | 28 | 18 | 108 | 33 | 0 | 21 | 1 | 30 | 20 | 51 | 44 | 0 | 0 | 61 | 30 | 0 | 130 | 19 | 24 | 10 | 0 | 0 | 8 | 190 | 32 | 298 | 88 | 48 | 83 | 35 | 17 | 12 | 17 | 6 | 396 | 28 | 105 | 17 | 3 | 51 | 17 | 53 | 17 | 9 | 12 | 400 | 18 | 29 | 17 | 107 | 0 | 17 | 21 | 36 | 17 | 287 | 0 | 0 |  | 714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 156 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 16 | 8 | 0 | 16 | 0 | 8 | 0 | 0 | 159 | 0 | 0 | 160 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 257 | 0 | 0 | 35 | 0 | 34 | 0 | 5 | 35 | 340 | 108 | 0 | 0 | 3 | 68 | 115 | 120 | 0 | 522 | 16 | 200 | 0 | 41 |  | 5446 | 3198 | 8644 | 3082 | 714 | 1261 | 659 | 1169 | 1221 | 30 | 120 | 76 | 108 | 204 | 0 | 86.94
14:00 | 0 | 0 | 0 | 0 | 200 | 68 | 0 | 405 | 333 |  | 0 | 225 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 16 | 16 | 32 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 25 | 27 | 30 | 28 | 49 | 0 | 0 | 30 | 0 | 0 | 17 | 67 | 0 | 0 | 0 |  | 0 | 16 | 0 | 10 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 295 | 185 | 8 | 0 | 5 | 0 | 0 | 51 | 0 | 28 | 0 | 21 | 10 | 28 | 15 | 104 | 33 | 0 | 21 | 1 | 30 | 20 | 51 | 47 | 0 | 0 | 61 | 30 | 0 | 130 | 19 | 24 | 10 | 0 | 16 | 8 | 100 | 32 | 158 | 92 | 48 | 88 | 35 | 15 | 12 | 17 | 6 | 396 | 28 | 105 | 17 | 3 | 51 | 17 | 72 | 17 | 9 | 12 | 400 | 17 | 25 | 17 | 107 | 0 | 17 | 18 | 36 | 17 | 328 | 0 | 0 |  | 713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 156 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 16 | 8 | 0 | 15 | 0 | 8 | 0 | 0 | 159 | 0 | 0 | 160 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 211 | 0 | 0 | 35 | 0 | 34 | 0 | 3 | 35 | 350 | 108 | 0 | 0 | 1 | 58 | 115 | 0 | 0 | 546 | 8 | 200 | 0 | 84 |  | 5302 | 3085 | 8387 | 3150 | 713 | 1202 | 438 | 1187 | 1255 | 30 | 0 | 92 | 104 | 216 | 0 | 86.94
15:00 | 0 | 0 | 0 | 0 | 200 | 68 | 0 | 405 | 334 |  | 0 | 225 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 16 | 16 | 32 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 25 | 27 | 30 | 28 | 40 | 0 | 0 | 30 | 0 | 0 | 17 | 58 | 0 | 0 | 0 |  | 0 | 32 | 0 | 10 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 300 | 183 | 8 | 0 | 5 | 0 | 0 | 51 | 0 | 28 | 0 | 21 | 10 | 30 | 18 | 104 | 33 | 0 | 21 | 0 | 30 | 20 | 51 | 47 | 0 | 0 | 62 | 30 | 0 | 130 | 19 | 24 | 10 | 0 | 16 | 8 | 50 | 32 | 70 | 90 | 48 | 88 | 35 | 11 | 12 | 17 | 6 | 396 | 28 | 105 | 17 | 2 | 51 | 17 | 72 | 17 | 13 | 12 | 400 | 17 | 9 | 17 | 107 | 0 | 17 | 13 | 36 | 17 | 328 | 0 | 0 |  | 806 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 156 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 16 | 8 | 0 | 15 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 157 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 198 | 0 | 0 | 35 | 0 | 34 | 0 | 3 | 35 | 320 | 105 | 0 | 0 | 1 | 39 | 115 | 0 | 0 | 515 | 7 | 200 | 0 | 49 |  | 5147 | 3042 | 8189 | 3147 | 806 | 1185 | 298 | 1182 | 1195 | 30 | 0 | 108 | 104 | 134 | 0 | 86.93
16:00 | 0 | 0 | 0 | 0 | 200 | 70 | 0 | 405 | 333 |  | 0 | 225 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 16 | 16 | 32 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 25 | 27 | 30 | 28 | 41 | 0 | 0 | 30 | 0 | 0 | 17 | 130 | 0 | 0 | 0 |  | 0 | 40 | 0 | 10 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 10 | 270 | 194 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 28 | 1 | 20 | 10 | 33 | 15 | 98 | 33 | 0 | 21 | 0 | 30 | 20 | 51 | 44 | 0 | 0 | 62 | 30 | 0 | 130 | 18 | 24 | 10 | 0 | 16 | 8 | 10 | 30 | 104 | 70 | 53 | 70 | 35 | 5 | 12 | 17 | 34 | 396 | 28 | 105 | 38 | 1 | 51 | 17 | 72 | 17 | 12 | 12 | 400 | 17 | 7 | 28 | 107 | 0 | 17 | 5 | 36 | 17 | 268 | 3 | 0 |  | 806 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 156 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 16 | 8 | 0 | 15 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 160 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 0 | 35 | 0 | 100 | 0 | 2 | 35 | 290 | 107 | 0 | 0 | 0 | 19 | 115 | 0 | 0 | 426 | 3 | 200 | 0 | 20 |  | 5141 | 2915 | 8056 | 3147 | 806 | 1152 | 254 | 1312 | 1076 | 30 | 3 | 116 | 98 | 62 | 0 | 86.93
17:00 | 0 | 0 | 0 | 0 | 200 | 73 | 0 | 404 | 328 |  | 0 | 225 | 0 | 1 | 34 | 12 | 0 | 0 | 0 | 16 | 16 | 32 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 25 | 27 | 30 | 28 | 48 | 0 | 0 | 30 | 0 | 0 | 17 | 152 | 0 | 0 | 0 |  | 0 | 40 | 11 | 10 | 11 | 0 | 0 | 2 | 0 | 0 | 0 | 20 | 270 | 171 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 28 | 8 | 20 | 10 | 33 | 15 | 100 | 33 | 0 | 21 | 0 | 30 | 31 | 53 | 47 | 0 | 0 | 63 | 30 | 0 | 130 | 18 | 24 | 10 | 0 | 16 | 8 | 50 | 77 | 143 | 90 | 48 | 40 | 35 | 0 | 12 | 17 | 65 | 396 | 37 | 105 | 51 | 0 | 118 | 17 | 72 | 17 | 9 | 12 | 400 | 17 | 1 | 40 | 107 | 0 | 17 | 1 | 44 | 17 | 258 | 6 | 0 |  | 805 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 7 | 0 | 8 | 151 | 17 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 42 | 16 | 8 | 0 | 15 | 0 | 8 | 0 | 0 | 159 | 0 | 0 | 160 | 0 | 18 | 0 | 0 | 10 | 0 | 0 | 162 | 1 | 1 | 35 | 0 | 113 | 0 | 0 | 35 | 300 | 107 | 0 | 0 | 0 | 2 | 115 | 0 | 0 | 491 | 0 | 200 | 0 | 2 |  | 5440 | 3008 | 8448 | 3168 | 805 | 1144 | 334 | 1567 | 1150 | 30 | 6 | 138 | 100 | 6 | 0 | 86.93
18:00 | 0 | 0 | 0 | 0 | 200 | 73 | 0 | 385 | 331 |  | 0 | 225 | 0 | 16 | 34 | 15 | 0 | 0 | 0 | 16 | 16 | 32 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 10 | 30 | 28 | 48 | 0 | 0 | 30 | 0 | 0 | 17 | 151 | 0 | 0 | 0 |  | 0 | 40 | 51 | 10 | 12 | 0 | 0 | 8 | 0 | 0 | 0 | 10 | 270 | 131 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 21 | 25 | 20 | 10 | 33 | 20 | 114 | 33 | 0 | 20 | 0 | 30 | 31 | 53 | 47 | 0 | 0 | 63 | 86 | 0 | 130 | 18 | 24 | 10 | 0 | 16 | 8 | 67 | 97 | 205 | 50 | 50 | 70 | 35 | 0 | 12 | 22 | 75 | 396 | 47 | 105 | 51 | 0 | 290 | 17 | 72 | 99 | 9 | 12 | 400 | 17 | 0 | 131 | 107 | 0 | 17 | 0 | 54 | 17 | 228 | 0 | 0 |  | 903 | 0 | 0 | 0 | 59 | 0 | 0 | 0 | 10 | 70 | 40 | 156 | 24 | 0 | 0 | 0 | 0 | 16 | 5 | 68 | 0 | 42 | 16 | 8 | 28 | 15 | 0 | 8 | 0 | 0 | 159 | 0 | 0 | 139 | 0 | 27 | 0 | 0 | 30 | 0 | 0 | 158 | 3 | 40 | 58 | 0 | 113 | 0 | 0 | 60 | 350 | 120 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 537 | 0 | 249 | 0 | 0 |  | 6015 | 3626 | 9641 | 3048 | 903 | 1225 | 462 | 2207 | 1295 | 30 | 0 | 357 | 114 | 0 | 0 | 86.92
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 0 | 200 | 73 | 0 | 402 | 333 |  | 0 | 225 | 0 | 17 | 34 | 20 | 0 | 0 | 0 | 16 | 16 | 32 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 27 | 30 | 28 | 48 | 0 | 0 | 30 | 0 | 0 | 17 | 152 | 0 | 0 | 0 |  | 6 | 40 | 36 | 10 | 10 | 0 | 0 | 14 | 0 | 0 | 0 | 10 | 270 | 131 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 21 | 8 | 21 | 10 | 33 | 20 | 112 | 53 | 0 | 20 | 0 | 30 | 31 | 53 | 47 | 0 | 0 | 63 | 86 | 0 | 130 | 19 | 24 | 10 | 0 | 16 | 8 | 10 | 95 | 44 | 50 | 48 | 70 | 35 | 0 | 12 | 51 | 72 | 396 | 47 | 105 | 51 | 0 | 290 | 17 | 72 | 100 | 9 | 12 | 400 | 17 | 0 | 162 | 107 | 0 | 17 | 0 | 54 | 17 | 258 | 0 | 0 |  | 904 | 0 | 0 | 0 | 66 | 0 | 0 | 0 | 13 | 70 | 32 | 180 | 24 | 0 | 0 | 0 | 0 | 32 | 6 | 67 | 0 | 50 | 40 | 8 | 32 | 18 | 0 | 8 | 0 | 0 | 159 | 0 | 0 | 136 | 0 | 43 | 0 | 0 | 10 | 0 | 0 | 154 | 12 | 10 | 70 | 0 | 113 | 0 | 0 | 75 | 380 | 140 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 522 | 0 | 253 | 0 | 0 |  | 5922 | 3742 | 9664 | 3172 | 904 | 1252 | 194 | 2297 | 1314 | 30 | 0 | 389 | 112 | 0 | 0 | 86.92
19:30 | 0 | 0 | 0 | 0 | 200 | 73 | 0 | 408 | 324 |  | 0 | 225 | 0 | 17 | 34 | 25 | 0 | 0 | 0 | 16 | 16 | 32 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 27 | 30 | 28 | 48 | 0 | 0 | 30 | 0 | 0 | 17 | 151 | 0 | 0 | 0 |  | 12 | 40 | 51 | 10 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 10 | 270 | 131 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 21 | 8 | 21 | 10 | 33 | 20 | 110 | 53 | 0 | 20 | 0 | 30 | 31 | 53 | 47 | 0 | 0 | 63 | 86 | 0 | 130 | 20 | 24 | 10 | 0 | 16 | 8 | 10 | 95 | 11 | 50 | 48 | 25 | 35 | 0 | 12 | 17 | 74 | 396 | 47 | 105 | 51 | 0 | 295 | 17 | 72 | 100 | 9 | 12 | 400 | 17 | 0 | 162 | 107 | 0 | 17 | 0 | 54 | 17 | 258 | 0 | 0 |  | 903 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 37 | 65 | 40 | 181 | 23 | 0 | 0 | 0 | 0 | 32 | 7 | 60 | 0 | 50 | 16 | 8 | 35 | 20 | 0 | 8 | 0 | 0 | 159 | 0 | 0 | 136 | 0 | 44 | 0 | 0 | 10 | 0 | 0 | 155 | 18 | 10 | 70 | 0 | 113 | 0 | 0 | 75 | 390 | 140 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 522 | 0 | 250 | 0 | 0 |  | 5819 | 3757 | 9576 | 3180 | 903 | 1236 | 116 | 2284 | 1321 | 30 | 0 | 396 | 110 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 0 | 200 | 73 | 0 | 407 | 316 |  | 0 | 225 | 0 | 17 | 34 | 25 | 0 | 0 | 0 | 16 | 16 | 32 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 27 | 30 | 28 | 48 | 0 | 0 | 30 | 0 | 0 | 17 | 151 | 0 | 0 | 0 |  | 12 | 40 | 51 | 10 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 10 | 300 | 131 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 21 | 8 | 21 | 10 | 33 | 21 | 110 | 62 | 0 | 21 | 0 | 30 | 31 | 53 | 47 | 0 | 0 | 62 | 86 | 0 | 130 | 19 | 24 | 10 | 0 | 16 | 8 | 0 | 97 | 70 | 25 | 48 | 0 | 35 | 0 | 12 | 17 | 75 | 396 | 47 | 105 | 51 | 0 | 200 | 17 | 72 | 100 | 9 | 12 | 400 | 17 | 0 | 162 | 107 | 0 | 17 | 0 | 46 | 17 | 258 | 0 | 0 |  | 903 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 31 | 60 | 40 | 181 | 24 | 0 | 0 | 0 | 0 | 32 | 12 | 59 | 0 | 50 | 16 | 8 | 35 | 20 | 0 | 8 | 0 | 0 | 159 | 0 | 0 | 136 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 156 | 18 | 0 | 70 | 0 | 113 | 0 | 0 | 75 | 360 | 108 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 523 | 0 | 249 | 0 | 0 |  | 5753 | 3673 | 9426 | 3221 | 903 | 1203 | 95 | 2184 | 1291 | 30 | 0 | 389 | 110 | 0 | 0 | 86.92
21:00 | 0 | 0 | 0 | 0 | 200 | 73 | 0 | 409 | 319 |  | 0 | 225 | 0 | 17 | 34 | 15 | 0 | 0 | 0 | 16 | 16 | 32 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 25 | 27 | 30 | 28 | 48 | 0 | 0 | 30 | 0 | 0 | 17 | 151 | 0 | 0 | 0 |  | 12 | 38 | 51 | 10 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 10 | 270 | 153 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 21 | 8 | 21 | 10 | 33 | 21 | 108 | 76 | 0 | 21 | 0 | 30 | 31 | 53 | 47 | 0 | 0 | 63 | 86 | 0 | 131 | 19 | 24 | 10 | 0 | 16 | 8 | 0 | 97 | 146 | 90 | 48 | 25 | 35 | 0 | 12 | 17 | 73 | 396 | 47 | 105 | 51 | 0 | 51 | 17 | 72 | 100 | 9 | 12 | 400 | 17 | 0 | 162 | 107 | 0 | 17 | 0 | 44 | 17 | 258 | 0 | 0 |  | 909 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 45 | 60 | 40 | 176 | 25 | 0 | 0 | 0 | 0 | 32 | 16 | 59 | 0 | 42 | 16 | 8 | 35 | 20 | 0 | 8 | 0 | 0 | 159 | 0 | 0 | 136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 18 | 0 | 70 | 0 | 113 | 0 | 0 | 75 | 340 | 109 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 536 | 0 | 250 | 0 | 0 |  | 5690 | 3645 | 9335 | 3179 | 909 | 1222 | 261 | 1936 | 1285 | 30 | 0 | 405 | 108 | 0 | 0 | 86.92
22:00 | 0 | 0 | 0 | 0 | 200 | 73 | 0 | 387 | 294 |  | 0 | 225 | 0 | 17 | 34 | 15 | 0 | 0 | 0 | 16 | 16 | 32 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 25 | 27 | 30 | 29 | 16 | 0 | 0 | 30 | 0 | 0 | 17 | 151 | 0 | 0 | 0 |  | 12 | 32 | 51 | 10 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 10 | 270 | 153 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 21 | 8 | 21 | 10 | 33 | 21 | 98 | 94 | 0 | 21 | 0 | 30 | 31 | 53 | 47 | 0 | 0 | 63 | 86 | 0 | 131 | 19 | 24 | 10 | 0 | 16 | 8 | 0 | 97 | 0 | 0 | 48 | 0 | 35 | 0 | 12 | 17 | 75 | 387 | 47 | 88 | 51 | 0 | 51 | 17 | 72 | 81 | 9 | 12 | 370 | 17 | 0 | 144 | 107 | 0 | 17 | 0 | 46 | 17 | 258 | 0 | 0 |  | 908 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | 40 | 7 | 24 | 174 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 42 | 16 | 8 | 35 | 20 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 18 | 0 | 70 | 0 | 70 | 0 | 0 | 75 | 320 | 109 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 517 | 0 | 249 | 0 | 0 |  | 5269 | 3459 | 8728 | 3139 | 908 | 1234 | 0 | 1805 | 1246 | 30 | 0 | 268 | 98 | 0 | 0 | 86.91
23:00 | 0 | 0 | 0 | 0 | 200 | 71 | 0 | 392 | 293 |  | 0 | 225 | 0 | 17 | 34 | 8 | 0 | 0 | 0 | 16 | 16 | 32 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 25 | 27 | 25 | 29 | 16 | 0 | 0 | 30 | 0 | 0 | 17 | 151 | 0 | 0 | 0 |  | 12 | 32 | 17 | 10 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 10 | 270 | 153 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 21 | 8 | 21 | 10 | 33 | 21 | 120 | 100 | 0 | 21 | 0 | 30 | 31 | 53 | 47 | 0 | 0 | 63 | 86 | 0 | 130 | 19 | 24 | 10 | 0 | 16 | 8 | 0 | 30 | 0 | 0 | 48 | 0 | 35 | 0 | 12 | 17 | 15 | 403 | 47 | 88 | 30 | 0 | 51 | 17 | 72 | 17 | 9 | 12 | 400 | 17 | 0 | 17 | 107 | 0 | 17 | 0 | 22 | 17 | 259 | 0 | 0 |  | 907 | 0 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 8 | 35 | 20 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 242 | 18 | 0 | 35 | 0 | 34 | 0 | 0 | 75 | 330 | 105 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 511 | 0 | 250 | 0 | 0 |  | 4944 | 3349 | 8293 | 3223 | 907 | 1275 | 0 | 1350 | 1251 | 30 | 0 | 137 | 120 | 0 | 0 | 86.91
24:00 | 0 | 0 | 0 | 0 | 200 | 71 | 0 | 399 | 326 |  | 0 | 225 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 16 | 8 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 22 | 27 | 25 | 30 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 151 | 0 | 0 | 0 |  | 12 | 0 | 0 | 10 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 5 | 270 | 153 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 8 | 21 | 10 | 33 | 21 | 92 | 93 | 0 | 21 | 0 | 30 | 31 | 53 | 47 | 0 | 0 | 62 | 86 | 0 | 130 | 20 | 24 | 10 | 0 | 16 | 8 | 0 | 30 | 0 | 0 | 48 | 0 | 35 | 0 | 12 | 17 | 6 | 404 | 28 | 50 | 17 | 0 | 51 | 17 | 72 | 0 | 9 | 12 | 400 | 17 | 0 | 17 | 107 | 0 | 17 | 0 | 0 | 17 | 258 | 0 | 0 |  | 722 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 8 | 0 | 20 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 248 | 18 | 0 | 35 | 0 | 34 | 0 | 0 | 70 | 330 | 109 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 512 | 0 | 250 | 0 | 0 |  | 4640 | 3040 | 7680 | 3215 | 722 | 1318 | 0 | 1051 | 1252 | 30 | 0 | 0 | 92 | 0 | 0 | 86.91
KWH | 0 | 0 | 0 | 0 | 4746700 | 1515909 | 0 | 9658370 | 7906000 |  | 0 | 5167300 | 0 | 126720 | 522759 | 130056 | 0 | 0 | 0 | 262080 | 254304 | 529920 | 0 | 0 | 0 | 0 | 392760 | 662358 | 605984 | 512604 | 600000 | 588060 | 702360 | 737200 | 666720 | 0 | 0 | 720000 | 0 | 0 | 237636 | 2514559 | 0 | 0 | 0 |  | 85200 | 352368 | 288718 | 264240 | 34560 | 0 | 0 | 430560 | 0 | 0 | 0 | 204200 | 7207000 | 4339000 | 133818 | 0 | 96264 | 0 | 0 | 1074244 | 0 | 317264 | 91594 | 475668 | 241200 | 757000 | 390780 | 2199360 | 1546560 | 0 | 476388 | 5400 | 716000 | 538080 | 1026600 | 969048 | 0 | 0 | 1377408 | 1078080 | 0 | 3100560 | 455000 | 517300 | 231840 | 0 | 323400 | 192384 | 609408 | 948436 | 1559079 | 790547 | 912000 | 677050 | 637200 | 119475 | 299520 | 399360 | 543636 | 9374000 | 630000 | 1699200 | 559527 | 21602 | 1972145 | 452016 | 1751338 | 653220 | 176400 | 305280 | 9446400 | 360960 | 161750 | 1101600 | 2564291 | 0 | 444240 | 135965 | 772800 | 320400 | 7559900 | 10036 | 0 |  | 18379636 | 0 | 0 | 0 | 452160 | 0 | 0 | 0 | 125280 | 258432 | 191625 | 4015320 | 469000 | 0 | 0 | 0 | 0 | 114698 | 39705 | 249000 | 0 | 715132 | 166355 | 139805 | 188973 | 354480 | 0 | 173574 | 0 | 0 | 3903900 | 0 | 0 | 4044364 | 0 | 221273 | 0 | 0 | 57600 | 0 | 0 | 6005091 | 107520 | 100907 | 901440 | 0 | 1484985 | 0 | 23660 | 770976 | 8317000 | 2653364 | 0 | 0 | 17340 | 446400 | 1911360 | 509345 | 0 | 10915650 | 86572 | 4967300 | 0 | 334800 |  | 119266226 | 73814022 | 193080248 | 77331576 | 18379636 | 29532634 | 3794591 | 28515543 | 28103850 | 720000 | 519381 | 2630713 | 2199360 | 1352964 | 0
Fuel Cost | 0 | 0 | 0 | 0 | 5316304 | 2016158.97 | 0 | 10141288.5 | 8538480 |  | 0 | 5632357 | 0 | 1416729.6 | 6926556.75 | 1723242 | 0 | 0 | 0 | 3831609.6 | 3578057.28 | 8590003.2 | 0 | 0 | 0 | 0 | 4995907.2 | 8941833 | 8126245.44 | 384453 | 450000 | 0 | 0 | 0 | 11340907.2 | 0 | 0 | 194400 | 0 | 0 | 3885348.6 | 2615141.36 | 0 | 0 | 0 |  | 1111860 | 5877498.24 | 4913980.36 | 3569882.4 | 438220.8 | 0 | 0 | 1433764.8 | 0 | 0 | 0 | 226662 | 7855630 | 5033240 | 172625.22 | 0 | 108778.32 | 0 | 0 | 1793987.48 | 0 | 5479149.28 | 1231939.3 | 651665.16 | 180900 | 1324750 | 293085 | 15791404.8 | 1685750.4 | 0 | 647887.68 | 86076 | 980920 | 710265.6 | 1786284 | 1676453.04 | 0 | 0 | 2672171.52 | 2458022.4 | 0 | 3131565.6 | 978250 | 770777 | 459043.2 | 0 | 242550 | 146211.84 | 12773191.68 | 12946151.4 | 32678295.84 | 16340606.49 | 12293760 | 13994623.5 | 8825220 | 1396662.75 | 3091046.4 | 5455257.6 | 7214049.72 | 8624080 | 7660800 | 24570432 | 7078016.55 | 0 | 23152982.3 | 4922454.24 | 18616722.94 | 8864195.4 | 2273796 | 3596198.4 | 8690688 | 4674432 | 2337287.5 | 13979304 | 29181631.58 | 0 | 5801774.4 | 1624781.75 | 11568816 | 4219668 | 0 | 0 | 0 |  | 55138908 | 0 | 0 | 0 | 4706985.6 | 0 | 0 | 0 | 2256292.8 | 4651776 | 2753651.25 | 4497158.4 | 909860 | 0 | 0 | 0 | 0 | 1923485.46 | 694440.45 | 3894360 | 0 | 11842585.92 | 2813063.05 | 1905542.15 | 3187974.51 | 733773.6 | 0 | 131395.518 | 0 | 0 | 20651631 | 0 | 0 | 4691462.24 | 0 | 283229.44 | 0 | 0 | 1208448 | 0 | 0 | 5945040.09 | 1445068.8 | 2116019.79 | 10664035.2 | 0 | 18859309.5 | 0 | 261443 | 9359648.64 | 74936170 | 2706431.28 | 0 | 0 | 196115.4 | 5236272 | 29301148.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 493013200.58 | 289902725.888 | 782915926.468 | 72695483.578 | 55138908 | 37033058.08 | 79111185.3 | 371943023.96 | 95587801 | 194400 | 0 | 44282023.35 | 15791404.8 | 11138638.4 | 0
Yesterday Day Peak | 0 | 0 | 0 | 0 | 200 | 70 | 0 | 403 | 346 |  | 0 | 225 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 16 | 16 | 32 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 22 | 25 | 27 | 25 | 28 | 49 | 0 | 0 | 30 | 0 | 0 | 10 | 40 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 345 | 218 | 8 | 0 | 5 | 0 | 0 | 51 | 0 | 30 | 0 | 21 | 10 | 28 | 9 | 108 | 33 | 0 | 19 | 1 | 30 | 0 | 51 | 44 | 0 | 0 | 60 | 30 | 0 | 130 | 19 | 24 | 10 | 0 | 0 | 8 | 85 | 32 | 204 | 92 | 48 | 87 | 35 | 18 | 12 | 17 | 6 | 384 | 28 | 105 | 17 | 4 | 51 | 17 | 60 | 17 | 9 | 12 | 400 | 18 | 35 | 17 | 107 | 0 | 17 | 22 | 36 | 17 | 297 | 0 | 0 |  | 785 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 156 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 16 | 8 | 0 | 16 | 0 | 8 | 0 | 0 | 159 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 35 | 0 | 103 | 0 | 5 | 35 | 300 | 108 | 0 | 0 | 4 | 73 | 115 | 243 | 0 | 468 | 17 | 200 | 0 | 66 |  | 8717 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 0 | 200 | 73 | 0 | 402 | 333 | 0 | 0 | 225 | 0 | 17 | 34 | 20 | 0 | 0 | 0 | 16 | 16 | 32 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 27 | 30 | 28 | 48 | 0 | 0 | 30 | 0 | 0 | 17 | 152 | 0 | 0 | 0 | 0 | 6 | 40 | 36 | 10 | 10 | 0 | 0 | 14 | 0 | 0 | 0 | 10 | 270 | 131 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 21 | 8 | 21 | 10 | 33 | 20 | 112 | 53 | 0 | 20 | 0 | 30 | 31 | 53 | 47 | 0 | 0 | 63 | 86 | 0 | 130 | 19 | 24 | 10 | 0 | 16 | 8 | 10 | 95 | 44 | 50 | 48 | 70 | 35 | 0 | 12 | 51 | 72 | 396 | 47 | 105 | 51 | 0 | 290 | 17 | 72 | 100 | 9 | 12 | 400 | 17 | 0 | 162 | 107 | 0 | 17 | 0 | 54 | 17 | 258 | 0 | 0 |  | 904 | 0 | 0 | 0 | 66 | 0 | 0 | 0 | 13 | 70 | 32 | 180 | 24 | 0 | 0 | 0 | 0 | 32 | 6 | 67 | 0 | 50 | 40 | 8 | 32 | 18 | 0 | 8 | 0 | 0 | 159 | 0 | 0 | 136 | 0 | 43 | 0 | 0 | 10 | 0 | 0 | 154 | 12 | 10 | 70 | 0 | 113 | 0 | 0 | 75 | 380 | 140 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 522 | 0 | 253 | 0 | 0 |  | 9664 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 0 | 200 | 70 | 0 | 400 | 330 | 0 | 0 | 225 | 0 | 17 | 34 | 20 | 0 | 0 | 0 | 16 | 16 | 32 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 27 | 30 | 28 | 50 | 0 | 0 | 30 | 0 | 0 | 17 | 150 | 0 | 0 | 0 | 0 | 12 | 40 | 50 | 10 | 10 | 0 | 0 | 15 | 0 | 0 | 0 | 330 | 0 | 150 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 30 | 8 | 21 | 10 | 33 | 20 | 152 | 100 | 0 | 19 | 0 | 30 | 43 | 53 | 40 | 0 | 0 | 66 | 86 | 0 | 130 | 19 | 24 | 10 | 0 | 16 | 8 | 100 | 95 | 150 | 50 | 48 | 50 | 35 | 0 | 12 | 51 | 70 | 400 | 47 | 105 | 51 | 0 | 290 | 35 | 72 | 17 | 9 | 12 | 400 | 17 | 0 | 162 | 107 | 0 | 17 |  | 0 | 17 | 330 |  |  |  | 934 | 0 | 0 | 0 | 99 | 0 | 0 | 0 | 40 | 70 | 40 | 180 | 24 |  | 0 | 0 | 0 | 34 | 25 | 67 | 0 | 50 | 40 | 8 | 32 | 20 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 150 |  | 43 | 0 | 0 | 50 | 0 | 0 | 350 | 18 | 100 | 70 | 0 | 113 | 0 | 0 | 75 | 400 | 110 |  | 35 |  |  | 113 | 0 |  | 520 |  | 250 | 0
Forecast for Day | 0 | 0 | 0 | 0 | 200 | 70 | 0 | 400 | 330 | 0 | 0 | 225 | 0 | 17 | 34 | 0 | 0 | 0 | 0 | 16 | 16 | 32 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 25 | 27 | 25 | 28 | 50 | 0 | 0 | 30 | 0 | 0 | 17 | 150 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 10 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 330 | 0 | 150 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 25 | 8 | 21 | 10 | 30 | 20 | 135 | 70 | 0 | 19 | 1.6 | 30 | 43 | 53 | 30 | 0 | 0 | 65 | 40 | 0 | 130 | 19 | 24 | 10 | 0 | 16 | 8 | 0 | 32 |  | 0 | 46 | 0 | 35 | 20 | 12 | 17 | 3 | 400 | 28 | 90 | 17 | 5 | 51 | 17 | 72 | 17 | 8 | 12 | 400 | 17 | 50 | 17 | 107 | 0 | 17 | 30 | 0 | 17 | 330 |  |  |  | 838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 8 | 0 | 20 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 150 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 350 | 18 | 0 | 35 | 0 | 34 | 0 | 8 | 35 | 300 | 110 |  | 0 | 6 | 100 | 35 | 0 |  | 420 | 30 | 230 | 0 | [5 empty] | g | h | o | c | h | t | s
Generation at 08:00(Today) | 0 | 0 | 0 | 0 | 200 | 64 | 0 | 392 | 335 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 25 | 0 | 0 | 16 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 160 | 220 | 141 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 21 | 10 | 30 | 0 | 86 | 34 | 0 | 19 | 0 | 30 | 31 | 25 | 16 | 0 | 0 | 62 | 40 | 0 | 50 | 19 | 24 | 10 | 0 | 16 | 8 | 0 | 32 | 0 | 0 | 18 | 0 | 0 | 6 | 12 | 17 | 6 | 372 | 9 | 2 | 16 | 1 | 0 | 17 | 17 | 0 | 9 | 12 | 400 | 17 | 7 | 17 | 20 | 0 | 0 | 1 | 0 | 4 | 330 | 0 | 0 | 0 | 611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 156 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 407 | 0 | 0 | 0 | 0 | 7 | 0 | 1 | 0 | 250 | 107 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 430 | 2 | 231 | 0 |  | 0 |  |  |  | 106.8642 | 18.3796 | 35.4602 | 28.1039 | 0.72 | 2.1994 | 1.353
193.0802
| Minimum Generation |  | 6243 | 5:00
| Highest Generation |  | 9664 | 19:00
| Day Peak Generation |  | 8717 | 12:00
| Evening Peak Generation |  | 9664 | 19:00
| HVDC Max Flow |  | 909 | 21:00
| HVDC EvPeak Flow |  | 904 | 19:00
| Load factor L.F |  | 83.25% | [161 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2022-12-27
Till now the maximum generation is : - |  |  |  | 14782 | 21:00 | Hrs on | 2022-04-16
The Summary of Yesterday's |  |  | 2022-12-26 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 8717 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 5809
Evening Peak Generation : |  |  | 9664 | MW Hour : | 19:00 | Available Max Generation : |  | 10484
E.P. Demand (at gen end) : |  |  | 9664 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 9800
Maximum Generation : |  |  | 9664 | MW Hour : | 19:00 | Reserve(Generation end) |  | 684
Total Gen. (MKWH) : |  |  | 193.0802 | System Load Factor : | 83.25% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 34 | MW at | 18:30 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2022-12-27
Actual : |  | 86.89 | Ft.(MSL) , | Rule curve : | 103.3 | Ft.( MSL )
Gas Consumed : |  | Total = | 834.57 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 109728541.658
: |  |  | Coal : | 95587801 | Oil : | 495336232.61 | Total : | 700652575.268
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 0 | 0:00 | 3362.0451 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 952.4089 |  |  | 0 | 0%
Khulna Area |  | 0 | 0:00 | 1257.1007 |  |  | 0 | 0%
Rajshahi Area |  | 0 | 0:00 | 1115.3614 |  |  | 0 | 0%
Cumilla Area |  | 0 | 0:00 | 949.4759 |  |  | 0 | 0%
Mymensingh Area |  | 0 | 0:00 | 784.409 |  |  | 0 | 0%
Sylhet Area |  | 0 | 0:00 | 350.5967 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 285.7977 |  |  | 0 | 0%
Rangpur Area |  | 0 | 0:00 | 619.3421 |  |  | 0 | 0%
Total |  | 0 |  | 9676.5375 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1, 2
2) Ghorasal-3, 4
3) Ashuganj-5
4) Baghabari-70,100 MW
5) Raozan unit-1 & 2
6) Siddhirganj 210 MW .
7) Shajibazar 330 MW
8) Sirajganj-2
9) Bibiana-II 341 MW CCPP (Summit)
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
08:02 | 18:48 | Savar 132/33kV S/S T-3 LT Scheduled S/D Due to Due to conversion of 132KV Main and Transfer BUS to Double BUS Scheme.
08:02 | 18:48 | Savar 132/33kV S/S T-3 HT Scheduled S/D Due to Due to conversion of 132KV Main and Transfer BUS to Double BUS Scheme.
08:09 |  | Barishal-Barishal(N) 132 kV Ckt-1 Scheduled S/D from Barishal 230/132kV end Due to Annual Maitenance and from
Barishal 132/33kV end Due to Annual Maintenance
08:14 | 16:25 | Bagerhat 132/33kV S/S Transformer-3 ( 423 T) LT Scheduled S/D Due to Annual Maintenance.
08:15 | 16:24 | Bagerhat 132/33kV S/S Transformer-3 ( 423 T) HT Scheduled S/D Due to Annual Maintenance.
08:21 | 15:25 | Pabna 132/33kV S/S T-2 LT Scheduled S/D
08:22 | 15:25 | Pabna 132/33kV S/S T-2 HT Scheduled S/D
08:31 | 10:22 | Cox'sbazar-Dohazari 132 kV Ckt-1 Scheduled S/D from Coxsbazar 132/33kV end Due to Annual Maintenance (Cox Side) |  |  |  |  | 20.0MW load interrup.
|  | and from Dohazari 132/33kVend. |  |  |  |  | Coxsbazar 132/33 kV end.
08:31 | 16:01 | Amnura-Chapainawabganj-132kV Ckt-1 Scheduled S/D from Amnura 132/33kV end Due to Annual maintenance and from
Chapai 132/33kV end Due to for annual maintenance
08:37 | 17:14 | Ashuganj-Ghorasal 132kV ckt-2 shutdown due to annual maintenance by Narsingdi ss.
08:39 | 13:57 | Bakulia-Sikalbaha 132 kV Ckt-1 Scheduled S/D from Shikalbaha 230/132kV end Due to Deadline checking and from
Bakulia 132/33kV end Due to For Annual Maintenance work.
08:41 | 09:21 | Rangpur 132/33kV S/S Rangpur-Teesta Solar-2 Tripped showing relays Due to Unknown
08:42 | 16:03 | Sonargaon 132/33kV S/S OPML(IEL-1) Scheduled S/D Due to Annual maintenance .
08:45 | 09:27 | Gollamari 132/33kV S/S Tr-2 LT Scheduled S/D Due to For WZPDCL maintenance work
08:46 | 09:26 | Gollamari 132/33kV S/S Tr-2 HT Scheduled S/D Due to WZPDCL maintenance
08:47 | 15:46 | Mahasthangar-Palashbari 132kV Ckt-2 Scheduled S/D from Palashbari 132/33kV end Due to Annual Maintenance.
08:52 | 15:53 | Kodda 132/33kV S/S Tr-3 (426T) HT Scheduled S/D Due to Annual maintenance
08:52 | 15:56 | Kodda 132/33kV S/S Tr-3 (426T) LT Scheduled S/D Due to Annual maintenance
08:52 | 16:58 | Ghorasal- Ishwardi 230 kV Ckt-2 Scheduled S/D from Ishurdi 230/132kV end Due to A/M
08:55 | 16:30 | Shahjibazar-Sreemangal 132kV Ckt-2 Scheduled S/D from Sreemongol 132/33kV end Due to For annual maintenance of
Sreemongol to Shahjibazar circuit-2 bay. and from Shahjibazar 132/33kV end Due to S/D taken by Sreemongal S/S.
09:10 | 14:21 | Rajshahi 230/132/33kV S/S T-02 (416T) HT Scheduled S/D Due to Annual Maintenance.
09:10 | 14:23 | Rajshahi 230/132/33kV S/S T-02 (416T) LT Scheduled S/D Due to Annual Maintenance.
09:11 |  | Jhenaidah 230/132kV S/S Jhenaidah (New)-Jhenaidah (Old) Ckt-1 Scheduled S/D Due to Annual Maintenance
09:19 | 22:23 | Aminbazar-Mirpur 132kV Ckt-2 Scheduled S/D from Mirpur 132/33kV end Due to Dead line checking and Disk insulator
replacement work. and from Aminbazar 400/230/132kV end Due to Annual maintenance
09:24 | 15:58 | Bog-Sherpur 132/33kV S/S Transformer-2 (414T) HT Scheduled S/D Due to Annual maintenance
09:30 | 15:40 | Purbasadipur-Thakurgaon-EPV 132kV Ckt-1 Scheduled S/D from Thakurgaon 132/33kV end Due to Annual Maintenance
09:32 | 14:46 | Jamalpur 132/33kV S/S T-3 HT Scheduled S/D Due to Annual maintenance work
09:32 | 14:46 | Jamalpur 132/33kV S/S T-3 LT Scheduled S/D Due to Annual maintenance work
09:40 | 12:26 | Bhandaria 132/33kV S/S Transformer-2 LT Forced S/D Due to 33 kv incoming breaker Spring charge motor repair.
09:52 |  | Gopalgonj(N) - Rampal P/S 400kv Ckt-1 open from Gopalgonj (N) S/S.
09:53 | 15:34 | Purbasadipur-Thakurgaon-EPV 132kV Ckt-1 Scheduled S/D from Purbasadipur 132/33kV end Due to annual maintanance
09:56 |  | Gopalgonj(N) - Rampal P/S 400kv Ckt-2 open from Gopalgonj (N) S/S.
09:57 | 19:48 | BSRM-Mirsharai 230 kV Ckt-1 Scheduled S/D from Mirsorai 230/33kV end Due to Annual Maintenance
09:58 |  | Khulna 330 MW CCPP GT P/S Synchronize.
10:10 | 16:22 | Tongi 230/132/33kV S/S Tongi-Mill Gate Ckt-1 Project Work S/D.
10:11 | 14:22 | Kishorgonj 132 KV bus coupler
10:11 |  | Kishorgonj 132 KV bus coupler
10:13 | 22:26 | Mirpur-Uttara 132kV Ckt-1 Scheduled S/D from Mirpur 132/33kV end Due to Relay installation work by SPMD
10:40 | 12:25 | Bhandaria 132/33kV S/S Transformer-2 HT Forced S/D Due to 33 kv incoming breaker Spring charge motor repair
11:15 | 12:32 | HVDC Bheramera- Jhenaidah 230kV Ckt-1 Project Work S/D from Jhenaidah 230/132kV end Due to Nldc Signal testing and operation
11:44 |  | Barisal GT Axu. Transformer close.
12:00 |  | Day Peak Gen. 8717 MW
12:01 |  | Sirajgonj Unit-2 GT was sync.
12:37 | 13:31 | HVDC Bheramera-Jhenaidah 230kV Ckt-2 Project Work S/D from Jhenaidah 230/132kV end Due to NLDC signal testing and
operation
13:29 |  | Sikalbaha 225MW ST sync
13:36 |  | Khulna 330 MW CCPP GT P/S Running as Island mood.
| 14:02 | Hathazari 230/132/33kV S/S Shikolbaha-02 is restored.
14:05 |  | Sikalbaha 225MW ST tripped |  |  |  |  | 67MW generation interrup.
14:05 |  | Modunaghat 400/230 KV xfr ATR-1 charged for the first time
| 14:08 | Shikalbaha 230/132kV S/S Hathazari-02 is restored.
15:29 |  | Ashugonj North 360MW GT was sync.
15:30 |  | Modunaghat Bashkhali 400 KV ckt-1 charged
15:34 | 15:58 | Savar 132/33kV S/S T-2 LT Forced S/D Due to 132 KV Transfer Bus Maintenance Work. |  |  |  |  | 30.0MW load interrup.
15:34 | 15:58 | Savar 132/33kV S/S T-2 HT Forced S/D Due to 132 KV Transfer Bus Maintenance Work. |  |  |  |  | 30.0MW load interrup.
16:18 |  | Modunaghat Bashkhali 400 KV ckt-1 shutdown
16:30 | 18:19 | Savar 132/33kV S/S Main Bus Scheduled S/D Due to Due to conversion of 132KV Main and Transfer BUS to 132KV Double Bus.
| 16:54 | Maniknagar-Siddhirganj 230kV Ckt-2 is restored.
| 17:05 | Maniknagar 230/132kV S/S Auto Transformer-02 (715T) HT is restored.
| 17:06 | Maniknagar 230/132kV S/S Auto Transformer-02 (715T) LT is restored.
17:22 |  | Sirajgonj Gas 225MW Unit-2 ST was sync.
| 17:35 | Hasnabad-Keraniganj 230kV Ckt-2 is restored.
17:45 |  | Bhola Natun Biddut BD LTD (GAS) GT11 was sync.
19:59 |  | Bhola Natun Biddut BD LTD (GAS) GT12 was shutdown
22:26 | 23:19 | Siddhirganj-Ullon (T at Maniknagar) 132kV Ckt-1 Forced S/D from Siddhirganj 132/33kV end Due to Shutdown by NLDC
02:24 |  | Ashugonj north 360 MW ST was sync. at 02:24 hrs.
05:24 |  | Kulaura 132/33kV S/S TR-1 LT Scheduled S/D Due to For station auxiliary-1 maintenance.
06:01 |  | Kulaura 132/33kV S/S TR-1 HT Scheduled S/D Due to For station auxiliary-1 maintenance.
06:44 | 07:33 | Aminbazar-Kallyanpur 132kV Ckt-2 Tripped from Aminbazar 400/230/132kV end showing 1.general trip 2.distance trip
r,y & b phase relays Due to due to rain
06:44 | 07:36 | Kallyanpur-Lalbag 132kV Ckt-1 Tripped from Kallyanpur 132/33kV end showing - relays Due to Trip (At lalbag end)
07:00 |  | Minimum load during the shift : 5809 MW
07:04 |  | Gopalganj 132/33kV S/S T1 LT Scheduled S/D Due to 33kv incoming -01 D's R phase finger adjustment work |  |  |  |  | 10.0MW load interrup.
07:05 |  | Gopalganj 132/33kV S/S T1 HT Scheduled S/D |  |  |  |  | 10.0MW load interrup.
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2022-12-26 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Line O/L
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 200 | 4746700 | Machine problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 73 | 1515909 | Machine problem
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 402 | 9658370 | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 333 | 7906000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 5167300 | GT-2 S/D due to Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 17 | 126720 | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 34 | 522759 | Fuel shortage
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 20 | 130056 | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 512604
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 16 | 262080 | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 16 | 254304 | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 392760
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 32 | 529920 | Fuel shortage
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 662358
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 605984
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 52 | 1188060 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 30 | 702360
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 28 | 737200 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 48 | 666720 | Engine problem
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 95 | 948436 | Fuel shortage
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 44 | 1559079 | Low Demand
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 50 | 790547 | Low Demand
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 70 | 677050 | Low Demand
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 35 | 637200 | Fuel shortage
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 1699200
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 17 | 360960 | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 1101600
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 135965
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 320400 | Fuel shortage
| Dhaka area Total |  |  |  | 5847 | 2307 | 44518601
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Machine problem
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 17 | 237636 | Machine problem
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 119475
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | 33 kV line problem
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 30 | 720000 | Low water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 152 | 2514559 | Gas shortage
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 51 | 559527 | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 40 | 352368 | Fuel shortage
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 36 | 288718 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 10 | 264240 | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 12 | 299520 | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 0 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 14 | 430560
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 10 | 34560 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 21602
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 290 | 1972145 | Engine problem
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 17 | 452016 | Engine problem
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 72 | 1751338 | Engine problem
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 305280 | Engine problem
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 107 | 2564291 | Engine problem
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 10036 | On test.
| Chattogram area Total |  |  |  | 2382 | 870 | 12897871
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 131 | 4339000 | Gas shortage
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 10 | 204200 | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 270 | 7207000 | FGMO
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 258 | 7559900 | Gas shortage
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 0 | 96264 | Gas shortage
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 0 | 0 | Gas shortage
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 0 | 133818 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1074244
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 72 | 543636 | Fuel shortage
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 21 | 317264 | Machine problem
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Machine problem
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 51 | 399360 | Fuel shortage
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 475668
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 10 | 241200
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 112 | 2199360
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 757000
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 8 | 91594 | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 20 | 390780 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 10 | 609408 | Low Demand
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 100 | 653220 | Fuel shortage
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 9 | 176400 | Fuel shortage
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 444240 | Engine problem
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 54 | 772800 | Fuel shortage
| Cumilla Area Total |  |  |  | 3285 | 1258 | 28686356
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 53 | 1546560 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 476388 | Gas shortage
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 5400
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 48 | 912000 | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 47 | 630000 | Fuel shortage
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 161750
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 85200 | Engine problem
| Mymensingh Area Total |  |  |  | 614 | 174 | 3817298
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 30 | 716000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 31 | 538080 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Gas shortage
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 1026600
| Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 47 | 969048
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 8 | 192384 | Engine problem
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 63 | 1377408
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 86 | 1078080
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 130 | 3100560 | Machine problem
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 19 | 455000
| Sylhet 50MW PP (EPL) |  | NENP | 27*2 | 50 | 24 | 517300 | Gas shortage
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 323400
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 0 | 0 | Under maint.
104 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 396 | 9374000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 231840
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 400 | 9446400
| Sylhet Area Total |  |  |  | 2477 | 1313 | 29346100
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Fuel shortage
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 904 | 18379636
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 66 | 452160 | Fuel shortage
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 13 | 125280 | Line O/L
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 70 | 258432 | Line O/L
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Under maint.
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 32 | 191625 | Fuel shortage
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 10 | 57600 | Low Demand
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 12 | 107520 | Fuel shortage
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Fuel shortage
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 446400
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 0 | 0 | 509345 | On test.
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 0 | 0 | 522 | 10915650 | On test.
| Khulna Area Total |  |  |  | 2384 | 1629 | 31443648
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Line O/L
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 24 | 469000 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 180 | 4015320 | Gas shortage
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 380 | 8317000 | Line O/L & Unit-2 Under maint.
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 140 | 2653364 | Machine problem
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Line O/L
| Barisal 307 MW |  | BCPCL | 0 | 0 | 253 | 4967300 | On test.
| Barisal Area Total |  |  |  | 1958 | 977 | 20421984
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 32 | 114698 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 6 | 39705 | Fuel shortage
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contract Expired
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 50 | 715132 | Engine problem
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 40 | 166355 | Fuel shortage
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 136 | 4044364 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 43 | 221273
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 154 | 6005091 | Gas shortage
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 188973 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 18 | 354480
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 173574 | Engine problem
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 8 | 139805 | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 67 | 249000 | Fuel shortage
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 10 | 100907 | Low Demand
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 70 | 901440 | Engine problem
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 75 | 770976 | Engine problem
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 17340
| Adani Power Jharkhanda Ltd |  | Import | 0 | 0 | 0 | 0 | On test.
| Rajshahi Area Total |  |  |  | 2129 | 749 | 14203113
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 159 | 3903900 | Machine problem
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 1484985
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 23660
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 115 | 1911360
| Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 86572
| Teesta Solar Limited |  | BPCL | 16*12.5 | 0 | 0 | 334800
| Rangpur Area Total |  |  |  | 750 | 387 | 7745277
| Total |  |  |  | 21826 | 9664 | 193080248
| Eastern Grid Total |  |  |  | 14605 | 5922 | 119266226
| Western Grid Total |  |  |  | 7221 | 3742 | 73814022
| National Grid Total |  |  |  | 21826 | 9664 | 193080248
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2022-12-26
| (a) ENTIRE EASTERN GRID : |  | 6396.58 | MW | (b) ENTIRE WESTERN GRID : |  | 2933.38 | MW
| i) Dhaka area |  | 3469.88 | MW | i) Khulna area |  | 1118 | MW
| ii) Chittagong area |  | 1044.7 | MW | ii) Rajshahi area |  | 920.8 | MW
| iii) Comilla area |  | 810 | MW | iii) Barisal area |  | 251.58 | MW
| iv) Mymensingh area |  | 741 | MW | iv) Rangpur area |  | 643 | MW
| v) Sylhet area |  | 331 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 9329.96 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | Chhatak | 18 | 18:00 | Kamrangirchar | 62 | 12:00 | Natore | 91 | 19:30 | Shitalakhya | 94 | 15:00
2 | AKSML | 90 | 15:00 | Chowmuhani | 128 | 18:30 | Kaptai | 3.5 | 18:00 | Nawabganj | 26.7 | 21:00 | Sholosohor | 21 | 12:00
3 | Aftabnagar | 22 | 13:00 | Chuadanga | 68 | 18:00 | Kazla | 75 | 19:30 | Netrakona | 83 | 20:00 | Shyampur | 124 | 00:00
4 | Agargaon | 52 | 13:00 | Coxsbazar | 84 | 18:00 | Keranigonj | 32 | 13:00 | New | 60 | 12:00 | Siddhirganj | 88 | 12:00
5 | Agrabad | 48 | 18:00 | Cumilla(N) | 85 | 20:00 | Khagrachori | 22 | 18:00 | Niamatpur | 45 | 09:00 | Sirajganj | 61 | 19:00
6 | Amnura | 33 | 08:00 | Cumilla(S) | 114 | 18:00 | Khulna | 69 | 18:00 | Noapara | 35 | 18:30 | Sonargaon | 73 | 09:00
7 | Ashuganj | 42 | 18:00 | Daudkandi | 96 | 19:00 | Khulshi | 142 | 14:00 | PHP | 2 | 00:00 | Sreemongol | 40 | 19:00
8 | BIPTC | N/A | N/A | Dhaka | 26 | 13:00 | Kishoreganj | 94 | 18:30 | Pabna | 75 | 18:00 | Srinagar | 26.22 | 21:00
9 | BSRM | 153 | 07:00 | Dhamrai | 102 | 18:00 | Kodda | 265 | 10:00 | Palashbari | 87 | 18:00 | Sunamganj | 32 | 18:30
10 | Bagerhat | 80 | 18:00 | Dhanmondi | 90 | 13:00 | Kulaura | 26 | 18:00 | Panchagarh | 53 | 18:00 | Sylhet | 85 | 14:00
11 | Bakulia | 68 | 18:00 | Dohazari | 60 | 18:00 | Kurigram | 60 | 18:00 | Patuakhali | 81 | 21:00 | TK | 19 | 18:30
12 | Banani | 30 | 13:00 | Faridpur | 100 | 19:30 | Kushtia | 98 | 18:30 | Payra | 0.64 | 18:30 | Tangail | 142 | 18:00
13 | Bangabhaban | 9 | 10:00 | Fatullah | 50 | 12:00 | Lalbag | 66 | 18:00 | Postogola | 32 | 13:00 | Thakurgaon | 65 | 18:00
14 | Barapukuria | 41 | 18:30 | Fenchuganj | 31 | 18:00 | Lalmonirhat | 21 | 18:00 | Purbachal | 11 | 13:00 | Tongi | 99 | 11:00
15 | Barguna | 12 | 18:00 | Feni | 80 | 18:00 | Madanganj | 36 | 01:00 | Purbasadipur | 94 | 18:00 | Ullon | 30 | 13:00
16 | Barishal | 71 | 19:00 | GPH | 95 | 12:00 | Madaripur | 65 | 20:00 | Rahanpur_I | 4.6 | 18:30 | Uttara | 60 | 13:00
17 | Barishal-230 | 50 | 18:30 | Ghorashal | 51 | 21:00 | Madartek | 49 | 13:00 | Rahim | 23 | 07:00 | UttaraNew | 13 | 18:00
18 | Baroaulia | 53 | 11:00 | Goalpara | 20 | 12:00 | Madunaghat | 36 | 18:00 | Rajbari | 48 | 18:00 | Zigatola | 32 | 12:00
19 | Baroirhat | 28 | 18:00 | Gollamari | 32 | 08:00 | Magura | 42 | 18:00 | Rajendrapur | 88 | 18:30
20 | Bashundhara | 104 | 18:00 | Gopalganj | 73.2 | 18:30 | Mahasthangarh | 42 | 18:00 | Rajshahi | 96 | 19:30
21 | BashundharaCement | 1 | 11:00 | Gulshan | 72 | 13:00 | Manikganj | 65 | 19:30 | Rajshahi-230 | 22 | 12:00
22 | Beanibazar | 39 | 18:00 | Halishahar | 78 | 15:00 | Maniknagar | 45 | 13:00 | Ramganj | 70 | 20:00
23 | Benapole | 40 | 18:00 | HaripurSBU | 137 | 18:30 | Matarbari | 29 | 18:00 | Rampur | 17 | 18:00
24 | Bhaluka | 108 | 21:00 | Hasnabad | 74 | 19:30 | Matuail | 55 | 15:00 | Rangamati | 10 | 18:30
25 | Bhandaria | 32 | 20:00 | Hathazari | 46 | 18:00 | Millgate | 56 | 12:00 | Rangpur | 118 | 18:30
26 | Bhangura | 21 | 18:30 | Ishurdi | 50 | 18:30 | Mirpur | 87.5 | 18:00 | Ruppur | 3.8 | 15:00
27 | Bheramara(GK) | 38 | 18:00 | Jaldhaka | 46 | 18:00 | Mirsorai | 3 | 18:00 | SSM | 12 | 09:00
28 | Bhulta | 198 | 16:00 | Jamalpur | 96 | 18:30 | Mithapukur | 22 | 08:00 | Saidpur | 81 | 18:30
29 | Bog-Sherpur | 44 | 18:30 | Jashore | 98 | 18:30 | Modern | 0 | 00:00 | Satkhira | 82 | 18:00
30 | Bogura | 113 | 19:00 | Jhenaidah | 90 | 18:00 | Mogbazar | 86 | 15:00 | Satmasjid | 66 | 13:00
31 | Borhanuddin | 28 | 19:30 | Joydebpur | 124 | 12:00 | Mongla | 16 | 23:00 | Savar | 144 | 15:00
32 | Brahmanbaria | 100 | 19:30 | Joypurhat | 39 | 18:30 | Motijheel | 24 | 13:00 | Shahjadpur | 75 | 18:30
33 | Cantonment | 86 | 14:00 | Juldah | 24 | 10:00 | Munshiganj | 61 | 21:00 | Shahjibazar | 86 | 18:00
34 | Chandpur | 41 | 19:30 | KSRM | 49 | 16:00 | Mymensingh | 156 | 19:00 | Shahmirpur | 33 | 01:00
35 | Chandraghona | 24 | 18:00 | Kabirpur | 204 | 16:00 | Naogaon | 83 | 19:30 | Shariatpur | 48 | 21:00
36 | Chapai | 43 | 13:00 | Kachua | 44 | 18:00 | Narail | 35 | 20:00 | Sherpur | 98 | 18:00
37 | Charsaidpur | 24.5 | 17:00 | Kallyanpur | 60 | 13:00 | Narinda | 51 | 13:00 | Shikalbaha | 22 | 10:00
38 | Chauddagram | 27 | 18:00 | Kalurghat | 24 | 12:00 | Narshingdi | 129 | 19:00 | Shikalbaha-230 | N/A | N/A
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2022-12-26 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 410 | 00:00 | 402 | 11:00 | Gopalganj_I | N/A | N/A | N/A | N/A
| Bhulta | 390 | 21:00 | 380 | 10:00 | Kaliakoir | 398 | 04:00 | 388 | 12:00
| Bibiana | 400 | 05:00 | 392 | 16:00 | Payra | 421 | 04:00 | 417 | 14:00
| BIPTC | 407 | 01:00 | 391 | 18:30 | Rahanpur_I | 414 | 19:00 | 390 | 12:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 239 | 21:00 | 229 | 12:00 | Hasnabad | 237 | 18:00 | 229 | 10:00
| AKSML | 240 | 18:30 | 207 | 12:00 | Hathazari | 240 | 18:30 | 222 | 11:00
| Aminbazar | 239 | 17:00 | 232 | 10:00 | Ishurdi | 242 | 00:00 | 231 | 12:00
| Ashuganj | 243 | 17:00 | 233 | 12:00 | Jhenaidah | 240 | 00:00 | 228 | 12:00
| Baghabari | 239 | 17:00 | 232 | 08:00 | Kaliakoir | 237 | 21:00 | 229 | 12:00
| Barapukuria | 234 | 16:00 | 227 | 00:00 | Keranigonj | 237 | 21:00 | 228 | 12:00
| Barishal | 246 | 01:00 | 242 | 12:00 | Khulna(S) | 241 | 00:00 | 232 | 12:00
| Bheramara | 239 | 00:00 | 228 | 12:00 | Maniknagar | 235 | 04:00 | 226 | 12:00
| Bhulta | 237 | 04:00 | 229 | 12:00 | Meghnaghat | 242 | 21:00 | 233 | 12:00
| Bibiana | 238 | 17:00 | 232 | 12:00 | Mirsorai | 236 | 18:30 | 208 | 12:00
| BIPTC | 242 | 22:00 | 229 | 12:00 | Rajshahi | 244 | 17:00 | 234 | 12:00
| Bogura | 238 | 21:00 | 230 | 12:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 249 | 00:00 | 247 | 11:00 | Rampura | 234 | 07:00 | 227 | 12:00
| BSRM | 237 | 18:00 | 212 | 12:00 | Shikalbaha | 240 | 20:00 | 219 | 12:00
| Cumilla(N) | 237 | 18:00 | 224 | 12:00 | Shyampur | 237 | 21:00 | 227 | 12:00
| Fenchuganj | 241 | 00:00 | 235 | 11:00 | Siddhirganj | 237 | 21:00 | 230 | 10:00
| Ghorashal | N/A | N/A | N/A | N/A | Sirajgonj | 237 | 21:00 | 232 | 11:00
| GPH | 239 | 18:30 | 212 | 12:00 | Tongi | 236 | 21:00 | 227 | 11:00
| Haripur | 233 | 00:00 | 227 | 12:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 136 | 00:00 | 129 | 12:00 | Kushtia | 139 | 01:00 | 131 | 12:00
| Agargaon | 138 | 00:00 | 133 | 12:00 | Lalbag | 137 | 21:00 | 132 | 12:00
| Agrabad | 138 | 19:00 | 123 | 12:00 | Lalmonirhat | 136 | 17:00 | 131 | 00:00
| AKS | 138 | 18:30 | 123 | 12:00 | Madanganj | 139 | 18:00 | 133 | 10:00
| Aminbazar | 138 | 01:00 | 132 | 10:00 | Madaripur | 139 | 05:00 | 134 | 12:00
| Amnura | 137 | 19:00 | 126 | 12:00 | Madartek | 136 | 00:00 | 130 | 12:00
| Ashuganj | 139 | 00:00 | 135 | 11:00 | Madunaghat | 139 | 18:00 | 125 | 13:00
| Bagerhat | 138 | 21:00 | 130 | 08:00 | Magura | 138 | 00:00 | 132 | 12:00
| Bakulia | 139 | 19:00 | 123 | 13:00 | Mahasthangarh | 139 | 17:00 | 134 | 12:00
| Banani | 139 | 01:00 | 130 | 12:00 | Manikganj | 132 | 22:00 | 127 | 08:00
| Bangabhaban | 135 | 18:00 | 127 | 11:00 | Maniknagar | 136 | 22:00 | 126 | 12:00
| Barapukuria | 138 | 16:00 | 133 | 00:00 | Matarbari | 134 | 22:00 | 119 | 12:00
| Barguna | 139 | 04:00 | 137 | 10:00 | Matuail | 137.3 | 21:00 | 132 | 10:00
| Barishal | 138 | 00:00 | 136 | 05:00 | Millgate | 139 | 03:00 | 130 | 12:00
| Barishal-230 | 140 | 01:00 | 137 | 12:00 | Mirpur | 138 | 21:00 | 131 | 11:00
| Baroaulia | 141 | 19:00 | 125 | 13:00 | Mithapukur | 139 | 17:00 | 132 | 02:00
| Baroirhat | 140 | 19:00 | 127 | 12:00 | Modern | 138 | 18:30 | 124 | 13:00
| Bashundhara | 139 | 00:00 | 131 | 12:00 | Mogbazar | 140 | 03:00 | 130 | 12:00
| BashundharaCement | 139 | 18:00 | 133 | 10:00 | Mongla | 137 | 21:00 | 129 | 12:00
| Beanibazar | 137 | 00:00 | 133 | 12:00 | Motijheel | 135 | 18:00 | 127 | 11:00
| Benapole | 138 | 04:00 | 128 | 12:00 | Munshiganj | 139 | 18:00 | 133 | 12:00
| Bhaluka | 137 | 00:00 | 124 | 12:00 | Mymensingh | 137 | 00:00 | 118 | 17:00
| Bhandaria | 141 | 05:00 | 134 | 12:00 | Naogaon | 139 | 21:00 | 132 | 08:00
| Bhangura | 143 | 21:00 | 137 | 12:00 | Narail | 138 | 03:00 | 130 | 12:00
| Bheramara | 138 | 00:00 | 131 | 12:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bheramara(GK) | 139 | 03:00 | 134 | 08:00 | Narshingdi | 135 | 07:00 | 129 | 11:00
| Bhulta | 130 | 18:00 | 126 | 10:00 | Natore | 137 | 21:00 | 131 | 12:00
| Bog-Sherpur | 141 | 21:00 | 135 | 02:00 | Nawabganj | 136 | 00:00 | 131 | 10:00
| Bogura | 141 | 21:00 | 135 | 12:00 | Netrakona | 136 | 00:00 | 124 | 13:00
| Bogura-230 | 141 | 21:00 | 135 | 12:00 | New | 139 | 00:00 | 131 | 12:00
| Brahmanbaria | 134 | 00:00 | 131 | 12:00 | Niamatpur | 136 | 21:00 | 131 | 08:00
| Cantonment | 139 | 00:00 | 132 | 12:00 | Noapara | 139 | 21:00 | 130 | 14:00
| Chandpur | 140 | 18:00 | 128 | 13:00 | Pabna | 140 | 00:00 | 135 | 08:00
| Chandraghona | 140 | 19:00 | 126 | 12:00 | Palashbari | 137 | 16:00 | 131 | 12:00
| Chapai | 138 | 21:00 | 130 | 07:00 | Panchagarh | 138 | 15:00 | 126 | 00:00
| Charsaidpur | 140 | 18:30 | 133 | 12:00 | Patuakhali | 138 | 04:00 | 135 | 10:00
| Chauddagram | 139 | 18:00 | 126 | 12:00 | Payra | 138 | 00:00 | 137 | 06:00
| Chhatak | 137 | 00:00 | 133 | 12:00 | PHP | 138 | 18:00 | 125 | 12:00
| Chowmuhani | 138 | 18:30 | 124 | 12:00 | Postogola | 136 | 21:00 | 130 | 12:00
| Chuadanga | 137 | 00:00 | 128 | 12:00 | Purbachal | 140 | 22:00 | 131 | 12:00
| Coxsbazar | 129 | 05:00 | 114 | 13:00 | Purbasadipur | 136 | 16:00 | 127 | 00:00
| Cumilla(N) | 141 | 18:30 | 126 | 02:00 | Rahim | 138 | 18:00 | 134 | 12:00
| Cumilla(S) | 141 | 18:30 | 129 | 11:00 | Rajbari | 135 | 05:00 | 125 | 12:00
| Daudkandi | 138 | 18:00 | 132 | 10:00 | Rajendrapur | 131 | 22:00 | 127 | 11:00
| Dhaka | 136 | 00:00 | 131 | 11:00 | Rajshahi | 136 | 21:00 | 129 | 12:00
| Dhamrai | 137 | 00:00 | 131 | 12:00 | Rajshahi-230 | 135 | 19:00 | 128 | 12:00
| Dhanmondi | 138 | 18:00 | 133 | 12:00 | Ramganj | 138 | 19:00 | 131 | 15:00
| Dohazari | 137 | 18:30 | 123 | 12:00 | Rampur | 138 | 20:00 | 124 | 13:00
| Faridpur | 136 | 12:00 | 128 | 08:00 | Rampura | 135 | 00:00 | 130 | 12:00
| Fatullah | 138 | 18:00 | 134 | 09:00 | Rangamati | 139 | 19:00 | 126 | 12:00
| Fenchuganj | 139 | 00:00 | 135 | 12:00 | Rangpur | 139 | 21:00 | 132 | 01:00
| Feni | 140 | 18:30 | 127 | 12:00 | Ruppur | 140 | 23:00 | 134 | 07:00
| Ghorashal | 140 | 00:00 | 140 | 00:00 | Saidpur | 137 | 16:00 | 129 | 00:00
| Goalpara | 140 | 19:30 | 130 | 09:00 | Satkhira | 137 | 00:00 | 130 | 08:00
| Gollamari | 139 | 21:00 | 132 | 12:00 | Satmasjid | 138 | 00:00 | 133 | 11:00
| Gopalganj | 140 | 21:00 | 130 | 08:00 | Savar | 140 | 21:00 | 131 | 10:00
| Gopalganj-400 | N/A | N/A | N/A | N/A | Shahjadpur | 146 | 21:00 | 140 | 12:00
| Gopalganj_I | N/A | N/A | N/A | N/A | Shahjibazar | 137 | 00:00 | 133 | 15:00
| Gulshan | 135 | 00:00 | 129 | 12:00 | Shahmirpur | 138 | 19:00 | 122 | 12:00
| Halishahar | 138 | 18:30 | 123 | 13:00 | Shariatpur | 137 | 00:00 | 134 | 10:00
| Haripur | 138 | 18:00 | 134 | 12:00 | Sherpur | 135 | 00:00 | 124 | 14:00
| HaripurSBU | 138 | 18:00 | 133 | 12:00 | Shikalbaha | 139 | 19:30 | 122 | 12:00
| Hasnabad | 135 | 00:00 | 131 | 10:00 | Shikalbaha-230 | 139 | 20:00 | 125 | 12:00
| Hathazari | 142 | 18:30 | 130 | 11:00 | Shitalakhya | 135 | 21:00 | 128 | 12:00
| Ishurdi | 140 | 00:00 | 133 | 12:00 | Sholosohor | 138 | 18:00 | 123 | 12:00
| Jaldhaka | 135 | 16:00 | 127 | 01:00 | Shyampur | 137 | 21:00 | 133 | 11:00
| Jamalpur | 136 | 00:00 | 126 | 12:00 | Shyampur-230 | 138 | 21:00 | 133 | 10:00
| Jashore | 136 | 05:00 | 128 | 00:00 | Siddhirganj | 137 | 03:00 | 132 | 02:00
| Jhenaidah | 140 | 00:00 | 131 | 12:00 | Sirajganj | 141 | 23:00 | 136 | 08:00
| Jhenaidah-230 | 139 | 00:00 | 131 | 12:00 | Sonargaon | 136 | 00:00 | 124 | 15:00
| Joydebpur | 143 | 21:00 | 139 | 04:00 | Sreemongol | 140 | 01:00 | 136 | 12:00
| Joypurhat | 138 | 21:00 | 132 | 08:00 | Srinagar | 137 | 21:00 | 131 | 10:00
| Juldah | 139 | 19:30 | 125 | 12:00 | SSM | 142 | 18:00 | 129 | 12:00
| Kabirpur | 137 | 00:00 | 129 | 08:00 | Sunamganj | 136 | 01:00 | 132 | 13:00
| Kachua | 140 | 18:30 | 128 | 12:00 | Sylhet | 137 | 00:00 | 134 | 12:00
| Kaliakoir | 133 | 03:00 | 130 | 10:00 | Tangail | 135 | 00:00 | 127 | 12:00
| Kallyanpur | 138 | 17:00 | 131 | 12:00 | Thakurgaon | 140 | 16:00 | 124 | 00:00
| Kalurghat | 138 | 18:00 | 125 | 13:00 | TK | 139 | 19:00 | 125 | 12:00
| Kamrangirchar | 136 | 18:30 | 132 | 10:00 | Tongi | 139 | 00:00 | 132 | 11:00
| Kaptai | 138 | 18:00 | 132 | 07:00 | Ullon | 136 | 06:00 | 129 | 12:00
| Kazla | 135 | 18:30 | 127 | 12:00 | Uttara | 138 | 02:00 | 129 | 12:00
| Keranigonj | 136 | 18:00 | 131 | 10:00 | UttaraNew | 137 | 04:00 | 131 | 10:00
| Khagrachori | 139 | 19:00 | 125 | 13:00 | Zigatola | 137 | 19:00 | 131 | 12:00
| Khulna | 139 | 21:00 | 131 | 12:00
| Khulna(S) | 140 | 21:00 | 131 | 14:00
| Khulshi | 137 | 18:30 | 124 | 12:00
| Kishoreganj | 132 | 00:00 | 127 | 09:00
| Kodda | 141 | 13:00 | 127 | 11:00
| KSRM | 139 | 18:30 | 123 | 12:00
| Kulaura | 139 | 00:00 | 134 | 12:00
| Kurigram | 135 | 21:00 | 128 | 07:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2022-12-26
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 150 | 4640 | 3040 | 7680 |  |  |  | QF-LDC-11
0:30 | 132 | 4555.5 | 2794 | 7349.5 | Date: | 2022-12-26
1:00 | 114 | 4471 | 2548 | 7019
1:30 | 119 | 4410.5 | 2431 | 6841.5
2:00 | 124 | 4350 | 2314 | 6664
2:30 | 132 | 4205 | 2303 | 6508 | [5 empty] | Gen. at Eve. Peak | 9664 | 9664 MW (19:00 )
3:00 | 140 | 4060 | 2292 | 6352 | [6 empty] | 19:00
3:30 | 158 | 4026.5 | 2289.5 | 6316 | [5 empty] | Gen. at Day Peak | 8717 | 8717 MW (12:00 )
4:00 | 176 | 3993 | 2287 | 6280 | [6 empty] | 12:00
4:30 | 188 | 3976.5 | 2285 | 6261.5 | [5 empty] | Highest Generation | 9664
5:00 | 200 | 3960 | 2283 | 6243 | [6 empty] | 19:00
5:30 | 206 | 4010.5 | 2329 | 6339.5
6:00 | 212 | 4061 | 2375 | 6436
6:30 | 152 | 4185.5 | 2443.5 | 6629
7:00 | 92 | 4310 | 2512 | 6822
7:30 | 112 | 4471.5 | 2686 | 7157.5
8:00 | 132 | 4633 | 2860 | 7493
8:30 | 147 | 4699 | 2978 | 7677
9:00 | 162 | 4765 | 3096 | 7861
9:30 | 165 | 4743.5 | 3120 | 7863.5
10:00 | 168 | 4722 | 3144 | 7866
10:30 | 199 | 4909 | 3167 | 8076
11:00 | 230 | 5096 | 3190 | 8286
11:30 | 275 | 5186.5 | 3315 | 8501.5
12:00 | 320 | 5277 | 3440 | 8717
12:30 | 305 | 5361.5 | 3319 | 8680.5
13:00 | 290 | 5446 | 3198 | 8644
13:30 | 325 | 5374 | 3141.5 | 8515.5
14:00 | 360 | 5302 | 3085 | 8387
14:30 | 380 | 5224.5 | 3063.5 | 8288
15:00 | 400 | 5147 | 3042 | 8189
15:30 | 350 | 5144 | 2978.5 | 8122.5
16:00 | 300 | 5141 | 2915 | 8056
16:30 | 245 | 5290.5 | 2961.5 | 8252
17:00 | 190 | 5440 | 3008 | 8448
17:30 | 126 | 5727.5 | 3317 | 9044.5
18:00 | 62 | 6015 | 3626 | 9641
18:30 | 84 | 5968.5 | 3684 | 9652.5
19:00 | 106 | 5922 | 3742 | 9664
19:30 | 120 | 5819 | 3757 | 9576
20:00 | 140 | 5753 | 3673 | 9426 |  |  |  | Executive Engineer
20:30 | 166 | 5721.5 | 3659 | 9380.5 |  |  |  | Network Operation Division
21:00 | 192 | 5690 | 3645 | 9335
21:30 | 176 | 5479.5 | 3552 | 9031.5
22:00 | 160 | 5269 | 3459 | 8728 |  |  |  |  | Page 6 of 7
22:30 | 180 | 5106.5 | 3404 | 8510.5
23:00 | 200 | 4944 | 3349 | 8293
23:30 | 175 | 4792 | 3194.5 | 7986.5
24:00 | 150 | 4640 | 3040 | 7680
9664 MW (19:00 )
8717 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2022-12-26 |  | Energy |  | 193080248
[13 empty] | 2022-12-26 |  |  |  |  | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 3215 | 722 | 1318 | 0 | 1051 | 1252 | 30 | 0 | 0 | 92 | 0 | 0
0:30 | 3293.5 | 722.5 | 1307 | 0 | 777.5 | 1133 | 30 | 0 | 0 | 86 | 0 | 0 | Date: | 2022-12-26
1:00 | 3372 | 723 | 1296 | 0 | 504 | 1014 | 30 | 0 | 0 | 80 | 0 | 0
1:30 | 3349 | 667 | 1259 | 0 | 439 | 1020.5 | 30 | 0 | 0 | 77 | 0 | 0 | [7 empty] | Total Energy | 193.0802 | Total Energy Gen 193.080 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 193.080 MKWHr
2:00 | 3326 | 611 | 1222 | 0 | 374 | 1027 | 30 | 0 | 0 | 74 | 0 | 0 | [7 empty] | Energy not Served | 0
2:30 | 3304 | 611 | 1126.5 | 0 | 344.5 | 1019 | 30 | 0 | 0 | 73 | 0 | 0 | [7 empty] | Energy Requirement | 193.0802
3:00 | 3282 | 611 | 1031 | 0 | 315 | 1011 | 30 | 0 | 0 | 72 | 0 | 0
3:30 | 3263.5 | 617.5 | 1024.5 | 0 | 306.5 | 1003 | 30 | 0 | 0 | 71 | 0 | 0 | [5 empty] | Shortage
4:00 | 3245 | 624 | 1018 | 0 | 298 | 995 | 30 | 0 | 0 | 70 | 0 | 0
4:30 | 3228 | 617.5 | 1022.5 | 0 | 298 | 995.5 | 30 | 0 | 0 | 70 | 0 | 0
5:00 | 3211 | 611 | 1027 | 0 | 298 | 996 | 30 | 0 | 0 | 70 | 0 | 0
5:30 | 3219.5 | 611 | 1106.5 | 0 | 307 | 993.5 | 30 | 0 | 0 | 72 | 0 | 0
6:00 | 3228 | 611 | 1186 | 0 | 316 | 991 | 30 | 0 | 0 | 74 | 0 | 0
6:30 | 3207 | 611 | 1248.5 | 0 | 461.5 | 994 | 30 | 0 | 0 | 75 | 2 | 0 |  |  |  | Coal
7:00 | 3186 | 611 | 1311 | 0 | 607 | 997 | 30 | 0 | 0 | 76 | 4 | 0
7:30 | 3251.5 | 610.5 | 1336.5 | 0 | 802 | 1007 | 30 | 0 | 18 | 80 | 22 | 0 |  |  | Oil |  |  |  | ,
8:00 | 3317 | 610 | 1362 | 0 | 997 | 1017 | 30 | 0 | 36 | 84 | 40 | 0
8:30 | 3256 | 706.5 | 1378 | 0 | 1077 | 1046 | 30 | 0 | 35 | 84 | 64.5 | 0
9:00 | 3195 | 803 | 1394 | 0 | 1157 | 1075 | 30 | 0 | 34 | 84 | 89 | 0
9:30 | 3155 | 803.5 | 1376.5 | 0 | 1168 | 1054.5 | 30 | 12.5 | 33 | 84 | 146.5 | 0
10:00 | 3115 | 804 | 1359 | 0 | 1179 | 1034 | 30 | 25 | 32 | 84 | 204 | 0
10:30 | 3124 | 803.5 | 1343 | 153 | 1206.5 | 1035.5 | 30 | 63 | 43.5 | 89 | 185 | 0
11:00 | 3133 | 803 | 1327 | 306 | 1234 | 1037 | 30 | 101 | 55 | 94 | 166 | 0
11:30 | 3126.5 | 794 | 1310 | 387 | 1227 | 1082 | 30 | 172 | 66.5 | 101 | 205.5 | 0
12:00 | 3120 | 785 | 1293 | 468 | 1220 | 1127 | 30 | 243 | 78 | 108 | 245 | 0
12:30 | 3101 | 749.5 | 1277 | 563.5 | 1194.5 | 1174 | 30 | 181.5 | 77 | 108 | 224.5 | 0
13:00 | 3082 | 714 | 1261 | 659 | 1169 | 1221 | 30 | 120 | 76 | 108 | 204 | 0
13:30 | 3082 | 714 | 1261 | 659 | 1169 | 1221 | 30 | 120 | 76 | 108 | 204 | 0
14:00 | 3082 | 714 | 1261 | 659 | 1169 | 1221 | 30 | 120 | 76 | 108 | 204 | 0
14:30 | 3114.5 | 760 | 1223 | 478.5 | 1175.5 | 1208 | 30 | 60 | 92 | 106 | 169 | 0
15:00 | 3147 | 806 | 1185 | 298 | 1182 | 1195 | 30 | 0 | 108 | 104 | 134 | 0
15:30 | 3147 | 806 | 1168.5 | 276 | 1247 | 1135.5 | 30 | 1.5 | 112 | 101 | 98 | 0
16:00 | 3147 | 806 | 1152 | 254 | 1312 | 1076 | 30 | 3 | 116 | 98 | 62 | 0
16:30 | 3157.5 | 805.5 | 1148 | 294 | 1439.5 | 1113 | 30 | 4.5 | 127 | 99 | 34 | 0
17:00 | 3168 | 805 | 1144 | 334 | 1567 | 1150 | 30 | 6 | 138 | 100 | 6 | 0
17:30 | 3108 | 854 | 1184.5 | 398 | 1887 | 1222.5 | 30 | 3 | 247.5 | 107 | 3 | 0
18:00 | 3048 | 903 | 1225 | 462 | 2207 | 1295 | 30 | 0 | 357 | 114 | 0 | 0
18:30 | 3110 | 903.5 | 1238.5 | 328 | 2252 | 1304.5 | 30 | 0 | 373 | 113 | 0 | 0
19:00 | 3172 | 904 | 1252 | 194 | 2297 | 1314 | 30 | 0 | 389 | 112 | 0 | 0
19:30 | 3180 | 903 | 1236 | 116 | 2284 | 1321 | 30 | 0 | 396 | 110 | 0 | 0
20:00 | 3221 | 903 | 1203 | 95 | 2184 | 1291 | 30 | 0 | 389 | 110 | 0 | 0
20:30 | 3200 | 906 | 1212.5 | 178 | 2060 | 1288 | 30 | 0 | 397 | 109 | 0 | 0
21:00 | 3179 | 909 | 1222 | 261 | 1936 | 1285 | 30 | 0 | 405 | 108 | 0 | 0
21:30 | 3159 | 908.5 | 1228 | 130.5 | 1870.5 | 1265.5 | 30 | 0 | 336.5 | 103 | 0 | 0
22:00 | 3139 | 908 | 1234 | 0 | 1805 | 1246 | 30 | 0 | 268 | 98 | 0 | 0
22:30 | 3181 | 907.5 | 1254.5 | 0 | 1577.5 | 1248.5 | 30 | 0 | 202.5 | 109 | 0 | 0
23:00 | 3223 | 907 | 1275 | 0 | 1350 | 1251 | 30 | 0 | 137 | 120 | 0 | 0
23:30 | 3219 | 814.5 | 1296.5 | 0 | 1200.5 | 1251.5 | 30 | 0 | 68.5 | 106 | 0 | 0 | Max Temp. in Dhaka |  | 28.9° C
24:00 | 3215 | 722 | 1318 | 0 | 1051 | 1252 | 30 | 0 | 0 | 92 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 193.080 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 193.080 MKWHr
Note on W13: Author:

## Generation
g | 2022-12-26
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3
2 | Karnaphuli Hydro PP Unit-4 & 5 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [7 empty] | 8 | 8 | 8 | 8 | 10 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 0 | 237636
| Teknaf 20MW PP (Solartech) | [6 empty] | 1 | 6 | 12 | 16 | 18 | 18 | 17 | 15 | 11 | 5 | 0 | [9 empty] | 119475
6 | Sikalbaha 225MW CCPP (Gas) | 151 | 151 | 151 | 151 | 151 | 125 | 30 | 30 | 31 | 31 | 31 | 40 | 42 | 67 | 58 | 130 | 152 | 151 |  | 152 | 151 | 151 | 151 | 151 | 151 | 151 | 2514559
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [16 empty] | 11 | 51 |  | 36 | 51 | 51 | 51 | 51 | 17 | 0 | 288718
12 | Hathazari 100 MW peaking PP | [7 empty] | 4 | 2 |  |  |  |  | 16 | 32 | 40 | 40 | 40 |  | 40 | 40 | 40 | 38 | 32 | 32 | 0 | 352368
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [6 empty] | 11 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 38 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 30 | 17 | 559527
| Daudkandi 200 MW PP (B.Trac) | [10 empty] | 50 | 85 | 190 | 100 | 50 | 10 | 50 | 67 |  | 10 | 10 | 0 |  |  |  |  | 609408
14 | Titas 50 MW Peaking PP | [10 empty] | 23 | 30 | 28 | 28 | 28 | 28 | 28 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 0 | 317264
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | [6 empty] | 12 | 15 | 32 | 32 | 30 | 32 | 32 | 32 | 32 | 30 | 77 | 97 |  | 95 | 95 | 97 | 97 | 97 | 30 | 30 | 948436
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 0 | [9 empty] | 0 | 133818
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4746700
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 0 | [10 empty] | 96264
33 | Ashuganj 225 MW CCPP | 182 | 183 | 187 | 185 | 182 | 202 | 218 | 224 | 192 | 187 | 207 | 218 | 189 | 185 | 183 | 194 | 171 | 131 |  | 131 | 131 | 131 | 153 | 153 | 153 | 153 | 4339000
34 | Ashuganj 450 MW CCPP(South) | 280 | 290 | 295 | 280 | 280 | 315 | 325 | 345 | 325 | 295 | 345 | 345 | 320 | 295 | 300 | 270 | 270 | 270 |  | 270 | 270 | 300 | 270 | 270 | 270 | 270 | 7207000
| Ashuganj 450 MW CCPP(North) | [14 empty] | 0 | 10 | 20 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 5 | 204200
| Ashuganj 420 MW CCPP(East) | 350 | 350 | 350 | 350 | 350 | 382 | 408 | 406 | 377 | 348 | 297 | 297 | 287 | 328 | 328 | 268 | 258 | 228 |  | 258 | 258 | 258 | 258 | 258 | 259 | 258 | 7559900
35 | Ashuganj 55 MW PP (Precision) | [25 empty] | 0 | 0
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 405 | 405 | 404 | 391 | 372 | 372 | 376 | 399 | 399 | 401 | 403 | 403 | 405 | 405 | 405 | 405 | 404 | 385 |  | 402 | 408 | 407 | 409 | 387 | 392 | 399 | 9658370
40 | Meghnaghat 450 MW CCPP(MPL) | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 |  | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 5167300
41 | Haripur 360MW CCPP(HPL) | 356 | 356 | 307 | 306 | 307 | 310 | 311 | 356 | 364 | 351 | 351 | 346 | 348 | 333 | 334 | 333 | 328 | 331 |  | 333 | 324 | 316 | 319 | 294 | 293 | 326 | 7906000
42 | RPCL 210MW CCPP | 103 | 101 | 113 | 113 | 113 | 112 | 71 | 97 | 62 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 53 | 53 | 62 | 76 | 94 | 100 | 93 | 1546560
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 0 | 3 | 10 | 28 | 24 | 35 | 29 | 25 | 9 | 7 | 1 | 0 | [8 empty] | 161750
44 | Fenchugonj CCPP Phase-1 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 716000
45 | Fenchugonj CCPP Phase-2 | 43 | 43 | 43 | 43 | 43 | 0 | [6 empty] | 20 | 20 | 20 | 20 | 31 | 31 |  | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 538080
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 40 | 40 | 40 | 40 | 40 | 40 | 64 | 64 | 62 | 62 | 61 | 60 | 61 | 61 | 62 | 62 | 63 | 63 |  | 63 | 63 | 62 | 63 | 63 | 63 | 62 | 1377408
48 | Shahjibazar 86MW PP (Shahjibazar) | 40 | 10 | 10 | 10 | 10 | 10 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 86 |  | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 1078080
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 |  | 130 | 130 | 130 | 131 | 131 | 130 | 130 | 3100560
51 | Sylhet 20 MW GTPP | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 18 | 18 | 20 | 19 | 19 | 19 | 19 | 18 | 18 | 18 |  | 19 | 20 | 19 | 19 | 19 | 19 | 20 | 455000
52 | Sylhet 50MW PP (EPL) | 26 | 26 | 11 | 11 | 11 | 11 | 20 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 517300
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 231840
54 | Hobiganj 11MW PP Cofidence-E | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 192384
55 | Fenchugonj 51 MW PP (Barakatullah) | 31 | 31 | 11 | 11 | 11 | 11 | 51 | 53 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 53 | 53 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 1026600
56 | Shahjahanulla 25 MW PP | 21 | 21 | 21 | 21 | 21 | 21 | 21 | [6 empty] | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 323400
57 | Bibiana-II 341 MW CCPP (Summit)
| Bibiyana South 400 MW | 400 | 400 | 385 | 370 | 370 | 370 | 370 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 |  | 400 | 400 | 400 | 400 | 370 | 400 | 400 | 9446400
58 | Nababganj 55 MW PP (Southern power ) | 17 |  |  |  |  | 5 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 35 | 35 | 35 | 35 | 55 |  | 55 | 55 | 55 | 35 | 35 | 35 | 35 | 605984
59 | Tangail Palli Power Gen 22 MW | 9 | [18 empty] | 6 | 12 | 12 | 12 | 12 | 12 | 12 | 85200
60 | Barabkunda 22 MW PP (Regent)
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 512604
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 |  | 19 | 19 | 19 | 19 | 19 | 21 | 21 | 21 | 21 | 21 | 20 |  | 20 | 20 | 21 | 21 | 21 | 21 | 21 | 476388
63 | Impoprt (Tripura) | 80 | 74 | 72 | 70 | 70 | 74 | 76 | 84 | 84 | 84 | 94 | 108 | 108 | 104 | 104 | 98 | 100 | 114 |  | 112 | 110 | 110 | 108 | 98 | 120 | 92 | 2199360
64 | Malancha, Ctg. EPZ (United) | 22 | 33 | 40 | 42 | 42 | 42 | 42 | 7 | 16 | 11 | 4 | 2 | 2 | 2 | 2 | 2 | 2 | 8 |  | 14 | 5 | 10 | 12 | 17 | 25 | 26 | 430560
65 | Feni 22MW PP (Doreen) | 21 | 18 | 18 | 18 | 18 | 18 | 18 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 20 | 20 | 20 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 475668
66 | Feni 11 MW PP (Doreen) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 241200
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 17 | 25 | 29 | 28 | 28 | 28 | 30 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 757000
68 | Cumilla 25 MW PP (Summit) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 9 | 18 | 15 | 18 | 15 | 15 | 20 |  | 20 | 20 | 21 | 21 | 21 | 21 | 21 | 390780
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 22 | 600000
70 | Summit Madhabdi | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 27 | 27 | 27 | 9 | 27 | 27 | 27 | 27 | 10 |  | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 588060
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 25 | 25 | 702360
72 | Rupganj 33 MW PP(Summit) | 30 | 30 | 32 | 32 | 33 | 33 | 33 | 32 | 32 | 32 | 30 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 28 | 28 | 28 | 28 | 29 | 29 | 30 | 737200
73 | Ghorashal 108MW PP (Regent) | 72 | 69 | 24 | 12 | 12 | 57 | 65 | 68 | 70 | 70 | 70 | 70 | 68 | 68 | 68 | 70 | 73 | 73 |  | 73 | 73 | 73 | 73 | 73 | 71 | 71 | 1515909
| Feni Lanka Power | [7 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 99 |  | 100 | 100 | 100 | 100 | 81 | 17 | 0 | 653220
| Chowmuhani 113 MW | [7 empty] | 8 | 9 | 9 | 9 | 9 | 9 | 9 | 13 | 12 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 176400
| Manikgonj 162MW PP(MPGL) | 17 |  |  |  |  | 2 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 28 | 40 | 131 |  | 162 | 162 | 162 | 162 | 144 | 17 | 17 | 1101600
77 | Siddhirganj 100 PP(Dutch Bangla) | [7 empty] | 15 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 262080
78 | Gazipur 52 MW PP | [6 empty] | 8 | 16 | 36 | 42 | 49 | 49 | 49 | 49 | 40 | 41 | 48 | 48 |  | 48 | 48 | 48 | 48 | 16 | 16 | 0 | 666720
79 | Kodda 150MW PP | [7 empty] | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 |  | 32 | 32 | 32 | 32 | 32 | 32 | 0 | 529920
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | [15 empty] | 1 | 8 | 25 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 91594
| Gazipur 100 MW PP | [6 empty] | 17 | 40 | 95 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 88 | 88 | 50 | 1699200
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 1 | 2 | 3 | 3 | 4 | 3 | 3 | 2 | 1 | 0 | [9 empty] | 21602
| Jodiac Power | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 452016
| Karnaphuli Power Ltd. | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 60 | 53 | 72 | 72 | 72 | 72 | 72 |  | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 1751338
82 | Madanganj 102 PP(Summit) | 17 | 17 | 17 |  |  |  |  | 6 | 27 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 |  | 34 | 34 | 34 | 34 | 34 | 34 | 0 | 522759
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL) | [7 empty] | 9 | [8 empty] | 1 | 16 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 126720
| Meghnaghat 104 MW PP (OPCL) | 17 | 17 |  |  |  | 5 | 17 | 17 | 17 | 17 | 17 | 18 | 18 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 360960
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 264240
92 | Fenchuganj 44MW (Energyprima) | 43 | 46 | 10 | 10 | 10 | 25 | 40 | 40 | 46 | 46 | 48 | 44 | 44 | 47 | 47 | 44 | 47 | 47 |  | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 969048
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 10 | 10 | 10 | 10 | 10 | 18 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1074244
94 | Gagnagar 102 MW PP (Digital Power) | 8 | [5 empty] | 8 | 8 | 8 | 8 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 8 | 254304
95 | Patenga 50MW PP (Baraka)
96 | Chattogram 108 MW PP (ECPV) | [16 empty] | 11 | 12 |  | 10 | 0 | [5 empty] | 34560
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [16 empty] | 12 | 15 |  | 20 | 25 | 25 | 15 | 15 | 8 | 0 | 130056
100 | Manikganj 55 MW PP (Northern) | 17 | [5 empty] | 17 | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 55 |  | 55 | 55 | 55 | 35 | 35 | 35 | 35 | 662358
101 | Kushiara 163 MW CCPP (KP)
102 | Sarishabari 3 MW Solar Plant | [7 empty] | 0 | 0 | 1 | 2 | 1 | 1 | 1 | 0 | 0 | [10 empty] | 5400
103 | Kamalaghat 54 MW PP(Banco Energy) | [8 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 54 |  | 54 | 54 | 54 | 17 | 17 | 17 | 17 | 392760
104 | Keranigonj 300 MW PP (APR) | [10 empty] | 108 | 204 | 298 | 158 | 70 | 104 | 143 | 205 |  | 44 | 11 | 70 | 146 |  |  | 0 | 1559079
105 | Bramhangoan 100 MW PP (Aggreko) | [10 empty] | 74 | 92 | 88 | 92 | 90 | 70 | 90 | 50 |  | 50 | 50 | 25 | 90 |  |  | 0 | 790547
106 | Mymensingh 200 MW PP (United) | 8 | 8 |  |  |  | 5 | 19 | 46 | 46 | 46 | 51 | 48 | 48 | 48 | 48 | 53 | 48 | 50 |  | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 912000
112 | Aurahati 100MW PP (Aggreko) | [10 empty] | 74 | 87 | 83 | 88 | 88 | 70 | 40 | 70 |  | 70 | 25 | 0 | 25 |  |  | 0 | 677050
114 | Kodda 149 MW PP Unit-1 (Summit) | [6 empty] | 7 | 32 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 637200
115 | Juldah 100 MW PP Unit-3 (Acorn) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 299520
116 | Chandpur 200MW (Desh energy) | 17 |  |  |  |  | 2 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 22 |  | 51 | 17 | 17 | 17 | 17 | 17 | 17 | 399360
117 | Ashuganj 150MW PP (Midland) | [7 empty] | 3 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 34 | 65 | 75 |  | 72 | 74 | 75 | 73 | 75 | 15 | 6 | 543636
118 | Bibiyana-III 400 MW CCPP | 412 | 405 | 368 | 376 | 363 | 363 | 387 | 385 | 384 | 388 | 385 | 384 | 396 | 396 | 396 | 396 | 396 | 396 |  | 396 | 396 | 396 | 396 | 387 | 403 | 404 | 9374000
| Jamalpur 115 MW PP (United) | 8 |  |  |  |  | 2 | 17 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 37 | 47 |  | 47 | 47 | 47 | 47 | 47 | 47 | 28 | 630000
| Anwara 300 MW PP (United) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 118 | 290 |  | 290 | 295 | 200 | 51 | 51 | 51 | 51 | 1972145
| Juldah unit-2 (Acorn) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 305280
| Anlima Energy Ltd. | 107 | 107 | 107 | 107 | 107 | 95 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 |  | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 2564291
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 444240
| Spectra Solar Plant Ltd. | [6 empty] | 0 | 2 | 12 | 20 | 22 | 22 | 21 | 18 | 13 | 5 | 1 | 0 | [8 empty] | 135965
| Chandpur 115(Doreen) | 36 | 34 |  |  |  | 8 | 31 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 44 | 54 |  | 54 | 54 | 46 | 44 | 46 | 22 | 0 | 772800
| Kanchan Purbachal Power Generation Ltd. | [6 empty] | 9 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 320400
| Mirsharai 150 MW (Oil) | [15 empty] | 3 | 6 | 0 | [8 empty] | 10036
Mirsharai 150 MW (Gas)
120 | Eastern Zone Total | 4471 | 4350 | 4060 | 3993 | 3960 | 4061 | 4310 | 4633 | 4765 | 4722 | 5096 | 5277 | 5446 | 5302 | 5147 | 5141 | 5440 | 6015 |  | 5922 | 5819 | 5753 | 5690 | 5269 | 4944 | 4640 | 119266226
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | [16 empty] | 16 | 59 |  | 66 | 65 | 65 | 65 | 75 | 85 | 32 | 452160
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL) | [9 empty] | 25 | 101 | 243 | 120 | 0 | [12 empty] | 509345
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [16 empty] | 7 | 10 |  | 13 | 37 | 31 | 45 | 40 |  |  | 125280
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | [16 empty] | 1 | 3 |  | 12 | 18 | 18 | 18 | 18 | 18 | 18 | 107520
130 | Mongla Orion 100 MW Solar PP | [6 empty] | 2 | 18 | 38 | 55 | 68 | 73 | 68 | 58 | 39 | 19 | 2 | 0 | [8 empty] | 446400
131 | Rampal 1320 MW (BIFPCL) | 392 | 405 | 405 | 405 | 405 | 400 | 406 | 395 | 402 | 402 | 377 | 468 | 522 | 546 | 515 | 426 | 491 | 537 |  | 522 | 522 | 523 | 536 | 517 | 511 | 512 | 10915650
132 | United Payra Power Ltd. | [25 empty] | 0 | 0
133 | Bhola Nutan Biddut BD LTD (GAS) | 102 | 101 | 104 | 104 | 108 | 107 | 102 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 105 | 107 | 107 | 120 |  | 140 | 140 | 108 | 109 | 109 | 105 | 109 | 2653364
Bhola Nutan Biddut BD LTD (OIL)
Barisal 110 MW PP (Summit )
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW | 202 | 202 | 186 | 170 | 171 | 171 | 171 | 172 | 173 | 173 | 201 | 200 | 200 | 200 | 200 | 200 | 200 | 249 |  | 253 | 250 | 249 | 250 | 249 | 250 | 250 | 4967300
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 184 | 156 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 151 | 156 |  | 180 | 181 | 181 | 176 | 174 | 183 | 175 | 4015320
140 | Bhola 33 MW PP (Venture) | 21 | 20 | 19 | 18 | 18 | 19 | 17 | 18 | 17 | 17 | 17 | 18 | 19 | 19 | 17 | 15 | 17 | 24 |  | 24 | 23 | 24 | 25 | 25 | 23 | 22 | 469000
141 | Noapara 100 MW PP (Bangla Trac) | [16 empty] | 10 | 30 |  | 10 | 10 | 0 |  |  |  | 0 | 57600
142 | Noapara 40 MW PP (Khanjahan Ali) | [16 empty] | 8 | 40 |  | 32 | 40 | 40 | 40 | 24 |  | 0 | 191625
143 | Gopalganj 100 MW Peaking PP | [17 empty] | 70 |  | 70 | 65 | 60 | 60 | 7 |  |  | 258432
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 723 | 611 | 611 | 624 | 611 | 611 | 611 | 610 | 803 | 804 | 803 | 785 | 714 | 713 | 806 | 806 | 805 | 903 |  | 904 | 903 | 903 | 909 | 908 | 907 | 722 | 18379636
147 | Bheramara 410 MW CCPP
148 | Payra 1320 MW | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 290 | 340 | 300 | 300 | 300 | 340 | 350 | 320 | 290 | 300 | 350 |  | 380 | 390 | 360 | 340 | 320 | 330 | 330 | 8317000
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 159 | 159 | 159 | 159 | 159 | 160 | 160 | 159 | 159 |  | 159 | 159 | 159 | 159 | 160 | 160 | 160 | 3903900
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [17 empty] | 16 |  | 32 | 32 | 32 | 32 |  |  |  | 114698
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 0 | 2 | 2 | 3 | 4 | 3 | 1 | 1 | 0 | 0 | [9 empty] | 17340
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 172 | 155 | 140 | 140 | 140 | 140 | 152 | 190 | 195 | 194 | 191 | 170 | 160 | 160 | 157 | 160 | 160 | 139 |  | 136 | 136 | 136 | 136 | 140 | 163 | 170 | 4044364
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | [12 empty] | 1 | 1 | 1 | 2 | 18 | 27 |  | 43 | 44 | 47 | 0 |  |  | 0 | 221273
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 269 | 233 | 239 | 238 | 242 | 323 | 362 | 413 | 356 | 340 | 313 | 290 | 257 | 211 | 198 | 175 | 162 | 158 |  | 154 | 155 | 156 | 168 | 200 | 242 | 248 | 6005091
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [16 empty] | 4 | 5 |  | 6 | 7 | 12 | 16 |  |  |  | 39705
162 | Bogra 22 MW PP (GBB) | 20 | 3 | 3 | 3 | 3 | 18 | 18 | 18 | 18 | 17 | 17 | 16 | 16 | 15 | 15 | 15 | 15 | 15 |  | 18 | 20 | 20 | 20 | 20 | 20 | 20 | 354480
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 173574
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | [6 empty] | 8 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 |  | 50 | 50 | 50 | 42 | 42 | 42 | 42 | 715132
167 | Katakhali 50 MW Peaking PP | [11 empty] | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 40 | 16 | 16 | 16 | 16 | 0 |  | 166355
168 | Santahar 50 MW Peaking PP | [17 empty] | 28 |  | 32 | 35 | 35 | 35 | 35 | 35 |  | 188973
169 | Natore 52 MW PP (Rajlanka) | [7 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 139805
170 | Chapainawabganj 100 MW Peaking PP | [17 empty] | 68 |  | 67 | 60 | 59 | 59 | 34 |  |  | 249000
171 | Baghabari 200 MW PP (Paramount) | [16 empty] | 1 | 40 |  | 10 | 10 | 0 |  |  |  |  | 100907
| Bagura 113 MW PP (Confidence)-2 | 35 | [5 empty] | 24 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 58 |  | 70 | 70 | 70 | 70 | 70 | 35 | 35 | 901440
172 | Confidence Power Bogura Unit-1 113 MW | [10 empty] | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 60 |  | 75 | 75 | 75 | 75 | 75 | 75 | 70 | 770976
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [5 empty] | 1 | 33 | 113 | 109 | 105 | 107 | 103 | 34 | 34 | 34 | 100 | 113 | 113 |  | 113 | 113 | 113 | 113 | 70 | 34 | 34 | 1484985
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 2 | 3 | 4 | 5 | 5 | 3 | 3 | 2 | 0 | [9 empty] | 23660
178 | Energypac Power Venture Thakurgaon Ltd. | [6 empty] | 20 | 95 | 112 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 75 | 1911360
| Intraco Solar 30 MW | [6 empty] | 0 | 3 | 4 | 10 | 15 | 17 | 16 | 8 | 7 | 3 | 0 | [9 empty] | 86572
Adani Power Jharkhanda Ltd
178 | Teesta Solar Limited | [6 empty] | 1 | 6 | 7 | 66 | 7 | 66 | 41 | 84 | 49 | 20 | 2 | 0 | [8 empty] | 334800