## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2022-12-31 | Saturday
|  | Date (day): | 2022-12-31 |  | Saturday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 8256.6 | MW |  |  | (b) At Evening Peak Hour : |  | 10244 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2022-12-30 | 2022-12-31 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 240 | 180 | 180
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  |  | Machine problem
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Under maint.
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 70 | 70 | 70 | 70 | 38 |  | Machine problem
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 395 | 344 | 370 | 340 | 72 |  | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 304 | 263 | 330 | 310 | 50 |  | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 225 | 225 | 225 |  | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 17 | 17 | 17 | 17 | 83 |  | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 34 | 17 | 34 | 34 | 68 |  | Fuel shortage
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 0 | 15 | 0 | 25 | 30 |  | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 13 | 13 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 9 | 9 | 9 | 9 | 91 |  | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 16 | 16 | 16 | 16 | 86 |  | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 54 | 17 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 32 | 0 | 32 | 32 | 117 |  | Fuel shortage
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 55 | 35 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 55 | 35 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 38 | 46 | 47 | 47 |  | 33 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 20 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 31 | 33 | 30 | 30
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 20 | 8 | 50 | 50
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 32 | 98 | 32 | 95 | 205 |  | Fuel shortage
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 150 | 0 | 0 | 150 | 150 |  | Fuel conservation
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 0 | 0 | 0 | 50 | 50 |  | Fuel conservation
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 20 | 0 | 0 | 50 | 50 |  | Fuel conservation
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 35 | 40 | 35 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 68 | 17 | 105 | 105
37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 17 | 17 | 17 | 17 | 87 |  | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 17 | 162 | 17 | 162
39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 24 | 0 | 30 | 0
40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 17 | 17 | 17 | 38 |  | Fuel shortage
| Dhaka area Total |  |  |  |  | 6263 | 5847 | 1660 | 1851 | 1805 | 2399 | 2371 | 898
41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 120 | 140 | 120 | 120 | 60 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 25 | 8 | 25 | 25
43 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 18 | 0 | 20 | 0
44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 20 | 6 | 20 | 40 |  | 10 | Engine problem
45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 46 | 30 | 46 | 46 | 184 |  | Low Water Level
46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | Under maint
47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 17 | 17 | 17 | 51 | 54 |  | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 24 | 0 | 24 | 32 | 66 |  | Fuel shortage
50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 0 | 51 | 51 |  | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 22 | 22 | 22 | 22 | 78 |  | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 25 | 25 | 25 | 25 | 75 |  | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 22 |  | Gas shortage
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 32 | 30 | 20 | 30
54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 0 | 12 | 96 |  | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 51 | 294 | 51 | 290
57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 17 | 17 | 17 | 17 |  | 37 | Engine problem
58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 72 | 72 | 72 | 72 |  | 38 | Engine problem
59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 25 | 25 | 25 | 75 |  | Fuel shortage
60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 68 | 68 | 68 | 68 |  | 48 | Engine problem
| Mirsharai 150 MW |  | Gas/HSD | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0
| Chattogram area Total |  |  |  |  | 2442 | 2382 | 586 | 754 | 577 | 926 | 941 | 508
61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 203 | 190 | 200 | 200 |  |  | FGMO
63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 325 | 290 | 310 | 320 |  |  | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 | 360 |  | Gas shortage
65 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 330 | 348 | 300 | 330 | 70 |  | Gas shortage
66 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 5 | 5 | 5 | 5 | 40 |  | Gas shortage
67 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 55 | 5 | 5 | 5 | 5 | 50 |  | Gas shortage
68 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
69 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
70 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 6 | 75 | 6 | 75 | 75 |  | Fuel shortage
71 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 25 | 30 |  | 22 | Engine problem
72 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under Maint.
73 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 17 | 17 | 17 | 17 | 183 |  | Fuel shortage
74 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 21 | 21 | 21
75 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 10 | 10 | 10 | 10
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 84 | 100 | 135 | 152
76 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 22 | 25 | 33 | 33
77 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 8 | 8 | 8 | 44 |  | Fuel shortage
78 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 15 | 21 | 21 | 21 |  | 4 | Engine problem
79 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 100 | 100 |  | Fuel conservation
80 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 81 | 17 | 17 | 17 | 97 |  | Fuel shortage
81 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 27 | 107 | 108 | 108 |  | 5 | Engine problem
82 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 17 |  | 37 | Engine problem
83 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 0 | 0 | 0 | 115 |  | Fuel shortage
| Cumilla Area Total |  |  |  |  | 3309 | 3285 | 1235 | 1315 | 1297 | 1528 | 1455 | 231
84 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 34 | 107 | 70 | 100 | 102 |  | Gas shortage
85 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 14 | 20 | 22 | 22
86 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0
87 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1 | 0 | 1.6 | 0
88 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 48 | 48 | 48 | 48 | 152 |  | Fuel shortage
89 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 28 | 47 | 28 | 47 | 68 |  | Fuel shortage
90 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 15 | 0 | 50 | 0
91 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 12 | 12
| Mymensingh Area Total |  |  |  |  | 717 | 614 | 152 | 234 | 231.6 | 229 | 102 | 0
92 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 30 | 30 | 30 | 30 |  | 40 | Machine problem.
93 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 31 | 31 | 20 | 30 |  | 60 | Machine problem
94 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 112 | 112 | 112 | 112 |  | 51 | ST Under S/D
95 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
96 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 51 | 53 | 48 | 48
97 | Fenchuganj 44MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 22 | 46 | 44 | 44 | 6
98 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 8 | 8 |  | 3 | Engine problem
99 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 63 | 64 | 62 | 64
100 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 30 | 86 | 50 | 86
101 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
102 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 0 | 0 | 0 |  | 231 | Under maint
103 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 19 | 19 | 19 | 19
104 | Sylhet 50MW PP (EPL) |  | Gas | NENP | 27*2 | 50 | 50 | 27 | 26 | 27 | 27 | 23 |  | Gas shortage
105 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 16 | 16 | 16
106 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 0 | 0 | 0 | 0 |  | 341 | Under maint.
107 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 410 | 400 | 350 | 400
108 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
109 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 400 | 400 | 400 | 400
| Sylhet Area Total |  |  |  |  | 2522 | 2477 | 1229 | 1301 | 1196 | 1294 | 29 | 1156
110 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 682 | 871 | 743 | 935
111 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 99 | 32 | 40 | 99 | 16 |  | Fuel shortage
112 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 40 |  | 14 | Engine problem
113 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
114 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 70 |  | 39 | Engine problem
115 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 | 410 |  | Gas shortage.
116 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 0 | 40 | 40
117 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 0 | 50 | 50 |  | Fuel conservation
118 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 17 | 18 | 18 | 87 |  | Fuel shortage
119 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Fuel shortage
120 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 61 | 0 | 100 | 0
| Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 2388 | 2384 | 842 | 920 | 941 | 1252 | 914 | 53
121 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 0 | 0 |  |  | Line O/L
122 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 19 | 23 | 18 | 24 |  | 16 | Engine problem
123 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 112 | 182 | 180 | 180 |  |  | Machine problem
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
124 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 480 | 610 | 500 | 622 |  | 622 | Unit-2 U/M
125 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 120 | 219 | 160 | 220
126 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 0 | 0 |  |  | Line O/L
| Barisal 307 MW |  | Coal | BCPCL | 0 | 0 | 0 | 309 | 309 | 300 | 300 |  |  | On test.
| Barisal Area Total |  |  |  |  | 1958 | 1958 | 1040 | 1343 | 1158 | 1346 | 0 | 638
127 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
128 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 34 |  | 18 | Engine problem
129 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 25 |  | 46 | Engine problem
130 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
131 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 34 | 8 | 42 | 42 |  | 8 | Engine problem
132 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 16 | 0 | 0 | 40 |  | 10 | Engine problem
133 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
134 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 166 | 170 | 200 | 160
135 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 |  | 220 | Under maint
136 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 348 | 313 | 350 | 320 | 94 |  | Gas shortage
137 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 32 |  | 18 | Engine problem
138 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 18 | 21 | 20 | 20 |  | 2 | Machine problem
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
139 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 8 | 8 |  | 3 | Engine problem
140 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 8 | 8 | 8 | 44 |  | Fuel shortage
141 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 51 | 0 | 67 | 37 |  | Fuel shortage
142 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 0 | 100 | 100 |  | Fuel conservation
143 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 35 | 50 | 35 | 50 | 63 |  | Fuel shortage
144 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 35 | 55 | 35 | 55 | 58 |  | Fuel shortage
145 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 2 | 0 | 6 | 0
| Adani Power Jharkhanda Ltd |  | Coal | Import | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Rajshahi Area Total |  |  |  |  | 2179 | 2129 | 670 | 684 | 704 | 961 | 777 | 325
146 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal shortage
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
147 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 160 | 160 | 160 | 160 |  |  | Machine problem
148 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
149 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
150 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 27 | 34 | 34 | 34 | 79 |  | Fuel shortage
151 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 4 | 0 | 8 | 0
152 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 115 | 75 | 115 | 115
153 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 24 | 0 | 30 | 0
| Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 0 | 0 | 136 | 0 | 0 | 0
| Rangpur Area Total |  |  |  |  | 830 | 750 | 466 | 269 | 347 | 309 | 204 | 85
| Total |  |  |  |  | 22608 | 21826 | 7880 | 8671 | 8256.6 | 10244 | 6793 | 3894
A. |  | 2022-12-30 | (Yesterday) |  |  |  |  | Friday
1 | Highest Generation : |  |  | 8671 | MW at | 19:30 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:30 | hrs.
2 | Minimum Generation : |  |  | 6199 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 8671 | MW
3 | Day peak Generation : |  |  | 7880 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 8313.7 | MW
4 | Evening peak Generation : |  |  | 8671 | MW at | 19:30 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 180.2012 | MKWHr | By Solar | 1.5788 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Gas : | 106.6891 | MKWHr |  | By Oil: | 29.3227 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 23.0596 | MKWHr |  | By Hydro: | 1.0483 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 6793 | MW | Dhaka | 2852.92 | 2852.92 |  | 0 |  | 18:00 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 3894 | MW | Chittagong | 921.9 | 921.9 |  | 0 |  | 19:00 |  | 0
|  |  | Total = |  |  | 10687 | MW | Khulna | 1032 | 1032 |  | 0 |  | 19:30 |  | 0
7 | Total Gas Supplied : |  |  | 821.19 | MMCFD |  |  | Rajshahi | 862.4 | 862.4 |  | 0 |  | 20:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 115158271.3 | ii) Oil : | Taka | 383302076.28 | Comilla | 749 | 749 |  | 0 |  | 21:00 |  | 0
|  | iii) Coal : |  | 126129134 | Total | Taka | 624589481.58 | Mymensingh | 735 | 735 |  | 0 |  | 22:00 |  | 0
9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0 | MKWHr. | Sylhet | 322 | 322 |  | 0 |  | 23:00 |  | 0
| ii) During Peak Demand : |  |  | 102 | MW (E to W) at | 19:30 | hrs | Barisal | 257.48 | 257.48 |  | 0 |  | 24:00 |  | 0
| iii) Maximum : |  |  | -40 | MW at | 7:00 | hrs | Rangpur | 581 | 581 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 22.2° C |  |  | Total | 8313.7 | 8313.7 |  | 0
B. |  | 2022-12-31 | (Today) |  |  |  | Saturday |  |  | Probable max. temperature in Dhaka |  |  | 24.3° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 9500 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 10244 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 8300 | MW
4 | Reserve(Generation end) |  |  |  | 744 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 197.4295 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5746 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 16.5251 | MKWHr. | ii) HVDC Flow at Peak Time |  | 871 | MW at | 19:30 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.9776 | MKWHr. | iii) Maximum HVDC Flow : |  | 872 | MW at | 21:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 86.67 |  | (b) Today: | 86.59 |  | (c) Rule Curve: |  | 103.1
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2022-12-30
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 201 | 0 | 0 | 73 | 0 | 391 | 296 |  | 0 | 225 | 0 | 18 | 34 | 0 | 0 | 0 | 0 | 9 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 22 | 22 | 22 | 25 | 28 | 8 | 0 | 46 | 0 | 120 | 0 | 25 | 0 | 0 | 0 | 0 |  | 10 | 0 | 0 | 22 | 0 | 21 | 0 | 25 | 0 | 0 | 0 | 290 | 0 | 183 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 0 | 8 | 21 | 10 | 33 | 15 | 70 | 93 | 0 | 0 | 0 | 30 | 20 | 53 | 47 | 112 | 0 | 40 | 10 | 0 | 0 | 19 | 27 | 10 | 0 | 16 | 8 | 0 | 32 | 0 | 0 | 48 | 0 | 35 | 0 | 25 | 17 | 6 | 363 | 28 | 17 | 17 | 0 | 51 | 17 | 72 | 51 | 9 | 25 | 400 | 17 | 0 | 17 | 87 | 0 | 17 | 0 | 0 | 17 | 258 | 0 | 0 |  | 729 | 0 | 0 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 8 | 18 | 22 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 35 | 0 | 27 | 0 | 0 | 35 | 360 | 110 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 307 | 0 | 0 |  | 4513 | 2637 | 7150 | 2859 | 729 | 1420 | 0 | 1181 | 827 | 46 | 0 | 18 | 70 | 0 | 0 | 86.68
2:00 | 0 | 0 | 202 | 0 | 0 | 73 | 0 | 391 | 294 |  | 0 | 225 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 22 | 22 | 22 | 25 | 28 | 0 | 0 | 46 | 0 | 120 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 0 | 0 | 22 | 0 | 20 | 0 | 29 | 0 | 0 | 0 | 290 | 0 | 186 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 0 | 8 | 21 | 9 | 33 | 15 | 64 | 96 | 0 | 0 | 0 | 30 | 20 | 53 | 47 | 112 | 0 | 40 | 10 | 0 | 0 | 19 | 27 | 10 | 0 | 16 | 8 | 0 | 32 | 0 | 0 | 48 | 0 | 35 | 0 | 25 | 17 | 6 | 363 | 28 | 17 | 17 | 0 | 51 | 17 | 72 | 17 | 9 | 25 | 400 | 17 | 0 | 17 | 87 | 0 | 17 | 0 | 0 | 17 | 259 | 0 | 0 |  | 607 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 159 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 35 | 0 | 34 | 0 | 0 | 0 | 340 | 109 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 0 | 0 | 308 | 0 | 0 |  | 4448 | 2355 | 6803 | 2870 | 607 | 1425 | 0 | 984 | 807 | 46 | 0 | 0 | 64 | 0 | 0 | 86.68
3:00 | 0 | 0 | 202 | 0 | 0 | 73 | 0 | 391 | 303 |  | 0 | 225 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 22 | 22 | 22 | 25 | 28 | 0 | 0 | 46 | 0 | 120 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 0 | 0 | 22 | 0 | 10 | 0 | 27 | 0 | 0 | 0 | 295 | 0 | 183 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 0 | 8 | 21 | 9 | 33 | 15 | 66 | 93 | 0 | 0 | 0 | 30 | 20 | 53 | 47 | 112 | 0 | 40 | 10 | 0 | 0 | 19 | 27 | 10 | 0 | 16 | 8 | 0 | 32 | 0 | 0 | 48 | 0 | 35 | 0 | 25 | 17 | 6 | 363 | 28 | 17 | 17 | 0 | 51 | 17 | 72 | 0 | 9 | 25 | 400 | 17 | 0 | 17 | 87 | 0 | 17 | 0 | 0 | 17 | 268 | 0 | 0 |  | 563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 159 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 300 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 309 | 0 | 0 |  | 4438 | 2088 | 6526 | 2878 | 563 | 1446 | 0 | 759 | 768 | 46 | 0 | 0 | 66 | 0 | 0 | 86.68
4:00 | 0 | 0 | 205 | 0 | 0 | 73 | 0 | 386 | 300 |  | 0 | 225 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 22 | 22 | 22 | 25 | 28 | 0 | 0 | 46 | 0 | 120 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 0 | 0 | 22 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 290 | 0 | 183 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 9 | 33 | 15 | 64 | 101 | 0 | 0 | 0 | 30 | 20 | 53 | 47 | 112 | 0 | 40 | 10 | 0 | 0 | 19 | 27 | 10 | 0 | 16 | 8 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 25 | 17 | 0 | 363 | 28 | 0 | 0 | 0 | 51 | 17 | 64 | 0 | 0 | 25 | 400 | 17 | 0 | 17 | 87 | 0 | 17 | 0 | 0 | 17 | 288 | 0 | 0 |  | 563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 159 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 0 | 0 |  | 4320 | 2034 | 6354 | 2899 | 563 | 1433 | 0 | 583 | 766 | 46 | 0 | 0 | 64 | 0 | 0 | 86.67
5:00 | 0 | 0 | 201 | 0 | 0 | 73 | 0 | 362 | 276 |  | 0 | 225 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 22 | 22 | 22 | 25 | 30 | 0 | 0 | 46 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12 | 0 | 0 | 22 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 310 | 0 | 193 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 9 | 33 | 15 | 64 | 103 | 0 | 0 | 0 | 30 | 20 | 53 | 47 | 112 | 0 | 40 | 10 | 0 | 0 | 19 | 27 | 10 | 0 | 16 | 8 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 25 | 17 | 0 | 326 | 28 | 0 | 0 | 0 | 51 | 17 | 72 | 0 | 0 | 25 | 341 | 17 | 0 | 17 | 87 | 0 | 17 | 0 | 0 | 0 | 298 | 0 | 0 |  | 564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 0 | 0 |  | 4167 | 2032 | 6199 | 2819 | 564 | 1407 | 0 | 532 | 767 | 46 | 0 | 0 | 64 | 0 | 0 | 86.67
6:00 | 0 | 0 | 195 | 0 | 0 | 73 | 0 | 363 | 275 |  | 0 | 225 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 22 | 22 | 22 | 25 | 30 | 0 | 0 | 46 | 0 | 120 | 0 | 1 | 0 | 0 | 0 | 0 |  | 12 | 0 | 0 | 22 | 0 | 1 | 0 | 37 | 0 | 0 | 0 | 320 | 0 | 196 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 0 | 1 | 21 | 9 | 33 | 15 | 74 | 93 | 0 | 0 | 0 | 30 | 20 | 53 | 44 | 112 | 0 | 65 | 30 | 0 | 0 | 19 | 27 | 10 | 0 | 16 | 8 | 0 | 10 | 0 | 0 | 48 | 0 | 10 | 0 | 25 | 17 | 2 | 340 | 28 | 10 | 2 | 0 | 51 | 17 | 72 | 1 | 0 | 25 | 342 | 17 | 0 | 17 | 87 | 0 | 17 | 0 | 0 | 9 | 314 | 0 | 0 |  | 563 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 5 | 0 | 22 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 18 | 300 | 109 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 309 | 0 | 0 |  | 4294 | 2175 | 6469 | 2873 | 563 | 1425 | 0 | 719 | 769 | 46 | 0 | 0 | 74 | 0 | 0 | 86.67
7:00 | 0 | 0 | 170 | 0 | 0 | 70 | 0 | 342 | 270 |  | 0 | 225 | 0 | 6 | 17 | 0 | 0 | 0 | 0 | 9 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 13 | 22 | 22 | 25 | 31 | 0 | 0 | 46 | 0 | 120 | 0 | 8 | 0 | 0 | 0 | 0 |  | 12 | 0 | 0 | 22 | 0 | 12 | 0 | 31 | 0 | 0 | 0 | 325 | 0 | 198 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 0 | 8 | 21 | 9 | 33 | 15 | 72 | 70 | 0 | 0 | 0 | 30 | 20 | 51 | 44 | 112 | 0 | 64 | 30 | 0 | 0 | 19 | 27 | 10 | 0 | 16 | 8 | 0 | 32 | 0 | 0 | 48 | 0 | 26 | 1 | 25 | 17 | 6 | 360 | 28 | 17 | 17 | 0 | 51 | 17 | 72 | 17 | 9 | 25 | 351 | 17 | 0 | 17 | 87 | 0 | 17 | 0 | 0 | 17 | 358 | 0 | 0 |  | 563 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 35 | 0 | 22 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 282 | 5 | 0 | 4 | 0 | 33 | 0 | 0 | 18 | 280 | 109 | 0 | 0 | 0 | 1 | 52 | 0 | 0 | 0 | 0 | 307 | 0 | 2 |  | 4398 | 2211 | 6609 | 2885 | 563 | 1364 | 0 | 928 | 747 | 46 | 0 | 0 | 72 | 4 | 0 | 86.66
8:00 | 0 | 0 | 200 | 0 | 0 | 70 | 0 | 342 | 335 |  | 0 | 225 | 0 | 14 | 20 | 0 | 0 | 0 | 0 | 9 | 8 | 32 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 13 | 22 | 22 | 25 | 31 | 5 | 0 | 46 | 0 | 120 | 0 | 19 | 0 | 0 | 0 | 0 |  | 7 | 10 | 0 | 22 | 0 | 20 | 0 | 37 | 0 | 0 | 0 | 325 | 0 | 195 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 0 | 8 | 21 | 9 | 30 | 15 | 70 | 35 | 0 | 0 | 0 | 30 | 20 | 51 | 47 | 112 | 0 | 64 | 30 | 0 | 0 | 19 | 27 | 10 | 0 | 16 | 8 | 0 | 32 | 0 | 0 | 48 | 0 | 35 | 5 | 25 | 17 | 6 | 369 | 28 | 18 | 17 | 1 | 51 | 17 | 72 | 34 | 9 | 25 | 370 | 17 | 2 | 17 | 87 | 0 | 9 | 1 | 0 | 17 | 370 | 0 | 0 |  | 564 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 43 | 0 | 22 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 146 | 0 | 0 | 0 | 0 | 0 | 405 | 17 | 0 | 35 | 0 | 35 | 0 | 0 | 18 | 320 | 109 | 0 | 0 | 0 | 14 | 85 | 0 | 0 | 0 | 4 | 309 | 0 | 12 |  | 4598 | 2495 | 7093 | 2920 | 564 | 1560 | 0 | 1063 | 789 | 46 | 0 | 42 | 70 | 39 | 0 | 86.66
9:00 | 0 | 0 | 200 | 0 | 0 | 70 | 0 | 384 | 325 |  | 0 | 225 | 0 | 17 | 34 | 0 | 0 | 0 | 0 | 9 | 8 | 32 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 13 | 22 | 22 | 25 | 31 | 16 | 0 | 46 | 0 | 120 | 0 | 25 | 0 | 0 | 0 | 0 |  | 8 | 20 | 0 | 22 | 0 | 20 | 0 | 37 | 0 | 0 | 0 | 305 | 0 | 193 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 0 | 8 | 21 | 10 | 24 | 15 | 80 | 34 | 0 | 0 | 0 | 30 | 20 | 51 | 47 | 112 | 0 | 64 | 30 | 0 | 0 | 19 | 27 | 10 | 0 | 16 | 8 | 0 | 33 | 0 | 0 | 48 | 0 | 35 | 11 | 25 | 17 | 6 | 374 | 28 | 34 | 17 | 1 | 51 | 17 | 72 | 70 | 9 | 25 | 400 | 17 | 4 | 17 | 87 | 0 | 17 | 2 | 0 | 17 | 338 | 0 | 0 |  | 563 | 0 | 0 | 0 | 86 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 43 | 0 | 21 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 148 | 0 | 0 | 0 | 0 | 0 | 390 | 17 | 0 | 35 | 0 | 35 | 0 | 2 | 18 | 380 | 105 | 0 | 0 | 0 | 32 | 115 | 0 | 0 | 0 | 10 | 307 | 0 | 21 |  | 4747 | 2637 | 7384 | 2939 | 563 | 1531 | 0 | 1243 | 847 | 46 | 0 | 52 | 80 | 83 | 0 | 86.66
10:00 | 0 | 0 | 200 | 0 | 0 | 70 | 0 | 394 | 325 |  | 0 | 225 | 0 | 16 | 34 | 0 | 0 | 0 | 0 | 9 | 8 | 32 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 13 | 22 | 22 | 25 | 31 | 16 | 0 | 46 | 0 | 120 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 24 | 0 | 22 | 0 | 20 | 0 | 33 | 0 | 0 | 0 | 290 | 0 | 183 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 0 | 8 | 21 | 10 | 23 | 15 | 82 | 34 | 0 | 0 | 0 | 30 | 31 | 51 | 47 | 112 | 0 | 65 | 30 | 0 | 0 | 19 | 27 | 10 | 0 | 16 | 8 | 0 | 33 | 0 | 0 | 48 | 0 | 35 | 16 | 25 | 17 | 6 | 392 | 28 | 51 | 17 | 2 | 51 | 17 | 72 | 70 | 9 | 25 | 370 | 17 | 7 | 17 | 85 | 0 | 17 | 6 | 0 | 17 | 350 | 0 | 0 |  | 563 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 4 | 43 | 0 | 19 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 153 | 0 | 0 | 0 | 0 | 0 | 314 | 17 | 0 | 35 | 0 | 30 | 0 | 2 | 25 | 450 | 105 | 0 | 0 | 0 | 49 | 115 | 0 | 0 | 0 | 16 | 307 | 0 | 41 |  | 4776 | 2696 | 7472 | 2940 | 563 | 1448 | 0 | 1277 | 917 | 46 | 0 | 60 | 82 | 139 | 0 | 86.65
11:00 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 388 | 312 |  | 0 | 225 | 0 | 17 | 34 | 0 | 0 | 0 | 0 | 9 | 16 | 32 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 13 | 22 | 23 | 25 | 31 | 16 | 0 | 46 | 0 | 120 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 24 | 0 | 22 | 0 | 20 | 0 | 31 | 0 | 0 | 0 | 290 | 0 | 183 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 0 | 8 | 21 | 10 | 22 | 15 | 78 | 34 | 0 | 12 | 0 | 30 | 31 | 51 | 22 | 112 | 0 | 64 | 30 | 0 | 0 | 19 | 27 | 10 | 0 | 16 | 8 | 0 | 32 | 0 | 0 | 58 | 0 | 35 | 18 | 25 | 17 | 6 | 399 | 28 | 51 | 17 | 3 | 51 | 17 | 72 | 70 | 13 | 25 | 400 | 17 | 9 | 17 | 68 | 0 | 17 | 15 | 0 | 17 | 350 | 0 | 0 |  | 563 | 0 | 0 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 118 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 12 | 8 | 0 | 19 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 154 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 0 | 35 | 0 | 22 | 0 | 3 | 35 | 460 | 110 | 0 | 0 | 1 | 60 | 115 | 0 | 0 | 0 | 21 | 306 | 0 | 110 |  | 4593 | 2842 | 7435 | 2811 | 563 | 1472 | 0 | 1231 | 926 | 46 | 0 | 68 | 78 | 240 | 0 | 86.65
12:00 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 395 | 304 |  | 0 | 225 | 0 | 17 | 34 | 0 | 0 | 0 | 0 | 9 | 16 | 32 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 13 | 22 | 16 | 25 | 31 | 20 | 0 | 46 | 0 | 120 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 24 | 0 | 22 | 0 | 20 | 0 | 32 | 0 | 0 | 0 | 325 | 0 | 203 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 0 | 8 | 21 | 10 | 22 | 15 | 84 | 34 | 0 | 14 | 1 | 30 | 31 | 51 | 22 | 112 | 0 | 63 | 30 | 0 | 0 | 19 | 27 | 10 | 0 | 16 | 8 | 0 | 32 | 150 | 0 | 48 | 20 | 35 | 18 | 25 | 17 | 6 | 410 | 28 | 68 | 17 | 4 | 51 | 17 | 72 | 81 | 27 | 25 | 400 | 17 | 15 | 17 | 68 | 0 | 17 | 24 | 0 | 17 | 330 | 0 | 0 |  | 682 | 0 | 0 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 112 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 16 | 8 | 0 | 18 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 166 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 35 | 0 | 27 | 0 | 4 | 35 | 480 | 120 | 0 | 0 | 2 | 61 | 115 | 0 | 0 | 0 | 24 | 309 | 0 | 136 |  | 4862 | 3018 | 7880 | 2864 | 682 | 1452 | 170 | 1272 | 949 | 46 | 0 | 72 | 84 | 289 | 0 | 86.65
13:00 | 0 | 0 | 68 | 0 | 0 | 70 | 0 | 396 | 304 |  | 0 | 225 | 0 | 17 | 34 | 0 | 0 | 0 | 0 | 9 | 16 | 32 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 13 | 22 | 14 | 25 | 31 | 43 | 0 | 46 | 0 | 120 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 24 | 0 | 22 | 0 | 20 | 0 | 42 | 0 | 0 | 0 | 290 | 0 | 183 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 0 | 8 | 21 | 10 | 22 | 15 | 104 | 34 | 0 | 14 | 1 | 30 | 31 | 51 | 40 | 112 | 0 | 64 | 30 | 0 | 0 | 19 | 27 | 10 | 0 | 16 | 8 | 50 | 32 | 120 | 0 | 48 | 50 | 35 | 17 | 25 | 17 | 6 | 406 | 28 | 105 | 17 | 3 | 51 | 17 | 72 | 100 | 28 | 25 | 400 | 17 | 30 | 17 | 68 | 0 | 17 | 24 | 0 | 17 | 330 | 0 | 0 |  | 682 | 0 | 0 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 16 | 8 | 0 | 17 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 322 | 0 | 0 | 35 | 0 | 27 | 0 | 5 | 35 | 540 | 135 | 0 | 0 | 2 | 59 | 115 | 0 | 0 | 0 | 22 | 307 | 0 | 125 |  | 5062 | 3140 | 8202 | 2962 | 682 | 1469 | 220 | 1352 | 1007 | 46 | 0 | 72 | 104 | 288 | 0 | 86.64
14:00 | 0 | 0 | 130 | 0 | 0 | 22 | 0 | 354 | 255 |  | 0 | 225 | 0 | 17 | 34 | 0 | 0 | 0 | 0 | 9 | 16 | 32 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 13 | 22 | 14 | 25 | 33 | 8 | 0 | 46 | 0 | 120 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 24 | 0 | 22 | 0 | 20 | 0 | 42 | 0 | 0 | 0 | 320 | 0 | 203 | 8 | 0 | 5 | 5 | 0 | 15 | 0 | 0 | 8 | 21 | 10 | 20 | 15 | 88 | 34 | 0 | 20 | 1 | 30 | 31 | 14 | 10 | 112 | 0 | 42 | 10 | 0 | 0 | 19 | 11 | 10 | 0 | 16 | 8 | 0 | 32 | 0 | 0 | 48 | 0 | 35 | 14 | 25 | 17 | 6 | 222 | 28 | 17 | 17 | 2 | 51 | 17 | 72 | 17 | 28 | 25 | 340 | 0 | 28 | 17 | 68 | 0 | 17 | 19 | 0 | 17 | 300 | 0 | 0 |  | 657 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 8 | 181 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 16 | 8 | 0 | 17 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 35 | 0 | 34 | 0 | 4 | 35 | 490 | 145 | 0 | 0 | 3 | 50 | 90 | 0 | 0 | 0 | 18 | 310 | 0 | 104 |  | 4136 | 2885 | 7021 | 2740 | 657 | 1177 | 0 | 1038 | 960 | 46 | 0 | 72 | 88 | 243 | 0 | 86.65
15:00 | 0 | 0 | 170 | 0 | 0 | 22 | 0 | 323 | 255 |  | 0 | 225 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 13 | 22 | 14 | 25 | 33 | 0 | 0 | 46 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12 | 24 | 0 | 22 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 285 | 0 | 187 | 8 | 0 | 5 | 5 | 0 | 15 | 0 | 0 | 8 | 21 | 10 | 20 | 15 | 86 | 34 | 0 | 20 | 1 | 30 | 31 | 14 | 10 | 112 | 0 | 40 | 10 | 0 | 0 | 19 | 11 | 10 | 0 | 16 | 8 | 0 | 32 | 0 | 0 | 57 | 0 | 35 | 11 | 25 | 17 | 6 | 322 | 28 | 17 | 17 | 2 | 51 | 17 | 64 | 0 | 28 | 25 | 340 | 0 | 18 | 17 | 68 | 0 | 17 | 13 | 0 | 17 | 330 | 0 | 0 |  | 657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 180 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 8 | 0 | 17 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 0 | 0 | 255 | 0 | 0 | 35 | 0 | 34 | 0 | 3 | 35 | 470 | 150 | 0 | 0 | 2 | 30 | 0 | 0 | 0 | 0 | 12 | 309 | 0 | 70 |  | 4072 | 2634 | 6706 | 2802 | 657 | 1173 | 0 | 801 | 939 | 46 | 0 | 40 | 86 | 162 | 0 | 86.64
16:00 | 0 | 0 | 180 | 0 | 0 | 22 | 0 | 336 | 288 |  | 0 | 225 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 35 | 13 | 22 | 14 | 25 | 33 | 0 | 0 | 37 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12 | 24 | 0 | 22 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 285 | 0 | 184 | 8 | 0 | 5 | 5 | 0 | 15 | 0 | 0 | 8 | 21 | 10 | 22 | 15 | 84 | 39 | 0 | 20 | 0 | 30 | 31 | 11 | 10 | 112 | 0 | 40 | 30 | 0 | 0 | 19 | 11 | 10 | 0 | 16 | 8 | 0 | 32 | 0 | 0 | 24 | 0 | 35 | 5 | 25 | 17 | 16 | 352 | 8 | 0 | 17 | 1 | 30 | 17 | 34 | 0 | 8 | 25 | 371 | 0 | 7 | 17 | 34 | 0 | 17 | 6 | 0 | 17 | 338 | 0 | 0 |  | 657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 181 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 8 | 0 | 17 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 159 | 0 | 0 | 0 | 0 | 0 | 261 | 0 | 0 | 35 | 0 | 0 | 0 | 2 | 35 | 430 | 157 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 5 | 311 | 0 | 29 |  | 4007 | 2507 | 6514 | 2897 | 657 | 1226 | 0 | 603 | 901 | 37 | 0 | 40 | 84 | 69 | 0 | 86.63
17:00 | 0 | 0 | 200 | 0 | 0 | 22 | 0 | 362 | 280 |  | 0 | 225 | 0 | 2 | 17 | 5 | 0 | 0 | 0 | 2 | 16 | 32 | 0 | 0 | 0 | 0 | 17 | 17 | 35 | 13 | 22 | 15 | 25 | 33 | 2 | 0 | 30 | 0 | 120 | 0 | 1 | 0 | 0 | 0 | 0 |  | 12 | 24 | 7 | 22 | 5 | 1 | 0 | 20 | 0 | 0 | 0 | 290 | 0 | 184 | 8 | 0 | 5 | 5 | 0 | 15 | 0 | 0 | 8 | 21 | 10 | 21 | 15 | 86 | 58 | 0 | 20 | 0 | 30 | 31 | 18 | 10 | 112 | 0 | 40 | 30 | 0 | 0 | 19 | 16 | 10 | 0 | 16 | 8 | 0 | 58 | 0 | 0 | 24 | 0 | 35 | 1 | 25 | 17 | 70 | 392 | 9 | 1 | 21 | 0 | 132 | 17 | 34 | 17 | 13 | 25 | 350 | 0 | 1 | 54 | 34 | 0 | 17 | 1 | 0 | 17 | 348 | 0 | 0 |  | 657 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 13 | 32 | 8 | 172 | 16 | 0 | 0 | 0 | 0 | 0 | 4 | 40 | 0 | 8 | 16 | 8 | 15 | 19 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 159 | 0 | 0 | 0 | 0 | 0 | 263 | 5 | 0 | 35 | 0 | 1 | 0 | 0 | 35 | 430 | 160 | 0 | 0 | 0 | 2 | 7 | 0 | 0 | 0 | 1 | 309 | 0 | 4 |  | 4383 | 2611 | 6994 | 2987 | 657 | 1229 | 0 | 913 | 899 | 30 | 0 | 183 | 86 | 10 | 0 | 86.63
18:00 | 0 | 0 | 200 | 0 | 0 | 54 | 0 | 333 | 254 |  | 0 | 225 | 0 | 16 | 34 | 25 | 0 | 0 | 0 | 9 | 16 | 48 | 0 | 0 | 0 | 0 | 54 | 17 | 35 | 13 | 22 | 17 | 25 | 33 | 16 | 0 | 40 | 0 | 140 | 0 | 8 | 0 | 0 | 0 | 0 |  | 12 | 24 | 34 | 22 | 11 | 6 | 0 | 35 | 0 | 0 | 0 | 325 | 0 | 205 | 8 | 0 | 5 | 5 | 0 | 15 | 0 | 0 | 8 | 21 | 10 | 16 | 21 | 102 | 75 | 0 | 20 | 0 | 30 | 31 | 52 | 35 | 112 | 0 | 64 | 86 | 0 | 0 | 19 | 27 | 10 | 0 | 16 | 8 | 0 | 95 | 0 | 0 | 47 | 0 | 35 | 0 | 25 | 17 | 75 | 359 | 47 | 17 | 17 | 0 | 286 | 17 | 64 | 17 | 60 | 25 | 360 | 14 | 0 | 162 | 68 | 0 | 17 | 0 | 0 | 17 | 348 | 0 | 0 |  | 871 | 0 | 0 | 0 | 114 | 0 | 0 | 0 | 45 | 74 | 32 | 181 | 21 | 0 | 0 | 0 | 0 | 34 | 4 | 51 | 0 | 8 | 19 | 8 | 35 | 19 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 159 | 0 | 0 | 0 | 0 | 0 | 225 | 17 | 0 | 35 | 0 | 33 | 0 | 0 | 55 | 420 | 220 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 0 | 311 | 0 | 0 |  | 5293 | 3196 | 8489 | 3064 | 871 | 1403 | 0 | 1750 | 891 | 40 | 0 | 368 | 102 | 0 | 0 | 86.63
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 240 | 0 | 0 | 67 | 0 | 348 | 276 |  | 0 | 225 | 0 | 17 | 23 | 25 | 0 | 0 | 0 | 9 | 16 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 13 | 22 | 24 | 25 | 33 | 8 | 0 | 30 | 0 | 140 | 0 | 8 | 0 | 0 | 0 | 0 |  | 12 | 0 | 17 | 22 | 11 | 6 | 0 | 37 | 0 | 0 | 0 | 290 | 0 | 183 | 8 | 0 | 5 | 5 | 0 | 48 | 0 | 0 | 8 | 21 | 10 | 24 | 21 | 102 | 101 | 0 | 20 | 0 | 30 | 31 | 53 | 44 | 112 | 0 | 64 | 86 | 0 | 0 | 19 | 26 | 10 | 0 | 16 | 8 | 0 | 98 | 0 | 0 | 47 | 0 | 36 | 0 | 25 | 17 | 75 | 400 | 47 | 17 | 17 | 0 | 290 | 17 | 70 | 17 | 85 | 25 | 400 | 17 | 0 | 162 | 68 | 0 | 17 | 0 | 0 | 17 | 348 | 0 | 0 |  | 871 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 30 | 0 | 182 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 8 | 0 | 8 | 0 | 21 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 0 | 312 | 17 | 0 | 40 | 0 | 34 | 0 | 0 | 55 | 550 | 221 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 310 | 0 | 0 |  | 5475 | 3166 | 8641 | 3189 | 871 | 1574 | 0 | 1757 | 1020 | 30 | 0 | 98 | 102 | 0 | 0 | 86.62
19:30 | 0 | 0 | 240 | 0 | 0 | 70 | 0 | 344 | 263 |  | 0 | 225 | 0 | 17 | 17 | 15 | 0 | 0 | 0 | 9 | 16 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 13 | 22 | 24 | 20 | 33 | 8 | 0 | 30 | 0 | 140 | 0 | 8 | 0 | 0 | 0 | 0 |  | 12 | 0 | 0 | 22 | 0 | 6 | 0 | 30 | 0 | 0 | 0 | 290 | 0 | 190 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 0 | 8 | 21 | 10 | 25 | 21 | 100 | 107 | 0 | 20 | 0 | 30 | 31 | 53 | 46 | 112 | 0 | 64 | 86 | 0 | 0 | 19 | 26 | 10 | 0 | 16 | 8 | 0 | 98 | 0 | 0 | 48 | 0 | 40 | 0 | 25 | 17 | 75 | 400 | 47 | 17 | 17 | 0 | 294 | 17 | 72 | 17 | 107 | 25 | 400 | 17 | 0 | 162 | 68 | 0 | 17 | 0 | 0 | 17 | 348 | 0 | 0 |  | 871 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 8 | 0 | 8 | 0 | 21 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 313 | 17 | 0 | 50 | 0 | 34 | 0 | 0 | 55 | 610 | 219 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | 0 | 309 | 0 | 0 |  | 5455 | 3216 | 8671 | 3201 | 871 | 1561 | 0 | 1778 | 1079 | 30 | 0 | 51 | 100 | 0 | 0 | 0
20:00 | 0 | 0 | 240 | 0 | 0 | 72 | 0 | 342 | 263 |  | 0 | 225 | 0 | 17 | 17 | 15 | 0 | 0 | 0 | 9 | 16 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 13 | 22 | 24 | 20 | 33 | 8 | 0 | 30 | 0 | 150 | 0 | 8 | 0 | 0 | 0 | 0 |  | 12 | 0 | 0 | 22 | 0 | 6 | 0 | 40 | 0 | 0 | 0 | 290 | 0 | 184 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 0 | 8 | 21 | 10 | 30 | 21 | 102 | 107 | 0 | 20 | 0 | 30 | 31 | 53 | 47 | 112 | 0 | 64 | 86 | 0 | 0 | 19 | 26 | 10 | 0 | 16 | 8 | 0 | 98 | 0 | 0 | 48 | 0 | 50 | 0 | 25 | 17 | 73 | 400 | 47 | 17 | 17 | 0 | 296 | 17 | 72 | 17 | 75 | 25 | 400 | 17 | 0 | 162 | 68 | 0 | 17 | 0 | 0 | 17 | 348 | 0 | 0 |  | 871 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 8 | 0 | 21 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 312 | 17 | 0 | 50 | 0 | 34 | 0 | 0 | 55 | 622 | 221 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | 0 | 310 | 0 | 0 |  | 5455 | 3179 | 8634 | 3208 | 871 | 1575 | 0 | 1756 | 1092 | 30 | 0 | 0 | 102 | 0 | 0 | 86.62
21:00 | 0 | 0 | 240 | 0 | 0 | 73 | 0 | 335 | 255 |  | 0 | 225 | 0 | 13 | 17 | 15 | 0 | 0 | 0 | 9 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 13 | 22 | 24 | 20 | 33 | 8 | 0 | 30 | 0 | 120 | 0 | 8 | 0 | 0 | 0 | 0 |  | 12 | 0 | 0 | 22 | 0 | 6 | 0 | 40 | 0 | 0 | 0 | 290 | 0 | 183 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 0 | 8 | 21 | 9 | 30 | 21 | 96 | 108 | 0 | 20 | 0 | 30 | 31 | 53 | 47 | 112 | 0 | 65 | 86 | 0 | 0 | 19 | 27 | 10 | 0 | 16 | 8 | 0 | 98 | 0 | 0 | 48 | 0 | 77 | 0 | 25 | 17 | 73 | 400 | 47 | 31 | 37 | 0 | 51 | 17 | 72 | 17 | 90 | 25 | 400 | 17 | 0 | 162 | 68 | 0 | 17 | 0 | 0 | 17 | 308 | 0 | 0 |  | 872 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 8 | 0 | 21 | 0 | 8 | 0 | 0 | 158 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 316 | 17 | 0 | 50 | 0 | 34 | 0 | 0 | 55 | 622 | 220 | 0 | 0 | 0 | 0 | 98 | 0 | 0 | 0 | 0 | 309 | 0 | 0 |  | 5116 | 3238 | 8354 | 3131 | 872 | 1573 | 0 | 1563 | 1089 | 30 | 0 | 0 | 96 | 0 | 0 | 86.62
22:00 | 0 | 0 | 240 | 0 | 0 | 74 | 0 | 333 | 259 |  | 0 | 225 | 0 | 16 | 17 | 15 | 0 | 0 | 0 | 9 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 35 | 13 | 22 | 24 | 17 | 33 | 0 | 0 | 46 | 0 | 120 | 0 | 8 | 0 | 0 | 0 | 0 |  | 12 | 0 | 0 | 22 | 0 | 4 | 0 | 42 | 0 | 0 | 0 | 290 | 0 | 183 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 0 | 8 | 21 | 9 | 33 | 21 | 92 | 108 | 0 | 22 | 0 | 30 | 31 | 53 | 47 | 112 | 0 | 40 | 50 | 0 | 0 | 19 | 27 | 10 | 0 | 16 | 8 | 0 | 70 | 0 | 0 | 48 | 0 | 149 | 0 | 25 | 17 | 75 | 375 | 47 | 50 | 51 | 0 | 51 | 17 | 72 | 3 | 108 | 25 | 400 | 17 | 0 | 92 | 68 | 0 | 17 | 0 | 0 | 17 | 338 | 0 | 0 |  | 870 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 8 | 0 | 21 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 171 | 0 | 0 | 0 | 0 | 0 | 321 | 17 | 0 | 50 | 0 | 34 | 0 | 0 | 55 | 622 | 220 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 309 | 0 | 0 |  | 5067 | 3157 | 8224 | 3100 | 870 | 1549 | 0 | 1476 | 1091 | 46 | 0 | 0 | 92 | 0 | 0 | 86.61
23:00 | 0 | 0 | 242 | 0 | 0 | 73 | 0 | 333 | 274 |  | 0 | 225 | 0 | 0 | 2 | 15 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 35 | 13 | 22 | 24 | 17 | 33 | 0 | 0 | 46 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12 | 0 | 0 | 22 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 290 | 0 | 183 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 0 | 8 | 21 | 9 | 33 | 21 | 96 | 108 | 0 | 20 | 0 | 30 | 31 | 53 | 47 | 112 | 0 | 40 | 50 | 0 | 0 | 20 | 27 | 10 | 0 | 16 | 8 | 0 | 45 | 0 | 0 | 48 | 0 | 103 | 0 | 25 | 17 | 25 | 375 | 47 | 17 | 17 | 0 | 51 | 17 | 72 | 0 | 65 | 25 | 400 | 0 | 0 | 17 | 68 | 0 | 17 | 0 | 0 | 17 | 338 | 0 | 0 |  | 776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 21 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 177 | 0 | 0 | 0 | 0 | 0 | 332 | 17 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 560 | 220 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 309 | 0 | 0 |  | 4708 | 2914 | 7622 | 3119 | 776 | 1573 | 0 | 983 | 1029 | 46 | 0 | 0 | 96 | 0 | 0 | 86.61
24:00 | 0 | 0 | 241 | 0 | 0 | 73 | 0 | 337 | 282 |  | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 35 | 13 | 22 | 23 | 17 | 33 | 0 | 0 | 46 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12 | 0 | 0 | 10 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 290 | 0 | 183 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 9 | 33 | 21 | 82 | 108 | 0 | 19 | 0 | 30 | 31 | 53 | 47 | 112 | 0 | 40 | 50 | 0 | 0 | 20 | 27 | 10 | 0 | 16 | 8 | 0 | 0 | 0 | 0 | 24 | 0 | 11 | 0 | 25 | 17 | 0 | 375 | 8 | 0 | 0 | 0 | 51 | 17 | 34 | 0 | 9 | 25 | 400 | 0 | 0 | 17 | 68 | 0 | 17 | 0 | 0 | 17 | 338 | 0 | 0 |  | 729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 0 | 0 | 161 | 0 | 0 | 0 | 0 | 177 | 0 | 0 | 0 | 0 | 0 | 327 | 17 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 500 | 219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 |  | 4308 | 2707 | 7015 | 3120 | 729 | 1576 | 0 | 491 | 971 | 46 | 0 | 0 | 82 | 0 | 0 | 86.61
KWH | 0 | 0 | 4224000 | 0 | 0 | 1501272 | 0 | 8787970 | 6810000 |  | 0 | 5906350 | 0 | 235200 | 528759 | 131280 | 0 | 0 | 0 | 120000 | 302112 | 317280 | 0 | 0 | 0 | 0 | 387720 | 633369 | 610703 | 369936 | 582000 | 467100 | 566700 | 759000 | 208800 | 0 | 1048320 | 0 | 3000000 | 0 | 362953 | 0 | 0 | 0 | 0 |  | 288000 | 247296 | 92017 | 516960 | 31680 | 268320 | 0 | 828000 | 0 | 0 | 0 | 7555000 | 0 | 4599500 | 200727 | 0 | 148680 | 144480 | 0 | 1126140 | 0 | 0 | 179563 | 503064 | 243180 | 670100 | 379660 | 1977600 | 1653120 | 0 | 247680 | 3600 | 716000 | 589320 | 1104600 | 906552 | 2768154 | 0 | 1229284 | 898560 | 0 | 0 | 458000 | 582320 | 249660 | 0 | 389760 | 192432 | 88512 | 1021200 | 234775 | 0 | 1130400 | 105000 | 992160 | 115425 | 603840 | 432480 | 575418 | 8862000 | 747600 | 756000 | 482581 | 18723 | 1944545 | 449888 | 1688611 | 705660 | 798000 | 605760 | 9146400 | 320640 | 122830 | 1087200 | 1799018 | 0 | 435600 | 109049 | 0 | 410040 | 7796000 | 0 | 0 |  | 16525090 | 0 | 0 | 0 | 1053120 | 0 | 0 | 0 | 47040 | 112128 | 70125 | 3289186 | 452900 | 0 | 0 | 0 | 0 | 48350 | 10931 | 147192 | 0 | 511794 | 120538 | 288955 | 84999 | 469680 | 0 | 174780 | 0 | 0 | 3890300 | 0 | 0 | 0 | 0 | 3929245 | 0 | 0 | 0 | 0 | 0 | 7640181 | 201120 | 0 | 812736 | 0 | 642892 | 0 | 28759 | 740160 | 11714700 | 3570436 | 0 | 0 | 14880 | 379440 | 1553664 | 0 | 0 | 0 | 134513 | 7454600 | 0 | 651600 |  | 113435188 | 66766034 | 180201222 | 71529097 | 16525090 | 35160012 | 428287 | 27666626 | 23059600 | 1048320 | 0 | 1227771 | 1977600 | 1578819 | 0
Fuel Cost | 0 | 0 | 6167040 | 0 | 0 | 1996691.76 | 0 | 9227368.5 | 7354800 |  | 0 | 6437921.5 | 0 | 2629536 | 7006056.75 | 1739460 | 0 | 0 | 0 | 1754400 | 4250715.84 | 5143108.8 | 0 | 0 | 0 | 0 | 4931798.4 | 8550481.5 | 8189527.23 | 277452 | 436500 | 0 | 0 | 0 | 3551688 | 0 | 283046.4 | 0 | 5670000 | 0 | 5934281.55 | 0 | 0 | 0 | 0 |  | 3758400 | 4124897.28 | 1566129.34 | 6984129.6 | 401702.4 | 3104462.4 | 0 | 2757240 | 0 | 0 | 0 | 8386050 | 0 | 5335420 | 258937.83 | 0 | 168008.4 | 215275.2 | 0 | 1880653.8 | 0 | 0 | 2415122.35 | 689197.68 | 182385 | 1172675 | 284745 | 14199168 | 1801900.8 | 0 | 336844.8 | 57384 | 980920 | 777902.4 | 1922004 | 1568334.96 | 3183377.1 | 0 | 2384810.96 | 2048716.8 | 0 | 0 | 984700 | 867656.8 | 494326.8 | 0 | 292320 | 146248.32 | 1855211.52 | 13939380 | 4920884 | 0 | 15237792 | 2170350 | 13741416 | 1349318.25 | 6231628.8 | 5907676.8 | 7635796.86 | 8153040 | 9090816 | 10931760 | 6104649.65 | 0 | 22828958.3 | 4899280.32 | 17949934.93 | 9575806.2 | 10286220 | 7135852.8 | 8414688 | 4152288 | 1774893.5 | 13796568 | 20472824.84 | 0 | 5688936 | 1303135.55 | 0 | 5400226.8 | 0 | 0 | 0 |  | 49575270 | 0 | 0 | 0 | 10962979.2 | 0 | 0 | 0 | 847190.4 | 2018304 | 1007696.25 | 3683888.32 | 878626 | 0 | 0 | 0 | 0 | 810829.5 | 191183.19 | 2302082.88 | 0 | 8475308.64 | 2038297.58 | 3938456.65 | 1433933.13 | 972237.6 | 0 | 132308.46 | 0 | 0 | 20579687 | 0 | 0 | 0 | 0 | 5029433.6 | 0 | 0 | 0 | 0 | 0 | 7563779.19 | 2703052.8 | 0 | 9614666.88 | 0 | 8164728.4 | 0 | 317786.95 | 8985542.4 | 105549447 | 3641844.72 | 0 | 0 | 168292.8 | 4450831.2 | 23817669.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 408213254.37 | 289855353.86 | 698068608.23 | 71115847.24 | 49575270 | 44042424.06 | 8946445.52 | 353879674.66 | 126129134 | 283046.4 | 0 | 20475956.1 | 14199168 | 9421642.25 | 0
Yesterday Day Peak | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 395 | 304 |  | 0 | 225 | 0 | 17 | 34 | 0 | 0 | 0 | 0 | 9 | 16 | 32 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 13 | 22 | 16 | 25 | 31 | 20 | 0 | 46 | 0 | 120 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 24 | 0 | 22 | 0 | 20 | 0 | 32 | 0 | 0 | 0 | 325 | 0 | 203 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 0 | 8 | 21 | 10 | 22 | 15 | 84 | 34 | 0 | 14 | 1 | 30 | 31 | 51 | 22 | 112 | 0 | 63 | 30 | 0 | 0 | 19 | 27 | 10 | 0 | 16 | 8 | 0 | 32 | 150 | 0 | 48 | 20 | 35 | 18 | 25 | 17 | 6 | 410 | 28 | 68 | 17 | 4 | 51 | 17 | 72 | 81 | 27 | 25 | 400 | 17 | 15 | 17 | 68 | 0 | 17 | 24 | 0 | 17 | 330 | 0 | 0 |  | 682 | 0 | 0 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 112 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 16 | 8 | 0 | 18 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 166 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 35 | 0 | 27 | 0 | 4 | 35 | 480 | 120 | 0 | 0 | 2 | 61 | 115 | 0 | 0 | 0 | 24 | 309 | 0 | 136 |  | 7880 | DayPeak
Yesterday Evening Peak | 0 | 0 | 240 | 0 | 0 | 70 | 0 | 344 | 263 | 0 | 0 | 225 | 0 | 17 | 17 | 15 | 0 | 0 | 0 | 9 | 16 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 13 | 22 | 24 | 20 | 33 | 8 | 0 | 30 | 0 | 140 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 22 | 0 | 6 | 0 | 30 | 0 | 0 | 0 | 290 | 0 | 190 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 0 | 8 | 21 | 10 | 25 | 21 | 100 | 107 | 0 | 20 | 0 | 30 | 31 | 53 | 46 | 112 | 0 | 64 | 86 | 0 | 0 | 19 | 26 | 10 | 0 | 16 | 8 | 0 | 98 | 0 | 0 | 48 | 0 | 40 | 0 | 25 | 17 | 75 | 400 | 47 | 17 | 17 | 0 | 294 | 17 | 72 | 17 | 107 | 25 | 400 | 17 | 0 | 162 | 68 | 0 | 17 | 0 | 0 | 17 | 348 | 0 | 0 |  | 871 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 8 | 0 | 8 | 0 | 21 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 313 | 17 | 0 | 50 | 0 | 34 | 0 | 0 | 55 | 610 | 219 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | 0 | 309 | 0 | 0 |  | 8671 | EvPeak
Forecast for Evening | 0 | 0 | 180 | 0 | 0 | 70 | 0 | 340 | 310 | 0 | 0 | 225 | 0 | 17 | 34 | 25 | 0 | 0 | 0 | 9 | 16 | 32 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 22 | 33 | 30 | 50 | 0 | 46 | 0 | 120 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 12 | 32 | 51 | 22 | 12 | 40 | 0 | 30 | 0 | 0 | 0 | 320 | 0 | 200 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 30 | 8 | 21 | 10 | 33 | 21 | 152 | 100 | 0 | 22 | 0 | 30 | 30 | 48 | 44 | 112 | 0 | 64 | 86 | 0 | 0 | 19 | 27 | 10 | 0 | 16 | 8 | 100 | 95 | 150 | 50 | 48 | 50 | 149 | 0 | 25 | 17 | 75 | 400 | 47 | 105 | 51 | 0 | 290 | 17 | 72 | 17 | 108 | 25 | 400 | 17 | 0 | 162 | 68 | 0 | 17 |  | 0 | 17 | 330 |  |  |  | 935 | 0 | 0 | 0 | 99 | 0 | 0 | 0 | 40 | 70 | 40 | 180 | 24 |  | 0 | 0 | 0 | 34 | 25 | 67 | 0 | 42 | 40 | 8 | 32 | 20 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 0 |  | 160 | 0 | 0 | 50 | 0 | 0 | 320 | 18 | 100 | 50 | 0 | 34 | 0 | 0 | 55 | 622 | 220 |  | 0 |  |  | 115 | 0 |  | 0 |  | 300 | 0
Forecast for Day | 0 | 0 | 180 | 0 | 0 | 70 | 0 | 370 | 330 | 0 | 0 | 225 | 0 | 17 | 34 |  | 0 | 0 | 0 | 9 | 16 | 32 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 25 | 22 | 33 | 30 | 50 | 0 | 46 | 0 | 120 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 12 | 24 | 0 | 22 | 0 | 20 | 0 | 20 | 0 | 0 | 0 | 310 | 0 | 200 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 25 | 8 | 21 | 10 | 33 | 21 | 135 | 70 | 0 | 22 | 1.6 | 30 | 20 | 48 | 44 | 112 | 0 | 62 | 50 | 0 | 0 | 19 | 27 | 10 | 0 | 16 | 8 | 0 | 32 | 0 | 0 | 48 | 0 | 35 | 20 | 25 | 17 | 6 | 350 | 28 | 105 | 17 | 5 | 51 | 17 | 72 | 17 | 108 | 25 | 400 | 17 | 50 | 17 | 68 | 0 | 17 | 30 | 0 | 17 | 300 |  |  |  | 743 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 40 | 180 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 8 | 0 | 20 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 350 | 18 | 0 | 35 | 0 | 34 | 0 | 8 | 35 | 500 | 160 |  | 0 | 6 | 100 | 115 | 0 |  | 0 | 30 | 300 | 0 | [5 empty] | g | h | o | c | h | t | s
Generation at 08:00(Today) | 0 | 0 | 180 | 0 | 0 | 68 | 0 | 402 | 358 | 0 | 0 | 225 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 13 | 22 | 24 | 17 | 33 | 0 | 0 | 46 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 22 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 335 | 0 | 209 | 8 | 0 | 5 | 5 | 0 | 51 | 0 | 0 | 1 | 21 | 9 | 33 | 21 | 84 | 108 | 0 | 19 | 0 | 30 | 0 | 33 | 30 | 112 | 0 | 62 | 70 | 0 | 0 | 19 | 27 | 10 | 0 | 8 | 8 | 0 | 32 | 0 | 0 | 46 | 0 | 20 | 4 | 25 | 17 | 2 | 350 | 20 | 12 | 9 | 0 | 51 | 17 | 43 | 0 | 0 | 25 | 400 | 17 | 2 | 17 | 68 | 0 | 17 | 3 | 0 | 9 | 300 | 0 | 0 | 0 | 564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 8 | 0 | 21 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 204 | 0 | 0 | 0 | 0 | 0 | 419 | 0 | 0 | 35 | 0 | 33 | 0 | 0 | 25 | 330 | 200 | 0 | 0 | 0 | 13 | 26 | 0 | 0 | 0 | 1 | 308 | 0 |  | 0 |  |  |  | 106.6891 | 16.5251 | 29.3227 | 23.0596 | 1.0483 | 1.9776 | 1.5788
180.2012
| Minimum Generation |  | 6199 | 5:00
| Highest Generation |  | 8671 | 19:30
| Day Peak Generation |  | 7880 | 12:00
| Evening Peak Generation |  | 8671 | 19:30
| HVDC Max Flow |  | 872 | 21:00
| HVDC EvPeak Flow |  | 871 | 19:30
| Load factor L.F |  | 86.59% | [161 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2022-12-31
Till now the maximum generation is : - |  |  |  | 14782 | 21:00 | Hrs on | 2022-04-16
The Summary of Yesterday's |  |  | 2022-12-30 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 7880 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 5746
Evening Peak Generation : |  |  | 8671 | MW Hour : | 19:30 | Available Max Generation : |  | 10244
E.P. Demand (at gen end) : |  |  | 8671 | MW Hour : | 19:30 | Max Demand (Evening) : |  | 9500
Maximum Generation : |  |  | 8671 | MW Hour : | 19:30 | Reserve(Generation end) |  | 744
Total Gen. (MKWH) : |  |  | 180.2012 | System Load Factor : | 86.59% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | -40 | MW at | 7:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2022-12-31
Actual : |  | 86.59 | Ft.(MSL) , | Rule curve : | 103.1 | Ft.( MSL )
Gas Consumed : |  | Total = | 821.19 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 115158271.3
: |  |  | Coal : | 126129134 | Oil : | 383302076.28 | Total : | 624589481.58
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 0 | 0:00 | 3137.9088 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 888.915 |  |  | 0 | 0%
Khulna Area |  | 0 | 0:00 | 1173.294 |  |  | 0 | 0%
Rajshahi Area |  | 0 | 0:00 | 1041.0039 |  |  | 0 | 0%
Cumilla Area |  | 0 | 0:00 | 886.1775 |  |  | 0 | 0%
Mymensingh Area |  | 0 | 0:00 | 732.1151 |  |  | 0 | 0%
Sylhet Area |  | 0 | 0:00 | 327.2236 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 266.7445 |  |  | 0 | 0%
Rangpur Area |  | 0 | 0:00 | 578.0526 |  |  | 0 | 0%
Total |  | 0 |  | 9031.435 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1, 2
2) Ghorasal-3, 7
3) Ashuganj-5
4) Baghabari-70,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
7) Shajibazar 330 MW
8) Sirajganj-1
9) Bibiana-II 341 MW CCPP (Summit)
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
08:11 | 08:36 | Joydebpur 132/33kV S/S GT-4 LT Tripped showing relay relays Due to 33kv BOF Feeder
E/F and O/C signal show but not trip.
08:11 | 08:36 | Joydebpur 132/33kV S/S GT-4 HT Tripped showing relay relays Due to Causes: 33kv BOF Feeder |  |  |  |  | 20 MW load interrup.
E/F and O/C but not trip.
08:23 |  | Gopalganj (regular) - Rampal 400 kv line-2 was closed at Gopalganj (reg) end.
08:26 |  | Gopalganj400 kv-Rampal CKT-1 Close from Gopalganj end.
08:39 |  | Cumilla(N) 230/132/33kV S/S 230KV T-01 LT Scheduled S/D Due to Annual
08:39 |  | Cumilla(N) 230/132/33kV S/S 230KV T-01 HT Scheduled S/D Due o Annual Maintenance work.
08:46 | 12:36 | Bibiana 400/230kV S/S ICT-01 HT Scheduled S/D Due to Maintenance.
08:46 | 12:36 | Bibiana 400/230kV S/S ICT-01 LT Scheduled S/D Due to Maintenance.
09:10 |  | Meghnaghat 230/132kV S/S Meghnaghat-Aminbazar-02 Scheduled S/D Due to As per request of NLDC.
09:11 |  | Maniknagar-Narinda 132kV Ckt-1 Forced S/D from Maniknagar 132/33kV end Due to Equipment maintenance,
Oil leakage repair,Cable replacement,Relay test & Line parameter measurement work.
09:12 |  | Aminbazar-Meghnaghat 230kV Ckt-2 Project Work S/D from Aminbazar 400/230/132kV end Due to Tower
dismantling work under this transmission line.
09:25 |  | Siddhirganj 132/33kV S/S T-2 LT Scheduled S/D Due to DPDC Maintenance work.
09:26 |  | Siddhirganj 132/33kV S/S T-2 HT Scheduled S/D Due to DPDC Maintenance work.
09:43 |  | Payra 400/132/33kV S/S 132/33 kV Transformer-03 LT Project Work S/D Due to Outgoing feeder connection. |  |  |  |  | 0.4 MW load interrup.
09:44 |  | Payra 400/132/33kV S/S 132/33 kV Transformer-04 LT Project Work S/D Due to Outgoing feeder connection. |  |  |  |  | 0.5 MW load interrup.
09:45 |  | Payra 400/132/33kV S/S 132/33 kV Transformer-03 HT Project Work S/D Due to Outgoing feeder connection.
09:45 |  | Payra 400/132/33kV S/S 132/33 kV Transformer-04 HT Project Work S/D Due to Outgoing feeder connection.
09:52 | 12:02 | Jhenaidah-Khulna 230kV Ckt-2 Project Work S/D from Jhenaidah 230/132kV end Due to NLDC signal testing
and from Khulna(S) 230/132kV end Due to SCADA Operation Work at Jhenaidah S/S
| 10:04 | Bhola CCPP GT1 sync.
10:12 |  | Ghorashal unit-4 tripped inlet gas pressure high |  |  |  |  | 200 MW Generation interrup.
| 10:30 | Godda (Adani Power) - Bogura (bypassed Rohonpur) 400 kv line-1 was switched on from Godda.
| 10:33 | Bhola Natun Biddut BD LTD GT2 sync.
| 10:35 | Godda (Adani Power) - Bogura (bypassed Rohonpur) 400 kv line-1 was switched off from Adani Power
12:26 |  | Jhenaidah 230/132kV S/S 230 kV Bus Project Work S/D Due to BUS 2 shutdown due to NLDC Signal Testing.
12:29 |  | Jhenaidah 230/132kV S/S LVAC-2 Project Work S/D.
12:31 |  | Jhenaidah 230/132kV S/S Transformer- 2 LT Project Work S/D.
12:32 |  | Jhenaidah 230/132kV S/S Transformer- 2 HT Project Work S/D Due to NLDC Signal Testing.
12:35 |  | Gopalganj 132/33kV S/S T2 LT Scheduled S/D Due to Installation of D/S Aux.T-2 |  |  |  |  | 5 MW load interrup.
12:36 |  | Gopalganj 132/33kV S/S T2 HT Scheduled S/D.
| 12:51 | Ghorasal unit-4 sync.
| 14:07 | Payra 400/132/33kV S/S 132/33 kV Transformer-03 HT is restored.
| 14:08 | Payra 400/132/33kV S/S 132/33 kV Transformer-03 LT is restored.
| 14:08 | Payra 400/132/33kV S/S 132/33 kV Transformer-04 HT is restored.
| 14:08 | Payra 400/132/33kV S/S 132/33 kV Transformer-04 LT is restored.
| 14:26 | Siddhirganj 132/33kV S/S T-2 HT is restored.
| 14:27 | Siddhirganj 132/33kV S/S T-2 LT is restored.
| 14:39 | Jhenaidah 230/132kV S/S 230 kV Bus is restored.
| 14:43 | Jhenaidah 230/132kV S/S Transformer- 2 HT is restored.
| 14:44 | Jhenaidah 230/132kV S/S Transformer- 2 LT is restored.
| 15:11 | Jhenaidah 230/132kV S/S LVAC-2 is restored.
| 16:18 | Bogura(New)-Naogaon 132 kV Ckt-1 is restored.
16:20 |  | Bogura (old) - Naogaon 132 KV Line-2. (132 KV C.B open Bogra (old) 132/33 KV S/S.
| 16:38 | Gopalganj 132/33kV S/S T2 HT is restored.
| 16:39 | Gopalganj 132/33kV S/S T2 LT is restored.
| 16:40 | Bakulia 132/33kV S/S T-2 (412T) HT is restored.
| 16:43 | Maniknagar-Narinda 132kV Ckt-1 is restored.
| 16:57 | Bakulia 132/33kV S/S T-2 (412T) LT is restored.
| 18:41 | Cumilla(N) 230/132/33kV S/S 230KV T-01 HT is restored.
| 18:41 | Cumilla(N) 230/132/33kV S/S 230KV T-01 LT is restored.
| 21:55 | Meghnaghat 230/132kV S/S Meghnaghat-Aminbazar-02 is restored.
22:00 |  | Duty Received condition : Load Shed free, normal.
| 22:05 | Aminbazar-Meghnaghat 230kV Ckt-2 is restored.
| 22:05 | Aminbazar-Meghnaghat 230kV Ckt-2 is restored.
06:53 |  | Bogura(New)-Naogaon 132 kV Ckt-1 Project Work S/D from aogaon 132/33kV end Due to project works of
Bogura 230 kV s/s. and from Bogura 230/132kVend.
07:17 |  | Baroaulia 132/33kV S/S T2(415T) LT Scheduled S/D Due to Annual Maintenance. |  |  |  |  | 15 MW load interrup.
07:20 |  | Baroaulia 132/33kV S/S T2(415T) HT Scheduled S/D Due to Annual Maintenance.
07:24 |  | Bakulia 132/33kV S/S T-3 (422T) LT Scheduled S/D Due to Annual Maintenance. |  |  |  |  | 10 MW load interrup.
07:25 |  | Bakulia 132/33kV S/S T-3 (422T) HT Scheduled S/D Due to Annual Maintenance.
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2022-12-30 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 240 | 4224000
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Machine problem
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 70 | 1501272 | Machine problem
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 344 | 8787970 | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 263 | 6810000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 5906350 | GT-2 S/D due to Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 17 | 235200 | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 17 | 528759 | Fuel shortage
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 15 | 131280 | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 13 | 369936
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 9 | 120000 | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 16 | 302112 | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 387720
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 0 | 317280 | Fuel shortage
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 633369
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 610703
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 46 | 1049100 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 20 | 566700 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 759000 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 8 | 208800 | High voltage
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 98 | 1021200 | Fuel shortage
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 234775 | Fuel conservation
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 0 | 0 | Fuel shortage
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 105000 | Fuel shortage
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 40 | 992160 | Fuel shortage
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 17 | 756000 | High voltage
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 17 | 320640 | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 1087200
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 109049
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 410040 | Fuel shortage
| Dhaka area Total |  |  |  | 5847 | 1851 | 38485615
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 140 | 3000000 | Machine problem
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 8 | 362953 | Low Demand
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 115425
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 6 | 268320 | High voltage
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 30 | 1048320 | Low water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Gas shortage
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 17 | 482581 | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 247296 | Low Demand
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 92017 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 22 | 516960 | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 25 | 603840 | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 0 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 30 | 828000
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 31680 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 18723
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 294 | 1944545
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 17 | 449888 | Engine problem
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 72 | 1688611 | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 25 | 605760 | High voltage
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 68 | 1799018 | Engine problem
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Chattogram area Total |  |  |  | 2382 | 754 | 14103937
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 190 | 4599500 | FGMO
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 290 | 7555000 | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | Gas shortage
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 348 | 7796000 | Gas shortage
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 5 | 148680 | Gas shortage
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 5 | 144480 | Gas shortage
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 200727 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1126140
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 75 | 575418 | Fuel shortage
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Machine problem
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Machine problem
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 17 | 432480 | Fuel shortage
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 503064
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 10 | 243180
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 100 | 1977600
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 25 | 670100 | Engine problem
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 8 | 179563 | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 21 | 379660 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 88512 | Fuel conservation
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 17 | 705660 | Fuel shortage
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 107 | 798000 | Engine problem
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 435600 | Engine problem
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 0 | 0 | Fuel shortage
| Cumilla Area Total |  |  |  | 3285 | 1315 | 28559364
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 107 | 1653120 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 247680 | Gas shortage
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 3600
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 48 | 1130400 | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 47 | 747600 | Fuel shortage
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 122830
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 288000
| Mymensingh Area Total |  |  |  | 614 | 234 | 4193230
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 30 | 716000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 31 | 589320 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 112 | 2768154 | ST under maint
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 1104600
| Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 46 | 906552
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 8 | 192432 | Engine problem
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 64 | 1229284
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 86 | 898560
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 0 | 0 | Under maint.
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 19 | 458000
| Sylhet 50MW PP (EPL) |  | NENP | 27*2 | 50 | 26 | 582320 | Gas shortage
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 389760 | Gas shortage
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 0 | 0 | Under maint.
104 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 400 | 8862000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 249660
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 400 | 9146400
| Sylhet Area Total |  |  |  | 2477 | 1301 | 28093042
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Fuel shortage
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 871 | 16525090
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 32 | 1053120 | Fuel shortage
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 47040 | Line O/L
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel conservation
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 112128 | Line O/L
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Under maint.
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 0 | 70125 | Fuel shortage
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Fuel conservation
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 201120 | Fuel shortage
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Fuel shortage
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 379440
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 0 | 0 | 0 | On test.
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 0 | 0 | 0 | 0 | Demi water shortage
| Khulna Area Total |  |  |  | 2384 | 920 | 18388063
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Line O/L
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 23 | 452900 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 182 | 3289186
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 610 | 11714700 | & Unit-2 Under maint.
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 219 | 3570436
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Line O/L
| Barisal 307 MW |  | BCPCL | 0 | 0 | 309 | 7454600 | On test.
| Barisal Area Total |  |  |  | 1958 | 1343 | 26481822
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 48350 | Low Demand
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 10931 | Fuel shortage
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contract Expired
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 8 | 511794 | Low Demand
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 120538 | Low Demand
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 170 | 3929245
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 313 | 7640181 | Gas shortage
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 84999 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 21 | 469680
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 174780 | Engine problem
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 8 | 288955 | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 51 | 147192 | Fuel shortage
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Fuel conservation
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 50 | 812736 | Fuel shortage
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 55 | 740160 | Fuel shortage
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 14880
| Adani Power Jharkhanda Ltd |  | Import | 0 | 0 | 0 | 0 | On test.
| Rajshahi Area Total |  |  |  | 2129 | 684 | 14994421
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 160 | 3890300 | Machine problem
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 34 | 642892 | Fuel shortage
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 28759
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 75 | 1553664 | Low Demand
| Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 134513
| Teesta Solar Limited |  | BPCL | 16*12.5 | 0 | 0 | 651600
| Rangpur Area Total |  |  |  | 750 | 269 | 6901728
| Total |  |  |  | 21826 | 8671 | 180201222
| Eastern Grid Total |  |  |  | 14605 | 5455 | 113435188
| Western Grid Total |  |  |  | 7221 | 3216 | 66766034
| National Grid Total |  |  |  | 21826 | 8671 | 180201222
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2022-12-30
| (a) ENTIRE EASTERN GRID : |  | 5580.82 | MW | (b) ENTIRE WESTERN GRID : |  | 2732.88 | MW
| i) Dhaka area |  | 2852.92 | MW | i) Khulna area |  | 1032 | MW
| ii) Chittagong area |  | 921.9 | MW | ii) Rajshahi area |  | 862.4 | MW
| iii) Comilla area |  | 749 | MW | iii) Barisal area |  | 257.48 | MW
| iv) Mymensingh area |  | 735 | MW | iv) Rangpur area |  | 581 | MW
| v) Sylhet area |  | 322 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 8313.7 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | Chhatak | 17 | 18:30 | Kamrangirchar | 55 | 12:00 | Natore | 82 | 18:30 | Shitalakhya | 70 | 00:00
2 | AKSML | 102 | 02:00 | Chowmuhani | 126 | 20:00 | Kaptai | 3.5 | 18:00 | Nawabganj | 27.2 | 13:00 | Sholosohor | 17 | 12:00
3 | Aftabnagar | 22 | 13:00 | Chuadanga | 64 | 18:00 | Kazla | 70 | 13:00 | Netrakona | 91 | 18:00 | Shyampur | 152 | 07:00
4 | Agargaon | 47 | 13:00 | Coxsbazar | 83 | 18:00 | Keranigonj | 40 | 14:00 | New | 42 | 12:00 | Siddhirganj | 66 | 00:00
5 | Agrabad | 38 | 18:30 | Cumilla(N) | 89 | 18:30 | Khagrachori | 22 | 13:00 | Niamatpur | 52 | 18:30 | Sirajganj | 57 | 18:30
6 | Amnura | 33 | 12:00 | Cumilla(S) | 104 | 13:00 | Khulna | 67 | 13:00 | Noapara | 29 | 18:30 | Sonargaon | 79 | 00:00
7 | Ashuganj | 38 | 00:00 | Daudkandi | 80 | 21:00 | Khulshi | 124 | 01:00 | PHP | 2 | 10:00 | Sreemongol | 32 | 13:00
8 | BIPTC | N/A | N/A | Dhaka | 14 | 12:00 | Kishoreganj | 92 | 19:00 | Pabna | 63 | 18:00 | Srinagar | 28.13 | 20:00
9 | BSRM | 158 | 07:00 | Dhamrai | 58 | 00:00 | Kodda | 163 | 10:00 | Palashbari | 77 | 20:00 | Sunamganj | 31 | 19:00
10 | Bagerhat | 70 | 18:30 | Dhanmondi | 72 | 13:00 | Kulaura | 28 | 18:00 | Panchagarh | 53 | 18:30 | Sylhet | 85 | 13:00
11 | Bakulia | 53 | 18:00 | Dohazari | 64 | 19:30 | Kurigram | 57 | 18:00 | Patuakhali | 78 | 21:00 | TK | 12.6 | 20:00
12 | Banani | 21 | 18:00 | Faridpur | 88 | 18:30 | Kushtia | 88 | 18:30 | Payra | 0.5 | 18:00 | Tangail | 131 | 19:30
13 | Bangabhaban | 3 | 02:00 | Fatullah | 44 | 00:00 | Lalbag | 53 | 00:00 | Postogola | 27 | 12:00 | Thakurgaon | 62 | 18:30
14 | Barapukuria | 39 | 18:00 | Fenchuganj | 26 | 18:00 | Lalmonirhat | 20 | 18:00 | Purbachal | 11 | 12:00 | Tongi | 79 | 12:00
15 | Barguna | 12 | 18:30 | Feni | 67 | 20:00 | Madanganj | 30 | 18:30 | Purbasadipur | 95 | 13:00 | Ullon | 30 | 12:00
16 | Barishal | 66 | 13:00 | GPH | 82 | 07:00 | Madaripur | 61 | 20:00 | Rahanpur_I | 8.4 | 18:30 | Uttara | 48 | 13:00
17 | Barishal-230 | 48 | 21:00 | Ghorashal | 49 | 01:00 | Madartek | 56 | 13:00 | Rahim | 26 | 00:00 | UttaraNew | 13 | 00:00
18 | Baroaulia | 42 | 09:00 | Goalpara | 19 | 13:00 | Madunaghat | 33 | 20:00 | Rajbari | 42 | 18:00 | Zigatola | 30 | 13:00
19 | Baroirhat | 36 | 13:00 | Gollamari | 34 | 18:30 | Magura | 40 | 18:00 | Rajendrapur | 86 | 13:00
20 | Bashundhara | 100 | 13:00 | Gopalganj | 74 | 18:00 | Mahasthangarh | 40 | 18:00 | Rajshahi | 89 | 21:00
21 | BashundharaCement | 0 | 00:00 | Gulshan | 52 | 13:00 | Manikganj | 70 | 20:00 | Rajshahi-230 | 20 | 13:00
22 | Beanibazar | 38 | 20:00 | Halishahar | 49 | 18:00 | Maniknagar | 39 | 13:00 | Ramganj | 70 | 14:00
23 | Benapole | 40 | 07:00 | HaripurSBU | 116 | 00:00 | Matarbari | 24 | 20:00 | Rampur | 15 | 00:00
24 | Bhaluka | 92 | 19:00 | Hasnabad | 58 | 11:00 | Matuail | 44 | 00:00 | Rangamati | 35 | 07:00
25 | Bhandaria | 32 | 21:00 | Hathazari | 40 | 12:00 | Millgate | 47 | 12:00 | Rangpur | 104 | 13:00
26 | Bhangura | 20 | 18:30 | Ishurdi | 44 | 19:00 | Mirpur | 81 | 12:00 | Ruppur | 3 | 09:00
27 | Bheramara(GK) | 36 | 18:30 | Jaldhaka | 45 | 18:00 | Mirsorai | 2 | 18:00 | SSM | 12 | 05:00
28 | Bhulta | 187 | 01:00 | Jamalpur | 100 | 19:30 | Mithapukur | 22 | 18:00 | Saidpur | 68 | 18:30
29 | Bog-Sherpur | 44 | 18:30 | Jashore | 89 | 13:00 | Modern | 0 | 00:00 | Satkhira | 75 | 18:30
30 | Bogura | 102 | 18:30 | Jhenaidah | 86 | 18:00 | Mogbazar | 71 | 13:00 | Satmasjid | 69 | 13:00
31 | Borhanuddin | 27 | 21:00 | Joydebpur | 90 | 12:00 | Mongla | 20 | 00:00 | Savar | 110 | 12:00
32 | Brahmanbaria | 96 | 18:30 | Joypurhat | 36 | 18:30 | Motijheel | 20 | 13:00 | Shahjadpur | 70 | 19:00
33 | Cantonment | 82 | 13:00 | Juldah | 15 | 00:00 | Munshiganj | 57 | 13:00 | Shahjibazar | 76 | 21:00
34 | Chandpur | 39 | 19:00 | KSRM | 42 | 18:30 | Mymensingh | 148 | 18:30 | Shahmirpur | 19 | 18:00
35 | Chandraghona | 22 | 18:00 | Kabirpur | 159 | 12:00 | Naogaon | 78 | 18:30 | Shariatpur | 46 | 21:00
36 | Chapai | 45 | 12:00 | Kachua | 42 | 18:30 | Narail | 37 | 18:30 | Sherpur | 88 | 18:30
37 | Charsaidpur | 49.5 | 12:00 | Kallyanpur | 60 | 13:00 | Narinda | 31.5 | 13:00 | Shikalbaha | 19 | 00:00
38 | Chauddagram | 24 | 13:00 | Kalurghat | 14 | 00:00 | Narshingdi | 125 | 20:00 | Shikalbaha-230 | N/A | N/A
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2022-12-30 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 418 | 03:00 | 210 | 18:30 | Gopalganj_I | N/A | N/A | N/A | N/A
| Bhulta | 398 | 03:00 | 389 | 11:00 | Kaliakoir | 405 | 06:00 | 396 | 12:00
| Bibiana | 403 | 21:00 | 395 | 00:00 | Payra | 427 | 17:00 | 418 | 09:00
| BIPTC | 407 | 02:00 | 394 | 18:00 | Rahanpur_I | 418 | 17:00 | 378 | 10:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 241 | 01:00 | 234 | 12:00 | Hasnabad | 241 | 04:00 | 234 | 10:00
| AKSML | 240 | 17:00 | 228 | 16:00 | Hathazari | 240 | 09:00 | 229 | 16:00
| Aminbazar | 242 | 01:00 | 236 | 10:00 | Ishurdi | 245 | 01:00 | 236 | 08:00
| Ashuganj | 247 | 17:00 | 235 | 13:00 | Jhenaidah | 243 | 01:00 | 231 | 08:00
| Baghabari | 240 | 00:00 | 235 | 08:00 | Kaliakoir | 241 | 02:00 | 230 | 15:00
| Barapukuria | 232 | 00:00 | 223 | 18:00 | Keranigonj | 239 | 00:00 | 233 | 12:00
| Barishal | 247 | 03:00 | 242 | 18:30 | Khulna(S) | 244 | 01:00 | 231 | 08:00
| Bheramara | 244 | 17:00 | 235 | 08:00 | Maniknagar | 239 | 17:00 | 233 | 12:00
| Bhulta | 241 | 17:00 | 235 | 11:00 | Meghnaghat | 244 | 04:00 | 239 | 23:00
| Bibiana | 243 | 00:00 | 235 | 07:00 | Mirsorai | 238 | 01:00 | 231 | 05:00
| BIPTC | 245 | 17:00 | 233 | 08:00 | Rajshahi | 249 | 17:00 | 229 | 20:00
| Bogura | 239 | 01:00 | 231 | 18:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 249 | 03:00 | 246 | 00:00 | Rampura | 238 | 03:00 | 234 | 11:00
| BSRM | 241 | 17:00 | 231 | 12:00 | Shikalbaha | 243 | 17:00 | 229 | 15:00
| Cumilla(N) | 240 | 17:00 | 234 | 12:00 | Shyampur | 239 | 17:00 | 233 | 12:00
| Fenchuganj | 245 | 17:00 | 239 | 12:00 | Siddhirganj | 239 | 00:00 | 237 | 15:00
| Ghorashal | N/A | N/A | N/A | N/A | Sirajgonj | 238 | 17:00 | 233 | 08:00
| GPH | 239 | 17:00 | 228 | 03:00 | Tongi | 239 | 17:00 | 235 | 15:00
| Haripur | 237 | 00:00 | 231 | 11:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 139 | 03:00 | 134 | 12:00 | Kushtia | 140 | 01:00 | 135 | 07:00
| Agargaon | 140 | 00:00 | 136 | 12:00 | Lalbag | 137 | 00:00 | 134 | 11:00
| Agrabad | 140 | 17:00 | 131 | 16:00 | Lalmonirhat | 135 | 14:00 | 126 | 18:00
| AKS | 140 | 08:00 | 132 | 15:00 | Madanganj | 141 | 18:00 | 136 | 05:00
| Aminbazar | 141 | 01:00 | 135 | 10:00 | Madaripur | 141 | 06:00 | 135 | 19:30
| Amnura | 137 | 00:00 | 128 | 12:00 | Madartek | 137 | 00:00 | 133 | 12:00
| Ashuganj | 140 | 00:00 | 139 | 15:00 | Madunaghat | 142 | 17:00 | 134 | 12:00
| Bagerhat | 141 | 17:00 | 131 | 08:00 | Magura | 140 | 17:00 | 134 | 13:00
| Bakulia | 140 | 18:30 | 134 | 12:00 | Mahasthangarh | 140 | 01:00 | 134 | 18:00
| Banani | 142 | 21:00 | 136 | 12:00 | Manikganj | 137 | 17:00 | 132 | 12:00
| Bangabhaban | 139 | 02:00 | 134 | 13:00 | Maniknagar | 138 | 06:00 | 135 | 11:00
| Barapukuria | 137 | 00:00 | 130 | 18:00 | Matarbari | 127 | 17:00 | 116 | 13:00
| Barguna | 141 | 17:00 | 137 | 18:30 | Matuail | 140.2 | 17:00 | 137 | 00:00
| Barishal | 140 | 03:00 | 136 | 18:30 | Millgate | 141 | 17:00 | 136 | 11:00
| Barishal-230 | 140 | 00:00 | 136 | 18:30 | Mirpur | 139 | 19:00 | 135 | 10:00
| Baroaulia | 141 | 05:00 | 131 | 00:00 | Mithapukur | 139 | 01:00 | 131 | 18:00
| Baroirhat | 140 | 00:00 | 134 | 15:00 | Modern | 140 | 00:00 | 134 | 12:00
| Bashundhara | 142 | 21:00 | 136 | 12:00 | Mogbazar | 140 | 01:00 | 135 | 12:00
| BashundharaCement | 141 | 18:00 | 136 | 05:00 | Mongla | 140 | 17:00 | 131 | 08:00
| Beanibazar | 138 | 00:00 | 135 | 12:00 | Motijheel | 139 | 02:00 | 134 | 13:00
| Benapole | 139 | 01:00 | 130 | 07:00 | Munshiganj | 141 | 18:00 | 136 | 12:00
| Bhaluka | 132 | 03:00 | 122 | 18:30 | Mymensingh | 135 | 06:00 | 124 | 19:00
| Bhandaria | 141 | 05:00 | 136 | 18:30 | Naogaon | 138 | 00:00 | 133 | 08:00
| Bhangura | 143 | 00:00 | 139 | 18:30 | Narail | 139 | 01:00 | 132 | 08:00
| Bheramara | 140 | 01:00 | 135 | 12:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bheramara(GK) | 141 | 17:00 | 136 | 12:00 | Narshingdi | 138 | 14:00 | 134 | 00:00
| Bhulta | 134 | 17:00 | 130 | 00:00 | Natore | 139 | 00:00 | 134 | 12:00
| Bog-Sherpur | 141 | 00:00 | 136 | 18:30 | Nawabganj | 137 | 00:00 | 133 | 10:00
| Bogura | 141 | 01:00 | 135 | 18:00 | Netrakona | 130 | 00:00 | 122 | 12:00
| Bogura-230 | 141 | 01:00 | 136 | 18:00 | New | 141 | 17:00 | 136 | 12:00
| Brahmanbaria | 137 | 17:00 | 134 | 08:00 | Niamatpur | 137 | 00:00 | 129 | 16:00
| Cantonment | 140 | 00:00 | 135 | 12:00 | Noapara | 139 | 00:00 | 132 | 07:00
| Chandpur | 140 | 06:00 | 134 | 12:00 | Pabna | 142 | 01:00 | 137 | 12:00
| Chandraghona | 141 | 18:30 | 135 | 11:00 | Palashbari | 138 | 00:00 | 130 | 18:00
| Chapai | 139 | 00:00 | 130 | 12:00 | Panchagarh | 138 | 01:00 | 125 | 18:00
| Charsaidpur | 141 | 18:00 | 137 | 00:00 | Patuakhali | 140 | 17:00 | 136 | 18:00
| Chauddagram | 141 | 01:00 | 134 | 16:00 | Payra | 141 | 17:00 | 138 | 09:00
| Chhatak | 139 | 01:00 | 135 | 12:00 | PHP | 141 | 17:00 | 135 | 12:00
| Chowmuhani | 142 | 21:00 | 133 | 12:00 | Postogola | 138 | 17:00 | 134 | 12:00
| Chuadanga | 139 | 17:00 | 130 | 08:00 | Purbachal | 142 | 17:00 | 136 | 12:00
| Coxsbazar | 128 | 09:00 | 119 | 16:00 | Purbasadipur | 137 | 00:00 | 124 | 18:00
| Cumilla(N) | 142 | 02:00 | 137 | 12:00 | Rahim | 140 | 14:00 | 137 | 01:00
| Cumilla(S) | 142 | 01:00 | 130 | 13:00 | Rajbari | 139 | 01:00 | 133 | 12:00
| Daudkandi | 139 | 19:30 | 135 | 12:00 | Rajendrapur | 134 | 14:00 | 130 | 11:00
| Dhaka | 139 | 06:00 | 135 | 12:00 | Rajshahi | 137 | 00:00 | 130 | 12:00
| Dhamrai | 140 | 01:00 | 135 | 12:00 | Rajshahi-230 | 136 | 00:00 | 128 | 12:00
| Dhanmondi | 139.5 | 17:00 | 137 | 12:00 | Ramganj | 138 | 17:00 | 130 | 16:00
| Dohazari | 137 | 00:00 | 131 | 13:00 | Rampur | 139 | 00:00 | 133 | 12:00
| Faridpur | 138 | 00:00 | 134 | 18:30 | Rampura | 138 | 03:00 | 134 | 14:00
| Fatullah | 139 | 02:00 | 136 | 11:00 | Rangamati | 141 | 17:00 | 134 | 16:00
| Fenchuganj | 142 | 02:00 | 136 | 13:00 | Rangpur | 137 | 14:00 | 128 | 18:00
| Feni | 141 | 09:00 | 135 | 16:00 | Ruppur | 143 | 17:00 | 136 | 12:00
| Ghorashal | 143 | 07:00 | 141 | 00:00 | Saidpur | 136 | 06:00 | 124 | 18:00
| Goalpara | 142 | 17:00 | 133 | 08:00 | Satkhira | 139 | 17:00 | 129 | 08:00
| Gollamari | 141 | 17:00 | 134 | 08:00 | Satmasjid | 140 | 00:00 | 135 | 12:00
| Gopalganj | 141 | 17:00 | 134 | 08:00 | Savar | 141 | 19:00 | 134 | 10:00
| Gopalganj-400 | N/A | N/A | N/A | N/A | Shahjadpur | 148 | 17:00 | 143 | 08:00
| Gopalganj_I | N/A | N/A | N/A | N/A | Shahjibazar | 139 | 00:00 | 137 | 07:00
| Gulshan | 138 | 00:00 | 134 | 11:00 | Shahmirpur | 141 | 06:00 | 132 | 16:00
| Halishahar | 141 | 17:00 | 133 | 15:00 | Shariatpur | 139 | 03:00 | 133 | 19:30
| Haripur | 140 | 14:00 | 137 | 01:00 | Sherpur | 134 | 05:00 | 127 | 17:00
| HaripurSBU | 140 | 18:00 | 137 | 12:00 | Shikalbaha | 141 | 17:00 | 129 | 07:00
| Hasnabad | 136 | 00:00 | 134 | 12:00 | Shikalbaha-230 | 140 | 17:00 | 134 | 11:00
| Hathazari | 141 | 02:00 | 135 | 16:00 | Shitalakhya | 137 | 17:00 | 132 | 12:00
| Ishurdi | 142 | 01:00 | 136 | 12:00 | Sholosohor | 140 | 17:00 | 133 | 12:00
| Jaldhaka | 136 | 01:00 | 125 | 18:00 | Shyampur | 136 | 06:00 | 133 | 11:00
| Jamalpur | 136 | 07:00 | 129 | 09:00 | Shyampur-230 | 138 | 03:00 | 134 | 12:00
| Jashore | 140 | 17:00 | 130 | 08:00 | Siddhirganj | 139 | 17:00 | 137 | 10:00
| Jhenaidah | 142 | 17:00 | 134 | 08:00 | Sirajganj | 142 | 00:00 | 137 | 08:00
| Jhenaidah-230 | 141 | 17:00 | 134 | 08:00 | Sonargaon | 138 | 21:00 | 133 | 18:00
| Joydebpur | 143 | 00:00 | 139 | 16:00 | Sreemongol | 141 | 14:00 | 139 | 15:00
| Joypurhat | 138 | 00:00 | 131 | 12:00 | Srinagar | 137 | 17:00 | 133 | 11:00
| Juldah | 140 | 16:00 | 135 | 12:00 | SSM | 142 | 00:00 | 138 | 12:00
| Kabirpur | 139 | 13:00 | 132 | 08:00 | Sunamganj | 137 | 00:00 | 134 | 13:00
| Kachua | 140 | 17:00 | 135 | 12:00 | Sylhet | 139 | 00:00 | 136 | 12:00
| Kaliakoir | 135 | 00:00 | 133 | 08:00 | Tangail | 136 | 03:00 | 131 | 16:00
| Kallyanpur | 140 | 00:00 | 134 | 12:00 | Thakurgaon | 140 | 01:00 | 125 | 18:00
| Kalurghat | 140 | 17:00 | 135 | 16:00 | TK | 140 | 18:00 | 134 | 12:00
| Kamrangirchar | 137 | 00:00 | 133 | 11:00 | Tongi | 142 | 17:00 | 136 | 15:00
| Kaptai | 140 | 17:00 | 138 | 00:00 | Ullon | 138 | 01:00 | 135 | 02:00
| Kazla | 138 | 02:00 | 135 | 12:00 | Uttara | 140 | 04:00 | 134 | 12:00
| Keranigonj | 139 | 19:30 | 132 | 12:00 | UttaraNew | 140 | 04:00 | 134 | 12:00
| Khagrachori | 142 | 17:00 | 134 | 11:00 | Zigatola | 136 | 00:00 | 132 | 12:00
| Khulna | 140 | 17:00 | 133 | 08:00
| Khulna(S) | 140 | 01:00 | 133 | 08:00
| Khulshi | 139 | 09:00 | 133 | 10:00
| Kishoreganj | 135 | 01:00 | 128 | 08:00
| Kodda | 142 | 00:00 | 130 | 12:00
| KSRM | 141 | 19:00 | 131 | 05:00
| Kulaura | 142 | 01:00 | 137 | 12:00
| Kurigram | 134 | 01:00 | 123 | 18:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2022-12-30
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 296 | 4308 | 2707 | 7015 |  |  |  | QF-LDC-11
0:30 | 328 | 4410.5 | 2672 | 7082.5 | Date: | 2022-12-30
1:00 | 360 | 4513 | 2637 | 7150
1:30 | 345 | 4480.5 | 2496 | 6976.5
2:00 | 330 | 4448 | 2355 | 6803
2:30 | 330 | 4443 | 2221.5 | 6664.5 | [5 empty] | Gen. at Eve. Peak | 8671 | 8671 MW (19:30 )
3:00 | 330 | 4438 | 2088 | 6526 | [6 empty] | 19:30
3:30 | 330 | 4379 | 2061 | 6440 | [5 empty] | Gen. at Day Peak | 7880 | 7880 MW (12:00 )
4:00 | 330 | 4320 | 2034 | 6354 | [6 empty] | 12:00
4:30 | 305 | 4243.5 | 2033 | 6276.5 | [5 empty] | Highest Generation | 8671
5:00 | 280 | 4167 | 2032 | 6199 | [6 empty] | 19:30
5:30 | 230 | 4230.5 | 2103.5 | 6334
6:00 | 180 | 4294 | 2175 | 6469
6:30 | 110 | 4346 | 2193 | 6539
7:00 | 40 | 4398 | 2211 | 6609
7:30 | 125 | 4498 | 2353 | 6851
8:00 | 210 | 4598 | 2495 | 7093
8:30 | 115 | 4672.5 | 2566 | 7238.5
9:00 | 20 | 4747 | 2637 | 7384
9:30 | 376 | 4761.5 | 2666.5 | 7428
10:00 | 732 | 4776 | 2696 | 7472
10:30 | 721 | 4684.5 | 2769 | 7453.5
11:00 | 710 | 4593 | 2842 | 7435
11:30 | 680 | 4727.5 | 2930 | 7657.5
12:00 | 650 | 4862 | 3018 | 7880
12:30 | 581 | 4962 | 3079 | 8041
13:00 | 512 | 5062 | 3140 | 8202
13:30 | 600 | 4599 | 3012.5 | 7611.5
14:00 | 688 | 4136 | 2885 | 7021
14:30 | 729 | 4104 | 2759.5 | 6863.5
15:00 | 770 | 4072 | 2634 | 6706
15:30 | 653 | 4039.5 | 2570.5 | 6610
16:00 | 536 | 4007 | 2507 | 6514
16:30 | 513 | 4195 | 2559 | 6754
17:00 | 490 | 4383 | 2611 | 6994
17:30 | 289 | 4838 | 2903.5 | 7741.5
18:00 | 88 | 5293 | 3196 | 8489
18:30 | 89 | 5384 | 3181 | 8565
19:00 | 90 | 5475 | 3166 | 8641
19:30 | 102 | 5455 | 3216 | 8671
20:00 | 126 | 5455 | 3179 | 8634 |  |  |  | Executive Engineer
20:30 | 120 | 5285.5 | 3208.5 | 8494 |  |  |  | Network Operation Division
21:00 | 114 | 5116 | 3238 | 8354
21:30 | 127 | 5091.5 | 3197.5 | 8289
22:00 | 140 | 5067 | 3157 | 8224 |  |  |  |  | Page 6 of 7
22:30 | 250 | 4887.5 | 3035.5 | 7923
23:00 | 360 | 4708 | 2914 | 7622
23:30 | 328 | 4508 | 2810.5 | 7318.5
24:00 | 296 | 4308 | 2707 | 7015
8671 MW (19:30 )
7880 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2022-12-30 |  | Energy |  | 180201222
[13 empty] | 2022-12-30 |  |  |  |  | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 3120 | 729 | 1576 | 0 | 491 | 971 | 46 | 0 | 0 | 82 | 0 | 0
0:30 | 2989.5 | 729 | 1498 | 0 | 836 | 899 | 46 | 0 | 9 | 76 | 0 | 0 | Date: | 2022-12-30
1:00 | 2859 | 729 | 1420 | 0 | 1181 | 827 | 46 | 0 | 18 | 70 | 0 | 0
1:30 | 2864.5 | 668 | 1422.5 | 0 | 1082.5 | 817 | 46 | 0 | 9 | 67 | 0 | 0 | [7 empty] | Total Energy | 180.2012 | Total Energy Gen 180.201 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 180.201 MKWHr
2:00 | 2870 | 607 | 1425 | 0 | 984 | 807 | 46 | 0 | 0 | 64 | 0 | 0 | [7 empty] | Energy not Served | 0
2:30 | 2874 | 585 | 1435.5 | 0 | 871.5 | 787.5 | 46 | 0 | 0 | 65 | 0 | 0 | [7 empty] | Energy Requirement | 180.2012
3:00 | 2878 | 563 | 1446 | 0 | 759 | 768 | 46 | 0 | 0 | 66 | 0 | 0
3:30 | 2888.5 | 563 | 1439.5 | 0 | 671 | 767 | 46 | 0 | 0 | 65 | 0 | 0 | [5 empty] | Shortage
4:00 | 2899 | 563 | 1433 | 0 | 583 | 766 | 46 | 0 | 0 | 64 | 0 | 0
4:30 | 2859 | 563.5 | 1420 | 0 | 557.5 | 766.5 | 46 | 0 | 0 | 64 | 0 | 0
5:00 | 2819 | 564 | 1407 | 0 | 532 | 767 | 46 | 0 | 0 | 64 | 0 | 0
5:30 | 2846 | 563.5 | 1416 | 0 | 625.5 | 768 | 46 | 0 | 0 | 69 | 0 | 0
6:00 | 2873 | 563 | 1425 | 0 | 719 | 769 | 46 | 0 | 0 | 74 | 0 | 0
6:30 | 2879 | 563 | 1394.5 | 0 | 823.5 | 758 | 46 | 0 | 0 | 73 | 2 | 0 |  |  |  | Coal
7:00 | 2885 | 563 | 1364 | 0 | 928 | 747 | 46 | 0 | 0 | 72 | 4 | 0
7:30 | 2902.5 | 563.5 | 1462 | 0 | 995.5 | 768 | 46 | 0 | 21 | 71 | 21.5 | 0 |  |  | Oil |  |  |  | ,
8:00 | 2920 | 564 | 1560 | 0 | 1063 | 789 | 46 | 0 | 42 | 70 | 39 | 0
8:30 | 2929.5 | 563.5 | 1545.5 | 0 | 1153 | 818 | 46 | 0 | 47 | 75 | 61 | 0
9:00 | 2939 | 563 | 1531 | 0 | 1243 | 847 | 46 | 0 | 52 | 80 | 83 | 0
9:30 | 2939.5 | 563 | 1489.5 | 0 | 1260 | 882 | 46 | 0 | 56 | 81 | 111 | 0
10:00 | 2940 | 563 | 1448 | 0 | 1277 | 917 | 46 | 0 | 60 | 82 | 139 | 0
10:30 | 2875.5 | 563 | 1460 | 0 | 1254 | 921.5 | 46 | 0 | 64 | 80 | 189.5 | 0
11:00 | 2811 | 563 | 1472 | 0 | 1231 | 926 | 46 | 0 | 68 | 78 | 240 | 0
11:30 | 2837.5 | 622.5 | 1462 | 85 | 1251.5 | 937.5 | 46 | 0 | 70 | 81 | 264.5 | 0
12:00 | 2864 | 682 | 1452 | 170 | 1272 | 949 | 46 | 0 | 72 | 84 | 289 | 0
12:30 | 2913 | 682 | 1460.5 | 195 | 1312 | 978 | 46 | 0 | 72 | 94 | 288.5 | 0
13:00 | 2962 | 682 | 1469 | 220 | 1352 | 1007 | 46 | 0 | 72 | 104 | 288 | 0
13:30 | 2962 | 682 | 1469 | 220 | 1352 | 1007 | 46 | 0 | 72 | 104 | 288 | 0
14:00 | 2962 | 682 | 1469 | 220 | 1352 | 1007 | 46 | 0 | 72 | 104 | 288 | 0
14:30 | 2882 | 669.5 | 1321 | 110 | 1076.5 | 973 | 46 | 0 | 56 | 95 | 225 | 0
15:00 | 2802 | 657 | 1173 | 0 | 801 | 939 | 46 | 0 | 40 | 86 | 162 | 0
15:30 | 2849.5 | 657 | 1199.5 | 0 | 702 | 920 | 41.5 | 0 | 40 | 85 | 115.5 | 0
16:00 | 2897 | 657 | 1226 | 0 | 603 | 901 | 37 | 0 | 40 | 84 | 69 | 0
16:30 | 2942 | 657 | 1227.5 | 0 | 758 | 900 | 33.5 | 0 | 111.5 | 85 | 39.5 | 0
17:00 | 2987 | 657 | 1229 | 0 | 913 | 899 | 30 | 0 | 183 | 86 | 10 | 0
17:30 | 3025.5 | 764 | 1316 | 0 | 1331.5 | 895 | 35 | 0 | 275.5 | 94 | 5 | 0
18:00 | 3064 | 871 | 1403 | 0 | 1750 | 891 | 40 | 0 | 368 | 102 | 0 | 0
18:30 | 3126.5 | 871 | 1488.5 | 0 | 1753.5 | 955.5 | 35 | 0 | 233 | 102 | 0 | 0
19:00 | 3189 | 871 | 1574 | 0 | 1757 | 1020 | 30 | 0 | 98 | 102 | 0 | 0
19:30 | 3201 | 871 | 1561 | 0 | 1778 | 1079 | 30 | 0 | 51 | 100 | 0 | 0
20:00 | 3208 | 871 | 1575 | 0 | 1756 | 1092 | 30 | 0 | 0 | 102 | 0 | 0
20:30 | 3169.5 | 871.5 | 1574 | 0 | 1659.5 | 1090.5 | 30 | 0 | 0 | 99 | 0 | 0
21:00 | 3131 | 872 | 1573 | 0 | 1563 | 1089 | 30 | 0 | 0 | 96 | 0 | 0
21:30 | 3115.5 | 871 | 1561 | 0 | 1519.5 | 1090 | 38 | 0 | 0 | 94 | 0 | 0
22:00 | 3100 | 870 | 1549 | 0 | 1476 | 1091 | 46 | 0 | 0 | 92 | 0 | 0
22:30 | 3109.5 | 823 | 1561 | 0 | 1229.5 | 1060 | 46 | 0 | 0 | 94 | 0 | 0
23:00 | 3119 | 776 | 1573 | 0 | 983 | 1029 | 46 | 0 | 0 | 96 | 0 | 0
23:30 | 3119.5 | 752.5 | 1574.5 | 0 | 737 | 1000 | 46 | 0 | 0 | 89 | 0 | 0 | Max Temp. in Dhaka |  | 22.2° C
24:00 | 3120 | 729 | 1576 | 0 | 491 | 971 | 46 | 0 | 0 | 82 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 180.201 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 180.201 MKWHr
Note on W13: Author:

## Generation
g | 2022-12-30
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 37 | 30 | 40 |  | 30 | 30 | 30 | 30 | 46 | 46 | 46 | 1048320
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 140 |  | 140 | 140 | 150 | 120 | 120 | 120 | 120 | 3000000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 25 | 25 | 25 | 25 |  | 1 | 8 | 19 | 25 | 25 | 25 | 25 | 25 | 25 |  |  | 1 | 8 |  | 8 | 8 | 8 | 8 | 8 |  | 0 | 362953
| Teknaf 20MW PP (Solartech) | [6 empty] | 1 | 5 | 11 | 16 | 18 | 18 | 17 | 14 | 11 | 5 | 1 | [9 empty] | 115425
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [16 empty] | 7 | 34 |  | 17 | [5 empty] | 0 | 92017
12 | Hathazari 100 MW peaking PP | [7 empty] | 10 | 20 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | [8 empty] | 247296
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 17 | 17 | 17 |  |  | 2 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 21 | 17 |  | 17 | 17 | 17 | 37 | 51 | 17 | 0 | 482581
| Daudkandi 200 MW PP (B.Trac) | [12 empty] | 50 | [13 empty] | 88512
14 | Titas 50 MW Peaking PP | [25 empty] | 0 | 0
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 32 | 32 | 32 |  |  | 10 | 32 | 32 | 33 | 33 | 32 | 32 | 32 | 32 | 32 | 32 | 58 | 95 |  | 98 | 98 | 98 | 98 | 70 | 45 | 0 | 1021200
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 200727
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4 | 201 | 202 | 202 | 205 | 201 | 195 | 170 | 200 | 200 | 200 | 0 |  | 68 | 130 | 170 | 180 | 200 | 200 |  | 240 | 240 | 240 | 240 | 240 | 242 | 241 | 4224000
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 148680
33 | Ashuganj 225 MW CCPP | 183 | 186 | 183 | 183 | 193 | 196 | 198 | 195 | 193 | 183 | 183 | 203 | 183 | 203 | 187 | 184 | 184 | 205 |  | 183 | 190 | 184 | 183 | 183 | 183 | 183 | 4599500
34 | Ashuganj 450 MW CCPP(South)
| Ashuganj 450 MW CCPP(North) | 290 | 290 | 295 | 290 | 310 | 320 | 325 | 325 | 305 | 290 | 290 | 325 | 290 | 320 | 285 | 285 | 290 | 325 |  | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 7555000
| Ashuganj 420 MW CCPP(East) | 258 | 259 | 268 | 288 | 298 | 314 | 358 | 370 | 338 | 350 | 350 | 330 | 330 | 300 | 330 | 338 | 348 | 348 |  | 348 | 348 | 348 | 308 | 338 | 338 | 338 | 7796000
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 144480
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 391 | 391 | 391 | 386 | 362 | 363 | 342 | 342 | 384 | 394 | 388 | 395 | 396 | 354 | 323 | 336 | 362 | 333 |  | 348 | 344 | 342 | 335 | 333 | 333 | 337 | 8787970
40 | Meghnaghat 450 MW CCPP(MPL) | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 |  | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 5906350
41 | Haripur 360MW CCPP(HPL) | 296 | 294 | 303 | 300 | 276 | 275 | 270 | 335 | 325 | 325 | 312 | 304 | 304 | 255 | 255 | 288 | 280 | 254 |  | 276 | 263 | 263 | 255 | 259 | 274 | 282 | 6810000
42 | RPCL 210MW CCPP | 93 | 96 | 93 | 101 | 103 | 93 | 70 | 35 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 39 | 58 | 75 |  | 101 | 107 | 107 | 108 | 108 | 108 | 108 | 1653120
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 0 | 2 | 4 | 7 | 9 | 15 | 30 | 28 | 18 | 7 | 1 | [9 empty] | 122830
44 | Fenchugonj CCPP Phase-1 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 716000
45 | Fenchugonj CCPP Phase-2 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 |  | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 589320
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 40 | 40 | 40 | 40 | 40 | 65 | 64 | 64 | 64 | 65 | 64 | 63 | 64 | 42 | 40 | 40 | 40 | 64 |  | 64 | 64 | 64 | 65 | 40 | 40 | 40 | 1229284
48 | Shahjibazar 86MW PP (Shahjibazar) | 10 | 10 | 10 | 10 | 10 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 10 | 10 | 30 | 30 | 86 |  | 86 | 86 | 86 | 86 | 50 | 50 | 50 | 898560
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP
51 | Sylhet 20 MW GTPP | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 20 | 20 | 458000
52 | Sylhet 50MW PP (EPL) | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 11 | 11 | 11 | 16 | 27 |  | 26 | 26 | 26 | 27 | 27 | 27 | 27 | 582320
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 249660
54 | Hobiganj 11MW PP Cofidence-E | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 192432
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 53 | 53 | 53 | 53 | 53 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 14 | 14 | 11 | 18 | 52 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 1104600
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 389760
57 | Bibiana-II 341 MW CCPP (Summit)
| Bibiyana South 400 MW | 400 | 400 | 400 | 400 | 341 | 342 | 351 | 370 | 400 | 370 | 400 | 400 | 400 | 340 | 340 | 371 | 350 | 360 |  | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 9146400
58 | Nababganj 55 MW PP (Southern power ) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 35 | 35 |  | 55 | 55 | 55 | 35 | 35 | 35 | 35 | 610703
59 | Tangail Palli Power Gen 22 MW | 10 | 12 | 12 | 12 | 12 | 12 | 12 | 7 | 8 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 288000
60 | Barabkunda 22 MW PP (Regent) | [19 empty] | 0 | 0 | 0 |  |  |  | 0
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 |  | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 369936
62 | Tangail 22 MW PP (Doreen) | [10 empty] | 12 | 14 | 14 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 22 | 20 | 19 | 247680
63 | Impoprt (Tripura) | 70 | 64 | 66 | 64 | 64 | 74 | 72 | 70 | 80 | 82 | 78 | 84 | 104 | 88 | 86 | 84 | 86 | 102 |  | 102 | 100 | 102 | 96 | 92 | 96 | 82 | 1977600
64 | Malancha, Ctg. EPZ (United) | 25 | 29 | 27 | 35 | 37 | 37 | 31 | 37 | 37 | 33 | 31 | 32 | 42 | 42 | 40 | 30 | 20 | 35 |  | 37 | 30 | 40 | 40 | 42 | 42 | 45 | 828000
65 | Feni 22MW PP (Doreen) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 503064
66 | Feni 11 MW PP (Doreen) | 10 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 9 | 9 | 9 | 9 | 243180
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 30 | 24 | 23 | 22 | 22 | 22 | 20 | 20 | 22 | 21 | 16 |  | 24 | 25 | 30 | 30 | 33 | 33 | 33 | 670100
68 | Cumilla 25 MW PP (Summit) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 379660
69 | Summit Ashulia | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 582000
70 | Summit Madhabdi | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 23 | 16 | 14 | 14 | 14 | 14 | 15 | 17 |  | 24 | 24 | 24 | 24 | 24 | 24 | 23 | 467100
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 20 | 20 | 20 | 17 | 17 | 17 | 566700
72 | Rupganj 33 MW PP(Summit) | 28 | 28 | 28 | 28 | 30 | 30 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 759000
73 | Ghorashal 108MW PP (Regent) | 73 | 73 | 73 | 73 | 73 | 73 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 22 | 22 | 22 | 22 | 54 |  | 67 | 70 | 72 | 73 | 74 | 73 | 73 | 1501272
| Feni Lanka Power | 51 | 17 |  |  |  | 1 | 17 | 34 | 70 | 70 | 70 | 81 | 100 | 17 |  |  | 17 | 17 |  | 17 | 17 | 17 | 17 | 3 |  | 0 | 705660
| Chowmuhani 113 MW | 9 | 9 | 9 |  |  |  | 9 | 9 | 9 | 9 | 13 | 27 | 28 | 28 | 28 | 8 | 13 | 60 |  | 85 | 107 | 75 | 90 | 108 | 65 | 9 | 798000
| Manikgonj 162MW PP(MPGL) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 54 | 162 |  | 162 | 162 | 162 | 162 | 92 | 17 | 17 | 1087200
77 | Siddhirganj 100 PP(Dutch Bangla) | 9 | [5 empty] | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  |  | 2 | 9 |  | 9 | 9 | 9 | 9 | 9 |  | 0 | 120000
78 | Gazipur 52 MW PP | 8 | [6 empty] | 5 | 16 | 16 | 16 | 20 | 43 | 8 |  |  | 2 | 16 |  | 8 | 8 | 8 | 8 |  |  | 0 | 208800
79 | Kodda 150MW PP | [7 empty] | 32 | 32 | 32 | 32 | 32 | 32 | 32 |  |  | 32 | 48 | [7 empty] | 0 | 317280
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 8 | 8 | 8 |  |  | 1 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 |  | 179563
| Gazipur 100 MW PP | 17 | 17 | 17 |  |  | 10 | 17 | 18 | 34 | 51 | 51 | 68 | 105 | 17 | 17 |  | 1 | 17 |  | 17 | 17 | 17 | 31 | 50 | 17 | 0 | 756000
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 1 | 1 | 2 | 3 | 4 | 3 | 2 | 2 | 1 | [10 empty] | 18723
| Jodiac Power | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 449888
| Karnaphuli Power Ltd. | 72 | 72 | 72 | 64 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 64 | 34 | 34 | 64 |  | 70 | 72 | 72 | 72 | 72 | 72 | 34 | 1688611
82 | Madanganj 102 PP(Summit) | 34 | 34 | 34 | 34 | 17 | 17 | 17 | 20 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 17 | 17 | 34 |  | 23 | 17 | 17 | 17 | 17 | 2 | 0 | 528759
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL) | 18 | [5 empty] | 6 | 14 | 17 | 16 | 17 | 17 | 17 | 17 |  |  | 2 | 16 |  | 17 | 17 | 17 | 13 | 16 |  | 0 | 235200
| Meghnaghat 104 MW PP (OPCL) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  |  |  |  | 14 |  | 17 | 17 | 17 | 17 | 17 |  | 0 | 320640
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 10 | 516960
92 | Fenchuganj 44MW (Energyprima) | 47 | 47 | 47 | 47 | 47 | 44 | 44 | 47 | 47 | 47 | 22 | 22 | 40 | 10 | 10 | 10 | 10 | 35 |  | 44 | 46 | 47 | 47 | 47 | 47 | 47 | 906552
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 15 | 15 | 15 | 15 | 15 |  | 48 | 51 | 51 | 51 | 51 | 51 | 51 | 1126140
94 | Gagnagar 102 MW PP (Digital Power) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 8 | 302112
95 | Patenga 50MW PP (Baraka) | 21 | 20 | 10 |  |  | 1 | 12 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  |  | 1 | 6 |  | 6 | 6 | 6 | 6 | 4 |  | 0 | 268320
96 | Chattogram 108 MW PP (ECPV) | [16 empty] | 5 | 11 |  | 11 | [5 empty] | 0 | 31680
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [16 empty] | 5 | 25 |  | 25 | 15 | 15 | 15 | 15 | 15 | 0 | 131280
100 | Manikganj 55 MW PP (Northern) | 35 | 35 | 35 | 35 | 35 | 35 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 55 | 55 | 55 | 35 | 17 | 17 | 17 | 633369
101 | Kushiara 163 MW CCPP (KP) | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 |  | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 2768154
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | [9 empty] | 3600
103 | Kamalaghat 54 MW PP(Banco Energy) | [7 empty] | 0 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 54 |  | 54 | 54 | 54 | 17 | 17 | 17 | 17 | 387720
104 | Keranigonj 300 MW PP (APR) | [10 empty] | 0 | 150 | 120 | [12 empty] | 0 | 234775
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 58 | 48 | 48 | 48 | 57 | 24 | 24 | 47 |  | 47 | 48 | 48 | 48 | 48 | 48 | 24 | 1130400
112 | Aurahati 100MW PP (Aggreko) | [11 empty] | 20 | 50 | [12 empty] | 0 | 105000
114 | Kodda 149 MW PP Unit-1 (Summit) | 35 | 35 | 35 |  |  | 10 | 26 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 36 | 40 | 50 | 77 | 149 | 103 | 11 | 992160
115 | Juldah 100 MW PP Unit-3 (Acorn) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 603840
116 | Chandpur 200MW (Desh energy) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 432480
117 | Ashuganj 150MW PP (Midland) | 6 | 6 | 6 |  |  | 2 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 16 | 70 | 75 |  | 75 | 75 | 73 | 73 | 75 | 25 | 0 | 575418
118 | Bibiyana-III 400 MW CCPP | 363 | 363 | 363 | 363 | 326 | 340 | 360 | 369 | 374 | 392 | 399 | 410 | 406 | 222 | 322 | 352 | 392 | 359 |  | 400 | 400 | 400 | 400 | 375 | 375 | 375 | 8862000
| Jamalpur 115 MW PP (United) | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 8 | 9 | 47 |  | 47 | 47 | 47 | 47 | 47 | 47 | 8 | 747600
| Anwara 300 MW PP (United) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 30 | 132 | 286 |  | 290 | 294 | 296 | 51 | 51 | 51 | 51 | 1944545
| Juldah unit-2 (Acorn) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 605760
| Anlima Energy Ltd. | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 85 | 68 | 68 | 68 | 68 | 68 | 34 | 34 | 68 |  | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 1799018
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 9 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 435600
| Spectra Solar Plant Ltd. | [6 empty] | 0 | 1 | 2 | 6 | 15 | 24 | 24 | 19 | 13 | 6 | 1 | [9 empty] | 109049
| Chandpur 115(Doreen) | [25 empty] | 0 | 0
| Kanchan Purbachal Power Generation Ltd. | 17 | 17 | 17 | 17 |  | 9 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 410040
| Mirsharai 150 MW (Oil) | [26 empty] | 0
Mirsharai 150 MW (Gas)
120 | Eastern Zone Total | 4513 | 4448 | 4438 | 4320 | 4167 | 4294 | 4398 | 4598 | 4747 | 4776 | 4593 | 4862 | 5062 | 4136 | 4072 | 4007 | 4383 | 5293 |  | 5475 | 5455 | 5455 | 5116 | 5067 | 4708 | 4308 | 113435188
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | 99 | 49 |  |  |  | 21 | 49 | 49 | 86 | 100 | 99 | 99 | 99 | 18 |  |  | 24 | 114 |  | 32 | 32 | 32 | 32 |  |  | 0 | 1053120
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [16 empty] | 13 | 45 | [8 empty] | 47040
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | [6 empty] | 5 | 17 | 17 | 17 | 0 | [5 empty] | 5 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 201120
130 | Mongla Orion 100 MW Solar PP | [6 empty] | 1 | 14 | 32 | 49 | 60 | 61 | 59 | 50 | 30 | 14 | 2 | [9 empty] | 379440
131 | Rampal 1320 MW (BIFPCL)
132 | United Payra Power Ltd. | [25 empty] | 0 | 0
133 | Bhola Nutan Biddut BD LTD (GAS) | 110 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 105 | 105 | 110 | 120 | 135 | 145 | 150 | 157 | 160 | 220 |  | 221 | 219 | 221 | 220 | 220 | 220 | 219 | 3570436
Bhola Nutan Biddut BD LTD (OIL)
Barisal 110 MW PP (Summit )
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW | 307 | 308 | 309 | 307 | 307 | 309 | 307 | 309 | 307 | 307 | 306 | 309 | 307 | 310 | 309 | 311 | 309 | 311 |  | 310 | 309 | 310 | 309 | 309 | 309 | 310 | 7454600
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 86 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 118 | 112 | 182 | 181 | 180 | 181 | 172 | 181 |  | 182 | 182 | 182 | 182 | 170 | 182 | 182 | 3289186
140 | Bhola 33 MW PP (Venture) | 21 | 20 | 18 | 18 | 17 | 19 | 17 | 16 | 17 | 16 | 17 | 19 | 20 | 16 | 14 | 14 | 16 | 21 |  | 23 | 23 | 23 | 24 | 24 | 23 | 21 | 452900
141 | Noapara 100 MW PP (Bangla Trac) | [25 empty] | 0 | 0
142 | Noapara 40 MW PP (Khanjahan Ali) | [13 empty] | 8 | 8 | 8 | 8 | 32 | [7 empty] | 0 | 70125
143 | Gopalganj 100 MW Peaking PP | [16 empty] | 32 | 74 |  | 30 | [6 empty] | 112128
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 729 | 607 | 563 | 563 | 564 | 563 | 563 | 564 | 563 | 563 | 563 | 682 | 682 | 657 | 657 | 657 | 657 | 871 |  | 871 | 871 | 871 | 872 | 870 | 776 | 729 | 16525090
147 | Bheramara 410 MW CCPP
148 | Payra 1320 MW | 360 | 340 | 300 | 300 | 300 | 300 | 280 | 320 | 380 | 450 | 460 | 480 | 540 | 490 | 470 | 430 | 430 | 420 |  | 550 | 610 | 622 | 622 | 622 | 560 | 500 | 11714700
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 160 | 159 | 159 | 159 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 |  | 160 | 160 | 160 | 158 | 160 | 160 | 161 | 3890300
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [17 empty] | 34 | [8 empty] | 48350
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 0 | 0 | 0 | 1 | 2 | 2 | 3 | 2 | 0 | 0 | [9 empty] | 14880
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 130 | 130 | 130 | 130 | 130 | 130 | 140 | 146 | 148 | 153 | 154 | 166 | 185 | 184 | 161 | 159 | 159 | 159 |  | 163 | 170 | 170 | 170 | 171 | 177 | 177 | 3929245
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 325 | 330 | 346 | 328 | 325 | 325 | 282 | 405 | 390 | 314 | 372 | 348 | 322 | 260 | 255 | 261 | 263 | 225 |  | 312 | 313 | 312 | 316 | 321 | 332 | 327 | 7640181
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [16 empty] | 4 | 4 | [8 empty] | 10931
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 19 | 19 | 18 | 17 | 17 | 17 | 17 | 19 | 19 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 469680
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 174780
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | 42 | 42 |  |  |  | 16 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 |  |  | 8 | 8 |  | 8 | 8 | 8 | 42 | 42 |  | 0 | 511794
167 | Katakhali 50 MW Peaking PP | [8 empty] | 0 | 4 | 12 | 16 | 16 | 16 | 16 | 16 | 16 | 19 | [8 empty] | 120538
168 | Santahar 50 MW Peaking PP | 18 | [15 empty] | 15 | 35 | [8 empty] | 84999
169 | Natore 52 MW PP (Rajlanka) | 8 |  |  |  |  | 5 | 35 | 43 | 43 | 43 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 0 | 288955
170 | Chapainawabganj 100 MW Peaking PP | [16 empty] | 40 | 51 |  | 51 | 51 | [5 empty] | 147192
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 35 | 35 |  |  |  |  | 4 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 40 | 50 | 50 | 50 | 50 | 35 | 35 | 812736
172 | Confidence Power Bogura Unit-1 113 MW | 35 |  |  |  |  | 18 | 18 | 18 | 18 | 25 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 55 |  | 55 | 55 | 55 | 55 | 55 | 35 | 0 | 740160
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | 27 | 34 | 34 |  |  | 30 | 33 | 35 | 35 | 30 | 22 | 27 | 27 | 34 | 34 |  | 1 | 33 |  | 34 | 34 | 34 | 34 | 34 | 34 | 0 | 642892
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 0 | 2 | 2 | 3 | 4 | 5 | 4 | 3 | 2 | 0 | [9 empty] | 28759
178 | Energypac Power Venture Thakurgaon Ltd. | 115 | 72 |  |  |  | 50 | 52 | 85 | 115 | 115 | 115 | 115 | 115 | 90 |  |  | 7 | 37 |  | 70 | 75 | 75 | 98 | 55 | 17 | 0 | 1553664
| Intraco Solar 30 MW | [6 empty] | 0 | 4 | 10 | 16 | 21 | 24 | 22 | 18 | 12 | 5 | 1 | [9 empty] | 134513
Adani Power Jharkhanda Ltd
178 | Teesta Solar Limited | [6 empty] | 2 | 12 | 21 | 41 | 110 | 136 | 125 | 104 | 70 | 29 | 4 | [9 empty] | 651600