## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2023-01-25 | Wednesday
|  | Date (day): | 2023-01-25 |  | Wednesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 9319.6 | MW |  |  | (b) At Evening Peak Hour : |  | 10703 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2023-01-24 | 2023-01-25 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 120 | 210 | 210 | 210 |  | -30
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 190 |  | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 | 365 |  | Gas shortage
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 75 | 76 | 74 | 74 | 34 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 391 | 366 | 350 | 350 | 62 |  | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 252 | 233 | 190 | 200 | 160 |  | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 0 | 0 |  | 450 | Under maint
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 8 | 8 | 8 | 8 | 92 |  | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 152 | 152 | 150 | 150 | 185 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 0 | 0 | 0 | 0 | 102 |  | Fuel shortage
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 25 | 15 | 15 | 15 | 40 |  | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 19 | 19 | 19 |  |  | Engine problem
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 0 | 8 | 0 | 8 | 92 |  | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 8 | 16 | 16 | 48 | 54 |  | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 54 | 17 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 48 | 48 | 16 | 48 | 101 |  | Fuel shortage
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 35 | 35 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 17 | 17 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 31 | 50 | 51 | 51 |  | 29 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 30 | 30 | 30 |  | 3 | Engine problem
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 8 | 17 | 8 | 17 | 35 |  | Fuel shortage
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 32 | 65 | 32 | 64 | 234 |  | Fuel shortage
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 0 | 300 |  | Fuel shortage
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Fuel shortage
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Fuel shortage
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 17 | 30 | 17 | 35 | 114 |  | Fuel shortage
36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 34 | 88 | 34 | 88 | 17 |  | Fuel shortage
37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 16 | 17 | 17 | 17 | 87 |  | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 35 | 17 | 17 | 17 | 145 |  | Fuel shortage
39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 19 | 0 | 30 | 0
40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 1 | 17 | 17 | 17 | 38 |  | Fuel shortage
| Dhaka area Total |  |  |  |  | 6263 | 5847 | 1401 | 1621 | 1403 | 1663 | 3243 | 952
41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 8 | 17 | 8 | 17
43 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 20 | 0 | 20 | 0
44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 33 | 32 | 33 | 33 | 17 |  | Fuel shortage
45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 30 | 30 | 30 | 30 | 200 |  | Low Water Level
46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 229 | 230 | 225 | 225
47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 51 | 68 | 34 | 68 | 37 |  | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 31 | 32 | 32 | 32 | 66 |  | Fuel shortage
50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 48 | 68 | 51 | 68 | 34 |  | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 22 | 22 | 22 | 22 | 78 |  | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 25 | 25 | 25 | 25 | 75 |  | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 22 |  | Gas shortage
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 2 | 5 | 10
54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 112 | 283 | 130 | 300
57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 17 | 17 | 17 | 17 | 37 |  | Fuel shortage
58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 62 | 92 | 51 | 92 | 18 |  | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 25 | 25 | 25 | 75 |  | Fuel shortage
60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 34 | 68 | 107 | 107 | 9 |  | Engine problem
| Mirsharai 150 MW |  | Gas/HSD | BPDB-RPCL | 18.5*9 | 0 | 0 | 18 | 0 | 0 | 0
| Chattogram area Total |  |  |  |  | 2442 | 2382 | 771 | 1011 | 820 | 1071 | 1136 | 150
61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 186 | 210 | 200 | 205 | 16 |  | Gas shortage
63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 310 | 310 | 320 | 320 |  |  | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Macine problem
65 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 345 | 347 | 300 | 300 | 100 |  | Gas shortage
66 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 10 | 10 | 10 | 10 | 40 |  | Gas shortage
67 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 55 | 0 | 40 | 5 | 5 | 50 |  | Gas shortage
68 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
69 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 51 | 51 | 51
70 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 6 | 6 | 6 | 6 | 144 |  | Fuel shortage
71 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 13 | 28 | 35 | 35 |  | 17 | Engine problem
72 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under Maint.
73 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 17 | 17 | 17 | 183 |  | Fuel shortage
74 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 21 | 21 | 21
75 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 8 | 8 |  |  | Engine problem
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 116 | 118 | 135 | 152
76 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 13 | 24 | 33 | 33
77 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 8 | 8 | 8 | 44 |  | Fuel shortage
78 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 15 | 15 | 15 | 15 |  | 10 | Engine problem
79 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 10 | 0 | 100 | 200 |  | Fuel shortage
80 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 52 | 17 | 110 | 114
81 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 108 | 9 | 113
82 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 17 |  | 37 | Engine problem
83 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 36 | 94 | 54 | 94 | 21 |  | Fuel shortage
| Cumilla Area Total |  |  |  |  | 3309 | 3285 | 1172 | 1502 | 1269 | 1628 | 1233 | 587
84 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 44 | 54 | 50 | 60 | 142 |  | Gas shortage
85 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 19 | 19
86 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0
87 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
88 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 58 | 48 | 58 | 48 | 152 |  | Fuel shortage
89 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 28 | 47 | 28 | 47 | 68 |  | Fuel shortage
90 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 0 | 0 | 50 | 0
91 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 6 | 6 | 6 | 16 |  | Fuel shortage
| Mymensingh Area Total |  |  |  |  | 717 | 614 | 157 | 174 | 212.6 | 180 | 142 | 0
92 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 30 | 30 | 30 | 30 |  | 40 | Machine problem.
93 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 43 | 43 | 43 | 43 |  | 47 | Machine problem
94 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under S/D
95 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
96 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 48 | 51 | 50 | 50
97 | Fenchuganj 44MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 43 | 50 | 50 | 50
98 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 8 | 8 |  | 3
99 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 61 | 62 | 62 | 62
100 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 60 | 86 | 60 | 86
101 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
102 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 25 | 135 | 0 | 0 |  | 231 | Machine problem
103 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 19 | 19 | 19
104 | Sylhet 50MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Gas shortage
105 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 0 | 0 | 16 | 16 |  | 9 | Engine problem
106 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 300 | 300 | 300 |  |  | FGMO
107 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 363 | 366 | 400 | 400
108 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
109 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 400 | 400 | 400 | 400
| Sylhet Area Total |  |  |  |  | 2472 | 2427 | 1411 | 1552 | 1448 | 1474 | 0 | 923
110 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 811 | 658 | 925 | 923
111 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 32 | 16 | 16 | 49 | 49 |  | Fuel shortage
112 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 43 | 0 | 45 |  | 9 | Engine problem
113 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
114 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 75 | 0 | 75 |  | 34 | Engine problem
115 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 | 410 |  | Gas shortage.
116 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 8 | 0 | 8 | 32 |  | Fuel shortage
117 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 0 | 0 | 95 |  | Fuel shortage
118 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 0 | 18 | 87 |  | Fuel shortage
119 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 105 | 50 | 105
120 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 56 | 0 | 100 | 0
| Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 660*2 | 617 | 617 | 0 | 0 | 0 | 0 |  |  | Coal Shortage.
| Khulna Area Total |  |  |  |  | 3005 | 3001 | 899 | 905 | 1091 | 1223 | 919 | 43
121 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 16 | 16 | 16 |  | 94 | Engine problem
122 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 20 | 25 | 19 | 25 |  | 15 | Engine problem
123 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 182 | 184 | 185 | 185 |  | 9 | ST Under S/D
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
124 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 1100 | 1192 | 1150 | 1190 |  | 54
125 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 175 | 220 | 220 | 220
126 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 54 | 150 | 35 | 150
127 | Barisal 307 MW |  | Coal | BCPCL | 307*1 | 307 | 307 | 0 | 0 | 0 | 0 |  |  | Coal Shortage.
| Barisal Area Total |  |  |  |  | 2265 | 2265 | 1531 | 1787 | 1625 | 1786 | 0 | 172
128 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
129 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 26 | 0 | 34 |  | 18 | Engine problem
130 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 4 | 21 | 0 | 42 |  | 29 | Engine problem
131 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
132 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 25 | 34 | 34 | 42 |  | 8 | Engine problem
133 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 16 | 41 | 15 | 41 |  | 9 | Engine problem
134 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
135 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
136 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 199 | 199 | 210 | 210 |  | 10 | Gas shortage
137 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 388 | 341 | 415 | 415
138 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 9 | 30 | 0 | 35 |  | 15 | Engine problem
139 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 18 | 21 | 22 | 22
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
140 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 8 | 8 |  |  | Engine problem
141 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 8 | 8 | 8 | 44 |  | Fuel shortage
142 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 42 | 97 | 10 | 97 |  | 12 | Engine problem
143 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel shortage
144 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 11 | 94 | 35 | 94 | 19 |  | Fuel shortage
145 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 35 | 95 | 35 | 95 | 18 |  | Fuel shortage
146 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 4 | 0 | 6 | 0
| Adani Power Jharkhanda Ltd |  | Coal | Import | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | On test.
| Rajshahi Area Total |  |  |  |  | 2179 | 2129 | 759 | 1015 | 798 | 1143 | 882 | 101
147 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 83 | 82 | 85 | 85
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
148 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 250 | 251 | 250 | 250 |  | 24
149 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
150 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
151 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 37 | 85 | 35 | 85 | 28 |  | Fuel shortage
152 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5 | 0 | 8 | 0
153 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 35 | 113 | 115 | 115
154 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 26 | 0 | 30 | 0
| Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 0 | 0 | 138 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 830 | 750 | 574 | 531 | 653 | 535 | 68 | 109
| Total |  |  |  |  | 23482 | 22700 | 8675 | 10098 | 9319.6 | 10703 | 7623 | 3037
A. |  | 2023-01-24 | (Yesterday) |  |  |  |  | Tuesday
1 | Highest Generation : |  |  | 10098 | MW at | 20:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 20:00 | hrs.
2 | Minimum Generation : |  |  | 6929 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 10293 | MW
3 | Day peak Generation : |  |  | 8675 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 9812.36 | MW
4 | Evening peak Generation : |  |  | 10098 | MW at | 20:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 180 | MW
5 | Total Energy Generation : |  | 206.4246 | MKWHr | By Solar | 1.6479 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Gas : | 117.3574 | MKWHr |  | By Oil: | 29.0574 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 36.0359 | MKWHr |  | By Hydro: | 0.70794 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 7623 | MW | Dhaka | 3446.46 | 3416.46 |  | 30 |  | 18:00 |  | 480
|  |  | For Plants S/D or M/C prob = |  |  | 3037 | MW | Chittagong | 1005.6 | 1005.6 |  | 0 |  | 19:00 |  | 500.4152
|  |  | Total = |  |  | 10660 | MW | Khulna | 1134.6 | 1134.6 |  | 0 |  | 19:30 |  | 230.3937
7 | Total Gas Supplied : |  |  | 861.45 | MMCFD |  |  | Rajshahi | 1056.7 | 1056.7 |  | 0 |  | 20:00 |  | 179.7071
8 | Fuel Cost : | i) Gas : | Taka | 121010093.632 | ii) Oil : | Taka | 386600122.64 | Comilla | 861 | 861 |  | 0 |  | 21:00 |  | 190.766
|  | iii) Coal : |  | 295941591.58 | Total | Taka | 803551807.852 | Mymensingh | 936 | 786 |  | 150 |  | 22:00 |  | 148.3736
9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0 | MKWHr. | Sylhet | 360 | 360 |  | 0 |  | 23:00 |  | 124.4126
| ii) During Peak Demand : |  |  | 880 | MW (E to W) at | 20:00 | hrs | Barisal | 284 | 284 |  | 0 |  | 24:00 |  | 105
| iii) Maximum : |  |  | 850 | MW at | 7:00 | hrs | Rangpur | 728 | 728 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 28.7° C |  |  | Total | 9812.36 | 9632.36 |  | 180
B. |  | 2023-01-25 | (Today) |  |  |  | Wednesday |  |  | Probable max. temperature in Dhaka |  |  | 29.0° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 10300 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 10703 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 9300 | MW
4 | Reserve(Generation end) |  |  |  | 403 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 210.5539 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 6996 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 19.0865 | MKWHr. | ii) HVDC Flow at Peak Time |  | 658 | MW at | 20:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.5315 | MKWHr. | iii) Maximum HVDC Flow : |  | 908 | MW at | 7:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 84.39 |  | (b) Today: | 84.27 |  | (c) Rule Curve: |  | 98.6
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2023-01-24
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 204 | 0 | 0 | 74 | 0 | 387 | 282 |  | 0 | 0 | 150 | 9 | 0 | 15 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 22 | 28 | 33 | 25 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 |  | 6 | 0 | 0 | 22 | 0 | 39 | 0 | 17 | 0 | 0 | 0 | 280 | 0 | 220 | 8 | 0 | 10 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 33 | 15 | 90 | 111 | 0 | 19 | 0 | 30 | 43 | 22 | 20 | 0 | 0 | 64 | 10 | 0 | 140 | 20 | 0 | 10 | 260 | 0 | 0 | 0 | 30 | 0 | 0 | 37 | 0 | 16 | 0 | 25 | 0 | 5 | 366 | 8 | 34 | 61 | 0 | 16 | 17 | 56 | 0 | 9 | 25 | 400 | 0 | 0 | 17 | 34 | 0 | 0 | 0 | 36 | 17 | 325 | 0 | 0 |  | 772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 82 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 340 | 0 | 0 | 35 | 0 | 35 | 0 | 0 | 35 | 1050 | 160 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4638 | 3211 | 7849 | 3422 | 772 | 1453 | 0 | 700 | 1382 | 30 | 0 | 0 | 90 | 0 | 0 | 84.41
2:00 | 0 | 0 | 210 | 0 | 0 | 74 | 0 | 355 | 277 |  | 0 | 0 | 150 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 22 | 28 | 33 | 25 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 |  | 6 | 0 | 0 | 22 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 275 | 0 | 182 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 33 | 15 | 88 | 110 | 0 | 19 | 0 | 30 | 43 | 22 | 20 | 0 | 0 | 64 | 10 | 0 | 140 | 20 | 0 | 10 | 270 | 0 | 0 | 0 | 30 | 0 | 0 | 37 | 0 | 16 | 0 | 25 | 0 | 6 | 364 | 0 | 34 | 38 | 0 | 16 | 17 | 55 | 0 | 0 | 0 | 400 | 0 | 0 | 17 | 34 | 0 | 0 | 0 | 35 | 0 | 325 | 0 | 0 |  | 772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 81 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 970 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4411 | 2968 | 7379 | 3294 | 772 | 1473 | 0 | 421 | 1301 | 30 | 0 | 0 | 88 | 0 | 0 | 84.41
3:00 | 0 | 0 | 160 | 0 | 0 | 73 | 0 | 353 | 286 |  | 0 | 0 | 150 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 22 | 28 | 33 | 25 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 275 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 21 | 8 | 33 | 15 | 84 | 110 | 0 | 19 | 0 | 30 | 43 | 11 | 10 | 0 | 0 | 63 | 10 | 0 | 140 | 20 | 0 | 10 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 6 | 366 | 0 | 17 | 34 | 0 | 16 | 17 | 55 | 0 | 0 | 0 | 370 | 0 | 0 | 17 | 34 | 0 | 0 | 0 | 36 | 0 | 317 | 0 | 0 |  | 772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 81 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 950 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4174 | 2925 | 7099 | 3203 | 772 | 1421 | 0 | 308 | 1281 | 30 | 0 | 0 | 84 | 0 | 0 | 84.4
4:00 | 0 | 0 | 160 | 0 | 0 | 32 | 0 | 353 | 289 |  | 0 | 0 | 150 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 22 | 28 | 33 | 25 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 275 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 21 | 8 | 33 | 15 | 84 | 111 | 0 | 19 | 0 | 30 | 43 | 11 | 10 | 0 | 0 | 63 | 10 | 0 | 140 | 20 | 0 | 10 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 6 | 365 | 0 | 17 | 34 | 0 | 16 | 17 | 17 | 0 | 0 | 0 | 370 | 0 | 0 | 17 | 17 | 0 | 0 | 0 | 17 | 0 | 317 | 0 | 0 |  | 761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 82 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 960 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4066 | 2886 | 6952 | 3202 | 761 | 1348 | 0 | 235 | 1292 | 30 | 0 | 0 | 84 | 0 | 0 | 84.4
5:00 | 0 | 0 | 160 | 0 | 0 | 32 | 0 | 352 | 287 |  | 0 | 0 | 150 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 22 | 28 | 33 | 25 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 275 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 21 | 8 | 33 | 15 | 84 | 110 | 0 | 19 | 0 | 30 | 43 | 11 | 10 | 0 | 0 | 63 | 10 | 0 | 140 | 20 | 0 | 10 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 6 | 365 | 0 | 17 | 34 | 0 | 16 | 17 | 17 | 0 | 0 | 0 | 370 | 0 | 0 | 17 | 17 | 0 | 0 | 0 | 17 | 0 | 317 | 0 | 0 |  | 761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 81 | 0 | 251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 950 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4053 | 2876 | 6929 | 3201 | 761 | 1336 | 0 | 235 | 1282 | 30 | 0 | 0 | 84 | 0 | 0 | 84.39
6:00 | 0 | 0 | 160 | 0 | 0 | 65 | 0 | 352 | 285 |  | 0 | 0 | 150 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 22 | 28 | 33 | 25 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 340 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 21 | 8 | 33 | 15 | 92 | 110 | 0 | 19 | 0 | 30 | 43 | 11 | 10 | 0 | 0 | 62 | 10 | 0 | 140 | 20 | 0 | 10 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 5 | 396 | 0 | 17 | 34 | 0 | 16 | 17 | 20 | 0 | 0 | 0 | 400 | 0 | 0 | 17 | 18 | 0 | 0 | 0 | 20 | 0 | 345 | 0 | 0 |  | 761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 80 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 970 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4309 | 2895 | 7204 | 3374 | 761 | 1407 | 0 | 240 | 1300 | 30 | 0 | 0 | 92 | 0 | 0 | 84.39
7:00 | 0 | 0 | 160 | 0 | 0 | 74 | 0 | 377 | 283 |  | 0 | 0 | 150 | 8 | 0 | 2 | 0 | 0 | 0 | 0 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 22 | 29 | 33 | 25 | 8 | 0 | 30 | 0 | 0 | 0 | 1 | 228 | 0 | 0 | 0 |  | 6 | 0 | 0 | 22 | 0 | 2 | 0 | 38 | 0 | 0 | 0 | 330 | 0 | 196 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 21 | 8 | 25 | 15 | 90 | 54 | 0 | 17 | 0 | 30 | 43 | 11 | 10 | 0 | 0 | 63 | 10 | 0 | 140 | 20 | 0 | 10 | 310 | 0 | 0 | 0 | 15 | 0 | 0 | 46 | 0 | 5 | 1 | 25 | 0 | 6 | 362 | 28 | 34 | 34 | 0 | 16 | 17 | 51 | 11 | 5 | 17 | 400 | 1 | 0 | 17 | 34 | 0 | 0 | 0 | 36 | 15 | 360 | 0 | 0 |  | 908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 81 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 154 | 0 | 415 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 1020 | 220 | 0 | 0 | 0 | 1 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4540 | 3328 | 7868 | 3327 | 908 | 1615 | 0 | 529 | 1351 | 30 | 0 | 16 | 90 | 2 | 149.2951 | 84.39
8:00 | 0 | 0 | 160 | 0 | 0 | 74 | 0 | 392 | 265 |  | 0 | 0 | 150 | 9 | 0 | 15 | 0 | 0 | 0 | 0 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 22 | 3 | 33 | 8 | 8 | 0 | 30 | 0 | 0 | 0 | 8 | 228 | 0 | 0 | 0 |  | 6 | 4 | 0 | 22 | 0 | 24 | 0 | 23 | 0 | 0 | 0 | 320 | 0 | 205 | 0 | 0 | 10 | 0 | 0 | 43 | 0 | 0 | 0 | 21 | 8 | 21 | 15 | 100 | 53 | 0 | 19 | 0 | 30 | 43 | 11 | 10 | 0 | 0 | 63 | 10 | 0 | 140 | 19 | 0 | 10 | 290 | 0 | 0 | 0 | 30 | 0 | 0 | 47 | 0 | 17 | 7 | 25 | 0 | 6 | 380 | 28 | 34 | 34 | 1 | 16 | 17 | 51 | 17 | 9 | 25 | 400 | 11 | 0 | 17 | 34 | 0 | 12 | 3 | 36 | 0 | 360 | 0 | 0 |  | 784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 8 | 0 | 21 | 0 | 8 | 80 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 213 | 0 | 420 | 0 | 0 | 0 | 15 | 0 | 0 | 1 | 0 | 1130 | 220 | 0 | 0 | 0 | 10 | 115 | 0 | 0 | 0 | 4 | 0 | 0 | 22 |  | 4583 | 3523 | 8106 | 3361 | 784 | 1566 | 0 | 737 | 1460 | 30 | 0 | 20 | 100 | 48 | 409.1793 | 84.38
9:00 | 0 | 0 | 160 | 0 | 0 | 74 | 0 | 397 | 268 |  | 0 | 0 | 152 | 8 | 0 | 15 | 0 | 0 | 0 | 0 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 22 | 9 | 33 | 25 | 8 | 0 | 30 | 0 | 0 | 0 | 8 | 237 | 0 | 0 | 0 |  | 6 | 23 | 0 | 22 | 0 | 26 | 0 | 6 | 0 | 0 | 0 | 305 | 0 | 183 | 0 | 0 | 10 | 0 | 0 | 43 | 0 | 0 | 0 | 21 | 8 | 14 | 15 | 110 | 53 | 0 | 19 | 1 | 30 | 43 | 11 | 10 | 0 | 0 | 63 | 10 | 0 | 122 | 19 | 0 | 10 | 290 | 0 | 0 | 0 | 32 | 0 | 0 | 47 | 0 | 17 | 13 | 25 | 0 | 6 | 362 | 28 | 34 | 37 | 2 | 100 | 17 | 55 | 17 | 9 | 25 | 400 | 14 | 0 | 17 | 34 | 0 | 0 | 0 | 36 | 0 | 387 | 0 | 0 |  | 600 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 8 | 0 | 21 | 0 | 8 | 82 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 208 | 0 | 420 | 0 | 0 | 0 | 15 | 40 | 0 | 2 | 0 | 1170 | 220 | 0 | 0 | 2 | 23 | 115 | 0 | 0 | 0 | 10 | 0 | 0 | 58 |  | 4674 | 3488 | 8162 | 3339 | 600 | 1553 | 0 | 878 | 1502 | 30 | 0 | 39 | 110 | 111 | 634.0436 | 84.37
10:00 | 0 | 0 | 160 | 0 | 0 | 74 | 0 | 393 | 273 |  | 0 | 0 | 150 | 9 | 0 | 15 | 0 | 0 | 0 | 0 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 16 | 22 | 9 | 33 | 17 | 8 | 0 | 30 | 0 | 0 | 0 | 8 | 234 | 0 | 0 | 0 |  | 6 | 23 | 0 | 22 | 2 | 27 | 0 | 2 | 0 | 0 | 0 | 350 | 0 | 210 | 8 | 0 | 10 | 0 | 0 | 43 | 0 | 0 | 0 | 21 | 8 | 14 | 15 | 110 | 47 | 0 | 19 | 1 | 30 | 43 | 11 | 10 | 0 | 0 | 61 | 10 | 0 | 20 | 18 | 0 | 10 | 310 | 0 | 0 | 0 | 32 | 0 | 0 | 46 | 0 | 17 | 18 | 25 | 0 | 5 | 408 | 28 | 34 | 48 | 3 | 100 | 17 | 55 | 17 | 9 | 25 | 400 | 0 | 0 | 17 | 34 | 0 | 0 | 13 | 36 | 0 | 393 | 0 | 0 |  | 588 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 8 | 0 | 20 | 0 | 8 | 81 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 206 | 0 | 423 | 0 | 0 | 0 | 15 | 40 | 0 | 3 | 0 | 1172 | 220 | 0 | 0 | 2 | 36 | 35 | 0 | 0 | 0 | 18 | 0 | 0 | 94 |  | 4750 | 3476 | 8226 | 3347 | 588 | 1582 | 0 | 839 | 1503 | 30 | 0 | 39 | 110 | 188 | 667.2203 | 84.37
11:00 | 0 | 0 | 130 | 0 | 0 | 74 | 0 | 393 | 265 |  | 0 | 0 | 152 | 9 | 0 | 15 | 0 | 0 | 0 | 0 | 8 | 48 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 19 | 22 | 9 | 33 | 25 | 8 | 0 | 30 | 0 | 0 | 0 | 8 | 235 | 0 | 0 | 0 |  | 6 | 31 | 0 | 22 | 5 | 32 | 0 | 2 | 0 | 0 | 0 | 310 | 0 | 183 | 8 | 0 | 10 | 0 | 0 | 43 | 0 | 0 | 0 | 21 | 8 | 13 | 15 | 110 | 47 | 0 | 19 | 2 | 30 | 43 | 48 | 44 | 0 | 0 | 62 | 60 | 0 | 25 | 18 | 0 | 10 | 300 | 0 | 0 | 0 | 32 | 0 | 0 | 47 | 0 | 17 | 20 | 25 | 0 | 6 | 366 | 28 | 34 | 51 | 4 | 110 | 17 | 55 | 17 | 9 | 25 | 400 | 2 | 0 | 17 | 34 | 0 | 4 | 17 | 36 | 0 | 316 | 7 | 0 |  | 676 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 25 | 10 | 8 | 0 | 18 | 0 | 8 | 80 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 205 | 0 | 417 | 0 | 0 | 0 | 0 | 40 | 0 | 4 | 35 | 1142 | 220 | 0 | 33 | 3 | 47 | 35 | 0 | 0 | 0 | 23 | 0 | 0 | 122 |  | 4758 | 3672 | 8430 | 3147 | 676 | 1676 | 0 | 939 | 1472 | 30 | 7 | 131 | 110 | 242 | 617.4553 | 84.36
12:00 | 0 | 0 | 120 | 0 | 0 | 75 | 0 | 391 | 252 |  | 0 | 0 | 152 | 8 | 0 | 25 | 0 | 0 | 0 | 0 | 8 | 48 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 19 | 22 | 9 | 33 | 25 | 8 | 0 | 30 | 0 | 0 | 0 | 8 | 229 | 0 | 0 | 0 |  | 6 | 31 | 48 | 22 | 0 | 33 | 0 | 2 | 0 | 0 | 0 | 310 | 0 | 186 | 8 | 0 | 10 | 0 | 0 | 43 | 0 | 13 | 0 | 20 | 8 | 13 | 15 | 116 | 44 | 0 | 19 | 2 | 30 | 43 | 48 | 43 | 0 | 0 | 61 | 60 | 0 | 25 | 18 | 0 | 10 | 310 | 0 | 0 | 0 | 32 | 0 | 0 | 58 | 0 | 17 | 20 | 25 | 0 | 6 | 363 | 28 | 34 | 51 | 4 | 112 | 17 | 62 | 17 | 9 | 25 | 400 | 16 | 0 | 35 | 34 | 0 | 17 | 19 | 36 | 1 | 345 | 18 | 0 |  | 811 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 20 | 0 | 0 | 0 | 0 | 0 | 4 | 42 | 0 | 25 | 16 | 0 | 9 | 18 | 0 | 8 | 83 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 199 | 0 | 388 | 0 | 0 | 11 | 0 | 37 | 0 | 5 | 35 | 1100 | 175 | 0 | 54 | 4 | 56 | 35 | 0 | 0 | 0 | 26 | 0 | 0 | 138 |  | 4912 | 3763 | 8675 | 3147 | 811 | 1604 | 0 | 1031 | 1433 | 30 | 18 | 211 | 116 | 274 | 529.9056 | 84.36
13:00 | 0 | 0 | 120 | 0 | 0 | 75 | 0 | 392 | 252 |  | 0 | 0 | 152 | 9 | 0 | 25 | 0 | 0 | 0 | 0 | 8 | 48 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 19 | 22 | 0 | 33 | 25 | 8 | 0 | 30 | 0 | 0 | 0 | 8 | 227 | 0 | 0 | 0 |  | 6 | 31 | 68 | 22 | 0 | 33 | 0 | 2 | 0 | 0 | 0 | 310 | 0 | 183 | 8 | 0 | 10 | 0 | 0 | 43 | 0 | 20 | 0 | 20 | 8 | 8 | 15 | 116 | 43 | 0 | 19 | 2 | 30 | 43 | 48 | 43 | 0 | 0 | 60 | 60 | 0 | 25 | 18 | 0 | 10 | 280 | 0 | 0 | 0 | 33 | 0 | 0 | 48 | 0 | 17 | 20 | 25 | 7 | 6 | 366 | 28 | 34 | 51 | 4 | 113 | 17 | 72 | 17 | 9 | 25 | 400 | 17 | 0 | 17 | 34 | 0 | 17 | 18 | 35 | 17 | 347 | 13 | 0 |  | 907 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 21 | 0 | 0 | 0 | 0 | 32 | 4 | 42 | 0 | 25 | 18 | 0 | 21 | 18 | 0 | 8 | 82 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 194 | 0 | 370 | 0 | 0 | 50 | 0 | 40 | 0 | 5 | 35 | 1080 | 200 | 0 | 54 | 3 | 57 | 35 | 0 | 0 | 0 | 26 | 0 | 0 | 134 |  | 4896 | 3925 | 8821 | 3127 | 907 | 1582 | 0 | 1081 | 1412 | 30 | 13 | 284 | 116 | 269 | 649.7104 | 84.35
14:00 | 0 | 0 | 120 | 0 | 0 | 72 | 0 | 391 | 241 |  | 0 | 0 | 153 | 8 | 0 | 15 | 0 | 0 | 0 | 0 | 8 | 48 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 19 | 22 | 3 | 33 | 25 | 8 | 0 | 30 | 0 | 0 | 0 | 8 | 226 | 0 | 0 | 0 |  | 6 | 31 | 68 | 22 | 0 | 33 | 0 | 2 | 0 | 0 | 0 | 310 | 0 | 184 | 8 | 0 | 10 | 0 | 0 | 51 | 0 | 20 | 0 | 20 | 8 | 13 | 9 | 116 | 33 | 0 | 19 | 1 | 30 | 43 | 48 | 43 | 0 | 0 | 61 | 60 | 0 | 20 | 18 | 0 | 10 | 280 | 0 | 0 | 0 | 32 | 0 | 0 | 58 | 0 | 17 | 18 | 25 | 0 | 6 | 366 | 28 | 34 | 51 | 3 | 113 | 17 | 72 | 17 | 8 | 25 | 400 | 17 | 0 | 17 | 34 | 0 | 17 | 17 | 36 | 17 | 346 | 9 | 0 |  | 906 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 20 | 0 | 0 | 0 | 0 | 31 | 13 | 42 | 0 | 25 | 32 | 0 | 35 | 18 | 0 | 8 | 82 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 192 | 0 | 350 | 0 | 0 | 35 | 0 | 35 | 0 | 5 | 35 | 1090 | 218 | 0 | 54 | 3 | 52 | 35 | 0 | 0 | 0 | 22 | 0 | 0 | 116 |  | 4859 | 3915 | 8774 | 3108 | 906 | 1574 | 0 | 1052 | 1422 | 30 | 9 | 320 | 116 | 237 | 439.5913 | 84.36
15:00 | 0 | 0 | 120 | 0 | 0 | 72 | 0 | 392 | 250 |  | 0 | 0 | 152 | 9 | 0 | 15 | 0 | 0 | 0 | 0 | 8 | 48 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 19 | 22 | 9 | 33 | 25 | 8 | 0 | 30 | 0 | 0 | 0 | 8 | 223 | 0 | 0 | 0 |  | 6 | 30 | 68 | 22 | 0 | 33 | 0 | 2 | 0 | 0 | 0 | 310 | 0 | 184 | 8 | 0 | 10 | 0 | 0 | 51 | 0 | 20 | 0 | 20 | 8 | 14 | 15 | 114 | 33 | 0 | 19 | 1 | 30 | 43 | 48 | 45 | 0 | 0 | 61 | 60 | 0 | 75 | 18 | 0 | 10 | 280 | 0 | 0 | 0 | 32 | 0 | 0 | 58 | 0 | 17 | 14 | 25 | 0 | 6 | 365 | 28 | 34 | 51 | 2 | 121 | 17 | 78 | 34 | 17 | 25 | 400 | 17 | 0 | 17 | 34 | 0 | 17 | 11 | 36 | 17 | 337 | 0 | 0 |  | 902 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 17 | 0 | 0 | 0 | 0 | 26 | 13 | 0 | 0 | 0 | 0 | 0 | 35 | 18 | 0 | 8 | 81 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 1070 | 218 | 0 | 54 | 2 | 36 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 76 |  | 4943 | 3565 | 8508 | 3162 | 902 | 1571 | 0 | 928 | 1401 | 30 | 0 | 240 | 114 | 160 | 430.3755 | 84.34
16:00 | 0 | 0 | 116 | 0 | 0 | 74 | 0 | 385 | 244 |  | 0 | 0 | 155 | 9 | 0 | 15 | 0 | 0 | 0 | 1 | 16 | 48 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 19 | 22 | 9 | 33 | 30 | 10 | 0 | 30 | 0 | 0 | 0 | 10 | 221 | 0 | 0 | 0 |  | 6 | 29 | 68 | 22 | 3 | 33 | 0 | 2 | 0 | 0 | 0 | 355 | 0 | 204 | 8 | 0 | 10 | 0 | 0 | 51 | 0 | 20 | 4 | 20 | 8 | 14 | 15 | 110 | 35 | 0 | 19 | 1 | 30 | 43 | 48 | 46 | 0 | 0 | 60 | 60 | 0 | 88 | 18 | 0 | 10 | 300 | 0 | 0 | 0 | 32 | 0 | 0 | 48 | 0 | 17 | 7 | 25 | 0 | 5 | 397 | 28 | 88 | 53 | 1 | 103 | 17 | 91 | 34 | 68 | 25 | 400 | 17 | 0 | 17 | 34 | 0 | 17 | 6 | 36 | 17 | 337 | 0 | 0 |  | 902 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 16 | 0 | 0 | 0 | 0 | 26 | 20 | 0 | 0 | 0 | 0 | 0 | 30 | 18 | 0 | 8 | 82 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191 | 0 | 328 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 1070 | 218 | 0 | 17 | 1 | 18 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 37 |  | 5176 | 3431 | 8607 | 3260 | 902 | 1578 | 0 | 1003 | 1402 | 30 | 0 | 241 | 110 | 81 | 249.7468 | 84.34
17:00 | 0 | 0 | 120 | 0 | 0 | 76 | 0 | 382 | 242 |  | 0 | 0 | 150 | 17 | 0 | 15 | 0 | 0 | 0 | 8 | 16 | 48 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 0 | 22 | 14 | 33 | 30 | 16 | 0 | 30 | 0 | 0 | 0 | 17 | 224 | 0 | 0 | 0 |  | 6 | 29 | 68 | 22 | 11 | 33 | 0 | 2 | 0 | 0 | 0 | 305 | 0 | 70 | 8 | 0 | 10 | 3 | 0 | 51 | 0 | 26 | 8 | 20 | 8 | 14 | 15 | 114 | 51 | 0 | 19 | 0 | 30 | 43 | 48 | 49 | 0 | 0 | 62 | 60 | 0 | 88 | 18 | 0 | 10 | 310 | 0 | 0 | 0 | 35 | 0 | 0 | 48 | 0 | 18 | 2 | 25 | 2 | 6 | 367 | 28 | 88 | 68 | 0 | 104 | 17 | 91 | 52 | 104 | 25 | 390 | 17 | 0 | 17 | 51 | 0 | 17 | 2 | 66 | 17 | 347 | 7 | 0 |  | 903 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 43 | 8 | 181 | 17 | 0 | 0 | 0 | 0 | 26 | 19 | 47 | 0 | 0 | 14 | 0 | 30 | 18 | 0 | 8 | 81 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 192 | 0 | 324 | 0 | 0 | 4 | 0 | 56 | 0 | 1 | 60 | 1100 | 218 | 0 | 17 | 0 | 4 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 9 |  | 5151 | 3649 | 8800 | 3063 | 903 | 1586 | 0 | 1296 | 1431 | 30 | 7 | 350 | 114 | 20 | 270.0215 | 84.33
18:00 | 0 | 0 | 117 | 0 | 0 | 76 | 0 | 372 | 240 |  | 0 | 0 | 152 | 17 | 0 | 15 | 0 | 0 | 0 | 8 | 16 | 48 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 19 | 22 | 28 | 33 | 30 | 17 | 0 | 30 | 0 | 0 | 0 | 17 | 224 | 0 | 0 | 0 |  | 6 | 23 | 68 | 22 | 12 | 33 | 0 | 2 | 0 | 0 | 0 | 310 | 0 | 70 | 8 | 0 | 10 | 20 | 0 | 51 | 0 | 30 | 8 | 21 | 8 | 14 | 15 | 132 | 30 | 0 | 19 | 0 | 30 | 43 | 48 | 50 | 0 | 0 | 62 | 86 | 0 | 112 | 18 | 0 | 10 | 270 | 0 | 0 | 0 | 65 | 0 | 0 | 57 | 0 | 30 | 0 | 25 | 15 | 6 | 367 | 47 | 88 | 68 | 0 | 278 | 17 | 91 | 52 | 105 | 25 | 360 | 17 | 0 | 17 | 60 | 0 | 17 | 0 | 94 | 17 | 357 | 0 | 0 |  | 826 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 50 | 86 | 8 | 177 | 24 | 8 | 0 | 0 | 0 | 34 | 19 | 96 | 0 | 25 | 30 | 8 | 30 | 19 | 0 | 8 | 81 | 0 | 251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 195 | 0 | 277 | 0 | 0 | 60 | 7 | 74 | 0 | 0 | 95 | 1100 | 209 | 0 | 54 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5466 | 3916 | 9382 | 3071 | 826 | 1542 | 0 | 1835 | 1432 | 30 | 0 | 514 | 132 | 0 | 480 | 84.33
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 192 | 0 | 0 | 76 | 0 | 371 | 238 |  | 0 | 0 | 154 | 10 | 0 | 15 | 0 | 0 | 0 | 8 | 16 | 48 | 0 | 0 | 0 | 0 | 54 | 35 | 17 | 19 | 22 | 28 | 33 | 30 | 17 | 0 | 30 | 0 | 0 | 0 | 17 | 223 | 0 | 0 | 0 |  | 6 | 32 | 68 | 22 | 0 | 33 | 0 | 2 | 0 | 0 | 0 | 310 | 0 | 115 | 8 | 0 | 10 | 30 | 0 | 51 | 0 | 28 | 8 | 21 | 8 | 16 | 15 | 118 | 43 | 0 | 19 | 0 | 30 | 43 | 48 | 50 | 0 | 0 | 62 | 86 | 0 | 118 | 19 | 0 | 10 | 290 | 0 | 0 | 0 | 65 | 0 | 0 | 57 | 0 | 35 | 0 | 25 | 17 | 6 | 366 | 47 | 88 | 68 | 0 | 278 | 17 | 91 | 52 | 101 | 25 | 400 | 17 | 0 | 17 | 68 | 0 | 17 | 0 | 94 | 17 | 367 | 0 | 0 |  | 642 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 43 | 78 | 8 | 179 | 24 | 16 | 0 | 0 | 0 | 34 | 19 | 97 | 0 | 25 | 35 | 8 | 30 | 21 | 0 | 8 | 81 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 198 | 0 | 341 | 0 | 0 | 92 | 53 | 85 | 0 | 0 | 95 | 1150 | 220 | 0 | 100 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5707 | 4061 | 9768 | 3265 | 642 | 1649 | 0 | 2071 | 1481 | 30 | 0 | 512 | 118 | 0 | 500.4152 | 84.31
19:30 | 0 | 0 | 210 | 0 | 0 | 76 | 0 | 366 | 233 |  | 0 | 0 | 152 | 9 | 0 | 15 | 0 | 0 | 0 | 8 | 16 | 48 | 0 | 0 | 0 | 0 | 54 | 35 | 17 | 19 | 22 | 28 | 33 | 30 | 17 | 0 | 30 | 0 | 0 | 0 | 17 | 224 | 0 | 0 | 0 |  | 6 | 32 | 68 | 22 | 0 | 33 | 0 | 3 | 0 | 0 | 0 | 325 | 0 | 169 | 8 | 0 | 10 | 30 | 0 | 51 | 0 | 28 | 8 | 21 | 8 | 16 | 15 | 116 | 60 | 0 | 19 | 0 | 30 | 43 | 51 | 50 | 0 | 0 | 62 | 86 | 0 | 0 | 19 | 0 | 10 | 305 | 0 | 0 | 50 | 65 | 0 | 0 | 48 | 0 | 35 | 0 | 25 | 17 | 6 | 365 | 47 | 88 | 68 | 0 | 282 | 17 | 92 | 52 | 107 | 25 | 400 | 17 | 0 | 17 | 68 | 0 | 17 | 0 | 94 | 17 | 357 | 0 | 0 |  | 670 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 43 | 75 | 8 | 182 | 24 | 16 | 0 | 0 | 0 | 26 | 19 | 97 | 0 | 34 | 40 | 8 | 30 | 21 | 0 | 8 | 82 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 198 | 0 | 341 | 0 | 0 | 94 | 105 | 85 | 0 | 0 | 95 | 1192 | 220 | 0 | 134 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5739 | 4226 | 9965 | 3239 | 670 | 1661 | 50 | 2169 | 1524 | 30 | 0 | 506 | 116 | 0 | 230.3937 | 0
20:00 | 0 | 0 | 210 | 0 | 0 | 76 | 0 | 366 | 233 |  | 0 | 0 | 152 | 8 | 0 | 15 | 0 | 0 | 0 | 8 | 16 | 48 | 0 | 0 | 0 | 0 | 54 | 35 | 17 | 19 | 22 | 28 | 33 | 30 | 17 | 0 | 30 | 0 | 0 | 0 | 17 | 230 | 0 | 0 | 0 |  | 6 | 32 | 68 | 22 | 0 | 32 | 0 | 2 | 0 | 0 | 0 | 310 | 0 | 210 | 8 | 0 | 10 | 40 | 0 | 51 | 0 | 28 | 8 | 21 | 8 | 24 | 15 | 118 | 54 | 0 | 19 | 0 | 30 | 43 | 51 | 50 | 0 | 0 | 62 | 86 | 0 | 135 | 19 | 0 | 10 | 300 | 0 | 0 | 10 | 65 | 0 | 0 | 48 | 0 | 30 | 0 | 25 | 17 | 6 | 366 | 47 | 88 | 68 | 0 | 283 | 17 | 92 | 52 | 108 | 25 | 400 | 17 | 0 | 17 | 68 | 0 | 17 | 0 | 94 | 17 | 347 | 0 | 0 |  | 658 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 43 | 75 | 8 | 184 | 25 | 16 | 0 | 0 | 0 | 26 | 21 | 97 | 0 | 34 | 41 | 8 | 30 | 21 | 0 | 8 | 82 | 0 | 251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 199 | 0 | 341 | 0 | 0 | 94 | 105 | 85 | 0 | 0 | 95 | 1192 | 220 | 0 | 150 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5860 | 4238 | 10098 | 3402 | 658 | 1666 | 10 | 2180 | 1525 | 30 | 0 | 509 | 118 | 0 | 179.7071 | 84.32
21:00 | 0 | 0 | 206 | 0 | 0 | 76 | 0 | 365 | 220 |  | 0 | 0 | 152 | 9 | 0 | 15 | 0 | 0 | 0 | 8 | 16 | 48 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 19 | 22 | 28 | 33 | 30 | 17 | 0 | 30 | 0 | 0 | 0 | 17 | 230 | 0 | 0 | 0 |  | 6 | 32 | 68 | 22 | 0 | 33 | 0 | 9 | 0 | 0 | 0 | 310 | 0 | 201 | 8 | 0 | 10 | 20 | 0 | 51 | 0 | 28 | 8 | 21 | 8 | 24 | 15 | 112 | 68 | 0 | 19 | 0 | 30 | 43 | 22 | 20 | 0 | 0 | 62 | 86 | 0 | 156 | 19 | 0 | 10 | 310 | 0 | 0 | 100 | 65 | 0 | 0 | 48 | 0 | 35 | 0 | 25 | 17 | 6 | 365 | 47 | 88 | 68 | 0 | 69 | 17 | 92 | 63 | 106 | 25 | 400 | 17 | 0 | 17 | 68 | 0 | 17 | 0 | 94 | 17 | 317 | 0 | 0 |  | 733 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 38 | 70 | 8 | 186 | 24 | 16 | 0 | 0 | 0 | 26 | 21 | 97 | 0 | 34 | 40 | 8 | 30 | 21 | 0 | 8 | 82 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202 | 0 | 433 | 17 | 0 | 94 | 105 | 85 | 0 | 0 | 95 | 1202 | 220 | 0 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5624 | 4274 | 9898 | 3397 | 733 | 1682 | 100 | 1812 | 1534 | 30 | 0 | 498 | 112 | 0 | 190.766 | 84.31
22:00 | 0 | 0 | 210 | 0 | 0 | 76 | 0 | 360 | 222 |  | 0 | 0 | 152 | 9 | 0 | 15 | 0 | 0 | 0 | 8 | 16 | 48 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 19 | 22 | 28 | 33 | 30 | 17 | 0 | 30 | 0 | 0 | 0 | 17 | 229 | 0 | 0 | 0 |  | 6 | 32 | 68 | 22 | 0 | 33 | 0 | 16 | 0 | 0 | 0 | 305 | 0 | 201 | 8 | 0 | 10 | 20 | 0 | 51 | 0 | 29 | 8 | 21 | 8 | 28 | 15 | 114 | 71 | 0 | 19 | 0 | 30 | 43 | 22 | 20 | 0 | 0 | 63 | 86 | 0 | 156 | 20 | 0 | 10 | 290 | 0 | 0 | 0 | 65 | 0 | 0 | 48 | 0 | 35 | 0 | 25 | 17 | 5 | 366 | 47 | 88 | 68 | 0 | 16 | 17 | 92 | 63 | 107 | 25 | 400 | 17 | 0 | 17 | 68 | 0 | 17 | 0 | 89 | 17 | 297 | 0 | 0 |  | 907 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 8 | 0 | 21 | 0 | 8 | 82 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 205 | 0 | 446 | 17 | 0 | 94 | 67 | 70 | 0 | 0 | 95 | 1192 | 220 | 0 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5441 | 4055 | 9496 | 3385 | 907 | 1684 | 0 | 1675 | 1524 | 30 | 0 | 177 | 114 | 0 | 148.3736 | 84.31
23:00 | 0 | 0 | 210 | 0 | 0 | 76 | 0 | 359 | 205 |  | 0 | 0 | 152 | 8 | 0 | 15 | 0 | 0 | 0 | 0 | 16 | 48 | 0 | 0 | 0 | 0 | 17 | 0 | 17 | 19 | 22 | 28 | 33 | 30 | 8 | 0 | 30 | 0 | 0 | 0 | 8 | 231 | 0 | 0 | 0 |  | 6 | 0 | 68 | 22 | 0 | 34 | 0 | 17 | 0 | 0 | 0 | 305 | 0 | 191 | 8 | 0 | 10 | 20 | 0 | 51 | 0 | 13 | 8 | 21 | 8 | 33 | 15 | 100 | 72 | 0 | 19 | 0 | 30 | 43 | 22 | 20 | 0 | 0 | 63 | 86 | 0 | 157 | 19 | 0 | 10 | 270 | 0 | 0 | 0 | 30 | 0 | 0 | 48 | 0 | 22 | 0 | 25 | 17 | 6 | 366 | 47 | 34 | 68 | 0 | 16 | 17 | 65 | 63 | 64 | 25 | 400 | 10 | 0 | 17 | 68 | 0 | 17 | 0 | 49 | 17 | 320 | 0 | 0 |  | 907 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 8 | 0 | 21 | 0 | 8 | 83 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 209 | 0 | 436 | 17 | 0 | 35 | 58 | 34 | 0 | 0 | 35 | 1130 | 220 | 0 | 54 | 0 | 0 | 114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5084 | 3879 | 8963 | 3409 | 907 | 1638 | 0 | 1287 | 1463 | 30 | 0 | 129 | 100 | 0 | 124.4126 | 84.3
24:00 | 0 | 0 | 210 | 0 | 0 | 76 | 0 | 352 | 212 |  | 0 | 0 | 145 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 17 | 19 | 22 | 28 | 33 | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 233 | 0 | 0 | 0 |  | 6 | 0 | 0 | 22 | 0 | 20 | 0 | 15 | 0 | 0 | 0 | 300 | 0 | 197 | 8 | 0 | 10 | 20 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 33 | 15 | 100 | 50 | 0 | 18 | 0 | 30 | 43 | 22 | 20 | 0 | 0 | 63 | 86 | 0 | 157 | 20 | 0 | 10 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 18 | 0 | 25 | 17 | 6 | 366 | 28 | 34 | 68 | 0 | 16 | 17 | 54 | 17 | 15 | 0 | 400 | 17 | 0 | 17 | 75 | 0 | 17 | 0 | 32 | 17 | 307 | 0 | 0 |  | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 22 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 81 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 209 | 0 | 440 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 1130 | 220 | 0 | 54 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4701 | 3633 | 8334 | 3370 | 906 | 1648 | 0 | 803 | 1461 | 30 | 0 | 16 | 100 | 0 | 105 | 84.3
KWH | 0 | 0 | 3938000 | 0 | 0 | 1652863 | 0 | 9084930 | 6126000 |  | 0 | 0 | 3630487 | 216000 | 0 | 314956 | 0 | 0 | 0 | 46080 | 267408 | 719040 | 0 | 0 | 0 | 0 | 201960 | 438214 | 431578 | 363744 | 528000 | 447840 | 820080 | 647500 | 193920 | 0 | 707940 | 0 | 0 | 0 | 196065 | 5442537 | 0 | 0 | 0 |  | 148560 | 428640 | 774599 | 452640 | 41280 | 586080 | 0 | 336480 | 0 | 0 | 0 | 7785700 | 0 | 4318000 | 133818 | 0 | 207504 | 207840 | 0 | 1105173 | 0 | 267696 | 66437 | 493992 | 174780 | 547100 | 337770 | 2531520 | 1489920 | 0 | 443376 | 10050 | 715000 | 978120 | 696000 | 692856 | 0 | 0 | 1495008 | 1146240 | 0 | 3102950 | 444000 | 0 | 251100 | 7066500 | 0 | 0 | 88512 | 812945 | 0 | 0 | 1125600 | 0 | 432288 | 139320 | 517440 | 139200 | 152218 | 8979000 | 630000 | 1151784 | 1286327 | 25801 | 2017309 | 450298 | 1589084 | 616740 | 888720 | 455040 | 9429500 | 241920 | 0 | 466560 | 1050055 | 0 | 280080 | 112721 | 1158720 | 270360 | 8120100 | 46836 | 0 |  | 19086545 | 0 | 0 | 0 | 315840 | 0 | 0 | 0 | 149280 | 329728 | 32625 | 4462405 | 479500 | 98880 | 0 | 0 | 0 | 247748 | 146775 | 572386 | 0 | 307860 | 180648 | 78965 | 280797 | 472320 | 0 | 176796 | 1937018 | 0 | 6060100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4689027 | 0 | 8798545 | 41760 | 0 | 716160 | 467852 | 762691 | 0 | 30219 | 764448 | 28038800 | 4899000 | 0 | 668400 | 24000 | 345600 | 1235328 | 0 | 0 | 0 | 153940 | 0 | 0 | 806290 |  | 118566349 | 87858276 | 206424625 | 79662679 | 19086545 | 37694722 | 88512 | 24824675 | 36035918 | 707940 | 46836 | 4097337 | 2531520 | 1647941 | 0
Fuel Cost | 0 | 0 | 5749480 | 0 | 0 | 2198307.79 | 0 | 9539176.5 | 6616080 |  | 0 | 0 | 4029840.57 | 2414880 | 0 | 4173167 | 0 | 0 | 0 | 673689.6 | 3762430.56 | 11655638.4 | 0 | 0 | 0 | 0 | 2568931.2 | 5915889 | 5787460.98 | 272808 | 396000 | 0 | 0 | 0 | 3298579.2 | 0 | 191143.8 | 0 | 0 | 0 | 3205662.75 | 5660238.48 | 0 | 0 | 0 |  | 1938708 | 7149715.2 | 13183674.98 | 6115166.4 | 523430.4 | 6780945.6 | 0 | 1120478.4 | 0 | 0 | 0 | 8642127 | 0 | 5008880 | 172625.22 | 0 | 234479.52 | 309681.6 | 0 | 1845638.91 | 0 | 4623109.92 | 893577.65 | 676769.04 | 131085 | 957425 | 253327.5 | 18176313.6 | 1624012.8 | 0 | 602991.36 | 160197 | 979550 | 1291118.4 | 1211040 | 1198640.88 | 0 | 0 | 2900315.52 | 2613427.2 | 0 | 3133979.5 | 954600 | 0 | 497178 | 7066500 | 0 | 0 | 1855211.52 | 11096699.25 | 0 | 0 | 15173088 | 0 | 5987188.8 | 1628650.8 | 5339980.8 | 1901472 | 2019932.86 | 8260680 | 7660800 | 16654796.64 | 16272036.55 | 0 | 23683207.66 | 4903745.22 | 16891962.92 | 8369161.8 | 11455600.8 | 5360371.2 | 8675140 | 3132864 | 0 | 5920646.4 | 11949625.9 | 0 | 3657844.8 | 1347015.95 | 17346038.4 | 3560641.2 | 0 | 0 | 0 |  | 57259635 | 0 | 0 | 0 | 3287894.4 | 0 | 0 | 0 | 2688532.8 | 5935104 | 468821.25 | 4997893.6 | 930230 | 1077792 | 0 | 0 | 0 | 4154733.96 | 2567094.75 | 8952117.04 | 0 | 5098161.6 | 3054757.68 | 1076292.95 | 4737045.39 | 977702.4 | 0 | 133834.572 | 11254074.58 | 0 | 32057929 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5439271.32 | 0 | 8710559.55 | 561254.4 | 0 | 8472172.8 | 6760461.4 | 9686175.7 | 0 | 333919.95 | 9280398.72 | 252629588 | 4996980 | 0 | 4946160 | 271440 | 4053888 | 18937578.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 401184516.9 | 485789495.052 | 886974011.952 | 76515183.112 | 57259635 | 44494910.52 | 1855211.52 | 316043387 | 295941591.58 | 191143.8 | 0 | 68701524.12 | 18176313.6 | 7795111.7 | 0
Yesterday Day Peak | 0 | 0 | 120 | 0 | 0 | 75 | 0 | 391 | 252 |  | 0 | 0 | 152 | 8 | 0 | 25 | 0 | 0 | 0 | 0 | 8 | 48 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 19 | 22 | 9 | 33 | 25 | 8 | 0 | 30 | 0 | 0 | 0 | 8 | 229 | 0 | 0 | 0 |  | 6 | 31 | 48 | 22 | 0 | 33 | 0 | 2 | 0 | 0 | 0 | 310 | 0 | 186 | 8 | 0 | 10 | 0 | 0 | 43 | 0 | 13 | 0 | 20 | 8 | 13 | 15 | 116 | 44 | 0 | 19 | 2 | 30 | 43 | 48 | 43 | 0 | 0 | 61 | 60 | 0 | 25 | 18 | 0 | 10 | 310 | 0 | 0 | 0 | 32 | 0 | 0 | 58 | 0 | 17 | 20 | 25 | 0 | 6 | 363 | 28 | 34 | 51 | 4 | 112 | 17 | 62 | 17 | 9 | 25 | 400 | 16 | 0 | 35 | 34 | 0 | 17 | 19 | 36 | 1 | 345 | 18 | 0 |  | 811 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 20 | 0 | 0 | 0 | 0 | 0 | 4 | 42 | 0 | 25 | 16 | 0 | 9 | 18 | 0 | 8 | 83 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 199 | 0 | 388 | 0 | 0 | 11 | 0 | 37 | 0 | 5 | 35 | 1100 | 175 | 0 | 54 | 4 | 56 | 35 | 0 | 0 | 0 | 26 | 0 | 0 | 138 |  | 8675 | DayPeak
Yesterday Evening Peak | 0 | 0 | 210 | 0 | 0 | 76 | 0 | 366 | 233 | 0 | 0 | 0 | 152 | 8 | 0 | 15 | 0 | 0 | 0 | 8 | 16 | 48 | 0 | 0 | 0 | 0 | 54 | 35 | 17 | 19 | 22 | 28 | 33 | 30 | 17 | 0 | 30 | 0 | 0 | 0 | 17 | 230 | 0 | 0 | 0 | 0 | 6 | 32 | 68 | 22 | 0 | 32 | 0 | 2 | 0 | 0 | 0 | 310 | 0 | 210 | 8 | 0 | 10 | 40 | 0 | 51 | 0 | 28 | 8 | 21 | 8 | 24 | 15 | 118 | 54 | 0 | 19 | 0 | 30 | 43 | 51 | 50 | 0 | 0 | 62 | 86 | 0 | 135 | 19 | 0 | 10 | 300 | 0 | 0 | 10 | 65 | 0 | 0 | 48 | 0 | 30 | 0 | 25 | 17 | 6 | 366 | 47 | 88 | 68 | 0 | 283 | 17 | 92 | 52 | 108 | 25 | 400 | 17 | 0 | 17 | 68 | 0 | 17 | 0 | 94 | 17 | 347 | 0 | 0 |  | 658 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 43 | 75 | 8 | 184 | 25 | 16 | 0 | 0 | 0 | 26 | 21 | 97 | 0 | 34 | 41 | 8 | 30 | 21 | 0 | 8 | 82 | 0 | 251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 199 | 0 | 341 | 0 | 0 | 94 | 105 | 85 | 0 | 0 | 95 | 1192 | 220 | 0 | 150 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 10098 | EvPeak
Forecast for Evening | 0 | 0 | 210 | 0 | 0 | 74 | 0 | 350 | 200 | 0 | 0 | 0 | 150 | 8 | 0 | 15 | 0 | 0 | 0 | 8 | 48 | 48 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 22 | 29 | 33 | 30 | 17 | 0 | 30 | 0 | 0 | 0 | 17 | 225 | 0 | 0 | 0 | 0 | 6 | 32 | 68 | 22 | 0 | 33 | 0 | 10 | 0 | 0 | 0 | 320 | 0 | 205 | 8 | 0 | 10 | 5 | 0 | 51 | 0 | 35 | 8 | 21 | 8 | 33 | 15 | 152 | 60 | 0 | 19 | 0 | 30 | 43 | 50 | 50 | 0 | 0 | 62 | 86 | 0 | 0 | 19 | 0 | 10 | 300 | 16 | 8 | 100 | 64 | 0 | 0 | 48 | 0 | 35 | 0 | 25 | 17 | 6 | 400 | 47 | 88 | 68 | 0 | 300 | 17 | 92 | 110 | 113 | 25 | 400 | 17 | 0 | 17 | 107 | 0 | 17 |  | 94 | 17 | 300 |  |  |  | 923 | 0 | 0 |  | 49 | 0 | 0 | 0 | 45 | 75 | 8 | 185 | 25 | 16 | 0 | 0 | 0 | 34 | 42 | 97 | 0 | 42 | 41 | 8 | 35 | 22 | 0 | 8 | 85 | 0 | 250 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 210 | 0 | 415 | 18 | 0 | 94 | 105 | 85 | 0 | 0 | 95 | 1190 | 220 |  | 150 |  |  | 115 | 0 |  | 0 |  | 0 | 0
Forecast for Day | 0 | 0 | 210 | 0 | 0 | 74 | 0 | 350 | 190 | 0 | 0 | 0 | 150 | 8 | 0 | 15 | 0 | 0 | 0 |  | 16 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 19 | 22 | 29 | 33 | 30 | 8 | 0 | 30 | 0 | 0 | 0 | 8 | 225 | 0 | 0 | 0 | 0 | 6 | 32 | 51 | 22 | 0 | 33 | 0 | 5 | 0 | 0 | 0 | 320 | 0 | 200 | 8 | 0 | 10 | 5 | 0 | 51 | 0 | 35 | 8 | 21 | 8 | 33 | 15 | 135 | 50 | 0 | 19 | 1.6 | 30 | 43 | 50 | 50 | 0 | 0 | 62 | 60 | 0 | 0 | 19 | 0 | 10 | 300 | 16 | 8 | 0 | 32 | 0 | 0 | 58 | 0 | 17 | 20 | 25 | 17 | 6 | 400 | 28 | 34 | 34 | 5 | 130 | 17 | 51 | 17 | 9 | 25 | 400 | 17 | 50 | 17 | 107 | 0 | 17 | 30 | 54 | 17 | 300 |  |  |  | 925 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 19 | 16 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 34 | 15 | 8 | 0 | 22 | 0 | 8 | 85 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 210 | 0 | 415 | 0 | 0 | 35 | 50 | 35 | 0 | 8 | 35 | 1150 | 220 |  | 35 | 6 | 100 | 115 | 0 |  | 0 | 30 | 0 |  | 130 |  |  |  |  | g | h | o | c | h | t | s
Generation at 08:00(Today) | 0 | 0 | 210 | 0 | 0 | 74 | 0 | 347 | 193 | 0 | 0 | 0 | 142 | 8 | 0 | 15 | 0 | 0 | 0 | 0 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 22 | 29 | 25 | 31 | 8 | 0 | 30 | 0 | 0 | 0 | 8 | 232 | 0 | 0 | 0 | 0 | 6 | 24 | 0 | 22 | 0 | 25 | 0 | 10 | 0 | 0 | 0 | 360 | 0 | 181 | 8 | 0 | 10 | 20 | 0 | 51 | 0 | 0 | 8 | 21 | 8 | 16 | 15 | 96 | 45 | 0 | 19 | 0 | 30 | 43 | 48 | 50 | 0 | 0 | 62 | 60 | 0 | 0 | 19 | 0 | 9 | 330 | 0 | 0 | 0 | 32 | 0 | 0 | 58 | 0 | 17 | 6 | 25 | 17 | 6 | 433 | 28 | 34 | 34 | 1 | 16 | 17 | 51 | 17 | 9 | 25 | 400 | 17 | 0 | 17 | 107 | 0 | 17 | 3 | 35 | 17 | 287 | 0 | 0 | 0 | 838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 19 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 8 | 0 | 22 | 0 | 8 | 70 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 196 | 0 | 442 | 0 | 0 | 0 | 50 | 28 | 0 | 1 | 0 | 1060 | 214 | 0 | 17 | 0 | 13 | 115 | 0 | 0 | 0 | 5 | 0 | 0 | 28 | 0 |  |  |  | 117.3574 | 19.0865 | 29.0574 | 36.0359 | 0.70794 | 2.5315 | 1.6479
206.4246
| Minimum Generation |  | 6929 | 5:00
| Highest Generation |  | 10098 | 20:00
| Day Peak Generation |  | 8675 | 12:00
| Evening Peak Generation |  | 10098 | 20:00
| HVDC Max Flow |  | 908 | 7:00
| HVDC EvPeak Flow |  | 658 | 20:00
| Load factor L.F |  | 85.18% | [161 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2023-01-25
Till now the maximum generation is : - |  |  |  | 14782 | 21:00 | Hrs on | 2022-04-16
The Summary of Yesterday's |  |  | 2023-01-24 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 8675 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 6996
Evening Peak Generation : |  |  | 10098 | MW Hour : | 20:00 | Available Max Generation : |  | 10703
E.P. Demand (at gen end) : |  |  | 10293 | MW Hour : | 20:00 | Max Demand (Evening) : |  | 10300
Maximum Generation : |  |  | 10098 | MW Hour : | 20:00 | Reserve(Generation end) |  | 403
Total Gen. (MKWH) : |  |  | 206.4246 | System Load Factor : | 85.18% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 850 | MW at | 7:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2023-01-25
Actual : |  | 84.27 | Ft.(MSL) , | Rule curve : | 98.6 | Ft.( MSL )
Gas Consumed : |  | Total = | 861.45 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 121010093.632
: |  |  | Coal : | 295941591.58 | Oil : | 386600122.64 | Total : | 803551807.852
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 30 | 720:00 | 3265.9867 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 925.1972 |  |  | 0 | 0%
Khulna Area |  | 0 | 0:00 | 1221.1835 |  |  | 0 | 0%
Rajshahi Area |  | 0 | 0:00 | 1083.4939 |  |  | 0 | 0%
Cumilla Area |  | 0 | 0:00 | 922.348 |  |  | 0 | 0%
Mymensingh Area |  | 150 | 3600:00 | 761.9973 |  |  | 0 | 0%
Sylhet Area |  | 0 | 0:00 | 340.5797 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 277.6321 |  |  | 0 | 0%
Rangpur Area |  | 0 | 0:00 | 601.6466 |  |  | 0 | 0%
Total |  | 180 |  | 9400.065 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 2
2) Ghorasal-3
3) Ashuganj-5
4) Baghabari-70,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
7) Shajibazar 330 MW
8) Sirajganj-1,2
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
08:15 | 13:04 | Sonargaon 132/33kV S/S Tr-2 LT Scheduled S/D Due to Corrective maintenance work for 33kv side B-phase CT oil | [5 empty] | 30.0MW load interrup.
leakage.
08:15 | 13:04 | Sonargaon 132/33kV S/S Tr-2 HT Scheduled S/D Due to Corrective maintenance work for 33kv side B-phase CT oil | [5 empty] | 30.0MW load interrup.
leakage.
08:16 | 17:07 | Barishal-Patuakhali(Barguna T at Bakergonj) 132 kV Ckt Scheduled S/D from Barguna 132/33kV end Due to Annual
maintenance
08:16 | 17:06 | Patuakhali 132/33kV S/S Barishal-Pautakhali 132kV Line Scheduled S/D Due to Annual Maintenance-2023
08:16 | 17:06 | Patuakhali 132/33kV S/S Barishal-Pautakhali 132kV Line Scheduled S/D Due to Annual Maintenance-2023
08:18 | 17:01 | Ashuganj-Sirajganj 230 kV Ckt-2 Scheduled S/D from Sirajgonj 230 end Due to Annual Maintenance
08:19 | 18:15 | Madaripur-Shariatpur 132kV Ckt-1 Scheduled S/D from Shariatpur 132/33kV end Due to Annual Maintenance and from
Madaripur 132/33kV end Due to Annue Maintenance
08:29 | 13:22 | Beanibazar 132/33kV S/S 132KV Transformer TR-02 LT Scheduled S/D Due to Annual maintenance
08:29 | 16:24 | Bagerhat-Mongla 132 kV Ckt-2 Scheduled S/D from Mongla 132/33kV end Due to Annual maintenance and from Bagerhat
132/33kV end Due to Annual Maintenance Work
08:30 | 13:21 | Beanibazar 132/33kV S/S 132KV Transformer TR-02 HT Scheduled S/D Due to Annual maintenance
08:33 | 16:07 | Gopalganj 132/33kV S/S Gallamari-2 Scheduled S/D
08:33 | 16:07 | Gopalganj 132/33kV S/S Gallamari-2 Scheduled S/D
08:33 | 16:32 | Kaliakoir 400/230/132kV S/S Bibiyana1 Scheduled S/D Due to Annual Maintenance
08:38 | 16:09 | Gollamari 132/33kV S/S E07 Gollamari-Gopalgonj Line - 2 Scheduled S/D Due to Annual maintenance
08:47 |  | TK chemical S/S 48/64MVA T-2(415T) LT Scheduled S/D
08:49 | 14:40 | Juldah-Shahmirpur 132kV Ckt-2 Scheduled S/D from Shahmirpur 132/33kV end Due to Order of BACKUP NLDC and
from Juldah 132/33kV end Due to annual maintanance
08:50 | 16:35 | Bibiyana-Kaliakoir 400 kV Ckt-1 Scheduled S/D from Bibiana 400/230kV end.
08:55 |  | Sikalbaha-TKCL 132kV Ckt-1 Scheduled S/D from Shikalbaha 230/132kV end Due to Bus Maintenance at T.K.Chemical End.
and from TK chemical end Due to Bus annual maintanance
08:56 | 17:06 | Kodda(300MW)-Tongi 230kV Ckt-1 Scheduled S/D from Tongi 230/132/33kV end Due to Annual Maintenance Work
| 09:02 | Aminbazar 400/230/132kV S/S 230/132kv Tr-01 HT is restored.
09:02 | 15:57 | Bibiyana-Fenchuganj 230 kV Ckt-1 Scheduled S/D from Fenchuganj 230/132/33kV end Due to Dead line checking and
from Bibiana 400/230kVend.
| 09:04 | Aminbazar 400/230/132kV S/S 230/132kv Tr-01 LT is restored.
09:07 | 14:55 | Chandraghona 132/33kV S/S TR-01(406T) LT Project Work S/D Due to Blastwall shutering and rebar binding work by CCCE
under G2G project
09:08 | 14:55 | Chandraghona 132/33kV S/S TR-01(406T) HT Project Work S/D Due to Blastwall shutering and rebar binding work by CCCE
under G2G project.
09:09 | 20:25 | Nawabganj 132/33kV S/S TR-2 LT Scheduled S/D Due to For Annual Maintenance work.
09:09 | 20:23 | Nawabganj 132/33kV S/S TR-2 HT Scheduled S/D Due to For Annual Maintenance work
| 09:12 | Faridpur 132/33kV S/S Transformer-1 HT is restored.
| 09:12 | Faridpur 132/33kV S/S Transformer-1 LT is restored.
09:13 | 16:38 | Hathazari-Kaptai 132kV Ckt-2 Scheduled S/D from Hathazari 230/132/33kV end Due to kaptai requirement
09:15 |  | Sunamganj 132/33kV S/S Tr-1 HT Scheduled S/D
09:15 |  | Srinagar 132/33kV S/S Tr-01 HT Scheduled S/D Due to Annual Maintenance.
09:15 |  | Srinagar 132/33kV S/S Tr-02 LT Scheduled S/D Due to Annual Maintenance.
Maintenance.
09:16 |  | TK chemical S/S 50/75 MVA T-1(405T) HT Scheduled S/D Due to Bus Annual Maintance
09:16 |  | Madunaghat-TKCL 132kV Ckt-1 Scheduled S/D from Madunaghat 132/33kV end Due to For maintenance work at
T.K chemical grid ss. and from TK chemical end Due to Bus annual maintenance
09:17 |  | TK chemical S/S 48/64MVA T-2(415T) HT Scheduled S/D Due to Bus annual maintenance
09:18 |  | Barapukuria 230/132/33kV S/S 132/33 KV T-5, 424T LT Scheduled S/D Due to 40 MVA T-5 Replacement work.
09:19 |  | Barapukuria 230/132/33kV S/S 132/33 KV T-5, 424T HT Scheduled S/D Due to 40 MVA T-5 Replacement work.
09:23 | 16:55 | Chauddagram-Feni 132 kV Ckt-1 Scheduled S/D from Feni 132/33kV end Due to shutdown taken by SPMD. and from
Chauddagram 132/33kV end Due to Shutdown for SPMD work at Feni end.
09:38 |  | Mymensingh 132/33kV S/S Transformer-1 (404T) HT Scheduled S/D
09:58 |  | Mymensingh 132/33kV S/S Bus A Scheduled S/D Due to Annual Maintenance work
09:58 | 11:07 | Bogura-Sirajganj 230 kV Ckt-2 Scheduled S/D from Bogura 230/132kV end Due to D/S Replacement and from Sirajgonj 230
end Due to Bogura Sub-station end work
10:10 | 12:05 | Tangail 132/33kV S/S Kaliakair-2 Scheduled S/D Due to Relay Testing for Annual Maintenance
10:14 |  | Chhatak 132/33kV S/S T-3 LT Scheduled S/D Due to Annual maintenance work, Load survived By T1&T2 Transformer
10:16 |  | Chhatak 132/33kV S/S T-3 HT Scheduled S/D Due to Annual Maintenance Work, Load Survived By T-1 and T-2 Transformer.
10:53 | 16:37 | Savar 132/33kV S/S T-1 LT Scheduled S/D Due to Annual maintenance work
10:53 | 16:37 | Savar 132/33kV S/S T-1 HT Scheduled S/D Due to Annual maintenance work
11:13 | 12:15 | Bogura-Sirajganj 230 kV Ckt-1 Scheduled S/D from Bogura 230/132kV end Due to D/S Replacement and from Sirajgonj
230 end Due to Sub-station end work
11:22 | 15:26 | Aminbazar-Meghnaghat 230kV Ckt-1 Scheduled S/D from Aminbazar 400/230/132kV end Due to Meghnaghat side s/d
11:22 | 17:43 | Keraniganj-Sreenagar 132kV Ckt-1 Scheduled S/D from Srinagar 132/33kV end Due to Dead Line Checking. and from
Keranigonj 230/132/33kV end Due to Annual maintenance and Dead line checking at sreenagar end
11:23 | 14:23 | Tangail 132/33kV S/S Tr-1 HT Scheduled S/D Due to Relay testing for annual maintenance
11:23 | 14:23 | Tangail 132/33kV S/S Tr-1 LT Scheduled S/D Due to Relay testing for annual maintenance
12:00 |  | Day Peak Generation = 8,675MW
12:09 |  | Kabirpur 132/33kV S/S XFR, T-3 LT Scheduled S/D Due to 33 kv DPEZ feeder breaker change.
12:10 | 15:02 | Kabirpur 132/33kV S/S XFR, T-3 HT Scheduled S/D Due to 33 kv DPEZ feeder breaker change.
12:23 |  | Rampal 400KV Bus reactor sd for CSD commissioning.
14:17 | 17:07 | Beanibazar 132/33kV S/S 132 KV Transformer TR-01 LT Scheduled S/D Due to Corrective maintenance
14:19 | 17:06 | Beanibazar 132/33kV S/S 132 KV Transformer TR-01 HT Scheduled S/D Due to Corrective maintenance
14:32 | 18:10 | Tangail 132/33kV S/S Tr-2 HT Scheduled S/D Due to relay and tan delta test
14:32 | 18:11 | Tangail 132/33kV S/S Tr-2 LT Scheduled S/D Due to relay and tan delta test
14:42 |  | Sylhet CCPP 225 MW ST was sync.
14:42 |  | Sylhet CCPP 225 MW ST was sync.
| 15:02 | Kabirpur 132/33kV S/S XFR, T-3 HT is restored.
| 15:02 | Kabirpur 132/33kV S/S XFR, T-3 HT is restored.
16:00 |  | Ashuganj CCPP 225MW ST tripped due to trip solenoid valve failure.
| 16:27 | Aminbazar-Kallyanpur 132kV Ckt-1 is restored.
16:42 | 20:23 | Nawabganj 132/33kV S/S TR-2 HT Tripped showing relay relays Due to Dead Zone Fault.
| 17:06 | Kodda(300MW)-Tongi 230kV Ckt-1 is restored.
18:47 |  | Ashuganj CCPP 225MW ST was sync.
20:00 |  | Evening Peak Gen. 10098 MW
00:36 | 00:50 | Shahjibazar 132/33kV S/S TR-06 HT Tripped showing relay relays Due to Over cureent | [5 empty] | 14.0MW load interrup.
00:36 | 00:50 | Shahjibazar 132/33kV S/S TR-06 LT Tripped showing relay relays Due to 132 Kv protection trip | [5 empty] | 14.0MW load interrup.
00:51 |  | Shahjibazar 132/33kV S/S TR-06 LT Scheduled S/D
00:51 |  | Shahjibazar 132/33kV S/S TR-06 HT Scheduled S/D
03:44 |  | Sylhet CCPP 225 MW tripped.
04:00 |  | Minimum generation 6993 MW
07:34 |  | Nawabganj 132/33kV S/S TR-2 LT Scheduled S/D Due to Annual maintenance
07:36 |  | Nawabganj 132/33kV S/S TR-2 HT Scheduled S/D Due to Annual maintenance
07:38 |  | Bagerhat-Mongla 132 kV Ckt-2 Scheduled S/D from Bagerhat 132/33kV end Due to Annual Maintenance Work and from
Mongla 132/33kV end Due to Annual maintenance
07:42 |  | Aminbazar-Kallyanpur 132kV Ckt-1 Scheduled S/D from Kallyanpur 132/33kV end Due to annual maintenance
07:49 |  | Cumilla(N)-Kachua 132 kV Ckt-2 Scheduled S/D from Kachua 132/33kV end Due to Annual Maintenance
07:51 |  | Cumilla(S)-Kachua 132 kV Ckt-1 Scheduled S/D from Cumilla(N) 230/132/33kV end Due to AM
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2023-01-24 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 210 | 3938000
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 76 | 1652863 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 366 | 9084930 | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 233 | 6126000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Under maint.
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 8 | 216000 | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 152 | 3630487 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 0 | 0 | Fuel shortage
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 15 | 314956 | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 363744
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 8 | 46080 | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 16 | 267408 | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 201960
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 48 | 719040 | Fuel shortage
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 35 | 438214 | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 17 | 431578 | Fuel shortage
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 50 | 975840 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 820080
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 30 | 647500 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 17 | 193920 | Fuel shortage
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 65 | 812945 | Fuel shortage
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Fuel shortage
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 0 | 0 | Fuel shortage
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Fuel shortage
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 30 | 432288 | Fuel shortage
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 88 | 1151784 | Fuel shortage
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 17 | 241920 | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 17 | 466560 | Fuel shortage
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 112721
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 270360 | Fuel shortage
| Dhaka area Total |  |  |  | 5847 | 1621 | 33557178
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Machine problem
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 17 | 196065 | Fuel shortage
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 139320
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 32 | 586080 | Fuel shortage
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 30 | 707940 | Low water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 230 | 5442537
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 68 | 1286327 | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 32 | 428640 | Fuel shortage
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 68 | 774599 | Engine problem
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 22 | 452640 | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 25 | 517440 | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 0 | Gas shortage
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 2 | 336480
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 41280 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 25801
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 283 | 2017309 | Engine problem
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 17 | 450298 | Fuel shortage
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 92 | 1589084 | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 25 | 455040 | Fuel shortage
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 68 | 1050055 | Fuel shortage
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 46836 | On test.
| Chattogram area Total |  |  |  | 2382 | 1011 | 16543771
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 210 | 4318000 | Gas shortage
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 310 | 7785700 | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint.
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 347 | 8120100 | Gas shortage
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 10 | 207504 | Gas shortage
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 40 | 207840
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 133818 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1105173
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 6 | 152218 | Fuel shortage
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 28 | 267696 | Machine problem
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 17 | 139200 | Fuel shortage
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 493992
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 174780 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 118 | 2531520
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 24 | 547100
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 8 | 66437 | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 15 | 337770 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 10 | 88512 | Fuel shortage
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 52 | 616740 | Fuel shortage
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 108 | 888720 | Engine problem
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 280080 | Engine problem
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 94 | 1158720 | Fuel shortage
| Cumilla Area Total |  |  |  | 3285 | 1502 | 29621620
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 54 | 1489920 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 443376
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 10050
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 48 | 1125600 | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 47 | 630000 | Fuel shortage
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 0
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 148560 | Engine problem
| Mymensingh Area Total |  |  |  | 614 | 174 | 3847506
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 30 | 715000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 43 | 978120 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Gas shortage
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 51 | 696000
| Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 50 | 692856
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 0 | 0 | Engine problem
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 62 | 1495008
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 86 | 1146240
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 135 | 3102950 | Machine problem
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 19 | 444000
| Sylhet 50MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Gas shortage
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 0 | 0 | Gas shortage
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7066500 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 366 | 8979000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 251100
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 400 | 9429500
| Sylhet Area Total |  |  |  | 2427 | 1552 | 34996274
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Fuel shortage
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 658 | 19086545
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 16 | 315840 | Fuel shortage
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 43 | 149280 | Engine problem
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel conservation
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 75 | 329728 | Engine problem
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 8 | 32625 | Fuel shortage
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Fuel shortage
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 41760 | Fuel shortage
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 105 | 467852
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 345600
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 0 | 0 | 0 | On test.
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 660*2 | 617 | 0 | 0 | Coal shortage
| Khulna Area Total |  |  |  | 3001 | 905 | 20769230
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 16 | 98880 | Line O/L
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 25 | 479500 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 184 | 4462405 | Machine problem
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1192 | 28038800 | Line O/L
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 4899000
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 150 | 668400
| Barisal 307 MW |  | BCPCL | 307*1 | 307 | 0 | 0 | Coal shortage
| Barisal Area Total |  |  |  | 2265 | 1787 | 38646985
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 26 | 247748 | Fuel shortage
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 21 | 146775 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contract Expired
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 34 | 307860 | Fuel shortage
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 41 | 180648 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 199 | 4689027 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 341 | 8798545 | Gas shortage
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 30 | 280797 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 21 | 472320
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 176796 | Engine problem
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 8 | 78965 | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 97 | 572386 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Fuel shortage
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 94 | 716160 | Fuel shortage
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 95 | 764448 | Fuel shortage
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 24000
| Adani Power Jharkhanda Ltd |  | Import | 0 | 0 | 0 | 0 | On test.
| Rajshahi Area Total |  |  |  | 2129 | 1015 | 17456475
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 82 | 1937018
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 251 | 6060100 | Machine problem
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 85 | 762691 | Fuel shortage
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 30219
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 113 | 1235328
| Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 153940
| Teesta Solar Limited |  | BPCL | 16*12.5 | 0 | 0 | 806290
| Rangpur Area Total |  |  |  | 750 | 531 | 10985586
| Total |  |  |  | 22700 | 10098 | 206424625
| Eastern Grid Total |  |  |  | 14555 | 5860 | 118566349
| Western Grid Total |  |  |  | 8145 | 4238 | 87858276
| National Grid Total |  |  |  | 22700 | 10098 | 206424625
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2023-01-24
| (a) ENTIRE EASTERN GRID : |  | 6429.06 | MW | (b) ENTIRE WESTERN GRID : |  | 3203.3 | MW
| i) Dhaka area |  | 3416.46 | MW | i) Khulna area |  | 1134.6 | MW
| ii) Chittagong area |  | 1005.6 | MW | ii) Rajshahi area |  | 1056.7 | MW
| iii) Comilla area |  | 861 | MW | iii) Barisal area |  | 284 | MW
| iv) Mymensingh area |  | 786 | MW | iv) Rangpur area |  | 728 | MW
| v) Sylhet area |  | 360 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 9632.36 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | Chhatak | 17 | 18:00 | Kamrangirchar | 67 | 13:00 | Natore | 100 | 19:30 | Shitalakhya | 108 | 12:00
2 | AKSML | 91 | 14:00 | Chowmuhani | 126 | 19:30 | Kaptai | 4 | 18:00 | Nawabganj | 27.8 | 21:00 | Sholosohor | 24 | 16:00
3 | Aftabnagar | 22 | 13:00 | Chuadanga | 69 | 18:30 | Kazla | 72 | 14:00 | Netrakona | 110 | 06:00 | Shyampur | 140 | 23:00
4 | Agargaon | 54 | 13:00 | Coxsbazar | 101 | 18:00 | Keranigonj | 42 | 13:00 | New | 58 | 12:00 | Siddhirganj | 96 | 12:00
5 | Agrabad | 48 | 18:00 | Cumilla(N) | 108 | 18:30 | Khagrachori | 24 | 18:00 | Niamatpur | 87 | 20:00 | Sirajganj | 85 | 19:30
6 | Amnura | 48 | 19:30 | Cumilla(S) | 133 | 18:00 | Khulna | 77 | 13:00 | Noapara | 32.5 | 18:30 | Sonargaon | 90 | 17:00
7 | Ashuganj | 46 | 20:00 | Daudkandi | 94 | 20:00 | Khulshi | 142 | 19:00 | PHP | 9 | 04:00 | Sreemongol | 38 | 19:30
8 | BIPTC | N/A | N/A | Dhaka | 20 | 19:30 | Kishoreganj | 94 | 21:00 | Pabna | 74 | 20:00 | Srinagar | 29.41 | 19:00
9 | BSRM | 112 | 19:30 | Dhamrai | 82 | 16:00 | Kodda | 219 | 15:00 | Palashbari | 99 | 19:00 | Sunamganj | 34 | 19:30
10 | Bagerhat | 72 | 18:30 | Dhanmondi | 81 | 13:00 | Kulaura | 26 | 18:00 | Panchagarh | 47 | 19:30 | Sylhet | 92 | 19:30
11 | Bakulia | 68 | 18:00 | Dohazari | 76 | 20:00 | Kurigram | 72 | 07:00 | Patuakhali | 82 | 20:00 | TK | 14.3 | 08:00
12 | Banani | 26 | 13:00 | Faridpur | 104 | 19:00 | Kushtia | 94 | 18:30 | Payra | 10.4 | 18:30 | Tangail | 149 | 22:00
13 | Bangabhaban | 9 | 10:00 | Fatullah | 54 | 10:00 | Lalbag | 66 | 19:00 | Postogola | 31 | 13:00 | Thakurgaon | 66 | 19:00
14 | Barapukuria | 51 | 19:30 | Fenchuganj | 29 | 20:00 | Lalmonirhat | 40 | 17:00 | Purbachal | 13 | 12:00 | Tongi | 92 | 11:00
15 | Barguna | 4 | 18:30 | Feni | 84 | 18:30 | Madanganj | 38 | 18:00 | Purbasadipur | 105 | 20:00 | Ullon | 36 | 19:00
16 | Barishal | 72 | 18:30 | GPH | 89 | 00:00 | Madaripur | 66 | 20:00 | Rahanpur_I | 3.5 | 07:00 | Uttara | 57 | 13:00
17 | Barishal-230 | 60 | 18:30 | Ghorashal | 50 | 00:00 | Madartek | 48 | 13:00 | Rahim | 40 | 11:00 | UttaraNew | 13 | 12:00
18 | Baroaulia | 63 | 12:00 | Goalpara | 20 | 12:00 | Madunaghat | 39 | 19:00 | Rajbari | 48 | 18:30 | Zigatola | 34 | 13:00
19 | Baroirhat | 33 | 18:30 | Gollamari | 32 | 13:00 | Magura | 44 | 18:30 | Rajendrapur | 82 | 17:00
20 | Bashundhara | 118 | 13:00 | Gopalganj | 74.8 | 19:00 | Mahasthangarh | 42 | 19:30 | Rajshahi | 102 | 20:00
21 | BashundharaCement | 7 | 10:00 | Gulshan | 72 | 14:00 | Manikganj | 74 | 18:00 | Rajshahi-230 | 29 | 12:00
22 | Beanibazar | 39 | 19:30 | Halishahar | 83.5 | 15:00 | Maniknagar | 40 | 13:00 | Ramganj | 68 | 18:00
23 | Benapole | 48 | 08:00 | HaripurSBU | 133 | 18:30 | Matarbari | 33 | 18:30 | Rampur | 18 | 19:00
24 | Bhaluka | 108 | 00:00 | Hasnabad | 71 | 19:30 | Matuail | 56 | 12:00 | Rangamati | 10 | 18:00
25 | Bhandaria | 32 | 19:30 | Hathazari | 45 | 18:00 | Millgate | 54 | 10:00 | Rangpur | 117 | 19:30
26 | Bhangura | 20 | 18:00 | Ishurdi | 51 | 19:30 | Mirpur | 88.5 | 18:30 | Ruppur | 4 | 15:00
27 | Bheramara(GK) | 39 | 18:30 | Jaldhaka | 48 | 19:30 | Mirsorai | 3 | 18:00 | SSM | 3 | 15:00
28 | Bhulta | 204 | 00:00 | Jamalpur | 101 | 21:00 | Mithapukur | 24 | 18:30 | Saidpur | 92 | 19:30
29 | Bog-Sherpur | 52 | 19:30 | Jashore | 105 | 13:00 | Modern | 0 | 00:00 | Satkhira | 83 | 08:00
30 | Bogura | 109 | 20:00 | Jhenaidah | 89 | 08:00 | Mogbazar | 82 | 13:00 | Satmasjid | 62 | 13:00
31 | Borhanuddin | 26 | 00:00 | Joydebpur | 135 | 16:00 | Mongla | 24 | 10:00 | Savar | 126 | 16:00
32 | Brahmanbaria | 104 | 19:30 | Joypurhat | 42 | 20:00 | Motijheel | 23 | 13:00 | Shahjadpur | 73 | 18:30
33 | Cantonment | 90 | 13:00 | Juldah | 28 | 12:00 | Munshiganj | 62 | 19:00 | Shahjibazar | 89 | 21:00
34 | Chandpur | 44 | 18:30 | KSRM | 27 | 10:00 | Mymensingh | 167 | 20:00 | Shahmirpur | 36 | 02:00
35 | Chandraghona | 24 | 18:00 | Kabirpur | 171 | 06:00 | Naogaon | 101 | 19:30 | Shariatpur | 48 | 19:30
36 | Chapai | 52 | 19:00 | Kachua | 49 | 21:00 | Narail | 40 | 18:30 | Sherpur | 110 | 00:00
37 | Charsaidpur | 33.5 | 11:00 | Kallyanpur | 57 | 12:00 | Narinda | 50 | 14:00 | Shikalbaha | 21 | 15:00
38 | Chauddagram | 30 | 18:00 | Kalurghat | 25 | 16:00 | Narshingdi | 138 | 21:00 | Shikalbaha-230 | N/A | N/A
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2023-01-24 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 415 | 05:00 | 396 | 16:00 | Gopalganj_I | N/A | N/A | N/A | N/A
| Bhulta | 394 | 05:00 | 381 | 16:00 | Kaliakoir | 398 | 05:00 | 374 | 16:00
| Bibiana | 406 | 05:00 | 396 | 07:00 | Payra | 420 | 01:00 | 410 | 16:00
| BIPTC | 406 | 05:00 | 393 | 13:00 | Rahanpur_I | 415 | 13:00 | 385 | 16:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 240 | 05:00 | 227 | 16:00 | Hasnabad | 235 | 00:00 | 229 | 10:00
| AKSML | 241 | 15:00 | 226 | 03:00 | Hathazari | 245 | 19:30 | 234 | 08:00
| Aminbazar | 240 | 01:00 | 230 | 10:00 | Ishurdi | 243 | 18:00 | 228 | 16:00
| Ashuganj | 242 | 19:00 | 235 | 12:00 | Jhenaidah | 243 | 18:00 | 224 | 12:00
| Baghabari | 236 | 01:00 | 227 | 16:00 | Kaliakoir | 238 | 04:00 | 225 | 16:00
| Barapukuria | 230 | 18:00 | 222 | 07:00 | Keranigonj | 239 | 05:00 | 226 | 16:00
| Barishal | 245 | 01:00 | 238 | 11:00 | Khulna(S) | 246 | 18:00 | 225 | 12:00
| Bheramara | 240 | 18:00 | 225 | 12:00 | Maniknagar | 235 | 02:00 | 225 | 16:00
| Bhulta | 240 | 05:00 | 228 | 16:00 | Meghnaghat | 242 | 00:00 | 236 | 13:00
| Bibiana | 241 | 02:00 | 233 | 10:00 | Mirsorai | 240 | 20:00 | 229 | 10:00
| BIPTC | 243 | 18:00 | 226 | 12:00 | Rajshahi | 242 | 01:00 | 227 | 16:00
| Bogura | 234 | 18:00 | 224 | 16:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 249 | 19:30 | 245 | 00:00 | Rampura | 236 | 00:00 | 227 | 16:00
| BSRM | 242 | 18:00 | 230 | 10:00 | Shikalbaha | 242 | 18:30 | 232 | 05:00
| Cumilla(N) | 238 | 18:00 | 228 | 10:00 | Shyampur | 238 | 01:00 | 227 | 12:00
| Fenchuganj | 242 | 19:00 | 235 | 10:00 | Siddhirganj | 238 | 00:00 | 230 | 11:00
| Ghorashal | N/A | N/A | N/A | N/A | Sirajgonj | 235 | 18:00 | 230 | 06:00
| GPH | 239 | 13:00 | 230 | 03:00 | Tongi | 236 | 01:00 | 223 | 11:00
| Haripur | 235 | 03:00 | 226 | 12:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 138 | 01:00 | 132 | 10:00 | Kushtia | 140 | 18:00 | 129 | 12:00
| Agargaon | 140 | 01:00 | 132 | 16:00 | Lalbag | 136 | 05:00 | 127 | 16:00
| Agrabad | 140 | 15:00 | 132 | 11:00 | Lalmonirhat | 133 | 00:00 | 126 | 07:00
| AKS | 141 | 19:00 | 133 | 08:00 | Madanganj | 136 | 03:00 | 130 | 10:00
| Aminbazar | 138 | 01:00 | 131 | 10:00 | Madaripur | 137 | 18:00 | 130 | 12:00
| Amnura | 140 | 18:00 | 124 | 07:00 | Madartek | 139 | 05:00 | 130 | 16:00
| Ashuganj | 138 | 18:00 | 134 | 12:00 | Madunaghat | 141 | 19:00 | 134 | 07:00
| Bagerhat | 139 | 18:00 | 125 | 12:00 | Magura | 139 | 04:00 | 126 | 12:00
| Bakulia | 141 | 19:00 | 133 | 10:00 | Mahasthangarh | 138 | 19:00 | 127 | 16:00
| Banani | 135 | 00:00 | 127 | 16:00 | Manikganj | 132 | 00:00 | 124 | 16:00
| Bangabhaban | 137 | 01:00 | 130 | 12:00 | Maniknagar | 138 | 04:00 | 130 | 12:00
| Barapukuria | 136 | 18:00 | 129 | 10:00 | Matarbari | 137 | 10:00 | 125 | 07:00
| Barguna | 137 | 19:00 | 130 | 01:00 | Matuail | 137.3 | 03:00 | 131.6 | 16:00
| Barishal | 139 | 04:00 | 130 | 03:00 | Millgate | 136 | 04:00 | 127 | 12:00
| Barishal-230 | 140 | 18:00 | 134 | 11:00 | Mirpur | 137 | 03:00 | 128 | 16:00
| Baroaulia | 142 | 18:30 | 135 | 10:00 | Mithapukur | 135 | 18:30 | 126 | 16:00
| Baroirhat | 142 | 18:00 | 133 | 10:00 | Modern | 140 | 13:00 | 133 | 10:00
| Bashundhara | 137 | 04:00 | 126 | 16:00 | Mogbazar | 142 | 03:00 | 132 | 12:00
| BashundharaCement | 136 | 03:00 | 130 | 10:00 | Mongla | 138 | 18:00 | 125 | 12:00
| Beanibazar | 135 | 00:00 | 132 | 13:00 | Motijheel | 137 | 01:00 | 130 | 12:00
| Benapole | 139 | 18:00 | 123 | 12:00 | Munshiganj | 137 | 19:00 | 131 | 16:00
| Bhaluka | 126 | 19:00 | 111 | 20:00 | Mymensingh | 127 | 07:00 | 114 | 20:00
| Bhandaria | 140 | 05:00 | 134 | 11:00 | Naogaon | 137 | 18:00 | 126 | 07:00
| Bhangura | 141 | 01:00 | 134 | 16:00 | Narail | 138 | 04:00 | 127 | 12:00
| Bheramara | 139 | 18:00 | 130 | 12:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bheramara(GK) | 138 | 00:00 | 131 | 12:00 | Narshingdi | 135 | 00:00 | 128 | 16:00
| Bhulta | 130 | 06:00 | 124 | 16:00 | Natore | 137 | 19:00 | 128 | 16:00
| Bog-Sherpur | 141 | 18:00 | 129 | 16:00 | Nawabganj | 136 | 05:00 | 127 | 10:00
| Bogura | 141 | 18:00 | 130 | 10:00 | Netrakona | 126 | 07:00 | 112 | 20:00
| Bogura-230 | 139 | 18:00 | 130 | 16:00 | New | 136 | 00:00 | 128 | 16:00
| Brahmanbaria | 134 | 18:00 | 130 | 16:00 | Niamatpur | 134 | 19:00 | 124 | 10:00
| Cantonment | 140 | 05:00 | 131 | 12:00 | Noapara | 140 | 18:00 | 126 | 12:00
| Chandpur | 142 | 17:00 | 133 | 10:00 | Pabna | 140 | 02:00 | 131 | 16:00
| Chandraghona | 141 | 19:00 | 134 | 10:00 | Palashbari | 134 | 18:00 | 123 | 16:00
| Chapai | 140 | 18:00 | 125 | 07:00 | Panchagarh | 137 | 18:00 | 121 | 16:00
| Charsaidpur | 137 | 00:00 | 131 | 12:00 | Patuakhali | 135 | 20:00 | 126 | 10:00
| Chauddagram | 142 | 18:00 | 133 | 10:00 | Payra | 133 | 18:00 | 128 | 08:00
| Chhatak | 135 | 00:00 | 132 | 13:00 | PHP | 141 | 18:00 | 132 | 10:00
| Chowmuhani | 142 | 22:00 | 133 | 09:00 | Postogola | 138 | 05:00 | 131 | 10:00
| Chuadanga | 138 | 03:00 | 125 | 11:00 | Purbachal | 138 | 01:00 | 131 | 16:00
| Coxsbazar | 135 | 13:00 | 124 | 07:00 | Purbasadipur | 135 | 18:00 | 121 | 16:00
| Cumilla(N) | 142 | 18:00 | 135 | 10:00 | Rahim | 138 | 03:00 | 133 | 11:00
| Cumilla(S) | 141 | 19:00 | 128 | 13:00 | Rajbari | 138 | 18:00 | 128 | 12:00
| Daudkandi | 138 | 19:00 | 132 | 11:00 | Rajendrapur | 128 | 05:00 | 121 | 16:00
| Dhaka | 139 | 05:00 | 131 | 16:00 | Rajshahi | 138 | 18:00 | 126 | 07:00
| Dhamrai | 138 | 01:00 | 129 | 16:00 | Rajshahi-230 | 134 | 19:00 | 123 | 07:00
| Dhanmondi | 139 | 05:00 | 132 | 16:00 | Ramganj | 140 | 00:00 | 132 | 13:00
| Dohazari | 138 | 13:00 | 130 | 11:00 | Rampur | 140 | 13:00 | 134 | 11:00
| Faridpur | 137 | 18:00 | 129 | 12:00 | Rampura | 137 | 01:00 | 131 | 10:00
| Fatullah | 138 | 01:00 | 131 | 10:00 | Rangamati | 140 | 13:00 | 134 | 03:00
| Fenchuganj | 139 | 00:00 | 135 | 10:00 | Rangpur | 136 | 18:00 | 125 | 16:00
| Feni | 142 | 17:00 | 134 | 10:00 | Ruppur | 140 | 18:00 | 131 | 11:00
| Ghorashal | 140 | 07:00 | 136 | 12:00 | Saidpur | 135 | 18:00 | 125 | 16:00
| Goalpara | 141 | 18:00 | 128 | 12:00 | Satkhira | 139 | 18:00 | 126 | 08:00
| Gollamari | 141 | 18:00 | 128 | 12:00 | Satmasjid | 139 | 01:00 | 132 | 10:00
| Gopalganj | 139 | 19:00 | 128 | 11:00 | Savar | 137 | 01:00 | 129 | 09:00
| Gopalganj-400 | 137 | 03:00 | 130 | 10:00 | Shahjadpur | 143 | 18:30 | 136 | 16:00
| Gopalganj_I | N/A | N/A | N/A | N/A | Shahjibazar | 135 | 01:00 | 132 | 10:00
| Gulshan | 137 | 01:00 | 131 | 10:00 | Shahmirpur | 139 | 12:00 | 134 | 05:00
| Halishahar | 140 | 13:00 | 132 | 10:00 | Shariatpur | 138 | 18:00 | 130 | 10:00
| Haripur | 138 | 03:00 | 133 | 11:00 | Sherpur | 126 | 07:00 | 115 | 21:00
| HaripurSBU | 137 | 00:00 | 132 | 16:00 | Shikalbaha | 141 | 15:00 | 134 | 05:00
| Hasnabad | 136 | 00:00 | 131 | 10:00 | Shikalbaha-230 | 140 | 15:00 | 134 | 12:00
| Hathazari | 143 | 18:00 | 135 | 08:00 | Shitalakhya | 137 | 01:00 | 131 | 10:00
| Ishurdi | 141 | 18:00 | 131 | 16:00 | Sholosohor | 140 | 13:00 | 134 | 03:00
| Jaldhaka | 133 | 18:00 | 121 | 13:00 | Shyampur | 136 | 04:00 | 130 | 10:00
| Jamalpur | 129 | 11:00 | 119 | 21:00 | Shyampur-230 | 138 | 05:00 | 131 | 10:00
| Jashore | 137 | 18:00 | 124 | 12:00 | Siddhirganj | 137 | 01:00 | 132 | 10:00
| Jhenaidah | 140 | 18:00 | 129 | 12:00 | Sirajganj | 141 | 18:00 | 129 | 16:00
| Jhenaidah-230 | 140 | 05:00 | 129 | 12:00 | Sonargaon | 136 | 00:00 | 133 | 09:00
| Joydebpur | 143 | 18:00 | 135 | 15:00 | Sreemongol | 135 | 18:00 | 132 | 10:00
| Joypurhat | 137 | 18:00 | 127 | 07:00 | Srinagar | 136 | 05:00 | 127 | 12:00
| Juldah | 139 | 13:00 | 133 | 10:00 | SSM | 146 | 19:00 | 138 | 10:00
| Kabirpur | 135 | 00:00 | 122 | 16:00 | Sunamganj | 134 | 00:00 | 131 | 10:00
| Kachua | 141 | 17:00 | 132 | 11:00 | Sylhet | 136 | 00:00 | 133 | 16:00
| Kaliakoir | 139 | 01:00 | 125 | 09:00 | Tangail | 128 | 00:00 | 123 | 19:30
| Kallyanpur | 138 | 04:00 | 129 | 16:00 | Thakurgaon | 138 | 18:00 | 118 | 16:00
| Kalurghat | 140 | 13:00 | 135 | 04:00 | TK | 140 | 17:00 | 135 | 03:00
| Kamrangirchar | 134 | 02:00 | 126 | 16:00 | Tongi | 136 | 01:00 | 130 | 11:00
| Kaptai | 140 | 00:00 | 131 | 10:00 | Ullon | 138 | 01:00 | 131 | 12:00
| Kazla | 137 | 03:00 | 130 | 12:00 | Uttara | 138 | 05:00 | 130 | 09:00
| Keranigonj | 135 | 05:00 | 128 | 10:00 | UttaraNew | 138 | 01:00 | 129 | 16:00
| Khagrachori | 141 | 22:00 | 133 | 10:00 | Zigatola | 135 | 04:00 | 127 | 16:00
| Khulna | 141 | 18:00 | 127 | 12:00
| Khulna(S) | 142 | 18:00 | 129 | 12:00
| Khulshi | 139 | 13:00 | 133 | 08:00
| Kishoreganj | 131 | 08:00 | 123 | 20:00
| Kodda | 140 | 17:00 | 121 | 16:00
| KSRM | 141 | 18:30 | 134 | 04:00
| Kulaura | 138 | 00:00 | 135 | 10:00
| Kurigram | 132 | 09:00 | 121 | 07:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2023-01-24
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 1150 | 4701 | 3633 | 8334 |  |  |  | QF-LDC-11
0:30 | 1110 | 4669.5 | 3422 | 8091.5 | Date: | 2023-01-24
1:00 | 1070 | 4638 | 3211 | 7849
1:30 | 1010 | 4524.5 | 3089.5 | 7614
2:00 | 950 | 4411 | 2968 | 7379
2:30 | 950 | 4292.5 | 2946.5 | 7239 | [5 empty] | Gen. at Eve. Peak | 10098 | 10098 MW (20:00 )
3:00 | 950 | 4174 | 2925 | 7099 | [6 empty] | 20:00
3:30 | 945 | 4120 | 2905.5 | 7025.5 | [5 empty] | Gen. at Day Peak | 8675 | 8675 MW (12:00 )
4:00 | 940 | 4066 | 2886 | 6952 | [6 empty] | 12:00
4:30 | 945 | 4059.5 | 2881 | 6940.5 | [5 empty] | Highest Generation | 10098
5:00 | 950 | 4053 | 2876 | 6929 | [6 empty] | 20:00
5:30 | 910 | 4181 | 2885.5 | 7066.5
6:00 | 870 | 4309 | 2895 | 7204
6:30 | 860 | 4424.5 | 3111.5 | 7536
7:00 | 850 | 4540 | 3328 | 7868
7:30 | 895 | 4561.5 | 3425.5 | 7987
8:00 | 940 | 4583 | 3523 | 8106
8:30 | 917.5 | 4628.5 | 3505.5 | 8134
9:00 | 895 | 4674 | 3488 | 8162
9:30 | 980 | 4712 | 3482 | 8194
10:00 | 1065 | 4750 | 3476 | 8226
10:30 | 1159.5 | 4754 | 3574 | 8328
11:00 | 1254 | 4758 | 3672 | 8430
11:30 | 1205.5 | 4835 | 3717.5 | 8552.5
12:00 | 1157 | 4912 | 3763 | 8675
12:30 | 1157 | 4904 | 3844 | 8748
13:00 | 1157 | 4896 | 3925 | 8821
13:30 | 1170.5 | 4877.5 | 3920 | 8797.5
14:00 | 1184 | 4859 | 3915 | 8774
14:30 | 1103.5 | 4901 | 3740 | 8641
15:00 | 1023 | 4943 | 3565 | 8508
15:30 | 1006.5 | 5059.5 | 3498 | 8557.5
16:00 | 990 | 5176 | 3431 | 8607
16:30 | 961 | 5163.5 | 3540 | 8703.5
17:00 | 932 | 5151 | 3649 | 8800
17:30 | 981 | 5308.5 | 3782.5 | 9091
18:00 | 1030 | 5466 | 3916 | 9382
18:30 | 1013 | 5586.5 | 3988.5 | 9575
19:00 | 996 | 5707 | 4061 | 9768
19:30 | 870 | 5739 | 4226 | 9965
20:00 | 880 | 5860 | 4238 | 10098 |  |  |  | Executive Engineer
20:30 | 1005 | 5742 | 4256 | 9998 |  |  |  | Network Operation Division
21:00 | 1130 | 5624 | 4274 | 9898
21:30 | 1125 | 5532.5 | 4164.5 | 9697
22:00 | 1120 | 5441 | 4055 | 9496 |  |  |  |  | Page 6 of 7
22:30 | 1140 | 5262.5 | 3967 | 9229.5
23:00 | 1160 | 5084 | 3879 | 8963
23:30 | 1155 | 4892.5 | 3756 | 8648.5
24:00 | 1150 | 4701 | 3633 | 8334
10098 MW (20:00 )
8675 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2023-01-24 |  | Energy |  | 206424625
[13 empty] | 2023-01-24 |  |  |  |  | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 3370 | 906 | 1648 | 0 | 803 | 1461 | 30 | 0 | 16 | 100 | 0 | 0
0:30 | 3396 | 839 | 1550.5 | 0 | 751.5 | 1421.5 | 30 | 0 | 8 | 95 | 0 | 0 | Date: | 2023-01-24
1:00 | 3422 | 772 | 1453 | 0 | 700 | 1382 | 30 | 0 | 0 | 90 | 0 | 0
1:30 | 3358 | 772 | 1463 | 0 | 560.5 | 1341.5 | 30 | 0 | 0 | 89 | 0 | 0 | [7 empty] | Total Energy | 206.4246 | Total Energy Gen 206.425 MKWHr Energy Not Served 6.277 MKWHr Energy Requirement 212.702 MKWHr
2:00 | 3294 | 772 | 1473 | 0 | 421 | 1301 | 30 | 0 | 0 | 88 | 0 | 0 | [7 empty] | Energy not Served | 6.2773
2:30 | 3248.5 | 772 | 1447 | 0 | 364.5 | 1291 | 30 | 0 | 0 | 86 | 0 | 0 | [7 empty] | Energy Requirement | 212.7019
3:00 | 3203 | 772 | 1421 | 0 | 308 | 1281 | 30 | 0 | 0 | 84 | 0 | 0
3:30 | 3202.5 | 766.5 | 1384.5 | 0 | 271.5 | 1286.5 | 30 | 0 | 0 | 84 | 0 | 0 | [5 empty] | Shortage
4:00 | 3202 | 761 | 1348 | 0 | 235 | 1292 | 30 | 0 | 0 | 84 | 0 | 0
4:30 | 3201.5 | 761 | 1342 | 0 | 235 | 1287 | 30 | 0 | 0 | 84 | 0 | 0
5:00 | 3201 | 761 | 1336 | 0 | 235 | 1282 | 30 | 0 | 0 | 84 | 0 | 0
5:30 | 3287.5 | 761 | 1371.5 | 0 | 237.5 | 1291 | 30 | 0 | 0 | 88 | 0 | 0
6:00 | 3374 | 761 | 1407 | 0 | 240 | 1300 | 30 | 0 | 0 | 92 | 0 | 0
6:30 | 3350.5 | 834.5 | 1511 | 0 | 384.5 | 1325.5 | 30 | 0 | 8 | 91 | 1 | 74.6476 |  |  |  | Coal
7:00 | 3327 | 908 | 1615 | 0 | 529 | 1351 | 30 | 0 | 16 | 90 | 2 | 149.2951
7:30 | 3344 | 846 | 1590.5 | 0 | 633 | 1405.5 | 30 | 0 | 18 | 95 | 25 | 279.2372 |  |  | Oil |  |  |  | ,
8:00 | 3361 | 784 | 1566 | 0 | 737 | 1460 | 30 | 0 | 20 | 100 | 48 | 409.1793
8:30 | 3350 | 692 | 1559.5 | 0 | 807.5 | 1481 | 30 | 0 | 29.5 | 105 | 79.5 | 521.6114
9:00 | 3339 | 600 | 1553 | 0 | 878 | 1502 | 30 | 0 | 39 | 110 | 111 | 634.0436
9:30 | 3343 | 594 | 1567.5 | 0 | 858.5 | 1502.5 | 30 | 0 | 39 | 110 | 149.5 | 650.632
10:00 | 3347 | 588 | 1582 | 0 | 839 | 1503 | 30 | 0 | 39 | 110 | 188 | 667.2203
10:30 | 3247 | 632 | 1629 | 0 | 889 | 1487.5 | 30 | 3.5 | 85 | 110 | 215 | 642.3378
11:00 | 3147 | 676 | 1676 | 0 | 939 | 1472 | 30 | 7 | 131 | 110 | 242 | 617.4553
11:30 | 3147 | 743.5 | 1640 | 0 | 985 | 1452.5 | 30 | 12.5 | 171 | 113 | 258 | 573.6804
12:00 | 3147 | 811 | 1604 | 0 | 1031 | 1433 | 30 | 18 | 211 | 116 | 274 | 529.9056
12:30 | 3137 | 859 | 1593 | 0 | 1056 | 1422.5 | 30 | 15.5 | 247.5 | 116 | 271.5 | 484.7485
13:00 | 3127 | 907 | 1582 | 0 | 1081 | 1412 | 30 | 13 | 284 | 116 | 269 | 439.5913
13:30 | 3127 | 907 | 1582 | 0 | 1081 | 1412 | 30 | 13 | 284 | 116 | 269 | 439.5913
14:00 | 3127 | 907 | 1582 | 0 | 1081 | 1412 | 30 | 13 | 284 | 116 | 269 | 439.5913
14:30 | 3144.5 | 904.5 | 1576.5 | 0 | 1004.5 | 1406.5 | 30 | 6.5 | 262 | 115 | 214.5 | 434.9834
15:00 | 3162 | 902 | 1571 | 0 | 928 | 1401 | 30 | 0 | 240 | 114 | 160 | 430.3755
15:30 | 3211 | 902 | 1574.5 | 0 | 965.5 | 1401.5 | 30 | 0 | 240.5 | 112 | 120.5 | 340.0612
16:00 | 3260 | 902 | 1578 | 0 | 1003 | 1402 | 30 | 0 | 241 | 110 | 81 | 249.7468
16:30 | 3161.5 | 902.5 | 1582 | 0 | 1149.5 | 1416.5 | 30 | 3.5 | 295.5 | 112 | 50.5 | 259.8841
17:00 | 3063 | 903 | 1586 | 0 | 1296 | 1431 | 30 | 7 | 350 | 114 | 20 | 270.0215
17:30 | 3067 | 864.5 | 1564 | 0 | 1565.5 | 1431.5 | 30 | 3.5 | 432 | 123 | 10 | 375.0107
18:00 | 3071 | 826 | 1542 | 0 | 1835 | 1432 | 30 | 0 | 514 | 132 | 0 | 480
18:30 | 3168 | 734 | 1595.5 | 0 | 1953 | 1456.5 | 30 | 0 | 513 | 125 | 0 | 490.2076
19:00 | 3265 | 642 | 1649 | 0 | 2071 | 1481 | 30 | 0 | 512 | 118 | 0 | 500.4152
19:30 | 3239 | 670 | 1661 | 50 | 2169 | 1524 | 30 | 0 | 506 | 116 | 0 | 340.0612
20:00 | 3402 | 658 | 1666 | 10 | 2180 | 1525 | 30 | 0 | 509 | 118 | 0 | 179.7071
20:30 | 3399.5 | 695.5 | 1674 | 55 | 1996 | 1529.5 | 30 | 0 | 503.5 | 115 | 0 | 185.2366
21:00 | 3397 | 733 | 1682 | 100 | 1812 | 1534 | 30 | 0 | 498 | 112 | 0 | 190.766
21:30 | 3391 | 820 | 1683 | 50 | 1743.5 | 1529 | 30 | 0 | 337.5 | 113 | 0 | 169.5698
22:00 | 3385 | 907 | 1684 | 0 | 1675 | 1524 | 30 | 0 | 177 | 114 | 0 | 148.3736
22:30 | 3397 | 907 | 1661 | 0 | 1481 | 1493.5 | 30 | 0 | 153 | 107 | 0 | 136.3931
23:00 | 3409 | 907 | 1638 | 0 | 1287 | 1463 | 30 | 0 | 129 | 100 | 0 | 124.4126
23:30 | 3389.5 | 906.5 | 1643 | 0 | 1045 | 1462 | 30 | 0 | 72.5 | 100 | 0 | 114.7063 | Max Temp. in Dhaka |  | 28.7° C
24:00 | 3370 | 906 | 1648 | 0 | 803 | 1461 | 30 | 0 | 16 | 100 | 0 | 105
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 206.425 MKWHr Energy Not Served 6.277 MKWHr Energy Requirement 212.702 MKWHr
Shortage
Note on W13: Author:

## Generation
g | 2023-01-24
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 707940
2 | Karnaphuli Hydro PP Unit-4 & 5 | [6 empty] | 0
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [6 empty] | 1 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 10 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 8 | 0 | 196065
| Teknaf 20MW PP (Solartech) | [6 empty] | 1 | 7 | 13 | 18 | 20 | 20 | 20 | 18 | 14 | 7 | 2 | [9 empty] | 139320
6 | Sikalbaha 225MW CCPP (Gas) | 227 | 227 | 227 | 226 | 227 | 228 | 228 | 228 | 237 | 234 | 235 | 229 | 227 | 226 | 223 | 221 | 224 | 224 |  | 223 | 224 | 230 | 230 | 229 | 231 | 233 | 5442537
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [11 empty] | 48 | 68 | 68 | 68 | 68 | 68 | 68 |  | 68 | 68 | 68 | 68 | 68 | 68 | 0 | 774599
12 | Hathazari 100 MW peaking PP | [7 empty] | 4 | 23 | 23 | 31 | 31 | 31 | 31 | 30 | 29 | 29 | 23 |  | 32 | 32 | 32 | 32 | 32 | 0 |  | 428640
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 61 | 38 | 34 | 34 | 34 | 34 | 34 | 34 | 37 | 48 | 51 | 51 | 51 | 51 | 51 | 53 | 68 | 68 |  | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 1286327
| Daudkandi 200 MW PP (B.Trac) | [20 empty] | 50 | 10 | 100 |  |  |  | 88512
14 | Titas 50 MW Peaking PP | [11 empty] | 13 | 20 | 20 | 20 | 20 | 26 | 30 |  | 28 | 28 | 28 | 28 | 29 | 13 | 0 | 267696
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 30 | 30 | 0 |  |  |  | 15 | 30 | 32 | 32 | 32 | 32 | 33 | 32 | 32 | 32 | 35 | 65 |  | 65 | 65 | 65 | 65 | 65 | 30 | 0 | 812945
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 0 | [7 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 133818
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4 | 204 | 210 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 130 | 120 | 120 | 120 | 120 | 116 | 120 | 117 |  | 192 | 210 | 210 | 206 | 210 | 210 | 210 | 3938000
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 10 | 0 | [5 empty] | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 207504
33 | Ashuganj 225 MW CCPP | 220 | 182 | 181 | 181 | 181 | 200 | 196 | 205 | 183 | 210 | 183 | 186 | 183 | 184 | 184 | 204 | 70 | 70 |  | 115 | 169 | 210 | 201 | 201 | 191 | 197 | 4318000
34 | Ashuganj 450 MW CCPP(South)
| Ashuganj 450 MW CCPP(North) | 280 | 275 | 275 | 275 | 275 | 340 | 330 | 320 | 305 | 350 | 310 | 310 | 310 | 310 | 310 | 355 | 305 | 310 |  | 310 | 325 | 310 | 310 | 305 | 305 | 300 | 7785700
| Ashuganj 420 MW CCPP(East) | 325 | 325 | 317 | 317 | 317 | 345 | 360 | 360 | 387 | 393 | 316 | 345 | 347 | 346 | 337 | 337 | 347 | 357 |  | 367 | 357 | 347 | 317 | 297 | 320 | 307 | 8120100
35 | Ashuganj 55 MW PP (Precision) | 5 | 0 | [14 empty] | 3 | 20 |  | 30 | 30 | 40 | 20 | 20 | 20 | 20 | 207840
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 387 | 355 | 353 | 353 | 352 | 352 | 377 | 392 | 397 | 393 | 393 | 391 | 392 | 391 | 392 | 385 | 382 | 372 |  | 371 | 366 | 366 | 365 | 360 | 359 | 352 | 9084930
40 | Meghnaghat 450 MW CCPP(MPL)
41 | Haripur 360MW CCPP(HPL) | 282 | 277 | 286 | 289 | 287 | 285 | 283 | 265 | 268 | 273 | 265 | 252 | 252 | 241 | 250 | 244 | 242 | 240 |  | 238 | 233 | 233 | 220 | 222 | 205 | 212 | 6126000
42 | RPCL 210MW CCPP | 111 | 110 | 110 | 111 | 110 | 110 | 54 | 53 | 53 | 47 | 47 | 44 | 43 | 33 | 33 | 35 | 51 | 30 |  | 43 | 60 | 54 | 68 | 71 | 72 | 50 | 1489920
43 | Sutiakhali 50 MW Solar PP
44 | Fenchugonj CCPP Phase-1 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 715000
45 | Fenchugonj CCPP Phase-2 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 978120
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 64 | 64 | 63 | 63 | 63 | 62 | 63 | 63 | 63 | 61 | 62 | 61 | 60 | 61 | 61 | 60 | 62 | 62 |  | 62 | 62 | 62 | 62 | 63 | 63 | 63 | 1495008
48 | Shahjibazar 86MW PP (Shahjibazar) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 86 |  | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 1146240
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 122 | 20 | 25 | 25 | 25 | 20 | 75 | 88 | 88 | 112 |  | 118 |  | 135 | 156 | 156 | 157 | 157 | 3102950
51 | Sylhet 20 MW GTPP | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 19 | 19 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 19 | 19 | 19 | 19 | 20 | 19 | 20 | 444000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 251100
54 | Hobiganj 11MW PP Cofidence-E
55 | Fenchugonj 51 MW PP (Barakatullah) | 22 | 22 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 |  | 48 | 51 | 51 | 22 | 22 | 22 | 22 | 696000
56 | Shahjahanulla 25 MW PP | [25 empty] | 0 | 0
57 | Bibiana-II 341 MW CCPP (Summit) | 260 | 270 | 280 | 280 | 270 | 290 | 310 | 290 | 290 | 310 | 300 | 310 | 280 | 280 | 280 | 300 | 310 | 270 |  | 290 | 305 | 300 | 310 | 290 | 270 | 280 | 7066500
| Bibiyana South 400 MW | 400 | 400 | 370 | 370 | 370 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 390 | 360 |  | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 9429500
58 | Nababganj 55 MW PP (Southern power ) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 431578
59 | Tangail Palli Power Gen 22 MW | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 148560
60 | Barabkunda 22 MW PP (Regent)
61 | Narshingdi 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  |  | 16 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 363744
62 | Tangail 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 17 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 18 | 443376
63 | Impoprt (Tripura) | 90 | 88 | 84 | 84 | 84 | 92 | 90 | 100 | 110 | 110 | 110 | 116 | 116 | 116 | 114 | 110 | 114 | 132 |  | 118 | 116 | 118 | 112 | 114 | 100 | 100 | 2531520
64 | Malancha, Ctg. EPZ (United) | 17 | 20 | 34 | 38 | 38 | 40 | 38 | 23 | 6 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 2 | 3 | 2 | 9 | 16 | 17 | 15 | 336480
65 | Feni 22MW PP (Doreen) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 20 | 20 | 20 | 20 | 20 | 20 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 493992
66 | Feni 11 MW PP (Doreen) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 174780
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 21 | 14 | 14 | 13 | 13 | 8 | 13 | 14 | 14 | 14 | 14 |  | 16 | 16 | 24 | 24 | 28 | 33 | 33 | 547100
68 | Cumilla 25 MW PP (Summit) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 9 | 15 | 15 | 15 | 15 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 337770
69 | Summit Ashulia | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 528000
70 | Summit Madhabdi | 28 | 28 | 28 | 28 | 28 | 28 | 29 | 3 | 9 | 9 | 9 | 9 | 0 | 3 | 9 | 9 | 14 | 28 |  | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 447840
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 820080
72 | Rupganj 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 8 | 25 | 17 | 25 | 25 | 25 | 25 | 25 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 647500
73 | Ghorashal 108MW PP (Regent) | 74 | 74 | 73 | 32 | 32 | 65 | 74 | 74 | 74 | 74 | 74 | 75 | 75 | 72 | 72 | 74 | 76 | 76 |  | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 1652863
| Feni Lanka Power | [6 empty] | 11 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 34 | 34 | 52 | 52 |  | 52 | 52 | 52 | 63 | 63 | 63 | 17 | 616740
| Chowmuhani 113 MW | 9 | 0 |  |  |  |  | 5 | 9 | 9 | 9 | 9 | 9 | 9 | 8 | 17 | 68 | 104 | 105 |  | 101 | 107 | 108 | 106 | 107 | 64 | 15 | 888720
| Manikgonj 162MW PP(MPGL) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 466560
77 | Siddhirganj 100 PP(Dutch Bangla) | [15 empty] | 1 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 0 | 0 | 46080
78 | Gazipur 52 MW PP | [6 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 10 | 16 | 17 |  | 17 | 17 | 17 | 17 | 17 | 8 | 0 | 193920
79 | Kodda 150MW PP | [6 empty] | 16 | 16 | 16 | 16 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 |  | 48 | 48 | 48 | 48 | 48 | 48 | 16 | 719040
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | [15 empty] | 4 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 |  | 66437
| Gazipur 100 MW PP | 34 | 34 | 17 | 17 | 17 | 17 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 88 | 88 | 88 |  | 88 | 88 | 88 | 88 | 88 | 34 | 34 | 1151784
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 1 | 2 | 3 | 4 | 4 | 4 | 3 | 2 | 1 | 0 | [9 empty] | 25801
| Jodiac Power | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 450298
| Karnaphuli Power Ltd. | 56 | 55 | 55 | 17 | 17 | 20 | 51 | 51 | 55 | 55 | 55 | 62 | 72 | 72 | 78 | 91 | 91 | 91 |  | 91 | 92 | 92 | 92 | 92 | 65 | 54 | 1589084
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP ( Summit) | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 152 | 150 | 152 | 152 | 152 | 153 | 152 | 155 | 150 | 152 |  | 154 | 152 | 152 | 152 | 152 | 152 | 145 | 3630487
87 | Meghnaghat 100 MW(IEL) | 9 | 8 | 8 | 9 | 9 | 8 | 8 | 9 | 8 | 9 | 9 | 8 | 9 | 8 | 9 | 9 | 17 | 17 |  | 10 | 9 | 8 | 9 | 9 | 8 | 9 | 216000
| Meghnaghat 104 MW PP (OPCL) | [6 empty] | 1 | 11 | 14 |  | 2 | 16 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 10 | 17 | 241920
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 22 | 22 | 0 |  |  |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 452640
92 | Fenchuganj 44MW (Energyprima) | 20 | 20 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 44 | 43 | 43 | 43 | 45 | 46 | 49 | 50 |  | 50 | 50 | 50 | 20 | 20 | 20 | 20 | 692856
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 10 | 10 | 10 | 27 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1105173
94 | Gagnagar 102 MW PP (Digital Power) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 267408
95 | Patenga 50MW PP (Baraka) | 39 | 0 |  |  |  |  | 2 | 24 | 26 | 27 | 32 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 32 | 33 | 33 | 34 | 20 | 586080
96 | Chattogram 108 MW PP (ECPV) | [9 empty] | 2 | 5 |  |  |  |  | 3 | 11 | 12 | [7 empty] | 0 | 41280
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 15 | 0 |  |  |  |  | 2 | 15 | 15 | 15 | 15 | 25 | 25 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 | 15 | 15 | 15 | 15 | 0 | 314956
100 | Manikganj 55 MW PP (Northern) | [9 empty] | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 0 | 0 | 438214
101 | Kushiara 163 MW CCPP (KP)
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 | 1 | 1 | 2 | 2 | 2 | 1 | 1 | 1 | 0 | [9 empty] | 10050
103 | Kamalaghat 54 MW PP(Banco Energy) | [15 empty] | 17 | 17 | 17 |  | 54 | 54 | 54 | 17 | 17 | 17 | 17 | 201960
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 37 | 37 | 37 | 37 | 37 | 37 | 46 | 47 | 47 | 46 | 47 | 58 | 48 | 58 | 58 | 48 | 48 | 57 |  | 57 | 48 | 48 | 48 | 48 | 48 | 48 | 1125600
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 16 | 16 | 0 |  |  |  | 5 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 18 | 30 |  | 35 | 35 | 30 | 35 | 35 | 22 | 18 | 432288
115 | Juldah 100 MW PP Unit-3 (Acorn) | 25 | 25 | 0 |  |  | 0 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 517440
116 | Chandpur 200MW (Desh energy) | [12 empty] | 7 |  |  |  | 2 | 15 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 139200
117 | Ashuganj 150MW PP (Midland) | 5 | 6 | 6 | 6 | 6 | 5 | 6 | 6 | 6 | 5 | 6 | 6 | 6 | 6 | 6 | 5 | 6 | 6 |  | 6 | 6 | 6 | 6 | 5 | 6 | 6 | 152218
118 | Bibiyana-III 400 MW CCPP | 366 | 364 | 366 | 365 | 365 | 396 | 362 | 380 | 362 | 408 | 366 | 363 | 366 | 366 | 365 | 397 | 367 | 367 |  | 366 | 365 | 366 | 365 | 366 | 366 | 366 | 8979000
| Jamalpur 115 MW PP (United) | 8 | 0 |  |  |  |  | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 47 |  | 47 | 47 | 47 | 47 | 47 | 47 | 28 | 630000
| Anwara 300 MW PP (United) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 100 | 100 | 110 | 112 | 113 | 113 | 121 | 103 | 104 | 278 |  | 278 | 282 | 283 | 69 | 16 | 16 | 16 | 2017309
| Juldah unit-2 (Acorn) | 25 | 0 |  |  |  |  | 17 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 0 | 455040
| Anlima Energy Ltd. | 34 | 34 | 34 | 17 | 17 | 18 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 51 | 60 |  | 68 | 68 | 68 | 68 | 68 | 68 | 75 | 1050055
| Bhairob 54.5 MW | [7 empty] | 12 |  |  | 4 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 280080
| Spectra Solar Plant Ltd. | [6 empty] | 0 | 3 | 0 | 13 | 17 | 19 | 18 | 17 | 11 | 6 | 2 | [9 empty] | 112721
| Chandpur 115(Doreen) | 36 | 35 | 36 | 17 | 17 | 20 | 36 | 36 | 36 | 36 | 36 | 36 | 35 | 36 | 36 | 36 | 66 | 94 |  | 94 | 94 | 94 | 94 | 89 | 49 | 32 | 1158720
| Kanchan Purbachal Power Generation Ltd. | 17 | 0 |  |  |  |  | 15 |  |  |  |  | 1 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 270360
| Mirsharai 150 MW (Oil) | [10 empty] | 7 | 18 | 13 | 9 |  |  | 7 | [8 empty] | 0 | 46836
Mirsharai 150 MW (Gas)
120 | Eastern Zone Total | 4638 | 4411 | 4174 | 4066 | 4053 | 4309 | 4540 | 4583 | 4674 | 4750 | 4758 | 4912 | 4896 | 4859 | 4943 | 5176 | 5151 | 5466 |  | 5707 | 5739 | 5860 | 5624 | 5441 | 5084 | 4701 | 118566349
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | [8 empty] | 16 | 32 | 32 | 32 | 32 | 32 | 32 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 0 | 315840
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [17 empty] | 50 |  | 43 | 43 | 43 | 38 |  |  |  | 149280
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | [22 empty] | 17 | 17 | 17 | 0 | 41760
130 | Mongla Orion 100 MW Solar PP | [6 empty] | 1 | 10 | 23 | 36 | 47 | 56 | 57 | 52 | 36 | 18 | 4 | [9 empty] | 345600
131 | Rampal 1320 MW (BIFPCL)
132 | United Payra Power Ltd. | [10 empty] | 33 | 54 | 54 | 54 | 54 | 17 | 17 | 54 |  | 100 | 134 | 150 |  |  | 54 | 54 | 668400
133 | Bhola Nutan Biddut BD LTD (GAS) | 160 | 160 | 160 | 160 | 160 | 160 | 220 | 220 | 220 | 220 | 220 | 175 | 200 | 218 | 218 | 218 | 218 | 209 |  | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 4899000
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [17 empty] | 8 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 98880
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 178 | 188 | 187 | 187 | 187 | 187 | 188 | 187 | 186 | 182 | 182 | 182 | 182 | 179 | 178 | 173 | 181 | 177 |  | 179 | 182 | 184 | 186 | 188 | 188 | 188 | 4462405
140 | Bhola 33 MW PP (Venture) | 22 | 20 | 19 | 19 | 18 | 20 | 19 | 19 | 18 | 18 | 15 | 20 | 21 | 20 | 17 | 16 | 17 | 24 |  | 24 | 24 | 25 | 24 | 24 | 24 | 22 | 479500
141 | Noapara 100 MW PP (Bangla Trac) | [25 empty] | 0 | 0
142 | Noapara 40 MW PP (Khanjahan Ali) | [16 empty] | 8 | 8 |  | 8 | 8 | 8 | 8 |  |  | 0 | 32625
143 | Gopalganj 100 MW Peaking PP | [16 empty] | 43 | 86 |  | 78 | 75 | 75 | 70 |  |  |  | 329728
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | [6 empty] | 7 | 15 | 15 | 15 | [7 empty] | 7 |  | 53 | 105 | 105 | 105 | 67 | 58 | 0 | 467852
146 | Bheramara HVDC | 772 | 772 | 772 | 761 | 761 | 761 | 908 | 784 | 600 | 588 | 676 | 811 | 907 | 906 | 902 | 902 | 903 | 826 |  | 642 | 670 | 658 | 733 | 907 | 907 | 906 | 19086545
147 | Bheramara 410 MW CCPP
148 | Payra 1320 MW | 1050 | 970 | 950 | 960 | 950 | 970 | 1020 | 1130 | 1170 | 1172 | 1142 | 1100 | 1080 | 1090 | 1070 | 1070 | 1100 | 1100 |  | 1150 | 1192 | 1192 | 1202 | 1192 | 1130 | 1130 | 28038800
149
150 | Barapukuria TPP Unit-1 | 82 | 81 | 81 | 82 | 81 | 80 | 81 | 80 | 82 | 81 | 80 | 83 | 82 | 82 | 81 | 82 | 81 | 81 |  | 81 | 82 | 82 | 82 | 82 | 83 | 81 | 1937018
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 250 | 250 | 250 | 250 | 251 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 251 |  | 250 | 250 | 251 | 250 | 250 | 250 | 250 | 6060100
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [12 empty] | 32 | 31 | 26 | 26 | 26 | 34 |  | 34 | 26 | 26 | 26 |  |  |  | 247748
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 0 | 2 | 2 | 3 | 4 | 3 | 3 | 2 | 1 | 0 | [9 empty] | 24000
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 186 | 130 | 130 | 130 | 130 | 130 | 154 | 213 | 208 | 206 | 205 | 199 | 194 | 192 | 191 | 191 | 192 | 195 |  | 198 | 198 | 199 | 202 | 205 | 209 | 209 | 4689027
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 340 | 367 | 346 | 307 | 308 | 307 | 415 | 420 | 420 | 423 | 417 | 388 | 370 | 350 | 340 | 328 | 324 | 277 |  | 341 | 341 | 341 | 433 | 446 | 436 | 440 | 8798545
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [11 empty] | 4 | 4 | 13 | 13 | 20 | 19 | 19 |  | 19 | 19 | 21 | 21 |  |  |  | 146775
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 21 | 20 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 19 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 472320
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 176796
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | [7 empty] | 16 | 16 | 25 | 25 | 25 | 25 | 25 |  |  |  | 25 |  | 25 | 34 | 34 | 34 | 16 | 16 | 0 | 307860
167 | Katakhali 50 MW Peaking PP | [10 empty] | 10 | 16 | 18 | 32 |  |  | 14 | 30 |  | 35 | 40 | 41 | 40 |  |  |  | 180648
168 | Santahar 50 MW Peaking PP | [11 empty] | 9 | 21 | 35 | 35 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 |  |  | 0 | 280797
169 | Natore 52 MW PP (Rajlanka) | [7 empty] | 8 | 8 | 8 | 8 | [6 empty] | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 0 | 78965
170 | Chapainawabganj 100 MW Peaking PP | [10 empty] | 42 | 42 | 42 | 42 |  |  | 47 | 96 |  | 97 | 97 | 97 | 97 |  |  | 0 | 572386
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 35 | 0 | [9 empty] | 11 | 50 | 35 |  |  | 4 | 60 |  | 92 | 94 | 94 | 94 | 94 | 35 | 0 | 716160
172 | Confidence Power Bogura Unit-1 113 MW | 35 | 0 | [8 empty] | 35 | 35 | 35 | 35 |  |  | 60 | 95 |  | 95 | 95 | 95 | 95 | 95 | 35 | 0 | 764448
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | 35 | 0 | [6 empty] | 40 | 40 | 40 | 37 | 40 | 35 |  |  | 56 | 74 |  | 85 | 85 | 85 | 85 | 70 | 34 | 34 | 762691
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 2 | 3 | 4 | 5 | 5 | 5 | 4 | 2 | 1 | [9 empty] | 30219
178 | Energypac Power Venture Thakurgaon Ltd. | 36 | 0 |  |  |  |  | 35 | 115 | 115 | 35 | 35 | 35 | 35 | 35 |  |  | 1 | 49 |  | 113 | 113 | 113 | 113 | 113 | 114 | 54 | 1235328
| Intraco Solar 30 MW | [6 empty] | 0 | 4 | 10 | 18 | 23 | 26 | 26 | 22 | 14 | 8 | 2 | [9 empty] | 153940
Adani Power Jharkhanda Ltd
178 | Teesta Solar Limited | [7 empty] | 22 | 58 | 94 | 122 | 138 | 134 | 116 | 76 | 37 | 9 | [9 empty] | 806290