## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2023-02-01 | Wednesday
|  | Date (day): | 2023-02-01 |  | Wednesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 9631.6 | MW |  |  | (b) At Evening Peak Hour : |  | 10873 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2023-01-31 | 2023-02-01 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 160 | 220 | 220 | 220
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Macine problem
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 | 365 |  | Gas shortage
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 68 | 75 | 71 | 71 | 37 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 388 | 339 | 350 | 350 | 62 |  | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 227 | 183 | 180 | 180 | 180 |  | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 0 | 0 |  | 450 | Under maint
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 50 | 50 | 25 | 50 | 50 |  | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 152 | 145 | 150 | 150 | 185 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 51 | 51 | 17 | 17 | 85 |  | Fuel shortage
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 15 | 15 | 15 | 15 | 40 |  | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 16 | 16 | 19 | 19 |  |  | Engine problem
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 42 | 50 | 50 | 50 | 50 |  | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 50 | 50 | 48 | 48 | 54 |  | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 17 | 17 | 35 | 19 |  | Fuel shortage
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 32 | 48 | 32 | 48 | 101 |  | Fuel shortage
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 35 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 17 | 17 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 48 | 49 | 51 | 51 |  | 29 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 16 | 25 | 25 |  | 3 | Engine problem
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 8 | 16 | 8 | 16 | 36 |  | Fuel shortage
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 48 | 147 | 32 | 145 | 200 |  | Fuel shortage
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 0 | 300 |  | Fuel shortage
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Fuel shortage
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Fuel shortage
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 17 | 17 | 17 | 17 | 132 |  | Fuel shortage
36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 52 | 35 | 52 | 53 |  | Fuel shortage
37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 55 | 54 | 17 | 55 | 49 |  | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 35 | 17 | 17 | 17 | 145 |  | Fuel shortage
39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 27 | 0 | 30 | 0
40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 17 | 17 | 17 | 38 |  | Fuel shortage
| Dhaka area Total |  |  |  |  | 6263 | 5847 | 1685 | 1749 | 1528 | 1791 | 2977 | 1172
41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 8 | 17 | 8 | 17
43 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 20 | 0 | 20 | 0
44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 26 | 33 | 25 | 33 | 25 |  | Fuel shortage
45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 30 | 30 | 30 | 30 | 200 |  | Low Water Level
46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 152 | 156 | 160 | 160 |  |  | ST Under S/D
47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 34 | 88 | 34 | 85 | 20 |  | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 32 | 32 | 24 | 32 | 66 |  | Fuel shortage
50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 83 | 51 | 83 | 19 |  | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 22 | 22 | 22 | 22 | 78 |  | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 25 | 25 | 25 | 25 | 75 |  | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 22 |  | Gas shortage
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 5 | 5 | 5
54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 105 | 273 | 100 | 300
57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 17 | 17 | 17 | 17 | 37 |  | Fuel shortage
58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 54 | 92 | 54 | 92 | 18 |  | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 25 | 25 | 25 | 75 |  | Fuel shortage
60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 92 | 107 | 107 | 107 |  | 9 | Engine problem
| Mirsharai 150 MW |  | Gas/HSD | BPDB-RPCL | 18.5*9 | 0 | 0 | 18 | 0 | 0 | 0
| Chattogram area Total |  |  |  |  | 2442 | 2382 | 666 | 1005 | 712 | 1033 | 1103 | 159
61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 0 | 94 | 100 | 100 | 121 |  | ST Under S/D
63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 345 | 285 | 300 | 300 |  |  | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Macine problem
65 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 382 | 300 | 320 | 320 | 80 |  | Gas shortage
66 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 42 | 42 | 42 | 42 |  |  | gas shortage
67 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 55 | 51 | 52 | 51 | 51 | 45
68 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 112 | 8 | 8 | 8 | 187 |  | Gas shortage
69 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 25 | 25 | 25 | 25
70 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 11 | 5 | 6 | 6 | 144 |  | Fuel shortage
71 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 21 | 20 | 25 | 25 |  | 27 | Engine problem
72 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under Maint.
73 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 34 | 34 | 34 | 34 | 166 |  | Fuel shortage
74 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 19 | 19 |  |  | Engine problem
75 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 5 | 5 | 5 |  |  | Engine problem
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 110 | 114 | 135 | 152
76 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 14 | 23 | 23 | 23 |  |  | Engine problem
77 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 8 | 8 | 8 | 44 |  | Fuel shortage
78 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 21 | 21 | 20 | 20 |  | 5 | Engine problem
79 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel shortage
80 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 17 | 17 | 17
81 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 118 | 9 | 113
82 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 17 |  | 37 | Engine problem
83 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 36 | 72 | 17 | 94 | 21 |  | Fuel shortage
| Cumilla Area Total |  |  |  |  | 3309 | 3285 | 1271 | 1279 | 1181 | 1379 | 1142 | 592
84 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 44 | 55 | 45 | 100 | 102 |  | Gas shortage
85 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 22 | 22 | 22
86 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0
87 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
88 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 57 | 58 | 48 | 55 | 145 |  | Fuel shortage
89 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 28 | 47 | 47 | 47 | 68 |  | Fuel shortage
90 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 0 | 0 | 50 | 0
91 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 6 | 6 | 6 | 16 |  | Fuel shortage
| Mymensingh Area Total |  |  |  |  | 717 | 614 | 156 | 188 | 219.6 | 230 | 102 | 0
92 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 30 | 30 | 30 | 30 |  | 40 | Machine problem.
93 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 43 | 43 | 43 | 43 |  | 47 | Machine problem
94 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 112 | 112 | 110 | 110 |  | 53 | ST Under maint
95 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
96 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 22 | 0 | 0 | 0 |  |  | Gas shortage
97 | Fenchuganj 44MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 46 | 0 | 0 | 0 |  |  | Gas shortage
98 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 8 | 8 |  | 3 | Engine problem
99 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 61 | 65 | 65 | 65
100 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 84 | 84 | 60 | 81
101 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
102 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 218 | 218 | 220 | 220
103 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 19 | 19
104 | Sylhet 50MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Gas shortage
105 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 8 | 0 | 0 | 0 |  | 25 | Engine problem
106 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 260 | 320 | 320 |  |  | FGMO
107 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 238 | 402 | 400 | 400 |  |  | FGMO
108 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
109 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 220 | 400 | 400 | 400 |  | 163
| Sylhet Area Total |  |  |  |  | 2472 | 2427 | 1428 | 1650 | 1685 | 1706 | 0 | 761
110 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 908 | 765 | 920 | 920
111 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 0 | 49 | 16 | 49 | 49 |  | Fuel shortage
112 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 45 |  | 9 | Engine problem
113 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
114 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 80 |  | 29 | Engine problem
115 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 | 410 |  | Gas shortage.
116 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 8 | 0 | 8 | 32 |  | Fuel shortage
117 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Fuel shortage
118 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 17 | 53 | 17 | 54 | 51 |  | Fuel shortage
119 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 85 | 50 | 85 | 85 |  | 20 | Engine problem
120 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 64 | 0 | 100 | 0
| Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 0 | 0 | 50 | 121 | 120 | 120 |  |  | On test.
| Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 660*2 | 617 | 617 | 0 | 0 | 0 | 0 |  |  | Coal Shortage.
| Khulna Area Total |  |  |  |  | 3005 | 3001 | 1124 | 1046 | 1258 | 1361 | 888 | 58
121 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 16 | 16 | 16 | 16 | 94 |  | Fuel shortage
122 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 19 | 24 | 19 | 25 |  | 15 | Engine problem
123 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 175 | 178 | 180 | 180
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
124 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 1122 | 1244 | 1200 | 1244
125 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 200 | 221 | 220 | 220
126 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 54 | 17 | 150
127 | Barisal 307 MW |  | Coal | BCPCL | 307*1 | 307 | 307 | 0 | 0 | 0 | 0 |  |  | Coal Shortage.
| Barisal Area Total |  |  |  |  | 2265 | 2265 | 1549 | 1737 | 1652 | 1835 | 94 | 15
128 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
129 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 34 | 0 | 34 |  | 18 | Engine problem
130 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 5 | 20 | 0 | 20 |  | 51 | Engine problem
131 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
132 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 42 | 8 | 25 | 42 |  | 8 | Engine problem
133 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 16 | 40 | 0 | 40 |  | 10 | Engine problem
134 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
135 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
136 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 180 | 175 | 180 | 180 |  | 40 | Gas shortage
137 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 424 | 439 | 400 | 400
138 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 6 | 35 | 0 | 35 |  | 15 | Engine problem
139 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 18 | 22 | 22 | 22
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
140 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 8 | 8 |  |  | Engine problem
141 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 8 | 8 | 8 | 44 |  | Fuel shortage
142 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 42 | 96 | 0 | 95 |  | 9 | Engine problem
143 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel shortage
144 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 50 | 50 | 50 | 50 | 63 |  | Fuel shortage
145 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 35 | 75 | 35 | 75 | 38 |  | Fuel shortage
146 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
| Adani Power Jharkhanda Ltd |  | Coal | Import | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | On test.
| Rajshahi Area Total |  |  |  |  | 2179 | 2129 | 831 | 1010 | 734 | 1009 | 946 | 151
147 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 80 | 80 | 80 | 80
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
148 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 250 | 250 | 250 | 250 |  | 24
149 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
150 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
151 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 56 | 78 | 49 | 84 | 29 |  | Fuel shortage
152 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5 | 0 | 8 | 0
153 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 35 | 115 | 115 | 115
154 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 24 | 0 | 30 | 0
| Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 0 | 0 | 136 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 830 | 750 | 586 | 523 | 662 | 529 | 69 | 109
| Total |  |  |  |  | 23482 | 22700 | 9296 | 10187 | 9631.6 | 10873 | 7321 | 3017
A. |  | 2023-01-31 | (Yesterday) |  |  |  |  | Tuesday
1 | Highest Generation : |  |  | 10187 | MW at | 19:30 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:30 | hrs.
2 | Minimum Generation : |  |  | 6945 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 10350 | MW
3 | Day peak Generation : |  |  | 9296 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 9820.13 | MW
4 | Evening peak Generation : |  |  | 10187 | MW at | 19:30 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 150 | MW
5 | Total Energy Generation : |  | 210.8595 | MKWHr | By Solar | 1.6523 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Gas : | 113.3493 | MKWHr |  | By Oil: | 35.5389 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 36.038 | MKWHr |  | By Hydro: | 0.72576 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 7321 | MW | Dhaka | 3648.13 | 3618.13 |  | 30 |  | 18:00 |  | 220.2564
|  |  | For Plants S/D or M/C prob = |  |  | 3017 | MW | Chittagong | 851.5 | 851.5 |  | 0 |  | 19:00 |  | 170
|  |  | Total = |  |  | 10338 | MW | Khulna | 1140 | 1140 |  | 0 |  | 19:30 |  | 150
7 | Total Gas Supplied : |  |  | 884.35 | MMCFD |  |  | Rajshahi | 1042.9 | 1042.9 |  | 0 |  | 20:00 |  | 140
8 | Fuel Cost : | i) Gas : | Taka | 117102968.928 | ii) Oil : | Taka | 443970153.71 | Comilla | 855 | 855 |  | 0 |  | 21:00 |  | 78
|  | iii) Coal : |  | 296030740.29 | Total | Taka | 857103862.928 | Mymensingh | 919 | 799 |  | 120 |  | 22:00 |  | 0
9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0 | MKWHr. | Sylhet | 367 | 367 |  | 0 |  | 23:00 |  | 0
| ii) During Peak Demand : |  |  | 1146 | MW (E to W) at | 19:30 | hrs | Barisal | 269.6 | 269.6 |  | 0 |  | 24:00 |  | 0
| iii) Maximum : |  |  | 670 | MW at | 7:00 | hrs | Rangpur | 727 | 727 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 29.6° C |  |  | Total | 9820.13 | 9670.13 |  | 150
B. |  | 2023-02-01 | (Today) |  |  |  | Wednesday |  |  | Probable max. temperature in Dhaka |  |  | 30.5° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 10500 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 10873 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 9500 | MW
4 | Reserve(Generation end) |  |  |  | 373 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 217.3382 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 7246 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.2109 | MKWHr. | ii) HVDC Flow at Peak Time |  | 765 | MW at | 19:30 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.3443 | MKWHr. | iii) Maximum HVDC Flow : |  | 910 | MW at | 23:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 83.67 |  | (b) Today: | 86.59 |  | (c) Rule Curve: |  | 97
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2023-01-31
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 210 | 0 | 0 | 72 | 0 | 381 | 248 |  | 0 | 0 | 153 | 24 | 17 | 15 | 0 | 0 | 0 | 27 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 16 | 22 | 29 | 28 | 25 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 164 | 0 | 0 | 0 |  | 6 | 0 | 0 | 22 | 0 | 3 | 0 | 18 | 0 | 0 | 0 | 290 | 0 | 135 | 8 | 0 | 42 | 10 | 0 | 51 | 0 | 0 | 8 | 21 | 5 | 33 | 21 | 90 | 109 | 0 | 19 | 0 | 30 | 43 | 31 | 49 | 0 | 0 | 66 | 10 | 0 | 218 | 19 | 0 | 10 | 265 | 16 | 8 | 0 | 32 | 0 | 0 | 49 | 0 | 35 | 0 | 25 | 34 | 5 | 367 | 28 | 17 | 34 | 0 | 16 | 17 | 55 | 0 | 0 | 0 | 220 | 17 | 0 | 17 | 107 | 0 | 17 | 0 | 36 | 0 | 331 | 0 | 0 |  | 908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 81 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 215 | 0 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 221 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4617 | 3328 | 7945 | 3262 | 908 | 1571 | 0 | 704 | 1331 | 30 | 49 | 0 | 90 | 0 | 0 | 83.68
2:00 | 0 | 0 | 170 | 0 | 0 | 72 | 0 | 381 | 253 |  | 0 | 0 | 153 | 25 | 17 | 15 | 0 | 0 | 0 | 25 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 16 | 22 | 29 | 28 | 25 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 165 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 295 | 0 | 139 | 8 | 0 | 42 | 10 | 0 | 51 | 0 | 0 | 0 | 21 | 5 | 33 | 21 | 86 | 108 | 0 | 19 | 0 | 30 | 43 | 11 | 30 | 46 | 0 | 66 | 10 | 0 | 218 | 19 | 0 | 10 | 270 | 16 | 8 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 6 | 344 | 28 | 17 | 34 | 0 | 16 | 17 | 55 | 0 | 0 | 0 | 220 | 17 | 0 | 17 | 107 | 0 | 17 | 0 | 0 | 0 | 331 | 0 | 0 |  | 813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 81 | 0 | 251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 900 | 221 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4382 | 3036 | 7418 | 3172 | 813 | 1527 | 0 | 508 | 1232 | 30 | 50 | 0 | 86 | 0 | 0 | 83.68
3:00 | 0 | 0 | 172 | 0 | 0 | 36 | 0 | 375 | 249 |  | 0 | 0 | 155 | 25 | 17 | 15 | 0 | 0 | 0 | 25 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 16 | 22 | 29 | 28 | 25 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 295 | 0 | 136 | 8 | 0 | 42 | 10 | 0 | 15 | 0 | 0 | 0 | 21 | 5 | 33 | 21 | 84 | 107 | 0 | 19 | 0 | 30 | 43 | 11 | 30 | 112 | 0 | 40 | 10 | 0 | 218 | 19 | 0 | 10 | 270 | 16 | 8 | 0 | 0 | 0 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 6 | 349 | 0 | 17 | 34 | 0 | 16 | 17 | 55 | 0 | 0 | 0 | 220 | 17 | 0 | 17 | 17 | 0 | 17 | 0 | 0 | 0 | 331 | 0 | 0 |  | 814 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 81 | 0 | 251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 900 | 173 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4241 | 3000 | 7241 | 3145 | 814 | 1485 | 0 | 400 | 1232 | 30 | 51 | 0 | 84 | 0 | 0 | 83.68
4:00 | 0 | 0 | 170 | 0 | 0 | 34 | 0 | 321 | 270 |  | 0 | 0 | 155 | 25 | 1 | 15 | 0 | 0 | 0 | 25 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 16 | 22 | 29 | 28 | 25 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 295 | 0 | 136 | 8 | 0 | 42 | 10 | 0 | 15 | 0 | 0 | 0 | 21 | 5 | 33 | 21 | 82 | 109 | 0 | 19 | 0 | 30 | 43 | 11 | 10 | 112 | 0 | 40 | 10 | 0 | 218 | 19 | 0 | 10 | 265 | 16 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 6 | 344 | 0 | 17 | 34 | 0 | 16 | 17 | 17 | 0 | 0 | 0 | 220 | 17 | 0 | 17 | 17 | 0 | 17 | 0 | 0 | 0 | 337 | 0 | 0 |  | 813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 81 | 0 | 251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 900 | 173 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4077 | 2922 | 6999 | 3053 | 813 | 1443 | 0 | 296 | 1232 | 30 | 50 | 0 | 82 | 0 | 0 | 83.67
5:00 | 0 | 0 | 170 | 0 | 0 | 34 | 0 | 321 | 274 |  | 0 | 0 | 155 | 25 | 0 | 15 | 0 | 0 | 0 | 25 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 16 | 22 | 29 | 28 | 25 | 3 | 0 | 30 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 295 | 0 | 0 | 8 | 0 | 42 | 21 | 0 | 15 | 0 | 0 | 0 | 21 | 5 | 33 | 21 | 82 | 109 | 0 | 19 | 0 | 30 | 43 | 11 | 10 | 112 | 0 | 66 | 84 | 0 | 218 | 19 | 0 | 10 | 280 | 16 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 6 | 344 | 0 | 25 | 34 | 0 | 16 | 17 | 17 | 0 | 0 | 0 | 220 | 17 | 0 | 17 | 17 | 0 | 17 | 0 | 0 | 0 | 317 | 0 | 0 |  | 814 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 81 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 860 | 173 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4063 | 2882 | 6945 | 2920 | 814 | 1552 | 0 | 306 | 1191 | 30 | 50 | 0 | 82 | 0 | 0 | 83.67
6:00 | 0 | 0 | 170 | 0 | 0 | 34 | 0 | 321 | 280 |  | 0 | 0 | 155 | 25 | 15 | 15 | 0 | 0 | 0 | 25 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 16 | 22 | 29 | 28 | 25 | 8 | 0 | 30 | 0 | 0 | 0 | 1 | 162 | 0 | 0 | 0 |  | 6 | 0 | 0 | 22 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 295 | 0 | 0 | 36 | 0 | 42 | 47 | 0 | 32 | 0 | 0 | 0 | 21 | 5 | 33 | 21 | 86 | 109 | 0 | 19 | 0 | 30 | 43 | 11 | 36 | 112 | 0 | 66 | 84 | 0 | 218 | 20 | 0 | 10 | 270 | 16 | 8 | 0 | 17 | 0 | 0 | 14 | 0 | 9 | 0 | 16 | 3 | 6 | 344 | 10 | 35 | 34 | 0 | 16 | 17 | 21 | 17 | 7 | 5 | 220 | 17 | 0 | 17 | 29 | 0 | 17 | 0 | 36 | 8 | 318 | 0 | 0 |  | 814 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 21 | 0 | 8 | 81 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 355 | 2 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 880 | 170 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4391 | 3005 | 7396 | 2905 | 814 | 1715 | 0 | 569 | 1211 | 30 | 50 | 16 | 86 | 0 | 0 | 83.67
7:00 | 0 | 0 | 170 | 0 | 0 | 38 | 0 | 324 | 285 |  | 0 | 0 | 153 | 24 | 51 | 15 | 0 | 0 | 0 | 25 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 16 | 22 | 29 | 33 | 25 | 8 | 0 | 30 | 0 | 0 | 0 | 8 | 161 | 0 | 0 | 0 |  | 6 | 2 | 0 | 22 | 0 | 16 | 0 | 40 | 0 | 0 | 0 | 360 | 0 | 0 | 36 | 0 | 42 | 50 | 0 | 51 | 0 | 0 | 0 | 21 | 5 | 33 | 21 | 88 | 48 | 0 | 19 | 0 | 30 | 43 | 11 | 46 | 112 | 0 | 65 | 60 | 0 | 218 | 19 | 0 | 10 | 290 | 16 | 8 | 0 | 32 | 0 | 0 | 46 | 0 | 17 | 1 | 25 | 34 | 6 | 294 | 28 | 35 | 34 | 0 | 16 | 17 | 52 | 17 | 9 | 25 | 220 | 17 | 0 | 17 | 105 | 0 | 17 | 0 | 36 | 17 | 392 | 0 | 0 |  | 908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 8 | 0 | 21 | 0 | 8 | 83 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 327 | 17 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 940 | 221 | 0 | 14 | 0 | 2 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 2 |  | 4771 | 3261 | 8032 | 2958 | 908 | 1771 | 0 | 931 | 1273 | 30 | 50 | 18 | 88 | 5 | 72 | 83.66
8:00 | 0 | 0 | 220 | 0 | 0 | 71 | 0 | 387 | 261 |  | 0 | 0 | 153 | 21 | 51 | 15 | 0 | 0 | 0 | 25 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 16 | 22 | 28 | 33 | 25 | 8 | 0 | 30 | 0 | 0 | 0 | 8 | 163 | 0 | 0 | 0 |  | 6 | 23 | 0 | 22 | 0 | 24 | 0 | 12 | 0 | 0 | 0 | 345 | 0 | 0 | 110 | 0 | 42 | 50 | 0 | 51 | 0 | 0 | 0 | 21 | 5 | 25 | 18 | 90 | 49 | 0 | 19 | 0 | 30 | 43 | 11 | 46 | 112 | 0 | 65 | 60 | 0 | 218 | 19 | 0 | 10 | 310 | 16 | 8 | 0 | 32 | 0 | 0 | 46 | 0 | 17 | 6 | 25 | 34 | 6 | 238 | 28 | 35 | 34 | 1 | 16 | 17 | 52 | 17 | 9 | 25 | 220 | 17 | 0 | 17 | 107 | 0 | 17 | 3 | 35 | 17 | 386 | 0 | 0 |  | 908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 19 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 8 | 0 | 21 | 0 | 8 | 84 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 444 | 17 | 0 | 0 | 85 | 40 | 0 | 0 | 0 | 1090 | 220 | 0 | 54 | 1 | 19 | 0 | 50 | 0 | 0 | 4 | 0 | 0 | 23 |  | 4911 | 3721 | 8632 | 3021 | 908 | 1961 | 0 | 1052 | 1424 | 30 | 50 | 39 | 90 | 57 | 165.8835 | 83.66
9:00 | 0 | 0 | 217 | 0 | 0 | 71 | 0 | 394 | 260 |  | 0 | 0 | 152 | 27 | 51 | 15 | 0 | 0 | 0 | 25 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 16 | 22 | 28 | 33 | 8 | 8 | 0 | 30 | 0 | 0 | 0 | 8 | 155 | 0 | 0 | 0 |  | 6 | 32 | 0 | 22 | 0 | 22 | 0 | 2 | 0 | 0 | 0 | 305 | 0 | 0 | 112 | 0 | 42 | 50 | 0 | 25 | 0 | 21 | 0 | 21 | 5 | 20 | 18 | 102 | 51 | 0 | 19 | 1 | 30 | 43 | 11 | 46 | 112 | 0 | 66 | 60 | 0 | 218 | 18 | 0 | 10 | 290 | 16 | 8 | 0 | 33 | 0 | 0 | 46 | 0 | 17 | 13 | 25 | 34 | 6 | 240 | 28 | 35 | 34 | 2 | 100 | 17 | 52 | 17 | 9 | 25 | 220 | 17 | 0 | 17 | 107 | 0 | 17 | 11 | 36 | 17 | 420 | 0 | 0 |  | 909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 18 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 16 | 8 | 0 | 21 | 0 | 8 | 82 | 0 | 251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 195 | 0 | 385 | 17 | 0 | 0 | 85 | 47 | 0 | 1 | 35 | 1162 | 185 | 0 | 54 | 1 | 38 | 0 | 50 | 0 | 0 | 6 | 0 | 0 | 75 |  | 4976 | 3893 | 8869 | 3022 | 909 | 1810 | 0 | 1218 | 1495 | 30 | 50 | 85 | 102 | 148 | 173.2561 | 83.66
10:00 | 0 | 0 | 160 | 0 | 0 | 68 | 0 | 395 | 252 |  | 0 | 0 | 153 | 46 | 45 | 15 | 0 | 0 | 0 | 30 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 16 | 22 | 28 | 25 | 25 | 8 | 0 | 30 | 0 | 0 | 0 | 8 | 155 | 0 | 0 | 0 |  | 6 | 32 | 0 | 22 | 0 | 26 | 0 | 2 | 0 | 0 | 0 | 320 | 0 | 0 | 112 | 0 | 42 | 50 | 0 | 25 | 0 | 21 | 0 | 19 | 5 | 19 | 21 | 106 | 44 | 0 | 19 | 1 | 30 | 43 | 11 | 46 | 112 | 0 | 64 | 60 | 0 | 218 | 18 | 0 | 10 | 280 | 16 | 8 | 0 | 33 | 0 | 0 | 48 | 0 | 17 | 17 | 25 | 34 | 6 | 237 | 28 | 35 | 34 | 3 | 100 | 17 | 52 | 17 | 9 | 25 | 220 | 46 | 0 | 17 | 107 | 0 | 17 | 17 | 36 | 17 | 350 | 0 | 0 |  | 909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 16 | 8 | 0 | 20 | 0 | 8 | 82 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 330 | 17 | 0 | 20 | 85 | 50 | 0 | 3 | 35 | 1122 | 183 | 0 | 54 | 3 | 57 | 0 | 50 | 0 | 0 | 13 | 0 | 0 | 92 |  | 4927 | 3848 | 8775 | 2893 | 909 | 1731 | 0 | 1311 | 1454 | 30 | 50 | 85 | 106 | 206 | 175.0993 | 83.65
11:00 | 0 | 0 | 160 | 0 | 0 | 68 | 0 | 393 | 227 |  | 0 | 0 | 153 | 50 | 40 | 15 | 0 | 0 | 0 | 42 | 40 | 32 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 16 | 22 | 26 | 25 | 25 | 8 | 0 | 30 | 0 | 0 | 0 | 8 | 155 | 0 | 0 | 0 |  | 6 | 32 | 0 | 22 | 0 | 26 | 0 | 2 | 0 | 0 | 0 | 346 | 0 | 0 | 112 | 0 | 42 | 50 | 0 | 25 | 0 | 21 | 0 | 19 | 5 | 15 | 21 | 102 | 44 | 0 | 19 | 1 | 30 | 43 | 11 | 46 | 112 | 0 | 63 | 60 | 0 | 218 | 18 | 0 | 10 | 310 | 16 | 8 | 0 | 42 | 0 | 0 | 57 | 0 | 17 | 19 | 25 | 34 | 10 | 233 | 28 | 52 | 34 | 4 | 104 | 17 | 53 | 17 | 9 | 25 | 220 | 52 | 0 | 17 | 98 | 0 | 17 | 25 | 36 | 17 | 376 | 18 | 0 |  | 908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 18 | 16 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 42 | 16 | 0 | 0 | 18 | 0 | 8 | 80 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 334 | 17 | 0 | 50 | 85 | 50 | 0 | 4 | 35 | 1122 | 183 | 0 | 17 | 4 | 68 | 35 | 50 | 0 | 0 | 16 | 0 | 0 | 78 |  | 5097 | 3912 | 9009 | 2932 | 908 | 1739 | 0 | 1416 | 1452 | 30 | 68 | 143 | 102 | 219 | 222.0996 | 83.65
12:00 | 0 | 0 | 160 | 0 | 0 | 68 | 0 | 388 | 227 |  | 0 | 0 | 152 | 50 | 51 | 15 | 0 | 0 | 0 | 42 | 50 | 32 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 16 | 22 | 26 | 33 | 25 | 8 | 0 | 30 | 0 | 0 | 0 | 8 | 152 | 0 | 0 | 0 |  | 6 | 32 | 0 | 22 | 0 | 26 | 0 | 2 | 0 | 0 | 0 | 345 | 0 | 0 | 112 | 0 | 42 | 51 | 0 | 25 | 0 | 21 | 0 | 19 | 5 | 14 | 21 | 110 | 44 | 0 | 19 | 2 | 30 | 43 | 22 | 46 | 112 | 0 | 61 | 84 | 0 | 218 | 18 | 0 | 10 | 310 | 8 | 8 | 0 | 48 | 0 | 0 | 57 | 0 | 17 | 20 | 25 | 34 | 11 | 238 | 28 | 52 | 34 | 4 | 105 | 17 | 54 | 17 | 9 | 25 | 220 | 55 | 0 | 35 | 92 | 0 | 17 | 27 | 36 | 17 | 382 | 18 | 0 |  | 908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 19 | 16 | 0 | 0 | 0 | 0 | 5 | 42 | 0 | 42 | 16 | 0 | 6 | 18 | 0 | 8 | 80 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 424 | 17 | 0 | 50 | 85 | 56 | 0 | 5 | 35 | 1122 | 200 | 0 | 17 | 5 | 64 | 35 | 50 | 0 | 0 | 24 | 0 | 0 | 136 |  | 5206 | 4090 | 9296 | 2920 | 908 | 1882 | 0 | 1485 | 1452 | 30 | 68 | 154 | 110 | 287 | 234.0801 | 83.65
13:00 | 0 | 0 | 160 | 0 | 0 | 70 | 0 | 380 | 215 |  | 0 | 0 | 152 | 49 | 51 | 15 | 0 | 0 | 0 | 50 | 50 | 32 | 0 | 0 | 0 | 0 | 17 | 35 | 0 | 16 | 22 | 26 | 33 | 25 | 8 | 0 | 30 | 0 | 0 | 0 | 8 | 153 | 0 | 0 | 0 |  | 6 | 32 | 0 | 22 | 0 | 26 | 0 | 2 | 0 | 0 | 0 | 305 | 0 | 0 | 112 | 0 | 38 | 51 | 0 | 25 | 0 | 26 | 5 | 19 | 5 | 14 | 21 | 98 | 33 | 0 | 19 | 2 | 30 | 43 | 31 | 46 | 112 | 0 | 63 | 84 | 0 | 218 | 18 | 0 | 10 | 310 | 12 | 8 | 0 | 47 | 0 | 0 | 57 | 0 | 17 | 18 | 25 | 34 | 8 | 397 | 28 | 52 | 34 | 4 | 108 | 17 | 54 | 17 | 17 | 25 | 222 | 55 | 0 | 17 | 107 | 0 | 17 | 16 | 36 | 17 | 346 | 18 | 0 |  | 909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 21 | 0 | 0 | 0 | 0 | 33 | 5 | 42 | 0 | 42 | 16 | 0 | 16 | 20 | 0 | 8 | 80 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 207 | 0 | 414 | 17 | 0 | 50 | 15 | 56 | 0 | 6 | 35 | 1142 | 221 | 0 | 17 | 3 | 59 | 74 | 50 | 0 | 0 | 18 | 0 | 0 | 148 |  | 5253 | 4153 | 9406 | 3020 | 909 | 1896 | 0 | 1437 | 1472 | 30 | 68 | 202 | 98 | 274 | 245 | 83.64
14:00 | 0 | 0 | 120 | 0 | 0 | 68 | 0 | 369 | 214 |  | 0 | 0 | 153 | 50 | 51 | 15 | 0 | 0 | 0 | 50 | 50 | 32 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 16 | 22 | 26 | 33 | 25 | 8 | 0 | 30 | 0 | 0 | 0 | 8 | 154 | 0 | 0 | 0 |  | 6 | 32 | 0 | 22 | 0 | 26 | 0 | 2 | 0 | 0 | 0 | 310 | 0 | 0 | 112 | 0 | 38 | 52 | 0 | 25 | 0 | 26 | 8 | 19 | 5 | 15 | 18 | 104 | 34 | 0 | 19 | 1 | 30 | 43 | 31 | 45 | 112 | 0 | 63 | 84 | 0 | 210 | 18 | 0 | 10 | 280 | 12 | 8 | 0 | 33 | 0 | 0 | 48 | 0 | 17 | 17 | 25 | 34 | 6 | 402 | 28 | 52 | 34 | 3 | 107 | 17 | 54 | 17 | 26 | 25 | 222 | 54 | 0 | 17 | 107 | 0 | 17 | 16 | 36 | 17 | 340 | 18 | 0 |  | 908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 19 | 0 | 0 | 0 | 0 | 34 | 11 | 42 | 0 | 42 | 16 | 0 | 16 | 20 | 0 | 8 | 80 | 0 | 249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 427 | 17 | 0 | 50 | 15 | 56 | 0 | 5 | 35 | 1162 | 221 | 0 | 17 | 1 | 39 | 114 | 50 | 0 | 0 | 26 | 0 | 0 | 106 |  | 5137 | 4185 | 9322 | 2978 | 908 | 1875 | 0 | 1445 | 1491 | 30 | 68 | 209 | 104 | 214 | 230.3938 | 83.65
15:00 | 0 | 0 | 120 | 0 | 0 | 66 | 0 | 358 | 194 |  | 0 | 0 | 153 | 51 | 51 | 15 | 0 | 0 | 0 | 50 | 50 | 32 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 16 | 22 | 26 | 33 | 24 | 8 | 0 | 30 | 0 | 0 | 0 | 8 | 151 | 0 | 0 | 0 |  | 6 | 32 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 112 | 0 | 38 | 50 | 0 | 25 | 0 | 18 | 8 | 19 | 5 | 16 | 21 | 96 | 34 | 0 | 19 | 1 | 30 | 43 | 31 | 45 | 112 | 0 | 63 | 84 | 0 | 211 | 18 | 0 | 10 | 280 | 12 | 8 | 0 | 33 | 0 | 0 | 48 | 0 | 17 | 13 | 25 | 34 | 6 | 402 | 28 | 52 | 34 | 2 | 112 | 17 | 63 | 17 | 29 | 25 | 400 | 54 | 14 | 17 | 107 | 0 | 17 | 7 | 36 | 17 | 339 | 18 | 0 |  | 908 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 17 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 16 | 20 | 0 | 8 | 81 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 309 | 17 | 0 | 50 | 15 | 56 | 0 | 4 | 35 | 1132 | 163 | 0 | 17 | 0 | 42 | 75 | 50 | 0 | 0 | 19 | 0 | 0 | 41 |  | 5254 | 3731 | 8985 | 3125 | 908 | 1671 | 0 | 1372 | 1463 | 30 | 68 | 109 | 96 | 143 | 196.2955 | 83.64
16:00 | 0 | 0 | 120 | 0 | 0 | 66 | 0 | 355 | 194 |  | 0 | 0 | 153 | 49 | 51 | 15 | 0 | 0 | 0 | 50 | 50 | 32 | 0 | 0 | 0 | 0 | 17 | 35 | 0 | 16 | 22 | 26 | 33 | 16 | 8 | 0 | 30 | 0 | 0 | 0 | 8 | 152 | 0 | 0 | 0 |  | 6 | 32 | 0 | 22 | 0 | 12 | 0 | 2 | 0 | 0 | 0 | 310 | 0 | 0 | 112 | 0 | 38 | 50 | 0 | 25 | 0 | 18 | 8 | 19 | 5 | 16 | 21 | 94 | 35 | 0 | 19 | 1 | 30 | 43 | 11 | 10 | 112 | 0 | 63 | 87 | 0 | 211 | 18 | 0 | 10 | 280 | 12 | 8 | 0 | 33 | 0 | 0 | 48 | 0 | 17 | 9 | 25 | 34 | 5 | 403 | 28 | 52 | 34 | 1 | 114 | 17 | 92 | 17 | 48 | 25 | 398 | 53 | 7 | 17 | 100 | 0 | 17 | 2 | 36 | 17 | 339 | 18 | 0 |  | 906 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 179 | 16 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 26 | 20 | 0 | 8 | 81 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 258 | 17 | 0 | 50 | 15 | 62 | 0 | 3 | 35 | 1110 | 163 | 0 | 17 | 0 | 26 | 35 | 52 | 0 | 0 | 8 | 0 | 0 | 18 |  | 5244 | 3540 | 8784 | 3065 | 906 | 1569 | 0 | 1415 | 1441 | 30 | 70 | 119 | 94 | 75 | 134.5499 | 83.63
17:00 | 0 | 0 | 120 | 0 | 0 | 73 | 0 | 350 | 188 |  | 0 | 0 | 145 | 50 | 51 | 15 | 0 | 0 | 0 | 50 | 50 | 32 | 0 | 0 | 0 | 0 | 17 | 35 | 0 | 16 | 22 | 26 | 33 | 23 | 16 | 0 | 30 | 0 | 0 | 0 | 17 | 151 | 0 | 0 | 0 |  | 6 | 32 | 0 | 22 | 0 | 32 | 0 | 2 | 0 | 0 | 0 | 290 | 0 | 99 | 112 | 0 | 36 | 51 | 0 | 25 | 0 | 17 | 8 | 19 | 5 | 21 | 21 | 112 | 49 | 0 | 21 | 0 | 30 | 43 | 11 | 10 | 112 | 0 | 64 | 87 | 0 | 211 | 18 | 0 | 10 | 285 | 12 | 8 | 0 | 35 | 0 | 0 | 53 | 0 | 17 | 3 | 25 | 34 | 6 | 402 | 37 | 52 | 34 | 0 | 106 | 17 | 92 | 17 | 67 | 25 | 400 | 54 | 2 | 17 | 106 | 0 | 17 | 2 | 48 | 17 | 280 | 18 | 0 |  | 905 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 179 | 17 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 30 | 21 | 0 | 8 | 80 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 258 | 17 | 0 | 50 | 15 | 49 | 0 | 1 | 50 | 1050 | 160 | 0 | 17 | 0 | 6 | 35 | 50 | 0 | 0 | 1 | 0 | 0 | 7 |  | 5374 | 3441 | 8815 | 3107 | 905 | 1567 | 0 | 1502 | 1380 | 30 | 68 | 122 | 112 | 22 | 100.4517 | 83.63
18:00 | 0 | 0 | 120 | 0 | 0 | 75 | 0 | 345 | 183 |  | 0 | 0 | 145 | 51 | 51 | 30 | 0 | 0 | 0 | 50 | 50 | 48 | 0 | 0 | 0 | 0 | 17 | 35 | 5 | 16 | 22 | 22 | 25 | 23 | 16 | 0 | 30 | 0 | 0 | 0 | 17 | 152 | 0 | 0 | 0 |  | 6 | 32 | 32 | 22 | 0 | 33 | 0 | 7 | 0 | 0 | 0 | 285 | 0 | 98 | 8 | 0 | 36 | 51 | 0 | 25 | 0 | 19 | 8 | 19 | 5 | 18 | 21 | 122 | 48 | 0 | 21 | 0 | 30 | 43 | 11 | 10 | 112 | 0 | 65 | 87 | 0 | 218 | 18 | 0 | 10 | 280 | 12 | 8 | 0 | 105 | 0 | 0 | 52 | 0 | 17 | 0 | 25 | 34 | 6 | 402 | 47 | 52 | 52 | 0 | 268 | 17 | 92 | 17 | 116 | 25 | 400 | 54 | 0 | 17 | 107 | 0 | 17 | 0 | 72 | 17 | 280 | 0 | 0 |  | 905 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 35 | 20 | 8 | 179 | 22 | 16 | 0 | 0 | 0 | 34 | 17 | 37 | 0 | 42 | 27 | 0 | 35 | 22 | 0 | 8 | 80 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 419 | 36 | 0 | 50 | 72 | 70 | 0 | 0 | 70 | 1080 | 200 | 0 | 150 | 0 | 0 | 51 | 50 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5639 | 4184 | 9823 | 3089 | 905 | 1667 | 0 | 2214 | 1410 | 30 | 50 | 336 | 122 | 0 | 220.2564 | 83.63
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170.4914 | 0
19:00 | 0 | 0 | 200 | 0 | 0 | 75 | 0 | 339 | 183 |  | 0 | 0 | 145 | 49 | 51 | 30 | 0 | 0 | 0 | 50 | 50 | 48 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 16 | 22 | 27 | 25 | 16 | 16 | 0 | 30 | 0 | 0 | 0 | 17 | 154 | 0 | 0 | 0 |  | 6 | 32 | 83 | 22 | 0 | 33 | 0 | 11 | 0 | 0 | 0 | 285 | 0 | 98 | 8 | 0 | 38 | 52 | 0 | 25 | 0 | 20 | 8 | 19 | 5 | 22 | 21 | 112 | 50 | 0 | 22 | 0 | 30 | 43 | 4 | 0 | 112 | 0 | 65 | 84 | 0 | 218 | 18 | 0 | 10 | 270 | 6 | 8 | 0 | 147 | 0 | 0 | 49 | 0 | 17 | 0 | 25 | 34 | 5 | 402 | 47 | 52 | 88 | 0 | 263 | 17 | 92 | 17 | 118 | 25 | 400 | 54 | 0 | 17 | 107 | 0 | 17 | 0 | 72 | 17 | 300 | 0 | 0 |  | 765 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 8 | 179 | 24 | 16 | 0 | 0 | 0 | 34 | 18 | 96 | 0 | 42 | 40 | 8 | 35 | 22 | 0 | 8 | 81 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 437 | 53 | 0 | 50 | 85 | 78 | 0 | 0 | 76 | 1130 | 221 | 0 | 150 | 0 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5834 | 4350 | 10184 | 3196 | 765 | 1683 | 0 | 2411 | 1461 | 30 | 120 | 406 | 112 | 0 | 170 | 83.62
19:30 | 0 | 0 | 220 | 0 | 0 | 75 | 0 | 339 | 183 |  | 0 | 0 | 145 | 50 | 51 | 15 | 0 | 0 | 0 | 50 | 50 | 48 | 0 | 0 | 0 | 0 | 17 | 55 | 17 | 16 | 22 | 27 | 33 | 16 | 16 | 0 | 30 | 0 | 0 | 0 | 17 | 156 | 0 | 0 | 0 |  | 6 | 32 | 83 | 22 | 0 | 33 | 0 | 5 | 0 | 0 | 0 | 285 | 0 | 94 | 8 | 0 | 42 | 52 | 0 | 25 | 0 | 20 | 8 | 19 | 5 | 23 | 21 | 114 | 55 | 0 | 22 | 0 | 30 | 43 | 0 | 0 | 112 | 0 | 65 | 84 | 0 | 218 | 18 | 0 | 10 | 260 | 0 | 8 | 0 | 147 | 0 | 0 | 58 | 0 | 17 | 0 | 25 | 34 | 5 | 402 | 47 | 52 | 88 | 0 | 273 | 17 | 92 | 17 | 118 | 25 | 400 | 54 | 0 | 17 | 107 | 0 | 17 | 0 | 72 | 17 | 300 | 0 | 0 |  | 765 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 8 | 178 | 24 | 16 | 0 | 0 | 0 | 34 | 20 | 96 | 0 | 8 | 40 | 8 | 35 | 22 | 0 | 8 | 80 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 439 | 53 | 0 | 50 | 50 | 78 | 0 | 0 | 75 | 1244 | 221 | 0 | 54 | 0 | 0 | 115 | 121 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5871 | 4316 | 10187 | 3240 | 765 | 1665 | 0 | 2270 | 1574 | 30 | 121 | 408 | 114 | 0 | 150 | 0
20:00 | 0 | 0 | 220 | 0 | 0 | 76 | 0 | 339 | 180 |  | 0 | 0 | 142 | 50 | 48 | 30 | 0 | 0 | 0 | 50 | 50 | 48 | 0 | 0 | 0 | 0 | 17 | 55 | 17 | 16 | 22 | 27 | 33 | 18 | 16 | 0 | 30 | 0 | 0 | 0 | 17 | 156 | 0 | 0 | 0 |  | 6 | 32 | 83 | 22 | 0 | 33 | 0 | 11 | 0 | 0 | 0 | 285 | 0 | 95 | 8 | 0 | 41 | 51 | 0 | 29 | 0 | 0 | 8 | 19 | 5 | 24 | 15 | 112 | 78 | 0 | 22 | 0 | 30 | 43 | 0 | 0 | 112 | 0 | 64 | 84 | 0 | 218 | 18 | 0 | 10 | 270 | 0 | 8 | 0 | 147 | 0 | 0 | 53 | 0 | 17 | 0 | 25 | 34 | 6 | 402 | 47 | 52 | 88 | 0 | 278 | 17 | 92 | 17 | 116 | 25 | 400 | 55 | 0 | 17 | 107 | 0 | 17 | 0 | 72 | 17 | 300 | 0 | 0 |  | 765 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 8 | 183 | 25 | 16 | 0 | 0 | 0 | 34 | 0 | 96 | 0 | 0 | 40 | 8 | 35 | 22 | 0 | 8 | 81 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 194 | 0 | 370 | 53 | 0 | 50 | 50 | 78 | 0 | 0 | 75 | 1232 | 221 | 0 | 54 | 0 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5894 | 4232 | 10126 | 3283 | 765 | 1611 | 0 | 2274 | 1563 | 30 | 120 | 368 | 112 | 0 | 140 | 83.62
21:00 | 0 | 0 | 220 | 0 | 0 | 76 | 0 | 339 | 180 |  | 0 | 0 | 140 | 50 | 17 | 15 | 0 | 0 | 0 | 50 | 50 | 48 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 16 | 22 | 27 | 33 | 23 | 16 | 0 | 30 | 0 | 0 | 0 | 17 | 156 | 0 | 0 | 0 |  | 6 | 32 | 83 | 22 | 0 | 19 | 0 | 9 | 0 | 0 | 0 | 290 | 0 | 98 | 8 | 0 | 41 | 51 | 0 | 43 | 0 | 0 | 8 | 19 | 5 | 29 | 21 | 110 | 98 | 0 | 22 | 0 | 30 | 43 | 0 | 0 | 112 | 0 | 64 | 87 | 0 | 218 | 18 | 0 | 10 | 290 | 0 | 8 | 0 | 147 | 0 | 0 | 52 | 0 | 17 | 0 | 25 | 34 | 6 | 402 | 47 | 52 | 88 | 0 | 67 | 17 | 92 | 17 | 118 | 25 | 400 | 54 | 0 | 17 | 107 | 0 | 17 | 0 | 72 | 17 | 300 | 0 | 0 |  | 859 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 8 | 183 | 25 | 16 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 8 | 82 | 0 | 252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 208 | 0 | 435 | 56 | 0 | 50 | 50 | 78 | 0 | 0 | 75 | 1244 | 221 | 0 | 17 | 0 | 0 | 115 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5660 | 4277 | 9937 | 3341 | 859 | 1709 | 0 | 1931 | 1578 | 30 | 120 | 259 | 110 | 0 | 78 | 83.62
22:00 | 0 | 0 | 180 | 0 | 0 | 76 | 0 | 339 | 182 |  | 0 | 0 | 140 | 49 | 0 | 15 | 0 | 0 | 0 | 50 | 24 | 32 | 0 | 0 | 0 | 0 | 17 | 0 | 17 | 16 | 22 | 27 | 33 | 23 | 16 | 0 | 30 | 0 | 0 | 0 | 17 | 158 | 0 | 0 | 0 |  | 6 | 32 | 83 | 22 | 0 | 19 | 0 | 9 | 0 | 0 | 0 | 280 | 0 | 94 | 8 | 0 | 41 | 50 | 0 | 43 | 0 | 0 | 8 | 19 | 5 | 33 | 15 | 110 | 99 | 0 | 22 | 0 | 30 | 43 | 0 | 0 | 112 | 0 | 64 | 87 | 0 | 219 | 18 | 0 | 10 | 295 | 0 | 8 | 0 | 77 | 0 | 0 | 49 | 0 | 17 | 0 | 25 | 34 | 6 | 402 | 47 | 52 | 88 | 0 | 16 | 17 | 92 | 17 | 117 | 25 | 400 | 54 | 0 | 17 | 107 | 0 | 17 | 0 | 64 | 17 | 320 | 0 | 0 |  | 908 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 8 | 183 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 8 | 80 | 0 | 251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 215 | 0 | 438 | 56 | 0 | 50 | 0 | 78 | 0 | 0 | 75 | 1244 | 221 | 0 | 0 | 0 | 0 | 114 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5424 | 4169 | 9593 | 3316 | 908 | 1718 | 0 | 1653 | 1575 | 30 | 120 | 163 | 110 | 0 | 0 | 83.61
23:00 | 0 | 0 | 150 | 0 | 0 | 76 | 0 | 339 | 171 |  | 0 | 0 | 140 | 49 | 0 | 15 | 0 | 0 | 0 | 35 | 24 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 16 | 22 | 27 | 33 | 23 | 16 | 0 | 30 | 0 | 0 | 0 | 8 | 159 | 0 | 0 | 0 |  | 6 | 32 | 83 | 22 | 0 | 19 | 0 | 11 | 0 | 0 | 0 | 280 | 0 | 85 | 8 | 0 | 41 | 51 | 0 | 43 | 0 | 0 | 8 | 19 | 5 | 33 | 17 | 104 | 100 | 0 | 19 | 0 | 30 | 43 | 0 | 0 | 112 | 0 | 64 | 87 | 0 | 217 | 19 | 0 | 10 | 300 | 0 | 8 | 0 | 50 | 0 | 0 | 48 | 0 | 17 | 0 | 25 | 34 | 8 | 402 | 47 | 35 | 88 | 0 | 16 | 17 | 86 | 17 | 38 | 25 | 400 | 54 | 0 | 17 | 107 | 0 | 17 | 0 | 28 | 17 | 300 | 0 | 0 |  | 910 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 8 | 80 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 400 | 56 | 0 | 50 | 0 | 34 | 0 | 0 | 75 | 1244 | 223 | 0 | 0 | 0 | 0 | 113 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5151 | 4066 | 9217 | 3260 | 910 | 1677 | 0 | 1395 | 1574 | 30 | 120 | 147 | 104 | 0 | 0 | 83.61
24:00 | 0 | 0 | 120 | 0 | 0 | 75 | 0 | 339 | 174 |  | 0 | 0 | 143 | 25 | 0 | 15 | 0 | 0 | 0 | 25 | 24 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 16 | 22 | 27 | 33 | 23 | 8 | 0 | 30 | 0 | 0 | 0 | 8 | 160 | 0 | 0 | 0 |  | 6 | 32 | 60 | 22 | 0 | 21 | 0 | 12 | 0 | 0 | 0 | 280 | 0 | 97 | 8 | 0 | 41 | 50 | 0 | 51 | 0 | 0 | 8 | 19 | 5 | 33 | 18 | 98 | 100 | 0 | 19 | 0 | 30 | 43 | 0 | 0 | 112 | 0 | 65 | 87 | 0 | 218 | 19 | 0 | 10 | 265 | 0 | 8 | 0 | 32 | 0 | 0 | 49 | 0 | 17 | 0 | 25 | 34 | 6 | 400 | 28 | 35 | 88 | 0 | 16 | 17 | 92 | 17 | 9 | 25 | 400 | 17 | 0 | 17 | 107 | 0 | 17 | 0 | 18 | 17 | 300 | 0 | 0 |  | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 80 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 371 | 17 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 1162 | 223 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4936 | 3631 | 8567 | 3243 | 907 | 1624 | 0 | 929 | 1492 | 30 | 120 | 124 | 98 | 0 | 0 | 83.61
KWH | 0 | 0 | 2463875 | 0 | 0 | 1503363 | 0 | 8761340 | 5378000 |  | 0 | 0 | 3582982 | 936960 | 705249 | 410681 | 0 | 0 | 0 | 873600 | 865152 | 586560 | 0 | 0 | 0 | 0 | 208080 | 310995 | 332911 | 368712 | 528000 | 635940 | 768000 | 541500 | 214560 | 0 | 725760 | 0 | 0 | 0 | 213350 | 3734545 | 0 | 0 | 0 |  | 148320 | 517392 | 489758 | 427680 | 0 | 447840 | 0 | 299520 | 0 | 0 | 0 | 7680600 | 0 | 1275000 | 1288000 | 0 | 955584 | 1025760 | 0 | 834921 | 0 | 233008 | 106488 | 463932 | 116640 | 607700 | 450300 | 2344320 | 1617600 | 0 | 452304 | 9500 | 716000 | 981720 | 298800 | 614808 | 2583736 | 0 | 1505376 | 1622400 | 0 | 4350030 | 432000 | 0 | 237780 | 6962000 | 268704 | 192384 | 0 | 1156691 | 0 | 0 | 1123200 | 0 | 371952 | 135270 | 493440 | 677760 | 167272 | 8396000 | 704400 | 979848 | 1185127 | 27000 | 1987200 | 449725 | 1587417 | 330600 | 896280 | 476160 | 6989900 | 948480 | 42660 | 462240 | 2271982 | 0 | 444600 | 131780 | 885120 | 347400 | 7971800 | 125454 | 0 |  | 21210909 | 0 | 0 | 0 | 318720 | 0 | 0 | 0 | 31200 | 21248 | 53250 | 4384333 | 478283 | 156576 | 0 | 0 | 0 | 164274 | 91582 | 499744 | 0 | 368287 | 184131 | 69067 | 215104 | 474240 | 0 | 197964 | 1906909 | 0 | 6067100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4708282 | 0 | 8851236 | 522240 | 0 | 821280 | 870624 | 937142 | 0 | 28269 | 807936 | 28064000 | 4797382 | 0 | 645600 | 21420 | 436320 | 1124352 | 1535563 | 0 | 0 | 135130 | 0 | 0 | 684980 |  | 118974778 | 91884677 | 210859455 | 72516065 | 21210909 | 40833211 | 0 | 30843834 | 36038009 | 725760 | 1661017 | 3034001 | 2344320 | 1652329 | 0
Fuel Cost | 0 | 0 | 3597257.5 | 0 | 0 | 1999472.79 | 0 | 9199407 | 5808240 |  | 0 | 0 | 3977110.02 | 10475212.8 | 9344549.25 | 5441523.25 | 0 | 0 | 0 | 12772032 | 12172688.64 | 9508137.6 | 0 | 0 | 0 | 0 | 2646777.6 | 4198432.5 | 4464336.51 | 276534 | 396000 | 0 | 0 | 0 | 3649665.6 | 0 | 195955.2 | 0 | 0 | 0 | 3488272.5 | 3883926.8 | 0 | 0 | 0 |  | 1935576 | 8630098.56 | 8335681.16 | 5777956.8 | 0 | 5181508.8 | 0 | 997401.6 | 0 | 0 | 0 | 8525466 | 0 | 1479000 | 1661520 | 0 | 1079809.92 | 1528382.4 | 0 | 1394318.07 | 0 | 4024048.16 | 1432263.6 | 635586.84 | 87480 | 1063475 | 337725 | 16832217.6 | 1763184 | 0 | 615133.44 | 151430 | 980920 | 1295870.4 | 519912 | 1063617.84 | 2971296.4 | 0 | 2920429.44 | 3699072 | 0 | 4393530.3 | 928800 | 0 | 470804.4 | 6962000 | 201528 | 146211.84 | 0 | 15788832.15 | 0 | 0 | 15140736 | 0 | 5151535.2 | 1581306.3 | 5092300.8 | 9258201.6 | 2219699.44 | 7724320 | 8565504 | 14168602.08 | 14991856.55 | 0 | 23329728 | 4897505.25 | 16874242.71 | 4486242 | 11553049.2 | 5609164.8 | 6430708 | 12282816 | 616437 | 5865825.6 | 25855155.16 | 0 | 5806476 | 1574771 | 13250246.4 | 4575258 | 0 | 0 | 0 |  | 63632727 | 0 | 0 | 0 | 3317875.2 | 0 | 0 | 0 | 561912 | 382464 | 765202.5 | 4910452.96 | 927869.02 | 1706678.4 | 0 | 0 | 0 | 2754874.98 | 1601769.18 | 7815996.16 | 0 | 6098832.72 | 3113655.21 | 941383.21 | 3628804.48 | 981676.8 | 0 | 149858.748 | 11079141.29 | 0 | 32094959 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5461607.12 | 0 | 8762723.64 | 7018905.6 | 0 | 9715742.4 | 12580516.8 | 11901703.4 | 0 | 312372.45 | 9808343.04 | 252856640 | 4893329.64 | 0 | 4777440 | 242260.2 | 5118033.6 | 17236316.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 450209306.37 | 497152066.908 | 947361373.278 | 68484222.308 | 63632727 | 48618746.62 | 0 | 393612712.22 | 296030740.29 | 195955.2 | 0 | 50357441.49 | 16832217.6 | 9596610.55 | 0
Yesterday Day Peak | 0 | 0 | 160 | 0 | 0 | 68 | 0 | 388 | 227 |  | 0 | 0 | 152 | 50 | 51 | 15 | 0 | 0 | 0 | 42 | 50 | 32 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 16 | 22 | 26 | 33 | 25 | 8 | 0 | 30 | 0 | 0 | 0 | 8 | 152 | 0 | 0 | 0 |  | 6 | 32 | 0 | 22 | 0 | 26 | 0 | 2 | 0 | 0 | 0 | 345 | 0 | 0 | 112 | 0 | 42 | 51 | 0 | 25 | 0 | 21 | 0 | 19 | 5 | 14 | 21 | 110 | 44 | 0 | 19 | 2 | 30 | 43 | 22 | 46 | 112 | 0 | 61 | 84 | 0 | 218 | 18 | 0 | 10 | 310 | 8 | 8 | 0 | 48 | 0 | 0 | 57 | 0 | 17 | 20 | 25 | 34 | 11 | 238 | 28 | 52 | 34 | 4 | 105 | 17 | 54 | 17 | 9 | 25 | 220 | 55 | 0 | 35 | 92 | 0 | 17 | 27 | 36 | 17 | 382 | 18 | 0 |  | 908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 19 | 16 | 0 | 0 | 0 | 0 | 5 | 42 | 0 | 42 | 16 | 0 | 6 | 18 | 0 | 8 | 80 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 424 | 17 | 0 | 50 | 85 | 56 | 0 | 5 | 35 | 1122 | 200 | 0 | 17 | 5 | 64 | 35 | 50 | 0 | 0 | 24 | 0 | 0 | 136 |  | 9296 | DayPeak
Yesterday Evening Peak | 0 | 0 | 220 | 0 | 0 | 75 | 0 | 339 | 183 | 0 | 0 | 0 | 145 | 50 | 51 | 15 | 0 | 0 | 0 | 50 | 50 | 48 | 0 | 0 | 0 | 0 | 17 | 55 | 17 | 16 | 22 | 27 | 33 | 16 | 16 | 0 | 30 | 0 | 0 | 0 | 17 | 156 | 0 | 0 | 0 | 0 | 6 | 32 | 83 | 22 | 0 | 33 | 0 | 5 | 0 | 0 | 0 | 285 | 0 | 94 | 8 | 0 | 42 | 52 | 0 | 25 | 0 | 20 | 8 | 19 | 5 | 23 | 21 | 114 | 55 | 0 | 22 | 0 | 30 | 43 | 0 | 0 | 112 | 0 | 65 | 84 | 0 | 218 | 18 | 0 | 10 | 260 | 0 | 8 | 0 | 147 | 0 | 0 | 58 | 0 | 17 | 0 | 25 | 34 | 5 | 402 | 47 | 52 | 88 | 0 | 273 | 17 | 92 | 17 | 118 | 25 | 400 | 54 | 0 | 17 | 107 | 0 | 17 | 0 | 72 | 17 | 300 | 0 | 0 |  | 765 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 8 | 178 | 24 | 16 | 0 | 0 | 0 | 34 | 20 | 96 | 0 | 8 | 40 | 8 | 35 | 22 | 0 | 8 | 80 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 439 | 53 | 0 | 50 | 50 | 78 | 0 | 0 | 75 | 1244 | 221 | 0 | 54 | 0 | 0 | 115 | 121 | 0 | 0 | 0 | 0 | 0 | 0 |  | 10187 | EvPeak
Forecast for Evening | 0 | 0 | 220 | 0 | 0 | 71 | 0 | 350 | 180 | 0 | 0 | 0 | 150 | 50 | 17 | 15 | 0 | 0 |  | 50 | 48 | 48 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 22 | 29 | 33 | 25 | 16 | 0 | 30 | 0 | 0 | 0 | 17 | 160 | 0 | 0 | 0 | 0 | 6 | 32 | 83 | 22 | 0 | 33 | 0 | 5 | 0 | 0 | 0 | 300 | 0 | 100 | 8 | 0 | 42 | 51 | 0 | 25 | 0 | 25 | 8 | 19 | 5 | 23 | 20 | 152 | 100 | 0 | 22 | 0 | 30 | 43 | 0 | 0 | 110 | 0 | 65 | 81 | 0 | 220 | 19 | 0 | 10 | 320 | 0 | 8 |  | 145 | 0 | 0 | 55 | 0 | 17 | 0 | 25 | 34 | 6 | 400 | 47 | 52 | 85 | 0 | 300 | 17 | 92 | 17 | 113 | 25 | 400 | 55 | 0 | 17 | 107 | 0 | 17 |  | 94 | 17 | 320 |  |  |  | 920 | 0 | 0 |  | 49 | 0 | 0 | 0 | 45 | 80 | 8 | 180 | 25 | 16 | 0 | 0 | 0 | 34 | 20 | 95 | 0 | 42 | 40 | 8 | 35 | 22 | 0 | 8 | 80 | 0 | 250 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 180 | 0 | 400 | 54 | 0 | 50 | 85 | 84 | 0 | 0 | 75 | 1244 | 220 |  | 150 |  |  | 115 | 120 |  | 0 |  | 0 | 0
Forecast for Day | 0 | 0 | 220 | 0 | 0 | 71 | 0 | 350 | 180 | 0 | 0 | 0 | 150 | 25 | 17 | 15 | 0 | 0 | 0 | 50 | 48 | 32 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 19 | 22 | 29 | 33 | 25 | 8 | 0 | 30 | 0 | 0 | 0 | 8 | 160 | 0 | 0 | 0 | 0 | 6 | 24 | 51 | 22 | 0 | 25 | 0 | 5 | 0 | 0 | 0 | 300 | 0 | 100 | 8 | 0 | 42 | 51 | 0 | 25 | 0 | 25 | 8 | 19 | 5 | 23 | 20 | 135 | 45 | 0 | 22 | 1.6 | 30 | 43 | 0 | 0 | 110 | 0 | 65 | 60 | 0 | 220 | 19 | 0 | 10 | 320 | 0 | 8 | 0 | 32 | 0 | 0 | 48 | 0 | 17 | 20 | 25 | 34 | 6 | 400 | 47 | 35 | 34 | 5 | 100 | 17 | 54 | 17 | 9 | 25 | 400 | 17 | 50 | 17 | 107 | 0 | 17 | 30 | 17 | 17 | 320 |  |  |  | 920 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 19 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 8 | 0 | 22 | 0 | 8 | 80 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 400 | 17 | 0 | 50 | 85 | 49 | 0 | 8 | 35 | 1200 | 220 |  | 17 | 6 | 100 | 115 | 120 |  | 0 | 30 | 0 |  | 130 |  |  |  |  | g | h | o | c | h | t | s
Generation at 08:00(Today) | 0 | 0 | 220 | 0 | 0 | 71 | 0 | 359 | 178 | 0 | 0 | 0 | 144 | 25 | 8 | 15 | 0 | 0 | 0 | 25 | 24 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 16 | 22 | 25 | 33 | 25 | 8 | 0 | 30 | 0 | 0 | 0 | 8 | 160 | 0 | 0 | 0 | 0 | 6 | 24 | 0 | 22 | 0 | 25 | 0 | 21 | 0 | 0 | 0 | 315 | 0 | 99 | 8 | 0 | 41 | 49 | 0 | 0 | 0 | 0 | 0 | 19 | 2 | 15 | 18 | 100 | 45 | 0 | 19 | 0 | 30 | 43 | 0 | 0 | 112 | 0 | 64 | 10 | 0 | 217 | 19 | 0 | 10 | 325 | 0 | 8 | 0 | 32 | 0 | 0 | 28 | 0 | 17 | 2 | 25 | 34 | 5 | 383 | 47 | 35 | 34 | 1 | 16 | 17 | 54 | 17 | 9 | 25 | 400 | 17 | 2 | 17 | 107 | 0 | 12 | 4 | 17 | 17 | 320 | 0 | 0 | 0 | 901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 8 | 0 | 22 | 0 | 8 | 80 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 440 | 17 | 0 | 0 | 54 | 36 | 0 | 0 | 0 | 1200 | 220 | 0 | 40 | 0 | 10 | 114 | 120 | 0 | 0 | 5 | 0 | 0 | 20 | 0 |  |  |  | 113.3493 | 21.2109 | 35.5389 | 36.038 | 0.72576 | 2.3443 | 1.6523
210.8595
| Minimum Generation |  | 6945 | 5:00
| Highest Generation |  | 10187 | 19:30
| Day Peak Generation |  | 9296 | 12:00
| Evening Peak Generation |  | 10187 | 19:30
| HVDC Max Flow |  | 910 | 23:00
| HVDC EvPeak Flow |  | 765 | 19:30
| Load factor L.F |  | 86.25% | [161 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2023-02-01
Till now the maximum generation is : - |  |  |  | 14782 | 21:00 | Hrs on | 2022-04-16
The Summary of Yesterday's |  |  | 2023-01-31 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 9296 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 7246
Evening Peak Generation : |  |  | 10187 | MW Hour : | 19:30 | Available Max Generation : |  | 10873
E.P. Demand (at gen end) : |  |  | 10350 | MW Hour : | 19:30 | Max Demand (Evening) : |  | 10500
Maximum Generation : |  |  | 10187 | MW Hour : | 19:30 | Reserve(Generation end) |  | 373
Total Gen. (MKWH) : |  |  | 210.8595 | System Load Factor : | 86.25% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 670 | MW at | 7:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2023-02-01
Actual : |  | 86.59 | Ft.(MSL) , | Rule curve : | 97 | Ft.( MSL )
Gas Consumed : |  | Total = | 884.35 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 117102968.928
: |  |  | Coal : | 296030740.29 | Oil : | 443970153.71 | Total : | 857103862.928
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 30 | 720:00 | 3265.9867 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 925.1972 |  |  | 0 | 0%
Khulna Area |  | 0 | 0:00 | 1221.1835 |  |  | 0 | 0%
Rajshahi Area |  | 0 | 0:00 | 1083.4939 |  |  | 0 | 0%
Cumilla Area |  | 0 | 0:00 | 922.348 |  |  | 0 | 0%
Mymensingh Area |  | 120 | 2880:00 | 761.9973 |  |  | 0 | 0%
Sylhet Area |  | 0 | 0:00 | 340.5797 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 277.6321 |  |  | 0 | 0%
Rangpur Area |  | 0 | 0:00 | 601.6466 |  |  | 0 | 0%
Total |  | 150 |  | 9400.065 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 2
2) Ghorasal-3
3) Ashuganj-5
4) Baghabari-70,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
7) Shajibazar 330 MW
8) Sirajganj-1,2
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
08:14 | 17:03 | Goalpara- Khulna (C) 132kV Ckt-2 Scheduled S/D from Goalpara 132/33kV end Due to Gantry painting work and from
Khulna (C) end Due to Due to annual maintenance
08:23 |  | Brahmongaon(Aggreko)-Hasnabad 132 kV Ckt-2 Forced S/D from Hasnabad 132/33kV end Due to NLDC instruction
08:25 | 16:47 | Aminbazar-Kaliakoir 230kV Ckt-1 Scheduled S/D from Kaliakoir 400/230/132kV end Due to Annual Maintenace
08:32 | 16:14 | Bibiyana-Fenchuganj 230 kV Ckt-2 Scheduled S/D from Fenchuganj 230/132/33kV end Due to Deadline Checking.
08:35 | 17:13 | Anowara-Sikalbaha 230 kV Ckt-2 Scheduled S/D from Shikalbaha 230/132kV end Due to For Deadline checking
08:37 | 16:30 | Kaliakoir-Tongi 230kV Ckt-2 Scheduled S/D from Kaliakoir 400/230/132kV end Due to Annual Maintenance and from Tongi
230/132/33kV end Due to Annual maintenance.
08:47 | 17:05 | Hathazari 230/132/33kV S/S Raojan-02 Scheduled S/D Due to Annual maintenance
09:05 | 14:50 | Sreemongol 132/33kV S/S 132/33kv T-2 LT Scheduled S/D Due to for relay testing.
09:06 | 14:48 | Sreemongol 132/33kV S/S 132/33kv T-2 HT Scheduled S/D Due to for relay testing.
09:06 | 14:48 | Sreemongol 132/33kV S/S 132/33kv T-3 HT Scheduled S/D Due to for relay testing.
09:06 | 14:50 | Sreemongol 132/33kV S/S 132/33kv T-3 LT Scheduled S/D Due to for relay testing.
09:07 | 17:17 | Aminbazar-Mirpur 132kV Ckt-2 Scheduled S/D from Mirpur 132/33kV end Due to Dead line checking(A/M)
09:21 | 14:12 | Shariatpur 132/33kV S/S T2-416T LT Scheduled S/D Due to Annual Maintenance by PBS.
09:22 | 14:11 | Shariatpur 132/33kV S/S T2-416T HT Scheduled S/D Due to Annual Maintenance by PBS.
09:26 | 12:01 | Shariatpur 132/33kV S/S Auxiliary-02 (PGCB) LT Scheduled S/D Due to Annual Maintenance by PBS.
09:26 | 12:02 | Shariatpur 132/33kV S/S Auxiliary-02 (PGCB) HT Scheduled S/D Due to Annual Maintenance by PBS.
09:30 | 14:06 | Shariatpur 132/33kV S/S 33 KV BUS Scheduled S/D Due to Annual Maintenance by PBS. 2 No Bus.
| 09:38 | Meghnaghat-Shyampur 230kV Ckt-2 is restored.
09:41 | 14:42 | Savar 132/33kV S/S T-3 LT Scheduled S/D Due to Annual maintenance.
09:42 | 14:42 | Savar 132/33kV S/S T-3 HT Scheduled S/D Due to Annual maintenance.
09:45 | 16:50 | Faridpur 132/33kV S/S Transformer-3 LT Scheduled S/D
09:45 | 16:50 | Faridpur 132/33kV S/S Transformer-3 LT Scheduled S/D
09:48 | 13:30 | Jamalpur United(20MW)-Sherpur 132kV Ckt-1 Scheduled S/D from Sherpur 132/33kV end Due to 132 KV UMPL-Sher
Ckt-01 CT Tendelta test.
09:53 |  | Saidpur 132/33kV S/S TR-4 (414T) LT Scheduled S/D Due to For oil centrifuging
09:53 |  | Aftabnagar 132/33kV GT-2 was S/D for A/M.
09:54 |  | Saidpur 132/33kV S/S TR-4 (414T) HT Scheduled S/D Due to For oil centrifuging
10:05 | 15:37 | Faridpur-Gopalganj(N) 132 kV Ckt-2 Scheduled S/D from Faridpur 132/33kV end Due to Annual maintenance. and from
Gopalganj 400/132kV end Due to Maintenance work Faridpur ss
10:11 |  | Aminbazar 400/230/132kV S/S 230/132kv Tr-02 LT Scheduled S/D Due to Jack Bus change
10:12 | 13:33 | Faridpur 132/33kV S/S Transformer-3 HT Scheduled S/D
10:12 |  | Aminbazar 400/230/132kV S/S 230/132kv Tr-02 HT Scheduled S/D Due to Jack Bus Change
10:20 | 10:51 | Ishurdi 230/132kV S/S 230/132 kV T-01 HT Forced S/D Due to 33 Kv incommer breaker Change
10:20 | 13:19 | Ishurdi 132/33kV S/S 132/33 kV T-1 HT Forced S/D Due to 33 Kv incommer breaker Change
10:20 | 13:25 | Ishurdi 132/33kV S/S 132/33 kV T-1 LT Forced S/D Due to 33 Kv incommer breaker Change
10:33 | 15:35 | Nawabganj 132/33kV S/S 132kV Main Bus-1 Scheduled S/D Due to For annual maintenance work
11:26 | 13:30 | Rangpur 132/33kV S/S T-1(414T) LT Scheduled S/D Due to Energy meter replacement
11:26 | 13:30 | Rangpur 132/33kV S/S T-1(414T) HT Scheduled S/D Due to Metre replacement
11:26 | 13:30 | Rangpur 132/33kV S/S T-1(414T) LT Scheduled S/D Due to Energy meter replacement
12:00 |  | Day peak generation: 9297 MW, load shed about 234 MW
12:14 | 13:37 | Cumilla(S) 132/33kV S/S TR-4 LT Forced S/D Due to Works by BPDB on 33KV T04 Bus
12:14 | 13:37 | Cumilla(S) 132/33kV S/S TR-4 HT Forced S/D Due to Works by BPDB on 33KV T04 Bus
| 12:16 | Gopalganj (O) - Gopalgan (N) Ckt-1 is restored.
| 12:17 | Gopalganj- Gopalganj(N) 132kV Ckt-2 is restored.
12:34 | 17:38 | Barishal 230/132kV S/S T-4 LT Project Work S/D Due to SAS integration
12:35 | 17:37 | Barishal 230/132kV S/S T-4 HT Project Work S/D Due to SAS integration
| 13:04 | Chauddagram-Cumilla(S) 132 kV Ckt-1 is restored.
| 13:11 | Barapukuria 230/132/33kV S/S 132/33 KV T-5, 424T HT is restored.
13:18 | 14:27 | Cumilla(S)-Kachua 132 kV Ckt-1 Project Work S/D from Cumilla(S) 132/33kV end.
13:31 | 14:35 | Jamalpur United (20MW)- Sherpur 132kV Ckt-2 Scheduled S/D from Sherpur 132/33kV end Due to Tandelta Test
| 13:57 | Mymensingh 132/33kV S/S 50 MW Solar Plant is restored.
| 13:57 | Mymensingh 132/33kV S/S 50 MW Solar Plant is restored.
14:00 |  | Condition : L/S free, Previous shift s/d continue.
| 14:13 | Barapukuria 230/132/33kV S/S 132/33 KV T-5, 424T LT is restored.
14:50 |  | Kamrangirchar gt1 was switched on
15:12 | 15:54 | Naogaon 132/33kV S/S T-2 LT Scheduled S/D Due to Red hot maintenance. | [5 empty] | 15.0MW load interrup.
15:13 | 15:53 | Naogaon 132/33kV S/S T-2 HT Scheduled S/D Due to Red hot maintenance. | [5 empty] | 15.0MW load interrup.
| 15:14 | Ashuganj-Cumilla(N) 230 kV Ckt-2 is restored.
15:43 |  | Mogbazar GT2 was switched on
16:19 |  | Ashuganj CCPP 225MW GT was sync.
17:53 |  | Meghnaghat-Shyampur 230kV Ckt-1 was switched on
19:30 |  | Evening Peak Generation: 10188 MW, load shed about 150 MW.
| 22:53 | Payra 400/132/33kV S/S 400/132/33 kV Auto Transformer-01 HT is restored.
| 22:53 | Payra 400/132/33kV S/S 400/132/33 kV Auto Transformer-01 LT is restored.
| 01:03 | Madanganj 132/33kV S/S Madanganj -Shitalakhya 132 kv Ckt is restored.
01:13 |  | Meghnaghat-Shyampur 230kV Ckt-2 Forced S/D from Shyampur 230/132kV end Due to Corossion Maintenance &
repair work in insulator disc at tower 22 and from Meghnaghat 230/132kV end Due to As per request of NLDC.
05:00 |  | Min. Gen. 7247 MW
06:21 |  | Ashuganj (S) 230 kv bus-coupler was closed.
07:38 |  | Ashuganj-Bhulta 400 kV Ckt-2 Scheduled S/D from Bhulta 400/230kV end Due to Due to Deadline checking works.
07:46 |  | Kabirpur -Tongi 132kV Ckt-1 Scheduled S/D from Tongi 230/132/33kV end.
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2023-01-31 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 220 | 2463875
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Machine problem
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 75 | 1503363 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 339 | 8761340 | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 183 | 5378000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Under maint.
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 50 | 936960 | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 145 | 3582982 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 51 | 705249 | Fuel shortage
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 15 | 410681 | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 16 | 368712 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 50 | 873600 | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 50 | 865152 | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 17 | 208080 | Fuel shortage
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 48 | 586560 | Fuel shortage
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 310995
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 17 | 332911 | Fuel shortage
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 49 | 1163940 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 768000
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 16 | 541500 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 16 | 214560 | Fuel shortage
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 147 | 1156691 | Fuel shortage
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Fuel shortage
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 0 | 0 | Fuel shortage
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Fuel shortage
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 17 | 371952 | Fuel shortage
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 52 | 979848 | Fuel shortage
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 54 | 948480 | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 17 | 462240 | Fuel shortage
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 131780
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 347400 | Fuel shortage
| Dhaka area Total |  |  |  | 5847 | 1749 | 34374851
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Machine problem
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 17 | 213350 | Fuel shortage
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 135270
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 33 | 447840 | Fuel shortage
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 30 | 725760 | Low water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 156 | 3734545 | ST under S/D
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 88 | 1185127 | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 32 | 517392 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 83 | 489758 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 22 | 427680 | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 25 | 493440 | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 0 | Gas shortage
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 5 | 299520
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 27000
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 273 | 1987200 | Engine problem
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 17 | 449725 | Fuel shortage
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 92 | 1587417 | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 25 | 476160 | Fuel shortage
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 107 | 2271982 | Engine problem
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 125454 | On test.
| Chattogram area Total |  |  |  | 2382 | 1005 | 15594620
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 94 | 1275000 | ST under S/D
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 285 | 7680600 | ST under S/D
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint.
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 300 | 7971800 | Gas shortage
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 42 | 955584
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 52 | 1025760 | Gas shortage
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 1288000 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 25 | 834921
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 5 | 167272 | Fuel shortage
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 20 | 233008 | Machine problem
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 34 | 677760 | Fuel shortage
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 463932
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 5 | 116640 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 114 | 2344320
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 23 | 607700 | Engine problem
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 8 | 106488 | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 21 | 450300 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Fuel shortage
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 17 | 330600
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 118 | 896280
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 444600 | Engine problem
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 72 | 885120 | Fuel shortage
| Cumilla Area Total |  |  |  | 3285 | 1279 | 28755685
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 55 | 1617600 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 452304
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 9500
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 58 | 1123200 | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 47 | 704400 | Fuel shortage
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 42660
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 148320 | Engine problem
| Mymensingh Area Total |  |  |  | 614 | 188 | 4097984
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 30 | 716000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 43 | 981720 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 112 | 2583736 | Gas shortage
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 0 | 298800 | Gas shortage
| Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 0 | 614808 | Gas shortage
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 8 | 192384
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 65 | 1505376
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 84 | 1622400
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 218 | 4350030
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 432000
| Sylhet 50MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Gas shortage
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 0 | 268704 | Gas shortage
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 260 | 6962000 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 402 | 8396000 | FGMO
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 237780
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 400 | 6989900
| Sylhet Area Total |  |  |  | 2427 | 1650 | 36151638
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Fuel shortage
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 765 | 21210909
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 49 | 318720 | Fuel shortage
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 31200 | Engine problem
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel conservation
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 21248 | Engine problem
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 8 | 53250 | Fuel shortage
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Fuel shortage
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 53 | 522240 | Fuel shortage
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 50 | 870624 | Engine problem
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 436320
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 0 | 121 | 1535563 | On test.
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 660*2 | 617 | 0 | 0 | Coal shortage
| Khulna Area Total |  |  |  | 3001 | 1046 | 25000074
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 16 | 156576 | Fuel shortage
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 24 | 478283 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 178 | 4384333
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1244 | 28064000
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 221 | 4797382
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 54 | 645600 | line O/L.
| Barisal 307 MW |  | BCPCL | 307*1 | 307 | 0 | 0 | Coal shortage
| Barisal Area Total |  |  |  | 2265 | 1737 | 38526174
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 34 | 164274 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 20 | 91582 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contract Expired
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 8 | 368287
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 40 | 184131 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 175 | 4708282
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 439 | 8851236 | Gas shortage
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 35 | 215104 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 474240 | Engine problem
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 197964 | Engine problem
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 8 | 69067 | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 96 | 499744
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Fuel shortage
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 50 | 821280 | Fuel shortage
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 75 | 807936 | Fuel shortage
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 21420
| Adani Power Jharkhanda Ltd |  | Import | 0 | 0 | 0 | 0 | On test.
| Rajshahi Area Total |  |  |  | 2129 | 1010 | 17474547
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 80 | 1906909
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 250 | 6067100 | Machine problem
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 78 | 937142 | Fuel shortage
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 28269
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 115 | 1124352
| Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 135130
| Teesta Solar Limited |  | BPCL | 16*12.5 | 0 | 0 | 684980
| Rangpur Area Total |  |  |  | 750 | 523 | 10883882
| Total |  |  |  | 22700 | 10187 | 210859455
| Eastern Grid Total |  |  |  | 14555 | 5871 | 118974778
| Western Grid Total |  |  |  | 8145 | 4316 | 91884677
| National Grid Total |  |  |  | 22700 | 10187 | 210859455
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2023-01-31
| (a) ENTIRE EASTERN GRID : |  | 6490.63 | MW | (b) ENTIRE WESTERN GRID : |  | 3179.5 | MW
| i) Dhaka area |  | 3618.13 | MW | i) Khulna area |  | 1140 | MW
| ii) Chittagong area |  | 851.5 | MW | ii) Rajshahi area |  | 1042.9 | MW
| iii) Comilla area |  | 855 | MW | iii) Barisal area |  | 269.6 | MW
| iv) Mymensingh area |  | 799 | MW | iv) Rangpur area |  | 727 | MW
| v) Sylhet area |  | 367 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 9670.13 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 7 | 00:00 | Chhatak | 21 | 18:30 | Kamrangirchar | 44 | 13:00 | Natore | 97 | 19:00 | Shitalakhya | 111 | 12:00
2 | AKSML | 93 | 23:00 | Chowmuhani | 132 | 19:00 | Kaptai | 4 | 18:00 | Nawabganj | 27.7 | 21:00 | Sholosohor | 22 | 09:00
3 | Aftabnagar | 24 | 18:00 | Chuadanga | 71 | 18:30 | Kazla | 80 | 19:00 | Netrakona | 120 | 07:00 | Shyampur | 146 | 01:00
4 | Agargaon | 57 | 13:00 | Coxsbazar | 94 | 18:30 | Keranigonj | 50 | 13:00 | New | 62 | 12:00 | Siddhirganj | 94 | 13:00
5 | Agrabad | 48 | 18:00 | Cumilla(N) | 95 | 19:30 | Khagrachori | 22 | 18:00 | Niamatpur | 89 | 13:00 | Sirajganj | 88 | 19:30
6 | Amnura | 47 | 13:00 | Cumilla(S) | 121 | 18:00 | Khulna | 77 | 13:00 | Noapara | 34 | 18:30 | Sonargaon | 96 | 00:00
7 | Ashuganj | 46 | 13:00 | Daudkandi | 99 | 19:30 | Khulshi | 153 | 15:00 | PHP | 9 | 00:00 | Sreemongol | 39 | 19:00
8 | BIPTC | N/A | N/A | Dhaka | 24 | 13:00 | Kishoreganj | 108 | 19:00 | Pabna | 76 | 18:00 | Srinagar | 29.39 | 20:00
9 | BSRM | 104 | 01:00 | Dhamrai | 82 | 16:00 | Kodda | 217 | 21:00 | Palashbari | 106 | 09:00 | Sunamganj | 34 | 19:30
10 | Bagerhat | 69 | 18:30 | Dhanmondi | 86 | 13:00 | Kulaura | 26 | 18:00 | Panchagarh | 51 | 18:30 | Sylhet | 95 | 18:00
11 | Bakulia | 62 | 18:30 | Dohazari | 66 | 18:30 | Kurigram | 64 | 18:00 | Patuakhali | 68.4 | 20:00 | TK | 19 | 18:30
12 | Banani | 28 | 13:00 | Faridpur | 96 | 19:00 | Kushtia | 94 | 18:00 | Payra | 10.8 | 18:30 | Tangail | 156 | 20:00
13 | Bangabhaban | 12 | 12:00 | Fatullah | 55 | 10:00 | Lalbag | 68 | 13:00 | Postogola | 32 | 13:00 | Thakurgaon | 70 | 18:30
14 | Barapukuria | 55 | 12:00 | Fenchuganj | 28 | 18:00 | Lalmonirhat | 38 | 07:00 | Purbachal | 13 | 12:00 | Tongi | 95 | 11:00
15 | Barguna | 12 | 18:30 | Feni | 86 | 18:00 | Madanganj | 25 | 18:00 | Purbasadipur | 106 | 18:00 | Ullon | 37 | 14:00
16 | Barishal | 82 | 12:00 | GPH | 84 | 14:00 | Madaripur | 65 | 18:30 | Rahanpur_I | 4.4 | 00:00 | Uttara | 61 | 13:00
17 | Barishal-230 | 48 | 20:00 | Ghorashal | 56 | 19:30 | Madartek | 49 | 13:00 | Rahim | 31 | 00:00 | UttaraNew | 14 | 14:00
18 | Baroaulia | 60 | 09:00 | Goalpara | 18 | 12:00 | Madunaghat | 38 | 18:00 | Rajbari | 48 | 18:30 | Zigatola | 60 | 13:00
19 | Baroirhat | 32 | 18:00 | Gollamari | 30 | 13:00 | Magura | 46 | 18:30 | Rajendrapur | 82 | 08:00
20 | Bashundhara | 119 | 13:00 | Gopalganj | 77 | 18:30 | Mahasthangarh | 44 | 08:00 | Rajshahi | 97 | 18:30
21 | BashundharaCement | 1 | 00:00 | Gulshan | 76 | 13:00 | Manikganj | 73 | 21:00 | Rajshahi-230 | 24 | 13:00
22 | Beanibazar | 41 | 18:00 | Halishahar | 82.5 | 11:00 | Maniknagar | 42 | 13:00 | Ramganj | 60 | 18:30
23 | Benapole | 46 | 08:00 | HaripurSBU | 148 | 19:30 | Matarbari | 38 | 18:30 | Rampur | 19 | 18:00
24 | Bhaluka | 104 | 00:00 | Hasnabad | 75 | 14:00 | Matuail | 58 | 15:00 | Rangamati | 10 | 18:00
25 | Bhandaria | 32 | 18:30 | Hathazari | 43 | 13:00 | Millgate | 54 | 09:00 | Rangpur | 122 | 18:30
26 | Bhangura | 22 | 18:30 | Ishurdi | 44 | 18:30 | Mirpur | 91 | 14:00 | Ruppur | 4 | 15:00
27 | Bheramara(GK) | 38 | 18:30 | Jaldhaka | 61 | 18:30 | Mirsorai | 2 | 09:00 | SSM | 1 | 00:00
28 | Bhulta | 199 | 00:00 | Jamalpur | 115 | 21:00 | Mithapukur | 42 | 13:00 | Saidpur | 99 | 09:00
29 | Bog-Sherpur | 48 | 08:00 | Jashore | 105 | 12:00 | Modern | 0 | 00:00 | Satkhira | 90 | 19:00
30 | Bogura | 114 | 19:00 | Jhenaidah | 86 | 18:00 | Mogbazar | 84 | 13:00 | Satmasjid | 63 | 13:00
31 | Borhanuddin | 29 | 21:00 | Joydebpur | 121 | 17:00 | Mongla | 24 | 15:00 | Savar | 134 | 15:00
32 | Brahmanbaria | 104 | 18:30 | Joypurhat | 44 | 19:30 | Motijheel | 24 | 13:00 | Shahjadpur | 78 | 18:30
33 | Cantonment | 99 | 13:00 | Juldah | 20 | 12:00 | Munshiganj | 59 | 19:30 | Shahjibazar | 87 | 19:30
34 | Chandpur | 45 | 20:00 | KSRM | 50 | 08:00 | Mymensingh | 176 | 19:30 | Shahmirpur | 30 | 14:00
35 | Chandraghona | 24 | 18:00 | Kabirpur | 224 | 15:00 | Naogaon | 104 | 13:00 | Shariatpur | 46 | 19:30
36 | Chapai | 54 | 09:00 | Kachua | 50 | 18:00 | Narail | 38 | 19:00 | Sherpur | 116 | 23:00
37 | Charsaidpur | 49 | 13:00 | Kallyanpur | 60 | 13:00 | Narinda | 48 | 13:00 | Shikalbaha | 20 | 11:00
38 | Chauddagram | 31 | 18:00 | Kalurghat | 27 | 15:00 | Narshingdi | 141 | 19:30 | Shikalbaha-230 | N/A | N/A
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2023-01-31 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 413 | 06:00 | 393 | 13:00 | Gopalganj | 420 | 04:00 | 394 | 13:00
| Bhulta | 395 | 06:00 | 382 | 12:00 | Kaliakoir | 395 | 03:00 | 382 | 14:00
| Bibiana | 407 | 06:00 | 396 | 13:00 | Payra | 420 | 00:00 | 409 | 12:00
| BIPTC | 403 | 04:00 | 391 | 10:00 | Rahanpur_I | 415 | 19:30 | 383 | 07:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 239 | 06:00 | 227 | 12:00 | Hasnabad | 233 | 00:00 | 226 | 13:00
| AKSML | 240 | 19:00 | 217 | 03:00 | Hathazari | 244 | 06:00 | 235 | 15:00
| Aminbazar | 237 | 01:00 | 229 | 15:00 | Ishurdi | 241 | 06:00 | 225 | 08:00
| Ashuganj | 242 | 06:00 | 232 | 12:00 | Jhenaidah | 242 | 04:00 | 224 | 08:00
| Baghabari | 233 | 17:00 | 227 | 06:00 | Kaliakoir | 236 | 04:00 | 226 | 12:00
| Barapukuria | 227 | 14:00 | 212 | 08:00 | Keranigonj | 238 | 06:00 | 227 | 11:00
| Barishal | 246 | 06:00 | 240 | 13:00 | Khulna(S) | 245 | 06:00 | 228 | 08:00
| Bheramara | 239 | 05:00 | 222 | 08:00 | Maniknagar | 237 | 06:00 | 227 | 12:00
| Bhulta | 241 | 06:00 | 229 | 12:00 | Meghnaghat | 241 | 02:00 | 236 | 21:00
| Bibiana | 241 | 18:00 | 234 | 13:00 | Mirsorai | 240 | 06:00 | 228 | 03:00
| BIPTC | 242 | 06:00 | 224 | 08:00 | Rajshahi | 242 | 06:00 | 223 | 07:00
| Bogura | 231 | 04:00 | 216 | 08:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 249 | 04:00 | 245 | 13:00 | Rampura | 237 | 04:00 | 227 | 12:00
| BSRM | 242 | 06:00 | 228 | 11:00 | Shikalbaha | 241 | 18:00 | 230 | 04:00
| Cumilla(N) | 239 | 14:00 | 228 | 13:00 | Shyampur | 237 | 06:00 | 227 | 11:00
| Fenchuganj | 245 | 06:00 | 237 | 01:00 | Siddhirganj | 237 | 05:00 | 230 | 12:00
| Ghorashal | N/A | N/A | N/A | N/A | Sirajgonj | 232 | 03:00 | 224 | 08:00
| GPH | 240 | 06:00 | 226 | 03:00 | Tongi | 228 | 18:00 | 218 | 15:00
| Haripur | 234 | 05:00 | 226 | 12:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 137 | 01:00 | 131 | 12:00 | Kushtia | 140 | 06:00 | 131 | 07:00
| Agargaon | 139 | 06:00 | 132 | 11:00 | Lalbag | 136 | 06:00 | 128 | 11:00
| Agrabad | 140 | 06:00 | 132 | 03:00 | Lalmonirhat | 131 | 22:00 | 115 | 08:00
| AKS | 140 | 06:00 | 130 | 12:00 | Madanganj | 138 | 03:00 | 130 | 04:00
| Aminbazar | 136 | 03:00 | 130 | 13:00 | Madaripur | 137 | 18:00 | 132 | 13:00
| Amnura | 136 | 19:30 | 122 | 08:00 | Madartek | 138 | 06:00 | 129 | 12:00
| Ashuganj | 135 | 00:00 | 130 | 12:00 | Madunaghat | 140 | 06:00 | 133 | 12:00
| Bagerhat | 138 | 02:00 | 129 | 12:00 | Magura | 140 | 05:00 | 128 | 08:00
| Bakulia | 139 | 06:00 | 131 | 12:00 | Mahasthangarh | 134 | 20:00 | 122 | 08:00
| Banani | 137 | 05:00 | 127 | 15:00 | Manikganj | 133 | 02:00 | 122 | 16:00
| Bangabhaban | 137 | 07:00 | 130 | 12:00 | Maniknagar | 136 | 02:00 | 130 | 12:00
| Barapukuria | 134 | 23:00 | 122 | 07:00 | Matarbari | 133 | 06:00 | 124 | 12:00
| Barguna | 136 | 18:00 | 128 | 22:00 | Matuail | 138 | 05:00 | 133 | 12:00
| Barishal | 139 | 05:00 | 134 | 13:00 | Millgate | 139 | 11:00 | 127 | 15:00
| Barishal-230 | 140 | 06:00 | 135 | 14:00 | Mirpur | 136 | 06:00 | 128 | 14:00
| Baroaulia | 141 | 19:30 | 134 | 13:00 | Mithapukur | 133 | 19:30 | 119 | 07:00
| Baroirhat | 140 | 17:00 | 132 | 12:00 | Modern | 140 | 06:00 | 132 | 11:00
| Bashundhara | 137 | 04:00 | 126 | 15:00 | Mogbazar | 140 | 06:00 | 130 | 12:00
| BashundharaCement | 138 | 03:00 | 132 | 22:00 | Mongla | 138 | 05:00 | 129 | 08:00
| Beanibazar | 135 | 06:00 | 130 | 12:00 | Motijheel | 137 | 07:00 | 130 | 12:00
| Benapole | 139 | 03:00 | 125 | 08:00 | Munshiganj | 136 | 18:00 | 133 | 12:00
| Bhaluka | 122 | 04:00 | 110 | 07:00 | Mymensingh | 131 | 02:00 | 110 | 11:00
| Bhandaria | 138 | 05:00 | 134 | 13:00 | Naogaon | 132 | 05:00 | 116 | 08:00
| Bhangura | 142 | 04:00 | 132 | 08:00 | Narail | 139 | 05:00 | 125 | 08:00
| Bheramara | 138 | 04:00 | 128 | 08:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bheramara(GK) | 137 | 04:00 | 133 | 11:00 | Narshingdi | 136 | 06:00 | 130 | 00:00
| Bhulta | 130 | 18:00 | 125 | 22:00 | Natore | 136 | 04:00 | 125 | 08:00
| Bog-Sherpur | 137 | 04:00 | 124 | 08:00 | Nawabganj | 135 | 06:00 | 127 | 12:00
| Bogura | 136 | 20:00 | 123 | 08:00 | Netrakona | 122 | 05:00 | 104 | 12:00
| Bogura-230 | 136 | 04:00 | 124 | 08:00 | New | 135 | 00:00 | 127 | 11:00
| Brahmanbaria | 132 | 04:00 | 126 | 12:00 | Niamatpur | 128 | 19:30 | 110 | 08:00
| Cantonment | 139 | 06:00 | 131 | 12:00 | Noapara | 136 | 19:30 | 129 | 08:00
| Chandpur | 141 | 17:00 | 133 | 12:00 | Pabna | 140 | 05:00 | 129 | 08:00
| Chandraghona | 141 | 06:00 | 133 | 12:00 | Palashbari | 131 | 19:30 | 116 | 07:00
| Chapai | 136 | 14:00 | 125 | 07:00 | Panchagarh | 136 | 13:00 | 113 | 07:00
| Charsaidpur | 139 | 06:00 | 134 | 10:00 | Patuakhali | 133 | 09:00 | 128 | 00:00
| Chauddagram | 139 | 06:00 | 132 | 12:00 | Payra | 132 | 04:00 | 129 | 22:00
| Chhatak | 134 | 03:00 | 131 | 12:00 | PHP | 140 | 06:00 | 131 | 12:00
| Chowmuhani | 140 | 17:00 | 130 | 12:00 | Postogola | 136 | 06:00 | 129 | 12:00
| Chuadanga | 137 | 06:00 | 124 | 08:00 | Purbachal | 140 | 06:00 | 129 | 13:00
| Coxsbazar | 130 | 09:00 | 122 | 13:00 | Purbasadipur | 132 | 13:00 | 113 | 07:00
| Cumilla(N) | 142 | 06:00 | 122 | 15:00 | Rahim | 138 | 05:00 | 134 | 15:00
| Cumilla(S) | 140 | 01:00 | 128 | 09:00 | Rajbari | 138 | 05:00 | 129 | 12:00
| Daudkandi | 138 | 18:00 | 133 | 12:00 | Rajendrapur | 135 | 00:00 | 129 | 08:00
| Dhaka | 138 | 05:00 | 131 | 12:00 | Rajshahi | 135 | 06:00 | 124 | 07:00
| Dhamrai | 138 | 06:00 | 130 | 14:00 | Rajshahi-230 | 138 | 09:00 | 123 | 07:00
| Dhanmondi | 140 | 06:00 | 134 | 12:00 | Ramganj | 139 | 17:00 | 130 | 13:00
| Dohazari | 138 | 17:00 | 130 | 11:00 | Rampur | 138 | 07:00 | 134 | 02:00
| Faridpur | 138 | 06:00 | 130 | 12:00 | Rampura | 138 | 05:00 | 130 | 12:00
| Fatullah | 137 | 06:00 | 132 | 12:00 | Rangamati | 140 | 06:00 | 133 | 12:00
| Fenchuganj | 139 | 06:00 | 134 | 14:00 | Rangpur | 133 | 22:00 | 120 | 07:00
| Feni | 140 | 17:00 | 133 | 12:00 | Ruppur | 140 | 01:00 | 131 | 08:00
| Ghorashal | 140 | 00:00 | 136 | 09:00 | Saidpur | 132 | 14:00 | 114 | 07:00
| Goalpara | 142 | 06:00 | 132 | 08:00 | Satkhira | 140 | 03:00 | 129 | 08:00
| Gollamari | 140 | 05:00 | 131 | 13:00 | Satmasjid | 139 | 06:00 | 131 | 12:00
| Gopalganj | 142 | 06:00 | 130 | 22:00 | Savar | 136 | 06:00 | 127 | 15:00
| Gopalganj-400 | 138 | 05:00 | 131 | 13:00 | Shahjadpur | 145 | 03:00 | 136 | 07:00
| Gopalganj_I | N/A | N/A | N/A | N/A | Shahjibazar | 134 | 05:00 | 131 | 15:00
| Gulshan | 137 | 05:00 | 130 | 12:00 | Shahmirpur | 138 | 17:00 | 133 | 12:00
| Halishahar | 139 | 06:00 | 131 | 12:00 | Shariatpur | 138 | 06:00 | 132 | 11:00
| Haripur | 138 | 05:00 | 134 | 15:00 | Sherpur | 130 | 20:00 | 113 | 16:00
| HaripurSBU | 139 | 06:00 | 134 | 14:00 | Shikalbaha | 140 | 05:00 | 134 | 12:00
| Hasnabad | 136 | 01:00 | 129 | 11:00 | Shikalbaha-230 | 140 | 07:00 | 134 | 04:00
| Hathazari | 142 | 03:00 | 136 | 15:00 | Shitalakhya | 136 | 06:00 | 127.2 | 13:00
| Ishurdi | 139 | 06:00 | 130 | 08:00 | Sholosohor | 141 | 06:00 | 132 | 03:00
| Jaldhaka | 144 | 08:00 | 114 | 07:00 | Shyampur | 136 | 02:00 | 130 | 12:00
| Jamalpur | 132 | 20:00 | 114 | 16:00 | Shyampur-230 | 136 | 02:00 | 132 | 10:00
| Jashore | 138 | 06:00 | 126 | 08:00 | Siddhirganj | 138 | 04:00 | 134 | 11:00
| Jhenaidah | 136 | 19:30 | 128 | 08:00 | Sirajganj | 138 | 02:00 | 126 | 07:00
| Jhenaidah-230 | 140 | 04:00 | 129 | 08:00 | Sonargaon | 136 | 00:00 | 133 | 13:00
| Joydebpur | 141 | 03:00 | 134 | 12:00 | Sreemongol | 134 | 06:00 | 130 | 12:00
| Joypurhat | 132 | 03:00 | 115 | 08:00 | Srinagar | 135 | 06:00 | 126 | 13:00
| Juldah | 140 | 19:00 | 131 | 12:00 | SSM | 143 | 19:30 | 137 | 12:00
| Kabirpur | 137 | 04:00 | 124 | 15:00 | Sunamganj | 133 | 09:00 | 129 | 12:00
| Kachua | 141 | 19:30 | 132 | 13:00 | Sylhet | 134 | 04:00 | 132 | 15:00
| Kaliakoir | 138 | 00:00 | 132 | 14:00 | Tangail | 134 | 00:00 | 125 | 16:00
| Kallyanpur | 134 | 01:00 | 128 | 13:00 | Thakurgaon | 136 | 22:00 | 106 | 07:28
| Kalurghat | 139 | 09:00 | 134 | 00:00 | TK | 140 | 05:00 | 133 | 12:00
| Kamrangirchar | 135 | 06:00 | 127 | 13:00 | Tongi | 138 | 08:00 | 130 | 11:00
| Kaptai | 140 | 01:00 | 136 | 07:00 | Ullon | 138 | 01:00 | 130 | 13:00
| Kazla | 137 | 06:00 | 129 | 13:00 | Uttara | 136 | 06:00 | 126 | 16:00
| Keranigonj | 135 | 06:00 | 127 | 11:00 | UttaraNew | 136 | 02:00 | 128 | 15:00
| Khagrachori | 140 | 06:00 | 132 | 11:00 | Zigatola | 133 | 05:00 | 126 | 13:00
| Khulna | 140 | 06:00 | 131 | 08:00
| Khulna(S) | 142 | 06:00 | 131 | 08:00
| Khulshi | 140 | 06:00 | 131 | 12:00
| Kishoreganj | 128 | 06:00 | 118 | 12:00
| Kodda | 137 | 00:00 | 129 | 08:00
| KSRM | 139 | 09:00 | 132 | 21:00
| Kulaura | 137 | 06:00 | 134 | 12:00
| Kurigram | 131 | 23:00 | 114 | 07:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2023-01-31
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 1228 | 4936 | 3631 | 8567 |  |  |  | QF-LDC-11
0:30 | 1172 | 4776.5 | 3479.5 | 8256 | Date: | 2023-01-31
1:00 | 1116 | 4617 | 3328 | 7945
1:30 | 1078 | 4499.5 | 3182 | 7681.5
2:00 | 1040 | 4382 | 3036 | 7418
2:30 | 1015 | 4311.5 | 3018 | 7329.5 | [5 empty] | Gen. at Eve. Peak | 10187 | 10187 MW (19:30 )
3:00 | 990 | 4241 | 3000 | 7241 | [6 empty] | 19:30
3:30 | 960 | 4159 | 2961 | 7120 | [5 empty] | Gen. at Day Peak | 9296 | 9296 MW (12:00 )
4:00 | 930 | 4077 | 2922 | 6999 | [6 empty] | 12:00
4:30 | 900 | 4070 | 2902 | 6972 | [5 empty] | Highest Generation | 10187
5:00 | 870 | 4063 | 2882 | 6945 | [6 empty] | 19:30
5:30 | 845 | 4227 | 2943.5 | 7170.5
6:00 | 820 | 4391 | 3005 | 7396
6:30 | 745 | 4581 | 3133 | 7714
7:00 | 670 | 4771 | 3261 | 8032
7:30 | 710 | 4841 | 3491 | 8332
8:00 | 750 | 4911 | 3721 | 8632
8:30 | 835 | 4943.5 | 3807 | 8750.5
9:00 | 920 | 4976 | 3893 | 8869
9:30 | 1010 | 4951.5 | 3870.5 | 8822
10:00 | 1100 | 4927 | 3848 | 8775
10:30 | 1155 | 5012 | 3880 | 8892
11:00 | 1210 | 5097 | 3912 | 9009
11:30 | 1256 | 5151.5 | 4001 | 9152.5
12:00 | 1302 | 5206 | 4090 | 9296
12:30 | 1359 | 5229.5 | 4121.5 | 9351
13:00 | 1416 | 5253 | 4153 | 9406
13:30 | 1526 | 5195 | 4169 | 9364
14:00 | 1636 | 5137 | 4185 | 9322
14:30 | 1587 | 5195.5 | 3958 | 9153.5
15:00 | 1538 | 5254 | 3731 | 8985
15:30 | 1409 | 5249 | 3635.5 | 8884.5
16:00 | 1280 | 5244 | 3540 | 8784
16:30 | 1200 | 5309 | 3490.5 | 8799.5
17:00 | 1120 | 5374 | 3441 | 8815
17:30 | 1095 | 5506.5 | 3812.5 | 9319
18:00 | 1070 | 5639 | 4184 | 9823
18:30 | 1115 | 5736.5 | 4267 | 10003.5
19:00 | 1160 | 5834 | 4350 | 10184
19:30 | 1146 | 5871 | 4316 | 10187
20:00 | 1110 | 5894 | 4232 | 10126 |  |  |  | Executive Engineer
20:30 | 1210 | 5777 | 4254.5 | 10031.5 |  |  |  | Network Operation Division
21:00 | 1310 | 5660 | 4277 | 9937
21:30 | 1345 | 5542 | 4223 | 9765
22:00 | 1380 | 5424 | 4169 | 9593 |  |  |  |  | Page 6 of 7
22:30 | 1355 | 5287.5 | 4117.5 | 9405
23:00 | 1330 | 5151 | 4066 | 9217
23:30 | 1279 | 5043.5 | 3848.5 | 8892
24:00 | 1228 | 4936 | 3631 | 8567
10187 MW (19:30 )
9296 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2023-01-31 |  | Energy |  | 210859455
[13 empty] | 2023-01-31 |  |  |  |  | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 3243 | 907 | 1624 | 0 | 929 | 1492 | 30 | 120 | 124 | 98 | 0 | 0
0:30 | 3252.5 | 907.5 | 1597.5 | 0 | 816.5 | 1411.5 | 30 | 84.5 | 62 | 94 | 0 | 0 | Date: | 2023-01-31
1:00 | 3262 | 908 | 1571 | 0 | 704 | 1331 | 30 | 49 | 0 | 90 | 0 | 0
1:30 | 3217 | 860.5 | 1549 | 0 | 606 | 1281.5 | 30 | 49.5 | 0 | 88 | 0 | 0 | [7 empty] | Total Energy | 210.8595 | Total Energy Gen 210.859 MKWHr Energy Not Served 2.441 MKWHr Energy Requirement 213.301 MKWHr
2:00 | 3172 | 813 | 1527 | 0 | 508 | 1232 | 30 | 50 | 0 | 86 | 0 | 0 | [7 empty] | Energy not Served | 2.441
2:30 | 3158.5 | 813.5 | 1506 | 0 | 454 | 1232 | 30 | 50.5 | 0 | 85 | 0 | 0 | [7 empty] | Energy Requirement | 213.3005
3:00 | 3145 | 814 | 1485 | 0 | 400 | 1232 | 30 | 51 | 0 | 84 | 0 | 0
3:30 | 3099 | 813.5 | 1464 | 0 | 348 | 1232 | 30 | 50.5 | 0 | 83 | 0 | 0 | [5 empty] | Shortage
4:00 | 3053 | 813 | 1443 | 0 | 296 | 1232 | 30 | 50 | 0 | 82 | 0 | 0
4:30 | 2986.5 | 813.5 | 1497.5 | 0 | 301 | 1211.5 | 30 | 50 | 0 | 82 | 0 | 0
5:00 | 2920 | 814 | 1552 | 0 | 306 | 1191 | 30 | 50 | 0 | 82 | 0 | 0
5:30 | 2912.5 | 814 | 1633.5 | 0 | 437.5 | 1201 | 30 | 50 | 8 | 84 | 0 | 0
6:00 | 2905 | 814 | 1715 | 0 | 569 | 1211 | 30 | 50 | 16 | 86 | 0 | 0
6:30 | 2931.5 | 861 | 1743 | 0 | 750 | 1242 | 30 | 50 | 17 | 87 | 2.5 | 36 |  |  |  | Coal
7:00 | 2958 | 908 | 1771 | 0 | 931 | 1273 | 30 | 50 | 18 | 88 | 5 | 72
7:30 | 2989.5 | 908 | 1866 | 0 | 991.5 | 1348.5 | 30 | 50 | 28.5 | 89 | 31 | 118.9418 |  |  | Oil |  |  |  | ,
8:00 | 3021 | 908 | 1961 | 0 | 1052 | 1424 | 30 | 50 | 39 | 90 | 57 | 165.8835
8:30 | 3021.5 | 908.5 | 1885.5 | 0 | 1135 | 1459.5 | 30 | 50 | 62 | 96 | 102.5 | 169.5698
9:00 | 3022 | 909 | 1810 | 0 | 1218 | 1495 | 30 | 50 | 85 | 102 | 148 | 173.2561
9:30 | 2957.5 | 909 | 1770.5 | 0 | 1264.5 | 1474.5 | 30 | 50 | 85 | 104 | 177 | 174.1777
10:00 | 2893 | 909 | 1731 | 0 | 1311 | 1454 | 30 | 50 | 85 | 106 | 206 | 175.0993
10:30 | 2912.5 | 908.5 | 1735 | 0 | 1363.5 | 1453 | 30 | 59 | 114 | 104 | 212.5 | 198.5994
11:00 | 2932 | 908 | 1739 | 0 | 1416 | 1452 | 30 | 68 | 143 | 102 | 219 | 222.0996
11:30 | 2926 | 908 | 1810.5 | 0 | 1450.5 | 1452 | 30 | 68 | 148.5 | 106 | 253 | 228.0898
12:00 | 2920 | 908 | 1882 | 0 | 1485 | 1452 | 30 | 68 | 154 | 110 | 287 | 234.0801
12:30 | 2970 | 908.5 | 1889 | 0 | 1461 | 1462 | 30 | 68 | 178 | 104 | 280.5 | 232.2369
13:00 | 3020 | 909 | 1896 | 0 | 1437 | 1472 | 30 | 68 | 202 | 98 | 274 | 230.3938
13:30 | 3020 | 909 | 1896 | 0 | 1437 | 1472 | 30 | 68 | 202 | 98 | 274 | 230.3938
14:00 | 3020 | 909 | 1896 | 0 | 1437 | 1472 | 30 | 68 | 202 | 98 | 274 | 230.3938
14:30 | 3072.5 | 908.5 | 1783.5 | 0 | 1404.5 | 1467.5 | 30 | 68 | 155.5 | 97 | 208.5 | 213.3446
15:00 | 3125 | 908 | 1671 | 0 | 1372 | 1463 | 30 | 68 | 109 | 96 | 143 | 196.2955
15:30 | 3095 | 907 | 1620 | 0 | 1393.5 | 1452 | 30 | 69 | 114 | 95 | 109 | 165.4227
16:00 | 3065 | 906 | 1569 | 0 | 1415 | 1441 | 30 | 70 | 119 | 94 | 75 | 134.5499
16:30 | 3086 | 905.5 | 1568 | 0 | 1458.5 | 1410.5 | 30 | 69 | 120.5 | 103 | 48.5 | 117.5008
17:00 | 3107 | 905 | 1567 | 0 | 1502 | 1380 | 30 | 68 | 122 | 112 | 22 | 100.4517
17:30 | 3098 | 905 | 1617 | 0 | 1858 | 1395 | 30 | 59 | 229 | 117 | 11 | 160.354
18:00 | 3089 | 905 | 1667 | 0 | 2214 | 1410 | 30 | 50 | 336 | 122 | 0 | 220.2564
18:30 | 3142.5 | 835 | 1675 | 0 | 2312.5 | 1435.5 | 30 | 85 | 371 | 117 | 0 | 195.1282
19:00 | 3196 | 765 | 1683 | 0 | 2411 | 1461 | 30 | 120 | 406 | 112 | 0 | 170
19:30 | 3240 | 765 | 1665 | 0 | 2270 | 1574 | 30 | 121 | 408 | 114 | 0 | 155
20:00 | 3283 | 765 | 1611 | 0 | 2274 | 1563 | 30 | 120 | 368 | 112 | 0 | 140
20:30 | 3312 | 812 | 1660 | 0 | 2102.5 | 1570.5 | 30 | 120 | 313.5 | 111 | 0 | 109
21:00 | 3341 | 859 | 1709 | 0 | 1931 | 1578 | 30 | 120 | 259 | 110 | 0 | 78
21:30 | 3328.5 | 883.5 | 1713.5 | 0 | 1792 | 1576.5 | 30 | 120 | 211 | 110 | 0 | 39
22:00 | 3316 | 908 | 1718 | 0 | 1653 | 1575 | 30 | 120 | 163 | 110 | 0 | 0
22:30 | 3288 | 909 | 1697.5 | 0 | 1524 | 1574.5 | 30 | 120 | 155 | 107 | 0 | 0
23:00 | 3260 | 910 | 1677 | 0 | 1395 | 1574 | 30 | 120 | 147 | 104 | 0 | 0
23:30 | 3251.5 | 908.5 | 1650.5 | 0 | 1162 | 1533 | 30 | 120 | 135.5 | 101 | 0 | 0 | Max Temp. in Dhaka |  | 29.6° C
24:00 | 3243 | 907 | 1624 | 0 | 929 | 1492 | 30 | 120 | 124 | 98 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 210.859 MKWHr Energy Not Served 2.441 MKWHr Energy Requirement 213.301 MKWHr
Shortage
Note on W13: Author:

## Generation
g | 2023-01-31
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 725760
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [5 empty] | 1 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 8 | 8 | 213350
| Teknaf 20MW PP (Solartech) | [6 empty] | 1 | 6 | 13 | 17 | 19 | 20 | 18 | 17 | 13 | 9 | 3 | [9 empty] | 135270
6 | Sikalbaha 225MW CCPP (Gas) | 164 | 165 | 162 | 162 | 162 | 162 | 161 | 163 | 155 | 155 | 155 | 152 | 153 | 154 | 151 | 152 | 151 | 152 |  | 154 | 156 | 156 | 156 | 158 | 159 | 160 | 3734545
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [17 empty] | 32 |  | 83 | 83 | 83 | 83 | 83 | 83 | 60 | 489758
12 | Hathazari 100 MW peaking PP | [6 empty] | 2 | 23 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 517392
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 52 |  | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 1185127
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP | [8 empty] | 21 | 21 | 21 | 21 | 26 | 26 | 18 | 18 | 17 | 19 |  | 20 | 20 |  |  |  |  | 0 | 233008
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 32 |  |  |  |  | 17 | 32 | 32 | 33 | 33 | 42 | 48 | 47 | 33 | 33 | 33 | 35 | 105 |  | 147 | 147 | 147 | 147 | 77 | 50 | 32 | 1156691
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 36 | 36 | 110 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 1288000
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4 | 210 | 170 | 172 | 170 | 170 | 170 | 170 | 220 | 217 | 160 | 160 | 160 | 160 | 120 | 120 | 120 | 120 | 120 |  | 200 | 220 | 220 | 220 | 180 | 150 | 120 | 2463875
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 38 | 38 | 38 | 38 | 36 | 36 |  | 38 | 42 | 41 | 41 | 41 | 41 | 41 | 955584
33 | Ashuganj 225 MW CCPP | 135 | 139 | 136 | 136 | [12 empty] | 99 | 98 |  | 98 | 94 | 95 | 98 | 94 | 85 | 97 | 1275000
34 | Ashuganj 450 MW CCPP(South)
| Ashuganj 450 MW CCPP(North) | 290 | 295 | 295 | 295 | 295 | 295 | 360 | 345 | 305 | 320 | 346 | 345 | 305 | 310 | 310 | 310 | 290 | 285 |  | 285 | 285 | 285 | 290 | 280 | 280 | 280 | 7680600
| Ashuganj 420 MW CCPP(East) | 331 | 331 | 331 | 337 | 317 | 318 | 392 | 386 | 420 | 350 | 376 | 382 | 346 | 340 | 339 | 339 | 280 | 280 |  | 300 | 300 | 300 | 300 | 320 | 300 | 300 | 7971800
35 | Ashuganj 55 MW PP (Precision) | 10 | 10 | 10 | 10 | 21 | 47 | 50 | 50 | 50 | 50 | 50 | 51 | 51 | 52 | 50 | 50 | 51 | 51 |  | 52 | 52 | 51 | 51 | 50 | 51 | 50 | 1025760
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 381 | 381 | 375 | 321 | 321 | 321 | 324 | 387 | 394 | 395 | 393 | 388 | 380 | 369 | 358 | 355 | 350 | 345 |  | 339 | 339 | 339 | 339 | 339 | 339 | 339 | 8761340
40 | Meghnaghat 450 MW CCPP(MPL)
41 | Haripur 360MW CCPP(HPL) | 248 | 253 | 249 | 270 | 274 | 280 | 285 | 261 | 260 | 252 | 227 | 227 | 215 | 214 | 194 | 194 | 188 | 183 |  | 183 | 183 | 180 | 180 | 182 | 171 | 174 | 5378000
42 | RPCL 210MW CCPP | 109 | 108 | 107 | 109 | 109 | 109 | 48 | 49 | 51 | 44 | 44 | 44 | 33 | 34 | 34 | 35 | 49 | 48 |  | 50 | 55 | 78 | 98 | 99 | 100 | 100 | 1617600
43 | Sutiakhali 50 MW Solar PP | [14 empty] | 14 | 7 | 2 | [9 empty] | 42660
44 | Fenchugonj CCPP Phase-1 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 716000
45 | Fenchugonj CCPP Phase-2 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 981720
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 66 | 66 | 40 | 40 | 66 | 66 | 65 | 65 | 66 | 64 | 63 | 61 | 63 | 63 | 63 | 63 | 64 | 65 |  | 65 | 65 | 64 | 64 | 64 | 64 | 65 | 1505376
48 | Shahjibazar 86MW PP (Shahjibazar) | 10 | 10 | 10 | 10 | 84 | 84 | 60 | 60 | 60 | 60 | 60 | 84 | 84 | 84 | 84 | 87 | 87 | 87 |  | 84 | 84 | 84 | 87 | 87 | 87 | 87 | 1622400
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 218 | 218 | 218 | 218 | 218 | 218 | 218 | 218 | 218 | 218 | 218 | 218 | 218 | 210 | 211 | 211 | 211 | 218 |  | 218 | 218 | 218 | 218 | 219 | 217 | 218 | 4350030
51 | Sylhet 20 MW GTPP | 19 | 19 | 19 | 19 | 19 | 20 | 19 | 19 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 19 | 19 | 432000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 237780
54 | Hobiganj 11MW PP Cofidence-E | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 192384
55 | Fenchugonj 51 MW PP (Barakatullah) | 31 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 22 | 31 | 31 | 31 | 11 | 11 | 11 |  | 4 | [5 empty] | 0 | 298800
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 8 | 12 | 12 | 12 | 12 | 12 | 12 |  | 6 | [5 empty] | 0 | 268704
57 | Bibiana-II 341 MW CCPP (Summit) | 265 | 270 | 270 | 265 | 280 | 270 | 290 | 310 | 290 | 280 | 310 | 310 | 310 | 280 | 280 | 280 | 285 | 280 |  | 270 | 260 | 270 | 290 | 295 | 300 | 265 | 6962000
| Bibiyana South 400 MW | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 222 | 222 | 400 | 398 | 400 | 400 |  | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 6989900
58 | Nababganj 55 MW PP (Southern power ) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 0 |  |  |  |  | 5 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 332911
59 | Tangail Palli Power Gen 22 MW | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 148320
60 | Barabkunda 22 MW PP (Regent)
61 | Narshingdi 22 MW PP (Doreen) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 368712
62 | Tangail 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 21 | 21 |  | 22 | 22 | 22 | 22 | 22 | 19 | 19 | 452304
63 | Impoprt (Tripura) | 90 | 86 | 84 | 82 | 82 | 86 | 88 | 90 | 102 | 106 | 102 | 110 | 98 | 104 | 96 | 94 | 112 | 122 |  | 112 | 114 | 112 | 110 | 110 | 104 | 98 | 2344320
64 | Malancha, Ctg. EPZ (United) | 18 | 20 | 29 | 30 | 32 | 42 | 40 | 12 | 2 | 2 | 2 | 2 | 2 | 2 | 0 | 2 | 2 | 7 |  | 11 | 5 | 11 | 9 | 9 | 11 | 12 | 299520
65 | Feni 22MW PP (Doreen) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 463932
66 | Feni 11 MW PP (Doreen) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 116640
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 20 | 19 | 15 | 14 | 14 | 15 | 16 | 16 | 21 | 18 |  | 22 | 23 | 24 | 29 | 33 | 33 | 33 | 607700
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 18 | 18 | 21 | 21 | 21 | 21 | 18 | 21 | 21 | 21 | 21 |  | 21 | 21 | 15 | 21 | 15 | 17 | 18 | 450300
69 | Summit Ashulia | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 528000
70 | Summit Madhabdi | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 28 | 28 | 28 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 22 |  | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 635940
71 | Maona 33 MW PP(Summit) | 28 | 28 | 28 | 28 | 28 | 28 | 33 | 33 | 33 | 25 | 25 | 33 | 33 | 33 | 33 | 33 | 33 | 25 |  | 25 | 33 | 33 | 33 | 33 | 33 | 33 | 768000
72 | Rupganj 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 8 | 25 | 25 | 25 | 25 | 25 | 24 | 16 | 23 | 23 |  | 16 | 16 | 18 | 23 | 23 | 23 | 23 | 541500
73 | Ghorashal 108MW PP (Regent) | 72 | 72 | 36 | 34 | 34 | 34 | 38 | 71 | 71 | 68 | 68 | 68 | 70 | 68 | 66 | 66 | 73 | 75 |  | 75 | 75 | 76 | 76 | 76 | 76 | 75 | 1503363
| Feni Lanka Power | [5 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 330600
| Chowmuhani 113 MW | [5 empty] | 7 | 9 | 9 | 9 | 9 | 9 | 9 | 17 | 26 | 29 | 48 | 67 | 116 |  | 118 | 118 | 116 | 118 | 117 | 38 | 9 | 896280
| Manikgonj 162MW PP(MPGL) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 462240
77 | Siddhirganj 100 PP(Dutch Bangla) | 27 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 30 | 42 | 42 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 35 | 25 | 873600
78 | Gazipur 52 MW PP |  |  |  |  | 3 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 8 | 214560
79 | Kodda 150MW PP | [5 empty] | 16 | 16 | 16 | 16 | 16 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 48 |  | 48 | 48 | 48 | 48 | 32 | 32 | 32 | 586560
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 8 | [11 empty] | 5 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 106488
| Gazipur 100 MW PP | 17 | 17 | 17 | 17 | 25 | 35 | 35 | 35 | 35 | 35 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 |  | 52 | 52 | 52 | 52 | 52 | 35 | 35 | 979848
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 1 | 2 | 3 | 4 | 4 | 4 | 3 | 2 | 1 | 0 | [9 empty] | 27000
| Jodiac Power | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 449725
| Karnaphuli Power Ltd. | 55 | 55 | 55 | 17 | 17 | 21 | 52 | 52 | 52 | 52 | 53 | 54 | 54 | 54 | 63 | 92 | 92 | 92 |  | 92 | 92 | 92 | 92 | 92 | 86 | 92 | 1587417
82 | Madanganj 102 PP(Summit) | 17 | 17 | 17 | 1 |  | 15 | 51 | 51 | 51 | 45 | 40 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 48 | 17 |  |  | 0 | 705249
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP ( Summit) | 153 | 153 | 155 | 155 | 155 | 155 | 153 | 153 | 152 | 153 | 153 | 152 | 152 | 153 | 153 | 153 | 145 | 145 |  | 145 | 145 | 142 | 140 | 140 | 140 | 143 | 3582982
87 | Meghnaghat 100 MW(IEL) | 24 | 25 | 25 | 25 | 25 | 25 | 24 | 21 | 27 | 46 | 50 | 50 | 49 | 50 | 51 | 49 | 50 | 51 |  | 49 | 50 | 50 | 50 | 49 | 49 | 25 | 936960
| Meghnaghat 104 MW PP (OPCL) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 46 | 52 | 55 | 55 | 54 | 54 | 53 | 54 | 54 |  | 54 | 54 | 55 | 54 | 54 | 54 | 17 | 948480
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 22 |  |  |  |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 427680
92 | Fenchuganj 44MW (Energyprima) | 49 | 30 | 30 | 10 | 10 | 36 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 45 | 45 | 10 | 10 | 10 |  | 0 | [5 empty] | 0 | 614808
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 15 | 15 | 15 | 32 | 51 | 51 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 29 | 43 | 43 | 43 | 51 | 834921
94 | Gagnagar 102 MW PP (Digital Power) | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 40 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 24 | 24 | 24 | 865152
95 | Patenga 50MW PP (Baraka) | 3 | [5 empty] | 16 | 24 | 22 | 26 | 26 | 26 | 26 | 26 |  | 12 | 32 | 33 |  | 33 | 33 | 33 | 19 | 19 | 19 | 21 | 447840
96 | Chattogram 108 MW PP (ECPV) | [26 empty] | 0
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 30 |  | 30 | 15 | 30 | 15 | 15 | 15 | 15 | 410681
100 | Manikganj 55 MW PP (Northern) | [9 empty] | 17 | 17 | 35 | 35 | 17 | 17 | 35 | 35 | 35 |  | 35 | 55 | 55 | 17 |  |  | 0 | 310995
101 | Kushiara 163 MW CCPP (KP) |  | 46 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 |  | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 2583736
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 | 1 | 1 | 1 | 2 | 2 | 1 | 1 | 1 | 0 | [9 empty] | 9500
103 | Kamalaghat 54 MW PP(Banco Energy) | [10 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 |  | 0 | 208080
104 | Keranigonj 300 MW PP (APR) | [25 empty] | 0 | 0
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 49 | 48 | 58 | 8 | 8 | 14 | 46 | 46 | 46 | 48 | 57 | 57 | 57 | 48 | 48 | 48 | 53 | 52 |  | 49 | 58 | 53 | 52 | 49 | 48 | 49 | 1123200
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 35 |  |  |  |  | 9 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 371952
115 | Juldah 100 MW PP Unit-3 (Acorn) | 25 |  |  |  |  | 16 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 493440
116 | Chandpur 200MW (Desh energy) | 34 |  |  |  |  | 3 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 |  | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 677760
117 | Ashuganj 150MW PP (Midland) | 5 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 10 | 11 | 8 | 6 | 6 | 5 | 6 | 6 |  | 5 | 5 | 6 | 6 | 6 | 8 | 6 | 167272
118 | Bibiyana-III 400 MW CCPP | 367 | 344 | 349 | 344 | 344 | 344 | 294 | 238 | 240 | 237 | 233 | 238 | 397 | 402 | 402 | 403 | 402 | 402 |  | 402 | 402 | 402 | 402 | 402 | 402 | 400 | 8396000
| Jamalpur 115 MW PP (United) | 28 | 28 |  |  |  | 10 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 37 | 47 |  | 47 | 47 | 47 | 47 | 47 | 47 | 28 | 704400
| Anwara 300 MW PP (United) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 100 | 100 | 104 | 105 | 108 | 107 | 112 | 114 | 106 | 268 |  | 263 | 273 | 278 | 67 | 16 | 16 | 16 | 1987200
| Juldah unit-2 (Acorn) | [5 empty] | 5 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 476160
| Anlima Energy Ltd. | 107 | 107 | 17 | 17 | 17 | 29 | 105 | 107 | 107 | 107 | 98 | 92 | 107 | 107 | 107 | 100 | 106 | 107 |  | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 2271982
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 444600
| Spectra Solar Plant Ltd. | [6 empty] | 0 | 3 | 11 | 17 | 25 | 27 | 16 | 16 | 7 | 2 | 2 | [9 empty] | 131780
| Chandpur 115(Doreen) | 36 |  |  |  |  | 36 | 36 | 35 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 48 | 72 |  | 72 | 72 | 72 | 72 | 64 | 28 | 18 | 885120
| Kanchan Purbachal Power Generation Ltd. | [5 empty] | 8 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 347400
| Mirsharai 150 MW (Oil) | [10 empty] | 18 | 18 | 18 | 18 | 18 | 18 | 18 | [8 empty] | 0 | 125454
| Mirsharai 150 MW (Gas) | [9 empty] | 0
120 | Eastern Zone Total | 4617 | 4382 | 4241 | 4077 | 4063 | 4391 | 4771 | 4911 | 4976 | 4927 | 5097 | 5206 | 5253 | 5137 | 5254 | 5244 | 5374 | 5639 |  | 5834 | 5871 | 5894 | 5660 | 5424 | 5151 | 4936 | 118974778
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | [14 empty] | 16 | 16 | 16 | 49 |  | 49 | 49 | 49 | 49 | 49 | 49 | 0 | 318720
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL) | 49 | 50 | 51 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 52 | 50 | 50 |  | 120 | 121 | 120 | 120 | 120 | 120 | 120 | 1535563
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [17 empty] | 35 | [8 empty] | 31200
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | [5 empty] | 2 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 36 |  | 53 | 53 | 53 | 56 | 56 | 56 | 17 | 522240
130 | Mongla Orion 100 MW Solar PP | [6 empty] | 2 | 19 | 38 | 57 | 68 | 64 | 59 | 39 | 42 | 26 | 6 | [9 empty] | 436320
131 | Rampal 1320 MW (BIFPCL)
132 | United Payra Power Ltd. | [6 empty] | 14 | 54 | 54 | 54 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 150 |  | 150 | 54 | 54 | 17 |  |  | 0 | 645600
133 | Bhola Nutan Biddut BD LTD (GAS) | 221 | 221 | 173 | 173 | 173 | 170 | 221 | 220 | 185 | 183 | 183 | 200 | 221 | 221 | 163 | 163 | 160 | 200 |  | 221 | 221 | 221 | 221 | 221 | 223 | 223 | 4797382
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [6 empty] | 16 | 16 | 16 | 16 | 16 | 16 | 0 |  |  |  |  | 16 |  | 16 | 16 | 16 | 16 |  |  | 0 | 156576
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 171 | 180 | 185 | 186 | 183 | 166 | 186 | 186 | 186 | 186 | 186 | 175 | 179 | 179 | 179 | 179 | 179 | 179 |  | 179 | 178 | 183 | 183 | 183 | 181 | 180 | 4384333
140 | Bhola 33 MW PP (Venture) | 21 | 20 | 19 | 19 | 18 | 20 | 20 | 19 | 18 | 17 | 18 | 19 | 21 | 19 | 17 | 16 | 17 | 22 |  | 24 | 24 | 25 | 25 | 25 | 23 | 22 | 478283
141 | Noapara 100 MW PP (Bangla Trac) | [25 empty] | 0 | 0
142 | Noapara 40 MW PP (Khanjahan Ali) | [15 empty] | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 |  | 0 | 53250
143 | Gopalganj 100 MW Peaking PP | [17 empty] | 20 | [8 empty] | 21248
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | [5 empty] | 50 | 50 | 85 | 85 | 85 | 85 | 85 | 15 | 15 | 15 | 15 | 15 | 72 |  | 85 | 50 | 50 | 50 |  |  | 0 | 870624
146 | Bheramara HVDC | 908 | 813 | 814 | 813 | 814 | 814 | 908 | 908 | 909 | 909 | 908 | 908 | 909 | 908 | 908 | 906 | 905 | 905 |  | 765 | 765 | 765 | 859 | 908 | 910 | 907 | 21210909
147 | Bheramara 410 MW CCPP
148 | Payra 1320 MW | 1000 | 900 | 900 | 900 | 860 | 880 | 940 | 1090 | 1162 | 1122 | 1122 | 1122 | 1142 | 1162 | 1132 | 1110 | 1050 | 1080 |  | 1130 | 1244 | 1232 | 1244 | 1244 | 1244 | 1162 | 28064000
149
150 | Barapukuria TPP Unit-1 | 81 | 81 | 81 | 81 | 81 | 81 | 83 | 84 | 82 | 82 | 80 | 80 | 80 | 80 | 81 | 81 | 80 | 80 |  | 81 | 80 | 81 | 82 | 80 | 80 | 80 | 1906909
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 250 | 251 | 251 | 251 | 250 | 250 | 250 | 250 | 251 | 250 | 250 | 250 | 250 | 249 | 250 | 250 | 250 | 250 |  | 250 | 250 | 250 | 252 | 251 | 250 | 250 | 6067100
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [12 empty] | 33 | 34 |  |  |  | 34 |  | 34 | 34 | 34 | 0 |  |  |  | 164274
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 1 | 1 | 3 | 4 | 5 | 3 | 1 | 0 | 0 | 0 | [9 empty] | 21420
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 215 | 170 | 170 | 130 | 130 | 130 | 130 | 166 | 195 | 180 | 180 | 180 | 207 | 220 | 200 | 150 | 150 | 150 |  | 160 | 175 | 194 | 208 | 215 | 220 | 220 | 4708282
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 383 | 321 | 327 | 290 | 294 | 355 | 327 | 444 | 385 | 330 | 334 | 424 | 414 | 427 | 309 | 258 | 258 | 419 |  | 437 | 439 | 370 | 435 | 438 | 400 | 371 | 8851236
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [11 empty] | 5 | 5 | 11 | 11 | 11 | 11 | 17 |  | 18 | 20 | [5 empty] | 91582
162 | Bogra 22 MW PP (GBB) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 20 | 18 | 18 | 20 | 20 | 20 | 20 | 21 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 474240
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 197964
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | [5 empty] | 8 | 8 | 8 | 42 | 42 | 42 | 42 | 42 | 42 |  |  |  | 42 |  | 42 | 8 |  |  |  |  | 0 | 368287
167 | Katakhali 50 MW Peaking PP | [8 empty] | 16 | 16 | 16 | 16 | 16 | 16 |  |  |  | 27 |  | 40 | 40 | 40 | 0 |  |  |  | 184131
168 | Santahar 50 MW Peaking PP | [11 empty] | 6 | 16 | 16 | 16 | 26 | 30 | 35 |  | 35 | 35 | 35 | 0 |  |  |  | 215104
169 | Natore 52 MW PP (Rajlanka) | [6 empty] | 8 | 8 | 8 | 8 | [9 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 0 | 69067
170 | Chapainawabganj 100 MW Peaking PP | [10 empty] | 42 | 42 | 42 | 42 |  |  |  | 37 |  | 96 | 96 | 96 | 96 | 16 |  | 0 | 499744
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [9 empty] | 20 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 821280
172 | Confidence Power Bogura Unit-1 113 MW | [8 empty] | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 50 | 70 |  | 76 | 75 | 75 | 75 | 75 | 75 | 0 | 807936
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [7 empty] | 40 | 47 | 50 | 50 | 56 | 56 | 56 | 56 | 62 | 49 | 70 |  | 78 | 78 | 78 | 78 | 78 | 34 | 0 | 937142
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 0 | 1 | 3 | 4 | 5 | 6 | 5 | 4 | 3 | 1 | [9 empty] | 28269
178 | Energypac Power Venture Thakurgaon Ltd. | [9 empty] | 0 | 35 | 35 | 74 | 114 | 75 | 35 | 35 | 51 |  | 115 | 115 | 115 | 115 | 114 | 113 | 0 | 1124352
| Intraco Solar 30 MW | [6 empty] | 0 | 4 | 6 | 13 | 16 | 24 | 18 | 26 | 19 | 8 | 1 | 0 | [8 empty] | 135130
Adani Power Jharkhanda Ltd
178 | Teesta Solar Limited | [6 empty] | 2 | 23 | 75 | 92 | 78 | 136 | 148 | 106 | 41 | 18 | 7 | [9 empty] | 684980