## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2023-02-16 | Thursday
|  | Date (day): | 2023-02-16 |  | Thursday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 9757.6 | MW |  |  | (b) At Evening Peak Hour : |  | 11396 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2023-02-15 | 2023-02-16 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 120 | 120 | 120 | 120
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 | 365 |  | Under maint.
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 0 | 0 | 0 |  | 412 | Under maint
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 269 | 269 | 280 | 280 | 80 |  | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 225 | 225 | 225 |  | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 17 | 51 | 50 | 50 | 50 |  | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 142 | 142 | 140 | 140 | 195 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 17 | 17 | 51 | 51 | 51 |  | Fuel shortage
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 15 | 20 | 15 | 30 | 25 |  | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 22 | 19 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 25 | 50 | 50 | 50 | 50 |  | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 |  |  | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 24 | 42 | 16 | 50 | 52 |  | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 35 | 0 | 35 | 19 |  | Fuel shortage
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 48 | 82 | 48 | 64 | 85 |  | Fuel shortage
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 35 | 17 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 35 | 17 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 47 | 47 | 49 | 49 |  | 31 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 26 | 24 | 28 | 28 |  | 5 | Engine problem
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 25 | 41 | 25 | 50 | 2
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 65 | 97 | 64 | 145 | 155 |  | Fuel shortage
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 0 | 300 |  | Fuel shortage
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Fuel shortage
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Fuel shortage
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 35 | 59 | 35 | 72 | 77 |  | Fuel shortage
36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 88 | 52 | 90 | 15 |  | Fuel shortage
37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 17 | 55 | 17 | 55 | 49 |  | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 17 | 144 | 17 | 162
39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 28 | 0 | 30 | 0
40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 17 | 0 | 17 | 38 |  | Fuel shortage
| Dhaka area Total |  |  |  |  | 6263 | 5847 | 1455 | 1930 | 1578 | 2108 | 2402 | 948
41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 8 | 25 | 8 | 25 |  |  | Fuel shortage
43 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 20 | 0 | 20 | 0
44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 13 | 19 | 19 | 19 | 31 |  | Fuel shortage
45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 60 | 60 | 60 | 60 | 170 |  | Low Water Level
46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 151 | 152 | 150 | 150 |  | 75 | ST Under maint
47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 23 | 85 | 17 | 85 | 20 |  | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 34 | 74 | 41 | 70 | 28 |  | Fuel shortage
50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 85 | 85 | 85 |  | 17 | Engine problem
51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 22 | 22 | 22 | 22 | 78 |  | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 38 | 25 | 38 | 25 | 75 |  | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 22 |  | Gas shortage
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 0 | 0 | 0 | 0
54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 100 | 272 | 100 | 300
57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 17 | 17 | 17 | 17 | 37 |  | Fuel shortage
58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 61 | 74 | 55 | 92 | 18 |  | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 38 | 25 | 25 | 25 | 75 |  | Fuel shortage
60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 107 | 107 | 107 | 107 |  | 9 | Engine problem
| Mirsharai 150 MW |  | Gas/HSD | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0
| Chattogram area Total |  |  |  |  | 2442 | 2382 | 696 | 1042 | 769 | 1082 | 1022 | 251
61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 201 | 223 | 220 | 220 |  |  | Capacity Test
63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 330 | 285 | 320 | 300 |  |  | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Macine problem
65 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 287 | 306 | 335 | 335 | 65 |  | Gas shortage
66 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 10 | 10 | 10 | 10 | 35 |  | Gas shortage
67 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 55 | 0 | 0 | 0 | 0 | 55 |  | Gas shortage
68 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
69 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 43 | 43 | 43 |  | 8 | Engine problem
70 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 73 | 133 | 75 | 150
71 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 37 | 31 | 36 | 36 |  | 16 | Engine problem
72 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under Maint.
73 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 34 | 35 | 34 | 34 | 166 |  | Fuel shortage
74 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 22 | 22 | 22 |  |  | Engine problem
75 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 8 | 8 |  | 3 | Engine problem
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 112 | 118 | 135 | 153
76 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 8 | 16 | 21 | 21 |  | 12 | Engine problem
77 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 8 | 0 | 8 | 44 |  | Fuel shortage
78 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 21 | 21 | 21 | 21 |  | 4 | Engine problem
79 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel shortage
80 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 34 | 17 | 17 | 17 | 80 |  | Fuel shortage
81 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 9 | 9 | 9 | 104 |  | Fuel shortage
82 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 17 |  | 37 | Engine problem
83 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 40 | 74 | 40 | 72 | 43 |  | Fuel shortage
| Cumilla Area Total |  |  |  |  | 3309 | 3285 | 1291 | 1384 | 1371 | 1484 | 1113 | 603
84 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 35 | 51 | 34 | 70 | 132 |  | Gas shortage
85 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 16 | 19 | 19 | 19 |  |  | Gas shortage
86 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0
87 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
88 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 74 | 103 | 100 | 100 | 100 |  | Fuel shortage
89 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 88 | 49 | 50 | 50 | 65 |  | Fuel shortage
90 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 45 | 0 | 50 | 0
91 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 6 | 6 | 6 | 16 |  | Fuel shortage
| Mymensingh Area Total |  |  |  |  | 717 | 614 | 266 | 228 | 260.6 | 245 | 132 | 0
92 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 43 | 43 | 43 |  | 27 | Machine problem.
93 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 43 | 43 | 43 | 43 |  | 47 | Machine problem
94 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 112 | 112 | 112 | 112 |  | 51 | ST Under maint
95 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
96 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 11 | 47 | 10 | 31
97 | Fenchuganj 44MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 10 | 30 | 10 | 30
98 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 8 | 5 | 8 |  | 3 | Engine problem
99 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 60 | 40 | 61 | 61
100 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 40 | 86 | 40 | 86
101 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
102 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 213 | 214 | 217 | 220
103 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 19 | 19
104 | Sylhet 50MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Gas shortage
105 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 8 | 8 | 8 | 8 |  | 17 | Engine problem
106 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 330 | 300 | 300 | 300 |  |  | FGMO
107 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 285 | 292 | 285 | 285 |  | 115 | ST under maint
108 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 7 | 8 | 10 | 10
109 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 400 | 350 | 400 | 400
| Sylhet Area Total |  |  |  |  | 2472 | 2427 | 1585 | 1599 | 1563 | 1656 | 0 | 690
110 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 901 | 757 | 914 | 919
111 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 0 | 33 | 0 | 32 | 83 |  | Fuel shortage
112 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 50 | 0 | 45 |  | 9 | Engine problem
113 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
114 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 30 | 0 | 80 |  | 29 | Engine problem
115 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 | 410 |  | Gas shortage.
116 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 16 | 0 | 8 | 32 |  | Fuel shortage
117 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Fuel shortage
118 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 55 | 17 | 55 | 50 |  | Fuel shortage
119 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 50 | 0 | 100
120 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 84 | 0 | 100 | 0
| Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 660*2 | 617 | 617 | 0 | 0 | 400 | 400 |  |  | Coal Shortage.
| Khulna Area Total |  |  |  |  | 3005 | 3001 | 985 | 991 | 1431 | 1639 | 921 | 38
121 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 16 | 16 | 16 | 94 |  | Fuel shortage
122 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 16 | 20 | 16 | 21 |  | 19 | Engine problem
123 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 188 | 192 | 190 | 192
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
124 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 1152 | 1122 | 1000 | 1244
125 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 108 | 200 | 110 | 110 |  | 110
126 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 35 | 150 | 150 | 150
127 | Barisal 307 MW |  | Coal | BCPCL | 307*1 | 307 | 307 | 154 | 188 | 150 | 150
| Barisal Area Total |  |  |  |  | 2265 | 2265 | 1653 | 1888 | 1632 | 1883 | 94 | 129
128 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
129 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 34 | 0 | 34 |  | 18 | Engine problem
130 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 4 | 26 | 0 | 30 |  | 41 | Engine problem
131 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
132 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage
133 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 39 | 40 | 32 | 40 |  | 10 | Engine problem
134 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 182 | 160 | 170 | 160 | 50 |  | Gas shortage
135 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
136 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
137 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 272 | 256 | 280 | 280 | 134 |  | Gas shortage
138 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 23 | 29 | 0 | 30 |  | 20 | Engine problem
139 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 18 | 18 | 22 | 22
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
140 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
141 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 52 | 8 | 0 | 8 | 44 |  | Fuel shortage
142 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 50 | 97 | 50 | 96
143 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel shortage
144 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 50 | 50 | 50 | 50 | 63 |  | Fuel shortage
145 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 35 | 95 | 37 | 95 | 18 |  | Fuel shortage
146 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 4 | 0 | 6 | 0
| Adani Power Jharkhanda Ltd |  | Coal | Import | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | On test.
| Rajshahi Area Total |  |  |  |  | 2179 | 2129 | 740 | 824 | 658 | 856 | 1170 | 89
147 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
148 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 250 | 250 | 250 | 250 |  | 24
149 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
150 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
151 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 42 | 77 | 42 | 80 | 33 |  | Fuel shortage
152 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5 | 0 | 8 | 0
153 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 36 | 115 | 35 | 113
154 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 31 | 0 | 30 | 0
| Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 0 | 0 | 133 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 830 | 750 | 497 | 442 | 495 | 443 | 158 | 109
| Total |  |  |  |  | 23482 | 22700 | 9168 | 10328 | 9757.6 | 11396 | 7012 | 2857
A. |  | 2023-02-15 | (Yesterday) |  |  |  |  | Wednesday
1 | Highest Generation : |  |  | 10328 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
2 | Minimum Generation : |  |  | 7097 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 10838 | MW
3 | Day peak Generation : |  |  | 9168 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 10318.55 | MW
4 | Evening peak Generation : |  |  | 10328 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 470 | MW
5 | Total Energy Generation : |  | 213.5986 | MKWHr | By Solar | 2.2963 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Gas : | 112.2538 | MKWHr |  | By Oil: | 37.4294 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 38.8776 | MKWHr |  | By Hydro: | 0.628 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 7012 | MW | Dhaka | 3756.05 | 3756.05 |  | 0 |  | 18:00 |  | 210
|  |  | For Plants S/D or M/C prob = |  |  | 2857 | MW | Chittagong | 1003 | 1003 |  | 0 |  | 19:00 |  | 470.0032
|  |  | Total = |  |  | 9869 | MW | Khulna | 1188.4 | 1188.4 |  | 0 |  | 19:30 |  | 470.0032
7 | Total Gas Supplied : |  |  | 872.64 | MMCFD |  |  | Rajshahi | 1117.1 | 987.1 |  | 130 |  | 20:00 |  | 370.4732
8 | Fuel Cost : | i) Gas : | Taka | 117210496.342 | ii) Oil : | Taka | 496739626.28 | Comilla | 868 | 868 |  | 0 |  | 21:00 |  | 140.0794
|  | iii) Coal : | Taka | 289798318 | Total | Taka | 903748440.622 | Mymensingh | 1002 | 792 |  | 210 |  | 22:00 |  | 129.9421
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0 | MKWHr. | Sylhet | 370 | 370 |  | 0 |  | 23:00 |  | 160.354
| ii) During Peak Demand : |  |  | 650 | MW (E to W) at | 19:00 | hrs | Barisal | 271 | 271 |  | 0 |  | 24:00 |  | 130
| iii) Maximum : |  |  | 250 | MW at | 21:00 | hrs | Rangpur | 743 | 613 |  | 130
10 | Maximum Temperature in Dhaka was |  |  |  | 27.2° C |  |  | Total | 10318.55 | 9848.55 |  | 470
B. |  | 2023-02-16 | (Today) |  |  |  | Thursday |  |  | Probable max. temperature in Dhaka |  |  | 28.3° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 10850 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 11396 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 9700 | MW
4 | Reserve(Generation end) |  |  |  | 546 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 224.3943 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 7185 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 19.7825 | MKWHr. | ii) HVDC Flow at Peak Time |  | 757 | MW at | 19:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.3309 | MKWHr. | iii) Maximum HVDC Flow : |  | 904 | MW at | 13:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 82.15 |  | (b) Today: | 82.09 |  | (c) Rule Curve: |  | 94.9
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2023-02-15 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 122 | 180 | 0 | 0 | 0 | 0 | 272 |  | 0 | 225 | 140 | 17 | 0 | 15 | 0 | 0 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 22 | 26 | 25 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142 | 0 | 0 | 0 |  | 6 | 0 | 0 | 22 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 225 | 8 | 0 | 10 | 0 | 0 | 43 | 0 | 0 | 8 | 22 | 8 | 33 | 21 | 94 | 104 | 0 | 19 | 0 | 42 | 43 | 31 | 30 | 112 | 0 | 64 | 40 | 0 | 216 | 19 | 0 | 9 | 275 | 8 | 8 | 0 | 32 | 0 | 0 | 9 | 0 | 17 | 0 | 25 | 34 | 75 | 404 | 49 | 30 | 17 | 0 | 16 | 17 | 57 | 17 | 9 | 25 | 400 | 17 | 0 | 17 | 107 | 0 | 0 | 0 | 18 | 0 | 302 | 0 | 0 |  | 774 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 311 | 0 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 1162 | 108 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 0 |  | 4785 | 3305 | 8090 | 3167 | 774 | 1644 | 0 | 868 | 1543 | 0 | 0 | 0 | 94 | 0 | 0 | 82.17
2:00 | 0 | 0 | 120 | 180 | 0 | 0 | 0 | 0 | 267 |  | 0 | 225 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 22 | 26 | 25 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 141 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 229 | 8 | 0 | 10 | 0 | 0 | 43 | 0 | 0 | 8 | 22 | 8 | 33 | 21 | 92 | 105 | 0 | 19 | 0 | 42 | 43 | 11 | 30 | 112 | 0 | 64 | 10 | 0 | 216 | 19 | 0 | 9 | 260 | 8 | 8 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 34 | 73 | 403 | 48 | 0 | 17 | 0 | 16 | 17 | 54 | 0 | 9 | 0 | 375 | 17 | 0 | 17 | 107 | 0 | 0 | 0 | 18 | 0 | 312 | 0 | 0 |  | 753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 35 | 1162 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 |  | 4462 | 3197 | 7659 | 3155 | 753 | 1578 | 0 | 539 | 1542 | 0 | 0 | 0 | 92 | 0 | 0 | 82.17
3:00 | 0 | 0 | 121 | 180 | 0 | 0 | 0 | 0 | 281 |  | 0 | 225 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 22 | 26 | 25 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 141 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 229 | 8 | 0 | 10 | 0 | 0 | 43 | 0 | 0 | 8 | 22 | 8 | 33 | 21 | 90 | 105 | 0 | 19 | 0 | 42 | 43 | 11 | 30 | 112 | 0 | 64 | 10 | 0 | 216 | 19 | 0 | 9 | 270 | 8 | 8 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 75 | 402 | 48 | 0 | 17 | 0 | 16 | 17 | 54 | 0 | 0 | 0 | 380 | 17 | 0 | 17 | 55 | 0 | 0 | 0 | 17 | 0 | 312 | 0 | 0 |  | 782 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1060 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 |  | 4395 | 3053 | 7448 | 3160 | 782 | 1601 | 0 | 375 | 1440 | 0 | 0 | 0 | 90 | 0 | 0 | 82.16
4:00 | 0 | 0 | 121 | 180 | 0 | 0 | 0 | 0 | 277 |  | 0 | 225 | 138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 22 | 26 | 25 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 229 | 8 | 0 | 10 | 0 | 0 | 43 | 0 | 0 | 8 | 22 | 8 | 33 | 18 | 82 | 105 | 0 | 19 | 0 | 42 | 43 | 11 | 30 | 112 | 0 | 64 | 10 | 0 | 216 | 20 | 0 | 9 | 270 | 8 | 8 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 75 | 250 | 49 | 0 | 17 | 0 | 16 | 17 | 54 | 0 | 0 | 0 | 360 | 17 | 0 | 17 | 51 | 0 | 0 | 0 | 18 | 0 | 312 | 0 | 0 |  | 793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 192 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 940 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 0 |  | 4206 | 2964 | 7170 | 2990 | 793 | 1611 | 0 | 373 | 1321 | 0 | 0 | 0 | 82 | 0 | 0 | 82.16
5:00 | 0 | 0 | 120 | 180 | 0 | 0 | 0 | 0 | 276 |  | 0 | 225 | 136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 22 | 27 | 25 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 229 | 8 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 22 | 8 | 33 | 21 | 82 | 108 | 0 | 19 | 0 | 42 | 43 | 11 | 10 | 112 | 0 | 40 | 10 | 0 | 216 | 20 | 0 | 9 | 290 | 8 | 8 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 75 | 285 | 24 | 0 | 17 | 0 | 16 | 17 | 54 | 0 | 0 | 0 | 360 | 17 | 0 | 17 | 52 | 0 | 0 | 0 | 18 | 0 | 312 | 0 | 0 |  | 809 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 192 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 900 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 0 |  | 4151 | 2946 | 7097 | 3012 | 809 | 1578 | 0 | 335 | 1281 | 0 | 0 | 0 | 82 | 0 | 0 | 82.16
6:00 | 0 | 0 | 121 | 180 | 0 | 0 | 0 | 0 | 286 |  | 0 | 225 | 131 | 0 | 0 | 1 | 0 | 0 | 0 | 4 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 22 | 27 | 25 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 132 | 0 | 0 | 0 |  | 0 | 0 | 0 | 12 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 221 | 8 | 0 | 10 | 0 | 0 | 27 | 0 | 0 | 0 | 22 | 8 | 33 | 21 | 86 | 105 | 0 | 19 | 0 | 42 | 43 | 22 | 16 | 112 | 0 | 64 | 40 | 0 | 216 | 20 | 0 | 9 | 295 | 8 | 5 | 0 | 0 | 0 | 0 | 9 | 0 | 1 | 0 | 12 | 13 | 75 | 285 | 34 | 5 | 17 | 0 | 16 | 17 | 54 | 17 | 2 | 9 | 340 | 17 | 0 | 17 | 107 | 0 | 0 | 0 | 18 | 0 | 301 | 0 | 0 |  | 729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 250 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 342 | 17 | 0 | 0 | 0 | 34 | 0 | 0 | 35 | 920 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 |  | 4389 | 3030 | 7419 | 3010 | 729 | 1660 | 0 | 584 | 1350 | 0 | 0 | 0 | 86 | 0 | 0 | 82.15
7:00 | 0 | 0 | 120 | 180 | 0 | 0 | 0 | 0 | 279 |  | 0 | 225 | 131 | 13 | 0 | 15 | 0 | 0 | 0 | 17 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 22 | 27 | 25 | 30 | 25 | 0 | 0 | 0 | 0 | 0 | 8 | 132 | 0 | 0 | 0 |  | 5 | 0 | 0 | 22 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 214 | 8 | 0 | 10 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 8 | 22 | 21 | 90 | 50 | 0 | 19 | 0 | 42 | 43 | 22 | 20 | 112 | 0 | 64 | 40 | 0 | 217 | 19 | 0 | 9 | 320 | 8 | 5 | 0 | 32 | 0 | 0 | 9 | 0 | 15 | 2 | 25 | 34 | 73 | 285 | 47 | 35 | 17 | 0 | 16 | 17 | 54 | 17 | 9 | 25 | 335 | 17 | 2 | 17 | 107 | 0 | 0 | 1 | 18 | 0 | 290 | 0 | 0 |  | 865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 339 | 17 | 0 | 8 | 0 | 40 | 0 | 0 | 35 | 1100 | 108 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 1 | 181 | 0 | 5 |  | 4613 | 3445 | 8058 | 2938 | 865 | 1694 | 0 | 910 | 1531 | 0 | 0 | 16 | 90 | 14 | 269.0999 | 82.15
8:00 | 0 | 0 | 120 | 180 | 0 | 0 | 0 | 0 | 294 |  | 0 | 225 | 138 | 17 | 0 | 15 | 0 | 0 | 0 | 17 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 22 | 27 | 25 | 28 | 25 | 0 | 0 | 0 | 0 | 0 | 8 | 147 | 0 | 0 | 0 |  | 6 | 0 | 0 | 22 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 227 | 8 | 0 | 10 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 8 | 15 | 9 | 96 | 44 | 0 | 19 | 1 | 42 | 43 | 22 | 20 | 112 | 0 | 64 | 40 | 0 | 217 | 19 | 0 | 9 | 290 | 8 | 5 | 0 | 32 | 0 | 0 | 9 | 0 | 17 | 5 | 25 | 34 | 73 | 285 | 47 | 35 | 17 | 1 | 16 | 17 | 54 | 17 | 9 | 25 | 340 | 17 | 11 | 17 | 107 | 0 | 12 | 6 | 18 | 0 | 315 | 0 | 0 |  | 780 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 8 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 35 | 15 | 42 | 0 | 1 | 35 | 1152 | 108 | 0 | 7 | 1 | 23 | 0 | 0 | 0 | 0 | 5 | 180 | 0 | 33 |  | 4610 | 3475 | 8085 | 2890 | 780 | 1663 | 0 | 963 | 1582 | 0 | 0 | 24 | 96 | 87 | 658.9261 | 82.15
9:00 | 0 | 0 | 120 | 180 | 0 | 0 | 0 | 0 | 293 |  | 0 | 225 | 148 | 18 | 5 | 15 | 0 | 0 | 0 | 17 | 16 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 27 | 25 | 28 | 25 | 0 | 0 | 0 | 0 | 0 | 8 | 151 | 0 | 0 | 0 |  | 6 | 40 | 0 | 22 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 203 | 8 | 0 | 10 | 0 | 0 | 43 | 0 | 18 | 0 | 0 | 8 | 13 | 14 | 100 | 34 | 0 | 19 | 1 | 42 | 43 | 22 | 20 | 112 | 0 | 63 | 40 | 0 | 219 | 19 | 0 | 7 | 300 | 8 | 5 | 0 | 32 | 0 | 0 | 9 | 0 | 17 | 13 | 25 | 34 | 75 | 285 | 47 | 35 | 17 | 2 | 100 | 17 | 54 | 17 | 9 | 25 | 400 | 17 | 22 | 17 | 107 | 0 | 17 | 14 | 17 | 0 | 297 | 0 | 0 |  | 784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 16 | 52 | 0 | 20 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 40 | 15 | 42 | 0 | 2 | 35 | 1172 | 108 | 0 | 17 | 2 | 47 | 5 | 0 | 0 | 0 | 15 | 152 | 0 | 66 |  | 4912 | 3573 | 8485 | 2982 | 784 | 1667 | 0 | 1072 | 1574 | 0 | 0 | 122 | 100 | 184 | 566.7686 | 82.14
10:00 | 0 | 0 | 118 | 180 | 0 | 0 | 0 | 0 | 280 |  | 0 | 225 | 148 | 17 | 17 | 15 | 0 | 0 | 0 | 17 | 20 | 48 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 12 | 22 | 25 | 25 | 26 | 25 | 0 | 0 | 0 | 0 | 0 | 8 | 153 | 0 | 0 | 0 |  | 6 | 42 | 0 | 22 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 206 | 8 | 0 | 10 | 0 | 0 | 43 | 0 | 38 | 0 | 0 | 8 | 13 | 21 | 104 | 35 | 0 | 19 | 2 | 43 | 43 | 22 | 20 | 112 | 0 | 61 | 40 | 0 | 218 | 19 | 0 | 7 | 300 | 8 | 5 | 0 | 49 | 0 | 0 | 9 | 0 | 17 | 17 | 38 | 34 | 73 | 283 | 49 | 52 | 17 | 3 | 100 | 17 | 54 | 34 | 9 | 25 | 400 | 17 | 34 | 17 | 107 | 0 | 17 | 21 | 18 | 0 | 295 | 0 | 0 |  | 853 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 15 | 0 | 0 | 0 | 0 | 0 | 4 | 44 | 0 | 25 | 16 | 52 | 0 | 18 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 293 | 0 | 0 | 50 | 0 | 42 | 0 | 3 | 35 | 1152 | 108 | 0 | 17 | 3 | 67 | 35 | 0 | 0 | 0 | 22 | 150 | 0 | 94 |  | 5030 | 3733 | 8763 | 2973 | 853 | 1639 | 0 | 1184 | 1552 | 0 | 0 | 192 | 104 | 266 | 494.8858 | 82.14
11:00 | 0 | 0 | 120 | 180 | 0 | 0 | 0 | 0 | 276 |  | 0 | 225 | 142 | 18 | 17 | 15 | 0 | 0 | 0 | 17 | 24 | 48 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 19 | 22 | 25 | 25 | 21 | 25 | 0 | 0 | 60 | 0 | 0 | 8 | 151 | 0 | 0 | 0 |  | 6 | 34 | 0 | 22 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 203 | 8 | 0 | 10 | 0 | 0 | 43 | 0 | 38 | 0 | 10 | 8 | 8 | 21 | 108 | 35 | 0 | 16 | 2 | 43 | 43 | 11 | 10 | 112 | 0 | 61 | 40 | 0 | 216 | 18 | 0 | 7 | 300 | 8 | 5 | 0 | 65 | 0 | 0 | 75 | 0 | 31 | 19 | 38 | 34 | 75 | 285 | 78 | 52 | 17 | 4 | 100 | 17 | 54 | 34 | 9 | 38 | 400 | 17 | 41 | 17 | 107 | 0 | 17 | 27 | 36 | 0 | 273 | 0 | 0 |  | 853 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 17 | 0 | 0 | 0 | 0 | 0 | 4 | 50 | 0 | 25 | 16 | 52 | 0 | 18 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 283 | 0 | 0 | 50 | 0 | 42 | 0 | 4 | 35 | 1152 | 108 | 0 | 17 | 4 | 80 | 36 | 0 | 0 | 0 | 28 | 154 | 0 | 117 |  | 5200 | 3778 | 8978 | 2929 | 853 | 1600 | 0 | 1356 | 1556 | 60 | 0 | 190 | 108 | 326 | 434.9834 | 82.14
12:00 | 0 | 0 | 120 | 180 | 0 | 0 | 0 | 0 | 269 |  | 0 | 225 | 142 | 17 | 17 | 15 | 0 | 0 | 0 | 25 | 24 | 48 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 19 | 22 | 25 | 25 | 26 | 25 | 0 | 0 | 60 | 0 | 0 | 8 | 151 | 0 | 0 | 0 |  | 6 | 34 | 0 | 22 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 201 | 8 | 0 | 10 | 0 | 0 | 43 | 0 | 37 | 0 | 19 | 8 | 8 | 21 | 112 | 35 | 0 | 16 | 2 | 43 | 43 | 11 | 10 | 112 | 0 | 60 | 40 | 0 | 213 | 18 | 0 | 7 | 330 | 8 | 5 | 0 | 65 | 0 | 0 | 74 | 0 | 35 | 20 | 38 | 34 | 73 | 285 | 88 | 52 | 23 | 4 | 100 | 17 | 61 | 34 | 9 | 38 | 400 | 17 | 45 | 17 | 107 | 0 | 17 | 28 | 40 | 0 | 287 | 0 | 0 |  | 901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 16 | 0 | 0 | 0 | 0 | 0 | 4 | 50 | 0 | 0 | 39 | 52 | 23 | 18 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 272 | 0 | 0 | 50 | 0 | 42 | 0 | 5 | 35 | 1152 | 108 | 0 | 35 | 4 | 84 | 36 | 0 | 0 | 0 | 31 | 154 | 0 | 133 |  | 5293 | 3875 | 9168 | 2959 | 901 | 1611 | 0 | 1378 | 1556 | 60 | 0 | 235 | 112 | 356 | 444.1992 | 82.14
13:00 | 0 | 0 | 120 | 180 | 0 | 0 | 0 | 0 | 267 |  | 0 | 225 | 140 | 20 | 17 | 15 | 0 | 0 | 0 | 34 | 24 | 64 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 19 | 22 | 25 | 25 | 26 | 25 | 0 | 0 | 60 | 0 | 0 | 8 | 151 | 0 | 0 | 0 |  | 6 | 38 | 0 | 33 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 196 | 8 | 0 | 10 | 0 | 0 | 43 | 0 | 36 | 0 | 21 | 8 | 8 | 21 | 116 | 32 | 0 | 19 | 2 | 43 | 43 | 11 | 10 | 113 | 0 | 61 | 40 | 0 | 206 | 18 | 0 | 7 | 330 | 8 | 5 | 0 | 65 | 0 | 0 | 74 | 0 | 35 | 20 | 38 | 34 | 75 | 290 | 79 | 52 | 34 | 4 | 100 | 17 | 54 | 34 | 13 | 38 | 400 | 17 | 45 | 17 | 107 | 0 | 17 | 28 | 20 | 0 | 273 | 0 | 0 |  | 904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 17 | 0 | 0 | 0 | 0 | 24 | 4 | 50 | 0 | 0 | 24 | 52 | 25 | 18 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 262 | 17 | 0 | 50 | 0 | 42 | 0 | 6 | 35 | 1182 | 108 | 0 | 35 | 5 | 81 | 36 | 0 | 0 | 0 | 30 | 152 | 0 | 128 |  | 5273 | 3913 | 9186 | 2911 | 904 | 1599 | 0 | 1398 | 1584 | 60 | 0 | 265 | 116 | 349 | 649.7104 | 82.14
14:00 | 0 | 0 | 120 | 180 | 0 | 0 | 0 | 0 | 266 |  | 0 | 225 | 140 | 43 | 17 | 15 | 0 | 0 | 0 | 40 | 24 | 82 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 19 | 22 | 26 | 25 | 26 | 25 | 0 | 0 | 60 | 0 | 0 | 8 | 150 | 0 | 0 | 0 |  | 6 | 42 | 0 | 33 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 212 | 8 | 0 | 10 | 0 | 0 | 43 | 0 | 36 | 0 | 21 | 8 | 8 | 21 | 110 | 30 | 0 | 19 | 2 | 43 | 43 | 11 | 10 | 112 | 0 | 61 | 40 | 0 | 204 | 18 | 0 | 8 | 280 | 8 | 5 | 0 | 65 | 0 | 0 | 74 | 0 | 35 | 18 | 38 | 34 | 68 | 298 | 79 | 52 | 34 | 3 | 100 | 17 | 54 | 34 | 11 | 38 | 400 | 17 | 39 | 17 | 106 | 0 | 17 | 24 | 18 | 0 | 282 | 0 | 0 |  | 903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 16 | 0 | 0 | 0 | 0 | 32 | 14 | 50 | 0 | 0 | 24 | 52 | 28 | 18 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 263 | 20 | 0 | 50 | 0 | 42 | 0 | 5 | 35 | 1172 | 120 | 0 | 35 | 0 | 75 | 36 | 0 | 0 | 0 | 26 | 153 | 0 | 111 |  | 5262 | 3900 | 9162 | 2924 | 903 | 1560 | 0 | 1419 | 1575 | 60 | 0 | 308 | 110 | 303 | 599.9453 | 82.14
15:00 | 0 | 0 | 122 | 180 | 0 | 0 | 0 | 0 | 264 |  | 0 | 225 | 140 | 48 | 17 | 15 | 0 | 0 | 0 | 50 | 32 | 82 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 19 | 22 | 25 | 33 | 24 | 25 | 0 | 0 | 60 | 0 | 0 | 8 | 151 | 0 | 0 | 0 |  | 6 | 42 | 68 | 33 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 221 | 8 | 0 | 10 | 0 | 0 | 43 | 0 | 36 | 5 | 22 | 8 | 8 | 21 | 116 | 33 | 0 | 19 | 1 | 43 | 43 | 11 | 10 | 112 | 0 | 61 | 40 | 0 | 204 | 18 | 0 | 8 | 280 | 8 | 5 | 0 | 65 | 0 | 0 | 9 | 0 | 33 | 13 | 25 | 34 | 68 | 290 | 48 | 52 | 34 | 2 | 100 | 17 | 54 | 34 | 9 | 25 | 400 | 17 | 31 | 17 | 89 | 0 | 17 | 18 | 20 | 0 | 288 | 0 | 0 |  | 901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 14 | 0 | 0 | 0 | 0 | 32 | 17 | 50 | 0 | 0 | 24 | 52 | 29 | 18 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 37 | 0 | 50 | 0 | 42 | 0 | 4 | 35 | 1142 | 220 | 0 | 35 | 3 | 56 | 36 | 0 | 0 | 0 | 20 | 155 | 0 | 84 |  | 5224 | 3930 | 9154 | 2947 | 901 | 1643 | 0 | 1328 | 1547 | 60 | 0 | 380 | 116 | 232 | 500.4152 | 82.13
16:00 | 0 | 0 | 120 | 180 | 0 | 0 | 0 | 0 | 265 |  | 0 | 225 | 142 | 48 | 17 | 15 | 0 | 0 | 0 | 52 | 32 | 64 | 0 | 0 | 0 | 0 | 17 | 17 | 12 | 19 | 22 | 25 | 33 | 24 | 25 | 0 | 0 | 30 | 0 | 0 | 8 | 151 | 0 | 0 | 0 |  | 6 | 42 | 68 | 22 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 212 | 8 | 0 | 10 | 0 | 0 | 43 | 0 | 37 | 8 | 22 | 8 | 12 | 21 | 110 | 35 | 0 | 19 | 1 | 43 | 43 | 11 | 10 | 112 | 0 | 60 | 40 | 0 | 204 | 18 | 0 | 8 | 310 | 8 | 8 | 0 | 65 | 0 | 0 | 18 | 0 | 35 | 8 | 25 | 34 | 78 | 292 | 48 | 52 | 34 | 1 | 100 | 17 | 54 | 17 | 9 | 25 | 396 | 17 | 17 | 17 | 89 | 0 | 17 | 11 | 18 | 0 | 288 | 0 | 0 |  | 901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 16 | 183 | 13 | 0 | 0 | 0 | 0 | 34 | 17 | 50 | 0 | 0 | 24 | 8 | 28 | 18 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 254 | 37 | 0 | 50 | 0 | 63 | 0 | 2 | 35 | 1102 | 220 | 0 | 17 | 1 | 33 | 36 | 0 | 0 | 0 | 10 | 157 | 0 | 44 |  | 5252 | 3796 | 9048 | 2993 | 901 | 1679 | 0 | 1328 | 1509 | 30 | 0 | 370 | 110 | 128 | 319.7865 | 82.13
17:00 | 0 | 0 | 123 | 180 | 0 | 0 | 0 | 0 | 259 |  | 0 | 225 | 142 | 50 | 20 | 15 | 0 | 0 | 0 | 50 | 32 | 48 | 0 | 0 | 0 | 0 | 17 | 17 | 35 | 19 | 22 | 25 | 33 | 24 | 41 | 0 | 0 | 30 | 0 | 0 | 18 | 151 | 0 | 0 | 0 |  | 6 | 49 | 68 | 22 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 219 | 8 | 0 | 10 | 0 | 0 | 43 | 0 | 29 | 8 | 22 | 8 | 14 | 21 | 112 | 35 | 0 | 19 | 0 | 43 | 43 | 12 | 10 | 112 | 0 | 62 | 40 | 0 | 204 | 18 | 0 | 8 | 300 | 8 | 8 | 0 | 67 | 0 | 0 | 18 | 0 | 34 | 2 | 25 | 30 | 97 | 292 | 48 | 52 | 53 | 0 | 100 | 17 | 67 | 17 | 9 | 25 | 400 | 17 | 4 | 17 | 93 | 0 | 17 | 3 | 24 | 12 | 288 | 0 | 0 |  | 901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 16 | 183 | 13 | 0 | 0 | 0 | 0 | 34 | 17 | 50 | 0 | 0 | 24 | 8 | 28 | 18 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 254 | 43 | 0 | 50 | 0 | 77 | 0 | 1 | 70 | 1042 | 170 | 0 | 17 | 0 | 9 | 36 | 0 | 0 | 0 | 3 | 154 | 0 | 13 |  | 5278 | 3703 | 8981 | 2955 | 901 | 1614 | 0 | 1505 | 1446 | 30 | 0 | 383 | 112 | 35 | 199.9818 | 82.12
18:00 | 0 | 0 | 121 | 180 | 0 | 0 | 0 | 0 | 266 |  | 0 | 225 | 142 | 51 | 17 | 15 | 0 | 0 | 0 | 50 | 42 | 64 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 22 | 25 | 33 | 24 | 41 | 0 | 0 | 30 | 0 | 0 | 25 | 151 | 0 | 0 | 0 |  | 6 | 74 | 85 | 22 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 220 | 8 | 0 | 10 | 0 | 0 | 43 | 0 | 31 | 8 | 22 | 8 | 13 | 21 | 120 | 35 | 0 | 19 | 0 | 43 | 43 | 14 | 10 | 112 | 0 | 62 | 86 | 0 | 204 | 18 | 0 | 8 | 315 | 8 | 8 | 0 | 82 | 0 | 0 | 44 | 0 | 35 | 0 | 25 | 36 | 120 | 292 | 48 | 88 | 85 | 0 | 274 | 17 | 74 | 17 | 9 | 25 | 400 | 33 | 0 | 17 | 107 | 0 | 17 | 0 | 54 | 17 | 295 | 0 | 0 |  | 900 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 40 | 0 | 16 | 186 | 18 | 0 | 0 | 0 | 0 | 34 | 23 | 98 | 0 | 0 | 40 | 8 | 29 | 18 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253 | 56 | 0 | 50 | 49 | 77 | 0 | 0 | 95 | 990 | 220 | 0 | 85 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 156 | 0 | 0 |  | 5878 | 4002 | 9880 | 3007 | 900 | 1738 | 0 | 2171 | 1396 | 30 | 0 | 518 | 120 | 0 | 210 | 82.12
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 120 | 180 | 0 | 0 | 0 | 0 | 269 |  | 0 | 225 | 142 | 51 | 17 | 20 | 0 | 0 | 0 | 50 | 42 | 82 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 22 | 22 | 25 | 33 | 24 | 41 | 0 | 0 | 60 | 0 | 0 | 25 | 152 | 0 | 0 | 0 |  | 6 | 74 | 85 | 22 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 285 | 0 | 223 | 8 | 0 | 10 | 0 | 0 | 43 | 0 | 31 | 8 | 22 | 8 | 16 | 21 | 118 | 51 | 0 | 19 | 0 | 43 | 43 | 47 | 30 | 112 | 0 | 40 | 86 | 0 | 214 | 18 | 0 | 8 | 300 | 8 | 8 | 0 | 97 | 0 | 0 | 103 | 0 | 59 | 0 | 25 | 35 | 133 | 292 | 49 | 88 | 85 | 0 | 272 | 17 | 74 | 17 | 9 | 25 | 350 | 55 | 0 | 144 | 107 | 0 | 17 | 0 | 74 | 17 | 306 | 0 | 0 |  | 757 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 50 | 30 | 16 | 192 | 20 | 16 | 0 | 0 | 0 | 34 | 26 | 97 | 0 | 0 | 40 | 8 | 29 | 18 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 256 | 55 | 0 | 50 | 50 | 77 | 0 | 0 | 95 | 1122 | 200 | 0 | 150 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 188 | 0 | 0 |  | 6183 | 4145 | 10328 | 2918 | 757 | 1764 | 0 | 2573 | 1560 | 60 | 0 | 578 | 118 | 0 | 470.0032 | 82.12
19:30 | 0 | 0 | 121 | 180 | 0 | 0 | 0 | 0 | 247 |  | 0 | 225 | 145 | 50 | 17 | 25 | 0 | 0 | 0 | 50 | 42 | 82 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 22 | 22 | 25 | 33 | 24 | 41 | 0 | 0 | 60 | 0 | 0 | 25 | 121 | 0 | 0 | 0 |  | 6 | 74 | 85 | 22 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 224 | 8 | 0 | 10 | 0 | 0 | 43 | 0 | 35 | 8 | 22 | 8 | 21 | 21 | 116 | 60 | 0 | 19 | 0 | 43 | 43 | 51 | 43 | 80 | 0 | 40 | 86 | 0 | 206 | 19 | 0 | 8 | 280 | 8 | 8 | 0 | 97 | 0 | 0 | 103 | 0 | 70 | 0 | 25 | 35 | 133 | 292 | 49 | 88 | 85 | 0 | 278 | 17 | 74 | 17 | 9 | 25 | 320 | 55 | 0 | 144 | 107 | 0 | 17 | 0 | 72 | 17 | 313 | 0 | 0 |  | 754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 30 | 16 | 192 | 21 | 16 | 0 | 0 | 0 | 34 | 25 | 97 | 0 | 0 | 40 | 8 | 30 | 19 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 258 | 55 | 0 | 50 | 50 | 77 | 0 | 0 | 95 | 1222 | 107 | 0 | 150 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 189 | 0 | 0 |  | 6119 | 4107 | 10226 | 2858 | 754 | 1621 | 0 | 2578 | 1661 | 60 | 0 | 578 | 116 | 0 | 470.0032 | 0
20:00 | 0 | 0 | 120 | 180 | 0 | 0 | 0 | 0 | 258 |  | 0 | 225 | 145 | 50 | 17 | 25 | 0 | 0 | 0 | 50 | 42 | 98 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 22 | 22 | 25 | 33 | 24 | 41 | 0 | 0 | 60 | 0 | 0 | 25 | 151 | 0 | 0 | 0 |  | 6 | 64 | 85 | 22 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 223 | 8 | 0 | 10 | 0 | 0 | 43 | 0 | 31 | 8 | 22 | 8 | 21 | 21 | 116 | 102 | 0 | 19 | 0 | 43 | 43 | 51 | 43 | 80 | 0 | 63 | 86 | 0 | 215 | 19 | 0 | 8 | 280 | 8 | 8 | 0 | 97 | 0 | 0 | 103 | 0 | 70 | 0 | 25 | 34 | 150 | 292 | 49 | 88 | 85 | 0 | 284 | 17 | 74 | 17 | 9 | 25 | 400 | 55 | 0 | 144 | 107 | 0 | 17 | 0 | 82 | 17 | 320 | 0 | 0 |  | 542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 30 | 16 | 192 | 21 | 16 | 0 | 0 | 0 | 34 | 25 | 97 | 0 | 0 | 40 | 8 | 29 | 19 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 266 | 55 | 0 | 50 | 50 | 78 | 0 | 0 | 95 | 1232 | 107 | 0 | 150 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 189 | 0 | 0 |  | 6354 | 3916 | 10270 | 3050 | 542 | 1640 | 0 | 2612 | 1671 | 60 | 0 | 579 | 116 | 0 | 370.4732 | 82.12
21:00 | 0 | 0 | 119 | 180 | 0 | 0 | 0 | 0 | 241 |  | 0 | 225 | 142 | 51 | 17 | 15 | 0 | 0 | 0 | 50 | 42 | 98 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 22 | 25 | 33 | 26 | 41 | 0 | 0 | 60 | 0 | 0 | 25 | 152 | 0 | 0 | 0 |  | 6 | 64 | 85 | 22 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 217 | 8 | 0 | 10 | 0 | 0 | 43 | 0 | 38 | 8 | 22 | 8 | 23 | 21 | 114 | 104 | 0 | 19 | 0 | 43 | 43 | 51 | 45 | 112 | 0 | 63 | 86 | 0 | 215 | 19 | 0 | 8 | 290 | 8 | 8 | 0 | 110 | 0 | 0 | 102 | 0 | 75 | 0 | 25 | 34 | 150 | 292 | 49 | 88 | 85 | 0 | 285 | 17 | 74 | 17 | 9 | 25 | 400 | 56 | 0 | 122 | 107 | 0 | 17 | 0 | 72 | 17 | 290 | 0 | 0 |  | 588 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 0 | 16 | 192 | 22 | 16 | 0 | 0 | 0 | 34 | 18 | 97 | 0 | 0 | 40 | 8 | 29 | 22 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 267 | 55 | 0 | 50 | 50 | 78 | 0 | 0 | 95 | 1244 | 107 | 0 | 100 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 229 | 0 | 0 |  | 6292 | 3954 | 10246 | 3044 | 588 | 1669 | 0 | 2501 | 1723 | 60 | 0 | 547 | 114 | 0 | 140.0794 | 82.12
22:00 | 0 | 0 | 118 | 180 | 0 | 0 | 0 | 0 | 240 |  | 0 | 225 | 140 | 20 | 5 | 15 | 0 | 0 | 0 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 35 | 22 | 22 | 26 | 33 | 26 | 25 | 0 | 0 | 30 | 0 | 0 | 25 | 152 | 0 | 0 | 0 |  | 6 | 64 | 17 | 22 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 220 | 8 | 0 | 10 | 0 | 0 | 43 | 0 | 30 | 8 | 22 | 8 | 25 | 21 | 110 | 97 | 0 | 19 | 0 | 43 | 43 | 11 | 10 | 80 | 0 | 40 | 86 | 0 | 215 | 19 | 0 | 8 | 260 | 8 | 8 | 0 | 145 | 0 | 0 | 107 | 0 | 105 | 0 | 25 | 34 | 150 | 292 | 49 | 88 | 85 | 0 | 267 | 17 | 74 | 17 | 9 | 25 | 350 | 56 | 0 | 57 | 107 | 0 | 17 | 0 | 72 | 17 | 312 | 0 | 0 |  | 896 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 16 | 192 | 22 | 16 | 0 | 0 | 0 | 28 | 0 | 50 | 0 | 0 | 0 | 8 | 12 | 22 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 55 | 0 | 50 | 15 | 78 | 0 | 0 | 95 | 1232 | 109 | 0 | 37 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 228 | 0 | 0 |  | 5746 | 4010 | 9756 | 2993 | 896 | 1542 | 0 | 2274 | 1710 | 30 | 0 | 201 | 110 | 0 | 129.9421 | 82.11
23:00 | 0 | 0 | 120 | 180 | 0 | 0 | 0 | 0 | 252 |  | 0 | 225 | 141 | 17 | 0 | 15 | 0 | 0 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 19 | 22 | 26 | 33 | 26 | 25 | 0 | 0 | 30 | 0 | 0 | 25 | 152 | 0 | 0 | 0 |  | 6 | 65 | 17 | 22 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 209 | 8 | 0 | 10 | 0 | 0 | 43 | 0 | 36 | 8 | 22 | 8 | 25 | 21 | 106 | 97 | 0 | 19 | 0 | 43 | 43 | 11 | 10 | 112 | 0 | 62 | 86 | 0 | 215 | 19 | 0 | 8 | 315 | 8 | 8 | 0 | 135 | 0 | 0 | 48 | 0 | 77 | 0 | 25 | 34 | 99 | 292 | 10 | 52 | 85 | 0 | 16 | 17 | 74 | 17 | 9 | 25 | 400 | 48 | 0 | 21 | 107 | 0 | 17 | 0 | 72 | 17 | 280 | 0 | 0 |  | 896 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 193 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 0 | 0 | 220 | 0 | 0 | 158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 283 | 55 | 0 | 50 | 15 | 34 | 0 | 0 | 35 | 1172 | 110 | 0 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 229 | 0 | 0 |  | 5353 | 3690 | 9043 | 3041 | 896 | 1646 | 0 | 1535 | 1621 | 30 | 0 | 168 | 106 | 0 | 160.354 | 82.11
24:00 | 0 | 0 | 120 | 180 | 0 | 0 | 0 | 0 | 251 |  | 0 | 225 | 145 | 17 | 0 | 15 | 0 | 0 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 22 | 26 | 33 | 28 | 25 | 0 | 0 | 30 | 0 | 0 | 25 | 152 | 0 | 0 | 0 |  | 6 | 65 | 17 | 22 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 226 | 8 | 0 | 10 | 0 | 0 | 43 | 0 | 38 | 8 | 22 | 8 | 33 | 21 | 100 | 94 | 0 | 19 | 0 | 43 | 43 | 11 | 10 | 112 | 0 | 63 | 86 | 0 | 214 | 19 | 0 | 8 | 290 | 8 | 8 | 0 | 77 | 0 | 0 | 48 | 0 | 17 | 0 | 25 | 34 | 68 | 82 | 9 | 52 | 85 | 0 | 16 | 17 | 74 | 17 | 9 | 25 | 390 | 17 | 0 | 17 | 107 | 0 | 17 | 0 | 36 | 0 | 310 | 0 | 0 |  | 896 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 192 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 279 | 55 | 0 | 50 | 0 | 34 | 0 | 0 | 35 | 1110 | 111 | 0 | 0 | 0 | 0 | 113 | 0 | 0 | 118 | 0 | 228 | 0 | 0 |  | 4868 | 3726 | 8594 | 2855 | 896 | 1620 | 0 | 1267 | 1656 | 30 | 0 | 170 | 100 | 0 | 130 | 82.11
KWH | 0 | 0 | 2878500 | 4378500 | 0 | 0 | 0 | 0 | 6476000 |  | 0 | 5211500 | 3393629 | 580800 | 185940 | 318923 | 0 | 0 | 0 | 583411 | 491760 | 919680 | 0 | 0 | 0 | 0 | 160200 | 307542 | 298806 | 393984 | 528000 | 601740 | 711200 | 635400 | 563040 | 0 | 0 | 628000 | 0 | 0 | 289342 | 3371840 | 0 | 0 | 0 |  | 138000 | 787056 | 606065 | 475680 | 0 | 447360 | 0 | 15840 | 0 | 0 | 0 | 7694000 | 0 | 5247000 | 217454 | 0 | 274824 | 0 | 0 | 1016500 | 0 | 527344 | 114197 | 443520 | 181080 | 501000 | 468350 | 2330880 | 1543680 | 0 | 437292 | 12900 | 1013000 | 972720 | 443400 | 501336 | 2741809 | 0 | 1441152 | 1209600 | 0 | 5285270 | 449000 | 0 | 190980 | 7227000 | 191472 | 162624 | 0 | 1380000 | 0 | 0 | 945600 | 0 | 783792 | 137700 | 573120 | 716640 | 2156145 | 7295000 | 1196400 | 1123200 | 1062181 | 26641 | 2416255 | 451996 | 1481194 | 450300 | 198240 | 556800 | 9156100 | 631680 | 291750 | 731520 | 2376109 | 0 | 313200 | 183614 | 827520 | 123480 | 7126800 | 0 | 0 |  | 19782545 | 0 | 0 | 0 | 83520 | 0 | 0 | 0 | 199200 | 57216 | 107250 | 4573151 | 406000 | 58848 | 0 | 0 | 0 | 324198 | 167176 | 925704 | 0 | 133023 | 331648 | 525043 | 278479 | 468000 | 0 | 238716 | 0 | 0 | 5735700 | 0 | 0 | 4417518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6972763 | 571200 | 0 | 1032960 | 285408 | 1044096 | 0 | 38264 | 1051392 | 28796500 | 3149536 | 0 | 876000 | 22440 | 563040 | 1086528 | 0 | 0 | 90900 | 190240 | 4254500 | 0 | 829760 |  | 123930099 | 89668462 | 213598561 | 72612433 | 19782545 | 39641347 | 0 | 32305641 | 38877600 | 628000 | 0 | 5123766 | 2330880 | 2296349 | 0
Fuel Cost | 0 | 0 | 4202610 | 6523965 | 0 | 0 | 0 | 0 | 6994080 |  | 0 | 5680535 | 3766928.19 | 6493344 | 2463705 | 4225729.75 | 0 | 0 | 0 | 8529468.82 | 6919063.2 | 14908012.8 | 0 | 0 | 0 | 0 | 2037744 | 4151817 | 4006988.46 | 295488 | 396000 | 0 | 0 | 0 | 9577310.4 | 0 | 0 | 169560 | 0 | 0 | 4730741.7 | 3506713.6 | 0 | 0 | 0 |  | 1800900 | 13128094.08 | 10315226.3 | 6426436.8 | 0 | 5175955.2 | 0 | 52747.2 | 0 | 0 | 0 | 8540340 | 0 | 6086520 | 280515.66 | 0 | 310551.12 | 0 | 0 | 1697555 | 0 | 9107230.88 | 1535949.65 | 607622.4 | 135810 | 876750 | 351262.5 | 16735718.4 | 1682611.2 | 0 | 594717.12 | 205626 | 1387810 | 1283990.4 | 771516 | 867311.28 | 3153080.35 | 0 | 2795834.88 | 2757888 | 0 | 5338122.7 | 965350 | 0 | 378140.4 | 7227000 | 143604 | 123594.24 | 0 | 18837000 | 0 | 0 | 12746688 | 0 | 10855519.2 | 1609713 | 5914598.4 | 9789302.4 | 28612044.15 | 6711400 | 14548224 | 16241472 | 13436589.65 | 0 | 28366833.7 | 4922236.44 | 15745092.22 | 6110571 | 2555313.6 | 6559104 | 8423612 | 8180256 | 4215787.5 | 9282988.8 | 27040120.42 | 0 | 4090392 | 2194187.3 | 12387974.4 | 1626231.6 | 0 | 0 | 0 |  | 59347635 | 0 | 0 | 0 | 869443.2 | 0 | 0 | 0 | 3587592 | 1029888 | 1541182.5 | 5121929.12 | 787640 | 641443.2 | 0 | 0 | 0 | 5436800.46 | 2923908.24 | 14478010.56 | 0 | 2202860.88 | 5608167.68 | 7156336.09 | 4697940.73 | 968760 | 0 | 180708.012 | 0 | 0 | 30341853 | 0 | 0 | 5124320.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6903035.37 | 7676928 | 0 | 12219916.8 | 4124145.6 | 13260019.2 | 0 | 422817.2 | 12763898.88 | 259456465 | 3212526.72 | 0 | 6482400 | 253796.4 | 6604459.2 | 16656474.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 493424438.46 | 502083302.162 | 995507740.622 | 71711237.172 | 59347635 | 45499259.17 | 0 | 411518754.55 | 289798318 | 169560 | 0 | 85220871.73 | 16735718.4 | 15506386.6 | 0
Yesterday Day Peak | 0 | 0 | 120 | 180 | 0 | 0 | 0 | 0 | 269 |  | 0 | 225 | 142 | 17 | 17 | 15 | 0 | 0 | 0 | 25 | 24 | 48 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 19 | 22 | 25 | 25 | 26 | 25 | 0 | 0 | 60 | 0 | 0 | 8 | 151 | 0 | 0 | 0 |  | 6 | 34 | 0 | 22 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 201 | 8 | 0 | 10 | 0 | 0 | 43 | 0 | 37 | 0 | 19 | 8 | 8 | 21 | 112 | 35 | 0 | 16 | 2 | 43 | 43 | 11 | 10 | 112 | 0 | 60 | 40 | 0 | 213 | 18 | 0 | 7 | 330 | 8 | 5 | 0 | 65 | 0 | 0 | 74 | 0 | 35 | 20 | 38 | 34 | 73 | 285 | 88 | 52 | 23 | 4 | 100 | 17 | 61 | 34 | 9 | 38 | 400 | 17 | 45 | 17 | 107 | 0 | 17 | 28 | 40 | 0 | 287 | 0 | 0 |  | 901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 16 | 0 | 0 | 0 | 0 | 0 | 4 | 50 | 0 | 0 | 39 | 52 | 23 | 18 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 272 | 0 | 0 | 50 | 0 | 42 | 0 | 5 | 35 | 1152 | 108 | 0 | 35 | 4 | 84 | 36 | 0 | 0 | 0 | 31 | 154 | 0 | 133 |  | 9168 | DayPeak
Yesterday Evening Peak | 0 | 0 | 120 | 180 | 0 | 0 | 0 | 0 | 269 | 0 | 0 | 225 | 142 | 51 | 17 | 20 | 0 | 0 | 0 | 50 | 42 | 82 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 22 | 22 | 25 | 33 | 24 | 41 | 0 | 0 | 60 | 0 | 0 | 25 | 152 | 0 | 0 | 0 | 0 | 6 | 74 | 85 | 22 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 285 | 0 | 223 | 8 | 0 | 10 | 0 | 0 | 43 | 0 | 31 | 8 | 22 | 8 | 16 | 21 | 118 | 51 | 0 | 19 | 0 | 43 | 43 | 47 | 30 | 112 | 0 | 40 | 86 | 0 | 214 | 18 | 0 | 8 | 300 | 8 | 8 | 0 | 97 | 0 | 0 | 103 | 0 | 59 | 0 | 25 | 35 | 133 | 292 | 49 | 88 | 85 | 0 | 272 | 17 | 74 | 17 | 9 | 25 | 350 | 55 | 0 | 144 | 107 | 0 | 17 | 0 | 74 | 17 | 306 | 0 | 0 |  | 757 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 50 | 30 | 16 | 192 | 20 | 16 | 0 | 0 | 0 | 34 | 26 | 97 | 0 | 0 | 40 | 8 | 29 | 18 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 256 | 55 | 0 | 50 | 50 | 77 | 0 | 0 | 95 | 1122 | 200 | 0 | 150 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 188 | 0 | 0 |  | 10328 | EvPeak
Forecast for Evening | 0 | 0 | 120 | 180 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 225 | 140 | 50 | 51 | 30 | 0 | 0 |  | 50 | 50 | 64 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 22 | 27 | 33 | 28 | 50 | 0 |  | 60 | 0 | 0 | 25 | 150 | 0 | 0 | 0 | 0 | 6 | 70 | 85 | 22 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 220 | 8 | 0 | 10 | 0 | 0 | 43 | 0 | 36 | 8 | 22 | 8 | 21 | 21 | 153 | 70 | 0 | 19 | 0 | 43 | 43 | 31 | 30 | 112 | 0 | 61 | 86 | 0 | 220 | 19 | 0 | 10 | 300 | 8 | 8 |  | 145 | 0 | 0 | 100 | 0 | 72 | 0 | 25 | 34 | 150 | 285 | 50 | 90 | 85 | 0 | 300 | 17 | 92 | 17 | 9 | 25 | 400 | 55 | 0 | 162 | 107 | 0 | 17 |  | 72 | 17 | 335 |  |  |  | 919 | 0 | 0 |  | 32 | 0 | 0 | 0 | 45 | 80 | 8 | 192 | 21 | 16 | 0 | 0 | 0 | 34 | 30 | 96 | 0 | 0 | 40 | 8 | 30 | 22 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 160 |  | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 55 | 0 | 50 | 100 | 80 | 0 | 0 | 95 | 1244 | 110 |  | 150 |  |  | 113 | 0 |  | 400 |  | 150 | 0
Forecast for Day | 0 | 0 | 120 | 180 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 225 | 140 | 50 | 51 | 15 | 0 | 0 | 0 | 50 | 16 | 48 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 19 | 22 | 27 | 33 | 28 | 25 | 0 |  | 60 | 0 | 0 | 8 | 150 | 0 | 0 | 0 | 0 | 6 | 41 | 85 | 22 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 220 | 8 | 0 | 10 | 0 | 0 | 43 | 0 | 36 | 0 | 22 | 8 | 21 | 21 | 135 | 34 | 0 | 19 | 1.6 | 43 | 43 | 10 | 10 | 112 | 0 | 61 | 40 | 0 | 217 | 19 | 0 | 10 | 300 | 8 | 5 | 0 | 64 | 0 | 0 | 100 | 0 | 35 | 20 | 38 | 34 | 75 | 285 | 50 | 52 | 17 | 5 | 100 | 17 | 55 | 17 | 9 | 25 | 400 | 17 | 50 | 17 | 107 | 0 | 17 | 30 | 40 | 0 | 335 |  |  |  | 914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 32 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 17 | 0 | 50 | 0 | 42 | 0 | 8 | 37 | 1000 | 110 |  | 150 | 6 | 100 | 35 | 0 |  | 400 | 30 | 150 |  | 130 |  |  |  |  | g | h | o | c | h | t | s
Generation at 08:00(Today) | 0 | 0 | 120 | 185 | 0 | 0 | 0 | 0 | 297 | 0 | 0 | 225 | 138 | 18 | 30 | 15 | 0 | 0 | 0 | 17 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 22 | 27 | 28 | 16 | 25 | 0 | 0 | 30 | 0 | 0 | 17 | 147 | 0 | 0 | 0 | 0 | 6 | 10 | 0 | 22 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 226 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 25 | 0 | 14 | 8 | 19 | 21 | 104 | 36 | 0 | 19 | 1 | 43 | 43 | 22 | 50 | 112 | 0 | 63 | 87 | 0 | 209 | 19 | 0 | 8 | 280 | 8 | 8 | 0 | 32 | 0 | 0 | 48 | 0 | 17 | 6 | 25 | 34 | 67 | 80 | 9 | 34 | 17 | 1 | 16 | 17 | 55 | 17 | 9 | 25 | 360 | 17 | 9 | 17 | 107 | 0 | 17 | 6 | 18 | 0 | 335 | 0 | 0 | 0 | 778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 342 | 8 | 0 | 35 | 0 | 42 | 0 | 1 | 35 | 870 | 111 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 328 | 6 | 216 | 0 | 29 | 0 |  |  |  | 112.2538 | 19.7825 | 37.4294 | 38.8776 | 0.628 | 2.3309 | 2.2963
213.5986
| Minimum Generation |  | 7097 | 5:00
| Highest Generation |  | 10328 | 19:00
| Day Peak Generation |  | 9168 | 12:00
| Evening Peak Generation |  | 10328 | 19:00
| HVDC Max Flow |  | 904 | 13:00
| HVDC EvPeak Flow |  | 757 | 19:00
| Load factor L.F |  | 86.17% | [161 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2023-02-16
Till now the maximum generation is : - |  |  |  | 14782 | 21:00 | Hrs on | 2022-04-16
The Summary of Yesterday's |  |  | 2023-02-15 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 9168 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 7185
Evening Peak Generation : |  |  | 10328 | MW Hour : | 19:00 | Available Max Generation : |  | 11396
E.P. Demand (at gen end) : |  |  | 10838 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 10850
Maximum Generation : |  |  | 10328 | MW Hour : | 19:00 | Reserve(Generation end) |  | 546
Total Gen. (MKWH) : |  |  | 213.5986 | System Load Factor : | 86.17% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 250 | MW at | 21:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2023-02-16
Actual : |  | 82.09 | Ft.(MSL) , | Rule curve : | 94.9 | Ft.( MSL )
Gas Consumed : |  | Total = | 872.64 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 117210496.342
: |  |  | Coal : | 289798318 | Oil : | 496739626.28 | Total : | 903748440.622
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 0 | 0:00 | 3732.0789 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 1029.075 |  |  | 0 | 0%
Khulna Area |  | 0 | 0:00 | 1351.8952 |  |  | 0 | 0%
Rajshahi Area |  | 130 | 3120:00 | 1191.7227 |  |  | 0 | 0%
Cumilla Area |  | 0 | 0:00 | 1017.9675 |  |  | 0 | 0%
Mymensingh Area |  | 210 | 5040:00 | 836.0795 |  |  | 0 | 0%
Sylhet Area |  | 0 | 0:00 | 378.4564 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 304.802 |  |  | 0 | 0%
Rangpur Area |  | 130 | 3120:00 | 660.1914 |  |  | 0 | 0%
Total |  | 470 |  | 10502.2687 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 2
2) Ghorasal-3,7
3) Ashuganj-5
4) Baghabari-70,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
7) Shajibazar 330 MW
8) Sirajganj-2,3
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
8:35 | 16:18 | Baroirhat-PHP 132 kV Ckt-1 Scheduled S/D from Baroirhat 132/33kV end Due to Annual Maintenance.
8:37 | 15:53 | Kodda(300MW)-Tongi 230kV Ckt-1 Scheduled S/D from Tongi 230/132/33kV end.
8:39 | - | Rampur 230/132/33 S/S Halishahar-2 Scheduled S/D Due to bay maintenance at Halishahar side.
8:40 | 13:05 | Halishahar-Khulshi 132kV Ckt-2 Scheduled S/D from Halishahar 132/33kV end Due to Due to annul maintenance.
8:40 | 13:56 | Goalpara 132/33kV S/S T-6 LT Forced S/D Due to U clamp change.
8:41 | 15:54 | Cumilla(N)-Shahjibazar 230 kV Ckt-1 Scheduled S/D from Cumilla(N) 230/132/33kV end Due to Shahjibazar end annual maintenance work.
8:41 | 17:01 | Goalpara 132/33kV S/S Bus 2 Scheduled S/D Due to Gantry painting.
8:42 | 13:54 | Goalpara 132/33kV S/S T-6 HT Forced S/D Due to U clamp change.
8:44 | - | Sirajganj 132/33kV S/S T3-(435) LT Project Work S/D Due to Due to T-3 Transformer Upgradation work by PGNS (G to G) Project
from 15/02/2023 to 31/05/2023.
8:45 | - | Sirajganj 132/33kV S/S T3-(435) HT Project Work S/D Due to Due to T-3 Transformer Upgradation work by PGNS (G to G) Project
from 15/02/2023 to 31/05/2023.
8:48 | 16:22 | Hathazari-Kaptai 132kV Ckt-2 Scheduled S/D from Hathazari 230/132/33kV end Due to Annual maintenance at Chandroghona s/s demand.
9:00 | 15:52 | Bibiyana-Shahjibazar 230 kV Ckt-1 Scheduled S/D from Bibiana 400/230kV end.
9:01 | 15:10 | Aminbazar-Keraniganj 230kV Ckt-2 Scheduled S/D from Keranigonj 230/132/33kV end Due to Annual Maintenance at Aminbazar End.
and from Aminbazar 400/230/132kV end Due to Red hot maintenance work.
9:12 | - | Madanganj 132/33kV S/S GT-1 LT Scheduled S/D.
9:14 | 17:50 | Jamalpur 132/33kV S/S T-2 LT Scheduled S/D Due to T-2 X-former painting work.
9:14 | 17:50 | Jamalpur 132/33kV S/S T-2 HT Scheduled S/D Due to T-2 X-former painting work.
9:17 | - | Madanganj 132/33kV S/S GT-1 HT Scheduled S/D.
9:45 | 10:32 | Sirajganj 132/33kV S/S T4-(445) LT Forced S/D Due to Emergency red hot maintenance of T-4, 33 kv CT (B-ph.).
9:45 | 10:31 | Sirajganj 132/33kV S/S T4-(445) HT Forced S/D Due to Emergency red hot maintenance of T-4, 33 kv CT (B-ph.).
10:50 | 19:17 | BIPTC S/S Baharampur-2 Project Work S/D Due to DFDR Commissioning work.
11:06 | 23:15 | Kalurghat 132/33kV S/S TRFO-01(506T) HT Project Work S/D Due to None.
11:32 | 13:13 | Hasnabad 132/33kV S/S 132/33kV 414 T-2 LT Forced S/D Due to Red hot 33 kv blue phase Reserve bus DS top.
11:42 | 20:59 | Barishal 230/132kV S/S T-5 HT Project Work S/D Due to SAS work.
11:42 | 21:01 | Barishal 230/132kV S/S T-5 LT Project Work S/D Due to SAS work.
11:45 | - | Manikganj 132/33kV S/S 132/33 kV Transformer GT-2(35/50 MVA) LT Scheduled S/D Due to due to remote switch at control
room not working.
12:19 | 13:25 | Sirajganj 132/33kV S/S T4-(445) HT Forced S/D Due to Red hot at 132 kv Bus DS.
- | 13:17 | Bhola Natun Biddut BD LTD (GAS) GT1 was sync.
14:24 | 15:22 | Agargaon 230/132kV S/S 132kV Transformer-1 (405T1) HT Scheduled S/D Due to For Oil Leakage finding.
- | 15:20 | Sreemongol 132/33kV S/S 132/33kv T-2 LT is restored.
- | 15:20 | Sreemongol 132/33kV S/S 132/33kv T-3 LT is restored.
- | 15:51 | Aminbazar-Kaliakoir 230kV Ckt-2 is restored.
- | 17:01 | Goalpara 132/33kV S/S Bus 2 is restored.
- | 17:13 | Monakasha-Rahanpur 400kV Ckt-1 is restored.
- | 19:17 | Bheramara-Baharampur ckt-2 swtchied on.
19:18 | - | Bhola Natun Biddut BD LTD GT2 was shutdown due to maint. work. | [5 empty] | 70MW generation interrup.
- | 20:48 | Lalbagh GT2 was sync.
- | 23:03 | Rampal 1320 MW (BIFPCL) Unit-1 was sync.
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2023-02-15 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 120 | 2878500
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4378500
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 0 | 0 | Under maint.
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 269 | 6476000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 5211500 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 51 | 580800 | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 142 | 3393629 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 17 | 185940 | Fuel shortage
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 20 | 318923 | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 393984
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 50 | 583411 | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 42 | 491760 | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 35 | 160200 | Fuel shortage
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 82 | 919680 | Fuel shortage
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 35 | 307542 | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 298806 | Fuel shortage
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 47 | 1129740 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 711200
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 24 | 635400 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 41 | 563040 | Engine problem
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 97 | 1380000 | Fuel shortage
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Fuel shortage
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 0 | 0 | Fuel shortage
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Fuel shortage
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 59 | 783792 | Fuel shortage
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 88 | 1123200 | Fuel shortage
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 55 | 631680 | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 144 | 731520 | Engine problem
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 183614
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 123480 | Fuel shortage
| Dhaka area Total |  |  |  | 5847 | 1930 | 34575841
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Machine problem
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 25 | 289342
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 137700
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 447360 | Fuel shortage
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 60 | 628000 | Low water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 152 | 3371840 | ST under maint.
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 85 | 1062181 | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 74 | 787056 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 85 | 606065 | Engine problem
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 22 | 475680 | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 25 | 573120 | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 0 | Gas shortage
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 0 | 15840
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 26641
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 272 | 2416255 | Engine problem
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 17 | 451996 | Fuel shortage
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 74 | 1481194 | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 25 | 556800 | Engine problem
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 107 | 2376109 | Engine problem
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Chattogram area Total |  |  |  | 2382 | 1042 | 15703179
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 223 | 5247000 | 0
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 285 | 7694000
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint.
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 306 | 7126800 | Gas shortage
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 10 | 274824 | Gas shortage
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 0 | 0 | Gas shortage
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 217454 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 1016500 | Machine problem
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 133 | 2156145 | Engine problem
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 31 | 527344 | Engine problem
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 35 | 716640 | Fuel shortage
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 443520
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 181080 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 118 | 2330880
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 16 | 501000 | Engine problem
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 8 | 114197 | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 21 | 468350 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Fuel shortage
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 17 | 450300 | Fuel shortage
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 9 | 198240 | Fuel shortage
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 313200 | Engine problem
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 74 | 827520 | Fuel shortage
| Cumilla Area Total |  |  |  | 3285 | 1384 | 30804994
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 51 | 1543680 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 437292 | Engine problem
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 12900
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 103 | 945600 | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 49 | 1196400 | Fuel shortage
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 291750
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 138000 | Engine problem
| Mymensingh Area Total |  |  |  | 614 | 228 | 4565622
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1013000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 43 | 972720 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 112 | 2741809 | ST under maint.
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 47 | 443400
| Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 30 | 501336 | Gas shortage
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 8 | 162624 | Engine problem
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 40 | 1441152 | Frequency control
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 86 | 1209600
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 214 | 5285270
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 449000
| Sylhet 50MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Gas shortage
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 8 | 191472 | Gas shortage
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7227000 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 292 | 7295000 | ST under maint.
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 8 | 190980
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 350 | 9156100 | Frequency control
| Sylhet Area Total |  |  |  | 2427 | 1599 | 38280463
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Fuel shortage
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 757 | 19782545
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 33 | 83520 | Fuel shortage
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 50 | 199200
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel conservation
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 30 | 57216 | Transformer O/L
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 16 | 107250 | Fuel shortage
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Fuel shortage
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 55 | 571200 | Fuel shortage
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 50 | 285408 | Transformer O/L
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 563040
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 0 | 0 | 0 | On test.
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 660*2 | 617 | 0 | 90900 | Coal shortage
| Khulna Area Total |  |  |  | 3001 | 991 | 21740279
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 16 | 58848 | Fuel shortage
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 20 | 406000 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 192 | 4573151
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1122 | 28796500 | Transformer O/L
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 200 | 3149536
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 150 | 876000
| Barisal 307 MW |  | BCPCL | 307*1 | 307 | 188 | 4254500 | Transformer O/L
| Barisal Area Total |  |  |  | 2265 | 1888 | 42114535
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 34 | 324198 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 26 | 167176 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contract Expired
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 133023 | Fuel shortage
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 40 | 331648 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 160 | 4417518 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 256 | 6972763 | Gas shortage
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 29 | 278479 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 18 | 468000 | Engine problem
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 238716
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 8 | 525043 | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 97 | 925704
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Fuel shortage
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 50 | 1032960 | Fuel shortage
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 95 | 1051392 | Fuel shortage
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 22440
| Adani Power Jharkhanda Ltd |  | Import | 0 | 0 | 0 | 0 | On test.
| Rajshahi Area Total |  |  |  | 2129 | 824 | 16889060
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 250 | 5735700 | Machine problem
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 77 | 1044096 | Fuel shortage
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 38264
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 115 | 1086528
| Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 190240
| Teesta Solar Limited |  | BPCL | 16*12.5 | 0 | 0 | 829760
| Rangpur Area Total |  |  |  | 750 | 442 | 8924588
| Total |  |  |  | 22700 | 10328 | 213598561
| Eastern Grid Total |  |  |  | 14555 | 6183 | 123930099
| Western Grid Total |  |  |  | 8145 | 4145 | 89668462
| National Grid Total |  |  |  | 22700 | 10328 | 213598561
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2023-02-15
| (a) ENTIRE EASTERN GRID : |  | 6789.05 | MW | (b) ENTIRE WESTERN GRID : |  | 3059.5 | MW
| i) Dhaka area |  | 3756.05 | MW | i) Khulna area |  | 1188.4 | MW
| ii) Chittagong area |  | 1003 | MW | ii) Rajshahi area |  | 987.1 | MW
| iii) Comilla area |  | 868 | MW | iii) Barisal area |  | 271 | MW
| iv) Mymensingh area |  | 792 | MW | iv) Rangpur area |  | 613 | MW
| v) Sylhet area |  | 370 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 9848.55 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | Chhatak | 19 | 18:00 | Kamrangirchar | 66 | 13:00 | Natore | 105 | 20:00 | Shitalakhya | 100 | 12:00
2 | AKSML | 38 | 15:00 | Chowmuhani | 136 | 19:30 | Kaptai | 3 | 18:00 | Nawabganj | 28.3 | 21:00 | Sholosohor | 22 | 14:00
3 | Aftabnagar | 24 | 18:30 | Chuadanga | 72 | 18:30 | Kazla | 76 | 19:00 | Netrakona | 108 | 06:00 | Shyampur | 160 | 12:00
4 | Agargaon | 55 | 13:00 | Coxsbazar | 94 | 19:00 | Keranigonj | 58 | 18:30 | New | 60 | 11:00 | Siddhirganj | 94 | 12:00
5 | Agrabad | 46 | 18:30 | Cumilla(N) | 98 | 19:30 | Khagrachori | 26 | 18:30 | Niamatpur | 96 | 18:30 | Sirajganj | 98 | 19:00
6 | Amnura | 46 | 18:30 | Cumilla(S) | 122 | 18:30 | Khulna | 72 | 18:30 | Noapara | 34 | 19:00 | Sonargaon | 87 | 00:00
7 | Ashuganj | 46 | 13:00 | Daudkandi | 106 | 20:00 | Khulshi | 158 | 10:00 | PHP | 5 | 02:00 | Sreemongol | 38 | 19:00
8 | BIPTC | N/A | N/A | Dhaka | 30 | 13:00 | Kishoreganj | 104 | 21:00 | Pabna | 79 | 18:30 | Srinagar | 29.09 | 21:00
9 | BSRM | 111 | 12:00 | Dhamrai | 86 | 16:00 | Kodda | 240 | 16:00 | Palashbari | 94 | 21:00 | Sunamganj | 35 | 18:30
10 | Bagerhat | 73 | 18:30 | Dhanmondi | 95 | 13:00 | Kulaura | 26 | 18:00 | Panchagarh | 54 | 18:30 | Sylhet | 98 | 18:00
11 | Bakulia | 67 | 18:30 | Dohazari | 64 | 18:30 | Kurigram | 60 | 18:00 | Patuakhali | 67 | 21:00 | TK | 20 | 18:30
12 | Banani | 28 | 13:00 | Faridpur | 96 | 18:30 | Kushtia | 86 | 19:00 | Payra | 12 | 18:30 | Tangail | 175 | 21:00
13 | Bangabhaban | 12 | 10:00 | Fatullah | 48 | 10:00 | Lalbag | 55 | 22:00 | Postogola | 29 | 13:00 | Thakurgaon | 66 | 07:48
14 | Barapukuria | 54 | 18:30 | Fenchuganj | 28 | 18:30 | Lalmonirhat | 37 | 18:00 | Purbachal | 28 | 12:00 | Tongi | 97 | 18:00
15 | Barguna | 12 | 18:30 | Feni | 88 | 20:00 | Madanganj | 30 | 12:00 | Purbasadipur | 111 | 18:00 | Ullon | 31 | 18:30
16 | Barishal | 64 | 19:30 | GPH | 90 | 23:00 | Madaripur | 66 | 20:00 | Rahanpur_I | 2.3 | 23:00 | Uttara | 34 | 18:30
17 | Barishal-230 | 67 | 19:00 | Ghorashal | 52 | 19:00 | Madartek | 51 | 20:00 | Rahim | 133 | 13:00 | UttaraNew | 15 | 09:00
18 | Baroaulia | 63 | 11:00 | Goalpara | 18 | 08:00 | Madunaghat | 37 | 18:00 | Rajbari | 46 | 19:00 | Zigatola | 54 | 13:00
19 | Baroirhat | 32 | 18:00 | Gollamari | 34 | 13:00 | Magura | 50 | 18:30 | Rajendrapur | 98 | 19:00
20 | Bashundhara | 108 | 13:00 | Gopalganj | 77.4 | 19:00 | Mahasthangarh | 48 | 07:00 | Rajshahi | 100 | 20:00
21 | BashundharaCement | 0 | 00:00 | Gulshan | 72 | 14:00 | Manikganj | 82 | 20:00 | Rajshahi-230 | 26 | 21:00
22 | Beanibazar | 41 | 18:00 | Halishahar | 78.5 | 11:00 | Maniknagar | 50 | 13:00 | Ramganj | 66 | 18:30
23 | Benapole | 40 | 18:30 | HaripurSBU | 158 | 19:30 | Matarbari | 34 | 17:00 | Rampur | 19 | 18:30
24 | Bhaluka | 104 | 00:00 | Hasnabad | 49 | 19:30 | Matuail | 62 | 10:00 | Rangamati | 12 | 18:00
25 | Bhandaria | 34 | 21:00 | Hathazari | 41 | 19:00 | Millgate | 58 | 10:00 | Rangpur | 114 | 14:00
26 | Bhangura | 26 | 18:30 | Ishurdi | 51 | 19:00 | Mirpur | 97 | 12:00 | Ruppur | 4 | 16:00
27 | Bheramara(GK) | 42 | 18:30 | Jaldhaka | 54 | 18:00 | Mirsorai | 2 | 08:00 | SSM | 18 | 19:30
28 | Bhulta | 219 | 06:00 | Jamalpur | 121 | 22:00 | Mithapukur | 24 | 19:30 | Saidpur | 89 | 15:00
29 | Bog-Sherpur | 68 | 18:00 | Jashore | 109 | 18:30 | Modern | 0 | 00:00 | Satkhira | 98 | 19:00
30 | Bogura | 99 | 19:30 | Jhenaidah | 96 | 18:30 | Mogbazar | 88 | 14:00 | Satmasjid | 65 | 14:00
31 | Borhanuddin | 32 | 21:00 | Joydebpur | 124 | 19:00 | Mongla | 24 | 10:00 | Savar | 136 | 16:00
32 | Brahmanbaria | 108 | 20:00 | Joypurhat | 52 | 18:30 | Motijheel | 24 | 13:00 | Shahjadpur | 82 | 19:30
33 | Cantonment | 94 | 18:30 | Juldah | 22 | 00:00 | Munshiganj | 61 | 21:00 | Shahjibazar | 91 | 18:30
34 | Chandpur | 40 | 20:00 | KSRM | 36 | 19:30 | Mymensingh | 196 | 20:00 | Shahmirpur | 30 | 01:00
35 | Chandraghona | 24 | 19:00 | Kabirpur | 237 | 15:00 | Naogaon | 107 | 11:00 | Shariatpur | 46 | 21:00
36 | Chapai | 56 | 19:30 | Kachua | 50 | 19:00 | Narail | 40 | 18:30 | Sherpur | 113 | 22:00
37 | Charsaidpur | 44 | 01:00 | Kallyanpur | 57 | 14:00 | Narinda | 50 | 13:00 | Shikalbaha | 24 | 19:30
38 | Chauddagram | 32 | 19:30 | Kalurghat | 28 | 12:00 | Narshingdi | 139 | 21:00 | Shikalbaha-230 | N/A | N/A
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2023-02-15 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 406 | 05:00 | 388 | 16:00 | Gopalganj | 425 | 04:00 | 390 | 15:00
| Bhulta | 395 | 20:00 | 379 | 12:00 | Kaliakoir | 398 | 20:00 | 382 | 16:00
| Bibiana | 406 | 20:00 | 395 | 03:00 | Payra | 415 | 20:00 | 408 | 16:00
| BIPTC | 409 | 20:00 | 388 | 11:00 | Rahanpur_I | 413 | 18:00 | 400 | 23:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 236 | 20:00 | 224 | 16:00 | Hasnabad | 234 | 21:00 | 221 | 12:00
| AKSML | 241 | 22:00 | 214 | 09:00 | Hathazari | 243 | 20:00 | 232 | 16:00
| Aminbazar | 238 | 19:30 | 228 | 11:00 | Ishurdi | 239 | 04:00 | 226 | 07:00
| Ashuganj | 242 | 19:00 | 231 | 10:00 | Jhenaidah | 241 | 04:00 | 223 | 11:00
| Baghabari | 235 | 04:00 | 220 | 15:00 | Kaliakoir | 236 | 20:00 | 226 | 15:00
| Barapukuria | 229 | 20:00 | 220 | 11:00 | Keranigonj | 239 | 21:00 | 220 | 12:00
| Barishal | 243 | 05:00 | 237 | 16:00 | Khulna(S) | 245 | 04:00 | 223 | 11:00
| Bheramara | 236 | 04:00 | 221 | 07:00 | Maniknagar | 233 | 02:00 | 222 | 12:00
| Bhulta | 236 | 04:00 | 225 | 12:00 | Meghnaghat | 240 | 00:00 | 230 | 11:00
| Bibiana | 239 | 20:00 | 233 | 09:00 | Mirsorai | 240 | 19:30 | 227 | 03:00
| BIPTC | 240 | 04:00 | 224 | 07:00 | Rajshahi | 238 | 20:00 | 224 | 07:00
| Bogura | 234 | 19:00 | 223 | 07:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 247 | 01:00 | 243 | 15:00 | Rampura | 234 | 04:00 | 224 | 11:00
| BSRM | 241 | 22:00 | 228 | 11:00 | Shikalbaha | 243 | 18:30 | 231 | 03:00
| Cumilla(N) | 237 | 20:00 | 226 | 11:00 | Shyampur | 234 | 20:00 | 221 | 12:00
| Fenchuganj | 242 | 08:00 | 230 | 04:00 | Siddhirganj | 235 | 21:00 | 227 | 13:00
| Ghorashal | N/A | N/A | N/A | N/A | Sirajgonj | 233 | 20:00 | 226 | 10:00
| GPH | 251 | 09:00 | 227 | 03:00 | Tongi | 234 | 22:00 | 217 | 12:00
| Haripur | 233 | 08:00 | 222 | 12:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 136 | 01:00 | 129 | 11:00 | Kushtia | 136 | 04:00 | 129 | 11:00
| Agargaon | 137 | 02:00 | 130 | 16:00 | Lalbag | 135 | 01:00 | 125 | 12:00
| Agrabad | 141 | 21:00 | 132 | 02:00 | Lalmonirhat | 132 | 19:00 | 122 | 07:00
| AKS | 138 | 22:00 | 132 | 09:00 | Madanganj | 135 | 02:00 | 126 | 12:00
| Aminbazar | 140 | 19:30 | 132 | 09:00 | Madaripur | 137 | 05:00 | 131 | 16:00
| Amnura | 135 | 18:00 | 122 | 07:00 | Madartek | 136 | 01:00 | 128 | 12:00
| Ashuganj | 139 | 19:00 | 135 | 10:00 | Madunaghat | 142 | 20:00 | 133 | 08:00
| Bagerhat | 140 | 03:00 | 125 | 10:00 | Magura | 137 | 02:00 | 126 | 11:00
| Bakulia | 140 | 20:00 | 134 | 10:00 | Mahasthangarh | 136 | 20:00 | 124 | 07:00
| Banani | 136 | 02:00 | 126 | 10:00 | Manikganj | 132 | 00:00 | 124 | 10:00
| Bangabhaban | 135 | 02:00 | 128 | 12:00 | Maniknagar | 135 | 04:00 | 127 | 12:00
| Barapukuria | 135 | 19:00 | 128 | 11:00 | Matarbari | 140 | 19:30 | 119 | 04:00
| Barguna | 136 | 00:00 | 127 | 11:00 | Matuail | 135 | 08:00 | 127 | 12:00
| Barishal | 138 | 19:30 | 133 | 16:00 | Millgate | 136 | 04:00 | 126 | 16:00
| Barishal-230 | 139 | 20:00 | 134 | 15:00 | Mirpur | 139 | 20:00 | 130 | 16:00
| Baroaulia | 142 | 20:00 | 135 | 07:00 | Mithapukur | 135 | 19:30 | 120 | 07:00
| Baroirhat | 140 | 22:00 | 134 | 03:00 | Modern | 141 | 21:00 | 132 | 10:00
| Bashundhara | 136 | 20:00 | 127 | 12:00 | Mogbazar | 138 | 02:00 | 130 | 10:00
| BashundharaCement | 135 | 02:00 | 126 | 12:00 | Mongla | 138 | 22:00 | 125 | 11:00
| Beanibazar | 135 | 04:00 | 130 | 10:00 | Motijheel | 135 | 02:00 | 128 | 12:00
| Benapole | 137 | 02:00 | 123 | 11:00 | Munshiganj | 135 | 21:00 | 127 | 12:00
| Bhaluka | 128 | 19:30 | 114 | 06:00 | Mymensingh | 134 | 20:00 | 119 | 09:00
| Bhandaria | 138 | 03:00 | 134 | 12:00 | Naogaon | 133 | 19:00 | 120 | 07:00
| Bhangura | 140 | 04:00 | 133 | 09:00 | Narail | 135 | 03:00 | 125 | 11:00
| Bheramara | 136 | 04:00 | 128 | 10:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bheramara(GK) | 136 | 04:00 | 129 | 11:00 | Narshingdi | 133 | 06:00 | 123 | 12:00
| Bhulta | 129 | 05:00 | 120 | 16:00 | Natore | 135 | 08:00 | 128 | 11:00
| Bog-Sherpur | 137 | 20:00 | 128 | 07:00 | Nawabganj | 136 | 21:00 | 125 | 12:00
| Bogura | 137 | 19:00 | 128 | 11:00 | Netrakona | 127 | 19:30 | 109 | 07:00
| Bogura-230 | 138 | 19:00 | 129 | 10:00 | New | 137 | 02:00 | 128 | 10:00
| Brahmanbaria | 135 | 19:00 | 131 | 10:00 | Niamatpur | 131 | 08:00 | 114 | 10:00
| Cantonment | 137 | 05:00 | 129 | 16:00 | Noapara | 137 | 22:00 | 124 | 10:00
| Chandpur | 140 | 22:00 | 132 | 03:00 | Pabna | 138 | 04:00 | 130 | 07:00
| Chandraghona | 141 | 18:30 | 134 | 03:00 | Palashbari | 133 | 19:00 | 120 | 07:00
| Chapai | 135 | 19:30 | 123 | 07:00 | Panchagarh | 136 | 19:00 | 112 | 07:00
| Charsaidpur | 136 | 20:00 | 127 | 12:00 | Patuakhali | 135 | 18:30 | 125 | 09:00
| Chauddagram | 139 | 07:00 | 131 | 12:00 | Payra | 138 | 21:00 | 127 | 07:00
| Chhatak | 133 | 02:00 | 131 | 12:00 | PHP | 139 | 08:00 | 130 | 10:00
| Chowmuhani | 137 | 07:00 | 130 | 16:00 | Postogola | 137 | 20:00 | 126 | 12:00
| Chuadanga | 134 | 04:00 | 124 | 10:00 | Purbachal | 137 | 03:00 | 127 | 10:00
| Coxsbazar | 131 | 07:00 | 124 | 06:00 | Purbasadipur | 134 | 19:00 | 115 | 07:00
| Cumilla(N) | 145 | 08:00 | 133 | 12:00 | Rahim | 136 | 00:00 | 128 | 12:00
| Cumilla(S) | 140 | 08:00 | 127 | 11:00 | Rajbari | 136 | 04:00 | 129 | 10:00
| Daudkandi | 137 | 20:00 | 130 | 12:00 | Rajendrapur | 138 | 20:00 | 128 | 16:00
| Dhaka | 137 | 22:00 | 129 | 12:00 | Rajshahi | 133 | 18:00 | 127 | 07:00
| Dhamrai | 137 | 21:00 | 128 | 16:00 | Rajshahi-230 | 133 | 20:00 | 123 | 07:00
| Dhanmondi | 136.5 | 20:00 | 128.5 | 12:00 | Ramganj | 138 | 00:00 | 130 | 16:00
| Dohazari | 138 | 21:00 | 129 | 22:00 | Rampur | 140 | 21:00 | 133 | 03:00
| Faridpur | 136 | 04:00 | 130 | 10:00 | Rampura | 136 | 04:00 | 128 | 12:00
| Fatullah | 138 | 10:00 | 127 | 12:00 | Rangamati | 141 | 22:00 | 134 | 03:00
| Fenchuganj | 136 | 00:00 | 134 | 09:00 | Rangpur | 132 | 09:00 | 118 | 06:00
| Feni | 139 | 22:00 | 133 | 10:00 | Ruppur | 138 | 03:00 | 130 | 08:00
| Ghorashal | 140 | 00:00 | 136 | 12:00 | Saidpur | 134 | 19:00 | 123 | 11:00
| Goalpara | 140 | 22:00 | 128 | 10:00 | Satkhira | 138 | 01:00 | 125 | 11:00
| Gollamari | 139 | 20:00 | 129 | 16:00 | Satmasjid | 136 | 01:00 | 130 | 12:00
| Gopalganj | 139 | 20:00 | 128 | 16:00 | Savar | 141 | 20:00 | 130 | 12:00
| Gopalganj-400 | 141 | 04:00 | -19 | 05:00 | Shahjadpur | 141 | 00:00 | 136 | 07:00
| Gopalganj_I | N/A | N/A | N/A | N/A | Shahjibazar | 135 | 00:00 | 131 | 12:00
| Gulshan | 136 | 22:00 | 128 | 12:00 | Shahmirpur | 138 | 17:00 | 131 | 09:00
| Halishahar | 140 | 19:30 | 132 | 09:00 | Shariatpur | 137 | 20:00 | 130 | 16:00
| Haripur | 136 | 08:00 | 128 | 12:00 | Sherpur | 134 | 20:00 | 115 | 00:00
| HaripurSBU | 137 | 14:00 | 129 | 10:00 | Shikalbaha | 141 | 17:00 | 133 | 04:00
| Hasnabad | 136 | 21:00 | 127 | 12:00 | Shikalbaha-230 | 140 | 18:30 | 133 | 03:00
| Hathazari | 142 | 20:00 | 135 | 09:00 | Shitalakhya | 136 | 20:00 | 127 | 10:00
| Ishurdi | 139 | 04:00 | 130 | 07:00 | Sholosohor | 140 | 20:00 | 133 | 04:00
| Jaldhaka | 132 | 19:00 | 116 | 07:00 | Shyampur | 136 | 04:00 | 129 | 12:00
| Jamalpur | 136 | 20:00 | 114 | 06:00 | Shyampur-230 | 136 | 20:00 | 127 | 10:00
| Jashore | 136 | 03:00 | 123 | 11:00 | Siddhirganj | 136 | 08:00 | 128 | 12:00
| Jhenaidah | 137 | 22:00 | 128 | 10:00 | Sirajganj | 136 | 20:00 | 127 | 07:00
| Jhenaidah-230 | 140 | 04:00 | 128 | 11:00 | Sonargaon | 136 | 21:00 | 127 | 12:00
| Joydebpur | 142 | 20:00 | 135 | 12:00 | Sreemongol | 134 | 03:00 | 132 | 08:00
| Joypurhat | 132 | 19:00 | 117 | 07:00 | Srinagar | 135 | 01:00 | 124 | 12:00
| Juldah | 140 | 18:00 | 135 | 07:00 | SSM | 145 | 21:00 | 137 | 10:00
| Kabirpur | 139 | 19:30 | 124 | 16:00 | Sunamganj | 132 | 04:00 | 129 | 11:00
| Kachua | 140 | 20:00 | 132 | 09:00 | Sylhet | 133 | 00:00 | 131 | 10:00
| Kaliakoir | 140 | 19:30 | 132 | 16:00 | Tangail | 136 | 19:30 | 126 | 16:00
| Kallyanpur | 140 | 20:00 | 132 | 12:00 | Thakurgaon | 138 | 19:00 | 110 | 06:56
| Kalurghat | 141 | 17:00 | 133 | 01:00 | TK | 141 | 18:00 | 134 | 10:00
| Kamrangirchar | 134 | 03:00 | 124 | 12:00 | Tongi | 136 | 21:00 | 129 | 11:00
| Kaptai | 140 | 07:00 | 134 | 13:00 | Ullon | 136 | 05:00 | 128 | 12:00
| Kazla | 135 | 22:00 | 126 | 13:00 | Uttara | 135 | 02:00 | 126 | 10:00
| Keranigonj | 135 | 01:00 | 125 | 12:00 | UttaraNew | 136 | 03:00 | 127 | 12:00
| Khagrachori | 140 | 08:00 | 132 | 10:00 | Zigatola | 135 | 04:00 | 123 | 13:00
| Khulna | 140 | 03:00 | 127 | 11:00
| Khulna(S) | 144 | 04:00 | 127 | 11:00
| Khulshi | 139 | 22:00 | 131 | 10:00
| Kishoreganj | 132 | 19:00 | 124 | 12:00
| Kodda | 142 | 20:00 | 128 | 16:00
| KSRM | 142 | 20:00 | 134 | 11:00
| Kulaura | 136 | 00:00 | 135 | 07:00
| Kurigram | 131 | 19:00 | 116 | 06:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2023-02-15
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 1000 | 4868 | 3726 | 8594 |  |  |  | QF-LDC-11
0:30 | 845 | 4826.5 | 3515.5 | 8342 | Date: | 2023-02-15
1:00 | 690 | 4785 | 3305 | 8090
1:30 | 685 | 4623.5 | 3251 | 7874.5
2:00 | 680 | 4462 | 3197 | 7659
2:30 | 635 | 4428.5 | 3125 | 7553.5 | [5 empty] | Gen. at Eve. Peak | 10328 | 10328 MW (19:00 )
3:00 | 590 | 4395 | 3053 | 7448 | [6 empty] | 19:00
3:30 | 595 | 4300.5 | 3008.5 | 7309 | [5 empty] | Gen. at Day Peak | 9168 | 9168 MW (12:00 )
4:00 | 600 | 4206 | 2964 | 7170 | [6 empty] | 12:00
4:30 | 563 | 4178.5 | 2955 | 7133.5 | [5 empty] | Highest Generation | 10328
5:00 | 526 | 4151 | 2946 | 7097 | [6 empty] | 19:00
5:30 | 508 | 4270 | 2988 | 7258
6:00 | 490 | 4389 | 3030 | 7419
6:30 | 538 | 4501 | 3237.5 | 7738.5
7:00 | 586 | 4613 | 3445 | 8058
7:30 | 798 | 4611.5 | 3460 | 8071.5
8:00 | 1010 | 4610 | 3475 | 8085
8:30 | 1060 | 4761 | 3524 | 8285
9:00 | 1110 | 4912 | 3573 | 8485
9:30 | 1077 | 4971 | 3653 | 8624
10:00 | 1044 | 5030 | 3733 | 8763
10:30 | 1032 | 5115 | 3755.5 | 8870.5
11:00 | 1020 | 5200 | 3778 | 8978
11:30 | 1090 | 5246.5 | 3826.5 | 9073
12:00 | 1160 | 5293 | 3875 | 9168
12:30 | 1095 | 5283 | 3894 | 9177
13:00 | 1030 | 5273 | 3913 | 9186
13:30 | 1025 | 5267.5 | 3906.5 | 9174
14:00 | 1020 | 5262 | 3900 | 9162
14:30 | 1045 | 5243 | 3915 | 9158
15:00 | 1070 | 5224 | 3930 | 9154
15:30 | 1075 | 5238 | 3863 | 9101
16:00 | 1080 | 5252 | 3796 | 9048
16:30 | 1020 | 5265 | 3749.5 | 9014.5
17:00 | 960 | 5278 | 3703 | 8981
17:30 | 885 | 5578 | 3852.5 | 9430.5
18:00 | 810 | 5878 | 4002 | 9880
18:30 | 730 | 6030.5 | 4073.5 | 10104
19:00 | 650 | 6183 | 4145 | 10328
19:30 | 590 | 6119 | 4107 | 10226
20:00 | 320 | 6354 | 3916 | 10270 |  |  |  | Executive Engineer
20:30 | 285 | 6323 | 3935 | 10258 |  |  |  | Network Operation Division
21:00 | 250 | 6292 | 3954 | 10246
21:30 | 450 | 6019 | 3982 | 10001
22:00 | 650 | 5746 | 4010 | 9756 |  |  |  |  | Page 6 of 7
22:30 | 720 | 5549.5 | 3850 | 9399.5
23:00 | 790 | 5353 | 3690 | 9043
23:30 | 895 | 5110.5 | 3708 | 8818.5
24:00 | 1000 | 4868 | 3726 | 8594
10328 MW (19:00 )
9168 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2023-02-15 |  | Energy |  | 213598561
[13 empty] | 2023-02-15 |  |  |  |  | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 2855 | 896 | 1620 | 0 | 1267 | 1656 | 30 | 0 | 170 | 100 | 0 | 0
0:30 | 3011 | 835 | 1632 | 0 | 1067.5 | 1599.5 | 15 | 0 | 85 | 97 | 0 | 0 | Date: | 2023-02-15
1:00 | 3167 | 774 | 1644 | 0 | 868 | 1543 | 0 | 0 | 0 | 94 | 0 | 0
1:30 | 3161 | 763.5 | 1611 | 0 | 703.5 | 1542.5 | 0 | 0 | 0 | 93 | 0 | 0 | [7 empty] | Total Energy | 213.5986 | Total Energy Gen 213.599 MKWHr Energy Not Served 6.401 MKWHr Energy Requirement 219.999 MKWHr
2:00 | 3155 | 753 | 1578 | 0 | 539 | 1542 | 0 | 0 | 0 | 92 | 0 | 0 | [7 empty] | Energy not Served | 6.4006
2:30 | 3157.5 | 767.5 | 1589.5 | 0 | 457 | 1491 | 0 | 0 | 0 | 91 | 0 | 0 | [7 empty] | Energy Requirement | 219.9992
3:00 | 3160 | 782 | 1601 | 0 | 375 | 1440 | 0 | 0 | 0 | 90 | 0 | 0
3:30 | 3075 | 787.5 | 1606 | 0 | 374 | 1380.5 | 0 | 0 | 0 | 86 | 0 | 0 | [5 empty] | Shortage
4:00 | 2990 | 793 | 1611 | 0 | 373 | 1321 | 0 | 0 | 0 | 82 | 0 | 0
4:30 | 3001 | 801 | 1594.5 | 0 | 354 | 1301 | 0 | 0 | 0 | 82 | 0 | 0
5:00 | 3012 | 809 | 1578 | 0 | 335 | 1281 | 0 | 0 | 0 | 82 | 0 | 0
5:30 | 3011 | 769 | 1619 | 0 | 459.5 | 1315.5 | 0 | 0 | 0 | 84 | 0 | 0
6:00 | 3010 | 729 | 1660 | 0 | 584 | 1350 | 0 | 0 | 0 | 86 | 0 | 0
6:30 | 2974 | 797 | 1677 | 0 | 747 | 1440.5 | 0 | 0 | 8 | 88 | 7 | 134.55 |  |  |  | Coal
7:00 | 2938 | 865 | 1694 | 0 | 910 | 1531 | 0 | 0 | 16 | 90 | 14 | 269.0999
7:30 | 2914 | 822.5 | 1678.5 | 0 | 936.5 | 1556.5 | 0 | 0 | 20 | 93 | 50.5 | 464.013 |  |  | Oil |  |  |  | ,
8:00 | 2890 | 780 | 1663 | 0 | 963 | 1582 | 0 | 0 | 24 | 96 | 87 | 658.9261
8:30 | 2936 | 782 | 1665 | 0 | 1017.5 | 1578 | 0 | 0 | 73 | 98 | 135.5 | 612.8474
9:00 | 2982 | 784 | 1667 | 0 | 1072 | 1574 | 0 | 0 | 122 | 100 | 184 | 566.7686
9:30 | 2977.5 | 818.5 | 1653 | 0 | 1128 | 1563 | 0 | 0 | 157 | 102 | 225 | 530.8272
10:00 | 2973 | 853 | 1639 | 0 | 1184 | 1552 | 0 | 0 | 192 | 104 | 266 | 494.8858
10:30 | 2951 | 853 | 1619.5 | 0 | 1270 | 1554 | 30 | 0 | 191 | 106 | 296 | 464.9346
11:00 | 2929 | 853 | 1600 | 0 | 1356 | 1556 | 60 | 0 | 190 | 108 | 326 | 434.9834
11:30 | 2944 | 877 | 1605.5 | 0 | 1367 | 1556 | 60 | 0 | 212.5 | 110 | 341 | 439.5913
12:00 | 2959 | 901 | 1611 | 0 | 1378 | 1556 | 60 | 0 | 235 | 112 | 356 | 444.1992
12:30 | 2935 | 902.5 | 1605 | 0 | 1388 | 1570 | 60 | 0 | 250 | 114 | 352.5 | 522.0722
13:00 | 2911 | 904 | 1599 | 0 | 1398 | 1584 | 60 | 0 | 265 | 116 | 349 | 599.9453
13:30 | 2911 | 904 | 1599 | 0 | 1398 | 1584 | 60 | 0 | 265 | 116 | 349 | 599.9453
14:00 | 2911 | 904 | 1599 | 0 | 1398 | 1584 | 60 | 0 | 265 | 116 | 349 | 599.9453
14:30 | 2929 | 902.5 | 1621 | 0 | 1363 | 1565.5 | 60 | 0 | 322.5 | 116 | 290.5 | 550.1803
15:00 | 2947 | 901 | 1643 | 0 | 1328 | 1547 | 60 | 0 | 380 | 116 | 232 | 500.4152
15:30 | 2970 | 901 | 1661 | 0 | 1328 | 1528 | 45 | 0 | 375 | 113 | 180 | 410.1009
16:00 | 2993 | 901 | 1679 | 0 | 1328 | 1509 | 30 | 0 | 370 | 110 | 128 | 319.7865
16:30 | 2974 | 901 | 1646.5 | 0 | 1416.5 | 1477.5 | 30 | 0 | 376.5 | 111 | 81.5 | 259.8841
17:00 | 2955 | 901 | 1614 | 0 | 1505 | 1446 | 30 | 0 | 383 | 112 | 35 | 199.9818
17:30 | 2981 | 900.5 | 1676 | 0 | 1838 | 1421 | 30 | 0 | 450.5 | 116 | 17.5 | 204.9909
18:00 | 3007 | 900 | 1738 | 0 | 2171 | 1396 | 30 | 0 | 518 | 120 | 0 | 210
18:30 | 2962.5 | 828.5 | 1751 | 0 | 2372 | 1478 | 45 | 0 | 548 | 119 | 0 | 340.0016
19:00 | 2918 | 757 | 1764 | 0 | 2573 | 1560 | 60 | 0 | 578 | 118 | 0 | 470.0032
19:30 | 2858 | 754 | 1621 | 0 | 2578 | 1661 | 60 | 0 | 578 | 116 | 0 | 420.2382
20:00 | 3050 | 542 | 1640 | 0 | 2612 | 1671 | 60 | 0 | 579 | 116 | 0 | 370.4732
20:30 | 3047 | 565 | 1654.5 | 0 | 2556.5 | 1697 | 60 | 0 | 563 | 115 | 0 | 255.2763
21:00 | 3044 | 588 | 1669 | 0 | 2501 | 1723 | 60 | 0 | 547 | 114 | 0 | 140.0794
21:30 | 3018.5 | 742 | 1605.5 | 0 | 2387.5 | 1716.5 | 45 | 0 | 374 | 112 | 0 | 135.0107
22:00 | 2993 | 896 | 1542 | 0 | 2274 | 1710 | 30 | 0 | 201 | 110 | 0 | 129.9421
22:30 | 3017 | 896 | 1594 | 0 | 1904.5 | 1665.5 | 30 | 0 | 184.5 | 108 | 0 | 145.1481
23:00 | 3041 | 896 | 1646 | 0 | 1535 | 1621 | 30 | 0 | 168 | 106 | 0 | 160.354
23:30 | 2948 | 896 | 1633 | 0 | 1401 | 1638.5 | 30 | 0 | 169 | 103 | 0 | 145.177 | Max Temp. in Dhaka |  | 27.2° C
24:00 | 2855 | 896 | 1620 | 0 | 1267 | 1656 | 30 | 0 | 170 | 100 | 0 | 130
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 213.599 MKWHr Energy Not Served 6.401 MKWHr Energy Requirement 219.999 MKWHr
Shortage
Note on W13: Author:

## Generation
g | 2023-02-15
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3
2 | Karnaphuli Hydro PP Unit-4 & 5 | [9 empty] | 0 | 60 | 60 | 60 | 60 | 60 | 30 | 30 | 30 |  | 60 | 60 | 60 | 60 | 30 | 30 | 30 | 628000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP |  |  |  |  | 0 | 1 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 18 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 289342
| Teknaf 20MW PP (Solartech) | [6 empty] | 2 | 5 | 13 | 17 | 19 | 20 | 20 | 18 | 13 | 8 | 2 | 0 | [8 empty] | 137700
6 | Sikalbaha 225MW CCPP (Gas) | 142 | 141 | 141 | 142 | 142 | 132 | 132 | 147 | 151 | 153 | 151 | 151 | 151 | 150 | 151 | 151 | 151 | 151 |  | 152 | 121 | 151 | 152 | 152 | 152 | 152 | 3371840
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [14 empty] | 68 | 68 | 68 | 85 |  | 85 | 85 | 85 | 85 | 17 | 17 | 17 | 606065
12 | Hathazari 100 MW peaking PP | [8 empty] | 40 | 42 | 34 | 34 | 38 | 42 | 42 | 42 | 49 | 74 |  | 74 | 74 | 64 | 64 | 64 | 65 | 65 | 787056
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 23 | 34 | 34 | 34 | 34 | 53 | 85 |  | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 1062181
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP | [8 empty] | 18 | 38 | 38 | 37 | 36 | 36 | 36 | 37 | 29 | 31 |  | 31 | 35 | 31 | 38 | 30 | 36 | 38 | 527344
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 32 | 0 |  |  |  |  | 32 | 32 | 32 | 49 | 65 | 65 | 65 | 65 | 65 | 65 | 67 | 82 |  | 97 | 97 | 97 | 110 | 145 | 135 | 77 | 1380000
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 217454
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4 | 122 | 120 | 121 | 121 | 120 | 121 | 120 | 120 | 120 | 118 | 120 | 120 | 120 | 120 | 122 | 120 | 123 | 121 |  | 120 | 121 | 120 | 119 | 118 | 120 | 120 | 2878500
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4378500
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 274824
33 | Ashuganj 225 MW CCPP | 225 | 229 | 229 | 229 | 229 | 221 | 214 | 227 | 203 | 206 | 203 | 201 | 196 | 212 | 221 | 212 | 219 | 220 |  | 223 | 224 | 223 | 217 | 220 | 209 | 226 | 5247000
34 | Ashuganj 450 MW CCPP(South)
| Ashuganj 450 MW CCPP(North) | 290 | 290 | 290 | 290 | 290 | 315 | 350 | 280 | 360 | 340 | 320 | 330 | 305 | 295 | 295 | 350 | 295 | 340 |  | 285 | 280 | 280 | 280 | 280 | 320 | 280 | 7694000
| Ashuganj 420 MW CCPP(East) | 302 | 312 | 312 | 312 | 312 | 301 | 290 | 315 | 297 | 295 | 273 | 287 | 273 | 282 | 288 | 288 | 288 | 295 |  | 306 | 313 | 320 | 290 | 312 | 280 | 310 | 7126800
35 | Ashuganj 55 MW PP (Precision) | [25 empty] | 0 | 0
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP
40 | Meghnaghat 450 MW CCPP(MPL) | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 |  | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 5211500
41 | Haripur 360MW CCPP(HPL) | 272 | 267 | 281 | 277 | 276 | 286 | 279 | 294 | 293 | 280 | 276 | 269 | 267 | 266 | 264 | 265 | 259 | 266 |  | 269 | 247 | 258 | 241 | 240 | 252 | 251 | 6476000
42 | RPCL 210MW CCPP | 104 | 105 | 105 | 105 | 108 | 105 | 50 | 44 | 34 | 35 | 35 | 35 | 32 | 30 | 33 | 35 | 35 | 35 |  | 51 | 60 | 102 | 104 | 97 | 97 | 94 | 1543680
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 2 | 11 | 22 | 34 | 41 | 45 | 45 | 39 | 31 | 17 | 4 | 0 | [8 empty] | 291750
44 | Fenchugonj CCPP Phase-1 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1013000
45 | Fenchugonj CCPP Phase-2 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 972720
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 64 | 64 | 64 | 64 | 40 | 64 | 64 | 64 | 63 | 61 | 61 | 60 | 61 | 61 | 61 | 60 | 62 | 62 |  | 40 | 40 | 63 | 63 | 40 | 62 | 63 | 1441152
48 | Shahjibazar 86MW PP (Shahjibazar) | 40 | 10 | 10 | 10 | 10 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 86 |  | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 1209600
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 216 | 216 | 216 | 216 | 216 | 216 | 217 | 217 | 219 | 218 | 216 | 213 | 206 | 204 | 204 | 204 | 204 | 204 |  | 214 | 206 | 215 | 215 | 215 | 215 | 214 | 5285270
51 | Sylhet 20 MW GTPP | 19 | 19 | 19 | 20 | 20 | 20 | 19 | 19 | 19 | 19 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 19 | 19 | 19 | 19 | 19 | 19 | 449000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 7 | 7 | 7 | 7 | 7 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 190980
54 | Hobiganj 11MW PP Cofidence-E | 8 | 8 | 8 | 8 | 8 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 162624
55 | Fenchugonj 51 MW PP (Barakatullah) | 31 | 11 | 11 | 11 | 11 | 22 | 22 | 22 | 22 | 22 | 11 | 11 | 11 | 11 | 11 | 11 | 12 | 14 |  | 47 | 51 | 51 | 51 | 11 | 11 | 11 | 443400
56 | Shahjahanulla 25 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 191472
57 | Bibiana-II 341 MW CCPP (Summit) | 275 | 260 | 270 | 270 | 290 | 295 | 320 | 290 | 300 | 300 | 300 | 330 | 330 | 280 | 280 | 310 | 300 | 315 |  | 300 | 280 | 280 | 290 | 260 | 315 | 290 | 7227000
| Bibiyana South 400 MW | 400 | 375 | 380 | 360 | 360 | 340 | 335 | 340 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 396 | 400 | 400 |  | 350 | 320 | 400 | 400 | 350 | 400 | 390 | 9156100
58 | Nababganj 55 MW PP (Southern power ) |  |  |  |  | 0 | 17 | 17 | 17 | [7 empty] | 12 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 17 | 17 | 298806
59 | Tangail Palli Power Gen 22 MW | 6 | 6 | 6 | 6 | 0 |  | 5 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 138000
60 | Barabkunda 22 MW PP (Regent)
61 | Narshingdi 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 |  |  |  | 12 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 22 |  | 22 | 22 | 22 | 22 | 22 | 19 | 19 | 393984
62 | Tangail 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 16 | 16 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 437292
63 | Impoprt (Tripura) | 94 | 92 | 90 | 82 | 82 | 86 | 90 | 96 | 100 | 104 | 108 | 112 | 116 | 110 | 116 | 110 | 112 | 120 |  | 118 | 116 | 116 | 114 | 110 | 106 | 100 | 2330880
64 | Malancha, Ctg. EPZ (United) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15840
65 | Feni 22MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  |  | 10 | 19 | 21 | 21 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 443520
66 | Feni 11 MW PP (Doreen) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 181080
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 22 | 15 | 13 | 13 | 8 | 8 | 8 | 8 | 8 | 12 | 14 | 13 |  | 16 | 21 | 21 | 23 | 25 | 25 | 33 | 501000
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 18 | 21 | 21 | 21 | 9 | 14 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 468350
69 | Summit Ashulia | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 528000
70 | Summit Madhabdi | 26 | 26 | 26 | 26 | 27 | 27 | 27 | 27 | 27 | 25 | 25 | 25 | 25 | 26 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 26 | 26 | 26 | 601740
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 711200
72 | Rupganj 33 MW PP(Summit) | 24 | 26 | 26 | 26 | 28 | 30 | 30 | 28 | 28 | 26 | 21 | 26 | 26 | 26 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 26 | 26 | 26 | 28 | 635400
73 | Ghorashal 108MW PP (Regent)
| Feni Lanka Power | 17 | 0 |  |  | 0 | 17 | 17 | 17 | 17 | 34 | 34 | 34 | 34 | 34 | 34 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 450300
| Chowmuhani 113 MW | 9 | 9 | 0 |  | 0 | 2 | 9 | 9 | 9 | 9 | 9 | 9 | 13 | 11 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 198240
| Manikgonj 162MW PP(MPGL) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 144 | 144 | 144 | 122 | 57 | 21 | 17 | 731520
77 | Siddhirganj 100 PP(Dutch Bangla) | 17 | 0 |  |  | 0 | 4 | 17 | 17 | 17 | 17 | 17 | 25 | 34 | 40 | 50 | 52 | 50 | 50 |  | 50 | 50 | 50 | 50 | 20 | 17 | 17 | 583411
78 | Gazipur 52 MW PP | [6 empty] | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 41 | 41 |  | 41 | 41 | 41 | 41 | 25 | 25 | 25 | 563040
79 | Kodda 150MW PP | [6 empty] | 16 | 16 | 48 | 48 | 48 | 48 | 64 | 82 | 82 | 64 | 48 | 64 |  | 82 | 82 | 98 | 98 |  |  | 0 | 919680
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 8 | 8 | 8 | 8 | 0 | [9 empty] | 5 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 114197
| Gazipur 100 MW PP | 30 | 0 |  |  | 0 | 5 | 35 | 35 | 35 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 88 |  | 88 | 88 | 88 | 88 | 88 | 52 | 52 | 1123200
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 1 | 2 | 3 | 4 | 4 | 4 | 3 | 2 | 1 | 0 | [9 empty] | 26641
| Jodiac Power | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 451996
| Karnaphuli Power Ltd. | 57 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 61 | 54 | 54 | 54 | 54 | 67 | 74 |  | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 1481194
82 | Madanganj 102 PP(Summit) | [8 empty] | 5 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 20 | 17 |  | 17 | 17 | 17 | 17 | 5 |  | 0 | 185940
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP ( Summit) | 140 | 140 | 140 | 138 | 136 | 131 | 131 | 138 | 148 | 148 | 142 | 142 | 140 | 140 | 140 | 142 | 142 | 142 |  | 142 | 145 | 145 | 142 | 140 | 141 | 145 | 3393629
87 | Meghnaghat 100 MW(IEL) | 17 | 0 |  |  |  |  | 13 | 17 | 18 | 17 | 18 | 17 | 20 | 43 | 48 | 48 | 50 | 51 |  | 51 | 50 | 50 | 51 | 20 | 17 | 17 | 580800
| Meghnaghat 104 MW PP (OPCL) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 33 |  | 55 | 55 | 55 | 56 | 56 | 48 | 17 | 631680
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 22 | 0 |  |  | 0 | 12 | 22 | 22 | 22 | 22 | 22 | 22 | 33 | 33 | 33 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 475680
92 | Fenchuganj 44MW (Energyprima) | 30 | 30 | 30 | 30 | 10 | 16 | 20 | 20 | 20 | 20 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 30 | 43 | 43 | 45 | 10 | 10 | 10 | 501336
93 | Ashuganj 51 MW PP (Midland) | 43 | 43 | 43 | 43 | 10 | 27 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1016500
94 | Gagnagar 102 MW PP (Digital Power) | 16 | 0 |  |  | 0 | 4 | 8 | 8 | 16 | 20 | 24 | 24 | 24 | 24 | 32 | 32 | 32 | 42 |  | 42 | 42 | 42 | 42 | 16 | 16 | 16 | 491760
95 | Patenga 50MW PP (Baraka) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 21 | 20 | 19 | 13 | 12 | 13 | 18 | 18 | 18 | 18 |  | 19 | 18 | 19 | 18 | 19 | 19 | 21 | 447360
96 | Chattogram 108 MW PP (ECPV) | [25 empty] | 0 | 0
97 | katpotti 52 MW
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 15 | 0 |  |  | 0 | 1 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 20 | 25 | 25 | 15 | 15 | 15 | 15 | 318923
100 | Manikganj 55 MW PP (Northern) | [9 empty] | 8 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 |  | 35 | 55 | 55 | 35 | 17 | 17 | 0 | 307542
101 | Kushiara 163 MW CCPP (KP) | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 113 | 112 | 112 | 112 | 112 | 112 |  | 112 | 80 | 80 | 112 | 80 | 112 | 112 | 2741809
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 1 | 1 | 0 | [9 empty] | 12900
103 | Kamalaghat 54 MW PP(Banco Energy) | [15 empty] | 17 | 17 | 17 |  | 35 | 35 | 35 | 17 | 17 |  | 0 | 160200
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 75 | 74 | 74 | 74 | 9 | 18 | 18 | 44 |  | 103 | 103 | 103 | 102 | 107 | 48 | 48 | 945600
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 17 | 0 |  |  | 0 | 1 | 15 | 17 | 17 | 17 | 31 | 35 | 35 | 35 | 33 | 35 | 34 | 35 |  | 59 | 70 | 70 | 75 | 105 | 77 | 17 | 783792
115 | Juldah 100 MW PP Unit-3 (Acorn) | 25 | 0 |  |  | 0 | 12 | 25 | 25 | 25 | 38 | 38 | 38 | 38 | 38 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 573120
116 | Chandpur 200MW (Desh energy) | 34 | 34 | 0 |  | 0 | 13 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 30 | 36 |  | 35 | 35 | 34 | 34 | 34 | 34 | 34 | 716640
117 | Ashuganj 150MW PP (Midland) | 75 | 73 | 75 | 75 | 75 | 75 | 73 | 73 | 75 | 73 | 75 | 73 | 75 | 68 | 68 | 78 | 97 | 120 |  | 133 | 133 | 150 | 150 | 150 | 99 | 68 | 2156145
118 | Bibiyana-III 400 MW CCPP | 404 | 403 | 402 | 250 | 285 | 285 | 285 | 285 | 285 | 283 | 285 | 285 | 290 | 298 | 290 | 292 | 292 | 292 |  | 292 | 292 | 292 | 292 | 292 | 292 | 82 | 7295000
| Jamalpur 115 MW PP (United) | 49 | 48 | 48 | 49 | 24 | 34 | 47 | 47 | 47 | 49 | 78 | 88 | 79 | 79 | 48 | 48 | 48 | 48 |  | 49 | 49 | 49 | 49 | 49 | 10 | 9 | 1196400
| Anwara 300 MW PP (United) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 274 |  | 272 | 278 | 284 | 285 | 267 | 16 | 16 | 2416255
| Juldah unit-2 (Acorn) | 25 | 0 |  |  | 0 | 9 | 25 | 25 | 25 | 25 | 38 | 38 | 38 | 38 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 556800
| Anlima Energy Ltd. | 107 | 107 | 55 | 51 | 52 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 106 | 89 | 89 | 93 | 107 |  | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 2376109
| Bhairob 54.5 MW | [7 empty] | 12 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 313200
| Spectra Solar Plant Ltd. | [6 empty] | 1 | 6 | 14 | 21 | 27 | 28 | 28 | 24 | 18 | 11 | 3 | 0 | [8 empty] | 183614
| Chandpur 115(Doreen) | 18 | 18 | 17 | 18 | 18 | 18 | 18 | 18 | 17 | 18 | 36 | 40 | 20 | 18 | 20 | 18 | 24 | 54 |  | 74 | 72 | 82 | 72 | 72 | 72 | 36 | 827520
| Kanchan Purbachal Power Generation Ltd. | [16 empty] | 12 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 0 | 123480
| Mirsharai 150 MW (Oil) | [25 empty] | 0 | 0
Mirsharai 150 MW (Gas)
120 | Eastern Zone Total | 4785 | 4462 | 4395 | 4206 | 4151 | 4389 | 4613 | 4610 | 4912 | 5030 | 5200 | 5293 | 5273 | 5262 | 5224 | 5252 | 5278 | 5878 |  | 6183 | 6119 | 6354 | 6292 | 5746 | 5353 | 4868 | 123930099
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | [17 empty] | 16 |  | 33 | 0 |  | 0 | 16 | 16 | 16 | 83520
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [15 empty] | 6 | 36 | 40 |  | 50 | 46 | 46 | 44 |  |  |  | 199200
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) |  |  |  |  | 0 | 17 | 17 | [5 empty] | 17 | 20 | 37 | 37 | 43 | 56 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 571200
130 | Mongla Orion 100 MW Solar PP | [6 empty] | 3 | 23 | 47 | 67 | 80 | 84 | 81 | 75 | 56 | 33 | 9 | 0 | [8 empty] | 563040
131 | Rampal 1320 MW (BIFPCL) | [25 empty] | 118 | 90900
132 | United Payra Power Ltd. | 56 | 0 | [5 empty] | 7 | 17 | 17 | 17 | 35 | 35 | 35 | 35 | 17 | 17 | 85 |  | 150 | 150 | 150 | 100 | 37 |  | 0 | 876000
133 | Bhola Nutan Biddut BD LTD (GAS) | 108 | 109 | 109 | 109 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 120 | 220 | 220 | 170 | 220 |  | 200 | 107 | 107 | 107 | 109 | 110 | 111 | 3149536
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [19 empty] | 16 | 16 | 16 | 16 | 16 |  | 0 | 58848
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW | 181 | 180 | 180 | 181 | 181 | 180 | 181 | 180 | 152 | 150 | 154 | 154 | 152 | 153 | 155 | 157 | 154 | 156 |  | 188 | 189 | 189 | 229 | 228 | 229 | 228 | 4254500
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 193 | 193 | 193 | 192 | 192 | 193 | 190 | 177 | 193 | 188 | 188 | 188 | 187 | 183 | 187 | 183 | 183 | 186 |  | 192 | 192 | 192 | 192 | 192 | 193 | 192 | 4573151
140 | Bhola 33 MW PP (Venture) | 18 | 17 | 16 | 16 | 15 | 17 | 16 | 16 | 16 | 15 | 17 | 16 | 17 | 16 | 14 | 13 | 13 | 18 |  | 20 | 21 | 21 | 22 | 22 | 20 | 19 | 406000
141 | Noapara 100 MW PP (Bangla Trac) | [25 empty] | 0 | 0
142 | Noapara 40 MW PP (Khanjahan Ali) | [15 empty] | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 |  | 0 | 107250
143 | Gopalganj 100 MW Peaking PP | [17 empty] | 0 |  | 30 | 30 | 30 | 0 |  |  |  | 57216
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | [7 empty] | 15 | 15 | [8 empty] | 49 |  | 50 | 50 | 50 | 50 | 15 | 15 | 0 | 285408
146 | Bheramara HVDC | 774 | 753 | 782 | 793 | 809 | 729 | 865 | 780 | 784 | 853 | 853 | 901 | 904 | 903 | 901 | 901 | 901 | 900 |  | 757 | 754 | 542 | 588 | 896 | 896 | 896 | 19782545
147 | Bheramara 410 MW CCPP
148 | Payra 1320 MW | 1162 | 1162 | 1060 | 940 | 900 | 920 | 1100 | 1152 | 1172 | 1152 | 1152 | 1152 | 1182 | 1172 | 1142 | 1102 | 1042 | 990 |  | 1122 | 1222 | 1232 | 1244 | 1232 | 1172 | 1110 | 28796500
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 200 | 200 | 200 | 200 | 200 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 |  | 250 | 250 | 250 | 250 | 250 | 220 | 200 | 5735700
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [12 empty] | 24 | 32 | 32 | 34 | 34 | 34 |  | 34 | 34 | 34 | 34 | 28 |  |  | 324198
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 1 | 2 | 3 | 4 | 4 | 5 | 0 | 3 | 1 | 0 | [9 empty] | 22440
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 168 | 168 | 168 | 172 | 175 | 175 | 177 | 181 | 183 | 186 | 184 | 182 | 178 | 176 | 176 | 176 | 175 | 171 |  | 160 | 150 | 153 | 177 | 179 | 158 | 182 | 4417518
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 311 | 315 | 315 | 331 | 336 | 342 | 339 | 316 | 305 | 293 | 283 | 272 | 262 | 263 | 250 | 254 | 254 | 253 |  | 256 | 258 | 266 | 267 | 278 | 283 | 279 | 6972763
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [9 empty] | 4 | 4 | 4 | 4 | 14 | 17 | 17 | 17 | 23 |  | 26 | 25 | 25 | 18 |  |  |  | 167176
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 19 | 19 | 22 | 22 | 22 | 22 | 468000
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 238716
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | [6 empty] | 25 | 25 | 25 | 25 | 25 | [15 empty] | 133023
167 | Katakhali 50 MW Peaking PP | [7 empty] | 8 | 16 | 16 | 16 | 39 | 24 | 24 | 24 | 24 | 24 | 40 |  | 40 | 40 | 40 | 40 |  |  |  | 331648
168 | Santahar 50 MW Peaking PP | [11 empty] | 23 | 25 | 28 | 29 | 28 | 28 | 29 |  | 29 | 30 | 29 | 29 | 12 |  |  | 278479
169 | Natore 52 MW PP (Rajlanka) | [6 empty] | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 525043
170 | Chapainawabganj 100 MW Peaking PP | [9 empty] | 44 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 98 |  | 97 | 97 | 97 | 97 | 50 | 50 | 50 | 925704
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 35 | 35 | 0 |  |  |  | 8 | 35 | 40 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1032960
172 | Confidence Power Bogura Unit-1 113 MW | 35 | 35 | 0 |  | 0 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 70 | 95 |  | 95 | 95 | 95 | 95 | 95 | 35 | 35 | 1051392
173 | Rangpur 20 MW GTPP | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | 34 | 0 |  |  | 0 | 34 | 40 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 63 | 77 | 77 |  | 77 | 77 | 78 | 78 | 78 | 34 | 34 | 1044096
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 5 | 4 | 2 | 1 | 0 | [8 empty] | 38264
178 | Energypac Power Venture Thakurgaon Ltd. | [8 empty] | 5 | 35 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 113 |  | 115 | 115 | 115 | 115 | 115 | 113 | 113 | 1086528
| Intraco Solar 30 MW | [6 empty] | 1 | 5 | 15 | 22 | 28 | 31 | 30 | 26 | 20 | 10 | 3 | 0 | [8 empty] | 190240
Adani Power Jharkhanda Ltd
178 | Teesta Solar Limited | [6 empty] | 5 | 33 | 66 | 94 | 117 | 133 | 128 | 111 | 84 | 44 | 13 | 0 | [8 empty] | 829760