## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2023-02-28 | Tuesday
|  | Date (day): | 2023-02-28 |  | Tuesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 10817.6 | MW |  |  | (b) At Evening Peak Hour : |  | 12821 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2023-02-27 | 2023-02-28 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 130 | 130 | 130 | 130 | 50 |  | Gas shortage
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 | 365 |  | Under maint.
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 413 | 391 | 400 | 400 | 12 |  | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 343 | 342 | 340 | 320 | 40 |  | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 40 | 58 | 31 | 60 | 40 |  | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 277 | 284 | 270 | 270 | 65 |  | FGMO
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 70 | 80 | 85 | 85 |  | 17 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 16 | 22 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 99 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 40 | 58 | 33 | 60 | 40 |  | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 40 | 58 | 40 | 58 | 44 |  | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 35 | 0 | 35 | 19 |  | Fuel shortage
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 48 | 115 | 48 | 98 | 51 |  | Fuel shortage
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 35 | 17 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 35 | 17 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 46 | 46 | 50 | 50 |  | 30 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 28 | 28 | 30 | 30
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 25 | 50 | 25 | 50
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 147 | 245 | 145 | 245 | 55 |  | Fuel shortage
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 0 | 300 |  | Fuel shortage
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Fuel shortage
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Fuel shortage
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 67 | 91 | 100 | 100 | 49 |  | Fuel shortage
36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 88 | 52 | 88 |  | 17 | Engine problem
37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 18 | 17 | 17 | 17 | 87 |  | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 17 | 91 | 17 | 162
39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 27 | 0 | 30 | 0
40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 16 | 17 | 17 | 17 | 38 |  | Fuel shortage
| Dhaka area Total |  |  |  |  | 6263 | 5847 | 2694 | 3034 | 2634 | 3125 | 2159 | 564
41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 17 | 25 | 25 | 25
43 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 20 | 0 | 20 | 0
44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 19 | 19 | 21 | 21 | 29 |  | Fuel shortage
45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 30 | 30 | 30 | 30 | 200 |  | Low Water Level
46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 219 | 227 | 220 | 220
47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 17 | 51 | 17 | 51 | 54 |  | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 56 | 69 | 50 | 70 |  | 28 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 51 | 85 | 17 | 85 |  | 17 | Engine problem
51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 44 | 61 | 44 | 85 |  | 15 | Engine problem
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 50 | 100 | 50 | 100
53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 15 | 12 | 15 | 15 | 7 |  | Gas shortage
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 0 | 0 | 0 | 0
54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 105 | 238 | 100 | 245 | 55 |  | Fuel shortage
57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 17 | 17 | 17 | 17 | 37 |  | Fuel shortage
58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 54 | 54 | 54 | 54 | 56 |  | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 50 | 90 | 50 | 100
60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 107 | 107 | 107 | 107 |  | 9 | Engine problem
| Mirsharai 150 MW |  | Gas/HSD | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0
| Chattogram area Total |  |  |  |  | 2442 | 2382 | 875 | 1185 | 842 | 1225 | 906 | 219
61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 203 | 182 | 190 | 190 |  |  | FGMO
63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 310 | 280 | 300 | 300 |  |  | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Macine problem
65 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 340 | 401 | 380 | 400 |  |  | FGMO
66 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 43 | 20 | 30 | 30
67 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 55 | 5 | 5 | 5 | 5 | 50 |  | Gas shortage
68 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
69 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 51 | 51 | 51
70 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 47 | 150 | 46 | 150
71 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 36 | 34 | 28 | 33 |  | 19 | Engine problem
72 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under Maint.
73 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 34 | 100 | 34 | 100 | 100 |  | Fuel shortage
74 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 15 | 17 | 17 |  | 5 | Engine problem
75 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 9 | 9 | 9 | 9 |  | 2 | Engine problem
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 108 | 110 | 135 | 153
76 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 28 | 33 | 33 | 33
77 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 8 | 0 | 8 | 44 |  | Fuel shortage
78 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 21 | 21 | 20 | 20 |  | 5 | Engine problem
79 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel shortage
80 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 34 | 80 | 17 | 114
81 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 87 | 9 | 113
82 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 0 | 17 | 17 |  | 37 | Engine problem
83 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 39 | 72 | 18 | 72 | 43 |  | Fuel shortage
| Cumilla Area Total |  |  |  |  | 3309 | 3285 | 1352 | 1666 | 1347 | 1823 | 758 | 591
84 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 32 | 49 | 32 | 80 | 122 |  | Gas shortage
85 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 19 | 19 |  |  | Gas shortage
86 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0
87 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
88 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 87 | 97 | 88 | 100 | 100 |  | Fuel shortage
89 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 19 | 56 | 12 | 50 | 65 |  | Fuel shortage
90 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 49 | 0 | 50 | 0
91 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 6 | 6 | 6 | 16 |  | Fuel shortage
| Mymensingh Area Total |  |  |  |  | 717 | 614 | 214 | 227 | 208.6 | 255 | 122 | 0
92 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 42 | 42 | 42 |  | 28 | Machine problem.
93 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 20 | 42 | 30 | 42 |  | 48 | Machine problem
94 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 112 | 112 | 0 | 0 |  | 163 | Gas shortage & ST U/M.
95 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
96 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 46 | 39 | 20 | 51
97 | Fenchuganj 44MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 42 | 40 | 40 | 50
98 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 8 | 8 |  | 3 | Engine problem
99 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 60 | 62 | 60 | 62
100 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 86 | 86 | 86 | 86
101 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
102 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 207 | 211 | 225 | 225
103 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 19 | 19
104 | Sylhet 50MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Gas shortage
105 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 6 | 8 | 8 | 8 |  | 17 | Engine problem
106 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 300 | 300 | 300 |  |  | FGMO
107 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 401 | 368 | 366 | 366 |  |  | FGMO
108 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 8 | 8 | 8 | 8
109 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 43 | 40 | 400 | 400
| Sylhet Area Total |  |  |  |  | 2472 | 2427 | 1410 | 1384 | 1612 | 1667 | 0 | 689
110 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 890 | 808 | 901 | 901
111 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 49 | 79 | 83 | 99 | 16 |  | Fuel shortage
112 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 38 | 0 | 47 |  | 7 | Engine problem
113 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
114 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 40 |  | 69 | Engine problem
115 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 200 | 180 | 370 | 400 |  |  | DCT
116 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 8 | 0 | 24 | 16 |  | Fuel shortage
117 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Fuel shortage
118 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 36 | 56 | 35 | 55 | 50 |  | Fuel shortage
119 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 50 |  |  | Line O/L
120 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 91 | 0 | 100 | 0
| Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 660*2 | 617 | 617 | 0 | 0 | 400 | 400 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3005 | 3001 | 1266 | 1169 | 1889 | 2016 | 428 | 76
121 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 0 | 16 | 94 |  | Line O/L
122 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 15 | 20 | 14 | 14 |  | 26 | Engine problem
123 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 180 | 184 | 175 | 175
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
124 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 950 | 1112 | 820 | 950 |  |  | Transformer O/L
125 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 224 | 222 | 220 | 220
126 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 116 | 17 | 100 |  |  | Line O/L
127 | Barisal 307 MW |  | Coal | BCPCL | 307*1 | 307 | 307 | 160 | 199 | 150 | 200
| Barisal Area Total |  |  |  |  | 2265 | 2265 | 1546 | 1853 | 1396 | 1675 | 94 | 26
128 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
129 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 32 | 0 | 32 |  | 20 | Engine problem
130 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 18 | 27 | 16 | 30 |  | 41 | Engine problem
131 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
132 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 42 | 50 | 42 | 42 |  | 8 | Engine problem
133 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 32 | 40 | 32 | 35 |  | 15 | Engine problem
134 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 180 | 161 | 0 | 0 | 210 |  | Gas shortage
135 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
136 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 196 | 154 | 122 | 122 | 98 |  | Gas shortage
137 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 0 | 0 | 0 | 0 |  | 414 | Under maint
138 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 25 | 28 | 26 | 36 |  | 14 | Engine problem
139 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 19 | 20 | 22 | 22
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
140 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
141 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 8 | 44 |  | Fuel shortage
142 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 58 | 86 | 40 | 95 |  | 9 | Enging problem
143 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel shortage
144 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 35 | 70 | 35 | 70 | 43 |  | Fuel shortage
145 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 35 | 75 | 35 | 75 | 38 |  | Fuel shortage
146 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 4 | 0 | 6 | 0
| Adani Power Jharkhanda Ltd |  | Coal | Import | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | On test.
| Rajshahi Area Total |  |  |  |  | 2179 | 2129 | 652 | 754 | 387 | 578 | 1024 | 521
147 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
148 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 250 | 250 | 250 | 250 | 24 |  | Machine problem
149 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
150 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
151 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 35 | 92 | 49 | 92 | 21 |  | Fuel shortage
152 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 6 | 0 | 8 | 0
153 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 35 | 94 | 35 | 115
154 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 32 | 0 | 30 | 0
| Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 0 | 0 | 126 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 830 | 750 | 484 | 436 | 502 | 457 | 170 | 85
| Total |  |  |  |  | 23482 | 22700 | 10493 | 11708 | 10817.6 | 12821 | 5661 | 2771
A. |  | 2023-02-27 | (Yesterday) |  |  |  |  | Monday
1 | Highest Generation : |  |  | 11708 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
2 | Minimum Generation : |  |  | 7905 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 11795 | MW
3 | Day peak Generation : |  |  | 10493 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 11285 | MW
4 | Evening peak Generation : |  |  | 11708 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 80 | MW
5 | Total Energy Generation : |  | 239.7473 | MKWHr | By Solar | 2.3968 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Gas : | 132.3868 | MKWHr |  | By Oil: | 43.4979 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 37.417 | MKWHr |  | By Hydro: | 0.72348 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 5661 | MW | Dhaka | 4213.2 | 4213.2 |  | 0 |  | 18:00 |  | 167
|  |  | For Plants S/D or M/C prob = |  |  | 2771 | MW | Chittagong | 1109.5 | 1109.5 |  | 0 |  | 19:00 |  | 80.177
|  |  | Total = |  |  | 8432 | MW | Khulna | 1327.6 | 1327.6 |  | 0 |  | 19:30 |  | 76.4907
7 | Total Gas Supplied : |  |  | 1026.84 | MMCFD |  |  | Rajshahi | 1221 | 1221 |  | 0 |  | 20:00 |  | 35.0198
8 | Fuel Cost : | i) Gas : | Taka | 141346506.946 | ii) Oil : | Taka | 571492748.66 | Comilla | 955 | 955 |  | 0 |  | 21:00 |  | 23.961
|  | iii) Coal : | Taka | 279348000 | Total | Taka | 992187255.606 | Mymensingh | 1007 | 927 |  | 80 |  | 22:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0 | MKWHr. | Sylhet | 382 | 382 |  | 0 |  | 23:00 |  | 0
| ii) During Peak Demand : |  |  | 130 | MW (E to W) at | 19:00 | hrs | Barisal | 293.7 | 293.7 |  | 0 |  | 24:00 |  | 0
| iii) Maximum : |  |  | 100 | MW at | 7:00 | hrs | Rangpur | 776 | 776 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 32.8° C |  |  | Total | 11285 | 11205 |  | 80
B. |  | 2023-02-28 | (Today) |  |  |  | Tuesday |  |  | Probable max. temperature in Dhaka |  |  | 33.2° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 11800 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 12821 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 10500 | MW
4 | Reserve(Generation end) |  |  |  | 1021 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 241.6312 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 8381 | MW at | 4:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 20.7956 | MKWHr. | ii) HVDC Flow at Peak Time |  | 808 | MW at | 19:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.5296 | MKWHr. | iii) Maximum HVDC Flow : |  | 893 | MW at | 2:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 79.75 |  | (b) Today: | 79.63 |  | (c) Rule Curve: |  | 93.15
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2023-02-27 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 130 | 180 | 0 | 0 | 0 | 396 | 347 |  | 0 | 180 | 274 | 29 | 0 | 30 | 0 | 0 | 65 | 40 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 22 | 24 | 33 | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 212 | 0 | 0 | 0 |  | 6 | 0 | 0 | 22 | 0 | 19 | 12 | 0 | 0 | 0 | 0 | 280 | 0 | 155 | 8 | 0 | 45 | 48 | 0 | 51 | 0 | 0 | 0 | 19 | 9 | 33 | 21 | 100 | 73 | 0 | 16 | 0 | 42 | 31 | 42 | 50 | 112 | 0 | 62 | 84 | 0 | 202 | 19 | 0 | 8 | 290 | 8 | 8 | 0 | 45 | 0 | 0 | 49 | 0 | 34 | 0 | 25 | 34 | 46 | 367 | 9 | 32 | 17 | 0 | 16 | 17 | 54 | 34 | 9 | 25 | 70 | 17 | 0 | 17 | 107 | 0 | 0 | 0 | 18 | 17 | 320 | 0 | 0 |  | 892 | 0 | 205 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 169 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 38 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 1132 | 224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159 | 0 | 0 |  | 5322 | 3547 | 8869 | 3648 | 892 | 1758 | 0 | 950 | 1491 | 30 | 0 | 0 | 100 | 0 | 0 | 79.77
2:00 | 0 | 0 | 130 | 180 | 0 | 0 | 0 | 396 | 350 |  | 0 | 225 | 279 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 22 | 24 | 33 | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 212 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 12 | 0 | 0 | 0 | 0 | 280 | 0 | 154 | 8 | 0 | 41 | 49 | 0 | 51 | 0 | 0 | 0 | 19 | 9 | 33 | 21 | 94 | 74 | 0 | 16 | 0 | 42 | 31 | 31 | 50 | 112 | 0 | 62 | 84 | 0 | 205 | 19 | 0 | 8 | 290 | 8 | 8 | 0 | 0 | 0 | 0 | 49 | 0 | 17 | 0 | 25 | 34 | 46 | 367 | 9 | 0 | 17 | 0 | 16 | 17 | 54 | 0 | 0 | 0 | 70 | 17 | 0 | 17 | 107 | 0 | 0 | 0 | 18 | 17 | 320 | 0 | 0 |  | 893 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 171 | 0 | 0 | 35 | 0 | 35 | 0 | 0 | 0 | 0 | 35 | 1022 | 224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159 | 0 | 0 |  | 5045 | 3391 | 8436 | 3654 | 893 | 1800 | 0 | 584 | 1381 | 30 | 0 | 0 | 94 | 0 | 0 | 79.77
3:00 | 0 | 0 | 133 | 180 | 0 | 0 | 0 | 397 | 350 |  | 0 | 250 | 283 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 22 | 24 | 33 | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 12 | 0 | 0 | 0 | 0 | 280 | 0 | 156 | 8 | 0 | 41 | 49 | 0 | 51 | 0 | 0 | 0 | 18 | 9 | 33 | 21 | 94 | 74 | 0 | 16 | 0 | 42 | 31 | 31 | 30 | 112 | 0 | 40 | 10 | 0 | 206 | 19 | 0 | 8 | 295 | 8 | 8 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 48 | 365 | 9 | 0 | 17 | 0 | 16 | 17 | 54 | 0 | 0 | 0 | 70 | 17 | 0 | 17 | 107 | 0 | 0 | 0 | 17 | 17 | 320 | 0 | 0 |  | 893 | 0 | 215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 1022 | 223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159 | 0 | 0 |  | 4869 | 3323 | 8192 | 3619 | 893 | 1736 | 0 | 439 | 1381 | 30 | 0 | 0 | 94 | 0 | 0 | 79.76
4:00 | 0 | 0 | 130 | 180 | 0 | 0 | 0 | 397 | 350 |  | 0 | 250 | 282 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 22 | 24 | 33 | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 213 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 12 | 0 | 0 | 0 | 0 | 290 | 0 | 198 | 8 | 0 | 41 | 10 | 0 | 10 | 0 | 0 | 0 | 18 | 9 | 33 | 21 | 94 | 73 | 0 | 16 | 0 | 42 | 31 | 11 | 10 | 112 | 0 | 40 | 10 | 0 | 205 | 19 | 0 | 8 | 290 | 8 | 8 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 46 | 374 | 9 | 0 | 17 | 0 | 16 | 17 | 54 | 0 | 0 | 0 | 70 | 17 | 0 | 17 | 107 | 0 | 0 | 0 | 18 | 17 | 320 | 0 | 0 |  | 893 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 920 | 224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 |  | 4798 | 3202 | 8000 | 3692 | 893 | 1608 | 0 | 403 | 1280 | 30 | 0 | 0 | 94 | 0 | 0 | 79.76
5:00 | 0 | 0 | 130 | 180 | 0 | 0 | 0 | 397 | 348 |  | 0 | 260 | 280 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 22 | 24 | 33 | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 20 | 12 | 0 | 0 | 0 | 0 | 280 | 0 | 211 | 8 | 0 | 41 | 5 | 0 | 10 | 0 | 0 | 0 | 18 | 9 | 33 | 21 | 86 | 74 | 0 | 16 | 0 | 42 | 31 | 11 | 10 | 80 | 0 | 40 | 10 | 0 | 205 | 19 | 0 | 8 | 290 | 8 | 8 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 48 | 366 | 9 | 0 | 17 | 0 | 16 | 17 | 54 | 0 | 0 | 0 | 70 | 17 | 0 | 17 | 107 | 0 | 0 | 0 | 18 | 17 | 340 | 0 | 0 |  | 889 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 900 | 164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 |  | 4782 | 3123 | 7905 | 3718 | 889 | 1516 | 0 | 406 | 1260 | 30 | 0 | 0 | 86 | 0 | 0 | 79.75
6:00 | 0 | 0 | 130 | 180 | 0 | 0 | 0 | 396 | 350 |  | 0 | 400 | 269 | 0 | 0 | 0 | 0 | 0 | 39 | 3 | 24 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 22 | 25 | 33 | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 0 |  | 2 | 0 | 0 | 22 | 0 | 20 | 12 | 2 | 0 | 0 | 0 | 280 | 0 | 221 | 8 | 0 | 41 | 5 | 0 | 10 | 0 | 0 | 0 | 18 | 9 | 33 | 21 | 86 | 35 | 0 | 16 | 0 | 42 | 31 | 11 | 10 | 80 | 0 | 40 | 10 | 0 | 205 | 19 | 0 | 8 | 300 | 8 | 8 | 0 | 5 | 0 | 0 | 49 | 0 | 2 | 0 | 12 | 5 | 46 | 366 | 9 | 2 | 17 | 0 | 16 | 17 | 54 | 17 | 3 | 9 | 70 | 17 | 0 | 17 | 89 | 0 | 0 | 0 | 18 | 17 | 340 | 0 | 0 |  | 889 | 0 | 230 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 11 | 0 | 0 | 240 | 0 | 0 | 172 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 0 | 3 | 0 | 5 | 0 | 20 | 0 | 0 | 0 | 920 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159 | 0 | 0 |  | 4993 | 3225 | 8218 | 3665 | 889 | 1661 | 0 | 536 | 1319 | 30 | 0 | 32 | 86 | 0 | 0 | 79.75
7:00 | 0 | 0 | 130 | 180 | 0 | 0 | 0 | 356 | 300 |  | 0 | 400 | 286 | 11 | 36 | 40 | 0 | 0 | 102 | 22 | 24 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 22 | 25 | 33 | 30 | 8 | 0 | 30 | 0 | 0 | 0 | 6 | 215 | 0 | 0 | 0 |  | 6 | 0 | 0 | 22 | 0 | 20 | 12 | 2 | 0 | 0 | 0 | 290 | 0 | 193 | 8 | 0 | 41 | 5 | 0 | 27 | 0 | 0 | 0 | 18 | 9 | 33 | 21 | 84 | 35 | 0 | 14 | 0 | 42 | 31 | 31 | 40 | 112 | 0 | 61 | 84 | 0 | 205 | 19 | 0 | 8 | 300 | 8 | 8 | 0 | 66 | 0 | 0 | 49 | 0 | 17 | 2 | 25 | 34 | 43 | 366 | 9 | 35 | 17 | 0 | 16 | 17 | 54 | 17 | 9 | 25 | 70 | 17 | 2 | 17 | 107 | 0 | 0 | 2 | 18 | 17 | 346 | 0 | 0 |  | 796 | 0 | 235 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 42 | 0 | 0 | 0 | 18 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 0 | 13 | 0 | 33 | 0 | 26 | 0 | 0 | 35 | 980 | 224 | 0 | 10 | 0 | 5 | 0 | 0 | 0 | 0 | 1 | 160 | 0 | 7 |  | 5491 | 3460 | 8951 | 3703 | 796 | 1860 | 0 | 1029 | 1390 | 30 | 0 | 40 | 84 | 19 | 105.0596 | 79.74
8:00 | 0 | 0 | 130 | 180 | 0 | 0 | 0 | 398 | 343 |  | 0 | 420 | 268 | 31 | 63 | 55 | 0 | 0 | 63 | 33 | 24 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 22 | 25 | 33 | 30 | 25 | 0 | 30 | 0 | 0 | 0 | 17 | 214 | 0 | 0 | 0 |  | 6 | 0 | 0 | 44 | 0 | 21 | 12 | 2 | 0 | 0 | 0 | 280 | 0 | 182 | 8 | 0 | 45 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 9 | 28 | 21 | 100 | 32 | 0 | 16 | 1 | 41 | 31 | 40 | 40 | 80 | 0 | 40 | 84 | 0 | 205 | 19 | 0 | 8 | 270 | 8 | 8 | 0 | 65 | 0 | 0 | 49 | 0 | 17 | 7 | 50 | 34 | 40 | 366 | 9 | 35 | 17 | 1 | 16 | 17 | 54 | 17 | 9 | 35 | 70 | 17 | 12 | 17 | 107 | 0 | 12 | 7 | 18 | 17 | 347 | 0 | 0 |  | 771 | 0 | 235 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 42 | 0 | 0 | 0 | 18 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 177 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 36 | 0 | 35 | 0 | 34 | 0 | 1 | 35 | 1102 | 224 | 0 | 17 | 1 | 24 | 0 | 0 | 0 | 0 | 8 | 160 | 0 | 38 |  | 5686 | 3659 | 9345 | 3665 | 771 | 1875 | 0 | 1236 | 1512 | 30 | 0 | 56 | 100 | 100 | 165.8835 | 79.74
9:00 | 0 | 0 | 130 | 180 | 0 | 0 | 0 | 399 | 346 |  | 0 | 450 | 262 | 33 | 62 | 55 | 0 | 0 | 32 | 33 | 40 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 33 | 30 | 25 | 0 | 30 | 0 | 0 | 0 | 17 | 214 | 0 | 0 | 0 |  | 6 | 40 | 0 | 44 | 0 | 20 | 13 | 0 | 0 | 0 | 0 | 275 | 0 | 182 | 8 | 0 | 44 | 5 | 0 | 43 | 0 | 0 | 0 | 18 | 9 | 29 | 21 | 98 | 32 | 0 | 19 | 1 | 41 | 31 | 22 | 40 | 80 | 0 | 40 | 84 | 0 | 207 | 18 | 0 | 8 | 260 | 8 | 8 | 0 | 145 | 0 | 0 | 86 | 0 | 51 | 13 | 50 | 34 | 47 | 366 | 19 | 52 | 17 | 2 | 100 | 17 | 54 | 17 | 9 | 50 | 70 | 18 | 24 | 17 | 107 | 0 | 17 | 16 | 17 | 17 | 360 | 0 | 0 |  | 771 | 0 | 230 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 14 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | 0 | 42 | 16 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 36 | 0 | 35 | 0 | 34 | 0 | 2 | 35 | 1122 | 196 | 0 | 17 | 2 | 47 | 0 | 0 | 0 | 0 | 17 | 159 | 0 | 67 |  | 6012 | 3708 | 9720 | 3620 | 771 | 1839 | 0 | 1524 | 1531 | 30 | 0 | 116 | 98 | 191 | 92.1575 | 79.73
10:00 | 0 | 0 | 130 | 180 | 0 | 0 | 0 | 407 | 336 |  | 0 | 450 | 265 | 33 | 62 | 55 | 0 | 0 | 38 | 35 | 40 | 48 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 16 | 22 | 25 | 33 | 28 | 25 | 0 | 30 | 0 | 0 | 0 | 17 | 214 | 0 | 0 | 0 |  | 6 | 40 | 17 | 44 | 0 | 19 | 15 | 0 | 0 | 0 | 0 | 280 | 0 | 183 | 8 | 0 | 44 | 5 | 0 | 43 | 0 | 13 | 0 | 18 | 9 | 30 | 21 | 106 | 32 | 0 | 19 | 2 | 42 | 31 | 22 | 40 | 80 | 0 | 40 | 84 | 0 | 207 | 18 | 0 | 8 | 270 | 8 | 8 | 0 | 145 | 0 | 0 | 86 | 0 | 73 | 18 | 50 | 34 | 48 | 367 | 19 | 52 | 17 | 3 | 105 | 17 | 54 | 17 | 9 | 50 | 50 | 18 | 38 | 17 | 107 | 0 | 17 | 23 | 18 | 17 | 360 | 0 | 0 |  | 889 | 0 | 225 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 14 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | 0 | 42 | 0 | 0 | 0 | 20 | 0 | 8 | 0 | 0 | 250 | 0 | 0 | 157 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 36 | 0 | 35 | 0 | 43 | 0 | 4 | 35 | 990 | 190 | 0 | 17 | 3 | 69 | 0 | 0 | 0 | 0 | 24 | 160 | 0 | 97 |  | 6137 | 3723 | 9860 | 3602 | 889 | 1835 | 0 | 1587 | 1400 | 30 | 0 | 130 | 106 | 281 | 68.1966 | 79.73
11:00 | 0 | 0 | 130 | 180 | 0 | 0 | 0 | 410 | 302 |  | 0 | 450 | 278 | 34 | 62 | 45 | 0 | 0 | 39 | 40 | 40 | 48 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 16 | 22 | 24 | 33 | 28 | 25 | 0 | 30 | 0 | 0 | 0 | 17 | 223 | 0 | 0 | 0 |  | 6 | 40 | 16 | 44 | 0 | 19 | 15 | 0 | 0 | 0 | 0 | 310 | 0 | 201 | 8 | 0 | 44 | 5 | 0 | 43 | 0 | 30 | 0 | 18 | 9 | 30 | 21 | 106 | 32 | 0 | 19 | 2 | 43 | 31 | 22 | 40 | 112 | 0 | 40 | 60 | 0 | 207 | 18 | 0 | 8 | 290 | 8 | 8 | 0 | 147 | 0 | 0 | 88 | 0 | 68 | 20 | 50 | 34 | 47 | 398 | 23 | 52 | 17 | 4 | 105 | 17 | 54 | 34 | 8 | 50 | 40 | 18 | 45 | 17 | 107 | 0 | 12 | 25 | 24 | 17 | 350 | 0 | 0 |  | 889 | 0 | 215 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 15 | 0 | 0 | 0 | 0 | 0 | 15 | 8 | 0 | 42 | 16 | 0 | 0 | 20 | 0 | 8 | 0 | 0 | 250 | 0 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 36 | 0 | 35 | 0 | 42 | 0 | 5 | 35 | 940 | 190 | 0 | 17 | 4 | 84 | 35 | 0 | 0 | 0 | 30 | 160 | 0 | 118 |  | 6269 | 3803 | 10072 | 3715 | 889 | 1843 | 0 | 1629 | 1350 | 30 | 0 | 173 | 106 | 337 | 72.8044 | 79.72
12:00 | 0 | 0 | 130 | 180 | 0 | 0 | 0 | 413 | 343 |  | 0 | 450 | 277 | 40 | 70 | 55 | 0 | 0 | 99 | 40 | 40 | 48 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 16 | 22 | 24 | 33 | 28 | 25 | 0 | 30 | 0 | 0 | 0 | 17 | 219 | 0 | 0 | 0 |  | 6 | 56 | 51 | 44 | 0 | 19 | 15 | 0 | 0 | 0 | 0 | 310 | 0 | 203 | 8 | 0 | 43 | 5 | 0 | 43 | 0 | 36 | 0 | 18 | 9 | 28 | 21 | 108 | 32 | 0 | 19 | 2 | 43 | 20 | 46 | 42 | 112 | 0 | 60 | 86 | 0 | 207 | 18 | 0 | 8 | 310 | 6 | 8 | 0 | 147 | 0 | 0 | 87 | 0 | 67 | 20 | 50 | 34 | 47 | 401 | 19 | 52 | 17 | 4 | 105 | 17 | 54 | 34 | 9 | 50 | 43 | 18 | 49 | 17 | 107 | 0 | 17 | 27 | 39 | 16 | 340 | 0 | 0 |  | 890 | 0 | 200 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 15 | 0 | 0 | 0 | 0 | 0 | 18 | 58 | 0 | 42 | 32 | 0 | 25 | 19 | 0 | 8 | 0 | 0 | 250 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 196 | 0 | 0 | 36 | 0 | 35 | 0 | 35 | 0 | 6 | 35 | 950 | 224 | 0 | 17 | 4 | 91 | 35 | 0 | 0 | 0 | 32 | 160 | 0 | 126 |  | 6545 | 3948 | 10493 | 3772 | 890 | 1988 | 0 | 1660 | 1360 | 30 | 0 | 324 | 108 | 361 | 0 | 79.72
13:00 | 0 | 0 | 130 | 180 | 0 | 0 | 0 | 412 | 337 |  | 0 | 450 | 280 | 42 | 78 | 55 | 0 | 0 | 96 | 40 | 40 | 48 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 16 | 22 | 18 | 33 | 27 | 25 | 0 | 30 | 0 | 0 | 0 | 17 | 208 | 0 | 0 | 0 |  | 6 | 56 | 79 | 44 | 0 | 19 | 15 | 0 | 0 | 0 | 0 | 305 | 0 | 215 | 8 | 0 | 40 | 5 | 0 | 43 | 0 | 36 | 0 | 18 | 9 | 28 | 21 | 112 | 31 | 0 | 19 | 2 | 43 | 20 | 48 | 48 | 112 | 0 | 61 | 86 | 0 | 207 | 18 | 0 | 8 | 320 | 0 | 8 | 0 | 147 | 0 | 0 | 88 | 0 | 71 | 20 | 50 | 34 | 47 | 367 | 25 | 52 | 17 | 4 | 105 | 17 | 54 | 34 | 9 | 50 | 40 | 18 | 49 | 17 | 107 | 0 | 17 | 29 | 40 | 17 | 320 | 0 | 0 |  | 889 | 0 | 195 | 0 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 16 | 0 | 0 | 0 | 0 | 32 | 23 | 64 | 0 | 42 | 32 | 0 | 28 | 18 | 0 | 8 | 0 | 0 | 250 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 38 | 0 | 39 | 0 | 35 | 0 | 6 | 35 | 1092 | 222 | 0 | 17 | 3 | 88 | 35 | 0 | 0 | 0 | 32 | 170 | 0 | 125 |  | 6536 | 4117 | 10653 | 3650 | 889 | 2001 | 0 | 1703 | 1512 | 30 | 0 | 398 | 112 | 358 | 169 | 79.71
14:00 | 0 | 0 | 130 | 180 | 0 | 0 | 0 | 401 | 332 |  | 0 | 450 | 277 | 41 | 80 | 55 | 0 | 0 | 0 | 40 | 41 | 48 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 16 | 22 | 16 | 33 | 21 | 25 | 0 | 30 | 0 | 0 | 0 | 17 | 206 | 0 | 0 | 0 |  | 6 | 51 | 74 | 44 | 0 | 17 | 12 | 0 | 0 | 0 | 0 | 315 | 0 | 209 | 8 | 0 | 43 | 5 | 0 | 43 | 0 | 28 | 0 | 18 | 9 | 33 | 21 | 124 | 31 | 0 | 19 | 2 | 42 | 22 | 45 | 48 | 80 | 0 | 60 | 86 | 0 | 208 | 18 | 0 | 8 | 270 | 0 | 8 | 0 | 147 | 0 | 0 | 88 | 0 | 71 | 17 | 50 | 34 | 42 | 371 | 19 | 52 | 17 | 3 | 103 | 17 | 54 | 34 | 9 | 50 | 43 | 18 | 42 | 17 | 107 | 0 | 17 | 24 | 19 | 17 | 320 | 0 | 0 |  | 890 | 0 | 190 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 15 | 0 | 0 | 0 | 0 | 32 | 23 | 64 | 0 | 42 | 32 | 0 | 28 | 18 | 0 | 8 | 0 | 0 | 250 | 0 | 0 | 162 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 0 | 56 | 0 | 50 | 0 | 49 | 0 | 6 | 35 | 1030 | 222 | 0 | 17 | 3 | 80 | 35 | 0 | 0 | 0 | 29 | 170 | 0 | 108 |  | 6287 | 4068 | 10355 | 3533 | 890 | 1907 | 0 | 1727 | 1450 | 30 | 0 | 380 | 124 | 314 | 0 | 79.72
15:00 | 0 | 0 | 130 | 180 | 0 | 0 | 0 | 397 | 332 |  | 0 | 450 | 282 | 41 | 80 | 55 | 0 | 0 | 0 | 45 | 50 | 48 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 16 | 22 | 16 | 33 | 21 | 25 | 0 | 30 | 0 | 0 | 0 | 17 | 206 | 0 | 0 | 0 |  | 6 | 51 | 74 | 44 | 0 | 18 | 12 | 0 | 0 | 0 | 0 | 310 | 0 | 196 | 8 | 0 | 43 | 5 | 0 | 43 | 0 | 28 | 0 | 18 | 9 | 33 | 21 | 116 | 32 | 0 | 19 | 1 | 42 | 42 | 45 | 45 | 112 | 0 | 60 | 86 | 0 | 205 | 18 | 0 | 8 | 320 | 8 | 8 | 0 | 147 | 0 | 0 | 49 | 0 | 62 | 13 | 50 | 34 | 46 | 369 | 18 | 52 | 17 | 2 | 105 | 17 | 54 | 34 | 9 | 50 | 42 | 18 | 33 | 17 | 107 | 0 | 17 | 20 | 18 | 17 | 320 | 0 | 0 |  | 889 | 0 | 190 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 17 | 0 | 0 | 0 | 0 | 32 | 23 | 64 | 0 | 42 | 32 | 0 | 28 | 18 | 0 | 8 | 0 | 0 | 250 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 56 | 0 | 50 | 0 | 49 | 0 | 5 | 35 | 1052 | 222 | 0 | 35 | 2 | 62 | 36 | 0 | 0 | 0 | 17 | 170 | 0 | 89 |  | 6316 | 4037 | 10353 | 3528 | 889 | 1993 | 0 | 1701 | 1472 | 30 | 0 | 380 | 116 | 244 | 62 | 79.7
16:00 | 0 | 0 | 130 | 180 | 0 | 0 | 0 | 408 | 332 |  | 0 | 450 | 280 | 57 | 66 | 55 | 0 | 0 | 0 | 58 | 50 | 48 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 16 | 22 | 18 | 33 | 28 | 25 | 0 | 30 | 0 | 0 | 0 | 18 | 208 | 0 | 0 | 0 |  | 6 | 53 | 77 | 44 | 0 | 19 | 12 | 0 | 0 | 0 | 0 | 310 | 0 | 203 | 8 | 0 | 43 | 5 | 0 | 43 | 0 | 34 | 0 | 15 | 9 | 28 | 21 | 118 | 32 | 0 | 19 | 1 | 42 | 42 | 48 | 48 | 112 | 0 | 61 | 86 | 0 | 205 | 18 | 0 | 8 | 300 | 8 | 8 | 0 | 147 | 0 | 0 | 49 | 0 | 53 | 8 | 50 | 34 | 55 | 370 | 18 | 52 | 17 | 1 | 105 | 17 | 54 | 34 | 9 | 50 | 50 | 18 | 18 | 17 | 107 | 0 | 17 | 9 | 18 | 17 | 320 | 0 | 0 |  | 888 | 0 | 190 | 0 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 16 | 0 | 0 | 0 | 0 | 24 | 30 | 64 | 0 | 42 | 32 | 0 | 28 | 17 | 0 | 8 | 0 | 0 | 250 | 0 | 0 | 161 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 56 | 0 | 50 | 0 | 56 | 0 | 3 | 35 | 1072 | 170 | 0 | 35 | 2 | 36 | 36 | 0 | 0 | 0 | 15 | 170 | 0 | 45 |  | 6346 | 3949 | 10295 | 3559 | 888 | 1923 | 0 | 1757 | 1492 | 30 | 0 | 390 | 118 | 138 | 134 | 79.7
17:00 | 0 | 0 | 130 | 180 | 0 | 0 | 0 | 389 | 291 |  | 0 | 380 | 276 | 59 | 80 | 55 | 0 | 0 | 0 | 58 | 50 | 48 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 22 | 22 | 24 | 33 | 28 | 40 | 0 | 30 | 0 | 0 | 0 | 25 | 207 | 0 | 0 | 0 |  | 6 | 69 | 78 | 55 | 0 | 19 | 12 | 0 | 0 | 0 | 0 | 280 | 0 | 183 | 8 | 0 | 20 | 5 | 0 | 43 | 0 | 28 | 3 | 15 | 9 | 31 | 21 | 104 | 32 | 0 | 19 | 0 | 42 | 42 | 42 | 40 | 80 | 0 | 61 | 86 | 0 | 211 | 18 | 0 | 8 | 270 | 8 | 8 | 0 | 147 | 0 | 0 | 58 | 0 | 53 | 2 | 50 | 36 | 83 | 369 | 9 | 52 | 17 | 0 | 105 | 17 | 54 | 34 | 9 | 50 | 15 | 18 | 5 | 17 | 107 | 0 | 17 | 4 | 27 | 17 | 344 | 0 | 0 |  | 889 | 0 | 190 | 0 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 15 | 0 | 0 | 0 | 0 | 32 | 23 | 64 | 0 | 42 | 36 | 0 | 28 | 18 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 161 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 56 | 0 | 53 | 0 | 92 | 0 | 2 | 35 | 1020 | 170 | 0 | 35 | 0 | 12 | 36 | 0 | 0 | 0 | 5 | 169 | 0 | 19 |  | 6150 | 3872 | 10022 | 3469 | 889 | 1732 | 0 | 1904 | 1439 | 30 | 0 | 406 | 104 | 49 | 161 | 79.69
18:00 | 0 | 0 | 130 | 180 | 0 | 0 | 0 | 345 | 272 |  | 0 | 380 | 274 | 57 | 80 | 55 | 0 | 0 | 0 | 58 | 50 | 75 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 22 | 24 | 33 | 28 | 41 | 0 | 30 | 0 | 0 | 0 | 25 | 223 | 0 | 0 | 0 |  | 6 | 69 | 85 | 72 | 0 | 19 | 12 | 0 | 0 | 0 | 0 | 280 | 0 | 182 | 8 | 0 | 20 | 5 | 0 | 51 | 0 | 32 | 8 | 15 | 9 | 31 | 21 | 113 | 33 | 0 | 19 | 0 | 43 | 42 | 42 | 40 | 80 | 0 | 61 | 86 | 0 | 211 | 18 | 0 | 8 | 260 | 8 | 8 | 0 | 195 | 0 | 0 | 76 | 0 | 66 | 0 | 70 | 74 | 120 | 368 | 9 | 71 | 42 | 0 | 105 | 17 | 54 | 67 | 33 | 57 | 25 | 17 | 0 | 17 | 107 | 0 | 0 | 0 | 72 | 17 | 300 | 0 | 0 |  | 880 | 0 | 185 | 0 | 79 | 0 | 0 | 0 | 25 | 0 | 8 | 183 | 16 | 0 | 0 | 0 | 0 | 32 | 23 | 86 | 0 | 42 | 40 | 0 | 28 | 19 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 161 | 0 | 0 | 0 | 0 | 0 | 159 | 0 | 0 | 56 | 0 | 70 | 0 | 92 | 0 | 0 | 75 | 970 | 170 | 0 | 35 | 0 | 0 | 78 | 0 | 0 | 0 | 0 | 171 | 0 | 0 |  | 6467 | 3944 | 10411 | 3412 | 880 | 1711 | 0 | 2379 | 1391 | 30 | 0 | 495 | 113 | 0 | 167 | 79.69
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 130 | 180 | 0 | 0 | 0 | 391 | 342 |  | 0 | 450 | 284 | 58 | 80 | 55 | 0 | 0 | 0 | 58 | 58 | 115 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 22 | 22 | 24 | 33 | 28 | 50 | 0 | 30 | 0 | 0 | 0 | 25 | 227 | 0 | 0 | 0 |  | 6 | 69 | 85 | 61 | 0 | 19 | 12 | 0 | 0 | 0 | 0 | 280 | 0 | 182 | 8 | 0 | 20 | 5 | 0 | 51 | 0 | 34 | 8 | 15 | 9 | 33 | 21 | 110 | 49 | 0 | 19 | 0 | 42 | 42 | 39 | 40 | 112 | 0 | 62 | 86 | 0 | 211 | 18 | 0 | 8 | 300 | 8 | 8 | 0 | 245 | 0 | 0 | 97 | 0 | 91 | 0 | 100 | 100 | 150 | 368 | 56 | 88 | 51 | 0 | 238 | 17 | 54 | 80 | 87 | 90 | 40 | 17 | 0 | 91 | 107 | 0 | 0 | 0 | 72 | 17 | 401 | 0 | 0 |  | 808 | 0 | 180 | 0 | 79 | 0 | 0 | 0 | 38 | 0 | 8 | 184 | 20 | 0 | 0 | 0 | 0 | 32 | 27 | 86 | 0 | 50 | 40 | 0 | 28 | 20 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 161 | 0 | 0 | 0 | 0 | 0 | 154 | 0 | 0 | 56 | 0 | 70 | 0 | 92 | 0 | 0 | 75 | 1112 | 222 | 0 | 116 | 0 | 0 | 94 | 0 | 0 | 0 | 0 | 199 | 0 | 0 |  | 7496 | 4212 | 11708 | 3587 | 808 | 1987 | 0 | 3071 | 1561 | 30 | 0 | 554 | 110 | 0 | 80.177 | 79.67
19:30 | 0 | 0 | 130 | 180 | 0 | 0 | 0 | 402 | 348 |  | 0 | 450 | 270 | 58 | 56 | 55 | 0 | 0 | 0 | 58 | 58 | 100 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 22 | 22 | 24 | 33 | 28 | 50 | 0 | 30 | 0 | 0 | 0 | 25 | 226 | 0 | 0 | 0 |  | 6 | 0 | 29 | 62 | 0 | 19 | 12 | 0 | 0 | 0 | 0 | 280 | 0 | 182 | 8 | 0 | 20 | 5 | 0 | 51 | 0 | 0 | 8 | 19 | 9 | 33 | 21 | 120 | 50 | 0 | 19 | 0 | 42 | 42 | 43 | 40 | 112 | 0 | 62 | 86 | 0 | 215 | 18 | 0 | 8 | 256 | 8 | 8 | 0 | 245 | 0 | 0 | 97 | 0 | 99 | 0 | 100 | 100 | 150 | 368 | 56 | 88 | 51 | 0 | 240 | 17 | 54 | 77 | 115 | 90 | 40 | 17 | 0 | 162 | 107 | 0 | 0 | 0 | 72 | 17 | 401 | 0 | 0 |  | 738 | 0 | 180 | 0 | 80 | 0 | 0 | 0 | 47 | 0 | 32 | 165 | 20 | 0 | 0 | 0 | 0 | 32 | 28 | 25 | 0 | 0 | 40 | 0 | 28 | 22 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 154 | 0 | 0 | 56 | 0 | 70 | 0 | 92 | 0 | 0 | 75 | 1222 | 222 | 0 | 116 | 0 | 0 | 104 | 0 | 0 | 0 | 0 | 201 | 0 | 0 |  | 7386 | 4170 | 11556 | 3586 | 738 | 1941 | 0 | 3139 | 1673 | 30 | 0 | 329 | 120 | 0 | 76.4907 | 0
20:00 | 0 | 0 | 130 | 180 | 0 | 0 | 0 | 402 | 347 |  | 0 | 450 | 275 | 58 | 50 | 40 | 0 | 0 | 0 | 58 | 58 | 100 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 22 | 22 | 24 | 33 | 28 | 25 | 0 | 30 | 0 | 0 | 0 | 25 | 226 | 0 | 0 | 0 |  | 6 | 0 | 17 | 71 | 0 | 19 | 12 | 0 | 0 | 0 | 0 | 280 | 0 | 182 | 8 | 0 | 20 | 5 | 0 | 51 | 0 | 0 | 8 | 19 | 9 | 33 | 21 | 112 | 59 | 0 | 19 | 0 | 42 | 42 | 42 | 40 | 112 | 0 | 62 | 86 | 0 | 210 | 18 | 0 | 8 | 260 | 8 | 8 | 0 | 145 | 0 | 0 | 97 | 0 | 99 | 0 | 100 | 100 | 150 | 368 | 56 | 88 | 51 | 0 | 248 | 17 | 54 | 50 | 114 | 90 | 40 | 17 | 0 | 162 | 107 | 0 | 1 | 0 | 72 | 17 | 401 | 0 | 0 |  | 738 | 0 | 180 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 32 | 186 | 20 | 0 | 0 | 0 | 0 | 32 | 0 | 25 | 0 | 0 | 0 | 0 | 15 | 22 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 155 | 0 | 0 | 56 | 0 | 70 | 0 | 92 | 0 | 0 | 75 | 1232 | 222 | 0 | 100 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 200 | 0 | 0 |  | 7221 | 4066 | 11287 | 3612 | 738 | 1948 | 0 | 2976 | 1682 | 30 | 0 | 189 | 112 | 0 | 35.0198 | 79.68
21:00 | 0 | 0 | 130 | 180 | 0 | 0 | 0 | 401 | 343 |  | 0 | 450 | 280 | 53 | 0 | 30 | 0 | 0 | 0 | 60 | 58 | 100 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 22 | 24 | 33 | 28 | 25 | 0 | 30 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 |  | 6 | 0 | 0 | 85 | 0 | 19 | 12 | 0 | 0 | 0 | 0 | 310 | 0 | 182 | 8 | 0 | 20 | 5 | 0 | 51 | 0 | 0 | 8 | 19 | 9 | 33 | 21 | 120 | 106 | 0 | 19 | 0 | 43 | 43 | 53 | 40 | 112 | 0 | 61 | 86 | 0 | 212 | 18 | 0 | 8 | 280 | 8 | 8 | 0 | 147 | 0 | 0 | 98 | 0 | 98 | 0 | 100 | 100 | 150 | 367 | 56 | 88 | 51 | 0 | 249 | 17 | 54 | 17 | 116 | 100 | 42 | 17 | 0 | 129 | 107 | 0 | 17 | 0 | 72 | 17 | 401 | 0 | 0 |  | 809 | 0 | 185 | 0 | 97 | 0 | 0 | 0 | 0 | 0 | 32 | 186 | 21 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 142 | 0 | 0 | 0 | 0 | 0 | 155 | 0 | 0 | 56 | 0 | 70 | 0 | 78 | 0 | 0 | 75 | 1244 | 222 | 0 | 17 | 0 | 0 | 114 | 0 | 0 | 0 | 0 | 200 | 0 | 0 |  | 7196 | 4018 | 11214 | 3678 | 809 | 1981 | 0 | 2770 | 1694 | 30 | 0 | 132 | 120 | 0 | 23.961 | 79.67
22:00 | 0 | 0 | 130 | 180 | 0 | 0 | 0 | 396 | 343 |  | 0 | 450 | 282 | 58 | 0 | 30 | 0 | 0 | 0 | 60 | 58 | 64 | 0 | 0 | 0 | 0 | 17 | 24 | 35 | 22 | 22 | 26 | 33 | 28 | 25 | 0 | 30 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 |  | 6 | 0 | 0 | 85 | 0 | 19 | 12 | 0 | 0 | 0 | 0 | 310 | 0 | 182 | 8 | 0 | 20 | 5 | 0 | 51 | 0 | 0 | 8 | 18 | 9 | 33 | 21 | 116 | 102 | 0 | 19 | 0 | 42 | 43 | 53 | 40 | 80 | 0 | 62 | 86 | 0 | 215 | 18 | 0 | 8 | 290 | 8 | 8 | 0 | 98 | 0 | 0 | 98 | 0 | 82 | 0 | 100 | 100 | 150 | 367 | 56 | 50 | 51 | 0 | 250 | 17 | 54 | 17 | 115 | 100 | 55 | 17 | 0 | 32 | 107 | 0 | 17 | 0 | 72 | 17 | 375 | 0 | 0 |  | 809 | 0 | 190 | 0 | 97 | 0 | 0 | 0 | 0 | 0 | 32 | 187 | 20 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158 | 0 | 0 | 56 | 0 | 70 | 0 | 78 | 0 | 0 | 75 | 1244 | 222 | 0 | 17 | 0 | 0 | 75 | 0 | 0 | 0 | 0 | 201 | 0 | 0 |  | 6915 | 3846 | 10761 | 3530 | 809 | 1960 | 0 | 2525 | 1695 | 30 | 0 | 96 | 116 | 0 | 0 | 79.67
23:00 | 0 | 0 | 130 | 180 | 0 | 0 | 0 | 395 | 348 |  | 0 | 450 | 268 | 57 | 0 | 30 | 0 | 0 | 0 | 60 | 50 | 64 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 22 | 22 | 26 | 33 | 28 | 25 | 0 | 30 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 |  | 6 | 0 | 0 | 85 | 0 | 19 | 12 | 0 | 0 | 0 | 0 | 310 | 0 | 181 | 8 | 0 | 30 | 5 | 0 | 51 | 0 | 0 | 8 | 18 | 9 | 33 | 21 | 112 | 104 | 0 | 15 | 0 | 41 | 43 | 42 | 50 | 80 | 0 | 62 | 86 | 0 | 211 | 19 | 0 | 8 | 270 | 8 | 8 | 0 | 98 | 0 | 0 | 98 | 0 | 71 | 0 | 100 | 100 | 61 | 367 | 56 | 35 | 51 | 0 | 249 | 17 | 54 | 17 | 78 | 100 | 65 | 18 | 0 | 17 | 107 | 0 | 17 | 0 | 69 | 17 | 380 | 0 | 0 |  | 881 | 0 | 200 | 0 | 97 | 0 | 0 | 0 | 0 | 0 | 32 | 187 | 20 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 56 | 0 | 70 | 0 | 72 | 0 | 0 | 35 | 1200 | 222 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 149 | 0 | 0 |  | 6694 | 3703 | 10397 | 3560 | 881 | 1930 | 0 | 2239 | 1549 | 30 | 0 | 96 | 112 | 0 | 0 | 79.66
24:00 | 0 | 0 | 130 | 180 | 0 | 0 | 0 | 395 | 352 |  | 0 | 450 | 248 | 59 | 0 | 30 | 0 | 0 | 0 | 60 | 24 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 22 | 22 | 26 | 33 | 28 | 8 | 0 | 30 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 |  | 6 | 0 | 0 | 72 | 0 | 19 | 12 | 0 | 0 | 0 | 0 | 290 | 0 | 182 | 8 | 0 | 30 | 5 | 0 | 51 | 0 | 0 | 8 | 18 | 9 | 33 | 21 | 102 | 93 | 0 | 15 | 0 | 42 | 43 | 11 | 50 | 80 | 0 | 40 | 86 | 0 | 212 | 19 | 0 | 8 | 270 | 8 | 8 | 0 | 98 | 0 | 0 | 98 | 0 | 67 | 0 | 100 | 34 | 30 | 365 | 56 | 35 | 51 | 0 | 249 | 17 | 54 | 17 | 39 | 100 | 98 | 17 | 0 | 17 | 107 | 0 | 17 | 0 | 24 | 17 | 360 | 0 | 0 |  | 881 | 0 | 210 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 32 | 187 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 157 | 0 | 0 | 56 | 0 | 35 | 0 | 49 | 0 | 0 | 35 | 1120 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 |  | 6324 | 3421 | 9745 | 3525 | 881 | 1818 | 0 | 1870 | 1471 | 30 | 0 | 48 | 102 | 0 | 0 | 79.66
KWH | 0 | 0 | 3117125 | 4378500 | 0 | 0 | 0 | 9615360 | 7988000 |  | 0 | 8941500 | 6645411 | 849600 | 891262 | 926397 | 0 | 0 | 880000 | 847680 | 862848 | 1075680 | 0 | 0 | 0 | 0 | 160200 | 297950 | 306991 | 385668 | 528000 | 557640 | 826100 | 683900 | 506400 | 0 | 723480 | 0 | 0 | 0 | 279975 | 5024542 | 0 | 0 | 0 |  | 124080 | 568944 | 635944 | 996960 | 0 | 463680 | 304560 | 22080 | 0 | 0 | 0 | 7434900 | 0 | 4561000 | 234181 | 0 | 868248 | 287040 | 0 | 1053527 | 0 | 282192 | 78235 | 399708 | 243720 | 785400 | 479260 | 2529600 | 1249920 | 0 | 413856 | 12650 | 1000000 | 770400 | 851400 | 953496 | 2425663 | 0 | 1321344 | 1741440 | 0 | 5159170 | 440000 | 0 | 189180 | 7030000 | 173856 | 192384 | 0 | 2571818 | 0 | 0 | 1699200 | 0 | 1256260 | 137970 | 1264320 | 1147680 | 1659345 | 8954000 | 584400 | 1068499 | 729309 | 26879 | 2629527 | 452685 | 1326467 | 660060 | 708960 | 1186560 | 1317700 | 427200 | 320020 | 731520 | 2565545 | 0 | 251640 | 186073 | 827520 | 430560 | 8300200 | 0 | 0 |  | 20795636 | 0 | 5046624 | 0 | 1266240 | 0 | 0 | 0 | 71040 | 0 | 169500 | 4450297 | 393400 | 0 | 0 | 0 | 0 | 341440 | 209824 | 588928 | 0 | 521980 | 305682 | 0 | 225116 | 451200 | 0 | 239958 | 0 | 0 | 5702900 | 0 | 0 | 3742236 | 0 | 0 | 0 | 0 | 0 | 4323691 | 0 | 0 | 927840 | 0 | 1085376 | 0 | 1103212 | 0 | 42056 | 942336 | 27655900 | 5010027 | 0 | 606000 | 26700 | 600480 | 799296 | 0 | 0 | 0 | 206980 | 4058200 | 0 | 837040 |  | 147000144 | 92747135 | 239747279 | 88169267 | 20795636 | 44217545 | 0 | 39193113 | 37417000 | 723480 | 0 | 4304790 | 2529600 | 2396848 | 0
Fuel Cost | 0 | 0 | 4551002.5 | 6523965 | 0 | 0 | 0 | 10096128 | 8627040 |  | 0 | 9746235 | 7376406.21 | 9498528 | 11809221.5 | 12274760.25 | 0 | 0 | 1540000 | 12393081.6 | 12140271.36 | 17436772.8 | 0 | 0 | 0 | 0 | 2037744 | 4022325 | 4116749.31 | 289251 | 396000 | 0 | 0 | 0 | 8613864 | 0 | 195339.6 | 0 | 0 | 0 | 4577591.25 | 5225523.68 | 0 | 0 | 0 |  | 1619244 | 9489985.92 | 10823766.88 | 13468929.6 | 0 | 5364777.6 | 386791.2 | 73526.4 | 0 | 0 | 0 | 8252739 | 0 | 5290760 | 302093.49 | 0 | 981120.24 | 427689.6 | 0 | 1759390.09 | 0 | 4873455.84 | 1052260.75 | 547599.96 | 182790 | 1374450 | 359445 | 18162528 | 1362412.8 | 0 | 562844.16 | 201641 | 1370000 | 1016928 | 1481436 | 1649548.08 | 2789512.45 | 0 | 2563407.36 | 3970483.2 | 0 | 5210761.7 | 946000 | 0 | 374576.4 | 7030000 | 130392 | 146211.84 | 0 | 35105315.7 | 0 | 0 | 22905216 | 0 | 17399201 | 1612869.3 | 13047782.4 | 15677308.8 | 22019508.15 | 8237680 | 7106304 | 15450495.54 | 9225758.85 | 0 | 30870646.98 | 4929739.65 | 14100344.21 | 8957014.2 | 9138494.4 | 13977676.8 | 1212284 | 5532240 | 4624289 | 9282988.8 | 29195902.1 | 0 | 3286418.4 | 2223572.35 | 12387974.4 | 5670475.2 | 0 | 0 | 0 |  | 62386908 | 0 | 5652218.88 | 0 | 13181558.4 | 0 | 0 | 0 | 1279430.4 | 0 | 2435715 | 4984332.64 | 763196 | 0 | 0 | 0 | 0 | 5725948.8 | 3669821.76 | 9210833.92 | 0 | 8643988.8 | 5169082.62 | 0 | 3797706.92 | 933984 | 0 | 181648.206 | 0 | 0 | 30168341 | 0 | 0 | 4340993.76 | 0 | 0 | 0 | 0 | 0 | 5015481.56 | 0 | 0 | 12470169.6 | 0 | 12839998.08 | 0 | 14010792.4 | 0 | 464718.8 | 11439959.04 | 249179659 | 5110227.54 | 0 | 4484400 | 301977 | 7043630.4 | 12253207.68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 592264798.85 | 497139930.206 | 1089404729.056 | 88931162.486 | 62386908 | 52415344.46 | 0 | 500015942.8 | 279348000 | 195339.6 | 0 | 71476805.86 | 18162528 | 16472697.85 | 0
Yesterday Day Peak | 0 | 0 | 130 | 180 | 0 | 0 | 0 | 413 | 343 |  | 0 | 450 | 277 | 40 | 70 | 55 | 0 | 0 | 99 | 40 | 40 | 48 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 16 | 22 | 24 | 33 | 28 | 25 | 0 | 30 | 0 | 0 | 0 | 17 | 219 | 0 | 0 | 0 |  | 6 | 56 | 51 | 44 | 0 | 19 | 15 | 0 | 0 | 0 | 0 | 310 | 0 | 203 | 8 | 0 | 43 | 5 | 0 | 43 | 0 | 36 | 0 | 18 | 9 | 28 | 21 | 108 | 32 | 0 | 19 | 2 | 43 | 20 | 46 | 42 | 112 | 0 | 60 | 86 | 0 | 207 | 18 | 0 | 8 | 310 | 6 | 8 | 0 | 147 | 0 | 0 | 87 | 0 | 67 | 20 | 50 | 34 | 47 | 401 | 19 | 52 | 17 | 4 | 105 | 17 | 54 | 34 | 9 | 50 | 43 | 18 | 49 | 17 | 107 | 0 | 17 | 27 | 39 | 16 | 340 | 0 | 0 |  | 890 | 0 | 200 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 15 | 0 | 0 | 0 | 0 | 0 | 18 | 58 | 0 | 42 | 32 | 0 | 25 | 19 | 0 | 8 | 0 | 0 | 250 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 196 | 0 | 0 | 36 | 0 | 35 | 0 | 35 | 0 | 6 | 35 | 950 | 224 | 0 | 17 | 4 | 91 | 35 | 0 | 0 | 0 | 32 | 160 | 0 | 126 |  | 10493 | DayPeak
Yesterday Evening Peak | 0 | 0 | 130 | 180 | 0 | 0 | 0 | 391 | 342 | 0 | 0 | 450 | 284 | 58 | 80 | 55 | 0 | 0 | 0 | 58 | 58 | 115 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 22 | 22 | 24 | 33 | 28 | 50 | 0 | 30 | 0 | 0 | 0 | 25 | 227 | 0 | 0 | 0 | 0 | 6 | 69 | 85 | 61 | 0 | 19 | 12 | 0 | 0 | 0 | 0 | 280 | 0 | 182 | 8 | 0 | 20 | 5 | 0 | 51 | 0 | 34 | 8 | 15 | 9 | 33 | 21 | 110 | 49 | 0 | 19 | 0 | 42 | 42 | 39 | 40 | 112 | 0 | 62 | 86 | 0 | 211 | 18 | 0 | 8 | 300 | 8 | 8 | 0 | 245 | 0 | 0 | 97 | 0 | 91 | 0 | 100 | 100 | 150 | 368 | 56 | 88 | 51 | 0 | 238 | 17 | 54 | 80 | 87 | 90 | 40 | 17 | 0 | 91 | 107 | 0 | 0 | 0 | 72 | 17 | 401 | 0 | 0 |  | 808 | 0 | 180 | 0 | 79 | 0 | 0 | 0 | 38 | 0 | 8 | 184 | 20 | 0 | 0 | 0 | 0 | 32 | 27 | 86 | 0 | 50 | 40 | 0 | 28 | 20 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 161 | 0 | 0 | 0 | 0 | 0 | 154 | 0 | 0 | 56 | 0 | 70 | 0 | 92 | 0 | 0 | 75 | 1112 | 222 | 0 | 116 | 0 | 0 | 94 | 0 | 0 | 0 | 0 | 199 | 0 | 0 |  | 11708 | EvPeak
Forecast for Evening | 0 | 0 | 130 | 180 | 0 | 0 | 0 | 400 | 320 | 0 | 0 | 450 | 270 | 60 | 85 | 55 | 0 | 0 | 0 | 60 | 58 | 98 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 22 | 28 | 33 | 30 | 50 | 0 | 30 | 0 | 0 | 0 | 25 | 220 | 0 | 0 | 0 | 0 | 6 | 70 | 85 | 85 | 0 | 21 | 15 | 0 | 0 | 0 | 0 | 300 | 0 | 190 | 8 | 0 | 30 | 5 | 0 | 51 | 0 | 33 | 8 | 17 | 9 | 33 | 20 | 153 | 80 | 0 | 19 | 0 | 42 | 42 | 51 | 50 | 0 | 0 | 62 | 86 | 0 | 225 | 19 | 0 | 8 | 300 | 8 | 8 |  | 245 | 0 | 0 | 100 | 0 | 100 | 0 | 100 | 100 | 150 | 366 | 50 | 88 | 51 | 0 | 245 | 17 | 54 | 114 | 113 | 100 | 400 | 17 | 0 | 162 | 107 | 0 | 17 |  | 72 | 17 | 400 |  |  |  | 901 | 0 | 400 |  | 99 | 0 | 0 | 0 | 47 | 40 | 24 | 175 | 14 | 16 | 0 | 0 | 0 | 32 | 30 | 95 | 0 | 42 | 35 | 8 | 36 | 22 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 122 | 0 | 0 | 55 | 0 | 70 | 50 | 92 | 0 | 0 | 75 | 950 | 220 |  | 100 |  |  | 115 | 0 |  | 400 |  | 200 | 0
Forecast for Day | 0 | 0 | 130 | 180 | 0 | 0 | 0 | 400 | 340 | 0 | 0 | 450 | 270 | 31 | 85 | 55 | 0 | 0 | 0 | 33 | 40 | 48 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 22 | 22 | 28 | 33 | 30 | 25 | 0 | 30 | 0 | 0 | 0 | 25 | 220 | 0 | 0 | 0 | 0 | 6 | 50 | 17 | 44 | 0 | 21 | 15 | 0 | 0 | 0 | 0 | 300 | 0 | 190 | 8 | 0 | 30 | 5 | 0 | 51 | 0 | 28 | 0 | 17 | 9 | 33 | 20 | 135 | 32 | 0 | 19 | 1.6 | 42 | 30 | 20 | 40 | 0 | 0 | 60 | 86 | 0 | 225 | 19 | 0 | 8 | 300 | 8 | 8 | 0 | 145 | 0 | 0 | 88 | 0 | 100 | 20 | 50 | 34 | 46 | 366 | 12 | 52 | 17 | 5 | 100 | 17 | 54 | 17 | 9 | 50 | 400 | 17 | 50 | 17 | 107 | 0 | 17 | 30 | 18 | 17 | 380 |  |  |  | 901 | 0 | 370 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 14 | 0 | 0 | 0 | 0 | 0 | 16 | 40 | 0 | 42 | 32 | 0 | 26 | 22 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122 | 0 | 0 | 35 | 0 | 35 | 0 | 49 | 0 | 8 | 35 | 820 | 220 |  | 17 | 6 | 100 | 35 | 0 |  | 400 | 30 | 150 |  | 130 |  |  |  |  | g | h | o | c | h | t | s
Generation at 08:00(Today) | 0 | 0 | 130 | 180 | 0 | 0 | 0 | 393 | 348 | 0 | 0 | 450 | 250 | 33 | 78 | 55 | 0 | 0 | 0 | 33 | 24 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 22 | 27 | 33 | 15 | 25 | 0 | 30 | 0 | 0 | 0 | 17 | 227 | 0 | 0 | 0 | 0 | 6 | 32 | 0 | 33 | 0 | 19 | 12 | 0 | 0 | 0 | 0 | 280 | 0 | 182 | 8 | 0 | 30 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 9 | 7 | 21 | 86 | 44 | 0 | 16 | 1 | 41 | 43 | 5 | 5 | 80 | 0 | 40 | 5 | 0 | 212 | 19 | 0 | 8 | 265 | 8 | 8 | 0 | 65 | 0 | 0 | 48 | 0 | 72 | 8 | 38 | 34 | 40 | 366 | 9 | 35 | 34 | 1 | 16 | 17 | 54 | 17 | 9 | 38 | 370 | 17 | 14 | 17 | 107 | 0 | 17 | 8 | 18 | 17 | 378 | 0 | 0 | 0 | 765 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 16 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118 | 0 | 0 | 0 | 0 | 35 | 0 | 34 | 0 | 1 | 35 | 650 | 167 | 0 | 0 | 1 | 15 | 0 | 0 | 0 | 361 | 8 | 151 | 0 | 41 | 0 |  |  |  | 132.3868 | 20.7956 | 43.4979 | 37.417 | 0.72348 | 2.5296 | 2.3968
239.7473
| Minimum Generation |  | 7905 | 5:00
| Highest Generation |  | 11708 | 19:00
| Day Peak Generation |  | 10493 | 12:00
| Evening Peak Generation |  | 11708 | 19:00
| HVDC Max Flow |  | 893 | 2:00
| HVDC EvPeak Flow |  | 808 | 19:00
| Load factor L.F |  | 85.32% | [161 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2023-02-28
Till now the maximum generation is : - |  |  |  | 14782 | 21:00 | Hrs on | 2022-04-16
The Summary of Yesterday's |  |  | 2023-02-27 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 10493 | MW Hour : | 12:00 | Min. Gen. at | 4:00 | 8381
Evening Peak Generation : |  |  | 11708 | MW Hour : | 19:00 | Available Max Generation : |  | 12821
E.P. Demand (at gen end) : |  |  | 11795 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 11800
Maximum Generation : |  |  | 11708 | MW Hour : | 19:00 | Reserve(Generation end) |  | 1021
Total Gen. (MKWH) : |  |  | 239.7473 | System Load Factor : | 85.32% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 100 | MW at | 7:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2023-02-28
Actual : |  | 79.63 | Ft.(MSL) , | Rule curve : | 93.15 | Ft.( MSL )
Gas Consumed : |  | Total = | 1026.84 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 141346506.946
: |  |  | Coal : | 279348000 | Oil : | 571492748.66 | Total : | 992187255.606
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 0 | 0:00 | 4047.4117 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 1118.4033 |  |  | 0 | 0%
Khulna Area |  | 0 | 0:00 | 1469.8011 |  |  | 0 | 0%
Rajshahi Area |  | 0 | 0:00 | 1296.3347 |  |  | 0 | 0%
Cumilla Area |  | 0 | 0:00 | 1107.0207 |  |  | 0 | 0%
Mymensingh Area |  | 80 | 1920:00 | 909.6507 |  |  | 0 | 0%
Sylhet Area |  | 0 | 0:00 | 411.3395 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 331.6075 |  |  | 0 | 0%
Rangpur Area |  | 0 | 0:00 | 718.2807 |  |  | 0 | 0%
Total |  | 80 |  | 11409.85 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 2
2) Ghorasal-3,7
3) Ashuganj-5
4) Baghabari-100 MW & 71 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
7) Shajibazar 330 MW
8) Sirajganj-1&2
9) Kushiara 163 MW
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
8:01 | 17:17 | Mirpur 132/33kV S/S Reserve Bus Scheduled S/D Due to Aminbazar ckt-2 DS 114 changing work.
8:21 | 13:09 | Juldah-Shahmirpur 132kV Ckt-1 Scheduled S/D from Juldah 132/33kV end Due to S/D and from Shahmirpur 132/33kV end Due to
Annual Maintenance.
8:25 | 15:43 | Chandraghona-Rangamati 132 kV Ckt-1 Scheduled S/D from Rangamati 132/33kV end Due to Annual Maintenance in Chandraghona
end and from Chandraghona 132/33kV end Due to Annual Maintenance.
8:26 | 20:45 | Kabirpur -Kodda 132kV Ckt-2 Scheduled S/D from Kabirpur 132/33kV end Due to Kadda ckt-2 shutdown due conductor restringing
work between tower no 26 & 27.
9:13 | 17:34 | Hasnabad-Shyampur 230kV Ckt-1 Scheduled S/D from Shyampur 230/132kV end Due to CT replacement at hasnabad end and from
Hasnabad 230/132kV end Due to New CT Installation.
9:35 | 17:50 | Baroirhat 132/33kV S/S TR-1, 406T LT Scheduled S/D Due to 33 kv U clamp change.
9:35 | 14:36 | Cumilla(N)-Cumilla(S) 132 kV Ckt-1 Scheduled S/D from Cumilla(S) 132/33kV end Due to Annual Maintenance from Cumilla(N) End.
9:37 | 17:48 | Baroirhat 132/33kV S/S TR-1, 406T HT Scheduled S/D Due to 33 kv U clamp change.
9:43 | 12:18 | Feni-PHP 132kV Ckt-1 Scheduled S/D from Feni 132/33kV end Due to S/D taken by SPMD for AMS-2022.
10:20 | 17:20 | KSRM 132/33kV S/S Transformer-02 HT Scheduled S/D Due to cleaning purpose.
10:22 | 17:04 | Aminbazar-Manikgonj PP 132kV Ckt-1 Scheduled S/D from Aminbazar 400/230/132kV end Due to Hot spot maintenance.
10:51 | 14:18 | Fenchuganj-Kulaura 132 kV Ckt-1 Scheduled S/D from Kulaura 132/33kV end Due to LA change work in Fenchuganj s/s. and from
Fenchuganj 230/132/33kV end Due to Due to LA Replace.
11:00 | 14:33 | Madanganj 132/33kV S/S Madanganj-Fatullah 132KV Ckt Scheduled S/D. | [5 empty] | 16.0MW load interrup.
12:27 | 13:56 | Baroirhat-Feni 132 kV Ckt-2 Scheduled S/D from Baroirhat 132/33kV end Due to Relay test at feni end . and from Feni 132/33kV
end Due to S/D taken by AE/NLDC/SPMD for AMS-2022.
- | 15:38 | Kallyanpur 132/33kV S/S GT-1 (132kV) HT is restored.
15:48 | - | Aminbazar 400/230/132kV S/S 132 kv Bus 02 Scheduled S/D.
- | 17:02 | Hathazari 230/132/33kV S/S MT-03 LT is restored.
- | 17:14 | Bhandaria 132/33kV S/S Transformer-2 HT is restored.
- | 17:15 | Bhandaria 132/33kV S/S Transformer-2 LT is restored.
- | 17:17 | Aminbazar-Mirpur 132kV Ckt-2 is restored.
17:25 | - | Load of Uttara 132/33kV SS was shifted to Mirpur 132/33kV SS.
21:31 | - | Sirajgonj Unit-1 was shutdown due to gas shortage (DCT of Bheramara 410 MW).
- | 22:58 | Bibiyana South 400 MW ST was sync.
- | 4:29 | Rampal U-1 sync.
5:40 | - | Pabna- Shahjadpur 132kV Ckt-1 Forced S/D from Pabna 132/33kV end Due to Ishwardi-Bheramara Line load control.
7:16 | - | Kallyanpur 132/33kV S/S GT-2 (132kV) LT Scheduled S/D.
7:16 | - | Kallyanpur 132/33kV S/S GT-2 (132kV) HT Scheduled S/D Due to 33kv UGC testing work & 33kv BKR maintenance.
7:28 | - | Bhandaria 132/33kV S/S Transformer-1 LT Project Work S/D Due to Project work.
7:29 | - | Kabirpur -Kodda 132kV Ckt-2 Scheduled S/D from Kabirpur 132/33kV end Due to Conductor restriking Between 26,27 no. tower.
7:30 | - | Bhandaria 132/33kV S/S Transformer-1 HT Project Work S/D Due to Project work.
7:37 | - | Khulshi-Madunaghat 132kV Ckt-2 Project Work S/D from Khulshi 132/33kV end Due to In Order to paint at the tower.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2023-02-27 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 130 | 3117125
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4378500
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 391 | 9615360 | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 342 | 7988000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 8941500
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 58 | 849600 | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 284 | 6645411 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 80 | 891262 | Fuel shortage
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 55 | 926397
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 385668
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 880000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 58 | 847680 | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 58 | 862848 | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 35 | 160200 | Fuel shortage
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 115 | 1075680 | Fuel shortage
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 35 | 297950 | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 306991 | Fuel shortage
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 46 | 1085640 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 826100
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 28 | 683900 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 50 | 506400 | 0:00
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 245 | 2571818 | Fuel shortage
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Fuel shortage
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 0 | 0 | Fuel shortage
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Fuel shortage
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 91 | 1256260 | Fuel shortage
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 88 | 1068499 | Fuel shortage
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 17 | 427200 | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 91 | 731520 | Fuel shortage
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 186073
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 430560 | Fuel shortage
| Dhaka area Total |  |  |  | 5847 | 3034 | 57944142
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 25 | 279975
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 137970
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 463680 | Fuel shortage
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 30 | 723480 | Low water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 227 | 5024542
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 51 | 729309 | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 69 | 568944 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 85 | 635944 | Engine problem
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 61 | 996960 | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 100 | 1264320
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 12 | 304560 | Gas shortage
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 0 | 22080
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 26879
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 238 | 2629527 | Fuel shortage
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 17 | 452685 | Fuel shortage
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 54 | 1326467 | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 90 | 1186560
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 107 | 2565545 | Engine problem
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Chattogram area Total |  |  |  | 2382 | 1185 | 19339427
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 182 | 4561000 | FGMO
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 280 | 7434900 | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint.
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 401 | 8300200
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 20 | 868248 | Gas shortage
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 5 | 287040 | Gas shortage
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 234181 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1053527
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 150 | 1659345
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 34 | 282192 | Engine problem
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 100 | 1147680 | Fuel shortage
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 15 | 399708 | Engine problem
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 9 | 243720 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 110 | 2529600
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 785400
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 8 | 78235 | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 21 | 479260 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Fuel shortage
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 80 | 660060 | Fuel shortage
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 87 | 708960 | Fuel shortage
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 0 | 251640 | Engine problem
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 72 | 827520 | Fuel shortage
| Cumilla Area Total |  |  |  | 3285 | 1666 | 32792416
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 49 | 1249920 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 413856 | Engine problem
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 12650
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 97 | 1699200 | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 56 | 584400 | Fuel shortage
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 320020
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 124080 | Engine problem
| Mymensingh Area Total |  |  |  | 614 | 227 | 4404126
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 42 | 1000000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 42 | 770400 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 112 | 2425663 | ST under maint.
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 39 | 851400 | Gas shortage
| Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 40 | 953496 | Gas shortage
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 8 | 192384 | Engine problem
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 62 | 1321344
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 86 | 1741440
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 211 | 5159170 | Machine problem
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 440000
| Sylhet 50MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Gas shortage
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 8 | 173856 | Gas shortage
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7030000 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 368 | 8954000 | FGMO
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 8 | 189180 | Engine problem
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 40 | 1317700 | ST Sync. Process on
| Sylhet Area Total |  |  |  | 2427 | 1384 | 32520033
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Fuel shortage
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 808 | 20795636
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 79 | 1266240 | Fuel shortage
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 38 | 71040 | Line O/L
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel conservation
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Line O/L
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 180 | 5046624 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 8 | 169500 | Fuel shortage
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Fuel shortage
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 56 | 927840 | Fuel shortage
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Line O/L
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 600480
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 0 | 0 | 0 | On test.
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 660*2 | 617 | 0 | 0 | Line O/L
| Khulna Area Total |  |  |  | 3001 | 1169 | 28877360
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Fuel shortage
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 20 | 393400 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 184 | 4450297
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1112 | 27655900 | Transformer O/L
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 222 | 5010027
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 116 | 606000 | Transformer O/L
| Barisal 307 MW |  | BCPCL | 307*1 | 307 | 199 | 4058200 | Transformer O/L
| Barisal Area Total |  |  |  | 2265 | 1853 | 42173824
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 32 | 341440 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 27 | 209824 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contract Expired
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 50 | 521980
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 40 | 305682 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 161 | 3742236 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 154 | 4323691 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 0 | 0 | Under maint.
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 28 | 225116 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 20 | 451200
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 239958
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 86 | 588928 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Fuel shortage
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 70 | 1085376 | Fuel shortage
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 75 | 942336 | Fuel shortage
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 26700
| Adani Power Jharkhanda Ltd |  | Import | 0 | 0 | 0 | 0 | On test.
| Rajshahi Area Total |  |  |  | 2129 | 754 | 13004467
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 250 | 5702900 | Machine problem
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 92 | 1103212 | Fuel shortage
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 42056
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 94 | 799296 | Fuel shortage
| Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 206980
| Teesta Solar Limited |  | BPCL | 16*12.5 | 0 | 0 | 837040
| Rangpur Area Total |  |  |  | 750 | 436 | 8691484
| Total |  |  |  | 22700 | 11708 | 239747279
| Eastern Grid Total |  |  |  | 14555 | 7496 | 147000144
| Western Grid Total |  |  |  | 8145 | 4212 | 92747135
| National Grid Total |  |  |  | 22700 | 11708 | 239747279
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2023-02-27
| (a) ENTIRE EASTERN GRID : |  | 7586.7 | MW | (b) ENTIRE WESTERN GRID : |  | 3618.3 | MW
| i) Dhaka area |  | 4213.2 | MW | i) Khulna area |  | 1327.6 | MW
| ii) Chittagong area |  | 1109.5 | MW | ii) Rajshahi area |  | 1221 | MW
| iii) Comilla area |  | 955 | MW | iii) Barisal area |  | 293.7 | MW
| iv) Mymensingh area |  | 927 | MW | iv) Rangpur area |  | 776 | MW
| v) Sylhet area |  | 382 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 11205 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 4 | 11:00 | Chhatak | 20 | 20:00 | Kamrangirchar | 51 | 17:00 | Natore | 116 | 19:00 | Shitalakhya | 116 | 15:00
2 | AKSML | 14 | 21:00 | Chowmuhani | 141 | 19:00 | Kaptai | 3.5 | 18:30 | Nawabganj | 31.4 | 21:00 | Sholosohor | 28 | 15:00
3 | Aftabnagar | 30 | 18:30 | Chuadanga | 77 | 19:00 | Kazla | 82 | 13:00 | Netrakona | 112 | 09:00 | Shyampur | 132 | 00:00
4 | Agargaon | 62 | 13:00 | Coxsbazar | 94 | 18:30 | Keranigonj | 60 | 19:00 | New | 65.2 | 12:00 | Siddhirganj | 104 | 13:00
5 | Agrabad | 56 | 19:00 | Cumilla(N) | 133 | 18:30 | Khagrachori | 24 | 18:30 | Niamatpur | 104 | 19:30 | Sirajganj | 86 | 19:00
6 | Amnura | 44 | 19:00 | Cumilla(S) | 124 | 14:00 | Khulna | 98 | 19:00 | Noapara | 38 | 20:00 | Sonargaon | 109 | 12:00
7 | Ashuganj | 54 | 23:00 | Daudkandi | 108 | 21:00 | Khulshi | 157 | 18:30 | PHP | 9 | 18:00 | Sreemongol | 45 | 19:30
8 | BIPTC | N/A | N/A | Dhaka | 36 | 13:00 | Kishoreganj | 120 | 20:00 | Pabna | 83 | 19:00 | Srinagar | 31.52 | 21:00
9 | BSRM | 111 | 01:00 | Dhamrai | 100 | 16:00 | Kodda | 266 | 18:00 | Palashbari | 110 | 08:00 | Sunamganj | 36 | 18:30
10 | Bagerhat | 85 | 18:30 | Dhanmondi | 115 | 13:00 | Kulaura | 28 | 18:30 | Panchagarh | 52 | 18:30 | Sylhet | 102 | 18:30
11 | Bakulia | 79 | 19:00 | Dohazari | 82 | 19:30 | Kurigram | 58 | 18:30 | Patuakhali | 68 | 21:00 | TK | 21 | 18:30
12 | Banani | 40 | 13:00 | Faridpur | 109 | 19:00 | Kushtia | 100 | 19:00 | Payra | 11.2 | 19:00 | Tangail | 201 | 19:30
13 | Bangabhaban | 17 | 10:00 | Fatullah | 60 | 12:00 | Lalbag | 70 | 12:00 | Postogola | 34 | 13:00 | Thakurgaon | 74 | 19:00
14 | Barapukuria | 53 | 13:00 | Fenchuganj | 30 | 18:30 | Lalmonirhat | 42 | 19:00 | Purbachal | 17 | 18:30 | Tongi | 105 | 21:00
15 | Barguna | 14 | 19:00 | Feni | 99 | 18:30 | Madanganj | 28 | 23:00 | Purbasadipur | 107 | 19:00 | Ullon | 39 | 18:30
16 | Barishal | 76 | 13:00 | GPH | 88 | 20:00 | Madaripur | 74 | 20:00 | Rahanpur_I | 16.2 | 22:00 | Uttara | 66 | 18:00
17 | Barishal-230 | 64 | 18:30 | Ghorashal | 52 | 19:00 | Madartek | 59 | 19:30 | Rahim | 34 | 14:00 | UttaraNew | 16 | 15:00
18 | Baroaulia | 47 | 17:00 | Goalpara | 22 | 19:00 | Madunaghat | 45 | 18:30 | Rajbari | 50 | 18:30 | Zigatola | 64 | 13:00
19 | Baroirhat | 42 | 18:30 | Gollamari | 32 | 18:30 | Magura | 54 | 19:00 | Rajendrapur | 94 | 18:30
20 | Bashundhara | 134 | 18:30 | Gopalganj | 81.6 | 19:00 | Mahasthangarh | 56 | 07:00 | Rajshahi | 107 | 19:30
21 | BashundharaCement | 13 | 11:00 | Gulshan | 94 | 15:00 | Manikganj | 93 | 19:00 | Rajshahi-230 | 28 | 19:00
22 | Beanibazar | 42 | 18:00 | Halishahar | 86.5 | 15:00 | Maniknagar | 59 | 13:00 | Ramganj | 80 | 18:30
23 | Benapole | 52 | 19:00 | HaripurSBU | 144 | 14:00 | Matarbari | 36 | 18:30 | Rampur | 23 | 18:30
24 | Bhaluka | 110 | 09:00 | Hasnabad | 70 | 14:00 | Matuail | 62 | 12:00 | Rangamati | 12 | 18:30
25 | Bhandaria | 35 | 22:00 | Hathazari | 50 | 19:00 | Millgate | 70 | 16:00 | Rangpur | 118 | 19:00
26 | Bhangura | 32 | 08:00 | Ishurdi | 57 | 19:00 | Mirpur | 111.5 | 18:30 | Ruppur | 4.4 | 15:00
27 | Bheramara(GK) | 46 | 18:30 | Jaldhaka | 58 | 19:00 | Mirsorai | 2 | 02:00 | SSM | 0 | 00:00
28 | Bhulta | 242 | 12:00 | Jamalpur | 130 | 21:00 | Mithapukur | 32 | 07:00 | Saidpur | 108 | 12:00
29 | Bog-Sherpur | 68 | 07:00 | Jashore | 116 | 19:00 | Modern | 0 | 00:00 | Satkhira | 104 | 19:00
30 | Bogura | 126 | 19:00 | Jhenaidah | 98 | 18:30 | Mogbazar | 111 | 15:00 | Satmasjid | 70 | 13:00
31 | Borhanuddin | 35 | 21:00 | Joydebpur | 145 | 16:00 | Mongla | 18 | 00:00 | Savar | 164 | 12:00
32 | Brahmanbaria | 130 | 20:00 | Joypurhat | 61 | 19:30 | Motijheel | 30 | 13:00 | Shahjadpur | 93 | 08:00
33 | Cantonment | 108 | 19:00 | Juldah | 26 | 00:00 | Munshiganj | 75 | 19:00 | Shahjibazar | 85 | 19:00
34 | Chandpur | 45 | 19:30 | KSRM | 14 | 16:00 | Mymensingh | 183 | 18:30 | Shahmirpur | 33.2 | 03:00
35 | Chandraghona | 24 | 19:00 | Kabirpur | 280 | 12:00 | Naogaon | 110 | 08:00 | Shariatpur | 50 | 20:00
36 | Chapai | 65 | 07:00 | Kachua | 62 | 18:30 | Narail | 44 | 18:30 | Sherpur | 134 | 22:00
37 | Charsaidpur | 45 | 00:00 | Kallyanpur | 84 | 18:30 | Narinda | 58 | 13:00 | Shikalbaha | 25 | 02:00
38 | Chauddagram | 35 | 18:30 | Kalurghat | 32 | 12:00 | Narshingdi | 147 | 19:30 | Shikalbaha-230 | N/A | N/A
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2023-02-27 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 407 | 05:00 | 390 | 15:00 | Kaliakoir | N/A | N/A | N/A | N/A
| Bhulta | 396 | 00:00 | 385 | 12:00 | Madunaghat_I | 418 | 13:00 | 398 | 15:00
| Bibiana | 409 | 06:00 | 398 | 12:00 | Payra | 417 | 05:00 | 409 | 16:00
| BIPTC | 401 | 03:00 | 392 | 11:00 | Rahanpur_I | 421 | 16:00 | 392 | 10:00
| Gopalganj | 419 | 05:00 | 391 | 15:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 236 | 06:00 | 226 | 12:00 | Hasnabad | 237 | 05:00 | 224 | 12:00
| AKSML | 243 | 19:00 | 218 | 02:00 | Hathazari | 243 | 19:00 | 230 | 05:00
| Aminbazar | 237 | 05:00 | 228 | 15:00 | Ishurdi | 237 | 05:00 | 228 | 12:00
| Ashuganj | 242 | 00:00 | 232 | 12:00 | Jhenaidah | 238 | 05:00 | 224 | 13:00
| Baghabari | 233 | 01:00 | 225 | 12:00 | Kaliakoir | N/A | N/A | N/A | N/A
| Barapukuria | 226 | 20:00 | 211 | 07:00 | Keranigonj | 235 | 05:00 | 225 | 12:00
| Barishal | 239 | 00:00 | 233 | 13:00 | Khulna(S) | 240 | 05:00 | 228 | 12:00
| Bheramara | 234 | 05:00 | 224 | 12:00 | Madunaghat_I | 242 | 13:00 | 230 | 02:00
| Bhulta | 238 | 06:00 | 229 | 12:00 | Maniknagar | 235 | 05:00 | 226 | 12:00
| Bibiana | 242 | 19:30 | 235 | 12:00 | Meghnaghat | 242 | 04:00 | 234 | 12:00
| BIPTC | 238 | 05:00 | 226 | 12:00 | Mirsorai | 239 | 18:00 | 228 | 15:00
| Bogura | 230 | 18:00 | 217 | 08:00 | Rajshahi | 238 | 18:00 | 228 | 07:00
| Borhanuddin | 246 | 01:00 | 224 | 15:00 | Rampur | N/A | N/A | N/A | N/A
| BSRM | 241 | 19:00 | 228 | 16:00 | Rampura | 236 | 04:00 | 233 | 09:00
| Cumilla(N) | 237 | 19:00 | 229 | 15:00 | Shikalbaha | 240 | 18:00 | 230 | 03:00
| Fenchuganj | 244 | 08:00 | 239 | 16:00 | Shyampur | 236 | 06:00 | 227 | 12:00
| Ghorashal | N/A | N/A | N/A | N/A | Siddhirganj | 237 | 04:00 | 229 | 12:00
| GPH | 240 | 22:00 | 229 | 16:00 | Sirajgonj | 231 | 02:00 | 224 | 07:00
| Haripur | 235 | 03:00 | 227 | 12:00 | Tongi | 230 | 7:00 | 218 | 16:00
| 132 kV | KV |  | KV
| Aftabnagar | 136 | 05:00 | 128 | 12:00 | Lalbag | 137 | 06:00 | 129 | 12:00
| Agargaon | 137 | 05:00 | 130 | 12:00 | Lalmonirhat | 130 | 17:00 | 126 | 01:00
| Agrabad | 139 | 19:00 | 131 | 15:00 | Madanganj | 137 | 07:00 | 132 | 11:00
| AKS | 136 | 17:00 | 131 | 15:00 | Madaripur | 137 | 00:00 | 130 | 12:00
| Aminbazar | 136 | 01:00 | 130 | 15:00 | Madartek | 136 | 06:00 | 129 | 12:00
| Amnura | 132 | 10:00 | 125 | 07:00 | Madunaghat | 140 | 19:00 | 133 | 03:00
| Ashuganj | 140 | 00:00 | 135 | 12:00 | Magura | 137 | 04:00 | 128 | 12:00
| Bagerhat | 137 | 00:00 | 127 | 18:30 | Mahasthangarh | 132 | 18:00 | 121 | 07:00
| Bakulia | 138 | 09:00 | 132 | 15:00 | Manikganj | 138 | 08:00 | 120 | 11:00
| Banani | 136 | 06:00 | 123 | 15:00 | Maniknagar | 136 | 06:00 | 128 | 13:00
| Bangabhaban | 136 | 08:00 | 129 | 12:00 | Matarbari | 137 | 14:00 | 123 | 02:00
| Barapukuria | 133 | 19:30 | 122 | 07:00 | Matuail | 136.7 | 08:00 | 131.8 | 12:00
| Barguna | 134 | 19:30 | 127 | 12:00 | Millgate | 136 | 04:00 | 124 | 15:00
| Barishal | 136 | 03:00 | 131 | 12:00 | Mirpur | 139 | 20:00 | 127 | 16:00
| Barishal-230 | 137 | 05:00 | 132 | 12:00 | Mithapukur | 133 | 20:00 | 120 | 07:00
| Baroaulia | 140 | 17:00 | 134 | 15:00 | Modern | 139 | 22:00 | 132 | 14:00
| Baroirhat | 138 | 19:00 | 130 | 03:00 | Mogbazar | 138 | 05:00 | 130 | 12:00
| Bashundhara | 135 | 04:00 | 125 | 12:00 | Mongla | 137 | 22:00 | 128 | 12:00
| BashundharaCement | 137 | 07:00 | 132 | 12:00 | Motijheel | 135 | 00:00 | 129 | 12:00
| Beanibazar | 136 | 04:00 | 133 | 11:00 | Munshiganj | 137 | 07:00 | 132 | 14:00
| Benapole | 135 | 04:00 | 125 | 12:00 | Mymensingh | 134 | 23:00 | 112 | 12:00
| Bhaluka | 128 | 00:00 | 108 | 13:00 | Naogaon | 128 | 03:00 | 115 | 07:00
| Bhandaria | 137 | 06:00 | 130 | 12:00 | Narail | 137 | 03:00 | 125 | 18:30
| Bhangura | 139 | 03:00 | 132 | 12:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bheramara | 137 | 05:00 | 132 | 12:00 | Narshingdi | 135 | 08:00 | 127 | 12:00
| Bheramara(GK) | 139 | 00:00 | 135 | 13:00 | Natore | 133 | 18:00 | 126 | 07:00
| Bhulta | 129 | 18:00 | 122 | 12:00 | Nawabganj | 136 | 04:00 | 128 | 12:00
| Bog-Sherpur | 134 | 02:00 | 124 | 07:00 | Netrakona | 132 | 00:00 | 110 | 15:00
| Bogura | 135 | 18:00 | 124 | 07:00 | New | 135 | 00:00 | 126 | 09:00
| Bogura-230 | 135 | 20:00 | 125 | 08:00 | Niamatpur | 126 | 18:00 | 108 | 07:00
| Brahmanbaria | 136 | 00:00 | 130 | 12:00 | Noapara | 137 | 02:00 | 128 | 12:00
| Cantonment | 137 | 06:00 | 130 | 12:00 | Pabna | 138 | 10:00 | 131 | 12:00
| Chandpur | 141 | 19:00 | 127 | 15:00 | Palashbari | 130 | 23:00 | 116 | 07:00
| Chandraghona | 141 | 19:00 | 133 | 03:00 | Panchagarh | 133 | 19:30 | 112 | 07:00
| Chapai | 133 | 18:00 | 127 | 07:00 | Patuakhali | 134 | 19:30 | 126 | 23:00
| Charsaidpur | 138 | 07:00 | 132 | 15:00 | Payra | 131 | 00:00 | 128 | 11:00
| Chauddagram | 140 | 19:00 | 130 | 14:00 | PHP | 138 | 19:30 | 130 | 03:00
| Chhatak | 135 | 04:00 | 133 | 12:00 | Postogola | 136 | 09:00 | 130 | 12:00
| Chowmuhani | 139 | 19:30 | 126 | 15:00 | Purbachal | 137 | 01:00 | 128 | 16:00
| Chuadanga | 134 | 06:00 | 124 | 18:30 | Purbasadipur | 131 | 19:30 | 112 | 07:00
| Coxsbazar | 133 | 13:00 | 122 | 01:00 | Rahim | 137 | 00:00 | 133 | 12:00
| Cumilla(N) | 140 | 19:00 | 132 | 15:00 | Rajbari | 136 | 05:00 | 129 | 12:00
| Cumilla(S) | 139 | 07:00 | 129 | 15:00 | Rajendrapur | 138 | 21:00 | 127 | 15:00
| Daudkandi | 136 | 08:00 | 129 | 15:00 | Rajshahi | 133 | 17:00 | 126 | 07:00
| Dhaka | 137 | 07:00 | 129 | 12:00 | Rajshahi-230 | 133 | 17:00 | 126 | 07:00
| Dhamrai | 136 | 00:00 | 127 | 12:00 | Ramganj | 139 | 22:00 | 125 | 14:00
| Dhanmondi | 138 | 06:00 | 131.7 | 14:00 | Rampur | 138 | 18:00 | 131 | 02:00
| Dohazari | 138 | 13:00 | 128 | 01:00 | Rampura | 136 | 04:00 | 128 | 15:00
| Faridpur | 135 | 02:00 | 130 | 12:00 | Rangamati | 141 | 22:00 | 132 | 15:00
| Fatullah | 137 | 06:00 | 131 | 12:00 | Rangpur | 133 | 05:00 | 121 | 07:00
| Fenchuganj | 138 | 00:00 | 136 | 04:00 | Ruppur | 138 | 00:00 | 132 | 11:00
| Feni | 140 | 19:00 | 130 | 12:00 | Saidpur | 131 | 20:00 | 112 | 07:00
| Ghorashal | 142 | 00:00 | 136 | 13:00 | Satkhira | 137 | 05:00 | 128 | 12:00
| Goalpara | 139 | 22:00 | 130 | 12:00 | Satmasjid | 137 | 06:00 | 130 | 13:00
| Gollamari | 135 | 05:00 | 128 | 12:00 | Savar | 137 | 19:30 | 128 | 01:00
| Gopalganj | 136 | 05:00 | 127 | 12:00 | Shahjadpur | 141 | 02:00 | 134 | 07:00
| Gopalganj-400 | 136 | 05:00 | 132 | 11:00 | Shahjibazar | 137 | 01:00 | 134 | 00:00
| Gulshan | 136 | 07:00 | 128 | 12:00 | Shahmirpur | 139 | 19:00 | 131 | 03:00
| Halishahar | 139 | 19:00 | 132 | 02:00 | Shariatpur | 136 | 04:00 | 129 | 15:00
| Haripur | 137 | 00:00 | 133 | 12:00 | Sherpur | 131 | 23:00 | 112 | 17:00
| HaripurSBU | 138 | 06:00 | 132 | 16:00 | Shikalbaha | 141 | 19:00 | 132 | 03:00
| Hasnabad | 136 | 07:00 | 130 | 12:00 | Shikalbaha-230 | 139 | 18:30 | 132 | 03:00
| Hathazari | 142 | 19:00 | 135 | 05:00 | Shitalakhya | 137 | 07:00 | 131 | 12:00
| Ishurdi | 137 | 01:00 | 133 | 12:00 | Sholosohor | 140 | 19:00 | 132 | 02:00
| Jaldhaka | 130 | 20:00 | 115 | 07:00 | Shyampur | 137 | 06:00 | 130 | 11:00
| Jamalpur | 134 | 23:00 | 116 | 17:00 | Shyampur-230 | 137 | 08:00 | 130 | 12:00
| Jashore | 134 | 18:00 | 125 | 12:00 | Siddhirganj | 137 | 07:00 | 132 | 12:00
| Jhenaidah | 139 | 05:00 | 130 | 12:00 | Sirajganj | 136 | 01:00 | 125 | 07:00
| Jhenaidah-230 | 138 | 05:00 | 129 | 12:00 | Sonargaon | 137 | 18:00 | 132 | 09:00
| Joydebpur | 141 | 00:00 | 135 | 15:00 | Sreemongol | 136 | 09:00 | 133 | 11:00
| Joypurhat | 126 | 01:00 | 112 | 07:00 | Srinagar | 136 | 08:00 | 128 | 15:00
| Juldah | 138 | 13:00 | 132 | 15:00 | SSM | 142 | 17:00 | 137 | 15:00
| Kabirpur | 138 | 21:00 | 121 | 12:00 | Sunamganj | 135 | 03:00 | 131 | 11:00
| Kachua | 142 | 19:00 | 128 | 15:00 | Sylhet | 135 | 00:00 | 133 | 12:00
| Kaliakoir | N/A | N/A | N/A | N/A | Tangail | 136 | 23:00 | 124 | 15:00
| Kallyanpur | 136 | 19:30 | 130 | 12:00 | Thakurgaon | 133 | 19:30 | 110 | 07:00
| Kalurghat | 139 | 00:00 | 132 | 03:00 | TK | 139 | 13:00 | 134 | 14:00
| Kamrangirchar | 135 | 02:00 | 128 | 12:00 | Tongi | 136 | 00:00 | 127 | 15:00
| Kaptai | 140 | 00:00 | 135 | 08:00 | Ullon | 136 | 05:00 | 128 | 14:00
| Kazla | 136 | 07:00 | 128 | 13:00 | Uttara | 136 | 05:00 | 124 | 15:00
| Keranigonj | 136 | 05:00 | 128 | 12:00 | UttaraNew | 137 | 19:30 | 128 | 12:00
| Khagrachori | 139 | 19:00 | 132 | 15:00 | Zigatola | 136 | 07:00 | 128 | 13:00
| Khulna | 138 | 17:00 | 130 | 12:00
| Khulna(S) | 139 | 05:00 | 130 | 12:00
| Khulshi | 138 | 19:00 | 131 | 15:00
| Kishoreganj | 134 | 00:00 | 120 | 15:00
| Kodda | 140 | 19:00 | 128 | 16:00
| KSRM | 140 | 19:00 | 133 | 15:00
| Kulaura | 138 | 00:00 | 135 | 15:00
| Kurigram | 131 | 20:00 | 117 | 07:00
| Kushtia | 138 | 03:00 | 131 | 12:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2023-02-27
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 292 | 6324 | 3421 | 9745 |  |  |  | QF-LDC-11
0:30 | 482 | 5823 | 3484 | 9307 | Date: | 2023-02-27
1:00 | 672 | 5322 | 3547 | 8869
1:30 | 717 | 5183.5 | 3469 | 8652.5
2:00 | 762 | 5045 | 3391 | 8436
2:30 | 787 | 4957 | 3357 | 8314 | [5 empty] | Gen. at Eve. Peak | 11708 | 11708 MW (19:00 )
3:00 | 812 | 4869 | 3323 | 8192 | [6 empty] | 19:00
3:30 | 801 | 4833.5 | 3262.5 | 8096 | [5 empty] | Gen. at Day Peak | 10493 | 10493 MW (12:00 )
4:00 | 790 | 4798 | 3202 | 8000 | [6 empty] | 12:00
4:30 | 777 | 4790 | 3162.5 | 7952.5 | [5 empty] | Highest Generation | 11708
5:00 | 764 | 4782 | 3123 | 7905 | [6 empty] | 19:00
5:30 | 729 | 4887.5 | 3174 | 8061.5
6:00 | 694 | 4993 | 3225 | 8218
6:30 | 397 | 5242 | 3342.5 | 8584.5
7:00 | 100 | 5491 | 3460 | 8951
7:30 | 140 | 5588.5 | 3559.5 | 9148
8:00 | 180 | 5686 | 3659 | 9345
8:30 | 324 | 5849 | 3683.5 | 9532.5
9:00 | 468 | 6012 | 3708 | 9720
9:30 | 584 | 6074.5 | 3715.5 | 9790
10:00 | 700 | 6137 | 3723 | 9860
10:30 | 760 | 6203 | 3763 | 9966
11:00 | 820 | 6269 | 3803 | 10072
11:30 | 815 | 6407 | 3875.5 | 10282.5
12:00 | 810 | 6545 | 3948 | 10493
12:30 | 790 | 6540.5 | 4032.5 | 10573
13:00 | 770 | 6536 | 4117 | 10653
13:30 | 885 | 6411.5 | 4092.5 | 10504
14:00 | 1000 | 6287 | 4068 | 10355
14:30 | 1045 | 6301.5 | 4052.5 | 10354
15:00 | 1090 | 6316 | 4037 | 10353
15:30 | 1080 | 6331 | 3993 | 10324
16:00 | 1070 | 6346 | 3949 | 10295
16:30 | 1035 | 6248 | 3910.5 | 10158.5
17:00 | 1000 | 6150 | 3872 | 10022
17:30 | 713 | 6308.5 | 3908 | 10216.5
18:00 | 426 | 6467 | 3944 | 10411
18:30 | 278 | 6981.5 | 4078 | 11059.5
19:00 | 130 | 7496 | 4212 | 11708
19:30 | 160 | 7386 | 4170 | 11556
20:00 | 170 | 7221 | 4066 | 11287 |  |  |  | Executive Engineer
20:30 | 160 | 7208.5 | 4042 | 11250.5 |  |  |  | Network Operation Division
21:00 | 150 | 7196 | 4018 | 11214
21:30 | 205 | 7055.5 | 3932 | 10987.5
22:00 | 260 | 6915 | 3846 | 10761 |  |  |  |  | Page 6 of 7
22:30 | 275 | 6804.5 | 3774.5 | 10579
23:00 | 290 | 6694 | 3703 | 10397
23:30 | 291 | 6509 | 3562 | 10071
24:00 | 292 | 6324 | 3421 | 9745
11708 MW (19:00 )
10493 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2023-02-27 |  | Energy |  | 239747279
[13 empty] | 2023-02-27 |  |  |  |  | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 3525 | 881 | 1818 | 0 | 1870 | 1471 | 30 | 0 | 48 | 102 | 0 | 0
0:30 | 3586.5 | 886.5 | 1788 | 0 | 1410 | 1481 | 30 | 0 | 24 | 101 | 0 | 0 | Date: | 2023-02-27
1:00 | 3648 | 892 | 1758 | 0 | 950 | 1491 | 30 | 0 | 0 | 100 | 0 | 0
1:30 | 3651 | 892.5 | 1779 | 0 | 767 | 1436 | 30 | 0 | 0 | 97 | 0 | 0 | [7 empty] | Total Energy | 239.7473 | Total Energy Gen 239.747 MKWHr Energy Not Served 1.121 MKWHr Energy Requirement 240.868 MKWHr
2:00 | 3654 | 893 | 1800 | 0 | 584 | 1381 | 30 | 0 | 0 | 94 | 0 | 0 | [7 empty] | Energy not Served | 1.1206
2:30 | 3636.5 | 893 | 1768 | 0 | 511.5 | 1381 | 30 | 0 | 0 | 94 | 0 | 0 | [7 empty] | Energy Requirement | 240.8678
3:00 | 3619 | 893 | 1736 | 0 | 439 | 1381 | 30 | 0 | 0 | 94 | 0 | 0
3:30 | 3655.5 | 893 | 1672 | 0 | 421 | 1330.5 | 30 | 0 | 0 | 94 | 0 | 0 | [5 empty] | Shortage
4:00 | 3692 | 893 | 1608 | 0 | 403 | 1280 | 30 | 0 | 0 | 94 | 0 | 0
4:30 | 3705 | 891 | 1562 | 0 | 404.5 | 1270 | 30 | 0 | 0 | 90 | 0 | 0
5:00 | 3718 | 889 | 1516 | 0 | 406 | 1260 | 30 | 0 | 0 | 86 | 0 | 0
5:30 | 3691.5 | 889 | 1588.5 | 0 | 471 | 1289.5 | 30 | 0 | 16 | 86 | 0 | 0
6:00 | 3665 | 889 | 1661 | 0 | 536 | 1319 | 30 | 0 | 32 | 86 | 0 | 0
6:30 | 3684 | 842.5 | 1760.5 | 0 | 782.5 | 1354.5 | 30 | 0 | 36 | 85 | 9.5 | 52.5298 |  |  |  | Coal
7:00 | 3703 | 796 | 1860 | 0 | 1029 | 1390 | 30 | 0 | 40 | 84 | 19 | 105.0596
7:30 | 3684 | 783.5 | 1867.5 | 0 | 1132.5 | 1451 | 30 | 0 | 48 | 92 | 59.5 | 135.4715 |  |  | Oil |  |  |  | ,
8:00 | 3665 | 771 | 1875 | 0 | 1236 | 1512 | 30 | 0 | 56 | 100 | 100 | 165.8835
8:30 | 3642.5 | 771 | 1857 | 0 | 1380 | 1521.5 | 30 | 0 | 86 | 99 | 145.5 | 129.0205
9:00 | 3620 | 771 | 1839 | 0 | 1524 | 1531 | 30 | 0 | 116 | 98 | 191 | 92.1575
9:30 | 3611 | 830 | 1837 | 0 | 1555.5 | 1465.5 | 30 | 0 | 123 | 102 | 236 | 80.177
10:00 | 3602 | 889 | 1835 | 0 | 1587 | 1400 | 30 | 0 | 130 | 106 | 281 | 68.1966
10:30 | 3658.5 | 889 | 1839 | 0 | 1608 | 1375 | 30 | 0 | 151.5 | 106 | 309 | 70.5005
11:00 | 3715 | 889 | 1843 | 0 | 1629 | 1350 | 30 | 0 | 173 | 106 | 337 | 72.8044
11:30 | 3743.5 | 889.5 | 1915.5 | 0 | 1644.5 | 1355 | 30 | 0 | 248.5 | 107 | 349 | 36.4022
12:00 | 3772 | 890 | 1988 | 0 | 1660 | 1360 | 30 | 0 | 324 | 108 | 361 | 0
12:30 | 3711 | 889.5 | 1994.5 | 0 | 1681.5 | 1436 | 30 | 0 | 361 | 110 | 359.5 | 0
13:00 | 3650 | 889 | 2001 | 0 | 1703 | 1512 | 30 | 0 | 398 | 112 | 358 | 0
13:30 | 3650 | 889 | 2001 | 0 | 1703 | 1512 | 30 | 0 | 398 | 112 | 358 | 0
14:00 | 3650 | 889 | 2001 | 0 | 1703 | 1512 | 30 | 0 | 398 | 112 | 358 | 0
14:30 | 3589 | 889 | 1997 | 0 | 1702 | 1492 | 30 | 0 | 389 | 114 | 301 | 31
15:00 | 3528 | 889 | 1993 | 0 | 1701 | 1472 | 30 | 0 | 380 | 116 | 244 | 62
15:30 | 3543.5 | 888.5 | 1958 | 0 | 1729 | 1482 | 30 | 0 | 385 | 117 | 191 | 98
16:00 | 3559 | 888 | 1923 | 0 | 1757 | 1492 | 30 | 0 | 390 | 118 | 138 | 134
16:30 | 3514 | 888.5 | 1827.5 | 0 | 1830.5 | 1465.5 | 30 | 0 | 398 | 111 | 93.5 | 147.5
17:00 | 3469 | 889 | 1732 | 0 | 1904 | 1439 | 30 | 0 | 406 | 104 | 49 | 161
17:30 | 3440.5 | 884.5 | 1721.5 | 0 | 2141.5 | 1415 | 30 | 0 | 450.5 | 108.5 | 24.5 | 164
18:00 | 3412 | 880 | 1711 | 0 | 2379 | 1391 | 30 | 0 | 495 | 113 | 0 | 167
18:30 | 3499.5 | 844 | 1849 | 0 | 2725 | 1476 | 30 | 0 | 524.5 | 111.5 | 0 | 123.5885
19:00 | 3587 | 808 | 1987 | 0 | 3071 | 1561 | 30 | 0 | 554 | 110 | 0 | 80.177
19:30 | 3586 | 738 | 1941 | 0 | 3139 | 1673 | 30 | 0 | 329 | 120 | 0 | 57.5984
20:00 | 3612 | 738 | 1948 | 0 | 2976 | 1682 | 30 | 0 | 189 | 112 | 0 | 35.0198
20:30 | 3645 | 773.5 | 1964.5 | 0 | 2873 | 1688 | 30 | 0 | 160.5 | 116 | 0 | 29.4904
21:00 | 3678 | 809 | 1981 | 0 | 2770 | 1694 | 30 | 0 | 132 | 120 | 0 | 23.961
21:30 | 3604 | 809 | 1970.5 | 0 | 2647.5 | 1694.5 | 30 | 0 | 114 | 118 | 0 | 11.9805
22:00 | 3530 | 809 | 1960 | 0 | 2525 | 1695 | 30 | 0 | 96 | 116 | 0 | 0
22:30 | 3545 | 845 | 1945 | 0 | 2382 | 1622 | 30 | 0 | 96 | 114 | 0 | 0
23:00 | 3560 | 881 | 1930 | 0 | 2239 | 1549 | 30 | 0 | 96 | 112 | 0 | 0
23:30 | 3542.5 | 881 | 1874 | 0 | 2054.5 | 1510 | 30 | 0 | 72 | 107 | 0 | 0 | Max Temp. in Dhaka |  | 32.8° C
24:00 | 3525 | 881 | 1818 | 0 | 1870 | 1471 | 30 | 0 | 48 | 102 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 239.747 MKWHr Energy Not Served 1.121 MKWHr Energy Requirement 240.868 MKWHr
Shortage
Note on W13: Author:

## Generation
g | 2023-02-27
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 723480
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [5 empty] | 0 | 6 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 18 | 25 | 25 |  | 25 | 25 | 25 |  |  |  |  | 279975
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 2 | 7 | 13 | 18 | 20 | 20 | 20 | 17 | 13 | 8 | 2 | [9 empty] | 137970
6 | Sikalbaha 225MW CCPP (Gas) | 212 | 212 | 214 | 213 | 218 | 215 | 215 | 214 | 214 | 214 | 223 | 219 | 208 | 206 | 206 | 208 | 207 | 223 |  | 227 | 226 | 226 | 225 | 228 | 227 | 226 | 5024542
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [9 empty] | 17 | 16 | 51 | 79 | 74 | 74 | 77 | 78 | 85 |  | 85 | 29 | 17 |  |  |  |  | 635944
12 | Hathazari 100 MW peaking PP | [8 empty] | 40 | 40 | 40 | 56 | 56 | 51 | 51 | 53 | 69 | 69 |  | 69 | [6 empty] | 568944
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 42 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 729309
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP | [9 empty] | 13 | 30 | 36 | 36 | 28 | 28 | 34 | 28 | 32 |  | 34 | [6 empty] | 282192
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 65 | 65 | 40 | 41 | 40 | 39 | 102 | 63 | 32 | 38 | 39 | 99 | 96 | [13 empty] | 880000
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 45 | 0 |  |  | 0 | 5 | 66 | 65 | 145 | 145 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 195 |  | 245 | 245 | 145 | 147 | 98 | 98 | 98 | 2571818
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 234181
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4 | 130 | 130 | 133 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 |  | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 3117125
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4378500
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 45 | 41 | 41 | 41 | 41 | 41 | 41 | 45 | 44 | 44 | 44 | 43 | 40 | 43 | 43 | 43 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 30 | 30 | 868248
33 | Ashuganj 225 MW CCPP | 155 | 154 | 156 | 198 | 211 | 221 | 193 | 182 | 182 | 183 | 201 | 203 | 215 | 209 | 196 | 203 | 183 | 182 |  | 182 | 182 | 182 | 182 | 182 | 181 | 182 | 4561000
34 | Ashuganj 450 MW CCPP(South)
| Ashuganj 450 MW CCPP(North) | 280 | 280 | 280 | 290 | 280 | 280 | 290 | 280 | 275 | 280 | 310 | 310 | 305 | 315 | 310 | 310 | 280 | 280 |  | 280 | 280 | 280 | 310 | 310 | 310 | 290 | 7434900
| Ashuganj 420 MW CCPP(East) | 320 | 320 | 320 | 320 | 340 | 340 | 346 | 347 | 360 | 360 | 350 | 340 | 320 | 320 | 320 | 320 | 344 | 300 |  | 401 | 401 | 401 | 401 | 375 | 380 | 360 | 8300200
35 | Ashuganj 55 MW PP (Precision) | 48 | 49 | 49 | 10 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 287040
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 396 | 396 | 397 | 397 | 397 | 396 | 356 | 398 | 399 | 407 | 410 | 413 | 412 | 401 | 397 | 408 | 389 | 345 |  | 391 | 402 | 402 | 401 | 396 | 395 | 395 | 9615360
40 | Meghnaghat 450 MW CCPP(MPL) | 180 | 225 | 250 | 250 | 260 | 400 | 400 | 420 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 380 | 380 |  | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 8941500
41 | Haripur 360MW CCPP(HPL) | 347 | 350 | 350 | 350 | 348 | 350 | 300 | 343 | 346 | 336 | 302 | 343 | 337 | 332 | 332 | 332 | 291 | 272 |  | 342 | 348 | 347 | 343 | 343 | 348 | 352 | 7988000
42 | RPCL 210MW CCPP | 73 | 74 | 74 | 73 | 74 | 35 | 35 | 32 | 32 | 32 | 32 | 32 | 31 | 31 | 32 | 32 | 32 | 33 |  | 49 | 50 | 59 | 106 | 102 | 104 | 93 | 1249920
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 0 | 2 | 12 | 24 | 38 | 45 | 49 | 49 | 42 | 33 | 18 | 5 | 0 | [8 empty] | 320020
44 | Fenchugonj CCPP Phase-1 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 41 | 41 | 42 | 43 | 43 | 43 | 42 | 42 | 42 | 42 | 43 |  | 42 | 42 | 42 | 43 | 42 | 41 | 42 | 1000000
45 | Fenchugonj CCPP Phase-2 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 20 | 20 | 22 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 43 | 43 | 43 | 43 | 770400
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 62 | 62 | 40 | 40 | 40 | 40 | 61 | 40 | 40 | 40 | 40 | 60 | 61 | 60 | 60 | 61 | 61 | 61 |  | 62 | 62 | 62 | 61 | 62 | 62 | 40 | 1321344
48 | Shahjibazar 86MW PP (Shahjibazar) | 84 | 84 | 10 | 10 | 10 | 10 | 84 | 84 | 84 | 84 | 60 | 86 | 86 | 86 | 86 | 86 | 86 | 86 |  | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 1741440
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 202 | 205 | 206 | 205 | 205 | 205 | 205 | 205 | 207 | 207 | 207 | 207 | 207 | 208 | 205 | 205 | 211 | 211 |  | 211 | 215 | 210 | 212 | 215 | 211 | 212 | 5159170
51 | Sylhet 20 MW GTPP | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 19 | 19 | 440000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 189180
54 | Hobiganj 11MW PP Cofidence-E | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 192384
55 | Fenchugonj 51 MW PP (Barakatullah) | 42 | 31 | 31 | 11 | 11 | 11 | 31 | 40 | 22 | 22 | 22 | 46 | 48 | 45 | 45 | 48 | 42 | 42 |  | 39 | 43 | 42 | 53 | 53 | 42 | 11 | 851400
56 | Shahjahanulla 25 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 6 |  |  | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 173856
57 | Bibiana-II 341 MW CCPP (Summit) | 290 | 290 | 295 | 290 | 290 | 300 | 300 | 270 | 260 | 270 | 290 | 310 | 320 | 270 | 320 | 300 | 270 | 260 |  | 300 | 256 | 260 | 280 | 290 | 270 | 270 | 7030000
| Bibiyana South 400 MW | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 50 | 40 | 43 | 40 | 43 | 42 | 50 | 15 | 25 |  | 40 | 40 | 40 | 42 | 55 | 65 | 98 | 1317700
58 | Nababganj 55 MW PP (Southern power ) |  |  |  |  | 0 | 5 | 17 | 17 | [8 empty] | 17 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 306991
59 | Tangail Palli Power Gen 22 MW | 6 | 0 |  |  | 0 | 2 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 124080
60 | Barabkunda 22 MW PP (Regent) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 13 | 15 | 15 | 15 | 15 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 304560
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 0 |  |  |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 385668
62 | Tangail 22 MW PP (Doreen) | 16 | 16 | 16 | 16 | 16 | 16 | 14 | 16 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 15 | 15 | 413856
63 | Impoprt (Tripura) | 100 | 94 | 94 | 94 | 86 | 86 | 84 | 100 | 98 | 106 | 106 | 108 | 112 | 124 | 116 | 118 | 104 | 113 |  | 110 | 120 | 112 | 120 | 116 | 112 | 102 | 2529600
64 | Malancha, Ctg. EPZ (United) |  |  |  |  | 0 | 2 | 2 | 2 | [18 empty] | 22080
65 | Feni 22MW PP (Doreen) | 19 | 19 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 15 | 15 | 15 |  | 15 | 19 | 19 | 19 | 18 | 18 | 18 | 399708
66 | Feni 11 MW PP (Doreen) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 243720
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 28 | 29 | 30 | 30 | 28 | 28 | 33 | 33 | 28 | 31 | 31 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 785400
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 479260
69 | Summit Ashulia | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 528000
70 | Summit Madhabdi | 24 | 24 | 24 | 24 | 24 | 25 | 25 | 25 | 25 | 25 | 24 | 24 | 18 | 16 | 16 | 18 | 24 | 24 |  | 24 | 24 | 24 | 24 | 26 | 26 | 26 | 557640
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 826100
72 | Rupganj 33 MW PP(Summit) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 28 | 28 | 28 | 27 | 21 | 21 | 28 | 28 | 28 |  | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 683900
73 | Ghorashal 108MW PP (Regent)
| Feni Lanka Power | 34 | 0 |  |  | 0 | 17 | 17 | 17 | 17 | 17 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 67 |  | 80 | 77 | 50 | 17 | 17 | 17 | 17 | 660060
| Chowmuhani 113 MW | 9 | 0 |  |  | 0 | 3 | 9 | 9 | 9 | 9 | 8 | 9 | 9 | 9 | 9 | 9 | 9 | 33 |  | 87 | 115 | 114 | 116 | 115 | 78 | 39 | 708960
| Manikgonj 162MW PP(MPGL) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 91 | 162 | 162 | 129 | 32 | 17 | 17 | 731520
77 | Siddhirganj 100 PP(Dutch Bangla) | 40 | 0 |  |  | 0 | 3 | 22 | 33 | 33 | 35 | 40 | 40 | 40 | 40 | 45 | 58 | 58 | 58 |  | 58 | 58 | 58 | 60 | 60 | 60 | 60 | 847680
78 | Gazipur 52 MW PP | [5 empty] | 0 | 8 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 40 | 41 |  | 50 | 50 | 25 | 25 | 25 | 25 | 8 | 506400
79 | Kodda 150MW PP |  |  |  |  | 0 | 32 | 32 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 75 |  | 115 | 100 | 100 | 100 | 64 | 64 | 48 | 1075680
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | [16 empty] | 3 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 78235
| Gazipur 100 MW PP | 32 | 0 |  |  | 0 | 2 | 35 | 35 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 71 |  | 88 | 88 | 88 | 88 | 50 | 35 | 35 | 1068499
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 0 | 1 | 2 | 3 | 4 | 4 | 4 | 3 | 2 | 1 | 0 | [9 empty] | 26879
| Jodiac Power | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 452685
| Karnaphuli Power Ltd. | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1326467
82 | Madanganj 102 PP(Summit) | [5 empty] | 0 | 36 | 63 | 62 | 62 | 62 | 70 | 78 | 80 | 80 | 66 | 80 | 80 |  | 80 | 56 | 50 |  |  |  |  | 891262
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP ( Summit) | 274 | 279 | 283 | 282 | 280 | 269 | 286 | 268 | 262 | 265 | 278 | 277 | 280 | 277 | 282 | 280 | 276 | 274 |  | 284 | 270 | 275 | 280 | 282 | 268 | 248 | 6645411
87 | Meghnaghat 100 MW(IEL) | 29 | 0 |  |  |  | 0 | 11 | 31 | 33 | 33 | 34 | 40 | 42 | 41 | 41 | 57 | 59 | 57 |  | 58 | 58 | 58 | 53 | 58 | 57 | 59 | 849600
| Meghnaghat 104 MW PP (OPCL) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 17 |  | 17 | 17 | 17 | 17 | 17 | 18 | 17 | 427200
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 22 | 0 |  |  | 0 | 22 | 22 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 55 | 72 |  | 61 | 62 | 71 | 85 | 85 | 85 | 72 | 996960
92 | Fenchuganj 44MW (Energyprima) | 50 | 50 | 30 | 10 | 10 | 10 | 40 | 40 | 40 | 40 | 40 | 42 | 48 | 48 | 45 | 48 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 50 | 50 | 953496
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 10 | 10 | 10 | 27 | 51 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1053527
94 | Gagnagar 102 MW PP (Digital Power) | 24 | 0 |  |  | 0 | 24 | 24 | 24 | 40 | 40 | 40 | 40 | 40 | 41 | 50 | 50 | 50 | 50 |  | 58 | 58 | 58 | 58 | 58 | 50 | 24 | 862848
95 | Patenga 50MW PP (Baraka) | 19 | 19 | 19 | 19 | 20 | 20 | 20 | 21 | 20 | 19 | 19 | 19 | 19 | 17 | 18 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 463680
96 | Chattogram 108 MW PP (ECPV) | [19 empty] | 0 | [6 empty] | 0
97 | katpotti 52 MW
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 30 | 0 |  |  |  | 0 | 40 | 55 | 55 | 55 | 45 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 40 | 30 | 30 | 30 | 30 | 926397
100 | Manikganj 55 MW PP (Northern) | [9 empty] | 7 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 |  | 35 | 35 | 35 | 35 | 24 | 17 |  | 297950
101 | Kushiara 163 MW CCPP (KP) | 112 | 112 | 112 | 112 | 80 | 80 | 112 | 80 | 80 | 80 | 112 | 112 | 112 | 80 | 112 | 112 | 80 | 80 |  | 112 | 112 | 112 | 112 | 80 | 80 | 80 | 2425663
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 1 | 1 | 0 | [9 empty] | 12650
103 | Kamalaghat 54 MW PP(Banco Energy) | [15 empty] | 17 | 17 | 17 |  | 35 | 35 | 35 | 17 | 17 |  |  | 160200
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 86 | 86 | 88 | 87 | 88 | 88 | 49 | 49 | 58 | 76 |  | 97 | 97 | 97 | 98 | 98 | 98 | 98 | 1699200
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 34 | 17 | 0 |  | 0 | 2 | 17 | 17 | 51 | 73 | 68 | 67 | 71 | 71 | 62 | 53 | 53 | 66 |  | 91 | 99 | 99 | 98 | 82 | 71 | 67 | 1256260
115 | Juldah 100 MW PP Unit-3 (Acorn) | 25 | 25 | 0 |  | 0 | 12 | 25 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 70 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1264320
116 | Chandpur 200MW (Desh energy) | 34 | 34 | 0 |  | 0 | 5 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 36 | 74 |  | 100 | 100 | 100 | 100 | 100 | 100 | 34 | 1147680
117 | Ashuganj 150MW PP (Midland) | 46 | 46 | 48 | 46 | 48 | 46 | 43 | 40 | 47 | 48 | 47 | 47 | 47 | 42 | 46 | 55 | 83 | 120 |  | 150 | 150 | 150 | 150 | 150 | 61 | 30 | 1659345
118 | Bibiyana-III 400 MW CCPP | 367 | 367 | 365 | 374 | 366 | 366 | 366 | 366 | 366 | 367 | 398 | 401 | 367 | 371 | 369 | 370 | 369 | 368 |  | 368 | 368 | 368 | 367 | 367 | 367 | 365 | 8954000
| Jamalpur 115 MW PP (United) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 19 | 19 | 23 | 19 | 25 | 19 | 18 | 18 | 9 | 9 |  | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 584400
| Anwara 300 MW PP (United) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 100 | 105 | 105 | 105 | 105 | 103 | 105 | 105 | 105 | 105 |  | 238 | 240 | 248 | 249 | 250 | 249 | 249 | 2629527
| Juldah unit-2 (Acorn) | 25 | 0 |  |  | 0 | 9 | 25 | 35 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 57 |  | 90 | 90 | 90 | 100 | 100 | 100 | 100 | 1186560
| Anlima Energy Ltd. | 107 | 107 | 107 | 107 | 107 | 89 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 |  | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 2565545
| Bhairob 54.5 MW | [6 empty] | 0 | 12 | 17 | 17 | 12 | 17 | 17 | 17 | 17 | 17 | 17 |  |  |  |  | 1 | 17 | 17 | 17 | 17 | 251640
| Spectra Solar Plant Ltd. | [5 empty] | 0 | 2 | 7 | 16 | 23 | 25 | 27 | 29 | 24 | 20 | 9 | 4 | 0 | [8 empty] | 186073
| Chandpur 115(Doreen) | 18 | 18 | 17 | 18 | 18 | 18 | 18 | 18 | 17 | 18 | 24 | 39 | 40 | 19 | 18 | 18 | 27 | 72 |  | 72 | 72 | 72 | 72 | 72 | 69 | 24 | 827520
| Kanchan Purbachal Power Generation Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 16 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 430560
| Mirsharai 150 MW (Oil) | [26 empty] | 0
Mirsharai 150 MW (Gas)
120 | Eastern Zone Total | 5322 | 5045 | 4869 | 4798 | 4782 | 4993 | 5491 | 5686 | 6012 | 6137 | 6269 | 6545 | 6536 | 6287 | 6316 | 6346 | 6150 | 6467 |  | 7496 | 7386 | 7221 | 7196 | 6915 | 6694 | 6324 | 147000144
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | 16 | 0 |  |  | 0 | 11 | 49 | 49 | 49 | 66 | 49 | 49 | 63 | 78 | 62 | 77 | 77 | 79 |  | 79 | 80 | 80 | 97 | 97 | 97 | 98 | 1266240
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [17 empty] | 25 |  | 38 | 47 | [5 empty] | 71040
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 38 | 35 | 0 |  | 0 | 3 | 13 | 36 | 36 | 36 | 36 | 36 | 38 | 56 | 56 | 56 | 56 | 56 |  | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 927840
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 0 | 5 | 24 | 47 | 69 | 84 | 91 | 88 | 80 | 62 | 36 | 12 | [9 empty] | 600480
131 | Rampal 1320 MW (BIFPCL)
132 | United Payra Power Ltd. | [5 empty] | 0 | 10 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 35 | 35 | 35 |  | 116 | 116 | 100 | 17 | 17 |  |  | 606000
133 | Bhola Nutan Biddut BD LTD (GAS) | 224 | 224 | 223 | 224 | 164 | 165 | 224 | 224 | 196 | 190 | 190 | 224 | 222 | 222 | 222 | 170 | 170 | 170 |  | 222 | 222 | 222 | 222 | 222 | 222 | 160 | 5010027
Bhola Nutan Biddut BD LTD (OIL)
Barisal 110 MW PP (Summit )
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW | 159 | 159 | 159 | 160 | 160 | 159 | 160 | 160 | 159 | 160 | 160 | 160 | 170 | 170 | 170 | 170 | 169 | 171 |  | 199 | 201 | 200 | 200 | 201 | 149 | 151 | 4058200
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 187 | 187 | 187 | 189 | 189 | 189 | 189 | 185 | 180 | 177 | 180 | 180 | 180 | 179 | 177 | 179 | 172 | 183 |  | 184 | 165 | 186 | 186 | 187 | 187 | 187 | 4450297
140 | Bhola 33 MW PP (Venture) | 18 | 17 | 16 | 15 | 14 | 15 | 15 | 14 | 14 | 14 | 15 | 15 | 16 | 15 | 17 | 16 | 15 | 16 |  | 20 | 20 | 20 | 21 | 20 | 20 | 18 | 393400
141 | Noapara 100 MW PP (Bangla Trac) | [26 empty] | 0
142 | Noapara 40 MW PP (Khanjahan Ali) | [17 empty] | 8 |  | 8 | 32 | 32 | 32 | 32 | 32 | 32 | 169500
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 892 | 893 | 893 | 893 | 889 | 889 | 796 | 771 | 771 | 889 | 889 | 890 | 889 | 890 | 889 | 888 | 889 | 880 |  | 808 | 738 | 738 | 809 | 809 | 881 | 881 | 20795636
147 | Bheramara 410 MW CCPP | 205 | 210 | 215 | 220 | 220 | 230 | 235 | 235 | 230 | 225 | 215 | 200 | 195 | 190 | 190 | 190 | 190 | 185 |  | 180 | 180 | 180 | 185 | 190 | 200 | 210 | 5046624
148 | Payra 1320 MW | 1132 | 1022 | 1022 | 920 | 900 | 920 | 980 | 1102 | 1122 | 990 | 940 | 950 | 1092 | 1030 | 1052 | 1072 | 1020 | 970 |  | 1112 | 1222 | 1232 | 1244 | 1244 | 1200 | 1120 | 27655900
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 200 | 200 | 200 | 200 | 200 | 240 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 |  | 250 | 250 | 250 | 250 | 250 | 200 | 200 | 5702900
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [12 empty] | 32 | 32 | 32 | 24 | 32 | 32 |  | 32 | 32 | 32 | 32 | 32 | 32 | 0 | 341440
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 0 | 1 | 2 | 3 | 4 | 4 | 3 | 3 | 2 | 2 | 0 | [9 empty] | 26700
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 169 | 170 | 170 | 176 | 181 | 172 | 175 | 177 | 174 | 157 | 185 | 180 | 160 | 162 | 163 | 161 | 161 | 161 |  | 161 | 160 | 160 | 142 |  |  |  | 3742236
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 170 | 171 | 172 | 176 | 177 | 178 | 178 | 184 | 180 | 160 | 180 | 196 | 180 | 167 | 162 | 162 | 160 | 159 |  | 154 | 154 | 155 | 155 | 158 | 162 | 157 | 4323691
Sirajgonj 225MW CCPP Unit-3 (Oil)
Sirajgonj 400 MW CCPP Unit-4
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [8 empty] | 4 | 4 | 15 | 18 | 23 | 23 | 23 | 30 | 23 | 23 |  | 27 | 28 | [5 empty] | 209824
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 20 | 18 | 18 | 18 | 18 | 18 | 21 | 20 | 20 | 19 | 18 | 18 | 18 | 17 | 18 | 19 |  | 20 | 22 | 22 | 22 | 22 | 22 | 21 | 451200
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 239958
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | [5 empty] | 0 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 |  | 50 | [6 empty] | 521980
167 | Katakhali 50 MW Peaking PP | [8 empty] | 16 |  | 16 | 32 | 32 | 32 | 32 | 32 | 36 | 40 |  | 40 | 40 | [5 empty] | 305682
168 | Santahar 50 MW Peaking PP | [11 empty] | 25 | 28 | 28 | 28 | 28 | 28 | 28 |  | 28 | 28 | 15 |  |  |  |  | 225116
169 | Natore 52 MW PP (Rajlanka) | [26 empty] | 0
170 | Chapainawabganj 100 MW Peaking PP | [5 empty] | 0 | 8 | 8 | 8 | 8 | 8 | 58 | 64 | 64 | 64 | 64 | 64 | 86 |  | 86 | 25 | 25 |  |  |  |  | 588928
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 35 | 35 | 0 |  | 0 | 5 | 33 | 35 | 35 | 35 | 35 | 35 | 39 | 50 | 50 | 50 | 53 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 35 | 1085376
172 | Confidence Power Bogura Unit-1 113 MW | 35 | 35 | 35 | 0 |  | 0 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 75 |  | 75 | 75 | 75 | 75 | 75 | 35 | 35 | 942336
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 34 | 0 |  |  | 0 | 20 | 26 | 34 | 34 | 43 | 42 | 35 | 35 | 49 | 49 | 56 | 92 | 92 |  | 92 | 92 | 92 | 78 | 78 | 72 | 49 | 1103212
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 2 | 4 | 5 | 6 | 6 | 6 | 5 | 3 | 2 | [9 empty] | 42056
178 | Energypac Power Venture Thakurgaon Ltd. | [10 empty] | 35 | 35 | 35 | 35 | 36 | 36 | 36 | 78 |  | 94 | 104 | 113 | 114 | 75 | 55 |  | 799296
| Intraco Solar 30 MW | [5 empty] | 0 | 1 | 8 | 17 | 24 | 30 | 32 | 32 | 29 | 17 | 15 | 5 | 0 | [8 empty] | 206980
Adani Power Jharkhanda Ltd
178 | Teesta Solar Limited | [5 empty] | 0 | 7 | 38 | 67 | 97 | 118 | 126 | 125 | 108 | 89 | 45 | 19 | 0 | [8 empty] | 837040