## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID COMPANY OF BANGLADESH LTD.
SYSTEM OPERATION DATA
Month:January 2023
Sl. | Items | Current Month |  | Previous Month |  | This Month Last Year |  | Max. Till-to-date
|  | 2023-01-01 |  | 2022-12-01 |  | 2022-01-01
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 10330 | 2023-01-30 | 10346 | 2022-12-01 | 10021 | 2022-01-25 | 14782 | 2022-04-16
|  |  | 19:00 |  | 18:00 |  | 19:00 |  | 21:00
2 | Minimum Generation (MW) | 5671 | 2023-01-07 | 5506 | 2022-12-17 | 5475 | 2022-01-08 | - | -
|  |  | 6:00 |  | 6:00 |  | 6:00 |  | -
3 | Maximum Evening Peak Generation (MW) | 10330 | 2023-01-30 | 10346 | 2022-12-01 | 10021 | 2022-01-25 | 14782 | 2022-04-16
|  |  | 19:00 |  | 18:00 |  | 19:00 |  | 21:00
4 | Maximum Day Peak Generation (MW) | 9332 | 2023-01-29 | 9246 | 2022-12-01 | 8945 | 2022-01-30 | 12895 | 2022-04-26
|  |  | 12:00 |  | 12:00 |  | 12:00 |  | 12:00
5 | Maximum Evening Peak Demand (MW) Estimated | 10496 | 2023-01-30 | 10550 | 2022-12-31 | 10021 | 2022-01-25 | 14782 | 2022-04-16
|  |  | 19:00 |  | 19:00 |  | 12:00 |  | 12:00
6 | Average Generation (MW) at Evening Peak | 9608.0645 |  | 9584.8065 |  | 9483.1935 |  | 13536.33 | 2022-04-27
7 | Average Generation (MW) at Day Peak | 8465.7742 |  | 8308.3226 |  | 8138.6774 |  | 11233.4 | 2022-04-27
8 | Maximum Power Import from India, BIPTC (MW) | 927 | 2023-01-01 | 934 | 2022-12-18 | 768 | 2022-01-31 | 956 | 27/3/2019
|  |  | 18:00 |  | 10:00 |  | 200:00 |  | 19:00
9 | Maximum Power Import from Tripura, India (MW) | 136 | 2023-01-28 | 122 | 2022-12-01 | 136 | 2022-01-26 | 194 | 12/06/19
|  |  | 18:00 |  | 18:00 |  | 18:30 |  | 19:00
10 | Maximum Load Shed (MW) at Evening Peak | 952 | 2023-01-09 | 188 | 2022-12-01 | - | - | 4395 | 04/10/2021
|  |  | 20:00 |  | 18:00 |  | - |  | 21:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | 8939 | 2023-01-09 | 10346 | 2022-12-01 | - | - | 13792 | 2021-04-27
|  | - | 20:00 | - | 18:00 | - | - |  | 20:00
12 | Minimum Load Shed (MW) at Evening Peak | 0 | 2023-01-07 | 0 | 2022-12-02 | - | -
|  |  | 19:30 |  | 18:00
13 | Generation During Min. Load Shed (MW) at Evening Peak | 9795 | 2023-01-07 | 8976 | 2022-12-02 | - | -
|  |  | 19:30 |  | 18:00
14 | Maximum Load Shed (MW) at Day Peak | 944 | 2023-01-09 | 52 | 2022-12-01 | - | -
|  |  | 12:00 |  | 12:00
15 | Generation During Max. Load Shed (MW) at Day Peak | 7776 | 2023-01-09 | 9246 | 2022-12-01 | - | -
|  |  | 12:00 |  | 12:00
16 | Minimum Load Shed (MW) at Day Peak | 0 | 2023-01-07 | 0 | 2022-12-02 | - | -
|  |  | 12:00 |  | 12:00
17 | Generation During Min. Load Shed (MW) at Day Peak | 7958 | 2023-01-07 | 8089 | 2022-12-02 | - | -
|  |  | 12:00 |  | 12:00
18 | Nos. of Days Load Shed at Evening Peak | 22 |  | 2 |  | -
19 | Nos. of Days Load Shed at Day Peak | 22 |  | 1 |  | -
20 | Gross Generation of BPDB (MKWH) | 1441.7073 |  | 1409.473 |  | 1181.174 |  | 3805.72 | 2019-09-19
21 | Station Use of BPDB (MKWH) | 47.6227 |  | 53.265 |  | 67.0345
22 | Net Generation of BPDB (MKWH) | 1394.0845 |  | 1356.208 |  | 1114.1395
23 | Net Generation of IPP (MKWH) | 3451.6051 |  | 3151.7645 |  | 3576.4276
24 | Net Generation of REB (MKWH) | 122.7522 |  | 135.1789 |  | 117.4558
24 | Net Generation of Rental Power Plant (MKWH) | 264.3287 |  | 277.2375 |  | 409.5082
25 | Total Net Generation (MKHWh) (BPDB, IPP, RPP & REB) | 5232.7705 |  | 4920.3889 |  | 5217.5311 |  | 7842.9924 | April'22
26 | Energy Generation by Gas (MKWH) | 3400.0318 |  | 3396.0047 |  | 2951.4743 |  | 4756.96 | Sep-19
27 | Energy Generation by Diesel (MKWH) | 52.972 |  | 33.738 |  | 221.4774 |  | 771.52 | July-18
28 | Energy Generation by Furnace Oil (MKWH) | 946.5709 |  | 1031.992 |  | 1606.076 |  | 2365.7466 | April'22
29 | Energy Generation by Hydro (MKWH) | 22.1863 |  | 32.3793 |  | 70.6636 |  | 104.66 | Sep-22
30 | Energy Generation by Solar (MKWH) | 29.9075 |  | 33.1894 |  | 27.2583 |  | 40.58 | March-22
31 | Energy Generation by Coal (MKWH) | 828.7249 |  | 446.3504 |  | 407.6161 |  | 950.96 | Sep'22
32 | Enegry Import from India (BIPTC & AC) (MKWH) | 647.0711 |  | 653.3183 |  | 535.5104 |  | 776.67 | August-22
33 | Monthly Load Factor (%) | 87.0884 |  | 85.1421 |  | 78.0725 |  | 92.62 | August-22

## QF-LDC-22
Page: 1/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month:November 2022
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quantity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 10330 | 2023-01-30 | 19:00
Generation Period
| Dhaka | MW | 3644.9
| Chattogram | MW | 995
| Cumilla | MW | 854
| Mymensingh | MW | 769
| Sylhet | MW | 358
a) | Total supply in East zone | MW | 6620.9
| Khulna | MW | 1158.4
| Barisal | MW | 245
| Rajshahi | MW | 1051.6
| Rangpur | MW | 774
b) | Total supply in West zone | MW | 3229
c) | Total supply in both zone ( a+b) | MW | 9849.9
Ref: | 27.21.0000.603.16.087.20.588 | Date: 20/12/2022
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
Page: 2/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month:January 2023
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Daily Maximum power Export through EWI/ NO-1
| a) Ghorashal end | AMPS | 640 | 2023-01-01 | 2:00
| b) Ishurdi end | MW | 400 | 2023-01-16 | 14:00
18 | Daily Maximum power Import through EWI/ NO-1
| a) Ghorashal end | AMPS | 1300 | 2023-01-29 | 12:00
| b) Ishurdi end | MW | 338 | 2023-01-09 | 24':00
19 | Daily Maximum Energy Export through EWI/NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
20 | Daily Maximum Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
21 | Total Energy Export through EWI/ NO-1
| a) Ghorashal end | MKWH | 0.82591
| b) Ishurdi end | MKWH | 105.37
22 | Total Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | -
| b) Ishurdi end | MKWH | -
23 | Transmission loss of EWI/ NO-1 | % | 3
24 | Daily Maximum power Export through EWI/ NO-2
| a) Ashuganj end | MW | 230 | 2023-01-08 | 08':00
| b)Serajganj end | MW | 516 | 2023-01-31 | 14':00
25 | Daily Maximum power Import through EWI/ NO-2
| a) Ashuganj end | MW | 450 | 2023-01-16 | 14':00
| b)Sirajganj end | MW | 230 | 2023-01-08 | 08':00
26 | Daily Maximum Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH
| b)Sirajganj end | MKWH | - | -
27 | Daily Maximum Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | - | -
| b)Sirajganj end | MKWH
28 | Total Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 1.544
| b)Sirajganj end | MKWH | 1.27
29 | Total Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | 123.594
| b)Sirajganj end | MKWH | 0.79
30 | Transmission loss of EWI /NO-2 | % | 3.947
* Total energy export from Ghorasal end and import from Ishurdi end and the transmission loss of EWI/NO-1 is taken
from the calculation of GMD, PGCB, Ishwardi.
* *Total energy export from Ashuganj end and import from Sirajganj end and the transmission loss of EWI/NO-2 is taken
from the calculation of Sirajganj switching sub station.
* **The energy meter of Ghorasal end is out of order.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-23
Page: 1/3 | [8 empty] | QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: January2023
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Manikganj | 132/33 kV transformer GT-4(50/75) LT | 2023-01-01 14:24 | 2023-01-01 16:08 | 1:44 | E/O | Due to Emergency maint.work | 0 | 0 | No interruption
| 132/33 kV transformer GT-4(50/75) HT | 2023-01-01 14:25 | 2023-01-01 16:05 | 1:40 | E/O |  | 0 | 0 | No interruption
Kaliakoir | 400/230 kV25 MVAR Shunt Reactor-1 | 2023-01-08 14:25 | 2023-01-08 14:25 | 0:00 | E/O | Due to Emergency maint.work | 0 | 0 | No interruption
| 400/230 kV25 MVAR Shunt Reactor-2 | 2023-01-08 14:27 | 2023-01-08 14:27 | 0:00 | E/O |  | 0 | 0 | No interruption
Kabirpur | Kabirpur 132/33kV S/S XFR, T-3 LT | 2023-01-09 05:21 | 2023-01-09 05:21 | 0:00 | T | Tripped showing TR-03 33 KV relays. | 0 | 0 | No interruption
| Kabirpur 132/33kV S/S XFR, T-3 HT | 2023-01-09 08:07 | 2023-01-09 14:54 | 6:47 | T | Due to Emergency maint.work at 33 kV side | 0 | 0 | No interruption
Savar | 132/33 kV transformer T-3 LT | 2023-01-17 09:36 | 2023-01-17 09:48 | 0:12 | T | Due to 33 kV feeder fault | 0 | 0 | No interruption
Jamalpur | 132/33 kV transformer T-3 LT & HT | 2023-01-17 12:03 | 2023-01-17 14:15 | 2:12 | E/O | Due to red-hot maint. | 10 | 22 | Power interruption
Netrakona | 132/33 kV transformer T1 (415T) HT | 2023-01-22 10:05 | 2023-01-22 12:00 | 1:55 | E/O | Due to Oil filling | 0 | 0 | No interruption
Kishoreganj | 132/33 kV transformer T1 (404T) LT & T2 | 2023-01-22 14:43 | 2023-01-22 14:54 | 0:11 | T | Due to Ashganj -01 Tripping | 10 | 1.8333 | Power interruption
Aminbazar | 400/230/132kV S/S 230/132kv Tr-01 HT | 2023-01-24 06:28 | 2023-01-24 09:02 | 2:34 | T | Due to to Relay panel signal is general trip,diff trip relay | 0 | 0 | No interruption
| 400/230/132kV S/S 230/132kv Tr-01 LT |  | 2023-01-24 09:04 |  | T |  | 0 | 0 | No interruption
Jamalpur | 132/33 kV transformer T-4 HT | 2023-01-29 10:04 | 2023-01-29 17:22 | 7:18 | E/O | Due to Oil leakage. | 0 | 0 | No interruption
Savar | 132/33 kV transformer T-3 LT | 2023-01-30 07:56 | 2023-01-30 07:56 | 0:00 | T | Due to Aminbazar and tanary feeder trip under DPBS-3. | 0 | 0 | No interruption
Sherpur | 132/33 kV transformer T-4 (414T) LT | 2023-01-31 09:53 | 2023-01-31 09:53 | 0:00 | E/O | Due to Oil leakage. | 0 | 0 | No interruption
| 132/33 kV transformer T-4 (414T) HT | 2023-01-31 09:54 | 2023-01-31 09:54 | 0:00 | E/O | Due to Oil leakage. | 0 | 0 | No interruption
|  |  | Total : | 24:33 |  | Unserved Energy: |  | 23.8333
Dhaka (South) Grid Circle :
Keraniganj | 230/132 kV transformer ATR-2 LT & HT | 2023-01-01 08:27 | 2023-01-01 20:31 | 12:04 | T | Tripped showing Under ground cable fault | 0 | 0 | No interruption
| 230/132 kV transformer ATR-1 LT & HT | 2023-01-01 17:17 | 2023-01-02 00:38 | 7:21 | E/O | Due to Emergency maint.work | 0 | 0 | No interruption
| 230/132 kV transformer ATR-1 HT | 2023-01-01 20:45 | 2023-01-02 00:38 | 3:53 | E/O | Due to Emergency maint.work | 0 | 0 | No interruption
Siddhirganj | 132/33kV S/S 120MW EGCB GT1 | 2023-01-16 11:11 | 2023-01-16 12:16 | 1:05 | E/O | Due to Emergency maint.work | 0 | 0 | No interruption
Sonargaon | 132/33 kV transformer Tr-2 LT | 2023-01-17 09:31 | 2023-01-17 11:49 | 2:18 | E/O | Due to 33 KV langolbond feeder LA burst. | 0 | 0 | No interruption
| 132/33 kV transformer Tr-2 HT | 2023-01-17 09:31 | 2023-01-17 11:30 | 1:59 | E/O |  | 0 | 0 | No interruption
Haripur | 230/132 kV transformer ATR-1 HT | 2023-01-18 22:11 | 2023-01-18 23:08 | 0:57 | E/O | Due to red hot maintanance. | 0 | 0 | No interruption
| 230/132 kV transformer ATR-1 LT | 2023-01-18 22:11 | 2023-01-18 23:08 | 0:57 | E/O |  | 0 | 0 | No interruption
| 230/132 kV transformer ATR-1 HT | 2023-01-18 22:11 | 2023-01-18 23:09 | 0:58 | E/O | Due to red hot maintanance. | 0 | 0 | No interruption
Sonargaon | 132/33 kV transformer T-2 LT & HT | 2023-01-22 08:40 | 2023-01-22 12:15 | 3:35 | E/O | Due to Oil leakage. | 30 | 107.5 | Power interruption
| 132/33 kV transformer T-2 LT | 2023-01-22 15:06 | 2023-01-22 18:20 | 3:14 | E/O | Due to Oil leakage. | 30 | 97 | Power interruption
| 132/33 kV transformer T-1 LT | 2023-01-23 08:17 | 2023-01-23 13:20 | 5:03 | E/O | Due to Oil leakage.at 33 kV CT | 30 | 151.5 | Power interruption
Nawabganj | 132/33 kV transformer T-2 HT | 2023-01-24 16:42 | 2023-01-24 20:23 | 3:41 | T | Due to Dead Zone Fault. | 0 | 0 | No interruption
Rampura | 132 kV Busbar-2 | 2023-01-26 22:10 | 2023-01-26 22:32 | 0:22 | T | Tripped showing E/F relay | 0 | 0 | No interruption
Srinagar | 132/33 kV transformer T-1 LT | 2023-01-27 07:23 | 2023-01-27 07:23 | 0:00 | E/O | Due to Red hot maintanance. | 0 | 0 | No interruption
| 132/33 kV transformer T-1 HT | 2023-01-27 07:24 | 2023-01-27 07:24 | 0:00 | E/O |  | 0 | 0 | No interruption
Shyampur | 230/132 kV transformer APR(Do4) | 2023-01-29 05:20 | 2023-01-29 05:20 | 0:00 | T | Tripped showing relay relays Due to SOTF. | 0 | 0 | No interruption
Sonargaon | 132/33 kV transformer T-1 LT | 2023-01-29 08:24 | 2023-01-29 10:02 | 1:38 | E/O | Due to red hot maintanance. | 30 | 49 | Power interruption
|  |  | Total : | 49:05 |  | Unserved Energy: |  | 405
Page: 2/3 | [8 empty] | QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: January2023
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Chattogram Grid Circle :
Madunaghat | 132/33 kV transformer( 507)T1 LT | 2023-01-03 14:52 | 2023-01-03 14:52 | 0:00 | E/O | Due to Emergency maint.work by PDB | 0 | 0 | No interruption
| 132/33 kV transformer( 507)T1 LT | 2023-01-04 04:48 | 2023-01-04 05:57 | 1:09 | E/O | Due to 33 kV Breaker fault | 21 | 24.15 | Power interruption
Sikalbaha(O) | 132/33 kV transformers T-3 & T4 | 2023-01-04 12:42 | 2023-01-04 12:42 | 0:00 | E/O | due to CT & Yellow phase isolator burn at Sikalbaha old-ECPV | 0 | 0 | Power interruption
Khagrachari | 132/33 kV transformer TR-1 HT | 2023-01-15 11:03 | 2023-01-15 11:03 | 0:00 | T | Tripped showing relay relays Due to 132 kV Transformer Trip | 0 | 0 | No interruption
Sikalbaha(O) | 132/33 kV transformer T-4 | 2023-01-17 22:42 | 2023-01-17 23:26 | 0:44 | E/O | Due to red-hot maint.at 33 kV bside | 18 | 13.2 | Power interruption
|  |  | Total : | 1:53 |  | Unserved Energy: |  | 37.35
Cumilla Grid Circle :
Shahjibazar | 132/33 kV transformer TR-06 LT | 2022-01-04 01:37 | 2022-01-04 01:45 | 0:08 | T | Due to 33 kV feeder fault | 19 | 2.5333 | Power interruption
Chattak | 132/33 kV transformer T-3 LT | 2023-01-05 12:40 | 2023-01-05 13:10 | 0:30 | E/O | Due to Emergency maint.work | 6 | 3 | Power interruption
Daudkandi | 132/33 kV transformer TR3-LT | 2023-01-07 10:30 | 2023-01-07 14:25 | 3:55 | E/O | Due to Emergency maint.work | 20 | 78.3333 | Power interruption
| 132/33 kV transformer TR3-HT | 2023-01-07 10:30 | 2023-01-07 14:24 | 3:54 | E/O | Due to Emergency maint.work | 0 | 0 | No interruption
Cumilla(S) | 132/33 kV transformer TR2-LT | 2023-01-11 11:57 | 2023-01-11 14:55 | 2:58 | E/O | Due to Emergency maint.work | 0 | 0 | No interruption
| 132/33 kV transformer TR2-HT | 2023-01-11 11:58 | 2023-01-11 14:54 | 2:56 | E/O | Due to Emergency maint.work | 0 | 0 | No interruption
Kulaura | 132/33 kV transformer TR2-LT | 2023-01-13 19:20 | 2023-01-13 20:31 | 1:11 | T | Due to 33 kV feeder fault | 7 | 8.2833 | Power interruption
Sreemongal | 132/33 kV transformer T-3 HT | 2023-01-21 06:30 | 2023-01-21 06:40 | 0:10 | T | Tripped showing 33 kV feeder fault | 16 | 2.6667 | Power interruption
| 132/33 kV transformer T-3 LT | 2023-01-21 06:30 | 2023-01-21 06:40 | 0:10 | T | Tripped showing 33 kV feeder fault | 16 | 2.6667 | Power interruption
| 132/33 kV transformer T-2 HT | 2023-01-21 06:30 | 2023-01-21 06:40 | 0:10 | T |  | 16 | 2.6667 | Power interruption
| 132/33 kV transformer T-2 LT | 2023-01-21 08:33 | 2023-01-21 08:52 | 0:19 | T | Tripped showing O/C. relay | 0 | 0 | No interruption
Cumilla(S) | 132/33 kV transformer TR1-LT | 2023-01-22 15:39 | 2023-01-22 16:19 | 0:40 | T | Tripped showing O/C. relay | 31 | 20.6667 | Power interruption
| 132/33 kV transformer TR2-LT | 2023-01-22 15:39 | 2023-01-22 17:56 | 2:17 | T |  | 0 | 0 | No interruption
Fenchuganj | 230/132 kV transformer TR-02 LT | 2023-01-22 16:44 | 2023-01-22 16:44 | 0:00 | E/O | Due to Oil leakage | 0 | 0 | No interruption
| 230/132 kV transformer TR-02 HT | 2023-01-22 18:44 | 2023-01-22 18:44 | 0:00 | E/O |  | 0 | 0 | No interruption
Shahjibazar | 132/33 kV transformer TR-06 HT & LT | 2023-01-26 00:36 | 2023-01-26 15:58 | 15:22 | T | Tripped showing O/C. relay | 14 | 215.1333 | Power interruption
Cumilla(S) | 132/33 kV transformer TR-4 LT & HT | 2023-01-31 12:14 | 2023-01-31 13:37 | 1:23 | E/O | Due to Emergency maint.work | 0 | 0 | No interruption
|  |  | Total : | 36:03 |  |  |  | 335.95
Khulna Grid Circle :
Khulna© | 132/33 kV transformer( 425)TR1 HT LT | 2023-01-07 09:30 | 2023-01-07 09:30 | 0:00 | E/O | Due to Transformers oil centrifuging work | 0 | 0 | No interruption
Rampal | 1320 MW (BIFPCL) | 2023-01-09 03:06 | 2023-01-09 03:06 | 0:00 | T | due to generator rotor E/F | 0 | 0 | No interruption
Barishal(S) | 132 kV bus coupler | 2023-01-09 23:24 | 2023-01-09 23:24 | 0:00 | T | Tripped showing O/C. relay | 0 | 0 | No interruption
Khulna © | 132/33 kV transformer TR1 425T HT | 2023-01-12 09:40 | 2023-01-12 09:40 | 0:00 | E/O | Due to For oil centrifuzing | 0 | 0 | No interruption
Barishal | 132/33 kV transformer Tr 1(405T) HT | 2023-01-16 01:25 | 2023-01-16 07:45 | 6:20 | E/O | Due to 33 kV Breaker fault | 58 | 367.3333 | Power interruption
| 132/33 kV transformer Tr 1(405T) LT | 2023-01-16 01:25 | 2023-01-16 01:55 | 0:30 | E/O | Due to 33 kV Breaker fault | 58 | 29 | Power interruption
| 132/33 kV transformer Tr 1(405T) LT | 2023-01-16 01:25 | 2023-01-16 07:50 | 6:25 | E/O | Due to 33 kV Breaker fault | 58 | 372.1667 | Power interruption
Gopalganj | 132/33 kV transformer T-02 LT & HT | 2023-01-16 09:54 | 2023-01-16 09:54 | 0:00 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Khulna © | 132/33 kV transformer TR -1425T LT | 2023-01-17 10:31 | 2023-01-17 10:31 | 0:00 | E/O | Due to Oil cetrifuging.. | 0 | 0 | No interruption
| 132/33 kV transformer TR -1425T HT | 2023-01-17 10:32 | 2023-01-17 10:32 | 0:00 | E/O | Due to Oil cetrifuging.. | 0 | 0 | No interruption
Shariatpur | 132/33 kV transformerT1 406T) LT & T2 | 2023-01-21 21:15 | 2023-01-21 21:30 | 0:15 | T | Tripped showing O/C. relay | 23 | 5.75 | Power interruption
| 132/33 kV transformerT2 406T) LT | 2023-01-21 21:15 | 2023-01-21 21:30 | 0:15 | T |  | 23 | 5.75 | Power interruption
| 132/33 kV transformerT2 416T) LT | 2023-01-26 04:32 | 2023-01-26 04:54 | 0:22 | E/O | Due to 33 kV Breaker fault | 15 | 5.5 | Power interruption
Khulna © | 132/33 kV transformer TR -1 LT | 2023-01-28 10:13 | 2023-01-28 13:30 | 3:17 | E/O | Due to oil centrifuge work. | 0 | 0 | No interruption
| 132/33 kV transformer TR -1 HT | 2023-01-28 10:14 | 2023-01-28 10:14 | 0:00 | E/O |  | 0 | 0 | No interruption
|  |  | Total : | 17:24 |  |  |  | 785.5
Page: 3/3 | [8 empty] | QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: January2023
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
HVDC Grid Circle :
Benapole | 132/33 kV transformer T01(406) LT | 2023-01-03 15:06 | 2023-01-03 16:59 | 1:53 | E/O | Due to red-hot maint. | 16 | 30.1333 | Power interruption
Jashore | 132/33 kV transformer T01(406) HT | 2023-01-03 15:07 | 2023-01-03 16:58 | 1:51 | E/O |  | 16 | 29.6 | Power interruption
Jhenaidah | 132/33 kV transformer T01 HT & LT | 2023-01-09 03:08 | 2023-01-09 03:08 | 0:00 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Shahjadpur | 132/33 kV transformer T04(435T) LT | 2023-01-11 11:33 | 2023-01-11 12:28 | 0:55 | E/O | Due to red-hot maint. | 14 | 12.8333 | Power interruption
| 132/33 kV transformer T04(435T) HT | 2023-01-11 11:35 | 2023-01-11 12:28 | 0:53 | E/O | Due to red-hot maint.
Ishurdi | 230/132 kV transformer T01 HT | 2023-01-16 11:07 | 2023-01-16 16:55 | 5:48 | E/O | Due to Oil leakage | 0 | 0 | No interruption
BIPTC | BIPTC 20DF11 | 2023-01-17 11:11 | 2023-01-17 12:19 | 1:08 | E/O | Due to Emergency maint.work | 0 | 0 | No interruption
Jashore | 132/33 kV transformer T03 HT & LT | 2023-01-19 22:24 | 2023-01-19 22:24 | 0:00 | E/O | Due to cable burst | 0 | 0 | No interruption
Pabna | 132/33 kV transformer T01 HT | 2023-01-21 17:03 | 2023-01-21 18:20 | 1:17 | E/O | Due to Breaker burst | 0 | 0 | No interruption
Bharamara G.K | 230/132 kV transformer T3 LT | 2023-01-23 08:57 | 2023-01-23 08:57 | 0:00 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Pabna | 132/33 kV transformer T01 HT | 2023-01-23 11:56 | 2023-01-23 21:42 | 9:46 | E/O | Due to Emergency maint.work | 0 | 0 | No interruption
Ishurdi | 132/33 kV transformer T01 HT | 2023-01-26 19:50 | 2023-01-26 21:32 | 1:42 | E/O | Due to Breaker maint | 15 | 25.5 | Power interruption
| 132/33 kV transformer T01 LT | 2023-01-26 19:55 | 2023-01-26 21:56 | 2:01 | T | Due to 33 kv feeder fault. | 0 | 0 | No interruption
| 132/33 kV transformer T01 HT | 2023-01-26 20:51 | 2023-01-26 21:32 | 0:41 | E/O | Due to Emergency maint.work | 15 | 10.25 | Power interruption
| 132/33 kV transformer T02 LT & HT | 2023-01-28 08:56 | 2023-01-28 08:56 | 0:00 | T | Tripped showing E/F. relay | 0 | 0 | No interruption
| 132/33 kV transformer T02 LT | 2023-01-28 17:49 | 2023-01-28 18:56 | 1:07 | E/O | Due to red-hot maint. | 25 | 27.9167 | Power interruption
| 132/33 kV transformer T01 HT | 2023-01-31 10:20 | 2023-01-31 13:19 | 2:59 | E/O | Due to Breaker maint | 0 | 0 | No interruption
| 132/33 kV transformer T01 LT | 2023-01-31 10:20 | 2023-01-31 13:25 | 3:05 | E/O |  | 0 | 0 | No interruption
|  |  | Total : | 35:06 |  |  |  | 136.2333
Bogura Grid Circle:
Barapukuria | 230/132 kV transformer T05 ,424 LT | 2023-01-02 23:19 | 2023-01-02 23:19 | 0:00 | E/O | Due to cable burst | 0 | 0 | No interruption
Palashbari | 132/33 kV transformer TR-4-434T HT | 2023-01-03 08:53 | 2023-01-03 10:50 | 1:57 | E/O | Due to changing of L/A | 0 | 0 | No interruption
Naogaon | 132/33 kV transformer T02 LT | 2023-01-03 14:45 | 2023-01-03 15:19 | 0:34 | T | Due to red-hot maint. | 10 | 5.6667 | Power interruption
| 132/33 kV transformer T02 HT | 2023-01-03 14:46 | 2023-01-03 15:18 | 0:32 | T | Due to red-hot maint. | 10 | 5.3333 | Power interruption
Bogura | 132 kV main Bus-2 | 2023-01-07 12:33 | 2023-01-07 12:33 | 0:00 | T | Tripped showing E/F. relay | 0 | 0 | No interruption
Panchugarh | 132/33 kV transformer427T(A+B) T02 HT | 2023-01-11 11:12 | 2023-01-11 11:12 | 0:00 | E/O | Due to oil centrifusing | 0 | 0 | No interruption
Barapukuria | 230/132 kV transformer T03 404T LT | 2023-01-19 23:40 | 2023-01-19 23:40 | 0:00 | E/O | Due to Gas Pressure Low. | 0 | 0 | No interruption
| 230/132 kV transformer T03 404T LT | 2023-01-20 10:39 | 2023-01-20 11:57 | 1:18 | E/O | Due to Gas Pressure Low. | 0 | 0 | No interruption
Naogaon | 132/33 kV transformer T02 LT | 2023-01-22 16:29 | 2023-01-22 17:30 | 1:01 | E/O | Due to red-hot maint. | 10 | 10.1667 | Power interruption
| 132/33 kV transformer T02 HT | 2023-01-22 16:30 | 2023-01-22 17:30 | 1:00 | E/O |  | 0 | 0
Barapukuria | 230/132 kV transformer T04 | 2023-01-23 10:11 | 2023-01-23 16:03 | 5:52 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Rajshahi | 132/33 kV transformer T01 HT | 2023-01-23 11:56 | 2023-01-23 21:42 | 9:46 | E/O | Due to Emergency maint.work | 23 | 224.6333 | Power interruption
Naogaon | 132/33 kV transformer T03 HT | 2023-01-23 19:50 | 2023-01-23 22:18 | 2:28 | E/O | Due to red-hot maint. | 0 | 0 | No interruption
Saidpur | 132/33 kV transformer T03 LT | 2023-01-26 11:14 | 2023-01-26 17:16 | 6:02 | E/O | Due to Oil leakage | 0 | 0 | No interruption
| 132/33 kV transformer T03 HT | 2023-01-26 11:15 | 2023-01-26 17:14 | 5:59 | E/O |  | 0 | 0 | No interruption
Thaurgaon | 132/33 kV transformer T432 LT | 2023-01-26 13:50 | 2023-01-26 16:45 | 2:55 | E/O | Due to Due to Abnormal Sound | 0 | 0 | No interruption
Sirajganj | 132/33 kV transformer T04 HT | 2023-01-26 16:30 | 2023-01-26 17:47 | 1:17 | E/O | Due to Emergency maint.work | 0 | 0 | No interruption
Naogaon | 132/33 kV transformer T02 LT | 2023-01-31 15:12 | 2023-01-31 15:54 | 0:42 | E/O | Due to red-hot maint. | 15 | 10.5 | Power interruption
| 132/33 kV transformer T02 HT | 2023-01-31 15:13 | 2023-01-31 15:53 | 0:40 | E/O | Due to red-hot maint. | 15 | 10 | Power interruption
|  |  | Total : | 42:03 |  |  |  | 266.3
Others :
Ashuganj | All 230 kV Ckts 230/132kV OAT-12 | 2022-01-09 04:23 | 2022-01-09 08:20 | 3:57 | T | Due to 230 kV Bus tripped | 0 | 0 | No interruption
| 132/33 kV transformerT3 with 33 kV Bus | 2022-01-25 16:48 | 2022-01-25 17:54 | 1:06 | E/O | Due to Emergency maint.work | 17 | 18.7 | Power interruption
|  |  | Total : | 5:03 |  | Unserved Energy: |  | 18.7
Total outage period of Sub-station Equipment : |  |  |  | 228:34 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.
Ashuganj 230kV bus & 230/132kV OAT-12

## QF-LDC-24
Page: 1/2 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month:January2023
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Tongi(N) | Tongi(N)-Tongi 132 kV Ckt-2 | 2023-01-02 01:30 | 2023-01-02 01:30 | 0:00 | T | Tripped showing Diff. relay | 0 | 0 | No interruption
Aminbazar | Aminbazar-Mirpur 132 kV Ckt-2 | 2023-01-04 13:58 | 2023-01-04 15:45 | 1:47 | T | Tripped showing E/F. relay | 0 | 0 | No interruption
| Aminbazar-Kallyanpur 132 kV Ckt-2 | 2023-01-06 06:46 | 2023-01-06 07:17 | 0:31 | T | Tripped showing General trip | 0 | 0 | No interruption
Bashundhara | Bashundhara-Tongi 132 kV Ckt-1 | 2023-01-11 12:38 | 2023-01-11 12:46 | 0:08 | T | Tripped showing Backup protection relay | 0 | 0 | No interruption
Aminbazar | Aminbazar 400/230/132kV S/S Gopalganj-1 | 2023-01-13 10:43 | 2023-01-13 11:47 | 1:04 | E/O | Due to Emergency maint.work | 0 | 0 | No interruption
Bashundhara | Bashundhara-Rampura 132 kV Ckt-1 | 2023-01-13 10:52 | 2023-01-13 11:15 | 0:23 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Kabirpur | Kabirpur-Manikganj 132 kV Ckt-1 | 2023-01-17 11:34 | 2023-01-17 11:51 | 0:17 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Aminbazar | Aminbazar-Meghnaghat 230 kV Ckt-1 | 2023-01-23 17:03 | 2023-01-23 17:37 | 0:34 | E/O | Due to Emergency maint.work | 0 | 0 | No interruption
Tangail | Tangail-Mymensingh RPCL 132 kV Ckt-2 | 2023-01-23 18:18 | 2023-01-23 18:44 | 0:26 | T | Tripped showing general trip. | 0 | 0 | No interruption
| Tangail-Mymensingh RPCL 132 kV Ckt-1 | 2023-01-23 18:18 | 2023-01-23 18:33 | 0:15 | T |  | 0 | 0 | No interruption
Joydevpur | Joydevpur-Kodda 132 kV Ckt-1 | 2023-01-27 09:13 | 2023-01-27 17:13 | 8:00 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
| Joydevpur-Kodda 132 kV Ckt-1 | 2023-01-30 15:05 | 2023-01-30 16:04 | 0:59 | E/O | Due to Emergency maint.work | 0 | 0 | No interruption
|  |  | Total : | 14:24 |  | Unserved Energy: |  | 0
Dhaka (South) Grid Circle :
Meghnaghat | Meghnaghat-Shyampur 230 kV Ckt-1 | 2022-01-06 07:08 | 2022-01-06 07:36 | 0:28 | T | Due to Tripped showing Optimho and micromho relay | 0 | 0 | No interruption
| Meghnaghat-Shyampur 230 kV Ckt-1 | 2022-01-08 02:28 | 2022-01-08 02:28 | 0:00 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
| APR-Shyampur 230 kV Ckt | 2022-01-08 02:32 | 2022-01-08 02:32 | 0:00 | T | Tripped showing E/F. relay | 0 | 0 | No interruption
| Meghnaghat-Shyampur 230 kV Ckt-2 | 2022-01-08 05:31 | 2022-01-08 05:40 | 0:09 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
| APR-Shyampur 230 kV Ckt | 2022-01-08 05:45 | 2022-01-08 07:11 | 1:26 | T | Tripped showing E/F. relay | 0 | 0 | No interruption
| Meghnaghat-Shyampur 230 kV Ckt-1 | 2022-01-08 05:47 | 2022-01-08 07:04 | 1:17 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Madanganj | Madanganj-Shitalkhya 132 kV Ckt | 2022-01-16 10:51 | 2022-01-18 23:05 | 60:14 | E/O | Due to Emergency maint.work | 0 | 0 | Power interruption
Meghnaghat | Meghnaghat-Aminbazar 230 kV Ckt-1 | 2022-01-23 15:47 | 2022-01-23 17:32 | 1:45 | T | Due to DTT- Direct Transfer Trip | 0 | 0 | No interruption
Madanganj | Madanganj-Bashuundhara 132 kV Ckt | 2022-01-25 23:20 | 2022-01-25 23:52 | 0:32 | T | Tripped showing Differential relay relays | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Shyampur 230 kV Ckt-1 | 2022-01-29 03:39 | 2022-01-29 04:54 | 1:15 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
| Meghnaghat-Shyampur 230 kV Ckt-2 | 2022-01-29 03:42 | 2022-01-29 03:42 | 0:00 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Haripur | Haripur-Sonargaon 132 kV Ckt-1 | 2022-01-29 05:32 | 2022-01-29 05:47 | 0:15 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Shyampur 230 kV Ckt-1 | 2022-01-29 07:10 | 2022-01-29 07:10 | 0:00 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
| Meghnaghat-Shyampur 230 kV Ckt-1 | 2022-01-30 04:15 | 2022-01-30 04:37 | 0:22 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Shyampur | Shyampur-APR 230 kV Ckt | 2022-01-30 04:15 | 2022-01-30 04:41 | 0:26 | T | Tripped showing E/F. relay | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Shyampur 230 kV Ckt-2 | 2022-01-30 04:23 | 2022-01-30 04:34 | 0:11 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
| Meghnaghat-Shyampur 230 kV Ckt-2 | 2022-01-30 05:09 | 2022-01-30 05:09 | 0:00 | T | ripped showing SOTF relay | 0 | 0 | No interruption
| Meghnaghat-Shyampur 230 kV Ckt-1 | 2022-01-30 05:10 | 2022-01-31 17:53 | 36:43 | T |  | 0 | 0 | No interruption
Madanganj | Madanganj-Shitalakhya 132 kV Ckt | 2022-01-31 00:23 | 2022-01-31 00:23 | 0:00 | E/O | Due to Emergency maint.work | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Shyampur 230 kV Ckt-2 | 2022-01-31 00:32 | 2022-01-31 00:32 | 0:00 | E/O | Due to dense fog tripping. | 0 | 0 | No interruption
Brahmongaon | Brahmongaon(Aggreko)-Hasnabad 132 kV Ckt-2 | 2023-01-31 08:23 | 2023-01-31 08:23 | 0:00 | E/O | Due to Emergency maint.work | 0 | 0 | No interruption
|  |  | Total : | 105:03 |  | Unserved Energy: |  | 0
Chattogram Grid Circle :
Khulshi | Khulshi-Baraulia 132 kV Ckt-2 | 2023-01-03 11:10 | 2023-01-03 13:20 | 2:10 | T | Due to red-hot maint. | 0 | 0 | No interruption
| Khulshi-Baraulia 132 kV Ckt-1 | 2023-01-03 11:12 | 2023-01-03 13:19 | 2:07 | E/O | Due to Emergency maint.work | 0 | 0 | No interruption
Mirsorai | Mirsorai-150 MW P.S 230 kV Ckt-2 & 1 | 2023-01-06 10:12 | 2023-01-06 19:14 | 9:02 | E/O | Due to Emergency maint.work | 0 | 0 | No interruption
Baroaulia | Baroaulia-Hathazari 132 kV Ckt-1 | 2023-01-22 14:55 | 2023-01-22 16:05 | 1:10 | T | Due to red-hot maint. | 0 | 0 | No interruption
Sikalbaha(O) | Sikalbaha(O)-ECPV P.P 132 kV Ckt | 2023-01-26 19:59 | 2023-01-26 19:59 | 0:00 | T | Tripped showing Diff. relay | 0 | 0 | No interruption
Cox'sbazar | Cox'sbazar-Dohazari 132 kV Ckt-1 | 2023-01-30 00:30 | 2023-01-30 00:38 | 0:08 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
|  |  | Total : | 14:37 |  | Unserved Energy: |  | 0
Page: 2/2 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month:January2023
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Cumilla Grid Circle :
Chowmuhani | Chowmuhani-Ramganj 132 kV Ckt-1 | 2023-01-01 09:11 | 2023-01-01 14:39 | 5:28 | T | Due to red-hot maint. | 0 | 0 | No interruption
| Ashuganj-Cumilla(N) 230 kV Ckt-1 | 2023-01-09 04:24 | 2023-01-09 07:40 | 3:16 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
| Ashuganj-Cumilla(N) 230 kV Ckt-2 | 2023-01-09 04:24 | 2023-01-09 04:24 | 0:00 | T |  | 0 | 0 | No interruption
| Ashuganj-Sirajganj 230 kV Ckt-1 & 2 | 2023-01-09 04:25 | 2023-01-09 06:56 | 2:31 | T |  | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Daudkandi 132 kV Ckt-2 | 2023-01-09 06:59 | 2023-01-09 07:32 | 0:33 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Chandpur | Chandpur-Kachua 132 kV Ckt-2 | 2023-01-11 12:48 | 2023-01-11 13:10 | 0:22 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Daudkandi | Daudkandi-Sonargaon 132 kV Ckt-1 & 2 | 2023-01-14 09:50 | 2023-01-14 15:53 | 6:03 | E/O | Due to Emergency maint.work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV Ckt-1 | 2023-01-22 14:43 | 2023-01-22 14:53 | 0:10 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
| Ashuganj-Ghorashal 132 kV Ckt-2 | 2023-01-27 15:34 | 2023-01-27 16:02 | 0:28 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
| Ashuganj-Cumilla(N) 230 kV Ckt-2 | 2023-01-30 05:20 | 2023-01-30 05:41 | 0:21 | T |  | 0 | 0 | No interruption
| Ashuganj-Cumilla(N) 230 kV Ckt-1 | 2023-01-30 05:20 | 2023-01-30 05:41 | 0:21 | T |  | 0 | 0 | No interruption
|  |  | Total : | 19:33 |  | Unserved Energy: |  | 0
Page: 3/3 | [8 empty] | OF-LDC-24
Khulna Grid Circle :
Barishal | Barishal-Patuakhali(Barguna) 132 kV Ckt | 2023-01-01 15:05 | 2023-01-01 15:16 | 0:11 | T | Tripped showing Dist. relay. | 74 | 13.5667 | Power interruption
| Barishal-Madaripur 132 kV Ckt-2 | 2023-01-01 15:07 | 2023-01-01 15:35 | 0:28 | T | Tripped showing Dist. relay. | 112 | 52.2667 | Power interruption
Gopalganj | Gopalganj-Rampal 400 kV line | 2023-01-08 13:04 | 2023-01-08 13:18 | 0:14 | T | due to increasing Rampal generation & Aminbazar line overload | 0 | 0 | No interruption
Khulna (C) | Khulna ©-Noapara 132 kV Ckt-2 | 2023-01-20 08:26 | 2023-01-20 16:12 | 7:46 | E/O | Due to Emergency maint.work | 0 | 0 | No interruption
| Khulna ©-Noapara 132 kV Ckt-1 | 2023-01-20 08:26 | 2023-01-20 16:11 | 7:45 | E/O |  | 0 | 0 | No interruption
Bagerhat | Bagerhat-Goalpara 132 kV Ckt-1 | 2023-01-28 08:05 | 2023-01-28 08:05 | 0:00 | E/O | Due to Emergency maint.work | 0 | 0 | No interruption
Gopalganj(O) | Gopalganj(O)-Gopalganj (N) 132 Ckt-1 | 2023-01-29 09:53 | 2023-01-29 09:53 | 0:00 | E/O | Due to Over load | 0 | 0 | No interruption
Rampal | Rampal-Khulna(S) Ckt-2 | 2023-01-29 17:16 | 2023-01-29 17:32 | 0:16 | T | Tripped due to Dc 220v Supply Fault. | 0 | 0 | No interruption
|  |  | Total : | 16:40 |  | Unserved Energy: |  | 65.8333
HVDC Grid Circle :
Jhenaidah 230 S/S | Jhenaidah 230 S/S-Jashore 132 kV Ckt-1(L2) | 2023-01-02 10:43 | 2023-01-02 10:53 | 0:10 | E/O | Due to Emergency maint.work | 0 | 0 | No interruption
| Jhenaidah 230 S/S-Jashore 132 kV Ckt-1(L1) | 2023-01-02 10:49 | 2023-01-02 10:53 | 0:04 | E/O | Due to Emergency maint.work | 0 | 0 | No interruption
Bheramara | Bheramara-G.K 132 kV Ckt-1 | 2023-01-18 14:33 | 2023-01-18 14:33 | 0:00 | E/O | Due to SF6 Gas Filling of 132kV Line | 0 | 0 | No interruption
| Bheramara P/S-Kustia 132 kV Ckt-1 | 2023-01-26 13:47 | 2023-01-26 14:13 | 0:26 | E/O | Due to Emergency maint.work | 0 | 0 | No interruption
Shahjadpur | Shahjadpur-Sirajganj 132 kV Ckt-1 | 2023-01-27 08:32 | 2023-01-27 15:44 | 7:12 | E/O | Due to Emergency maint.work | 0 | 0
|  |  | Total : | 7:52 |  | Unserved Energy: |  | 0
Bogura Grid Circle:
Jaldhaka | Jaldhaka-Saidpur 132 kV Ckt-1 | 2023-01-18 06:17 | 2023-01-18 06:39 | 0:22 | T | Tripped showing O/C relay | 15 | 5.5 | Power interruption
| Jaldhaka-Saidpur 132 kV Ckt-2 | 2023-01-18 06:17 | 2023-01-18 06:50 | 0:33 | T |  | 0 | 0 | No interruption
Bogura | Bogura-Sirajganj 230 kV Ckt-1 | 2023-01-20 10:46 | 2023-01-20 12:05 | 1:19 | E/O | Due to Emergency maint.work | 0 | 0 | No interruption
| Bogura-Sirajganj 230 kV Ckt-2 | 2023-01-20 12:06 | 2023-01-20 16:24 | 4:18 | E/O |  | 0 | 0 | No interruption
Purbasadipur | Purbasadipur-Saidpur 132 kV Ckt-1 | 2023-01-26 09:54 | 2023-01-26 20:12 | 10:18 | E/O | Due to SF6 oil leakage | 0 | 0 | No interruption
Sirajganj | Sirajganj-Sherpur 132 kV Ckt-1 | 2023-01-27 08:31 | 2023-01-27 15:53 | 7:22 | E/O | Due to Emergency maint.work | 0 | 0 | No interruption
|  |  | Total : | 24:12 |  | Unserved Energy: |  | 5.5
Others :
Matuail | Matuail-Siddhirganj 132 kV Ckt-1 | 2023-01-06 07:37 | 2023-01-06 09:37 | 2:00 | T | Tripped showing Dist. relay. | 32 | 64 | Power interruption
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 64
Total outage period of Sub-station Equipment : |  |  |  | 188:56 | Hours
T = Tripping
E/O = Emergency Outage | [6 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-25
Page: 1/16 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: January 2023
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Kishoreganj | 132/33 kV transformer T-1 | 2022-12-01 09:15 | 2022-12-01 09:15 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Bhaluka | 132/33 kV transformer T-1 LT | 2023-12-01 09:22 | 2023-12-01 16:21 | 6:59 | S/O | Due to DS change | 0 | 0 | No interruption
| 132/33 kV transformer T-1 HT | 2023-12-01 09:23 | 2023-12-01 16:19 | 6:56 | S/O |  | 0 | 0 | No interruption
Jamalpur | 132/33 kV transformer T-4 LT & HT | 2023-01-01 10:30 | 2023-01-01 16:20 | 5:50 | S/O | Due to A/M work | 0 | 0 | No interruption
Kodda | 132/33 kV transformer Tr-5 LT | 2023-01-01 10:30 | 2023-01-01 17:38 | 7:08 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer Tr-5(446) HT | 2023-01-01 10:31 | 2023-01-01 17:37 | 7:06 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | 230 kV Bus-2 | 2023-01-01 10:59 | 2023-01-01 19:38 | 8:39 | S/O | Due to A/M work | 0 | 0 | No interruption
| 400/230 kV transformer ATR-2 LT | 2023-01-01 11:17 | 2023-01-01 19:38 | 8:21 | S/O | Due to A/M work | 0 | 0 | No interruption
| 400/230 kV transformer ATR-2 HT | 2023-01-01 11:17 | 2023-01-01 19:27 | 8:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Mirpur | 132/33 kV transformer Tr-1 LT | 2023-01-02 09:05 | 2023-01-02 09:05 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer Tr-1 HT | 2023-01-02 09:09 | 2023-01-08 02:45 | 137:36 | S/O | Due to A/M work | 0 | 0 | No interruption
Kallyanpur | 132/33 kV transformer G T-2 LT with 33 kV Bus | 2023-01-02 09:23 | 2023-01-02 16:59 | 7:36 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer G T-2 HT with 33 kV Bus | 2023-01-02 09:23 | 2023-01-02 16:58 | 7:35 | S/O | Due to A/M work | 0 | 0 | No interruption
Kodda | 132/33 kV transformer Tr-1(406) LT | 2023-01-02 09:53 | 2023-01-02 16:16 | 6:23 | S/O | Due to A/M work | 28 | 178.7333 | Power interruption
| 132/33 kV transformer Tr-1(406) HT | 2023-01-02 09:53 | 2023-01-02 16:14 | 6:21 | S/O | Due to A/M work | 28 | 177.8 | No interruption
| 132/33 kV transformer Tr-2(416) LT | 2023-01-02 09:54 | 2023-01-02 16:17 | 6:23 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer Tr-2(406) HT | 2023-01-02 09:55 | 2023-01-02 16:15 | 6:20 | S/O | Due to A/M work | 28 | 177.3333 | Power interruption
Bhaluka | 132/33 kV transformer Tr-1 LT | 2023-01-02 10:01 | 2023-01-02 16:32 | 6:31 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer Tr-1 HT | 2023-01-02 10:02 | 2023-01-02 16:32 | 6:30 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | 132/33 kV transformer T-4 LT & HT | 2023-01-02 10:31 | 2023-01-02 16:20 | 5:49 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | 400/230 kV transformer Tr-2 LT | 2023-01-02 10:32 | 2023-01-02 15:12 | 4:40 | S/O | Due to A/M work | 0 | 0 | No interruption
| 400/230 kV transformer Tr-2 HT | 2023-01-02 10:33 | 2023-01-02 15:11 | 4:38 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | 132/33 kV transformer T-1 (403T) HT | 2023-01-02 10:58 | 2023-01-02 14:38 | 3:40 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | 400/230 kV transformer Tr-2 LT | 2023-01-02 11:35 | 2023-01-02 20:04 | 8:29 | S/O | Due to A/M work | 0 | 0 | No interruption
| 400/230 kV transformer Tr-2 HT | 2023-01-02 11:49 | 2023-01-02 20:01 | 8:12 | S/O | Due to A/M work | 0 | 0 | No interruption
| 230 kV Bus-01 | 2023-01-02 15:46 | 2023-01-02 20:04 | 4:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Agargaon | 230/132 kV transformer T-1(705) LT | 2023-01-03 08:08 | 2023-01-03 16:52 | 8:44 | S/O | Due to A/M work | 0 | 0 | No interruption
| 230/132 kV transformer T-1(705) HT | 2023-01-03 08:09 | 2023-01-03 16:52 | 8:43 | S/O | Due to A/M work | 0 | 0 | No interruption
Kallyanpur | 132/33 kV transformer GT3 HT | 2023-01-03 09:05 | 2023-01-03 17:16 | 8:11 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer GT3 LT | 2023-01-03 09:05 | 2023-01-03 17:17 | 8:12 | S/O | Due to A/M work | 0 | 0 | No interruption
Mirpur | 132/33 kV transformer T-01HT | 2023-01-03 09:35 | 2023-01-03 14:43 | 5:08 | S/O | Due to A/M work | 0 | 0 | No interruption
Bhaluka | 132/33 kV transformer Tr-1 LT | 2023-01-03 09:42 | 2023-01-03 15:20 | 5:38 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer Tr-1 HT | 2023-01-03 09:42 | 2023-01-03 15:19 | 5:37 | S/O | Due to A/M work | 0 | 0 | No interruption
Kodda | 132/33 kV transformer Tr-4(436)LT | 2023-01-03 10:12 | 2023-01-03 14:48 | 4:36 | S/O | Due to A/M work | 30 | 138 | Power interruption
| 132/33 kV transformer Tr-5(446)LT | 2023-01-03 10:12 | 2023-01-03 10:35 | 0:23 | S/O | Due to A/M work | 20 | 7.6667 | Power interruption
| 132/33 kV transformer Tr-3(426T) LT | 2023-01-03 10:12 | 2023-01-03 14:48 | 4:36 | S/O | Due to A/M work | 30 | 138 | Power interruption
| 132/33 kV transformer Tr-3(426T) HT | 2023-01-03 10:13 | 2023-01-03 14:46 | 4:33 | S/O | Due to A/M work | 30 | 136.5 | Power interruption
| 132/33 kV transformer Tr-5(426T) HT | 2023-01-03 10:13 | 2023-01-03 10:34 | 0:21 | S/O | Due to A/M work | 20 | 7 | Power interruption
| 132/33 kV transformer Tr-4(436) HT | 2023-01-03 10:13 | 2023-01-03 14:46 | 4:33 | S/O | Due to A/M work | 30 | 136.5 | Power interruption
Kaliakoir | 400/230 kV transformer Tr-2 LT | 2023-01-03 10:14 | 2023-01-03 13:17 | 3:03 | S/O |  | 0 | 0 | No interruption
Page: 2/16 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: January 2023
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Kaliakoir | 400/230 kV transformer Tr-2 HT | 2023-01-03 10:15 | 2023-01-03 13:17 | 3:02 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | 132/33 kV transformer T-4 LT & HT | 2023-01-03 11:03 | 2023-01-03 13:05 | 2:02 | S/O | Due to A/M work | 0 | 0 | No interruption
Kodda | 132/33 kV transformer Tr-5(446)LT | 2023-01-03 14:30 | 2023-01-03 14:48 | 0:18 | S/O | Due to A/M work | 54 | 16.2 | Power interruption
| 132/33 kV transformer Tr-5(446)LT | 2023-01-03 14:30 | 2023-01-03 14:46 | 0:16 | S/O | Due to A/M work | 54 | 14.4 | Power interruption
Mirpur | 132/33 kV transformer Tr-1 LT |  | 2023-01-03 14:46 |  | S/O | After maint.work | 0 | 0 | No interruption
Cantonment | 132/33 kV transformer T-1 LT | 2023-01-03 15:26 | 2023-01-03 15:52 | 0:26 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-1 HT | 2023-01-03 15:27 | 2023-01-03 15:52 | 0:25 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Auxiliary transformer AT-2 LT | 2023-01-03 15:52 | 2023-01-03 16:13 | 0:21 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-2 LT | 2023-01-03 15:53 | 2023-01-03 16:12 | 0:19 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-2 HT | 2023-01-03 15:54 | 2023-01-03 16:12 | 0:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Kallyanpur | 230/132 kV transformer GT-3 LT | 2023-01-03 17:17 | 2023-01-03 17:17 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Agargaon | 230/132 kV transformer TR1(705T)-LT | 2023-01-04 08:36 | 2023-01-04 08:36 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | 132 kV Bus-A | 2023-01-04 10:10 | 2023-01-04 17:15 | 7:05 | S/O | Due to A/M work | 0 | 0 | No interruption
Bhaluka | 132/33 kV transformer Tr-1 HT | 2023-01-04 10:24 | 2023-01-04 16:27 | 6:03 | S/O | Due to A/M work | 0 | 0 | No interruption
Kodda | 132/33 kV transformer Tr-2(416) LT | 2023-01-04 11:14 | 2023-01-04 14:17 | 3:03 | S/O | Due to A/M work | 0 | 0 | No interruption
Bhaluka | 132/33 kV transformer Tr-02 LT & HT | 2023-01-04 09:44 | 2023-01-04 17:08 | 7:24 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132 kV Bus-A | 2023-01-05 10:30 | 2023-01-05 17:06 | 6:36 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | 132 kV Bus-A | 2023-01-05 10:38 | 2023-01-05 17:09 | 6:31 | S/O | Due to A/M work | 0 | 0 | No interruption
Kodda | 132/33 kV transformer Tr-2(416) LT | 2023-01-05 12:30 | 2023-01-05 13:43 | 1:13 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer Tr-2(416) HT | 2023-01-05 12:31 | 2023-01-05 13:42 | 1:11 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer Tr-4(436) LT | 2023-01-05 13:49 | 2023-01-05 14:51 | 1:02 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer Tr-4(436) HT | 2023-01-05 13:50 | 2023-01-05 14:50 | 1:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | 132 kV Bus-A | 2023-01-07 10:36 | 2023-01-07 17:02 | 6:26 | S/O | Due to A/M work | 0 | 0 | No interruption
Agargaon | 230/132 kV transformer TR1(715T)-LT | 2023-01-08 08:21 | 2023-01-08 20:34 | 12:13 | S/O | Due to A/M work | 0 | 0 | No interruption
| 230/132 kV transformer TR1(715T2)-HT | 2023-01-08 08:22 | 2023-01-08 20:31 | 12:09 | S/O | Due to A/M work | 0 | 0 | No interruption
Dhamrai | 132/33 kV transformer T1 LT | 2023-01-08 08:54 | 2023-01-08 17:00 | 8:06 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T1 HT | 2023-01-08 08:55 | 2023-01-08 16:59 | 8:04 | S/O | Due to A/M work | 0 | 0 | No interruption
Mirpur | 132/33 kV transformer T2 LT | 2023-01-08 10:10 | 2023-01-08 16:50 | 6:40 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T2 HT | 2023-01-08 10:13 | 2023-01-08 16:50 | 6:37 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | 132 kV Bus-A | 2023-01-08 10:32 | 2023-01-08 17:34 | 7:02 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi(N) | 132/33 kV transformer T2 HT(413T) | 2023-01-08 11:23 | 2023-01-08 15:26 | 4:03 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | 230/132 kV transformer TR2-LT | 2023-01-08 11:31 | 2023-01-08 15:04 | 3:33 | S/O | Due to A/M work | 0 | 0 | No interruption
| 230/132 kV transformer TR2-HT | 2023-01-08 11:32 | 2023-01-08 15:03 | 3:31 | S/O |  | 0 | 0 | No interruption
Kallyanpur | 132/33 kV transformer GT1 HT |  | 2023-01-08 20:24 |  | S/O | After maint.work | 0 | 0 | No interruption
| 132/33 kV transformer GT1 HT & LT | 2023-01-09 07:20 |  |  | S/O |  | 0 | 0 | No interruption
Dhamrai | 132/33 kV transformer T-1 LT | 2023-01-09 08:23 | 2023-01-09 16:59 | 8:36 | S/O | Due to A/M work | 0 | 0 | No interruption
Page: 3/16 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: January 2023
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Dhamrai | 132/33 kV transformer T-1 HT | 2023-01-09 08:23 | 2023-01-09 16:58 | 8:35 | S/O | Due to A/M work | 0 | 0 | No interruption
Mirpur | 132/33 kV transformer T-2 HT & LT | 2023-01-09 09:26 | 2023-01-09 09:26 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Bhaluka | 132/33 kV transformer Tr-02 LT | 2023-01-09 09:48 | 2023-01-09 16:41 | 6:53 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer Tr-02 HT | 2023-01-09 09:50 | 2023-01-09 16:46 | 6:56 | S/O | Due to A/M work | 0 | 0 | No interruption
Kabirpur | 132 kV Main Bus | 2023-01-09 10:14 | 2023-01-09 13:37 | 3:23 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | 132 kV Bus-A | 2023-01-09 10:20 | 2023-01-09 16:25 | 6:05 | S/O | Due to A/M work | 0 | 0 | No interruption
Kallyanpur | 132/33 kV transformer GT-02 LT & HT |  | 2023-01-09 20:20 |  | S/O | After maint.work | 0 | 0 | No interruption
Aminbazar | 230/132 kV transformer TR2-LT | 2023-01-09 06:55 |  |  | S/O | Due to maint.work | 0 | 0 | No interruption
| 230/132 kV transformer TR2-HT | 2023-01-09 06:57 | 2023-01-10 09:17 | 26:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Dhamrai | 132/33 kV transformer T-1 LT | 2023-01-10 08:00 | 2023-01-10 17:51 | 9:51 | S/O | Due to A/M work | 25 | 246.25 | Power interruption
| 132/33 kV transformer T-1 HT | 2023-01-10 08:01 | 2023-01-10 17:17 | 9:16 | S/O | Due to A/M work | 25 | 231.6667 | Power interruption
Kallyanpur | 132/33 kV transformer GT-3 LT | 2023-01-10 08:03 | 2023-01-10 21:27 | 13:24 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer GT-3 HT | 2023-01-10 08:04 | 2023-01-10 21:25 | 13:21 | S/O | Due to A/M work | 0 | 0 | No interruption
Mirpur | 132/33 kV transformer T-3 LT & HT | 2023-01-10 08:50 | 2023-01-10 16:16 | 7:26 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | 230/132 kV transformer TR2-LT |  | 2023-01-10 09:21 |  | S/O | After maint.work | 0 | 0 | No interruption
Bhaluka | 132/33 kV transformer Tr-02 HT | 2023-01-10 09:57 | 2023-01-10 17:27 | 7:30 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer Tr-02 LT | 2023-01-10 09:58 | 2023-01-10 09:58 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | 400/230 kV transformer TR2-LT | 2023-01-10 10:07 | 2023-01-10 16:40 | 6:33 | S/O | Due to A/M work | 0 | 0 | No interruption
| 400/230 kV transformer TR2-HT | 2023-01-10 10:08 | 2023-01-10 16:39 | 6:31 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | 230/132 kV transformer T01-HT & LT | 2023-01-10 10:25 | 2023-01-10 11:49 | 1:24 | S/O | Due to A/M work | 0 | 0 | No interruption
| 230/132 kV transformer T02-HT | 2023-01-10 11:58 | 2023-01-10 12:30 | 0:32 | S/O | Due to A/M work | 0 | 0 | No interruption
| 230/132 kV transformer T02-HT L | 2023-01-10 11:58 | 2023-01-10 13:08 | 1:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Dhamrai | 132/33 kV transformer Tr-1 LT | 2023-01-11 08:15 | 2023-01-11 18:26 | 10:11 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer Tr-1 HT | 2023-01-11 08:15 | 2023-01-11 18:25 | 10:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Bhaluka | 132/33 kV transformer Tr-01 HT | 2023-01-11 08:35 | 2023-01-11 12:28 | 3:53 | S/O | Due to A/M work | 0 | 0 | No interruption
Kallyanpur | 132/33 kV transformer GT3 LT | 2023-01-11 08:39 | 2023-01-11 16:07 | 7:28 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer GT3 HT | 2023-01-11 08:40 | 2023-01-11 16:07 | 7:27 | S/O | Due to A/M work | 0 | 0 | No interruption
Dhamrai | 33 kV Bus-01 | 2023-01-11 08:43 | 2023-01-11 18:18 | 9:35 | S/O | Due to A/M work | 0 | 0 | No interruption
Mirpur | 132/33 kV transformer Tr-3 LT | 2023-01-11 08:45 | 2023-01-11 18:13 | 9:28 | S/O | Due to A/M work | 0 | 0 | No interruption
Dhamrai | 132/33 kV transformer Tr-01 LT | 2023-01-11 08:46 | 2023-01-11 18:04 | 9:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Mirpur | 132/33 kV transformer Tr-3 HT | 2023-01-11 08:50 | 2023-01-11 18:13 | 9:23 | S/O | Due to A/M work | 0 | 0 | No interruption
Agargaon | 230/132 kV transformer T01(405)-HT | 2023-01-11 09:06 | 2023-01-11 17:19 | 8:13 | S/O | Due to A/M work | 0 | 0 | No interruption
Bhaluka | 132 kV Bus-B | 2023-01-11 09:33 | 2023-01-11 16:58 | 7:25 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | 230/132 kV transformer TR2-HT | 2023-01-11 09:59 | 2023-01-11 16:28 | 6:29 | S/O | Due to A/M work | 0 | 0 | No interruption
| 230/132 kV transformer TR2-LT | 2023-01-11 09:59 | 2023-01-11 16:29 | 6:30 | S/O | Due to A/M work | 0 | 0 | No interruption
Page: 4/16 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: January 2023
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Bhaluka | 132/33 kV transformer T-2 HT | 2023-01-11 12:54 | 2023-01-11 14:16 | 1:22 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-2 HT |  | 2023-01-11 14:18 |  | S/O | After maint.work | 0 | 0 | No interruption
Tongi(N) | 230/132 kV transformer TR2(4161-3) HT | 2023-01-11 15:20 | 2023-01-11 16:40 | 1:20 | S/O | Due to relay test | 0 | 0 | No interruption
| 230/132 kV transformer TR2(4161-3) LT | 2023-01-11 15:20 | 2023-01-11 16:42 | 1:22 | S/O |  | 0 | 0 | No interruption
Dhamrai | 132/33 kV transformer Tr-01 HT | 2023-01-12 09:11 | 2023-01-12 15:03 | 5:52 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi(N) | 230/132 kV transformer TR3 LT | 2023-01-12 09:54 | 2023-01-12 11:02 | 1:08 | S/O | Due to Relay Testing Work by SPMD | 0 | 0 | No interruption
Agargaon | 230/132 kV transformer T02(415)-LT | 2023-01-14 08:41 | 2023-01-14 17:27 | 8:46 | S/O | Due to A/M work | 0 | 0 | No interruption
| 230/132 kV transformer T02(415)-HT | 2023-01-14 08:49 | 2023-01-14 17:14 | 8:25 | S/O | Due to A/M work | 0 | 0 | No interruption
Kodda | 132/33 kV transformer Tr-05 LT | 2023-01-14 10:17 | 2023-01-14 17:16 | 6:59 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | 132 kV Bus-A | 2023-01-14 10:46 | 2023-01-14 10:46 | 0:00 | S/O |  | 0 | 0 | No interruption
| 132/33 kV transformer T-3(424T) LT | 2023-01-14 10:56 | 2023-01-14 16:56 | 6:00 | S/O |  | 0 | 0 | No interruption
Kaliakoir | Kaliakoir 400/230/132kV S/S 400 kv 25 MVAR Shunt Reactor -1,2 |  | 2023-01-14 22:41 |  | S/O | After maint.work | 0 | 0 | No interruption
Dhamrai | 132/33 kV transformer T2 LT | 2023-01-15 08:57 | 2023-01-15 17:39 | 8:42 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T2 HT | 2023-01-15 08:58 | 2023-01-15 17:38 | 8:40 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | 132 kV Bus-B | 2023-01-15 09:59 | 2023-01-15 13:55 | 3:56 | S/O | Due to A/M work | 0 | 0 | No interruption
Kodda | 132/33 kV transformer Tr-03 LT | 2023-01-15 10:39 | 2023-01-15 14:02 | 3:23 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer Tr-03 HT | 2023-01-15 10:40 | 2023-01-15 14:00 | 3:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Bhaluka | 132 kV Bus-A | 2023-01-15 10:58 | 2023-01-15 16:35 | 5:37 | S/O | Due to A/M work | 0 | 0 | No interruption
Kishoreganj | 132/33 kV transformer Tr-1(404T) LT | 2023-01-15 12:30 | 2023-01-15 15:21 | 2:51 | S/O | Due to Relay testing work by SPMD-2 | 0 | 0 | No interruption
| 132/33 kV transformer Tr-1(404T) HT | 2023-01-15 12:31 | 2023-01-15 15:20 | 2:49 | S/O |  | 0 | 0 | No interruption
| 132/33 kV transformer Tr-2(404T) HT | 2023-01-15 15:26 | 2023-01-15 17:11 | 1:45 | S/O | Due to A/M work | 0 | 0 | No interruption
Dhamrai | 132/33 kV transformer T-02 LT | 2023-01-16 07:59 | 2023-01-16 07:59 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-02 LT | 2023-01-16 08:00 | 2023-01-16 08:00 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-02 HT | 2023-01-16 08:00 | 2023-01-16 17:39 | 9:39 | S/O | Due to A/M work | 0 | 0 | No interruption
Kishoreganj | 132/33 kV transformer T3(A+B) (424TA) & 424TB ) HT | 2023-01-16 08:36 | 2023-01-16 14:47 | 6:11 | S/O | Due to A/M work | 0 | 0 | No interruption
Kodda | 132/33 kV transformer Tr-04 (436T) LT | 2023-01-16 09:56 | 2023-01-16 14:10 | 4:14 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer Tr-04 (436T) HT | 2023-01-16 09:56 | 2023-01-16 14:08 | 4:12 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | 230/132 kV transformer ATR-03-LT | 2023-01-16 10:48 | 2023-01-16 17:54 | 7:06 | S/O | Due to A/M work | 0 | 0 | No interruption
| 230/132 kV transformer ATR-03-HT | 2023-01-16 10:50 | 2023-01-16 17:52 | 7:02 | S/O |  | 0 | 0 | No interruption
| 400/230/132kV S/S ATR-02 LT | 2023-01-16 11:05 | 2023-01-16 17:58 | 6:53 | S/O | Due to DS Automation Work | 0 | 0 | No interruption
| 400/230/132kV S/S ATR-02 HT | 2023-01-16 11:08 | 2023-01-16 17:58 | 6:50 | S/O |  | 0 | 0 | No interruption
| 230 kV Bus-02 | 2023-01-16 11:24 | 2023-01-16 17:47 | 6:23 | S/O |  | 0 | 0 | No interruption
Mymensingh | 132 kV Bus-A |  | 2023-01-16 15:40 |  | S/O | After maint.work | 0 | 0 | No interruption
Dhamrai | 132/33 kV transformer T-02 LT |  | 2023-01-16 17:40 |  | S/O |  | 0 | 0 | No interruption
| 132/33 kV transformer T-02 HT | 2023-01-16 08:43 | 2023-01-16 16:21 | 7:38 | S/O | Due to A/M work | 0 | 0 | No interruption
Page: 5/16 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: January 2023
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Kodda | 132/33 kV transformer Tr-02 (436T) HT | 2023-01-17 09:06 | 2023-01-17 15:04 | 5:58 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer Tr-02 (436T) LT | 2023-01-17 09:06 | 2023-01-17 15:06 | 6:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | 132/33 kV transformer T-01(404T) HT | 2023-01-17 09:35 | 2023-01-17 16:42 | 7:07 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-01(404T) LT | 2023-01-17 09:35 | 2023-01-17 16:43 | 7:08 | S/O | Due to A/M work | 0 | 0 | No interruption
Satmosjid | 132/33 kV Auxiliary transformer T-r1 LT | 2023-01-17 09:44 | 2023-01-17 09:44 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Auxiliary transformer T-r1 HT | 2023-01-17 09:47 | 2023-01-17 15:46 | 5:59 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | 132 kV Bus-B | 2023-01-17 10:45 | 2023-01-17 16:06 | 5:21 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | 230 kV Bus-1 | 2023-01-18 07:43 | 2023-01-18 14:46 | 7:03 | S/O | Due to A/M work | 0 | 0 | No interruption
Dhamrai | 132/33 kV transformer T2 LT | 2023-01-18 08:15 | 2023-01-18 18:11 | 9:56 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T2 HT | 2023-01-18 08:17 | 2023-01-18 18:01 | 9:44 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer Tr022 LT | 2023-01-18 08:18 | 2023-01-18 18:07 | 9:49 | S/O | Due to A/M work | 0 | 0 | No interruption
| 33 kV Bus section -02 | 2023-01-18 08:42 | 2023-01-18 18:00 | 9:18 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T2 HT | 2023-01-18 09:28 | 2023-01-18 17:16 | 7:48 | S/O | Due to A/M work | 0 | 0 | No interruption
Savar | Transfer Bus | 2023-01-18 10:10 | 2023-01-18 12:10 | 2:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Dhamrai | 132/33 kV transformer T2 LT | 2023-01-19 08:25 | 2023-01-19 13:02 | 4:37 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T2 LT | 2023-01-19 08:32 | 2023-01-19 13:00 | 4:28 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T2 HT | 2023-01-19 08:32 | 2023-01-19 12:59 | 4:27 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer Auxi T02 HT | 2023-01-19 08:48 | 2023-01-19 12:36 | 3:48 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | 132 kV Bus-B | 2023-01-19 09:46 | 2023-01-19 16:55 | 7:09 | S/O | Due to A/M work | 0 | 0 | No interruption
Savar | 132 kVmain Bus | 2023-01-19 11:02 | 2023-01-19 18:16 | 7:14 | S/O | Due to maint. work | 0 | 0 | No interruption
Aminbazar | 400/230/132kV S/S ATR-02 LT | 2023-01-20 09:45 | 2023-01-20 16:29 | 6:44 | S/O | Due to maint. work | 0 | 0 | No interruption
| 400/230/132kV S/S ATR-02 HT | 2023-01-20 09:58 | 2023-01-20 16:27 | 6:29 | S/O | Due to maint. work | 0 | 0 | No interruption
Kishoreganj | 132/33 kV transformer T-1 LT & HT | 2023-01-21 08:34 | 2023-01-21 13:26 | 4:52 | S/O | Due to maint.work | 0 | 0 | No interruption
Savar | 132 kVmain Bus-A | 2023-01-21 09:27 | 2023-01-21 13:26 | 3:59 | S/O | Due to replacement work | 0 | 0 | No interruption
Tangail | 132 kVmain Bus | 2023-01-21 10:04 | 2023-01-21 15:03 | 4:59 | S/O | Due to A/M work | 130 | 647.8333 | Power interruption
Mymensingh | 132 kV Bus-B | 2023-01-21 11:53 | 2023-01-21 16:28 | 4:35 | S/O | Due to A/M work | 0 | 0 | No interruption
Savar | 132 kV main Bus | 2023-01-21 15:56 | 2023-01-21 17:25 | 1:29 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T1 LT & HT | 2023-01-21 16:06 | 2023-01-21 17:55 | 1:49 | S/O | Due to A/M work | 0 | 0 | No interruption
Netrakona | 132/33 kV transformer T-1415T HT |  | 2023-01-22 12:22 |  | S/O | After maint.work | 0 | 0 | No interruption
Savar | 132/33 kV transformer T-1 LT | 2023-01-23 09:12 | 2023-01-23 17:30 | 8:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Mirpur | 132/33 kV transformer T-2 LT | 2023-01-23 09:30 | 2023-01-23 17:40 | 8:10 | S/O | Due to Relay test . | 0 | 0 | No interruption
Mymensingh | 132/33kV Transformer-3 (424T) HT | 2023-01-23 10:33 | 2023-01-23 17:44 | 7:11 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 Transformer-1 (404T) HT | 2023-01-24 09:38 | 2023-01-24 14:10 | 4:32 | S/O |  | 0 | 0 | No interruption
| 132 kV Bus-A | 2023-01-24 09:58 | 2023-01-24 17:45 | 7:47 | S/O | Due to A/M work | 0 | 0 | No interruption
Savar | 132/33 kV transformer T-1 LT & HT | 2023-01-24 10:53 | 2023-01-24 16:37 | 5:44 | S/O | Due to A/M work | 0 | 0 | No interruption
Tangail | 132/33 kV transformer Tr-1 HT & LT | 2023-01-24 11:23 | 2023-01-24 14:23 | 3:00 | S/O | Due to Relay test . | 0 | 0 | No interruption
Kabirpur | 132/33 kV transformer T-3 LT | 2023-01-24 12:09 | 2023-01-24 12:09 | 0:00 | S/O | Due to 33 kv DPEZ feeder breaker change. | 0 | 0 | No interruption
| 132/33 kV transformer T-3 HT | 2023-01-24 12:10 | 2023-01-24 15:02 | 2:52 | S/O |  | 0 | 0 | No interruption
Tangail | 132/33 kV transformer Tr-2 HT | 2023-01-24 14:32 | 2023-01-24 18:10 | 3:38 | S/O | Due to relay and tan delta test | 0 | 0 | No interruption
| 132/33 kV transformer Tr-2 LT | 2023-01-24 14:32 | 2023-01-24 18:11 | 3:39 | S/O |  | 0 | 0 | No interruption
Page: 6/16 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: January 2023
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Savar | 132/33 kV transformer T-1 HT & LT | 2023-01-25 09:18 | 2023-01-25 17:30 | 8:12 | S/O | Due to Relay test . | 0 | 0 | No interruption
Tangail | 132/33 kV transformer Tr-3 LT & HT | 2023-01-25 10:21 | 2023-01-25 13:34 | 3:13 | S/O | Due to Relay test . | 0 | 0 | No interruption
| 132/33 kV transformer Tr-4 HT | 2023-01-25 13:36 | 2023-01-25 17:08 | 3:32 | S/O | Due to Relay and tan delta test | 0 | 0 | No interruption
| 132/33 kV transformer Tr-4 HT | 2023-01-25 13:36 | 2023-01-25 17:09 | 3:33 | S/O |  | 0 | 0 | No interruption
Banani | 132/33 kV transformer GT-2 | 2023-01-26 09:25 | 2023-01-26 14:12 | 4:47 | S/O | Due to A/M work | 0 | 0 | No interruption
Savar | 132/33 kV transformer T-2 HT & LT | 2023-01-26 09:33 | 2023-01-26 17:33 | 8:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Mirpur | 132/33 kV transformer T-3 LT | 2023-01-26 09:57 | 2023-01-26 16:58 | 7:01 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-3 HT | 2023-01-26 09:57 | 2023-01-26 16:57 | 7:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Joydevpur | 132/33 kV transformer GT-2 HT | 2023-01-27 09:19 | 2023-01-27 12:50 | 3:31 | S/O | Due to A/M work | 0 | 0 | No interruption
Kodda | 132 kV Bus-1 | 2023-01-27 09:25 | 2023-01-27 16:42 | 7:17 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer Tr-1 HT | 2023-01-27 09:46 | 2023-01-27 10:52 | 1:06 | S/O | Due to A/M work | 0 | 0 | No interruption
Joydevpur | 132 kV Bus | 2023-01-27 09:47 | 2023-01-27 12:42 | 2:55 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | 230/132 kV transformer ATR-02-LT | 2023-01-27 10:33 | 2023-01-27 19:47 | 9:14 | S/O | Due to A/M work | 0 | 0 | No interruption
Kodda | 132/33 kV transformer T-3 HT | 2023-01-27 10:54 | 2023-01-27 11:23 | 0:29 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-r5 HT | 2023-01-27 11:26 | 2023-01-27 12:08 | 0:42 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-2(416) HT | 2023-01-27 12:52 | 2023-01-27 14:19 | 1:27 | S/O | Due to A/M work | 0 | 0 | No interruption
Savar | 132/33 kV transformer T-1 LT | 2023-01-28 08:02 | 2023-01-28 18:16 | 10:14 | S/O | Due to replacemnet work | 0 | 0 | No interruption
| 132/33 kV transformer T-2 LT | 2023-01-28 08:02 | 2023-01-28 18:16 | 10:14 | S/O |  | 0 | 0 | No interruption
| 132/33 kV transformer T-3 LT | 2023-01-28 08:02 | 2023-01-28 18:16 | 10:14 | S/O |  | 0 | 0 | No interruption
| 132/33 kV transformer T-2 HT | 2023-01-28 08:04 | 2023-01-28 18:16 | 10:12 | S/O |  | 0 | 0 | No interruption
| 230/132 kV transformer ATR-03-LT | 2023-01-28 09:23 | 2023-01-28 09:23 | 0:00 | S/O | Due to replacemnet work | 0 | 0 | No interruption
| 230/132 kV transformer ATR-03-HT | 2023-01-28 09:24 | 2023-01-28 09:24 | 0:00 | S/O |  | 0 | 0 | No interruption
| 132 kV Bus-A |  | 2023-01-28 18:16 |  | S/O | After maint.work | 0 | 0 | No interruption
| 132/33 kV transformer T-2 LT | 2023-01-29 09:45 | 2023-01-29 17:46 | 8:01 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-3 LT | 2023-01-30 07:56 |  |  | S/O |  | 0 | 0 | No interruption
| 132/33 kV transformer T-3 LT | 2023-01-30 09:24 | 2023-01-30 16:47 | 7:23 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-3 HT | 2023-01-30 09:25 | 2023-01-30 16:47 | 7:22 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | 230/132 kV transformer TR-03-LT |  | 2023-01-30 16:18 |  | S/O | After maint.work | 0 | 0 | No interruption
| 230/132 kV transformer TR-03-HT |  | 2023-01-30 16:20 |  | S/O |  | 0 | 0 | No interruption
Savar | 132/33 kV transformer T-3 LT | 2023-01-31 09:41 | 2023-01-31 14:42 | 5:01 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-3 HT | 2023-01-31 09:42 | 2023-01-31 14:42 | 5:00 | S/O |  | 0 | 0 | No interruption
Aminbazar | 230/132 kV transformer TR-02-LT | 2023-01-31 10:11 | 2023-01-31 10:11 | 0:00 | S/O | Due to changing work | 0 | 0 | No interruption
| 230/132 kV transformer TR-02-HT | 2023-01-31 10:12 | 2023-01-31 10:12 | 0:00 | S/O |  | 0 | 0 | No interruption
|  |  | Total : | 1247:29 |  | Unserved Energy: |  | 2253.8833
Page: 7/16 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: January 2023
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (South) Grid Circle :
Maniknagar | 230/132 kV transformer TR-01(705T) LT | 2023-01-01 09:20 | 2023-01-01 17:19 | 7:59 | S/O | Due to A/M work | 0 | 0 | No interruption
| 230/132 kV transformer TR-01(705T) HT | 2023-01-01 09:21 | 2023-01-01 17:18 | 7:57 | S/O | Due to Tan Delta test | 0 | 0 | No interruption
Munshiganj | 132/33 kV transformer T-1 HT | 2023-01-01 09:56 | 2023-01-01 13:01 | 3:05 | S/O | Due to A/M work | 0 | 0 | No interruption
Shyampur | 230/132 kV Auxiliary transformer TR-01 LT & HT | 2023-01-01 10:12 | 2023-01-01 10:12 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Maniknagar | 132 kV main Bus |  | 2023-01-01 14:00 |  | S/O | After maint.work | 0 | 0 | No interruption
Hasnabad | 132/33 kV transformer 414T-2 LT & HT | 2023-01-02 09:34 | 2023-01-02 12:31 | 2:57 | S/O | Due to SPMD work | 0 | 0 | No interruption
| 132/33 kV transformer 424T-5 LT | 2023-01-02 12:32 | 2023-01-02 15:11 | 2:39 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer 424T-5 HT | 2023-01-02 12:32 | 2023-01-02 15:10 | 2:38 | S/O | Due to A/M work | 0 | 0 | No interruption
Siddhirganj | 132 kV Bus-B | 2023-01-04 09:38 | 2023-01-04 15:45 | 6:07 | S/O | Due to A/M work | 0 | 0 | No interruption
Srinagar | 132/33 kV transformer Tr-1 HT | 2023-01-05 10:09 | 2023-01-05 16:52 | 6:43 | S/O | Due to A/M work | 0 | 0 | No interruption
Keraniganj | 230/132 kV transformer TR-01 HT | 2023-01-07 09:09 | 2023-01-07 15:03 | 5:54 | S/O | Due to A/M work | 0 | 0 | No interruption
| 230/132 kV transformer TR-01 LT | 2023-01-07 09:09 | 2023-01-07 15:04 | 5:55 | S/O | Due to maint.work | 0 | 0 | No interruption
| 230/132 kV transformer TR-02 HT | 2023-01-07 09:12 | 2023-01-07 15:05 | 5:53 | S/O | Due to PBS maint.work | 0 | 0 | No interruption
| 230/132 kV transformer TR-02 LT | 2023-01-07 09:13 | 2023-01-07 15:05 | 5:52 | S/O |  | 0 | 0 | No interruption
Siddhirganj | 132/33 kV transformer EGCB GT-1 | 2023-01-07 09:39 | 2023-01-07 09:39 | 0:00 | S/O | Due to Corrective maintenance. | 0 | 0 | No interruption
Munshiganj | 132/33 kV transformer T-1 LT | 2023-01-08 08:02 | 2023-01-08 14:40 | 6:38 | S/O | Due to A/M work | 10 | 66.3333 | Power interruption
Rampura | 230/132 kV transformer TR-03 LT | 2023-01-08 12:52 | 2023-01-08 20:20 | 7:28 | S/O | Due to DFR Test of bushing. | 0 | 0 | No interruption
| 230/132 kV transformer TR-03 HT | 2023-01-08 12:52 | 2023-01-08 20:19 | 7:27 | S/O |  | 0 | 0 | No interruption
Munshiganj | 132/33 kV transformer T-1 HT | 2023-01-10 08:05 | 2023-01-10 10:43 | 2:38 | S/O |  | 0 | 0 | No interruption
| 132/33 kV transformer T-2 HT | 2023-01-10 08:05 | 2023-01-10 15:40 | 7:35 | S/O | Due to A/M work | 0 | 0 | No interruption
Madartek | 132/33 kV transformer GT-2 | 2023-01-10 09:18 | 2023-01-10 16:38 | 7:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Narsinghdi | 132 kV main Bus-2 | 2023-01-10 09:21 | 2023-01-10 13:25 | 4:04 | S/O | Due to A/M work | 0 | 0 | No interruption
Shyampur | 230/132 kV transformer Auxi TR-1 HT |  | 2023-01-10 14:05 |  | S/O | After maint.work | 0 | 0 | No interruption
| 230/132 kV transformer Auxi TR-1 LT |  | 2023-01-10 14:40 |  | S/O | After maint.work | 0 | 0 | No interruption
Srinagar | 132/33 kV transformer T-01 LT | 2023-01-12 08:00 | 2023-01-12 12:21 | 4:21 | S/O | Due to A/M work | 12 | 52.2 | Power interruption
Bhulta | 230 kV Bus-2 | 2023-01-12 08:48 | 2023-01-12 17:16 | 8:28 | S/O | Due to A/M work | 0 | 0 | No interruption
Maniknagar | 230/132 kV transformer Auxi TR-1 LT | 2023-01-12 08:57 | 2023-01-12 09:34 | 0:37 | S/O | Due to A/M work | 0 | 0 | No interruption
Sonargaon | 132 kV Bus-A | 2023-01-12 11:19 | 2023-01-12 15:10 | 3:51 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-1 LT | 2023-01-12 09:03 | 2023-01-12 17:26 | 8:23 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-1 HT | 2023-01-12 09:03 | 2023-01-12 17:18 | 8:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Srinagar | 132/33 kV transformer T-02 LT | 2023-01-14 08:00 | 2023-01-14 15:57 | 7:57 | S/O | Due to A/M work | 4 | 31.8 | Power interruption
Bhulta | 230 kV Bus-1 | 2023-01-14 09:20 | 2023-01-14 17:08 | 7:48 | S/O | Due to A/M work | 0 | 0 | No interruption
Nawabganj | 132/33 kV transformer T-1 HT |  | 2023-01-14 14:04 |  | S/O | After maint.work | 0 | 0 | No interruption
Shyampur | 230/132 kV transformer APR(D04) | 2023-01-16 12:18 | 2023-01-16 19:59 | 7:41 | S/O | Due to A/M work | 0 | 0 | No interruption
Bashundhara | 132/33 kV transformer GT-02 | 2023-01-17 09:38 | 2023-01-17 14:17 | 4:39 | S/O | Due to A/M work | 0 | 0 | No interruption
Bhulta | 230 kV Bus-2 |  | 2023-01-17 11:00 |  | S/O | After maint.work | 0 | 0 | No interruption
Satmosjid | 132/33 kV transformer T-2 HT | 2023-01-18 08:56 | 2023-01-18 15:47 | 6:51 | S/O | Due to A/M work | 0 | 0 | No interruption
Bhulta | 400/230 kV transformer ATR-02 HT | 2023-01-18 09:49 | 2023-01-18 17:03 | 7:14 | S/O | Due to A/M work | 0 | 0 | No interruption
| 400/230 kV transformer ATR-02 LT | 2023-01-18 09:49 | 2023-01-18 17:04 | 7:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Maniknagar | 230/132 kV Auto transformer 02 LT | 2023-01-19 08:24 | 2023-01-19 08:24 | 0:00 | S/O | Due to project vwork | 0 | 0 | No interruption
| 230/132 kV Auto transformer 02 HT | 2023-01-19 08:25 | 2023-01-19 08:25 | 0:00 | S/O |  | 0 | 0 | No interruption
Bhulta | 400/230 kV transformer ATR-02 LT | 2023-01-19 08:57 | 2023-01-19 17:34 | 8:37 | S/O | Due to A/M work | 0 | 0 | No interruption
| 400/230 kV transformer ATR-02 HT | 2023-01-19 08:58 | 2023-01-19 17:33 | 8:35 | S/O | Due to A/M work | 0 | 0 | No interruption
Sonargaon | 132 kV Bus Coupler | 2023-01-19 10:30 | 2023-01-19 14:25 | 3:55 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-2 HT | 2023-01-20 08:18 | 2023-01-20 20:06 | 11:48 | S/O | Due to A/M work | 5 | 59 | Power interruption
| 132/33 kV transformer T-2 LT | 2023-01-20 08:18 | 2023-01-20 20:10 | 11:52 | S/O | Due to A/M work | 5 | 59.3333 | Power interruption
Maniknagar | 132/33 kV transformer GT-2 HT | 2023-01-20 09:17 | 2023-01-20 16:21 | 7:04 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-2 LT |  | 2023-01-20 20:52 |  | S/O | After maint.work | 0 | 0 | No interruption
| 132/33 kV transformer GT-2 HT |  | 2023-01-20 20:51 |  | S/O |  | 0 | 0 | No interruption
Nawabganj | 132/33 kV transformer T-1 LT | 2023-01-22 09:04 | 2023-01-22 16:06 | 7:02 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-1 HT | 2023-01-22 09:05 | 2023-01-22 16:05 | 7:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Rampura | 230 kV Basbar-1 | 2023-01-22 09:45 | 2023-01-22 15:44 | 5:59 | S/O | Due to A/M work | 0 | 0 | No interruption
Page: 8/16 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: January 2023
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (South) Grid Circle :
Nawabganj | 132/33 kV transformer T-1 LT | 2023-01-23 08:29 | 2023-01-23 16:02 | 7:33 | S/O | Due to A/M work | 0 | 0 | No interruption
Rampura | 230 kV Bas-2 | 2023-01-23 08:55 | 2023-01-23 16:17 | 7:22 | S/O | Due to A/M work | 0 | 0 | No interruption
Sonargaon | 132/33 kV transformer T-r2 LT | 2023-01-24 08:15 | 2023-01-24 13:04 | 4:49 | S/O | Due to Corrective maintenance work | 30 | 144.5 | Power interruption
| 132/33 kV transformer T-r2 HT | 2023-01-24 08:15 | 2023-01-24 13:04 | 4:49 | S/O |  | 30 | 144.5 | Power interruption
Nawabganj | 132/33 kV transformer T-R-2 LT | 2023-01-24 09:09 | 2023-01-24 20:25 | 11:16 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-R-2 HT | 2023-01-24 09:09 | 2023-01-24 20:23 | 11:14 | S/O | Due to A/M work | 0 | 0 | No interruption
Sreenagar | 132/33 kV transformer T-1 LT & HT | 2023-01-24 09:15 | 2023-01-24 09:15 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Nawabganj | 132/33 kV transformer T-R-2 LT | 2023-01-25 07:34 | 2023-01-25 15:28 | 7:54 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-R-2 HT | 2023-01-25 07:36 | 2023-01-25 15:26 | 7:50 | S/O | Due to A/M work | 0 | 0 | No interruption
Haripur | 230/132kV transformer Auto TR-1 LT | 2023-01-25 09:21 | 2023-01-25 17:34 | 8:13 | S/O | Due to A/M work | 0 | 0 | No interruption
| 230/132kV transformer Auto TR-1 HT | 2023-01-25 09:21 | 2023-01-25 17:33 | 8:12 | S/O | Due to A/M work | 0 | 0 | No interruption
Nawabganj | 132 kV bus coupler | 2023-01-26 09:55 | 2023-01-26 09:55 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Sreenagar | 132/33 kV transformer T-1 HT |  | 2023-01-27 10:28 |  | S/O | After maint.work | 0 | 0 | No interruption
| 132/33 kV transformer T-1 LT |  | 2023-01-27 10:30 |  | S/O |  | 0 | 0 | No interruption
Maniknagar | 230/132kV transformer Auto TR-1 LT | 2023-01-28 10:03 | 2023-01-28 16:54 | 6:51 | S/O | Due to A/M work | 0 | 0 | No interruption
| 230/132kV transformer Auto TR-1 HT | 2023-01-28 10:04 | 2023-01-28 16:54 | 6:50 | S/O | Due to A/M work | 0 | 0 | No interruption
Shyampur | 230/132kV transformer APR(D04) |  | 2023-01-29 09:09 |  | S/O | After maint.work | 0 | 0 | No interruption
Madanganj | 132/33 kV transformer GT-2 LT | 2023-01-29 09:36 | 2023-01-29 09:36 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Purbachol | 132/33 kV transformer GT-2 | 2023-01-29 09:37 | 2023-01-29 09:37 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Nawabganj | 132 kV main Bus-2 | 2023-01-30 15:12 | 2023-01-30 16:56 | 1:44 | S/O | Due to A/M work | 0 | 0 | No interruption
Aftabnagar | 132/33 kV transformer GT-2 | 2023-01-31 09:53 | 2023-01-31 09:53 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Nawabganj | 132 kV main Bus-1 | 2023-01-31 10:33 | 2023-01-31 15:35 | 5:02 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 361:40 |  | Unserved Energy: |  | 557.6667
Chattogram Grid Circle :
Chandraghona | 132/33 kV transformer TR-01(406T)LT | 2023-01-03 10:35 | 2023-01-03 11:21 | 0:46 | S/O | Due to A/M work | 7 | 5.3667 | Power interruption
| 132/33 kV transformer TR-02(406T)LT | 2023-01-03 10:35 | 2023-01-03 12:26 | 1:51 | S/O | Due to A/M work | 7 | 12.95 | Power interruption
| 132/33 kV transformer TR-01(406T)HT | 2023-01-03 10:36 | 2023-01-03 11:21 | 0:45 | S/O | Due to A/M work | 7 | 5.25 | Power interruption
| 132 kV main Bus-1 | 2023-01-03 10:36 | 2023-01-03 10:56 | 0:20 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer TR-02(416T) HT | 2023-01-03 10:36 | 2023-01-03 12:26 | 1:50 | S/O | Due to A/M work | 7 | 12.8333 | Power interruption
Rangamati | 132/33 kV transformer TR2 HT(415) LT | 2023-01-03 10:39 | 2023-01-03 16:32 | 5:53 | S/O | Due to relay testing | 0 | 0 | No interruption
Madunaghat | 132/33 kV transformer TR1 LT(5017) LT | 2023-01-03 14:52 | 2023-01-03 14:52 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Cox'sbazar | 132/33 kV transformer( 405T) T1 HT | 2023-01-06 08:26 | 2023-01-06 13:14 | 4:48 | S/O | Due to A/M work | 0 | 0 | No interruption
Halishahar | 132/33 kV transformer( 413T) TR-2 HT |  | 2023-01-06 16:25 |  | S/O | After maint.work | 0 | 0 | No interruption
| 132/33 kV transformer T-03 HT | 2023-01-07 08:23 | 2023-01-07 13:40 | 5:17 | S/O | Due to A/M work | 40 | 211.3333 | Power interruption
Khulshi | 132 kV main Bus |  | 2023-01-07 11:02 |  | S/O | After maint.work | 0 | 0 | No interruption
Cox'sbazar | 132/33 kV transformer( 405T) T1 HT | 2023-01-08 08:06 | 2023-01-08 11:14 | 3:08 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer( 415T) T2 HT | 2023-01-08 08:28 | 2023-01-08 13:37 | 5:09 | S/O | Due to A/M work | 17 | 87.55 | Power interruption
Chandraghona | 132/33 kV transformer TR-01(406T)LT & HT | 2023-01-08 09:48 | 2023-01-08 17:21 | 7:33 | S/O | Due to project work | 0 | 0 | No interruption
| 132/33 kV transformer TR-01(406T)LT | 2023-01-09 09:26 | 2023-01-09 17:21 | 7:55 | S/O | Due to project work | 0 | 0 | No interruption
| 132/33 kV transformer TR-01(406T)HT | 2023-01-09 09:28 | 2023-01-09 17:40 | 8:12 | S/O | Due to project work | 0 | 0 | No interruption
Dohazari | 132/33 kV transformer T1 LT | 2023-01-11 09:40 | 2023-01-11 15:32 | 5:52 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T1 HT | 2023-01-11 09:40 | 2023-01-11 15:31 | 5:51 | S/O | Due to A/M work | 0 | 0 | No interruption
Chandraghona | 132/33 kV transformer TR-01(406T)LT | 2023-01-11 09:46 | 2023-01-11 15:45 | 5:59 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer TR-01(406T)HT | 2023-01-11 09:46 | 2023-01-11 15:44 | 5:58 | S/O | Due to A/M work | 0 | 0 | No interruption
Dohazari | 132/33 kV transformer T2 LT | 2023-01-12 08:09 | 2023-01-12 17:22 | 9:13 | S/O | Due to A/M work | 0 | 0 | No interruption
Khagrachari | 132/33 kV transformer TR LT | 2023-01-13 10:03 | 2023-01-13 12:31 | 2:28 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer TR HT | 2023-01-13 10:04 | 2023-01-13 12:29 | 2:25 | S/O | Due to A/M work | 0 | 0 | No interruption
Madaunaghat | 132/33 kV transformer TR2 HT | 2023-01-14 08:14 | 2023-01-14 14:31 | 6:17 | S/O | Due to A/M work | 0 | 0 | No interruption
Juldah | 132/33 kV transformer T2 416 TLT | 2023-01-14 08:32 | 2023-01-14 13:56 | 5:24 | S/O | Due to A/M work | 0 | 0 | No interruption
Madaunaghat | 132/33 kV transformer TR -1 LT |  | 2023-01-14 09:22 |  |  | After maint.work | 0 | 0 | No interruption
| 132/33 kV transformer TR -1 HT | 2023-01-14 09:31 | 2023-01-14 13:32 | 4:01 | S/O | Due to A/M work | 0 | 0 | No interruption
KSRM | 132/33 kV transformer T02 LT | 2023-01-15 09:45 | 2023-01-15 16:37 | 6:52 | S/O | Due to preventive maintenance 33 kv bus | 0 | 0 | No interruption
| 132/33 kV transformer T -02 HT | 2023-01-15 09:49 | 2023-01-15 16:38 | 6:49 | S/O |  | 0 | 0 | No interruption
Chandraghona | 132/33 kV transformer TR-01(406T)LT | 2023-01-15 10:08 | 2023-01-15 15:22 | 5:14 | S/O | Due to project work | 0 | 0 | No interruption
Page: 9/16 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: January 2023
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Chattogram Grid Circle :
Chandraghona | 132/33 kV transformer TR-01(406T)HT | 2023-01-15 10:08 | 2023-01-15 15:21 | 5:13 | S/O | Due to project work | 0 | 0 | No interruption
Dohazari | 132/33 kV transformer T2 LT | 2023-01-15 10:45 | 2023-01-15 12:16 | 1:31 | S/O | Due to project work | 0 | 0 | No interruption
| 132/33 kV transformer T2 HT | 2023-01-15 10:46 | 2023-01-15 12:15 | 1:29 | S/O | Due to project work | 0 | 0 | No interruption
Khagrachari | 132/33 kV transformer TR1 HT |  | 2023-01-16 14:47 |  | S/O | After maint.work | 0 | 0 | No interruption
Dohazari | 132/33 kV transformer T2 HT | 2023-01-17 06:19 | 2023-01-17 06:19 | 0:00 | S/O | Due to project work | 0 | 0 | No interruption
| 132/33 kV transformer T2 LT | 2023-01-17 06:20 | 2023-01-17 06:20 | 0:00 | S/O |  | 0 | 0 | No interruption
Chandraghona | 132/33 kV transformer TR-01(406T) HT | 2023-01-17 08:16 | 2023-01-17 15:21 | 7:05 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer TR-01(406T) LT | 2023-01-17 08:17 | 2023-01-17 15:21 | 7:04 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T2 HT |  | 2023-01-17 16:08 |  | S/O | After maint.work | 0 | 0 | No interruption
| 132/33 kV transformer T2 LT |  | 2023-01-17 16:09 |  | S/O |  | 0 | 0 | No interruption
Dohazari | 132/33 kV transformer T2 LT | 2023-01-18 06:11 | 2023-01-18 06:11 | 0:00 | S/O | Due to project work | 0 | 0 | No interruption
| 132/33 kV transformer T2 HT | 2023-01-18 06:12 | 2023-01-18 06:12 | 0:00 | S/O |  | 0 | 0 | No interruption
Chandraghona | 132/33 kV transformer TR-02(416T) LT | 2023-01-18 08:22 | 2023-01-18 16:07 | 7:45 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer TR-02(416T) HT | 2023-01-18 08:23 | 2023-01-18 16:05 | 7:42 | S/O | Due to A/M work | 0 | 0 | No interruption
Dohazari | 132/33 kV transformer T2 HT |  | 2023-01-18 16:24 |  | S/O | After maint.work | 0 | 0 | No interruption
| 132/33 kV transformer T2 LT |  | 2023-01-18 16:25 |  | S/O |  | 0 | 0 | No interruption
| 132/33 kV transformer T2 LT | 2023-01-19 06:36 | 2023-01-21 11:43 | 53:07 | S/O | Due to 33kv piling work. | 0 | 0 | No interruption
| 132/33 kV transformer T2 HT | 2023-01-19 06:37 | 2023-01-19 16:46 | 10:09 | S/O |  | 0 | 0 | No interruption
| 132/33 kV transformer T2 HT & LT | 2023-01-21 06:41 | 2023-01-21 06:41 | 0:00 | S/O | Due to project work | 0 | 0 | No interruption
Sikalbaha | 230/132kV Transformer ATR 02 HT | 2023-01-21 09:28 | 2023-01-21 17:13 | 7:45 | S/O | Due to A/M work | 0 | 0 | No interruption
Chandraghona | 132 kV main Bus-1 | 2023-01-22 08:31 | 2023-01-22 14:27 | 5:56 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T1 HT | 2023-01-22 11:01 | 2023-01-22 15:32 | 4:31 | S/O | Due to project work | 0 | 0 | No interruption
| 132 kV main Bus-2 | 2023-01-23 08:32 | 2023-01-23 14:21 | 5:49 | S/O | Due to A/M work | 0 | 0 | No interruption
T.K chemical | 48/64MVA T-2(415T) LT | 2023-01-24 08:47 | 2023-01-24 08:47 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Chandraghona | 132/33 kV transformer TR-1(406T) LT | 2023-01-24 09:07 | 2023-01-24 14:55 | 5:48 | S/O | Due to project work | 0 | 0 | No interruption
| 132/33 kV transformer TR-1(406T) HT | 2023-01-24 09:08 | 2023-01-24 14:55 | 5:47 | S/O | Due to A/M work | 0 | 0 | No interruption
T.K chemical | 50/75 MVA T-1(405T) HT | 2023-01-24 09:16 | 2023-01-24 09:16 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
| 48/64MVA T-2(415T) HT | 2023-01-24 09:17 | 2023-01-24 09:17 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Kharachari | 132/33 kV transformer T1 HT | 2023-01-25 08:18 | 2023-01-25 17:42 | 9:24 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T2 HT | 2023-01-26 08:37 | 2023-01-26 15:58 | 7:21 | S/O | Due to A/M work | 0 | 0 | No interruption
Chandraghona | 132/33 kV transformer TR-1(406T) LT | 2023-01-28 10:15 | 2023-01-28 15:21 | 5:06 | S/O | Due to project work | 0 | 0 | No interruption
| 132/33 kV transformer TR-1(406T) HT | 2023-01-28 10:16 | 2023-01-28 15:21 | 5:05 | S/O |  | 0 | 0 | No interruption
| 132/33 kV transformer TR-1(406T) HT | 2023-01-30 09:09 | 2023-01-30 14:33 | 5:24 | S/O | Due to project work | 0 | 0 | No interruption
|  |  | Total : | 294:51 |  | Unserved Energy: |  | 335.2833
Cumilla Grid Circle :
Chattak | 132/33 kV transformer T1 HT & LT | 2023-01-01 10:55 | 2023-01-01 13:35 | 2:40 | S/O | Due to maint.work | 0 | 0 | No interruption
| 132 kV Bus-A | 2023-01-01 11:10 | 2023-01-01 11:10 | 0:00 | S/O |  | 0 | 0 | No interruption
| 132/33 kV transformer T-3 HT | 2023-01-01 13:55 | 2023-01-01 15:07 | 1:12 | S/O | Due to A/M work | 0 | 0 | No interruption
Chaddagram | 132/33 kV transformer T-2 LT HT | 2023-01-02 07:46 | 2023-01-02 17:27 | 9:41 | S/O | Due to A/M work | 0 | 0 | No interruption
Sunamganj | 132 kV Bus-2 | 2023-01-02 08:38 | 2023-01-02 16:37 | 7:59 | S/O | Due to A/M work | 18 | 143.7 | Power interruption
Fenchuganj | 230/132 kV transformer T02 HT | 2023-01-02 08:43 | 2023-01-02 17:30 | 8:47 | S/O | Due to relay testing | 0 | 0 | No interruption
| 230/132 kV transformer T02 LT | 2023-01-02 08:43 | 2023-01-02 17:32 | 8:49 | S/O |  | 0 | 0 | No interruption
Beanibazar | 132 kV Bus-1 | 2023-01-02 10:16 | 2023-01-02 15:32 | 5:16 | S/O | Due to A/M work | 0 | 0 | No interruption
Sylhet | 132/33 kV transformer T-4 LT & HT | 2023-01-03 09:03 | 2023-01-03 10:58 | 1:55 | S/O | Due to oil collection of test. | 0 | 0 | No interruption
Fenchuganj | 230/132 kV transformer T01 HT & LT | 2023-01-03 10:32 | 2023-01-03 10:32 | 0:00 | S/O | Due to painting work | 0 | 0 | No interruption
Chattak | 132 kV Bus-A |  | 2023-01-03 10:32 |  | S/O | After maint.work | 0 | 0 | No interruption
| 132/33 kV transformer T02 HT |  | 2023-01-03 13:42 |  | S/O |  | 0 | 0 | No interruption
Sylhet | 132/33 kV transformer T-1 HT |  | 2023-01-03 15:46 |  | S/O | After maint.work | 0 | 0 | No interruption
Cumilla(N) | 230/132 kV transformer T04 HT | 2023-01-04 10:55 | 2023-01-04 14:09 | 3:14 | S/O | Due to maint.work | 0 | 0 | No interruption
Page: 10/16 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: January 2023
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Cumilla Grid Circle :
Cumilla(N) | 230/132 kV transformer T02 HT | 2023-01-06 09:58 | 2023-01-06 17:08 | 7:10 | S/O | Due to A/M work | 0 | 0 | No interruption
| 230/132 kV transformer T02 LT | 2023-01-06 09:58 | 2023-01-06 17:09 | 7:11 | S/O | Due to A/M work | 0 | 0 | No interruption
Cumilla(S) | 132/33 kV transformer TR-1 LT | 2023-01-07 08:54 | 2023-01-07 12:49 | 3:55 | S/O | Due to 33 kV Bus-1 maint.work | 16 | 62.6667 | Power interruption
| 132/33 kV transformer TR-2 LT | 2023-01-07 08:54 | 2023-01-07 12:50 | 3:56 | S/O | Due to 33 kV Bus-2 maint.work | 0 | 0 | No interruption
| 132/33 kV transformer TR-1 HT | 2023-01-07 08:55 | 2023-01-07 12:49 | 3:54 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer TR-2 HT | 2023-01-07 08:56 | 2023-01-07 12:50 | 3:54 | S/O | Due to 33 kV Bus-2maint.work | 0 | 0 | No interruption
Chowmuhani | 132/33 kV transformer TR-3-435 HT | 2023-01-07 09:09 | 2023-01-07 10:20 | 1:11 | S/O | Due to 33 kV Bus-maint.work | 0 | 0 | No interruption
| 132/33 kV transformer TR-3-435 LT | 2023-01-07 09:10 | 2023-01-07 10:20 | 1:10 | S/O |  | 0 | 0 | No interruption
Cumilla(N) | 230/132 kV transformer T02 LT | 2023-01-07 09:13 | 2023-01-07 15:17 | 6:04 | S/O | Due to A/M work | 0 | 0 | No interruption
| 230/132 kV transformer T02 HT | 2023-01-07 09:13 | 2023-01-07 15:16 | 6:03 | S/O | Due to A/M work | 20 | 121 | Power interruption
Chowmuhani | 132/33 kV transformer TR-3-425 HT & LT | 2023-01-07 09:57 | 2023-01-07 13:25 | 3:28 | S/O |  | 0 | 0 | No interruption
Ashuganj | 230 kV Bus coupler | 2023-01-09 08:45 | 2023-01-09 08:45 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Daudkandi | 132/33 kV transformer TR-3 LT | 2023-01-09 09:35 | 2023-01-09 16:43 | 7:08 | S/O | Due to relay testing | 0 | 0 | No interruption
| 132/33 kV transformer TR-3 HT | 2023-01-09 09:36 | 2023-01-09 16:42 | 7:06 | S/O | Due to relay testing | 0 | 0 | No interruption
| 132/33 kV transformer T-1 LT | 2023-01-10 09:02 | 2023-01-10 12:47 | 3:45 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-1 HT | 2023-01-10 09:03 | 2023-01-10 12:45 | 3:42 | S/O | Due to A/M work | 0 | 0 | No interruption
Fenchuganj | 230/132 kV transformer T01 HT |  | 2023-01-10 09:10 |  | S/O | After maint.work | 0 | 0 | No interruption
| 230/132 kV transformer T01 LT |  | 2023-01-10 09:11 |  | S/O | Due to relay testing | 0 | 0 | No interruption
Shahjibazar | 132/33 kV transformer T-02 LT | 2023-01-10 09:59 | 2023-01-10 17:11 | 7:12 | S/O | Due to relay testing | 0 | 0 | No interruption
| 132/33 kV transformer T-02 HT | 2023-01-10 10:02 | 2023-01-10 17:10 | 7:08 | S/O | Due to relay testing | 0 | 0 | No interruption
Daudkandi | 132/33 kV transformer T-2 LT | 2023-01-10 12:54 | 2023-01-10 16:30 | 3:36 | S/O | Due to relay testing | 0 | 0 | No interruption
| 132/33 kV transformer T-2 HT | 2023-01-10 12:54 | 2023-01-10 16:28 | 3:34 | S/O |  | 0 | 0 | No interruption
Chandpur | 132/33 kV transformer 422 T- LT | 2023-01-10 13:09 | 2023-01-10 14:32 | 1:23 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer 422 T- HT | 2023-01-10 13:10 | 2023-01-10 14:32 | 1:22 | S/O | Due to A/M work | 0 | 0 | No interruption
Kulaura | 132/33 kV transformer TR-1 LT | 2023-01-11 08:11 | 2023-01-11 17:46 | 9:35 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer TR-1 HT | 2023-01-11 08:12 | 2023-01-11 17:45 | 9:33 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer TR-2 LT | 2023-01-12 08:22 | 2023-01-12 17:27 | 9:05 | S/O | Due to A/M work | 0 | 0 | No interruption
Sylhet | 132/33 kV transformer T-2 LT | 2023-01-12 08:57 | 2023-01-12 17:12 | 8:15 | S/O | Due to A/M work | 14 | 115.5 | Power interruption
Beanibazar | 132 kV Bus-1 | 2023-01-12 09:38 | 2023-01-12 17:07 | 7:29 | S/O | Due to A/M work | 0 | 0 | No interruption
Chaddagram | 132/33 kV transformer T-2 LT | 2023-01-12 15:35 | 2023-01-12 16:59 | 1:24 | S/O | Due to A/M work | 0 | 0 | No interruption
Chandpur | 132/33 kV transformer 412 T- HT | 2023-01-14 07:30 | 2023-01-14 07:30 | 0:00 | S/O | Due to maint.of 33 kV feeder | 0 | 0 | No interruption
Sylhet | 132/33 kV transformer T-1 LT | 2023-01-14 09:17 | 2023-01-14 15:47 | 6:30 | S/O | Due to Ten delta test . | 0 | 0 | No interruption
| 132/33 kV transformer 412 T- HT |  | 2023-01-14 14:16 |  | S/O | After maint.work | 0 | 0 | No interruption
| 132/33 kV transformer T-4 LT & HT | 2023-01-15 09:28 | 2023-01-15 14:41 | 5:13 | S/O | Due to A/M work | 0 | 0 | No interruption
Beanibazar | 132 kV Bus-1 | 2023-01-15 11:12 | 2023-01-15 15:17 | 4:05 | S/O | Due to A/M work | 0 | 0 | No interruption
B.Baria | 132/33 kV transformer 402T LT | 2023-01-15 11:35 | 2023-01-15 12:29 | 0:54 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer 402T HT | 2023-01-15 11:35 | 2023-01-15 12:24 | 0:49 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer 402T HT | 2023-01-15 12:26 | 2023-01-15 12:29 | 0:03 | S/O | Due to A/M work | 0 | 0 | No interruption
Fenchuganj | 230/132 kV transformer T02 HT | 2023-01-16 10:12 | 2023-01-16 16:48 | 6:36 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132 kV Bus-2 | 2023-01-16 10:16 | 2023-01-16 16:30 | 6:14 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer 422T LT | 2023-01-16 14:29 | 2023-01-16 14:56 | 0:27 | S/O | Due to A/M work | 18 | 8.1 | Power interruption
| 132/33 kV transformer 422T HT | 2023-01-16 14:30 | 2023-01-16 14:55 | 0:25 | S/O | Due to A/M work | 0 | 0 | No interruption
Cumilla(N) | 230/132 kV transformer T05 HT & LT | 2023-01-17 07:29 | 2023-01-17 19:25 | 11:56 | S/O | Due to A/M work | 0 | 0 | No interruption
Fenchuganj | 230/132 kV transformer T02 HT | 2023-01-17 09:38 | 2023-01-17 15:52 | 6:14 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132 kV Bus-2 | 2023-01-17 09:42 | 2023-01-17 15:46 | 6:04 | S/O | Due to A/M work | 0 | 0 | No interruption
Shahjibazar | 230/132 kV transformer T02 HT | 2023-01-17 11:03 | 2023-01-17 12:00 | 0:57 | S/O | Due to New multifunction meter Installation | 0 | 0 | No interruption
Page: 11/16 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: January 2023
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Cumilla Grid Circle :
Shahjibazar | 230/132 kV transformer T02 LT | 2023-01-17 11:03 | 2023-01-17 12:19 | 1:16 | S/O |  | 0 | 0 | No interruption
| 132/33 kV transformer T04 LT | 2023-01-17 12:23 | 2023-01-17 13:27 | 1:04 | S/O | Due to New multifunction meter Installation. | 0 | 0 | No interruption
| 132/33 kV transformer T04 HT | 2023-01-17 12:24 | 2023-01-17 13:15 | 0:51 | S/O |  | 0 | 0 | No interruption
| 132/33 kV transformer T06 LT | 2023-01-17 13:34 | 2023-01-17 19:39 | 6:05 | S/O |  | 13 | 79.0833 | Power interruption
| 132/33 kV transformer TR-06 HT | 2023-01-17 13:35 | 2023-01-17 14:46 | 1:11 | S/O | Due to New multifunction meter Installation. | 0 | 0 | No interruption
Fenchuganj | 230/132 kV transformer T02 HT | 2023-01-18 09:29 | 2023-01-18 17:13 | 7:44 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132 kV Bus-2 | 2023-01-18 09:36 | 2023-01-18 17:07 | 7:31 | S/O | Due to A/M work | 0 | 0 | No interruption
Kachua | 132/33 kV transformer TR-01 LT | 2023-01-18 12:33 | 2023-01-18 14:06 | 1:33 | S/O | Due to 33 KV Kachua-1 Feeder bus DS connection. | 0 | 0 | No interruption
| 132/33 kV transformer TR-01 HT | 2023-01-18 12:34 | 2023-01-18 14:05 | 1:31 | S/O |  | 0 | 0 | No interruption
Sreemongal | 132/33 kV transformer TR-03 LT | 2023-01-19 11:03 | 2023-01-19 12:51 | 1:48 | S/O | Due to Installation work | 0 | 0 | No interruption
| 132/33 kV transformer TR-02 LT | 2023-01-19 11:03 | 2023-01-19 12:51 | 1:48 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer TR-02 HT | 2023-01-19 11:05 | 2023-01-19 12:13 | 1:08 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer TR-03 HT | 2023-01-19 11:05 | 2023-01-19 13:13 | 2:08 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer TR-01AB LT | 2023-01-19 12:48 | 2023-01-19 14:35 | 1:47 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer TR-01AB HT | 2023-01-19 13:10 | 2023-01-19 14:30 | 1:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Chowmuhani | 132/33 kV transformer TR-1-415TLT | 2023-01-20 08:14 | 2023-01-20 14:36 | 6:22 | S/O | Due to A/M work | 30 | 191 | Power interruption
| 132/33 kV transformer TR-1-415THT | 2023-01-20 08:14 | 2023-01-20 14:42 | 6:28 | S/O | Due to A/M work | 30 | 194 | Power interruption
| 132/33 kV transformer TR-2-425T LT | 2023-01-20 08:16 | 2023-01-20 17:13 | 8:57 | S/O | Due to A/M work | 34 | 304.3 | Power interruption
| 132/33 kV transformer TR-2-425THT | 2023-01-20 08:16 | 2023-01-20 17:13 | 8:57 | S/O | Due to A/M work | 34 | 304.3 | Power interruption
| 132/33 kV transformer TR-2-435T LT | 2023-01-20 08:28 | 2023-01-20 11:10 | 2:42 | S/O | Due to A/M work | 22 | 59.4 | Power interruption
| 132/33 kV transformer TR-2-435T LT | 2023-01-20 08:28 | 2023-01-20 11:08 | 2:40 | S/O | Due to A/M work | 22 | 58.6667 | Power interruption
| 132 kV main Bus | 2023-01-20 08:31 | 2023-01-20 17:18 | 8:47 | S/O | Due to A/M work | 86 | 755.3667 | Power interruption
| 132/33 kV transformer TR-2-435T LT | 2023-01-20 14:36 | 2023-01-20 17:18 | 2:42 | S/O | Due to maint.work | 0 | 0 | No interruption
| 132/33 kV transformer TR-2-435 HT | 2023-01-20 14:36 | 2023-01-20 17:15 | 2:39 | S/O |  | 0 | 0 | No interruption
Chandpur | 132/33 kV transformer TR-402 LT | 2023-01-21 07:26 | 2023-01-21 14:15 | 6:49 | S/O | Due to maint.work | 5.5 | 37.4917 | Power interruption
| 132/33 kV transformer TR-402 HT | 2023-01-21 07:28 | 2023-01-21 14:16 | 6:48 | S/O | Due to maint.work | 5.5 | 37.4 | Power interruption
Sylhet | 132/33 kV transformer T-4- LT | 2023-01-21 09:01 | 2023-01-21 09:01 | 0:00 | S/O | After maint.work | 0 | 0 | No interruption
| 132/33 kV transformer T-4- LT | 2023-01-21 09:10 | 2023-01-21 09:10 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-2- HT | 2023-01-21 09:11 | 2023-01-21 15:34 | 6:23 | S/O | Due to A/M work | 0 | 0 | No interruption
Kulaura | 132 kV Bus-A | 2023-01-21 09:55 | 2023-01-22 12:01 | 26:06 | S/O | Due to A/M work | 0 | 0 | No interruption
Chandpur | 132/33 kV transformer TR-402 LT | 2023-01-22 07:26 | 2023-01-22 07:26 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer TR-402 HT | 2023-01-22 07:28 | 2023-01-22 07:28 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Beanibazar | 132/33 kV transformer TR02-LT | 2023-01-22 08:47 | 2023-01-22 16:58 | 8:11 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer TR02-HT | 2023-01-22 08:48 | 2023-01-22 16:54 | 8:06 | S/O | Due to A/M work | 0 | 0 | No interruption
Kulaura | 132 kV Bus-A | 2023-01-22 12:01 | 2023-01-22 12:01 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Beanibazar | 132/33 kV transformer TR-2 LT | 2023-01-23 09:09 | 2023-01-23 16:34 | 7:25 | S/O | Due to A/M work | 0 | 0 | No interruption
Sylhet | 132/33 kV transformer T-2- HT | 2023-01-23 09:11 | 2023-01-23 14:54 | 5:43 | S/O | Due to A/M work | 0 | 0 | No interruption
Beanibazar | 132 kV Bus-A | 2023-01-23 11:35 | 2023-01-23 16:32 | 4:57 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer TR-402 LT | 2023-01-24 08:29 | 2023-01-24 13:22 | 4:53 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer TR-402 HT | 2023-01-24 08:30 | 2023-01-24 13:21 | 4:51 | S/O | Due to A/M work | 0 | 0 | No interruption
Sunamganj | 132/33 kV transformer TR01-HT | 2023-01-24 09:15 | 2023-01-24 09:15 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Chattak | 132/33 kV transformer T-3- LT | 2023-01-24 10:14 | 2023-01-24 12:25 | 2:11 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-3- HT | 2023-01-24 10:16 | 2023-01-25 12:25 | 26:09 | S/O | Due to A/M work | 0 | 0 | No interruption
Beanibazar | 132/33 kV transformer TR-1 LT | 2023-01-24 14:17 | 2023-01-24 17:07 | 2:50 | S/O | Due to Corrective maintenance | 0 | 0 | No interruption
Page: 12/16 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: January 2023
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Cumilla Grid Circle :
Beanibazar | 132/33 kV transformer TR-1 HT | 2023-01-24 14:19 | 2023-01-24 17:06 | 2:47 | S/O | Due to A/M work | 0 | 0 | No interruption
Shahjibazar | 132/33 kV transformer TR-06 LT | 2023-01-25 00:51 | 2023-01-25 00:51 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Daudkandi | 132/33 kV transformer T-3 LT | 2023-01-25 08:54 | 2023-01-25 12:19 | 3:25 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-3 HT | 2023-01-25 08:54 | 2023-01-25 12:17 | 3:23 | S/O | Due to maintenance work | 0 | 0 | No interruption
Beanibazar | 132/33 kV transformer TR-1 LT | 2023-01-25 09:08 | 2023-01-25 16:32 | 7:24 | S/O | Due to Earth blade adjustment. | 0 | 0 | No interruption
| 132/33 kV transformer TR-1 HT | 2023-01-25 09:09 | 2023-01-25 16:30 | 7:21 | S/O |  | 0 | 0 | No interruption
Sunamganj | 132/33 kV transformer TR-1 LT | 2023-01-25 10:01 | 2023-01-25 15:36 | 5:35 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer TR-1 HT | 2023-01-25 10:03 | 2023-01-25 15:34 | 5:31 | S/O | Due to A/M work | 0 | 0 | No interruption
Fenchuganj | 230/132 kV transformer T02 HT |  | 2023-01-25 16:54 |  | S/O | After maint.work | 0 | 0 | No interruption
| 230/132 kV transformer T02 LT |  | 2023-01-25 16:55 |  | S/O |  | 0 | 0 | No interruption
Beanibazar | 132/33 kV transformer TR-1 LT | 2023-01-26 09:13 | 2023-01-26 16:33 | 7:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Fenchuganj | 230/132 kV transformer T02 HT | 2023-01-26 09:13 | 2023-01-26 16:45 | 7:32 | S/O | Due to A/M work | 0 | 0 | No interruption
Beanibazar | 132/33 kV transformer TR-1 HT | 2023-01-26 09:14 | 2023-01-26 16:32 | 7:18 | S/O | Due to Earth blade adjustment. | 0 | 0 | No interruption
Fenchuganj | 230/132 kV transformer T02 LT | 2023-01-26 09:14 | 2023-01-26 16:45 | 7:31 | S/O | Due to A/M work | 0 | 0 | No interruption
Kachua | 132/33 kV transformer TR-1 LT | 2023-01-26 09:21 | 2023-01-26 11:50 | 2:29 | S/O | Due to work on relay panel. | 0 | 0 | No interruption
| 132/33 kV transformer TR-1 HT | 2023-01-26 09:22 | 2023-01-26 11:49 | 2:27 | S/O | Due to work on relay panel. | 0 | 0 | No interruption
| 132/33 kV transformer TR-2 LT | 2023-01-26 11:53 | 2023-01-26 14:13 | 2:20 | S/O | Due to work on relay panel. | 0 | 0 | No interruption
Shahjibazar | 132/33 kV transformer TR-06 LT |  | 2023-01-27 07:45 |  | S/O | After maint.work | 0 | 0 | No interruption
Sylhet | 132/33 kV transformer T-1- LT & HT | 2023-01-28 09:02 | 2023-01-28 14:19 | 5:17 | S/O | Due to A/M work | 9 | 47.55 | Power interruption
Fenchuganj | 230/132 kV transformer T02 HT | 2023-01-28 11:51 | 2023-01-28 17:40 | 5:49 | S/O |  | 0 | 0 | No interruption
B.Baria | 132/33 kV transformer 401T LT | 2023-01-29 08:59 | 2023-01-29 13:17 | 4:18 | S/O | Due to relay testing | 0 | 0 | No interruption
Cumilla(S) | 132/33 kV transformer TR-1 LT | 2023-01-29 09:21 | 2023-01-29 12:46 | 3:25 | S/O | Due to project work | 0 | 0 | No interruption
| 132/33 kV transformer TR-2 HT | 2023-01-29 12:50 | 2023-01-29 16:24 | 3:34 | S/O | Due to project work | 0 | 0 | No interruption
| 132/33 kV transformer TR-3 LT | 2023-01-30 10:03 | 2023-01-30 12:52 | 2:49 | S/O | Due to project work | 0 | 0 | No interruption
| 132/33 kV transformer TR-3 HT | 2023-01-30 10:04 | 2023-01-30 12:52 | 2:48 | S/O |  | 0 | 0 | No interruption
| 132/33 kV transformer TR-4 LT | 2023-01-30 13:03 | 2023-01-30 16:18 | 3:15 | S/O | Due to project work | 0 | 0 | No interruption
| 132/33 kV transformer TR-4 HT | 2023-01-30 13:04 | 2023-01-30 16:18 | 3:14 | S/O |  | 0 | 0 | No interruption
Sreemongal | 132/33 kV transformer T-2 LT | 2023-01-31 09:05 | 2023-01-31 14:50 | 5:45 | S/O | Due to relay testing | 0 | 0 | No interruption
| 132/33 kV transformer T-2 HT & T3 | 2023-01-31 09:06 | 2023-01-31 14:48 | 5:42 | S/O |  | 0 | 0 | No interruption
|  |  | Total : | 573:53 |  | Unserved Energy: |  | 2519.525
Page: 13/16 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: January 2023
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Khulna Grid Circle :
Faridpur | 132/33 kV transformer T3 LT | 2023-01-01 11:24 | 2023-01-01 11:24 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer T3 HT | 2023-01-01 11:25 | 2023-01-01 11:25 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Satkhira | 132/33 kV transformer T2 HT |  | 2023-01-01 17:45 |  | S/O | After maint.work | 0 | 0 | No interruption
| 132/33 kV transformer T2 LT |  | 2023-01-01 17:48 |  | S/O |  | 0 | 0 | No interruption
Magura | 132/33 kV transformer T1(405T) LT | 2023-01-02 08:20 | 2023-01-02 16:20 | 8:00 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T1(405T) HT | 2023-01-02 08:21 | 2023-01-02 16:18 | 7:57 | S/O | Due to A/M work | 0 | 0 | No interruption
Gollamari | 132/33 kV transformer Tr -2 LT | 2023-01-02 08:38 | 2023-01-02 11:51 | 3:13 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer Tr -2 HT | 2023-01-02 08:39 | 2023-01-02 11:50 | 3:11 | S/O |  | 0 | 0 | No interruption
Satkhira | 132/33 kV transformer T2 LT | 2023-01-02 09:40 | 2023-01-02 16:37 | 6:57 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T2 HT | 2023-01-02 09:40 | 2023-01-02 16:36 | 6:56 | S/O |  | 0 | 0 | No interruption
Gollamari | 132/33 kV transformer Tr -1 LT | 2023-01-02 13:05 | 2023-01-02 13:25 | 0:20 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer Tr -1 HT | 2023-01-02 13:06 | 2023-01-02 13:24 | 0:18 | S/O |  | 0 | 0 | No interruption
Magura | 132/33 kV transformer T1(405T) LT & HT | 2023-01-03 08:17 | 2023-01-03 15:48 | 7:31 | S/O | Due to C/M work | 0 | 0 | No interruption
Satkhira | 132/33 kV transformer T1 LT & HT | 2023-01-03 09:33 | 2023-01-03 09:33 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Payra | 400/230 kV transformer T03 LT | 2023-01-03 11:17 | 2023-01-03 15:20 | 4:03 | S/O | Due to Outgoing feeder connection. | 0 | 0 | No interruption
| 400/230 kV transformer T03 HT | 2023-01-03 11:18 | 2023-01-03 15:19 | 4:01 | S/O |  | 0 | 0 | No interruption
Satkhira | 132/33 kV transformer T1 HT | 2023-01-04 09:49 | 2023-01-04 14:58 | 5:09 | S/O | Due to A/M work | 0 | 0 | No interruption
Gollamari | 132/33 kV transformer Tr -2 LT | 2023-01-05 09:56 | 2023-01-05 18:17 | 8:21 | S/O | Due to project work | 0 | 0 | No interruption
| 132/33 kV transformer Tr1 HT | 2023-01-05 09:57 | 2023-01-05 18:16 | 8:19 | S/O | Due to project work | 0 | 0 | No interruption
Faridpur | 132/33 kV transformer T2 LT | 2023-01-06 08:17 | 2023-01-06 08:17 | 0:00 | S/O | Due to CB change | 0 | 0 | No interruption
| 132/33 kV transformer T2 HT | 2023-01-06 08:18 | 2023-01-06 08:18 | 0:00 | S/O |  | 0 | 0 | No interruption
Barguna | 132/33 kV transformer T1 LT | 2023-01-07 07:54 | 2023-01-07 14:52 | 6:58 | S/O |  | 0 | 0 | No interruption
| 132/33 kV transformer T1 HT | 2023-01-07 07:55 | 2023-01-07 14:52 | 6:57 | S/O | Due to A/M work | 0 | 0 | No interruption
Gollamari | 132 kV bus coupler | 2023-01-08 09:29 | 2023-01-08 21:07 | 11:38 | S/O | Due to A/M work | 0 | 0 | No interruption
Faridpur | 132/33 kV transformer T2 HT |  | 2023-01-08 11:20 |  | S/O | After maint.work | 0 | 0 | No interruption
| 132/33 kV transformer T2 LT |  | 2023-01-08 11:22 |  | S/O |  | 0 | 0 | No interruption
Gopalganj | 400/132 kV transformer T1 |  | 2023-01-08 20:30 |  | S/O | After maint.work | 0 | 0 | No interruption
Gollamari | 132/33 kV transformer Tr -2 LT | 2023-01-09 10:02 | 2023-01-09 11:29 | 1:27 | S/O | Due to 33 kV bus maint.work | 0 | 0 | No interruption
| 132/33 kV transformer Tr1 HT | 2023-01-09 10:03 | 2023-01-09 11:28 | 1:25 | S/O |  | 0 | 0 | No interruption
| 132/33 kV transformer Tr -1 LT | 2023-01-10 11:16 | 2023-01-10 13:16 | 2:00 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer Tr -1 HT | 2023-01-10 11:17 | 2023-01-10 13:15 | 1:58 | S/O | Due to maint.work | 0 | 0 | No interruption
Khulna © | 132/33 kV transformer Tr -1 HT |  | 2023-01-10 15:05 |  | S/O | After maint.work | 0 | 0 | No interruption
| 132/33 kV transformer Tr -1 LT |  | 2023-01-10 15:06 |  | S/O |  | 0 | 0 | No interruption
| 132/33 kV transformer Tr -1 HT |  | 2023-01-16 14:15 |  | S/O |  | 0 | 0 | No interruption
Patuakhali | 132/33 kV transformer T3 LT | 2023-01-17 07:21 | 2023-01-17 08:21 | 1:00 | S/O | Due to 33 Kv capacitor bank DS loop remove | 0 | 0 | No interruption
| 132/33 kV transformer T3 HT | 2023-01-17 07:22 | 2023-01-17 08:21 | 0:59 | S/O |  | 0 | 0 | No interruption
| 132/33 kV transformer T1 HT & LT | 2023-01-17 08:25 | 2023-01-17 08:51 | 0:26 | S/O | Due to 33kv capacitor bank isolator DS loop removal | 8 | 3.4667 | Power interruption
| 132/33 kV transformer T2 HT |  | 2023-01-17 17:17 |  | S/O | After maint.work | 0 | 0 | No interruption
| 132/33 kV transformer T2 LT |  | 2023-01-17 17:18 |  | S/O |  | 0 | 0 | No interruption
Khulna © | 132 kV main Bus | 2023-01-19 08:50 | 2023-01-19 18:30 | 9:40 | S/O | Due to Bus DS Change. | 0 | 0 | No interruption
Payra | 400/132/33 kV Auto Transformer02 LT |  | 2023-01-20 16:13 |  | S/O | After maint.work | 0 | 0 | No interruption
| 400/132/33 kV Auto Transformer01 HT | 2023-01-20 16:17 | 2023-01-20 16:17 | 0:00 | S/O | Due to project work | 0 | 0 | No interruption
Faridpur | 132/33 kV transformer T1 LT | 2023-01-21 08:13 | 2023-01-21 14:43 | 6:30 | S/O | Due to project work | 19 | 123.5 | Power interruption
| 132/33 kV transformer T1 HT | 2023-01-21 08:13 | 2023-01-21 14:42 | 6:29 | S/O |  | 19 | 123.1833 | Power interruption
| 132/33 kV transformer T3 LT & HT | 2023-01-21 09:59 | 2023-01-21 14:45 | 4:46 | S/O | Due to project work | 0 | 0 | No interruption
Khulna © | 132/33 kV transformer TR-1 HT |  | 2023-01-21 17:05 |  | S/O | After maint.work | 0 | 0 | No interruption
|  |  | 2023-01-21 17:06 |  | S/O |  | 0 | 0 | No interruption
Madaripur | 132/33 kV transformer TR-1405 HT | 2023-01-22 13:33 | 2023-01-22 15:31 | 1:58 | S/O | Due to maint. work | 0 | 0 | No interruption
Payra | 400/132/33kV S/S 400/132/33 kV Auto Transformer-01 HT |  | 2023-01-22 22:35 |  | S/O | After maint.work | 0 | 0 | No interruption
Faridpur | 132/33 kV transformer T1 LT | 2023-01-24 06:58 | 2023-01-24 06:58 | 0:00 | S/O | Due to project work | 0 | 0 | No interruption
| 132/33 kV transformer T1 HT & LT | 2023-01-24 09:12 | 2023-01-24 09:12 | 0:00 | S/O | After maint.work | 0 | 0 | No interruption
Page: 14/16 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: January 2023
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Khulna Grid Circle :
Rampal | 400 kV Bus reactor | 2023-01-24 12:23 | 2023-01-24 12:23 | 0:00 | S/O | CSD commissioning. | 0 | 0 | No interruption
Payra | 400/132/33 kV Auto Transformer02 LT | 2023-01-25 10:31 | 2023-01-25 10:31 | 0:00 | S/O | Due to project work | 0 | 0 | No interruption
| 400/132/33 kV Auto Transformer02 HT | 2023-01-25 10:35 | 2023-01-25 10:35 | 0:00 | S/O |  | 0 | 0 | No interruption
Bhandaria | 132/33 kV transformer T2 LT | 2023-01-26 07:12 | 2023-01-26 11:11 | 3:59 | S/O | Due to project work | 0 | 0 | No interruption
| 132/33 kV transformer T2 HT | 2023-01-26 07:13 | 2023-01-26 11:12 | 3:59 | S/O |  | 0 | 0 | No interruption
Gopalganj | 400/132 kV transformer ATR3 LT | 2023-01-26 11:46 | 2023-01-26 15:48 | 4:02 | S/O | Due to project work | 0 | 0 | No interruption
| 400/132 kV transformer ATR01 LT | 2023-01-26 11:46 | 2023-01-26 15:39 | 3:53 | S/O | Due to project work | 0 | 0 | No interruption
Faridpur | 33 kV Bus | 2023-01-28 08:10 | 2023-01-28 13:30 | 5:20 | S/O | Due to installation work | 0 | 0 | No interruption
Payra | 400/132/33 kV Auto Transformer02 LT |  | 2023-01-29 08:58 |  | S/O | After maint.work | 0 | 0 | No interruption
| 400/132/33 kV Auto Transformer01LT | 2023-01-29 11:14 | 2023-01-29 11:14 | 0:00 | S/O | Due to project work | 0 | 0 | No interruption
Barishal | 132/33 kV transformer T4 LT | 2023-01-29 15:17 | 2023-01-29 15:58 | 0:41 | S/O | Due to project work | 0 | 0 | No interruption
| 132/33 kV transformer T5 LT | 2023-01-29 16:01 | 2023-01-29 16:50 | 0:49 | S/O | Due to project work | 0 | 0 | No interruption
| 230/132kV Transformer T-4 LT | 2023-01-30 10:45 | 2023-01-30 18:33 | 7:48 | S/O | Due to project work | 0 | 0 | No interruption
| 230/132kV Transformer T-4 HT | 2023-01-30 10:46 | 2023-01-30 18:30 | 7:44 | S/O |  | 0 | 0 | No interruption
Khulna (S) | 230/132kV Transformer T-R1 HT |  | 2023-01-30 16:55 |  | S/O | After maint.work | 0 | 0 | No interruption
| 230/132kV Transformer T-R1 LT |  | 2023-01-30 16:58 |  | S/O |  | 0 | 0 | No interruption
Shariatpur | 132/33 kV transformer T2 LT | 2023-01-31 09:21 | 2023-01-31 14:12 | 4:51 | S/O | Due to Annual Maintenance by PBS. | 0 | 0 | No interruption
| 132/33 kV transformer T2 HT | 2023-01-31 09:22 | 2023-01-31 14:11 | 4:49 | S/O |  | 0 | 0 | No interruption
| 132/33kV S/S Auxiliary Tarnsformer-02 (PGCB) LT | 2023-01-31 09:26 | 2023-01-31 12:01 | 2:35 | S/O |  | 0 | 0 | No interruption
| 132/33kV S/S Auxiliary Tarnsformer-02 (PGCB) HT | 2023-01-31 09:26 | 2023-01-31 12:02 | 2:36 | S/O |  | 0 | 0 | No interruption
| 33 kV Bus | 2023-01-31 09:30 | 2023-01-31 14:06 | 4:36 | S/O |  | 0 | 0 | No interruption
Faridpur | 132/33 kV transformer T3 LT | 2023-01-31 09:45 | 2023-01-31 16:50 | 7:05 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T3 HT | 2023-01-31 10:12 | 2023-01-31 13:33 | 3:21 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T4 LT | 2023-01-31 12:34 | 2023-01-31 17:38 | 5:04 | S/O | Due to SAS integration | 0 | 0 | No interruption
| 132/33 kV transformer T4 HT | 2023-01-31 12:35 | 2023-01-31 17:37 | 5:02 | S/O |  | 0 | 0 | No interruption
| 400/132/33 kV Auto Transformer01 LT & LT |  | 2023-01-31 22:53 |  | S/O | After maint.work | 0 | 0 | No interruption
|  |  | Total : | 216:41 |  | Unserved Energy : |  | 250.15
HVDC Grid Circle
Baghabari | 230/132 kV auxi transformer TR-1 LT | 2023-01-02 12:01 | 2023-01-02 12:01 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
| 230/132 kV auxi transformer TR-1 HT | 2023-01-02 12:04 | 2023-01-04 10:14 | 46:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Chuadanga | 132/33 kV transformer Tr2(426t) HT | 2023-01-04 08:13 | 2023-01-04 14:38 | 6:25 | S/O | Due to A/M work | 0 | 0 | No interruption
Ruppur | 132/11 kV Auxi transformer Tr-01 HT | 2023-01-04 08:30 | 2023-01-04 16:55 | 8:25 | S/O | Due to A/M work | 0 | 0 | No interruption
Ishurdi | 230/132 kV transformer T01 HT | 2023-01-04 09:15 | 2023-01-04 19:53 | 10:38 | S/O | Due to A/M work | 0 | 0 | No interruption
Baghabari | 230/132 kV transformer TR-2 LT | 2023-01-04 11:44 | 2023-01-04 11:44 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
| 230/132 kV auxi transformer TR-2 LT | 2023-01-04 11:45 | 2023-01-04 11:45 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Chuadanga | 132/33 kV transformer Tr3 HT | 2023-01-05 08:12 | 2023-01-05 14:32 | 6:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Baghabari | 230/132 kV transformer TR-2 HT |  | 2023-01-05 15:20 |  | S/O | Due to A/M work | 0 | 0 | No interruption
| 230/132 kV Auxiliary transformer TR-2 |  | 2023-01-05 15:20 |  | S/O | Due to A/M work | 0 | 0 | No interruption
| 230/132 kV transformer TR-2 LT |  | 2023-01-05 15:21 |  | S/O | Due to A/M work |  |  | No interruption
Kustia | 132/33 kV transformer T2 LT & HT | 2023-01-07 07:51 | 2023-01-07 17:06 | 9:15 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T2 HT | 2023-01-07 07:51 | 2023-01-07 17:08 | 9:17
| 132/33 kV transformer T01 LT | 2023-01-07 07:59 | 2023-01-07 16:57 | 8:58 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132 kV Bus-A & B | 2023-01-07 07:59 | 2023-01-07 16:51 | 8:52 | S/O | After maint.work | 0 | 0 | No interruption
| 132/33 kV transformer T01 HT | 2023-01-07 08:00 | 2023-01-07 16:56 | 8:56 | S/O | Due to A/M work | 0 | 0 | No interruption
Pabna | 132/33 kV transformer T03 LT | 2023-01-07 08:26 | 2023-01-07 15:39 | 7:13 | S/O | Due to A/M work | 0 | 0 | No interruption
BIPTC | BIPTC 11T01 HT & LT | 2023-01-07 08:38 | 2023-01-07 08:38 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
| BIPTC 21T01 LT | 2023-01-07 08:38 | 2023-01-07 08:38 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Pabna | 132/33 kV transformer T03 HT | 2023-01-07 09:20 | 2023-01-07 15:36 | 6:16 | S/O | Due to A/M work | 0 | 0 | No interruption
BIPTC | BIPTC 21T01 HT | 2023-01-07 09:38 |  |  | S/O | Due to A/M work | 0 | 0 | No interruption
HVDC | 230 kV 20DF42 Filter | 2023-01-07 16:38 | 2023-01-07 17:19 | 0:41 | S/O | Due to A/M work | 0 | 0 | No interruption
Page: 15/16 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: January 2023
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
HVDC Grid Circle
HVDC | 132/33 kV transformer T3 LT | 2023-01-08 08:37 | 2023-01-08 15:29 | 6:52 | S/O | Due to A/M work | 16 | 109.8667 | Power interruption
| 132/33 kV transformer T3 HT | 2023-01-08 08:38 | 2023-01-08 15:27 | 6:49 | S/O | Due to A/M work | 16 | 109.0667 | Power interruption
BIPTC | 400 kV Bus-1 | 2023-01-09 09:01 | 2023-01-09 16:58 | 7:57 | S/O | Due to A/M work | 0 | 0 | No interruption
HVDC | 400 kV filter Bus-1 | 2023-01-09 09:05 | 2023-01-09 09:05 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
BIPTC | 230 kV Bus-1 | 2023-01-10 10:10 | 2023-01-10 17:12 | 7:02 | S/O | Due to A/M work | 0 | 0 | No interruption
| BIPTC 21T01 LT |  | 2023-01-10 18:10 |  | S/O | After maint.work | 0 | 0 | No interruption
Jhenaidah | 230/132 kV transformer TR1 HT | 2023-01-11 08:40 | 2023-01-11 16:41 | 8:01 | S/O | Due to A/M work | 0 | 0 | No interruption
| 230/132 kV transformer TR1 LT | 2023-01-11 08:40 | 2023-01-11 16:44 | 8:04 | S/O | Due to A/M work | 0 | 0 | No interruption
Shahjadpur | 132/33 kV transformer T04 HT | 2023-01-11 12:28 | 2023-01-11 12:28 | 0:00 | S/O | After maint.work | 0 | 0 | No interruption
Jhenaidah | 230/132 kV transformer TR2 LT | 2023-01-12 09:06 | 2023-01-12 16:31 | 7:25 | S/O | Due to dead line checking | 0 | 0 | No interruption
| 230 kV Bus | 2023-01-15 10:04 | 2023-01-15 14:28 | 4:24 | S/O | Due to A/M work | 0 | 0 | No interruption
| 230 kV Bus | 2023-01-16 09:26 | 2023-01-16 13:25 | 3:59 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132 kV Bus-A | 2023-01-17 09:17 | 2023-01-17 13:27 | 4:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Ruppur | 132/11kV S/S TR-02 HT | 2023-01-18 09:07 | 2023-01-18 16:35 | 7:28 | S/O | Due to A/M work | 0 | 0 | No interruption
Jhenaidah | 132 kV Bus-2 | 2023-01-18 09:27 | 2023-01-18 12:34 | 3:07 | S/O | Due to A/M work | 0 | 0 | No interruption
HVDC | pole-1 | 2023-01-19 00:46 | 2023-01-19 02:33 | 1:47 | S/O | Due to A/M work | 0 | 0 | No interruption
BIPTC | 21T01 LT | 2023-01-19 00:46 | 2023-01-19 02:33 | 1:47 | S/O | Due to A/M work | 0 | 0 | No interruption
Pabna | 132 kV main Bus | 2023-01-21 08:31 | 2023-01-21 14:38 | 6:07 | S/O | Due to A/M work | 35 | 214.0833 | Power interruption
Noapara | 132 kV Bus-B | 2023-01-23 07:27 | 2023-01-23 13:07 | 5:40 | S/O | Due to Upgradation | 0 | 0 | No interruption
Pabna | 132/33 kV transformer T01LT |  | 2023-01-23 21:43 |  | S/O | Due to A/M work | 0 | 0 | No interruption
Ishurdi | 132/33 kV transformer T02 HT | 2023-01-25 08:12 | 2023-01-25 17:01 | 8:49 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T02 LT | 2023-01-25 08:12 | 2023-01-25 17:10 | 8:58 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T02 HT & LT | 2023-01-26 08:30 | 2023-01-26 16:44 | 8:14 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132 kV Bus-1 | 2023-01-26 08:57 | 2023-01-26 16:25 | 7:28 | S/O | Due to A/M work | 0 | 0 | No interruption
Bharamara | HVDC block-2 33/.4kV aux. transformer-2 | 2023-01-26 10:44 | 2023-01-26 11:39 | 0:55 | S/O | Due to A/M work | 0 | 0 | No interruption
| HVDC block-2 33/.4kV aux. transformer-2 | 2023-01-26 11:48 | 2023-01-26 12:48 | 1:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Shahjadpur | 132 kV main Bus | 2023-01-27 08:40 | 2023-01-27 15:29 | 6:49 | S/O | Due to A/M work | 40 | 272.6667 | Power interruption
Ishurdi | 132/33 kV transformer T01 HT & LT | 2023-01-27 15:02 | 2023-01-27 20:34 | 5:32 | S/O | Due to A/M work | 0 | 0 | No interruption
| 230/132 kV transformer T01 HT | 2023-01-31 10:20 | 2023-01-31 10:51 | 0:31 | S/O | Due to changing work | 0 | 0 | No interruption
|  |  | Total : | 276:21 |  | Unserved Energy : |  | 705.6833
Bogura Grid Circle:
Palashbari | 132/33 kV transformer TR3-424 HT | 2023-01-02 07:11 | 2023-01-03 08:50 | 25:39 | S/O | Due to changing of L/A | 0 | 0 | No interruption
Barapukuria | 230/132 kV transformer T5 424 LT |  | 2023-01-03 14:35 |  | S/O | After maint.work | 0 | 0 | No interruption
Bogura(Sherpur) | 132/33 kV transformer T2(414T) HT | 2023-01-05 10:28 | 2023-01-05 15:26 | 4:58 | S/O | Due to Nondigram Feeder Commissioning. | 0 | 0 | No interruption
Rajshahi | 132/33 kV transformer T1-405 HT | 2023-01-06 08:18 | 2023-01-06 09:27 | 1:09 | S/O | Due to A/M work | 8 | 9.2 | Power interruption
| 132/33 kV transformer T1-405 LT | 2023-01-06 08:18 | 2023-01-06 09:28 | 1:10 | S/O |  |  |  | No interruption
| 132/33 kV transformer T2(415T) LT | 2023-01-06 09:33 | 2023-01-06 11:33 | 2:00 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T2(415T) HT | 2023-01-06 09:34 | 2023-01-06 11:32 | 1:58 | S/O | Due to A/M work | 0 | 0 | No interruption
Rangpur | 132/33 kV transformer T1 (414) HT |  | 2023-01-06 09:58 |  | S/O | After maint.work | 0 | 0 | No interruption
| 132/33 kV transformer T2 (404) HT |  | 2023-01-06 09:59 |  | S/O |  |  | 0 | No interruption
Rajshahi | 132/33 kV transformerT3 (425T) LT | 2023-01-06 15:02 | 2023-01-06 16:38 | 1:36 | S/O | Due to A/M work | 12 | 19.2 | Power interruption
| 132/33 kV transformerT3 (425T) HT | 2023-01-06 15:02 | 2023-01-06 16:35 | 1:33 | S/O | Due to A/M work | 0 | 0 | No interruption
C.nawabganj | 132/33 kV transformer T1 (405) HT | 2023-01-07 07:31 | 2023-01-07 18:55 | 11:24 | S/O | Due to A/M work | 25 | 285 | Power interruption
| 132/33 kV transformer T1-405 HT | 2023-01-07 07:31 | 2023-01-07 18:56 | 11:25 | S/O | Due to A/M work | 25 | 285.4167 | Power interruption
| 132/33 kV transformer T4-435 HT | 2023-01-07 07:41 | 2023-01-07 18:56 | 11:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogura | 132/33 kV transformer T1 LT | 2023-01-07 08:26 | 2023-01-07 10:14 | 1:48 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T1 HT | 2023-01-07 08:27 | 2023-01-07 10:14 | 1:47 | S/O | Due to A/M work | 0 | 0 | No interruption
Page: 16/16 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: January 2023
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Bogura Grid Circle:
C.nawabganj | 132 kV main Bus | 2023-01-07 08:40 | 2023-01-07 18:54 | 10:14 | S/O | Due to Bus change | 25 | 255.8333 | Power interruption
Bogura | 132/33 kV transformer T2 LT | 2023-01-07 10:55 | 2023-01-07 14:50 | 3:55 | S/O | Due to replacement work | 0 | 0 | No interruption
| 132/33 kV transformer T2 HT | 2023-01-07 10:55 | 2023-01-07 14:49 | 3:54 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T1 LT & HT | 2023-01-09 07:28 | 2023-01-09 07:28 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogura | 132 kV main Bus-2 |  | 2023-01-12 13:34 |  | S/O | Due to A/M work | 0 | 0 | No interruption
Naogaon | 132/33 kV transformer T1 HT | 2023-01-14 08:03 | 2023-01-14 13:35 | 5:32 | S/O | Due to A/M work | 33 | 182.6 | Power interruption
| 132/33 kV transformer T2 HT | 2023-01-14 08:03 | 2023-01-14 13:36 | 5:33 | S/O | Due to A/M work | 23 | 127.65 | Power interruption
| 132/33 kV transformer T3 LT | 2023-01-14 08:03 | 2023-01-14 13:41 | 5:38 | S/O | Due to A/M work | 23 | 129.5667 | Power interruption
C.nawabganj | 132/33 kV transformer T1(405) HT | 2023-01-14 08:18 | 2023-01-14 16:57 | 8:39 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T2(405) HT | 2023-01-14 08:18 | 2023-01-14 16:58 | 8:40 | S/O | Due to A/M work | 25 | 216.6667 | Power interruption
| 132/33 kV transformer T3 LT | 2023-01-14 08:19 | 2023-01-14 16:59 | 8:40 | S/O | Due to A/M work | 25 | 216.6667 | Power interruption
| 132/33 kV transformer T4 HT | 2023-01-14 08:20 | 2023-01-14 16:59 | 8:39 | S/O | Due to A/M work | 5 | 43.25 | Power interruption
| 132 kV main Bus | 2023-01-14 08:45 | 2023-01-14 16:56 | 8:11 | S/O | Due to A/M work | 0 | 0 | No interruption
Rajshahi | 230/132 kV transformer T02 HT | 2023-01-14 09:27 | 2023-01-14 14:16 | 4:49 | S/O | Due to A/M work | 0 | 0 | No interruption
Panchugarh | Panchagarh 132/33kV S/S 427T(A+B) HT |  | 2023-01-14 21:50 |  |  | After maint.work | 0 | 0 | No interruption
Lalmonirhat | 132/33 kV transformer T2 415T LT | 2023-01-16 10:48 | 2023-01-16 14:40 | 3:52 | S/O | Due to CT test | 0 | 0 | No interruption
| 132/33 kV transformer T1 415T HT & LT | 2023-01-16 10:48 | 2023-01-16 12:55 | 2:07 | S/O |  | 0 | 0 | No interruption
| 132/33 kV transformer T2 415T HT & LT | 2023-01-16 13:05 | 2023-01-16 14:40 | 1:35 | S/O |  | 0 | 0 | No interruption
Rajshahi | 132/33 kV transformer T3 425T HT | 2023-01-20 08:21 | 2023-01-20 10:25 | 2:04 | S/O | Due to A/M work | 17 | 35.1333 | Power interruption
| 132/33 kV transformer T3 425T LT | 2023-01-20 08:22 | 2023-01-20 10:26 | 2:04 | S/O |  | 17 | 35.1333 | Power interruption
| 132/33 kV transformer T1 405T HT | 2023-01-20 10:38 | 2023-01-20 12:27 | 1:49 | S/O | Due to A/M work | 6 | 10.9 | Power interruption
| 132/33 kV transformer T1 405T LT | 2023-01-20 10:39 | 2023-01-20 12:26 | 1:47 | S/O | Due to maint. work | 6 | 10.7 | Power interruption
| 132/33 kV transformer T2 (415T) HT | 2023-01-20 10:40 | 2023-01-20 12:33 | 1:53 | S/O | Due to maint. work | 0 | 0 | No interruption
| 132/33 kV transformer T2 (415T) LT | 2023-01-20 10:42 | 2023-01-20 12:34 | 1:52 | S/O | Due to maint. work | 0 | 0 | No interruption
| 230/132 kV transformer T01 LT | 2023-01-21 11:09 | 2023-01-21 12:17 | 1:08 | S/O | Due to A/M work | 0 | 0 | No interruption
| 230/132 kV transformer T01 HT | 2023-01-21 11:10 | 2023-01-21 12:16 | 1:06 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogura | 230 kV main Bus-2 |  | 2023-01-22 12:16 |  | S/O | After maint.work | 0 | 0 | No interruption
| 230 kV main Bus-1 | 2023-01-22 12:50 | 2023-01-22 12:50 | 0:00 | S/O | Due to replacement work | 0 | 0 | No interruption
Sirajganj | 132/33 kV transformer T14 LT | 2023-01-23 08:36 | 2023-01-23 08:36 | 0:00 | S/O | Due to project work | 0 | 0 | No interruption
Barapukuria | 230/132 kV transformer T5 424 LT | 2023-01-24 09:18 | 2023-01-24 09:18 | 0:00 | S/O | Due to replacement work | 0 | 0 | No interruption
| 230/132 kV transformer T5 424 HT | 2023-01-24 09:19 | 2023-01-24 09:19 | 0:00 | S/O |  | 0 | 0 | No interruption
C.nawabganj | 132/33 kV transformer T4(435) LT | 2023-01-25 09:10 | 2023-01-25 13:05 | 3:55 | S/O | Due to maint. work | 0 | 0 | No interruption
| 132/33 kV transformer T4(435) HT | 2023-01-25 09:12 | 2023-01-25 13:03 | 3:51 | S/O | Due to maint. work | 0 | 0 | No interruption
Sirajganj | 230 kV Bus-1 | 2023-01-25 09:15 | 2023-01-25 16:18 | 7:03 | S/O | Due to A/M work | 0 | 0 | No interruption
| 231 kV Bus-2 | 2023-01-26 09:42 | 2023-01-26 15:19 | 5:37 | S/O | Due to A/M work | 0 | 0 | No interruption
Barapukuria | 230/132 kV transformer T3 404 LT | 2023-01-26 10:47 | 2023-01-26 13:56 | 3:09 | S/O | Due to 33 KV line isolator maintenance. | 0 | 0 | No interruption
| 230/132 kV transformer T3 404 HT | 2023-01-26 10:55 | 2023-01-26 13:54 | 2:59 | S/O |  | 0 | 0 | No interruption
Sirajganj | 132/33 kV transformer T4(445) HT |  | 2023-01-27 15:10 |  | S/O | After maint.work | 0 | 0 | No interruption
| 132/33 kV transformer T4(445) LT |  | 2023-01-27 15:12 |  | S/O |  | 0 | 0 | No interruption
Rangpur | 132/33 kV transformer T1 HT | 2023-01-30 12:47 | 2023-01-30 14:45 | 1:58 | S/O | Due to replacement work | 0 | 0 | No interruption
| 132/33 kV transformer T1 LT & HT | 2023-01-31 11:26 | 2023-01-31 13:30 | 2:04 | S/O | Due to replacement work | 0 | 0 | No interruption
| 230/132 kV transformer T3 404 HT |  | 2023-01-31 13:11 |  | S/O | After maint.work | 0 | 0
| 230/132 kV transformer T3 404 LT |  | 2023-01-31 14:13 |  | S/O
|  |  | Total : | 211:59 |  | Unserved Energy : |  | 1862.9167
Others :
Ashuganj | 230/132 kV transformer OAT-12 | 2022-01-10 10:32 | 2022-01-10 10:32 | 3:57 | S/O | Due to protection work | 0 | 0 | No interruption
Ashuganj | 230/132 kV transformer OAT12 | 2022-01-11 09:15 | 2022-01-11 09:15 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
| 400/230 kV transformer T2 |  | 2022-01-17 14:56 |  | S/O | After maint.work | 0 | 0 | No interruption
| 400/230 kV transformer T1 |  | 2022-01-17 15:09 |  | S/O |  | 0 | 0 | No interruption
| 230/132kV OAT12 | 2022-01-23 07:25 | 2022-01-23 07:40 | 0:15 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 4:12 |  |  |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 810:00 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-26
Page: 1/15 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: January2023
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Tangail | Tangail-RPCL 132 kV Ckt-2 | 2023-01-01 09:15 | 2023-01-01 17:16 | 8:01 | S/O | Due to dead line checking | 0 | 0 | No interruption
| Tangail-RPCL 132 kV Ckt-2 | 2023-01-02 09:14 | 2023-01-02 17:30 | 8:16 | S/O | Due to dead line checking | 0 | 0 | No interruption
| Tangail-RPCL 132 kV Ckt-2 | 2023-01-03 10:00 | 2023-01-03 16:45 | 6:45 | S/O | Due to A/M work | 0 | 0 | No interruption
Savar | Savar-Manikganj P.S 132 kV Ckt-1 | 2023-01-03 10:18 | 2023-01-03 16:42 | 6:24 | S/O | Due to A/M work | 0 | 0 | No interruption
Agargaon | Agargaon-Basantek 132 kV Ckt-2 | 2023-01-03 12:31 | 2023-01-03 15:23 | 2:52 | S/O | Due to A/M work | 0 | 0 | No interruption
Savar | Savar-Manikganj P.S 132 kV Ckt-1 | 2023-01-04 09:28 | 2023-01-04 18:18 | 8:50 | S/O | Due to A/M work | 0 | 0 | No interruption
Bhaluka | Bhaluka-Mymensingh 132 kV Ckt-1 | 2023-01-04 10:43 | 2023-01-04 16:52 | 6:09 | S/O | Due to A/M work | 0 | 0 | No interruption
Kishoreganj | Kishoreganj-Mymensingh 132 kV Ckt-2 | 2023-01-04 14:57 | 2023-01-04 16:56 | 1:59 | S/O | Due to A/M work | 0 | 0 | No interruption
Savar | Savar-Manikganj P.S 132 kV Ckt-2 | 2023-01-05 09:42 | 2023-01-05 16:22 | 6:40 | S/O | Due to Dead Line checking work. | 0 | 0 | No interruption
Mymensingh | Mymensingh-50 MW Solar P.S 132 kV Ckt | 2023-01-05 09:50 | 2023-01-05 18:11 | 8:21 | S/O | Due to A/M work | 0 | 0 | No interruption
Bhaluka | Bhaluka-Mymensingh 132 kV Ckt-2 | 2023-01-05 09:56 | 2023-01-05 17:20 | 7:24 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | Jamalpur-Mymensingh 132 kV Ckt-1 | 2023-01-05 10:06 | 2023-01-05 13:58 | 3:52 | S/O | Due to A/M work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Tongi 132 kV Ckt-2 | 2023-01-05 10:48 | 2023-01-05 13:56 | 3:08 | S/O | Due to A/M work | 0 | 0 | No interruption
New Tongi | New Tongi-Tongi 132 kV Ckt-2 |  | 2023-01-05 13:57 |  | S/O | After maint.work | 0 | 0 | No interruption
Jamalpur | Jamalpur-Mymensingh 132 kV Ckt-2 | 2023-01-05 14:02 | 2023-01-05 17:31 | 3:29 | S/O | Due to A/M work | 0 | 0 | No interruption
Tangail | Tangail-RPCL 132 kV Ckt-1 | 2023-01-06 09:23 | 2023-01-06 13:16 | 3:53 | S/O | Due to A/M work | 70 | 271.8333 | Power interruption
Kabirpur | Kabirpur-Tongi 132 kV Ckt-1 | 2023-01-06 10:42 | 2023-01-06 14:16 | 3:34 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar--Kallyanpur 132 kV Ckt-2 | 2023-01-06 06:46 | 2023-01-06 07:17 | 0:31 | S/O | Due to A/M work | 0 | 0 | No interruption
Manikganj P.S | Manikganj P.S -Savar 132 kV Ckt-2 | 2023-01-07 09:24 | 2023-01-07 15:57 | 6:33 | S/O | Due to dead line checking | 0 | 0 | No interruption
Mymensingh | Mymensingh-50 MW Solar P.S 132 kV Ckt | 2023-01-07 09:39 | 2023-01-07 18:30 | 8:51 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Netrakona 132 kV Ckt-1 | 2023-01-07 09:47 | 2023-01-07 14:43 | 4:56 | S/O | Due to A/M work | 0 | 0 | No interruption
| Mymensingh-Netrakona 132 kV Ckt-1 | 2023-01-07 10:09 | 2023-01-07 14:42 | 4:33 | S/O | Due to A/M work | 0 | 0 | No interruption
| Mymensingh-Netrakona 132 kV Ckt-2 | 2023-01-07 14:45 | 2023-01-07 17:21 | 2:36 | S/O | Due to A/M work | 0 | 0 | No interruption
Dhamrai | Dhamrai-Kaliakoir 132 kV Ckt-1 | 2023-01-08 08:05 | 2023-01-08 16:25 | 8:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-50 MW Solar P.S 132 kV Ckt | 2023-01-08 09:30 | 2023-01-08 18:27 | 8:57 | S/O | Due to A/M work | 0 | 0 | No interruption
Bhaluka | Bhaluka-Mymensingh 132 kV Ckt-1 | 2023-01-08 09:45 | 2023-01-08 13:50 | 4:05 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Manikganj P/P 132 kV Ckt-1 | 2023-01-08 10:23 | 2023-01-08 18:03 | 7:40 | S/O | Due to A/M work | 0 | 0 | No interruption
Bhaluka | Bhaluka-Mymensingh 132 kV Ckt-2 | 2023-01-08 14:27 | 2023-01-08 17:03 | 2:36 | S/O | Due to A/M work | 0 | 0 | No interruption
Dhamrai | Dhamrai-Kaliakoir 132 kV Ckt-1 | 2023-01-09 08:48 | 2023-01-09 17:16 | 8:28 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-50 MW Solar P.S 132 kV Ckt | 2023-01-09 09:25 | 2023-01-09 17:40 | 8:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Manikganj P/P 132 kV Ckt-1 | 2023-01-09 09:37 | 2023-01-09 19:15 | 9:38 | S/O | Due to dead line checking | 0 | 0 | No interruption
Mymensingh RPCL | Mymensingh RPCL-Mymensingh 132 kV Ckt-1 | 2023-01-09 09:50 | 2023-01-09 13:22 | S/O | S/O | Due to A/M work | 0 | 0 | No interruption
| Mymensingh RPCL-Mymensingh 132 kV Ckt-2 | 2023-01-09 13:27 | 2023-01-09 16:40 | S/O | S/O | Due to A/M work | 0 | 0 | No interruption
Dhamrai | Dhamrai-Kaliakoir 132 kV Ckt-1 | 2023-01-09 07:33 | 2023-01-09 07:33 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Meghanghat 230 kV Ckt-1 | 2023-01-10 09:27 | 2023-01-10 17:37 | 8:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Manikganj P/P 132 kV Ckt-2 | 2023-01-10 12:40 | 2023-01-10 16:21 | 3:41 | S/O | Due to A/M work | 8 | 29.4667 | Power interruption
Bashundhara | Bashundhara-Tongi 132 kV Ckt-1 | 2023-01-10 14:29 | 2023-01-10 15:10 | 0:41 | S/O | Due to A/M work | 0 | 0 | No interruption
| Bashundhara-Tongi 132 kV Ckt-2 | 2023-01-10 15:13 | 2023-01-10 15:56 | 0:43 | S/O | Due to A/M work | 0 | 0 | No interruption
Dhamrai | Dhamrai-Kaliakoir 132 kV Ckt-1 |  | 2023-01-10 16:59 |  | S/O | After maint.work | 0 | 0 | No interruption
Page: 2/15 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: January2023
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Dhamrai | Dhamrai-Kaliakoir 132 kV Ckt-1 | 2023-01-11 07:33 |  |  | S/O | After maint.work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Manikganj P/P 132 kV Ckt-2 | 2023-01-11 08:27 | 2023-01-11 17:01 | 8:34 | S/O | Due to dead line checking | 0 | 0 | No interruption
| Aminbazar-Meghnaghat 230 kV Ckt-1 | 2023-01-11 09:00 | 2023-01-11 17:48 | 8:48 | S/O | Due to dead line checking | 0 | 0 | No interruption
Bhaluka | Bhaluka-Mymensingh 132 kV Ckt-1 | 2023-01-11 09:33 | 2023-01-11 12:58 | 3:25 | S/O | Due to A/M work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Tongi 132 kV Ckt-2 | 2023-01-11 11:19 | 2023-01-11 12:28 | 1:09 | S/O | Due to A/M work | 0 | 0 | No interruption
| Kabirpur-Tongi 132 kV Ckt-1 | 2023-01-11 12:31 | 2023-01-11 13:20 | 0:49 | S/O | Due to A/M work | 0 | 0 | No interruption
Bhaluka | Bhaluka-Mymensingh 132 kV Ckt-2 | 2023-01-11 12:51 | 2023-01-11 14:23 | 1:32 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Tongi 230 kV Ckr-2 | 2023-01-11 13:30 | 2023-01-11 15:06 | 1:36 | S/O | Due to A/M work | 0 | 0 | No interruption
Dhamrai | Dhamrai-Kaliakoir 132 kV Ckt-1 |  | 2023-01-11 17:34 |  |  | After maint.work | 0 | 0 | No interruption
| Dhamrai-Kaliakoir 132 kV Ckt-1 | 2023-01-12 08:17 | 2023-01-12 14:36 | 6:19 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Meghnaghat 230 kV Ckt-2 | 2023-01-12 08:49 | 2023-01-12 17:28 | 8:39 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Manikganj P/P 132 kV Ckt-1 | 2023-01-12 09:10 | 2023-01-12 15:22 | 6:12 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | Tongi-Uttara 132 kV Ckt-1 | 2023-01-12 11:08 | 2023-01-12 12:50 | 1:42 | S/O | Due to A/M work | 0 | 0 | No interruption
| Tongi-Uttara 132 kV Ckt-2 |  | 2023-01-12 14:18 |  | S/O | After maint.work | 0 | 0 | No interruption
Kodda | Kodda-Tongi 230 kV Ckt-1 | 2023-01-12 14:36 | 2023-01-12 16:26 | 1:50 | S/O | Due to relay testing | 0 | 0 | No interruption
Aminbazar | Aminbazar-Meghnaghat 230 kV Ckt-2 | 2023-01-13 08:44 | 2023-01-13 17:36 | 8:52 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Manikganj P/P 132 kV Ckt-2 | 2023-01-14 09:02 | 2023-01-14 17:15 | 8:13 | S/O | Due to A/M work | 0 | 0 | No interruption
Mirpur | Mirpur-Uttara 132 kV Ckt-1 | 2023-01-14 09:39 | 2023-01-14 16:07 | 6:28 | S/O | Due to A/M work | 0 | 0 | No interruption
Manikganj P.S | Manikganj P.S -Savar 132 kV Ckt-1 | 2023-01-14 10:03 | 2023-01-14 17:17 | 7:14 | S/O | Due to A/M work | 0 | 0 | No interruption
Dhamrai | Dhamrai-Kaliakoir 132 kV Ckt-2 | 2023-01-15 08:17 | 2023-01-15 17:26 | 9:09 | S/O | Due to A/M work | 0 | 0 | No interruption
Kishoreganj | Kishoreganj-Mymensingh 132 kV Ckt-1 | 2023-01-15 09:20 | 2023-01-15 14:00 | 4:40 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | Jamalpur-Mymensingh 132 kV Ckt-1 | 2023-01-15 10:12 | 2023-01-15 14:36 | 4:24 | S/O | Due to A/M work | 0 | 0 | No interruption
Dhamrai | Dhamrai-Kaliakoir 132 kV Ckt-2 | 2023-01-16 07:41 | 2023-01-16 07:41 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | Jamalpur-Mymensingh 132 kV Ckt-2 | 2023-01-16 09:19 | 2023-01-16 16:24 | 7:05 | S/O | Due to A/M work | 0 | 0 | No interruption
| Jamalpur-Mymensingh 132 kV Ckt-2 | 2023-01-16 09:31 | 2023-01-16 09:31 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Manikganj P.S | Manikganj P.S -Savar 132 kV Ckt-2 | 2023-01-16 10:06 | 2023-01-16 17:32 | 7:26 | S/O | Due to A/M work | 0 | 0 | No interruption
Kishoreganj | Kishoreganj-Mymensingh 132 kV Ckt-2 | 2023-01-16 10:19 | 2023-01-16 15:55 | 5:36 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar 400/230/132kV S/S Gopalganj-1 | 2023-01-16 11:03 | 2023-01-16 18:15 | 7:12 | S/O | Due to A/M work | 0 | 0 | No interruption
| Aminbazar 400/230/132kV S/S Gopalganj-2 | 2023-01-16 11:04 | 2023-01-16 18:48 | 7:44 | S/O | Due to A/M work | 0 | 0 | No interruption
Kishoreganj | Kishoreganj-Mymensingh 132 kV Ckt-2 |  | 2023-01-16 15:55 |  | S/O | After maint.work | 0 | 0 | No interruption
Dhamrai | Dhamrai-Kaliakoir 132 kV Ckt-2 |  | 2023-01-16 17:28 |  | S/O | After maint.work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Gopalganj 400 kV Ckt-2 |  | 2023-01-16 17:50 |  | S/O |  | 0 | 0 | No interruption
|  |  | 2023-01-16 17:52 |  | S/O |  | 0 | 0 | No interruption
Dhamrai | Dhamrai-Kaliakoir 132 kV Ckt-2 | 2023-01-17 08:27 | 2023-01-17 16:10 | 7:43 | S/O | Due to A/M work | 0 | 0 | No interruption
Agarogon | Agarogon-Satmosjid 132 kV Ckt-1 | 2023-01-17 08:40 | 2023-01-17 14:14 | 5:34 | S/O | Due to A/M work | 0 | 0 | No interruption
Mirpur | Mirpur-Uttara 3PH 132 kV Ckt-1 | 2023-01-17 09:27 | 2023-01-17 20:11 | 10:44 | S/O | Due to Dead line checking work. | 0 | 0 | No interruption
Mymensingh | Mymensingh-Netrakona 132 kV ckt-1 | 2023-01-17 10:02 | 2023-01-17 16:30 | 6:28 | S/O | Due to A/M work | 0 | 0 | No interruption
Savar | Savar-Manikganj P.S 132 kV Ckt-2 | 2023-01-17 10:12 | 2023-01-17 17:11 | 6:59 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Meghnaghat 230 kV Ckt-2 | 2023-01-17 13:28 | 2023-01-17 16:06 | 2:38 | S/O | Due to A/M work | 0 | 0 | No interruption
| Aminbazar-Meghnaghat 230 kV Ckt-1 | 2023-01-17 16:16 | 2023-01-17 16:34 | 0:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Page: 3/15 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: January2023
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Agarogon | Agarogon-Satmosjid 132 kV Ckt-2 | 2023-01-18 08:49 | 2023-01-18 15:03 | 6:14 | S/O | Due to relay test | 0 | 0 | No interruption
Mymensingh | Mymensingh-Netrakona 132 kV Ckt-2 | 2023-01-18 09:42 | 2023-01-18 17:57 | 8:15 | S/O | Due to relay test | 0 | 0 | No interruption
Mirpur | Mirpur-Uttara 3PH 132 kV Ckt-1 | 2023-01-18 09:45 | 2023-01-18 20:16 | 10:31 | S/O | Due to Dead line checking work. | 0 | 0 | No interruption
Mymensingh | Mymensingh RPCL-Mymensingh 132 kV Ckt-1 | 2023-01-19 09:56 | 2023-01-19 16:44 | 6:48 | S/O | Due to A/M work | 0 | 0 | No interruption
Savar | Savar-Manikganj P.S 132 kV Ckt-1 | 2023-01-19 09:58 | 2023-01-19 15:40 | 5:42 | S/O | Due to A/M work | 0 | 0 | No interruption
Bhaluka | Bhaluka-Mymensingh 132 kV Ckt-2 | 2023-01-19 10:20 | 2023-01-19 17:20 | 7:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Kodda 132 kV Ckt-1 | 2023-01-19 10:54 | 2023-01-19 17:07 | 6:13 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | Jamalpur-Mymensingh 132 kV Ckt-1 | 2023-01-19 13:08 | 2023-01-19 15:59 | 2:51 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Netrakona 132 kV Ckt-1 | 2023-01-19 13:18 | 2023-01-19 15:13 | 1:55 | S/O | Due to A/M work | 0 | 0 | No interruption
| Mymensingh-Netrakona 132 kV Ckt-2 | 2023-01-19 15:15 | 2023-01-19 17:33 | 2:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Manikganj P.S | Manikganj P.S -Savar 132 kV Ckt-2 | 2023-01-19 15:47 | 2023-01-19 17:41 | 1:54 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | Jamalpur-Mymensingh 132 kV Ckt-2 | 2023-01-19 16:04 | 2023-01-19 17:41 | 1:37 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kallyanpur 132 kV Ckt-1 | 2023-01-21 06:47 | 2023-01-21 19:31 | 12:44 | S/O | Due to project work | 0 | 0 | No interruption
| Aminbazar-Kallyanpur 132 kV Ckt-2 | 2023-01-21 06:48 | 2023-01-21 19:31 | 12:43 | S/O | Due to project work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Kodda 132 kV Ckt-2 | 2023-01-21 10:06 | 2023-01-21 16:23 | 6:17 | S/O | Due to Dead line checking work. | 0 | 0 | No interruption
Kodda | Kodda-Tongi 230 kV Ckt-1 | 2023-01-21 10:09 | 2023-01-21 15:54 | 5:45 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh RPCL-Mymensingh 132 kV Ckt-2 | 2023-01-21 10:34 | 2023-01-21 16:27 | 5:53 | S/O | Due to A/M work | 0 | 0 | No interruption
Savar | Savar-Manikganj P.S 132 kV Ckt-2 | 2023-01-21 10:54 | 2023-01-21 15:24 | 4:30 | S/O | Due to A/M work | 0 | 0 | No interruption
Bhaluka | Bhaluka-Mymensingh 132 kV Ckt-1 | 2023-01-21 11:15 | 2023-01-21 17:13 | 5:58 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Kodda(300 MW) 230 kV Ckt-1 | 2023-01-22 08:31 | 2023-01-22 16:53 | 8:22 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kaliakoir 230 kV Ckt-2 | 2023-01-22 09:20 | 2023-01-22 17:07 | 7:47 | S/O | Due to A/M work | 0 | 0 | No interruption
| Aminbazar-Kaliakoir 230 kV Ckt-2 | 2023-01-22 07:23 | 2023-01-22 07:23 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Kodda | Kodda-Tongi 230 kV Ckt-1 | 2023-01-23 08:49 | 2023-01-23 16:14 | 7:25 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Solar 50 MW P/S 132 kV Ckt | 2023-01-23 10:08 | 2023-01-23 10:08 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Mirpur 132 kV Ckt-1 | 2023-01-23 11:45 | 2023-01-23 15:02 | 3:17 | S/O | Due to A/M work | 0 | 0 | No interruption
| Aminbazar-Mirpur 132 kV Ckt-2 | 2023-01-23 11:45 | 2023-01-23 14:57 | 3:12 | S/O | Due to A/M work | 0 | 0 | No interruption
| Aminbazar-Mirpur 132 kV Ckt-2 | 2023-01-23 15:06 | 2023-01-23 16:25 | 1:19 | S/O | Due to relay test | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Bibiyana 230 kV Ckt-1 | 2023-01-24 08:33 | 2023-01-24 16:32 | 7:59 | S/O | Due to A/M work | 0 | 0 | No interruption
Kodda | Kodda-Tongi 230 kV Ckt-1 | 2023-01-24 08:56 | 2023-01-24 17:06 | 8:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Tangail | Tangail-Kaliakoir 132 kV Ckt-2 | 2023-01-24 10:10 | 2023-01-24 12:05 | 1:55 | S/O | Due to relay Testing | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kallyanpur 132 kV Ckt-1 | 2023-01-25 07:42 | 2023-01-25 17:40 | 9:58 | S/O | Due to A/M work | 0 | 0 | No interruption
| Aminbazar-Kallyanpur 132 kV Ckt-1 | 2023-01-26 08:46 | 2023-01-26 16:39 | 7:53 | S/O | Due to dead line checking | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Bibiyana 230 kV Ckt-1 | 2023-01-25 08:19 | 2023-01-25 16:23 | 8:04 | S/O | Due to A/M work | 0 | 0 | No interruption
Kodda | Kodda-Tongi 230 kV Ckt-1 | 2023-01-25 09:06 | 2023-01-25 16:01 | 6:55 | S/O | Due to A/M work | 0 | 0 | No interruption
Mirpur | Mirpur-Uttara 132 kV Ckt-1 | 2023-01-25 09:57 | 2023-01-25 17:16 | 7:19 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Bibiyana 230 kV Ckt-1 | 2023-01-26 09:26 | 2023-01-26 13:17 | 3:51 | S/O | Due to Dead line checking work. | 0 | 0 | No interruption
Mirpur | Mirpur-Uttara 132 kV Ckt-1 | 2023-01-26 09:34 | 2023-01-26 11:24 | 1:50 | S/O | Due to relay Testing | 0 | 0 | No interruption
Joydevpur | Joydevpur-Kodda 132 kV Ckt-2 | 2023-01-27 09:27 | 2023-01-27 17:15 | 7:48 | S/O | Due to A/M work | 0 | 0 | No interruption
Kodda | Kodda-Rajendrapur 132 kV Ckt-1 | 2023-01-27 14:25 | 2023-01-27 15:25 | 1:00 | S/O | Due to project work | 0 | 0 | No interruption
| Kodda-Rajendrapur 132 kV Ckt-2 | 2023-01-27 15:26 | 2023-01-27 16:08 | 0:42 | S/O | Due to project work | 0 | 0 | No interruption
Manikganj P.S | Manikganj P.S -Savar 132 kV Ckt-1 | 2023-01-28 08:10 | 2023-01-28 19:09 | 10:59 | S/O | Due to replacemnt work | 0 | 0 | No interruption
| Manikganj P.S -Savar 132 kV Ckt-2 | 2023-01-28 08:10 | 2023-01-28 18:15 | 10:05 | S/O |  | 60 | 605 | Power interruption
Page: 4/15 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: January2023
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Kaliakoir | Kaliakoir-Tongi 230 kV Ckr-2 | 2023-01-28 09:29 | 2023-01-28 16:17 | 6:48 | S/O | Due to A/M work | 0 | 0 | No interruption
| Kaliakoir-Tongi 230 kV Ckr-2 | 2023-01-28 09:54 | 2023-01-28 16:15 | 6:21 | S/O | Due to A/M work | 40 | 254 | Power interruption
Aminbazar | Aminbazar-Mirpur 132 kV Ckt-1 | 2023-01-28 09:38 | 2023-01-28 17:19 | 7:41 | S/O | Due to Dead line & Disc Change work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Tongi 230 kV Ckr-2 | 2023-01-29 08:31 | 2023-01-29 17:29 | 8:58 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kaliakoir 230 kV Ckt-1 | 2023-01-29 09:09 | 2023-01-29 18:12 | 9:03 | S/O | Due to A/M work | 0 | 0 | No interruption
Kodda | Kodda-Rajendrapur 132 kV Ckt-1 | 2023-01-29 10:10 | 2023-01-29 17:14 | 7:04 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kaliakoir 230 kV Ckt-1 | 2023-01-30 08:39 | 2023-01-30 17:09 | 8:30 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Tongi 230 kV Ckr-2 | 2023-01-30 09:20 | 2023-01-30 17:14 | 7:54 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kaliakoir 230 kV Ckt-1 | 2023-01-31 08:25 | 2023-01-31 16:47 | 8:22 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Tongi 230 kV Ckr-2 | 2023-01-31 08:37 | 2023-01-31 16:30 | 7:53 | S/O | Due to dead line checking | 0 | 0 | No interruption
Aminbazar | Aminbazar-Mirpur 132 kV Ckt-2 | 2023-01-31 09:07 | 2023-01-31 17:17 | 8:10 | S/O |  | 0 | 0 | No interruption
Jamalpur | Jamalpur united(20 MW) -Sherpur 132 kV Ckt-1 | 2023-01-31 09:48 | 2023-01-31 13:30 | 3:42 | S/O | Due to CT Tendelta test. | 0 | 0 | No interruption
| Jamalpur united(20 MW) -Sherpur 132 kV Ckt-2 | 2023-01-31 13:31 | 2023-01-31 14:35 | 1:04 | S/O | Due to CT Tendelta test. | 0 | 0 | No interruption
|  |  | Total : | 696:21 |  | Unserved Energy: |  | 1160.3
Dhaka (South) Grid Circle :
Maniknagar | Maniknagar-Siddhirganj 230 kV Ckt-1 | 2023-01-01 09:23 | 2023-01-01 17:18 | 7:55 | S/O | Due to A/M work | 0 | 0 | No interruption
Sonargaon | Sonargaon-IEL 132 kV Ckt-2 | 2023-01-01 09:43 | 2023-01-01 14:34 | 4:51 | S/O | Due to A/M work | 0 | 0 | No interruption
Aftabnagar | Aftabnagar-Rampura 132 kV Ckt-1 | 2023-01-03 12:32 | 2023-01-03 15:22 | 2:50 | S/O | Due to A/M work | 0 | 0 | No interruption
Haripur | Haripur-Sonargaon 132 kV Ckt-1 & 2 | 2023-01-04 09:02 | 2023-01-04 16:43 | 7:41 | S/O | Due to A/M work | 0 | 0 | No interruption
| Haripur-Sonargaon 132 kV Ckt-1 | 2023-01-05 08:20 | 2023-01-05 17:01 | 8:41 | S/O | Due to A/M work | 0 | 0 | No interruption
| Haripur-Sonargaon 132 kV Ckt-2 | 2023-01-05 08:20 | 2023-01-05 17:02 | 8:42 | S/O | Due to A/M work | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Ullon (T at maniknagar) 132 kV Ckt-1 | 2023-01-05 08:42 | 2023-01-05 21:19 | 12:37 | S/O | Due to A/M work | 0 | 0 | No interruption
Aftabnagar | Aftabnagar-Rampura 132 kV Ckt-1 | 2023-01-05 08:50 | 2023-01-05 16:40 | 7:50 | S/O | Due to A/M work | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Shyampur 230 kV Ckt-1 | 2023-01-06 07:08 | 2023-01-06 07:36 | 0:28 | S/O | Due to A/M work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Keraniganj (pre-1Lalbagh) | 2023-01-08 09:50 | 2023-01-08 09:50 | 0:00 | S/O | Due to dead line checking | 0 | 0 | No interruption
| Hasnabad-Aggreko Aurahati 132 kV Ckt | 2023-01-08 10:00 | 2023-01-08 19:32 | 9:32 | S/O |  | 0 | 0 | No interruption
Ghorashal | Ghorashal-Tongi 230 kV Ckt-1 | 2023-01-08 14:18 | 2023-01-08 14:40 | 0:22 | S/O | Due to A/M work | 0 | 0 | No interruption
Aggreko | Aggreko-Hasnabad 132 kV Ckt-2 | 2023-01-09 10:11 | 2023-01-09 16:24 | 6:13 | S/O | Due to A/M work | 0 | 0 | No interruption
Madanganj | Madanganj-Summit 55 MW 132 kV Ckt | 2023-01-09 10:25 | 2023-01-09 17:08 | 6:43 | S/O | Due to A/M work | 0 | 0 | No interruption
Haripur | Haripur-Madanganj 132 kV Ckt-1 | 2023-01-10 10:33 | 2023-01-10 10:33 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
| Haripur-Shyampur 132 kV Ckt | 2023-01-10 10:25 | 2023-01-10 17:08 | 6:43 | S/O | Due to A/M work | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Aminbazar 230 kV Ckt-1 | 2023-01-10 09:24 | 2023-01-10 17:34 | 8:10 | S/O | Due to A/M work | 0 | 0 | No interruption
| Meghnaghat-Shyampur 230 kV Ckt-1 | 2023-01-10 09:45 | 2023-01-10 17:40 | 7:55 | S/O | Due to A/M work | 0 | 0 | No interruption
| Meghnaghat-Aminbazar 230 kV Ckt-1 | 2023-01-11 08:58 | 2023-01-11 18:07 | 9:09 | S/O | Due to A/M work | 0 | 0 | No interruption
| Meghnaghat-Shyampur 230 kV Ckt-2 | 2023-01-12 09:22 | 2023-01-12 17:20 | 7:58 | S/O | Due to A/M work | 0 | 0 | No interruption
Mdanganj | Mdanganj-DPDC Char sayepur 132 kV Ckt-1 | 2023-01-12 11:17 | 2023-01-12 21:09 | 9:52 | S/O | Due to Safety Purpose | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Aminbazar 230 kV Ckt-2 | 2023-01-13 08:47 | 2023-01-13 17:34 | 8:47 | S/O | Due to A/M work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Shyampur 230 kV Ckt-1 | 2023-01-14 08:43 | 2023-01-14 20:21 | 11:38 | S/O | Due to dead line checking | 0 | 0 | No interruption
Mdanganj | Mdanganj-DPDC Char Sayepur 132 kV Ckt-1 | 2023-01-14 08:50 | 2023-01-14 20:29 | 11:39 | S/O | Due to dead line checking | 0 | 0 | No interruption
Haripur | Haripur-Madnganj 132 kV Ckt-1 |  | 2023-01-14 21:14 |  | S/O | After maint.work | 0 | 0 | No interruption
Munshiganj | Munshiganj-Sinha peoples energy Limited | 2023-01-15 07:27 | 2023-01-15 07:27 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Shyampur 230 kV Ckt-01 | 2023-01-15 07:39 | 2023-01-15 07:39 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Bhulta | Bhulta-Rampura 230 kV Ckt-1 | 2023-01-15 08:22 | 2023-01-15 16:48 | 8:26 | S/O | Due to dead line checking | 0 | 0 | No interruption
Page:5/15 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: January2023
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (South) Grid Circle :
| Bhulta-Haripur 230 kV Ckt-1 | 2023-01-15 08:40 | 2023-01-15 14:46 | 6:06 | S/O | Due to A/M work | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Shyampur 230 kV Ckt-1 |  | 2023-01-15 20:41 |  | S/O | After maint.work | 0 | 0 | No interruption
Munshiganj | Munshiganj-Sinha peoples energy Limited | 2023-01-16 07:40 | 2023-01-16 07:40 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
APR | APR-Hasnabad 230 kV Ckt-2 | 2023-01-16 08:18 | 2023-01-16 12:13 | 3:55 | S/O | Due to A/M work | 0 | 0 | No interruption
Bhulta | Bhulta-Rampura 230 kV Ckt-2 | 2023-01-16 08:34 | 2023-01-16 08:34 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
| Bhulta-Rampura 230 kV Ckt-2 | 2023-01-16 08:45 | 2023-01-16 16:39 | 7:54 | S/O | Due to A/M work | 0 | 0 | No interruption
| Bhulta-Haripur 230 kV Ckt-2 | 2023-01-16 09:19 | 2023-01-16 11:30 | 2:11 | S/O | Due to A/M work | 0 | 0 | No interruption
Moghbazar | Moghbazar-Rampura 132 kV Ckt-2 | 2023-01-16 09:40 | 2023-01-16 09:40 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Munshiganj | Munshiganj-Sinha peoples energy Limited |  | 2023-01-16 15:58 |  | S/O | After maint.work | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Shyampur 230 kV Ckt-2 | 2023-01-17 07:44 | 2023-01-17 17:40 | 9:56 | S/O | Due to dead line checking | 0 | 0 | No interruption
Bhulta | Bhulta-Ghorashal 230 kV Ckt-2 | 2023-01-17 09:25 | 2023-01-17 16:19 | 6:54 | S/O | Due to A/M work | 0 | 0 | No interruption
Ghorashal | Ghorashal-Ishurdi 230 kV Ckt-2 | 2023-01-17 09:26 | 2023-01-17 17:43 | 8:17 | S/O | Due to PT Maintanence work. | 0 | 0 | No interruption
Bhulta | Bhulta-Rampura 230 kV Ckt-3 | 2023-01-17 09:30 | 2023-01-17 16:43 | 7:13 | S/O | Due to A/M work | 0 | 0 | No interruption
Moghbazar | Moghbazar-Rampura 132 kV Ckt-2 |  | 2023-01-17 10:42 |  | S/O | After maint.work | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Aminabazar 230 kV Ckt-2 | 2023-01-17 13:29 | 2023-01-17 15:58 | 2:29 | S/O | Due to A/M work | 0 | 0 | No interruption
| Meghnaghat-Aminabazar 230 kV Ckt-1 | 2023-01-17 16:12 | 2023-01-17 16:33 | 0:21 | S/O | Due to test for meghnaghat CR. | 0 | 0 | No interruption
Hasnabad | Hasnabad-Keraniganj 230 kV Ckt-1 | 2023-01-18 08:56 | 2023-01-18 08:56 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Bhulta | Bhulta-Rampura 230 kV Ckt-4 | 2023-01-18 09:19 | 2023-01-18 15:54 | 6:35 | S/O | Due to A/M work | 0 | 0 | No interruption
| Bhulta-Rampura 230 kV Ckt-4 | 2023-01-18 09:36 | 2023-01-18 15:57 | 6:21 | S/O | Due to A/M work | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-120 MW EGCB GT-2 | 2023-01-18 12:39 | 2023-01-18 16:22 | 3:43 | S/O | Due to A/M work | 0 | 0 | No interruption
Maniknagar | Maniknagar-Siddhirganj 230 kV Ckt-1 |  | 2023-01-18 16:09 |  | S/O | After maint.work | 0 | 0 | No interruption
| Maniknagar-Siddhirganj 230 kV Ckt-2 | 2023-01-18 08:31 | 2023-01-18 08:31 | 0:00 | S/O | Due to project work | 0 | 0 | No interruption
| Hasnabad-Keraniganj 230 kV Ckt-2 | 2023-01-19 09:24 | 2023-01-19 15:51 | 6:27 | S/O | Due to maint.work | 0 | 0 | No interruption
Haripur | Haripur-Rahim steel 132 kV Ckt | 2023-01-20 07:20 | 2023-01-20 07:20 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Madanganj | Madanganj-Shitalakhya 132 kV Ckt | 2023-01-21 07:42 | 2023-01-21 07:42 | 0:00 | S/O | Due to maint.work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Sitalakhya 132 kV Ckt-1 | 2023-01-21 07:47 | 2023-01-21 17:36 | 9:49 | S/O | Due to A/M work | 0 | 0 | No interruption
| Hasnabad-Sitalakhya 132 kV Ckt-1 | 2023-01-22 07:47 | 2023-01-23 07:42 | 23:55 | S/O | Due to A/M work | 0 | 0 | No interruption
Bhulta | Bhulta-Haripur 230 kV Ckt-2 | 2023-01-23 09:48 | 2023-01-23 13:06 | 3:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Keraniganj | Keraniganj-Sreenagar (T at Powerpac 100MW) 132kV Ckt-2 | 2023-01-23 10:06 | 2023-01-23 16:27 | 6:21 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kallyanpur 132 kV Ckt-1 | 2023-01-24 07:16 | 2023-01-24 16:27 | 9:11 | S/O | Due to A/M work | 0 | 0 | No interruption
| Aminbazar-Meghnaghat 230 kV Ckt-1 | 2023-01-24 11:22 | 2023-01-24 15:26 | 4:04 | S/O | Due to A/M work | 0 | 0 | No interruption
Keraniganj | Keraniganj-Sreenagar 132kV Ckt-1 | 2023-01-24 11:22 | 2023-01-24 17:43 | 6:21 | S/O | Due to A/M work | 0 | 0 | No interruption
| Keraniganj-Sreenagar (T at Powerpac 100MW) 132kV Ckt-2 | 2023-01-25 09:44 | 2023-01-25 18:00 | 8:16 | S/O | Due to A/M work | 0 | 0 | No interruption
| Keraniganj-Sreenagar (T at Powerpac 100MW) 132kV Ckt-2 | 2023-01-25 10:15 | 2023-01-25 17:59 | 7:44 | S/O | Due to dead line checking | 0 | 0 | No interruption
Mirpur | Mirpur-Uttara 3PH 132 kV Ckt-1 | 2023-01-26 09:34 | 2023-01-26 11:24 | 1:50 | S/O | Due to relay testing | 0 | 0 | No interruption
Kamrangirchar | Kamrangirchar-Keraniganj 132 kV Ckt-1 | 2023-01-27 09:48 | 2023-01-27 17:19 | 7:31 | S/O | Due to dead line checking | 0 | 0 | No interruption
Keraniganj | Keraniganj-Lalbagh 132 kV Ckt-3 | 2023-01-28 09:33 | 2023-01-28 14:39 | 5:06 | S/O | Due to A/M work | 0 | 0 | No interruption
Haripur | Haripur-Madanganj 132 kV Ckt-1 | 2023-01-28 10:38 | 2023-01-28 13:49 | 3:11 | S/O | Due to A/M work | 32 | 101.8667 | Power interruption
Keraniganj | Keraniganj-Sreenagar 132 kV Ckt-1 | 2023-01-29 09:29 | 2023-01-29 13:57 | 4:28 | S/O | Due to dead line checking | 0 | 0 | No interruption
Aggreko | Aggreko-Keraniganj 132 kV Ckt-1 | 2023-01-29 09:47 | 2023-01-29 13:55 | 4:08 | S/O | Due to dead line checking | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Shyampur 230 kV Ckt-2 |  | 2023-01-29 12:52 |  | S/O | After maint.work | 0 | 0 | No interruption
|  |  | 2023-01-31 09:38 |  | S/O
|  |  | Total : | 358:17 |  | Unserved Energy: |  | 101.8667
Page: 6/15 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: January2023
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Chattogram Grid Circle :
BSRM | BSRM-Mirsharai 230 kV Ckt-1 | 2023-01-01 09:47 | 2023-01-01 15:31 | 5:44 | S/O | Due to A/M work | 0 | 0 | No interruption
Bakulia | Bakulia-Khulshi 132 kV Ckt-1 | 2023-01-02 08:49 | 2023-01-02 19:08 | 10:19 | S/O | Due to A/M work | 0 | 0 | No interruption
BSRM | BSRM-Mirsharai 230 kV Ckt-1 | 2023-01-02 09:55 | 2023-01-02 15:49 | 5:54 | S/O | Due to A/M work | 0 | 0 | No interruption
Cox'sbazar | Cox'sbazar-Dohazari 132 kV Ckt-1 | 2023-01-03 08:20 | 2023-01-03 16:37 | 8:17 | S/O | Due to A/M work | 20 | 165.6667 | Power interruption
Bakulia | Bakulia-Khulshi 132 kV Ckt-1 | 2023-01-03 08:51 | 2023-01-03 14:41 | 5:50 | S/O | Due to dead line checking | 0 | 0 | No interruption
BSRM | BSRM-Mirsharai 230 kV Ckt-1 | 2023-01-03 09:54 | 2023-01-03 09:54 | 0:00 | S/O |  | 0 | 0 | No interruption
Chandraghona | Chandraghona-Kaptai 132 kV Ckt-1 | 2023-01-03 10:01 | 2023-01-03 12:28 | 2:27 | S/O | Due to A/M work | 0 | 0 | No interruption
| Chandraghona-Kaptai 132 kV Ckt-2 | 2023-01-03 10:26 | 2023-01-03 11:18 | 0:52 | S/O | Due to A/M work | 0 | 0 | No interruption
Cox'sbazar | Cox'sbazar-Dohazari 132 kV Ckt-1 | 2023-01-04 08:47 | 2023-01-04 16:20 | 7:33 | S/O | Due to A/M work | 0 | 0 | No interruption
Bakulia | Bakulia-Khulshi 132 kV Ckt-1 | 2023-01-04 08:59 | 2023-01-04 16:25 | 7:26 | S/O | Due to A/M work | 14 | 104.0667 | Power interruption
| Bakulia-Khulshi 132 kV Ckt-1 | 2023-01-05 15:42 | 2023-01-05 15:42 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
BSRM | BSRM-Mirsharai 230 kV Ckt-2 | 2023-01-05 09:44 | 2023-01-05 16:00 | 6:16 | S/O | Due to A/M work | 0 | 0 | No interruption
Cox'sbazar | Cox'sbazar-Dohazari 132 kV Ckt-1 | 2023-01-06 08:45 | 2023-01-06 10:50 | 2:05 | S/O | Due to A/M work | 0 | 0 | No interruption
BSRM | BSRM-GPH 230 kV Ckt-2 | 2023-01-06 10:28 | 2023-01-06 11:38 | 1:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Cox'sbazar | Cox'sbazar-Dohazari 132 kV Ckt-1 |  | 2023-01-06 10:54 |  | S/O | After maint.work | 0 | 0 | No interruption
Halishahar | Khulshi-Halishahar 132 kV Ckt-3 | 2023-01-07 06:46 | 2023-01-07 06:46 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulshi | Khulshi-Madunaghat 132 kV Ckt-2 | 2023-01-07 10:58 | 2023-01-07 10:58 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
BSRM | BSRM-Mirsharai 230 kV Ckt-2 | 2023-01-08 09:28 | 2023-01-08 14:08 | 4:40 | S/O | Due to A/M work | 0 | 0 | No interruption
Bakulia | Bakulia-MSMI 132 kV Ckt-2 | 2023-01-09 08:55 | 2023-01-09 14:55 | 6:00 | S/O | Due to A/M work | 0 | 0 | No interruption
BSRM | BSRM-Mirsharai 230 kV Ckt-2 | 2023-01-09 10:46 | 2023-01-09 14:33 | 3:47 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulshi | Khulshi-Halishahar 132 kV Ckt-3 | 2023-01-09 14:18 | 2023-01-09 17:47 | 3:29 | S/O | Due to A/M work | 10 | 34.8333 | Power interruption
| Khulshi-Halishahar 132 kV Ckt-3 | 2023-01-09 14:20 | 2023-01-09 17:47 | 3:27 | S/O | Due to Construction work of CDA. | 0 | 0 | No interruption
Chandraghona | Chandraghona-Rangamati 132 kV Ckt-1 | 2023-01-10 08:52 | 2023-01-10 16:44 | 7:52 | S/O | Due to dead line checking | 0 | 0 | No interruption
Bakulia | Bakulia-MSMI 132 kV Ckt-2 | 2023-01-10 09:07 | 2023-01-10 15:13 | 6:06 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulshi | Khulshi-Halishahar 132 kV Ckt-3 | 2023-01-10 10:27 | 2023-01-10 18:17 | 7:50 | S/O | Due to A/M work | 0 | 0 | No interruption
Halishahar | Halishahar-Khulshi 132 kV Ckt-3 | 2023-01-10 10:27 | 2023-01-10 18:09 | 7:42 | S/O | Due to A/M work | 0 | 0 | No interruption
Bakulia | Bakulia-MSMI 132 kV Ckt-2 | 2023-01-11 08:50 | 2023-01-11 15:36 | 6:46 | S/O | Due to A/M work | 0 | 0 | No interruption
Chandraghona | Chandraghona-Rangamati 132 kV Ckt-1 | 2023-01-11 08:55 | 2023-01-11 17:30 | 8:35 | S/O | Due to A/M work | 0 | 0 | No interruption
Bakulia | Bakulia-MSMI 132 kV Ckt-2 | 2023-01-11 09:12 | 2023-01-11 15:37 | 6:25 | S/O | Due to A/M work | 0 | 0 | No interruption
Halishahar | Halishahar-Khulshi 132 kV Ckt-3 | 2023-01-11 10:46 | 2023-01-11 12:27 | 1:41 | S/O | Due to Construction work of CDA | 0 | 0 | No interruption
Khulshi | Khulshi-Halishahar 132 kV Ckt-3 | 2023-01-11 10:47 | 2023-01-11 12:53 | 2:06 | S/O | Due to Construction work of CDA | 0 | 0 | No interruption
Chandraghona | Chandraghona-Rangamati 132 kV Ckt-1 | 2023-01-12 08:39 | 2023-01-12 17:14 | 8:35 | S/O | Due to dead line checking | 0 | 0 | No interruption
Juldah | Juldah-Juldah P/S 132 kV Ckt-1 | 2023-01-14 08:25 | 2023-01-14 15:03 | 6:38 | S/O | Due to A/M work | 25 | 165.8333 | Power interruption
| Juldah-Shahmirpur 132 kV Ckt-1 | 2023-01-14 08:40 | 2023-01-14 13:47 | 5:07 | S/O | Due to A/M work | 0 | 0 | No interruption
| Juldah-Shahmirpur 132 kV Ckt-2 | 2023-01-14 08:41 | 2023-01-14 13:49 | 5:08 | S/O | Due to A/M work | 0 | 0 | No interruption
Halishahar | Halishahar-Juldah 132 kV Ckt-1 | 2023-01-14 08:59 | 2023-01-14 14:05 | 5:06 | S/O | Due to A/M work | 0 | 0 | No interruption
Chandraghona | Chandraghona-Rangamati 132 kV Ckt-1 | 2023-01-14 09:00 | 2023-01-14 17:16 | 8:16 | S/O | Due to A/M work | 0 | 0 | No interruption
Madunaghat | Madunaghat(Gis)-Bashkahli 400 kV line |  | 2023-01-14 13:49 |  | S/O | new connection
Chandraghona | Chandraghona-Rangamati 132 kV Ckt-1 | 2023-01-15 09:06 | 2023-01-15 14:27 | 5:21 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulshi | Khulshi-MSML 132 kV Ckt-2 | 2023-01-15 09:37 | 2023-01-15 15:19 | 5:42 | S/O | Due to A/M work | 0 | 0 | No interruption
Halishahar | Halishahar-Juldah 132 kV Ckt-1 | 2023-01-16 08:38 | 2023-01-16 15:01 | 6:23 | S/O | Due to A/M work | 0 | 0 | No interruption
Page: 7/15 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: January2023
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Chattogram Grid Circle :
Halishahar | Halishahar-Juldah 132 kV Ckt-1 | 2023-01-16 09:30 | 2023-01-16 14:58 | 5:28 | S/O | Due to A/M work | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Kulaura 132 kV Ckt-1 | 2023-01-16 10:31 | 2023-01-16 13:11 | 2:40 | S/O | Due to A/M work | 0 | 0 | No interruption
| Fenchuganj-Sreemongal 132 kV Ckt-1 | 2023-01-16 13:14 | 2023-01-16 16:15 | 3:01 | S/O | Due to A/M work | 0 | 0 | No interruption
Chandraghona | Chandraghona-Rangamati 132 kV Ckt-2 | 2023-01-17 08:44 | 2023-01-17 16:44 | 8:00 | S/O | Due to A/M work | 0 | 0 | No interruption
| Chandraghona-Rangamati 132 kV Ckt-2 | 2023-01-17 08:55 | 2023-01-17 16:46 | 7:51 | S/O | Due to dead line checking | 0 | 0 | No interruption
AKSML | AKSML-Khulshi 132 kV Ckt-1 | 2023-01-17 09:17 | 2023-01-17 17:04 | 7:47 | S/O | Due to A/M work | 0 | 0 | No interruption
| AKSML-Baroaulia 132 kV Ckt-1 | 2023-01-17 09:24 | 2023-01-17 17:07 | 7:43 | S/O | Due to A/M work | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Sreemongal 132 kV Ckt-2 | 2023-01-17 11:10 | 2023-01-17 12:34 | 1:24 | S/O | Due to A/M work | 0 | 0 | No interruption
| Fenchuganj-Sylhet(Bianibazar) 132 kV Ckt-2 | 2023-01-17 13:00 | 2023-01-17 14:19 | 1:19 | S/O | Due to A/M work | 0 | 0 | No interruption
Chandraghona | Chandraghona-Rangamati 132 kV Ckt-2 | 2023-01-18 08:40 | 2023-01-18 17:01 | 8:21 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulshi | Khulshi-Baraulia 132 kV Ckt-2 | 2023-01-18 08:48 | 2023-01-18 16:02 | 7:14 | S/O | Due to deadline checking. | 0 | 0 | No interruption
Baroauila | Baroauila-Khulshi 132 kV Ckt-1 | 2023-01-18 08:50 | 2023-01-18 16:01 | 7:11 | S/O | Due to A/M work | 0 | 0 | No interruption
Chandraghona | Chandraghona-Rangamati 132 kV Ckt-2 | 2023-01-19 08:42 | 2023-01-19 17:02 | 8:20 | S/O | Due to dead line checking | 0 | 0 | No interruption
Juldah | Juldah-Sikalbaha 132 kV Ckt-1 | 2023-01-19 08:53 | 2023-01-19 16:01 | 7:08 | S/O | Due to dead line checking | 0 | 0 | No interruption
Chandraghona | Chandraghona-Rangamati 132 kV Ckt-2 | 2023-01-20 08:49 | 2023-01-20 16:45 | 7:56 | S/O |  | 0 | 0 | No interruption
| Chandraghona-Rangamati 132 kV Ckt-2 | 2023-01-21 08:43 | 2023-01-21 15:21 | 6:38 | S/O | Due to A/M work | 0 | 0 | No interruption
Juldah | Juldah-Sikalbaha 132 kV Ckt-1 | 2023-01-22 08:22 | 2023-01-22 16:56 | 8:34 | S/O | Due to deadline checking. | 0 | 0 | No interruption
Baroierhat | Baroierhat-Feni 132 kV Ckt-2 | 2023-01-22 08:23 | 2023-01-22 15:13 | 6:50 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Kaptai 132 kV Ckt-1 | 2023-01-22 08:50 | 2023-01-22 16:17 | 7:27 | S/O | Due to A/M work | 0 | 0 | No interruption
Juldah | Juldah-Shahmirpur 132 kV Ckt-1 | 2023-01-23 08:35 | 2023-01-23 14:46 | 6:11 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Kaptai 132 kV Ckt-1 | 2023-01-23 08:47 | 2023-01-23 16:18 | 7:31 | S/O | Due to A/M work | 0 | 0 | No interruption
Baroierhat | Baroierhat-PHP 132 kV Ckt-1 | 2023-01-23 09:15 | 2023-01-23 15:02 | 5:47 | S/O | Due to A/M work | 0 | 0 | No interruption
Juldah | Juldah-Shahmirpur 132 kV Ckt-2 | 2023-01-24 08:49 | 2023-01-24 14:40 | 5:51 | S/O | Due to A/M work | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-TKCL 132 kV Ckt-1 | 2023-01-24 08:55 | 2023-01-24 08:55 | 0:00 | S/O | Due to maint. work | 0 | 0 | No interruption
Hathazari | Hathazari-Kaptai 132 kV Ckt-1 | 2023-01-24 09:13 | 2023-01-24 16:38 | 7:25 | S/O | Due to maint. work | 0 | 0 | No interruption
Madunaghat | Madunaghat-TKCL 132 kV Ckt-1 | 2023-01-24 09:16 | 2023-01-24 09:16 | 0:00 | S/O | Due to maint. work | 0 | 0 | No interruption
Shahmirpur | Shahmirpur-Sikalbaha 132 kV Ckt-1 | 2023-01-25 08:17 | 2023-01-25 15:45 | 7:28 | S/O | Due to maint. work | 0 | 0 | No interruption
Hathazari | Hathazari-Kaptai 132 kV Ckt-2 | 2023-01-25 08:27 | 2023-01-25 16:05 | 7:38 | S/O | Due to maint. work | 0 | 0 | No interruption
Shahmirpur | Shahmirpur-Sikalbaha 132 kV Ckt-1 | 2023-01-26 08:15 | 2023-01-26 15:43 | 7:28 | S/O | Due to A/M work | 0 | 0 | No interruption
Baroierhat | Baroierhat-Hathazari 132 kV Ckt-1 | 2023-01-26 08:58 | 2023-01-26 17:33 | 8:35 | S/O | Due to A/M work | 0 | 0 | No interruption
| Baroierhat-Hathazari 132 kV Ckt-2 | 2023-01-27 08:51 | 2023-01-27 17:00 | 8:09 | S/O | Due to A/M work | 0 | 0 | No interruption
Shahmirpur | Shahmirpur-Sikalbaha 132 kV Ckt-2 | 2023-01-28 08:17 | 2023-01-28 15:40 | 7:23 | S/O | Due to deadline checking. | 0 | 0 | No interruption
Baroierhat | Baroierhat-Hathazari 132 kV Ckt-2 | 2023-01-28 08:36 | 2023-01-28 16:57 | 8:21 | S/O | Due to A/M work | 0 | 0 | No interruption
Anowara | Anowara-Sikalbaha 230 kV Ckt-1 | 2023-01-29 10:17 | 2023-01-29 15:24 | 5:07 | S/O | Due to A/M work | 0 | 0 | No interruption
| Anowara-Sikalbaha 230 kV Ckt-1 | 2023-01-30 08:59 | 2023-01-30 17:46 | 8:47 | S/O | Due to deadline checking. | 0 | 0 | No interruption
Hathazari | Hathazari-Raozan 132 kV Ckt-1 | 2023-01-30 09:25 | 2023-01-30 15:48 | 6:23 | S/O | Due to A/M work | 0 | 0 | No interruption
Anowara | Anowara-Sikalbaha 230 kV Ckt-2 | 2023-01-31 08:35 | 2023-01-31 17:13 | 8:38 | S/O | Due to deadline checking. | 0 | 0 | No interruption
Hathazari | Hathazari-Raozan 132 kV Ckt-2 | 2023-01-31 08:47 | 2023-01-31 17:05 | 8:18 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 442:27 |  | Unserved Energy: |  | 470.4
Page: 8/15 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: January2023
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Cumilla Grid Circle :
Ashuganj(S) | Ashuganj(S)-Ghorashal 132 kV Ckt-2 | 2023-01-01 08:23 | 2023-01-01 17:19 | 8:56 | S/O | Due to A/M work | 0 | 0 | No interruption
B.Baria | B.Baria-Shahjibazar 132 kV Ckt-1 | 2023-01-01 08:38 | 2023-01-01 16:02 | 7:24 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Shahjibazar 132 kV Ckt-1 | 2023-01-01 10:56 | 2023-01-01 15:04 | 4:08 | S/O | Due to relay testing | 0 | 0 | No interruption
Chhatak | Chhatak-Sunamganj 132 kV Ckt-1 | 2023-01-02 08:39 | 2023-01-02 16:36 | 7:57 | S/O | Due to A/M work | 0 | 0 | No interruption
B.Baria | B.Baria-Shahjibazar 132 kV Ckt-1 | 2023-01-02 08:46 | 2023-01-02 16:51 | 8:05 | S/O | Due to A/M work | 0 | 0 | No interruption
| B.Baria-Shahjibazar 132 kV Ckt-1 | 2023-01-03 08:39 | 2023-01-03 17:17 | 8:38 | S/O | Due to A/M work | 0 | 0 | No interruption
Bibiyana | Bibiyana-Fenchuganj 230 kV Ckt-1 | 2023-01-03 08:41 | 2023-01-03 16:05 | 7:24 | S/O | Due to A/M work | 0 | 0 | No interruption
Chattak | Chattak-Sylhet 132 kV Ckt-2 | 2023-01-03 09:42 | 2023-01-03 11:40 | 1:58 | S/O | Due to A/M work | 0 | 0 | No interruption
| Chattak-Sylhet 132 kV Ckt-2 | 2023-01-03 09:58 | 2023-01-03 11:41 | 1:43 | S/O | Due to maint. work | 0 | 0 | No interruption
| Chattak-Sylhet 132 kV Ckt-1 | 2023-01-03 11:46 | 2023-01-03 12:47 | 1:01 | S/O | Due to A/M work | 0 | 0 | No interruption
B.Baria | B.Baria-Shahjibazar 132 kV Ckt-1 | 2023-01-04 08:29 | 2023-01-04 17:16 | 8:47 | S/O | Due to A/M work | 0 | 0 | No interruption
Cumilla(S) | Cumilla(S)-Tripura 132 kV Ckt-1 | 2023-01-04 09:09 | 2023-01-04 16:13 | 7:04 | S/O | Due to A/M work | 0 | 0 | No interruption
Midland P.S | Midland P.S-Ashuganj S.S 230 kV Ckt | 2023-01-04 09:14 |  |  | S/O | Due to A/M work | 0 | 0 | No interruption
B.Baria | B.Baria-Nartsingdi 132 kV Ckt-1 | 2023-01-05 08:36 | 2023-01-05 17:26 | 8:50 | S/O | Due to A/M work | 0 | 0 | No interruption
B.Baria | B.Baria-Shahjibazar 132 kV Ckt-2 | 2023-01-05 08:41 | 2023-01-05 15:57 | 7:16 | S/O | Due to A/M work | 0 | 0 | No interruption
Cumilla(S) | Cumilla(S)-Tripura 132 kV Ckt-1 | 2023-01-05 09:26 | 2023-01-05 16:15 | 6:49 | S/O | Due to A/M work | 0 | 0 | No interruption
B.Baria | B.Baria-Nartsingdi 132 kV Ckt-2 | 2023-01-07 08:25 | 2023-01-07 15:30 | 7:05 | S/O | Due to A/M work | 0 | 0 | No interruption
B.Baria | B.Baria-Shahjibazar 132 kV Ckt-2 | 2023-01-07 08:53 | 2023-01-07 16:54 | 8:01 | S/O | Due to A/M work | 0 | 0 | No interruption
Cumilla(S) | Cumilla(S)-Tripura 132 kV Ckt-2 | 2023-01-07 09:38 | 2023-01-07 17:13 | 7:35 | S/O | Due to A/M work | 0 | 0 | No interruption
B.Baria | B.Baria-Shahjibazar 132 kV Ckt-2 | 2023-01-08 09:30 | 2023-01-08 16:40 | 7:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Ghorashal 230 kV Ckt-1 |  | 2023-01-09 07:10 |  | S/O | After maint.work | 0 | 0 | No interruption
| Ashuganj-Ghorashal 230 kV Ckt-2 |  | 2023-01-09 07:11 |  | S/O |  | 0 | 0 | No interruption
| Ashuganj-Ashuganj Modular 230 kV Ckt | 2023-01-09 08:13 | 2023-01-09 09:08 | 0:55 | S/O | After maint.work | 0 | 0 | No interruption
| Ashuganj-Ashuganj (S) 230 kV Ckt-2 |  | 2023-01-09 08:30 |  | S/O | After maint.work | 0 | 0 | No interruption
B.Baria | B.Baria-Shahjibazar 132 kV Ckt-2 | 2023-01-09 08:42 | 2023-01-09 15:04 | 6:22 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV Ckt-1 |  | 2023-01-09 08:52 |  | S/O | After maint.work | 0 | 0 | No interruption
| Ashuganj-Ashuganj(S) 230 kV Ckt-1 |  | 2023-01-09 08:57 |  | S/O | After maint.work | 0 | 0 | No interruption
| Ashuganj-Comilla(N) 230 kV Ckt-2 |  | 2023-01-09 10:02 |  | S/O |  | 0 | 0 | No interruption
B.Baria | B.Baria-Shahjibazar 132 kV Ckt-2 | 2023-01-10 09:02 | 2023-01-10 15:28 | 6:26 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Comilla(N) 230 kV Ckt-1 & 2 | 2023-01-10 09:52 | 2023-01-10 17:25 | 7:33 | S/O | Due to A/M work | 0 | 0 | No interruption
Daudkandi | Daudkandi-Sonargaon 132 kV Ckt-1 | 2023-01-11 09:22 | 2023-01-11 16:18 | 6:56 | S/O | Due to A/M work | 0 | 0 | No interruption
| Daudkandi-Sonargaon 132 kV Ckt-2 | 2023-01-11 09:22 | 2023-01-11 16:19 | 6:57 | S/O | Due to A/M work | 0 | 0 | No interruption
B.Baria | B.Baria-Nartsingdi 132 kV Ckt-1 | 2023-01-11 09:39 | 2023-01-11 17:04 | 7:25 | S/O | Due to A/M work | 0 | 0 | No interruption
| B.Baria-Nartsingdi 132 kV Ckt-2 | 2023-01-11 09:39 | 2023-01-11 19:35 | 9:56 | S/O | Due to A/M work | 0 | 0 | No interruption
Cumilla(S) | Cumilla(S)-Lakthanavi 53.2 Mw 132 kV Ckt | 2023-01-12 08:35 | 2023-01-12 20:38 | 12:03 | S/O | Due to A/M work | 0 | 0 | No interruption
Page: 9/15 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: January2023
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Cumilla Grid Circle :
B.Baria | B.Baria-Nartsingdi 132 kV Ckt-1 & 2 | 2023-01-12 09:05 | 2023-01-12 17:26 | 8:21 | S/O | Due to A/M work | 0 | 0 | No interruption
Chowmuhani | Chowmuhani-Ramganj 132 kV Ckt-1 | 2023-01-12 09:35 | 2023-01-12 14:42 | 5:07 | S/O | Due to A/M work | 0 | 0 | No interruption
| Chowmuhani-Feni 132 kV Ckt-1 | 2023-01-14 08:22 | 2023-01-14 16:02 | 7:40 | S/O | Due to A/M work | 0 | 0 | No interruption
| Chowmuhani-Ramganj 132 kV Ckt-2 | 2023-01-14 09:01 | 2023-01-14 14:55 | 5:54 | S/O | Due to A/M work | 0 | 0 | No interruption
B.Baria | B.Baria-Narsingdi 132 kV Ckt-1 & 2 | 2023-01-14 09:25 | 2023-01-14 17:01 | 7:36 | S/O | Due to A/M work | 0 | 0 | No interruption
Chowmuhani | Chowmuhani-Feni 132 kV Ckt-1 | 2023-01-15 08:28 | 2023-01-15 16:06 | 7:38 | S/O | Due to A/M work | 0 | 0 | No interruption
B.Baria | B.Baria-Narsingdi 132 kV Ckt-2 | 2023-01-15 09:03 | 2023-01-15 16:53 | 7:50 | S/O | Due to A/M work | 0 | 0 | No interruption
| B.Baria-Narsingdi 132 kV Ckt-1 | 2023-01-15 09:03 | 2023-01-15 16:51 | 7:48 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV Ckt-1 | 2023-01-15 13:05 | 2023-01-15 14:06 | 1:01 | S/O | Due to A/M work | 0 | 0 | No interruption
Chowmuhani | Chowmuhani-Feni 132 kV Ckt-1 | 2023-01-16 08:22 | 2023-01-16 17:18 | 8:56 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV Ckt-2 | 2023-01-16 09:06 | 2023-01-16 10:00 | 0:54 | S/O | Due to A/M work | 0 | 0 | No interruption
B.Baria | B.Baria-Narsingdi 132 kV Ckt-1 | 2023-01-16 09:25 | 2023-01-16 16:43 | 7:18 | S/O | Due to A/M work | 0 | 0 | No interruption
| Fenchuganj-Sylhet 132 kV Ckt-1 | 2023-01-16 09:45 | 2023-01-16 16:44 | 6:59 | S/O | Due to A/M work | 0 | 0 | No interruption
Chowmuhani | Chowmuhani-Feni 132 kV Ckt-2 | 2023-01-17 08:40 | 2023-01-17 15:40 | 7:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Kulaura 132 kV Ckt-2 | 2023-01-17 09:58 | 2023-01-17 11:08 | 1:10 | S/O | Due to A/M work | 0 | 0 | No interruption
| Fenchuganj-Fenchuganj 132 kV Ckt-2 | 2023-01-17 14:22 | 2023-01-17 15:31 | 1:09 | S/O | Due to A/M work | 0 | 0 | No interruption
B.Baria | B.Baria-Nartsingdi 132 kV Ckt-1 |  | 2023-01-17 15:38 |  | S/O | After maint.work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV Ckt-1 | 2023-01-18 08:30 | 2023-01-18 17:27 | 8:57 | S/O | Due to A/M work | 0 | 0 | No interruption
Chowmuhani | Chowmuhani-Feni 132 kV Ckt-2 | 2023-01-18 08:54 | 2023-01-18 15:42 | 6:48 | S/O | Due to Yearly Deadline Checking. | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Sreemongal 132 kV Ckt-1 | 2023-01-18 11:08 | 2023-01-18 11:56 | 0:48 | S/O | Due to maint.work | 0 | 0 | No interruption
| Fenchuganj-Sreemongal 132 kV Ckt-2 | 2023-01-18 11:57 | 2023-01-18 12:50 | 0:53 | S/O | Due to maint.work | 0 | 0 | No interruption
Shahjibazar | Shahjibazar-Sreemongal 132 kV Ckt-2 | 2023-01-18 11:53 | 2023-01-18 13:23 | 1:30 | S/O | Due to A/M work | 0 | 0 | No interruption
| Shahjibazar-Sreemongal 132 kV Ckt-1 | 2023-01-18 11:53 | 2023-01-18 13:23 | 1:30 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV Ckt-1 | 2023-01-19 08:30 | 2023-01-19 14:54 | 6:24 | S/O | Due to A/M work | 0 | 0 | No interruption
Chowmuhani | Chowmuhani-Feni 132 kV Ckt-2 | 2023-01-19 08:44 | 2023-01-19 15:51 | 7:07 | S/O | Due to A/M work | 0 | 0 | No interruption
Bibiyana | Bibiyana-Fenchuganj 230 kV Ckt-1 | 2023-01-19 09:46 | 2023-01-19 17:51 | 8:05 | S/O | Due to A/M work | 0 | 0 | No interruption
Chowmuhani | Chowmuhani-Feni 132 kV Ckt-1 | 2023-01-20 08:23 | 2023-01-20 14:42 | 6:19 | S/O | Due to A/M work | 23 | 145.2833 | Power interruption
| Chowmuhani-Feni 132 kV Ckt-2 | 2023-01-20 08:25 | 2023-01-20 11:06 | 2:41 | S/O | Due to A/M work | 0 | 0 | No interruption
| Chowmuhani-Ramganj 132 kV Ckt-1 | 2023-01-20 08:27 | 2023-01-20 14:25 | 5:58 | S/O | Due to maint. work | 16 | 95.4667 | Power interruption
| Chowmuhani-HFPL 132 kV Ckt | 2023-01-20 08:28 | 2023-01-20 12:25 | 3:57 | S/O | Due to A/M work | 22 | 86.9 | Power interruption
| Chowmuhani-Ramganj 132 kV Ckt-2 | 2023-01-20 08:30 | 2023-01-20 14:27 | 5:57 | S/O |  | 16 | 95.2 | Power interruption
Page: 10/15 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: January2023
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Cumilla Grid Circle :
| Chowmuhani-HFPL 132 kV Ckt | 2023-01-20 14:45 | 2023-01-20 17:10 | 2:25 | S/O | Due to A/M work | 9 | 21.75 | Power interruption
Ashuganj | Ashuganj-Sirajganj 230 kV Ckt-1 | 2023-01-21 08:29 | 2023-01-21 17:13 | 8:44 | S/O | Due to A/M work | 0 | 0 | No interruption
Bibiyana | Bibiyana-Fenchuganj 230 kV Ckt-1 | 2023-01-21 09:17 | 2023-01-21 16:43 | 7:26 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV Ckt-2 | 2023-01-22 07:48 | 2023-01-22 07:48 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
| Ashuganj-Sirajganj 230 kV Ckt-2 | 2023-01-23 08:30 | 2023-01-23 17:16 | 8:46 | S/O | Due to A/M work | 0 | 0 | No interruption
Bibiyana | Bibiyana-Fenchuganj 230 kV Ckt-1 | 2023-01-23 09:24 | 2023-01-23 17:27 | 8:03 | S/O | Due to Dead line checking . | 0 | 0 | No interruption
Bibiyana | Bibiyana-Fenchuganj 230 kV Ckt-1 | 2023-01-23 09:48 | 2023-01-23 17:28 | 7:40 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV Ckt-2 | 2023-01-24 08:18 | 2023-01-24 17:01 | 8:43 | S/O | Due to A/M work | 0 | 0 | No interruption
Bibiyana | Bibiyana-Kaliakoir 400 kV Ckt-1 | 2023-01-24 08:50 | 2023-01-24 16:35 | 7:45 | S/O | Due to A/M work | 0 | 0 | No interruption
| Bibiyana-Fenchuganj 230 kV Ckt-1 | 2023-01-24 09:02 | 2023-01-24 15:57 | 6:55 | S/O | Due to A/M work | 0 | 0 | No interruption
Chauddagram | Chauddagram-Feni 132 kV Ckt-1 | 2023-01-24 09:23 | 2023-01-24 16:55 | 7:32 | S/O | Due to SPMD work | 0 | 0 | No interruption
Comilla(N) | Comilla(N)-Kachua 132 kV Ckt-2 | 2023-01-25 07:49 | 2023-01-25 16:58 | 9:09 | S/O | Due to A/M work | 0 | 0 | No interruption
| Comilla(N)-Kachua 132 kV Ckt-1 | 2023-01-25 07:51 | 2023-01-25 16:57 | 9:06 | S/O | Due to A/M work | 0 | 0 | No interruption
Bibiyana | Bibiyana-Kaliakoir 400 kV Ckt-1 | 2023-01-25 08:28 | 2023-01-25 16:25 | 7:57 | S/O | Due to A/M work | 0 | 0 | No interruption
| Bibiyana-Fenchuganj 230 kV Ckt-1 | 2023-01-25 08:37 | 2023-01-25 16:18 | 7:41 | S/O | Due to A/M work | 0 | 0 | No interruption
| Bibiyana-Fenchuganj 230 kV Ckt-1 | 2023-01-25 08:47 | 2023-01-25 16:20 | 7:33 | S/O | Due to A/M work | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Sreemongal 132 kV Ckt-1 | 2023-01-25 09:18 | 2023-01-25 17:33 | 8:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Bhulta 400 kV Ckt-1 | 2023-01-25 10:22 | 2023-01-25 17:02 | 6:40 | S/O | Due to A/M work | 0 | 0 | No interruption
Comilla(S) | Comilla(S)-Kachua 132 kV Ckt-1 | 2023-01-26 08:21 | 2023-01-26 15:54 | 7:33 | S/O | Due to A/M work | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Sreemongal 132 kV Ckt-1 | 2023-01-26 08:26 | 2023-01-26 16:54 | 8:28 | S/O | Due to A/M work | 0 | 0 | No interruption
Bibiyana | Bibiyana-Kaliakoir 400 kV Ckt-1 | 2023-01-26 09:45 | 2023-01-26 17:10 | 7:25 | S/O | Due to A/M work | 0 | 0 | No interruption
| Bibiyana-Fenchuganj 230 kV Ckt-1 | 2023-01-26 09:51 | 2023-01-26 17:32 | 7:41 | S/O | Due to Dead line checking . | 0 | 0 | No interruption
| Bibiyana-Kaliakoir 400 kV Ckt-2 | 2023-01-26 13:23 | 2023-01-26 17:11 | 3:48 | S/O | Due to Due to Dead Line checking. | 0 | 0 | No interruption
Ashuganj | Ashuganj-Bhulta 400 kV Ckt-1 | 2023-01-27 09:00 | 2023-01-27 19:04 | 10:04 | S/O |  | 0 | 0 | No interruption
| Ashuganj-Bhulta 400 kV Ckt-1 | 2023-01-28 07:52 | 2023-01-28 19:03 | 11:11 | S/O | Due to Due to Dead Line checking. | 0 | 0 | No interruption
| Ashuganj(N)-South 230 kV Ckt-1 | 2023-01-28 08:23 | 2023-01-28 08:23 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Comilla(N) | Comilla(N)-Kachua 132 kV Ckt-2 | 2023-01-28 08:50 | 2023-01-28 14:28 | 5:38 | S/O | Due to A/M work | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Sreemongal 132 kV Ckt-2 | 2023-01-28 09:10 | 2023-01-28 17:02 | 7:52 | S/O | Due to A/M work | 0 | 0 | No interruption
| Fenchuganj-Sreemongal 132 kV Ckt-1 | 2023-01-28 09:20 | 2023-01-28 17:18 | 7:58 | S/O | Due to A/M work | 0 | 0 | No interruption
Bibiyana | Bibiyana-Fenchuganj 230 kV Ckt-1 | 2023-01-28 10:05 | 2023-01-28 16:18 | 6:13 | S/O | Due to A/M work | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Sreemongal 132 kV Ckt-2 | 2023-01-29 08:23 | 2023-01-29 17:28 | 9:05 | S/O | Due to maint. work | 0 | 0 | No interruption
Bibiyana | Bibiyana-Fenchuganj 230 kV Ckt-1 | 2023-01-29 09:14 | 2023-01-29 17:48 | 8:34 | S/O | Due to Due to Dead Line checking. | 0 | 0 | No interruption
Bibiyana | Bibiyana-Fenchuganj 230 kV Ckt-1 | 2023-01-29 09:27 | 2023-01-29 17:47 | 8:20 | S/O | Due to Due to Dead Line checking. | 0 | 0 | No interruption
Page: 11/15 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: January2023
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Cumilla Grid Circle :
Comilla(N) | Comilla(N)-Comilla(S) 132 kV Ckt-3 | 2023-01-29 09:46 | 2023-01-29 15:05 | 5:19 | S/O | Due to A/M work | 0 | 0 | No interruption
| Comilla(N)-Kachua 132 kV Ckt-2 | 2023-01-29 09:46 | 2023-01-29 15:03 | 5:17 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Bhulta 400 kV Ckt-1 | 2023-01-29 10:42 | 2023-01-29 15:51 | 5:09 | S/O | Due to A/M work | 0 | 0 | No interruption
| Ashuganj Network-South 230 kV Ckt-1 |  | 2023-01-29 17:31 |  | S/O | After maint.work | 0 | 0 | No interruption
Bibiyana | Bibiyana-Fenchuganj 230 kV Ckt-1 | 2023-01-30 08:15 | 2023-01-30 08:15 | 0:00 | S/O | Due to Due to Dead Line checking. | 0 | 0 | No interruption
Ashuganj | Ashuganj-Bhulta 400 kV Ckt-2 | 2023-01-30 08:25 | 2023-01-30 18:20 | 9:55 | S/O |  | 0 | 0 | No interruption
| Ashuganj-Cumilla(N) 230 kV Ckt-1 & 2 |  | 2023-01-30 08:30 |  | S/O | After maint.work | 0 | 0 | No interruption
| Ashuganj-Cumilla(N) 230 kV Ckt-2 | 2023-01-30 08:31 | 2023-01-31 15:14 | 30:43 | S/O | Due to Due to Dead Line checking. | 0 | 0 | No interruption
| Ashuganj-Cumilla(N) 230 kV Ckt-1 | 2023-01-30 08:31 | 2023-01-30 17:38 | 9:07 | S/O |  | 0 | 0 | No interruption
Shahjibazar | Shahjibazar-Sreemongal 132 kV Ckt-1 | 2023-01-30 09:05 | 2023-01-30 14:21 | 5:16 | S/O | Due to relay testing | 0 | 0 | No interruption
| Shahjibazar-Sreemongal 132 kV Ckt-2 | 2023-01-30 11:50 | 2023-01-30 14:23 | 2:33 | S/O |  | 0 | 0 | No interruption
Chauddagram | Chauddagram-Cumilla(S) 132 kV Ckt-1 | 2023-01-31 07:38 | 2023-01-31 13:04 | 5:26 | S/O | Due to A/M work | 0 | 0 | No interruption
Bibiyana | Bibiyana-Fenchuganj 230 kV Ckt-2 | 2023-01-31 08:32 | 2023-01-31 16:14 | 7:42 | S/O | Due to Due to Dead Line checking. | 0 | 0 | No interruption
Comilla(S) | Comilla(S)-Kachua 132 kV Ckt-2 | 2023-01-31 13:18 | 2023-01-31 14:27 | 1:09 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 677:25 |  | Unserved Energy: |  | 444.6
Khulna Grid Circle :
Barishal(N) | Barishal(N)-Madaripur 132 kV Ckt-1 | 2023-01-01 08:42 | 2023-01-01 08:42 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
| Barishal(N)-Madaripur 132 kV Ckt-1 | 2023-01-02 09:04 | 2023-01-02 16:09 | 7:05 | S/O | Due to A/M work | 0 | 0 | No interruption
| Barishal(N)-Madaripur 132 kV Ckt-1 | 2023-01-03 09:15 | 2023-01-03 17:11 | 7:56 | S/O | Due to A/M work | 0 | 0 | No interruption
Gallamari | Gallamari-Khulna(S) 132 kV Ckt-1 | 2023-01-03 17:12 | 2023-01-03 17:12 | 0:00 | S/O | Due to Instruction By Aldc,Khulna. | 0 | 0 | No interruption
| Gallamari-Khulna(S) 132 kV Ckt-2 | 2023-01-03 17:13 | 2023-01-03 17:13 | 0:00 | S/O |  | 0 | 0 | No interruption
Barishal(N) | Barishal(N)-Madaripur 132 kV Ckt-1 | 2023-01-05 09:05 | 2023-01-05 16:38 | 7:33 | S/O | Due to A/M work | 0 | 0 | No interruption
Goalpara | Goalpara-NWPGCL 132 kV Ckt | 2023-01-05 09:33 | 2023-01-05 16:32 | 6:59 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulna © | Khulna © -KPCL 132 kV Ckt-2 | 2023-01-05 09:39 | 2023-01-05 15:33 | 5:54 | S/O | Due to A/M work | 0 | 0 | No interruption
Gallamari | Gallamari-Khulna(S) 132 kV Ckt-1 | 2023-01-07 09:38 | 2023-01-07 18:23 | 8:45 | S/O | Due to SAS test | 0 | 0 | No interruption
Gopalganj | Gopalganj-Rampal 400 kV line-1 |  | 2023-01-09 06:53 |  | S/O | After maint.work | 0 | 0 | No interruption
| Gopalganj-Rampal 400 kV line-2 |  | 2023-01-09 06:58 |  | S/O |  | 0 | 0 | No interruption
Magura | Magura-Narail 132 kV Ckt-1 | 2023-01-09 08:28 | 2023-01-09 16:34 | 8:06 | S/O | Due to A/M work | 0 | 0 | No interruption
Barishal(N) | Barishal(N)-Madaripur 132 kV Ckt-2 | 2023-01-09 09:39 | 2023-01-09 16:41 | 7:02 | S/O | Due to A/M work | 0 | 0 | No interruption
Gallamari | Gallamari-Khulna(S) 132 kV Ckt-2 | 2023-01-09 10:19 | 2023-01-09 20:11 | 9:52 | S/O | Due to A/M work | 0 | 0 | No interruption
Gopalganj | Gopalganj-Rampal 400 kV line-1 & 2 | 2023-01-09 21:46 | 2023-01-09 21:46 | 0:00 | S/O | Due to line over load | 0 | 0 | No interruption
Magura | Magura-Narail 132 kV Ckt-1 | 2023-01-10 08:08 | 2023-01-10 15:39 | 7:31 | S/O | Due to A/M work | 40 | 300.6667 | Power interruption
Faridpur | Faridpur-Rajbari 132 kV Ckt-1 | 2023-01-10 08:30 | 2023-01-10 14:50 | 6:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Rajbari | Rajbari-Faridpur 132 kV Ckt-1 | 2023-01-10 08:31 | 2023-01-10 14:49 | 6:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Magura | Magura-Narail 132 kV Ckt-2 | 2023-01-10 08:07 | 2023-01-10 16:46 | 8:39 | S/O | Due to A/M work | 0 | 0 | No interruption
Faridpur | Faridpur-Rajbari 132 kV Ckt-1 | 2023-01-11 08:38 | 2023-01-11 13:56 | 5:18 | S/O | Due to A/M work | 0 | 0 | No interruption
| Faridpur-Rajbari 132 kV Ckt-1 | 2023-01-11 08:39 | 2023-01-11 13:55 | 5:16 | S/O | Due to A/M work | 0 | 0 | No interruption
Magura | Magura-Narail 132 kV Ckt-2 | 2023-01-11 08:08 | 2023-01-11 15:14 | 7:06 | S/O | Due to A/M work | 0 | 0 | No interruption
Faridpur | Faridpur-Rajbari 132 kV Ckt-1 | 2023-01-12 11:24 | 2023-01-12 13:44 | 2:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Rajbari | Rajbari-Faridpur 132 kV Ckt-1 | 2023-01-12 11:24 | 2023-01-12 13:42 | 2:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Page: 12/15 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: January2023
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Khulna Grid Circle :
Gopalganj | Gopalganj-Payra P/S 400 kV Ckt-2 | 2023-01-12 13:49 | 2023-01-12 14:55 | 1:06 | S/O | Due to A/M work | 0 | 0 | No interruption
Madaripur | Madaripur-Gopalganj (N) Ckt-3 |  | 2023-01-12 19:46 |  | S/O | After maint.work | 0 | 0 | No interruption
Rajbari | Rajbari-Faridpur 132 kV Ckt-2 | 2023-01-13 08:45 | 2023-01-13 08:45 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Faridpur | Faridpur-Gopalganj (N) 132 kV Ckt-2 | 2023-01-13 08:45 | 2023-01-13 08:45 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Gopalganj | Gopalganj-Payra P/S 400 kV Ckt-1 | 2023-01-13 09:55 | 2023-01-13 09:55 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Gallamari | Gallamari-Khulna(S) 132 kV Ckt-1 |  | 2023-01-14 08:52 |  | S/O | After maint.work | 0 | 0 | No interruption
| Gallamari-Khulna(S) 132 kV Ckt-2 |  | 2023-01-14 08:53 |  | S/O |  | 0 | 0 | No interruption
Rampal | Rampal-Gopalganj 400 kV Ckt-2 | 2023-01-14 09:01 | 2023-01-14 09:01 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
| Rampal-Gopalganj 400 kV Ckt-1 | 2023-01-14 13:20 | 2023-01-14 13:20 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Rajbari | Rajbari-Bheramara 132 kV Ckt-1 | 2023-01-15 09:11 | 2023-01-15 16:44 | 7:33 | S/O | Due to A/M work | 0 | 0 | No interruption
Faridpur | Faridpur-Rajbari 132 kV Ckt-2 |  | 2023-01-15 15:01 |  | S/O | After maint.work | 0 | 0 | No interruption
Rajbari | Rajbari-Bheramara 132 kV Ckt-1 | 2023-01-15 08:51 | 2023-01-15 14:45 | 5:54 | S/O | Due to A/M work | 0 | 0 | No interruption
Patuakhali | Patuakhali-Payra 132 kV Ckt-1 | 2023-01-17 07:23 | 2023-01-17 07:23 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulna (S) | Khulna (S)-Rampal 132 kV Ckt-1 | 2023-01-17 07:57 | 2023-01-17 17:10 | 9:13 | S/O | Due to A/M work | 0 | 0 | No interruption
Rajbari | Rajbari-Bheramara 132 kV Ckt-2 | 2023-01-17 08:32 | 2023-01-17 15:46 | 7:14 | S/O | Due to A/M work | 0 | 0 | No interruption
Patuakhali | Patuakhali-Payra 132 kV Ckt-1 |  | 2023-01-17 18:26 |  | S/O | After maint.work | 0 | 0 | No interruption
Khulna (S) | Khulna (S)-Rampal 132 kV Ckt-1 | 2023-01-18 08:14 | 2023-01-18 14:40 | 6:26 | S/O | Due to A/M work | 0 | 0 | No interruption
Patuakhali | Patuakhali-Payra 132 kV Ckt-2 | 2023-01-18 08:20 | 2023-01-18 17:27 | 9:07 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulna (C) | Khulna ©-Khulna(S) 132 kV Ckt-1 | 2023-01-18 08:32 | 2023-01-18 08:32 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
| Khulna ©-KPCL-2 132 kV Ckt | 2023-01-18 08:34 | 2023-01-18 08:34 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
| Khulna ©-Nort -West 132 kV Ckt-1 & 2 | 2023-01-18 08:39 | 2023-01-18 08:39 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Rajbari | Rajbari-Bheramara 132 kV Ckt-2 | 2023-01-18 09:23 | 2023-01-18 15:37 | 6:14 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulna (S) | Khulna (S)-Rampal 132 kV Ckt-2 | 2023-01-19 08:28 | 2023-01-19 17:21 | 8:53 | S/O | Due to A/M work | 0 | 0 | No interruption
Rajbari | Rajbari-Bheramara 132 kV Ckt-2 | 2023-01-19 08:52 | 2023-01-19 14:22 | 5:30 | S/O | Due to A/M work | 0 | 0 | No interruption
Payra | Payra-Gopalganj 400 kV Ckt-2 | 2023-01-19 08:33 | 2023-01-19 08:33 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulna (S) | Khulna (S)-Rampal 132 kV Ckt-2 | 2023-01-20 08:58 | 2023-01-20 15:18 | 6:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Rampal | Rampal-Gopalganj 400 kV Ckt-1 | 2023-01-20 09:42 | 2023-01-20 09:42 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Khulna (C) | Khulna ©-Khulna(S) 132 kV Ckt-1 |  | 2023-01-20 16:09 |  | S/O | After maint.work | 0 | 0 | No interruption
Gollamari | Gollamari-Gopalganj 132 kV Ckt-1 | 2023-01-21 08:35 | 2023-01-21 17:15 | 8:40 | S/O | Due to A/M work | 0 | 0 | No interruption
Gopalganj | Gopalganj-Gallamari 132 kV Ckt-1 | 2023-01-21 08:48 | 2023-01-21 08:48 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
| Gopalganj-Gallamari 132 kV Ckt-1 | 2023-01-22 08:08 | 2023-01-22 16:49 | 8:41 | S/O | Due to A/M work | 0 | 0 | No interruption
Gollamari | Gollamari-Gopalganj 132 kV Ckt-1 | 2023-01-22 08:37 | 2023-01-22 16:50 | 8:13 | S/O | Due to A/M work | 0 | 0 | No interruption
Gopalganj | Gopalganj-Payra P/S 400 kV Ckt-2 |  | 2023-01-22 21:31 |  | S/O | After maint.work | 0 | 0 | No interruption
| Gopalganj-Payra P/S 400 kV Ckt-1 | 2023-01-22 21:47 | 2023-01-22 21:47 | 0:00 | S/O | Due to Protection Test Purpose. | 0 | 0 | No interruption
Gopalganj | Gopalganj-Gollamari 132 kV Ckt-2 | 2023-01-23 07:53 | 2023-01-23 16:54 | 9:01 | S/O | Due to A/M work | 0 | 0 | No interruption
Madaripur | Madaripur-Shariatpur 132 kV Ckt-1 | 2023-01-23 08:46 | 2023-01-23 17:19 | 8:33 | S/O | Due to A/M work | 0 | 0 | No interruption
Barishal | Barishal-Patuakhali 132 kV Ckt | 2023-01-23 09:01 | 2023-01-23 17:54 | 8:53 | S/O | Due to A/M work | 0 | 0 | No interruption
Rampal | Rampal-Gopalganj 400 kV Ckt-2 | 2023-01-23 21:06 | 2023-01-23 21:06 | 0:00 | S/O | Line Shift From Gopalgon(N) permanent S/S | 0 | 0 | No interruption
Barishal | Barishal-Patuakhali(Barguna T at Bakergonj) 132 kV Ckt | 2023-01-24 08:16 | 2023-01-24 17:07 | 8:51 | S/O | Due to A/M work | 0 | 0 | No interruption
Page: 13/15 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: January2023
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Khulna Grid Circle :
Barishal | Barishal-Patuakhali(Barguna T at Bakergonj) 132 kV Ckt | 2023-01-24 08:16 | 2023-01-24 17:06 | 8:50 | S/O | Due to A/M work | 0 | 0 | No interruption
Madaripur | Madaripur-Shariatpur 132 kV Ckt-1 | 2023-01-24 08:19 | 2023-01-24 18:15 | 9:56 | S/O | Due to A/M work | 0 | 0 | No interruption
Bagerhat | Bagerhat-Mongla 132 kV Ckt-2 | 2023-01-24 08:29 | 2023-01-24 16:24 | 7:55 | S/O | Due to A/M work | 0 | 0 | No interruption
Gopalganj | Gopalganj-Gollamari 132 kV Ckt-2 | 2023-01-24 08:33 | 2023-01-24 16:07 | 7:34 | S/O | Due to A/M work | 0 | 0 | No interruption
Gollamari | Gollamari-Gopalganj 132 kV Ckt-2 | 2023-01-24 08:38 | 2023-01-24 16:09 | 7:31 | S/O | Due to A/M work | 0 | 0 | No interruption
Bagerhat | Bagerhat-Mongla 132 kV ckt-2 | 2023-01-25 07:38 | 2023-01-25 15:31 | 7:53 | S/O | Due to A/M work | 0 | 0 | No interruption
Madaripur | Madaripur-Shariatpur 132 kV Ckt-2 | 2023-01-25 08:12 | 2023-01-25 17:51 | 9:39 | S/O | Due to A/M work | 0 | 0 | No interruption
Patuakhali | Patuakhali-Barisal 132 kV Ckt | 2023-01-25 08:22 | 2023-01-25 16:32 | 8:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Barishal | Barishal-Patuakhali(Barguna T at Bakergonj) 132 kV Ckt | 2023-01-25 08:23 | 2023-01-25 16:32 | 8:09 | S/O | Due to A/M work | 0 | 0 | No interruption
Madaripur | Madaripur-Shariatpur 132 kV Ckt-2 | 2023-01-25 08:30 | 2023-01-25 17:51 | 9:21 | S/O | Due to A/M work | 0 | 0 | No interruption
| Madaripur-Shariatpur 132 kV Ckt-2 | 2023-01-26 08:09 | 2023-01-26 13:37 | 5:28 | S/O | Due to A/M work | 0 | 0 | No interruption
Bagerhat | Bagerhat-Mongla 132 kV Ckt-2 | 2023-01-26 08:17 | 2023-01-26 14:37 | 6:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Gopalganj(O) | Gopalganj(O)-Gopalganj(N) 132 kV Ckt-1 | 2023-01-26 09:05 | 2023-01-26 20:31 | 11:26 | S/O | Due to A/M work | 0 | 0 | No interruption
| Gopalganj(O)-Gopalganj(N) 132 kV Ckt-2 | 2023-01-26 09:17 | 2023-01-26 20:32 | 11:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Gopalganj(N) | Gopalganj(N)-Madaripur 132 kV Ckt-1 | 2023-01-26 09:24 | 2023-01-26 16:20 | 6:56 | S/O | Due to A/M work | 0 | 0 | No interruption
| Gopalganj(N)-Madaripur 132 kV Ckt-2 | 2023-01-26 09:31 | 2023-01-26 16:21 | 6:50 | S/O | Due to A/M work | 0 | 0 | No interruption
Faridpur | Faridpur-Gopalganj (N) 132 kV Ckt-1 | 2023-01-26 09:32 | 2023-01-26 16:17 | 6:45 | S/O | Due to A/M work | 0 | 0 | No interruption
Gopalganj(N) | Gopalganj(N)-Madaripur 132 kV Ckt-3 | 2023-01-26 09:33 | 2023-01-26 20:26 | 10:53 | S/O | Due to A/M work | 0 | 0 | No interruption
| Gopalganj(N)-Madaripur 132 kV Ckt-3 | 2023-01-26 09:42 | 2023-01-26 20:27 | 10:45 | S/O | Due to A/M work | 0 | 0 | No interruption
Faridpur | Faridpur-Gopalganj (N) 132 kV Ckt-2 | 2023-01-26 09:44 | 2023-01-26 16:18 | 6:34 | S/O | Due to A/M work | 0 | 0 | No interruption
Gopalganj(O) | Gopalganj(O)-Gopalganj(N) 132 kV Ckt-1 & 2 | 2023-01-26 09:49 | 2023-01-26 09:49 | 0:00 | S/O | Due to project work | 0 | 0 | No interruption
Gopalganj(N) | Gopalganj(N)-Madaripur 132 kV Ckt-3 | 2023-01-26 09:33 | 2023-01-26 20:26 | 10:53 | S/O | Due to project work | 0 | 0 | No interruption
| Gopalganj(N)-Madaripur 132 kV Ckt-4 | 2023-01-26 09:42 | 2023-01-26 20:27 | 10:45 | S/O | Due to project work | 0 | 0 | No interruption
Madaripur | Madaripur-Shariatpur 132 kV Ckt-1 | 2023-01-26 13:51 | 2023-01-26 15:52 | 2:01 | S/O | Due to project work | 0 | 0 | No interruption
Rajbari | Rajbari-Bheramara 132 kV Ckt-1 | 2023-01-27 08:07 | 2023-01-27 16:38 | 8:31 | S/O | Due to project work | 0 | 0 | No interruption
Barishal | Barishal-Bhola 230 kV Ckt-1 | 2023-01-27 08:32 | 2023-01-27 17:13 | 8:41 | S/O | Due to A/M work | 0 | 0 | No interruption
| Barishal-Bhola 230 kV Ckt-1 | 2023-01-28 08:24 | 2023-01-28 16:12 | 7:48 | S/O | Due to A/M work | 0 | 0 | No interruption
Rajbari | Rajbari-Bheramara 132 kV Ckt-1 | 2023-01-28 08:48 | 2023-01-28 14:57 | 6:09 | S/O | Due to A/M work | 0 | 0 | No interruption
Bagerhat | Bagerhat-Goalpara 132 kV Ckt-1 | 2023-01-29 08:13 | 2023-01-29 17:27 | 9:14 | S/O | Due to A/M work | 0 | 0 | No interruption
Barishal | Barishal-Bhola 230 kV Ckt-2 | 2023-01-29 08:32 | 2023-01-29 17:03 | 8:31 | S/O | Due to A/M work | 0 | 0 | No interruption
Faridpur | Faridpur-Gopalganj (N) 132 kV Ckt-1 | 2023-01-29 09:36 | 2023-01-29 15:03 | 5:27 | S/O | Due to A/M work | 0 | 0 | No interruption
Barishal | Barishal-Bhola 230 kV Ckt-2 | 2023-01-30 08:42 | 2023-01-30 18:04 | 9:22 | S/O | Due to A/M work | 0 | 0 | No interruption
Goalpara | Goalpara-Khulna© 132 kV Ckt-2 | 2023-01-30 09:07 | 2023-01-30 16:47 | 7:40 | S/O | Due to painting work | 0 | 0 | No interruption
| Goalpara-Khulna© 132 kV Ckt-2 | 2023-01-31 08:14 | 2023-01-31 17:03 | 8:49 | S/O | Due to A/M work | 0 | 0 | No interruption
Faridpur | Faridpur-Gopalganj (N) 132 kV Ckt-2 | 2023-01-31 10:05 | 2023-01-31 15:37 | 5:32 | S/O | Due to A/M work | 0 | 0 | No interruption
Gopalganj(O) | Gopalganj(O)-Gopalganj (N) 132 Ckt-1 |  | 2023-01-31 12:16 |  | S/O | After maint.work | 0 | 0 | No interruption
| Gopalganj(O)-Gopalganj (N) 132 Ckt-2 |  | 2023-01-31 12:17 |  | S/O |  | 0 | 0 | No interruption
|  |  | Total : | 532:13 |  | Unserved Energy: |  | 300.6667
Page: 14/15 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: January2023
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
HVDC Grid Circle :
Pabna | Pabna-Shahjadpur 132 kV Ckt-1 | 2023-01-01 08:37 | 2023-01-01 16:46 | 8:09 | S/O | Due to A/M work | 0 | 0 | No interruption
HVDC Bheramara | HVDC Bheramara-Jhenaidah 230 kV Ckt-1 | 2023-01-01 10:06 | 2023-01-01 18:40 | 8:34 | S/O | ue to Teleprotection Testing | 0 | 0 | No interruption
BIPTC | BIPTC-Bahrampur 132 kV CKt-3 | 2023-01-01 10:47 | 2023-01-01 10:47 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Benapole | Benapole-Jashore 132 kV Ckt-1 | 2023-01-02 08:22 | 2023-01-02 17:10 | 8:48 | S/O | Due to A/M work | 0 | 0 | No interruption
Pabna | Pabna-Shahjadpur 132 kV Ckt-1 | 2023-01-02 08:26 | 2023-01-02 17:01 | 8:35 | S/O | Due to A/M work | 0 | 0 | No interruption
HVDC Bheramara | HVDC Bheramara-Jhenaidah 230 kV Ckt-1 | 2023-01-02 09:19 | 2023-01-02 14:37 | 5:18 | S/O | Due to A/M work | 0 | 0 | No interruption
| HVDC Bheramara-Jhenaidah 230 kV Ckt-2 | 2023-01-02 14:53 | 2023-01-02 19:01 | 4:08 | S/O | Due to A/M work | 0 | 0 | No interruption
Benapole | Benapole-Jashore 132 kV Ckt-1 | 2023-01-03 08:19 | 2023-01-03 08:19 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
BIPTC | BIPTC-Bahrampur 132 kV CKt-4 | 2023-01-03 09:16 | 2023-01-03 18:10 | 8:54 | S/O | Due to A/M work | 0 | 0 | No interruption
Jhenaidah | Jhenaidah-Khulna 230 kV Ckt-1 | 2023-01-03 13:59 | 2023-01-03 15:59 | 2:00 | S/O | Due to relay testing | 0 | 0 | No interruption
| Jhenaidah-Khulna 230 kV Ckt-2 | 2023-01-03 13:59 | 2023-01-03 17:08 | 3:09 | S/O | Due to project work | 0 | 0 | No interruption
Benapole | Benapole-Jashore 132 kV Ckt-1 | 2023-01-04 08:31 | 2023-01-04 16:17 | 7:46 | S/O | Due to project work | 0 | 0 | No interruption
BIPTC | BIPTC-Bahrampur 132 kV CKt-4 | 2023-01-04 10:09 | 2023-01-04 18:39 | 8:30 | S/O | Due to project work | 0 | 0 | No interruption
Benapole | Benapole-Jashore 132 kV Ckt-2 | 2023-01-05 08:41 | 2023-01-05 16:17 | 7:36 | S/O | Due to project work | 0 | 0 | No interruption
| Benapole-Jashore 132 kV Ckt-2 | 2023-01-06 08:26 | 2023-01-06 13:43 | 5:17 | S/O | Due to A/M work | 0 | 0 | No interruption
HVDC Bheramara | HVDC Bheramara-Rajshahi 230 kV Ckt-1 | 2023-01-06 17:08 | 2023-01-06 17:08 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
| HVDC Bheramara-Rajshahi 230 kV Ckt-2 | 2023-01-06 17:10 | 2023-01-06 17:10 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Bheramara P/S | Bheramara P/S-Kustia 132 kV Ckt-1 | 2023-01-06 07:41 | 2023-01-06 07:41 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Jhenaidah | Jhenaidah-Kustia 132 kV Ckt-1 | 2023-01-07 07:56 | 2023-01-07 07:56 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
| Jhenaidah-Kustia 132 kV Ckt-2 | 2023-01-07 07:57 | 2023-01-07 16:53 | 8:56 | S/O | Due to A/M work | 0 | 0 | No interruption
Bheramara P/S | Bheramara P/S-Kustia 132 kV Ckt-1 | 2023-01-07 07:59 | 2023-01-07 16:54 | 8:55 | S/O | Due to A/M work | 0 | 0 | No interruption
| Bheramara P/S-Kustia 132 kV Ckt-2 | 2023-01-07 07:59 | 2023-01-07 16:55 | 8:56 | S/O | Due to A/M work | 0 | 0 | No interruption
Baghabari | Baghabari-Bhangura 132 kV Ckt-02 | 2023-01-07 08:15 | 2023-01-07 08:15 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
| Baghabari-Bhangura 132 kV Ckt-01 | 2023-01-07 08:18 | 2023-01-07 15:36 | 7:18 | S/O | Due to A/M work | 6 | 43.8 | Power interruption
Benapole | Benapole-Jashore 132 kV Ckt-2 | 2023-01-07 08:33 | 2023-01-07 18:02 | 9:29 | S/O | Due to A/M work | 0 | 0 | No interruption
| Jhenaidah -Kustia 132 kV Ckt-1 |  | 2023-01-07 16:51 |  | S/O | After maint.work | 0 | 0 | No interruption
Jashore | Jashore-Jhenaidah 132 kV Ckt-1 | 2023-01-08 09:00 | 2023-01-08 17:11 | 8:11 | S/O | Due to A/M work | 0 | 0 | No interruption
Jhenaidah | Jhenaidah2-Jashore Ckt-1 | 2023-01-08 09:01 | 2023-01-08 17:10 | 8:09 | S/O | Due to A/M work | 0 | 0 | No interruption
HVDC Bheramara | HVDC Bheramara-Jhenaidah 230 kV Ckt-1 |  | 2023-01-08 17:19 |  |  | After maint.work | 0 | 0 | No interruption
Jhenaidah | Jhenaidah2-Jashore Ckt-1/2 | 2023-01-09 09:07 | 2023-01-09 13:54 | 4:47 | S/O | Due to A/M work | 0 | 0 | No interruption
Shahjadpur | Shahjadpur-Sirajganj 132 kV Ckt-1 | 2023-01-10 08:52 | 2023-01-10 18:05 | 9:13 | S/O | Due to A/M work | 0 | 0 | No interruption
Jhenaidah | Jhenaidah2-Jashore Ckt-2 | 2023-01-10 09:12 | 2023-01-10 14:39 | 5:27 | S/O | Due to A/M work | 0 | 0 | No interruption
| Jhenaidah2-Jashore Ckt-(L1) | 2023-01-10 09:13 | 2023-01-10 14:40 | 5:27 | S/O | Due to A/M work | 0 | 0 | No interruption
Baghabari | Baghabari-Sirajganj 230 kV Ckt-1 | 2023-01-11 08:14 | 2023-01-11 17:16 | 9:02 | S/O | Due to A/M work | 0 | 0 | No interruption
Shahjadpur | Shahjadpur-Sirajganj 132 kV Ckt-1 | 2023-01-11 09:02 | 2023-01-11 16:44 | 7:42 | S/O | Due to A/M work | 0 | 0 | No interruption
Jashore | Jashore-Jhenaidah -2132 kV Ckt-(L1) | 2023-01-11 09:13 | 2023-01-11 16:18 | 7:05 | S/O | Due to A/M work | 0 | 0 | No interruption
Monakasha | Monakasha-Rahanpur 400 kV Ckt-1 | 2023-01-11 12:14 | 2023-01-11 17:29 | 5:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Baghabari | Baghabari-Sirajganj 132 kV Ckt-1 | 2023-01-12 08:45 | 2023-01-12 16:05 | 7:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Chuadanga | Chuadanga-Jhenaidah 132 kV Ckt-1 | 2023-01-14 08:12 | 2023-01-14 15:07 | 6:55 | S/O | Due to A/M work | 56 | 387.3333 | Power interruption
Baghabari | Baghabari-Sirajganj 230 kV Ckt-2 | 2023-01-15 08:33 | 2023-01-15 17:51 | 9:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Bheramara P/S | Bheramara P/S-Faripdpur 132 kV Ckt-1 & 2 | 2023-01-15 09:17 | 2023-01-15 16:43 | 7:26 | S/O | Due to A/M work | 0 | 0 | No interruption
Baghabari | Baghabari-Sirajganj 230 kV Ckt-2 | 2023-01-16 08:51 | 2023-01-16 17:06 | 8:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Bheramara P/S | Bheramara P/S-Faripdpur 132 kV Ckt-1 | 2023-01-16 08:52 | 2023-01-16 14:46 | 5:54 | S/O | Due to A/M work | 0 | 0 | No interruption
Page: 15/15 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: January2023
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
HVDC Grid Circle :
Bheramara P/S | Bheramara P/S-Faripdpur 132 kV Ckt-2 | 2023-01-17 08:33 | 2023-01-17 15:46 | 7:13 | S/O | Due to A/M work | 0 | 0 | No interruption
Bheramara P/S | Bheramara P/S-Faripdpur 132 kV Ckt-2 | 2023-01-18 09:22 | 2023-01-18 15:37 | 6:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Jhenaidah | Jhenaidah2-Jhenaidah 132 Ckt-3 | 2023-01-19 08:32 | 2023-01-19 15:12 | 6:40 | S/O | Due to A/M work | 0 | 0 | No interruption
Bheramara P/S | Bheramara P/S-Faripdpur 132 kV Ckt-2 | 2023-01-19 08:53 | 2023-01-19 14:22 | 5:29 | S/O | Due to A/M work | 0 | 0 | No interruption
Pabna | Pabna-Shahjadpur 132 kV Ckt-1 | 2023-01-21 08:28 | 2023-01-21 16:38 | 8:10 | S/O | Due to maint. work | 0 | 0 | No interruption
Ishurdi | Ishurdi-Pabna 132 kV Ckt | 2023-01-21 08:31 | 2023-01-21 14:38 | 6:07 | S/O | Due to maint. work | 0 | 0 | No interruption
Bheramara P/S | Bheramara P/S-Faripdpur 132 kV Ckt-1 | 2023-01-27 08:06 | 2023-01-27 16:37 | 8:31 | S/O | Due to maint. work | 0 | 0 | No interruption
Pabna | Pabna-Shahjadpur 132 kV Ckt-1 | 2023-01-27 08:25 | 2023-01-27 15:29 | 7:04 | S/O | Due to A/M work | 0 | 0 | No interruption
Bheramara P/S | Bheramara P/S-Faripdpur 132 kV Ckt-1 | 2023-01-28 08:47 | 2023-01-28 14:57 | 6:10 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 307:23 |  | Unserved Energy: |  | 431.1333
Bogura Grid Circle :
Bogura | Bogura(N)-Naogaon 132 kV Ckt-1 | 2023-01-01 06:43 | 2023-01-01 06:43 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
| Bogura(N)-Naogaon 132 kV Ckt-1 | 2023-01-02 06:44 | 2023-01-02 17:27 | 10:43 | S/O | Due to project work | 0 | 0 | No interruption
| Bogura(N)-Naogaon 132 kV Ckt-1 | 2023-01-03 09:29 | 2023-01-03 18:02 | 8:33 | S/O | Due to project work | 0 | 0 | No interruption
| Bogura(N)-Naogaon 132 kV Ckt-1 | 2023-01-04 06:44 | 2023-01-04 06:44 | 0:00 | S/O | Due to project work | 0 | 0 | No interruption
Lalmonirhat | Lalmonirhat-Rangpur 132 kV Ckt-2 | 2023-01-06 08:30 | 2023-01-06 16:40 | 8:10 | S/O | Due to project work | 12 | 98 | Power interruption
Rajshahi | Rajshahi-BIPTC 230 kV Ckt-1 | 2023-01-06 09:11 | 2023-01-06 17:09 | 7:58 | S/O | Due to A/M work | 0 | 0 | No interruption
| Rajshahi-BIPTC 230 kV Ckt-2 | 2023-01-06 09:12 | 2023-01-06 17:10 | 7:58 | S/O | Due to A/M work | 0 | 0 | No interruption
C.nawabganj | C.nawabganj-Rajshahi 132 kV Ckt-1 | 2023-01-07 07:45 | 2023-01-07 19:02 | 11:17 | S/O | Due to A/M work | 0 | 0 | No interruption
Lalmonirhat | Lalmonirhat-Rangpur 132 kV Ckt-2 | 2023-01-07 08:30 | 2023-01-07 16:24 | 7:54 | S/O | Due to A/M work | 9 | 71.1 | Power interruption
Bogura | Bogura-Bogura(N) 132 kV Ckt-2 | 2023-01-07 11:47 | 2023-01-07 16:20 | 4:33 | S/O | Due to A/M work | 0 | 0 | No interruption
Rajshahi | Rajshahi-BIPTC 230 kV Ckt-1 | 2023-01-08 08:03 | 2023-01-08 17:18 | 9:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogura | Bogura-Bogura(N) 132 kV Ckt-1 | 2023-01-08 09:55 | 2023-01-08 14:18 | 4:23 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogura | Bogura-Bogura(N) 132 kV Ckt-2 | 2023-01-08 08:39 | 2023-01-08 15:31 | 6:52 | S/O | Due to A/M work | 0 | 0 | No interruption
Rajshahi | Rajshahi-BIPTC 230 kV Ckt-02 | 2023-01-11 08:41 | 2023-01-11 14:52 | 6:11 | S/O | Due to A/M work | 0 | 0 | No interruption
Natore | Natore-Rajlanka 132 kV Ckt | 2023-01-14 07:16 | 2023-01-14 07:16 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
C.nawabganj | C.nawabganj-Rajshahi 132 kV Ckt-1 | 2023-01-14 08:37 | 2023-01-14 16:56 | 8:19 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogura | Bogura-Sirajganj 230 kV Ckt-1 | 2023-01-17 09:02 | 2023-01-17 13:48 | 4:46 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogura | Bogura-Mahasthangar(N) 132 kV Ckt-2 | 2023-01-17 09:14 | 2023-01-17 18:23 | 9:09 | S/O | Due to A/M work | 0 | 0 | No interruption
| Bogura-Mahasthangar(N) 132 kV Ckt-1 | 2023-01-18 08:58 | 2023-01-18 16:46 | 7:48 | S/O | Due to relay test | 0 | 0 | No interruption
Purbasadipur | Purbasadipur-Saidpur 132 kV Ckt-1 | 2023-01-18 13:30 | 2023-01-18 17:24 | 3:54 | S/O | Due to relay test | 0 | 0 | No interruption
Natore | Natore-Rajlanka 132 kV Ckt-2 | 2023-01-19 08:52 | 2023-01-19 14:37 | 5:45 | S/O | Due to replacemnet work | 0 | 0 | No interruption
Bogura | Bogura-Sirajganj 230 kV Ckt-2 | 2023-01-22 10:44 | 2023-01-22 13:02 | 2:18 | S/O |  | 0 | 0 | No interruption
| Bogura-Sirajganj 230 kV Ckt-2 | 2023-01-22 09:58 | 2023-01-22 11:07 | 1:09 | S/O | Due to replacemnet work | 0 | 0 | No interruption
| Bogura-Sirajganj 230 kV Ckt-1 | 2023-01-24 11:13 | 2023-01-24 12:15 | 1:02 | S/O |  | 0 | 0 | No interruption
| Bogura-Sirajganj 230 kV Ckt-1 | 2023-01-26 10:01 | 2023-01-26 11:06 | 1:05 | S/O | Due to A/M work | 0 | 0 | No interruption
| Bogura-Sirajganj 230 kV Ckt-1 | 2023-01-28 07:46 | 2023-01-28 19:03 | 11:17 | S/O | Due to replacemnet work | 0 | 0 | No interruption
| Bogura-Sirajganj 230 kV Ckt-1 | 2023-01-30 08:10 | 2023-01-30 18:04 | 9:54 | S/O | Due to project work | 0 | 0 | No interruption
|  |  | Total : | 160:13 |  | Unserved Energy: |  | 169.1
Others :
Maniknagar | Maniknagar-Matuail 132 kV Ckt-1 | 2023-01-06 11:20 | 2023-01-06 15:34 | 4:14 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 4:14 |  | Unserved Energy: |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 3178:33 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month:January 2023
| Area | Previous Month (December' 2022) |  |  |  | Current Month (January '2023)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 13 | 14 | 282 | 309 | 16 | 12 | 353 | 381
2 | Dhaka (South) Grid Circle. | 10 | 15 | 146 | 171 | 21 | 18 | 141 | 180
3 | Chattogram Grid Circle. | 6 | 9 | 101 | 116 | 5 | 6 | 141 | 152
4 | Cumilla Grid Circle. | 14 | 15 | 147 | 176 | 19 | 9 | 246 | 274
5 | Khulna Grid Circle. | 2 | 9 | 139 | 150 | 8 | 15 | 177 | 200
6 | HVDC Grid Circle | 3 | 2 | 95 | 100 | 6 | 20 | 101 | 127
7 | Bogura Grid Circle. | 12 | 20 | 187 | 219 | 5 | 20 | 85 | 110
8 | Others | 1 | 1 | 6 | 8 | 2 | 1 | 6 | 9
| Total | 61 | 85 | 1103 | 1249 | 82 | 101 | 1250 | 1433
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month:January 2023
| Area | Previous Month (December' 2022) |  |  |  | Current Month (January '2023)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 8.33 | 143.93 | 3197.93 | 3350.19 | 1.83 | 22 | 3414.18 | 3438.01
2 | Dhaka (South) Grid Circle. | 681.33 |  | 422.7 | 1104.03 |  | 405 | 659.54 | 1064.54
3 | Chattogram Grid Circle. | 15.2 | 93.18 | 522.7 | 631.08 |  | 37.35 | 805.68 | 843.03
4 | Cumilla Grid Circle. | 25.36 | 40.67 | 150.77 | 216.8 | 257.62 | 78.33 | 2964.13 | 3300.08
5 | Khulna Grid Circle. |  | 12.13 | 774.17 | 786.3 | 77.33 | 774 | 550.82 | 1402.15
6 | HVDC Grid Circle |  |  | 2117.47 | 2117.47 |  | 136.23 | 1136.81 | 1273.04
7 | Bogura Grid Circle. | 79.6 | 781.77 | 896.55 | 1757.92 | 16.5 | 255.3 | 2032.02 | 2303.82
8 | Others | Energy unserved ( MWH ) due to T: 27.45; Energy unserved ( MWH ) due to Total: 27.45; Energy unserved ( MWH ) due to Total: 0
9 | Total | Energy unserved ( MWH ) due to Total: 9991.24; Energy unserved ( MWH ) due to Total: 13624.67
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-29
Page: 1/1 | [9 empty] | QF-LDC-29
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month:January 2023
A) Power Interruption
SL. | Name of | Total Capacity | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of the Sub-Station |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Dhaka (North) | 8801.6 | 2 | 16 | 4 | 1 | 4 | 11 | 2277.71
2 | Dhaka (South) | 5031.6 | 3 | 7 | 10 | - | - | 10 | 962.67
3 | Chattogram | 2042 | 2 | 6 | 8 | 1 | 2 | 5 | 372.63
4 | Khulna | 2434 | 5 | 3 | 8 | 4 |  | 4 | 1035.65
5 | HVDC | 5954.3 | 6 | 4 | 10 |  | 2 | 8 | 841.91
6 | Bogura | 3145.6 | 6 | 14 | 20 | 4 | 1 | 16 | 2129.22
7 | Cumilla | 2981 | 9 | 16 | 25 | 6 | 1 | 18 | 2855.48
8 | Others | - | - | - | - | - | - | - | 0
| Total | 30390.1 | [6 empty] | 10475.27
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 99.95%
2 | Dhaka (South) | 99.74%
3 | Chattogram | 99.98%
4 | Khulna | 99.89%
5 | HVDC | 99.94% | [6 empty] | Executive Engineer
6 | Bogura | 99.82% | [6 empty] | Information Management Division
7 | Cumilla | 99.87% | [6 empty] | LDC, PGCB, Dhaka.

## QF-LDC-30
Page: 1/1 | [10 empty] | QF-LDC-30
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month:January 2023
A) Power Interruption
SL. | Name of | Total length | No. of Section in | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of Transmission line | the Transmission |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | (Ckt-KM) | Line | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 2254.4715 | - |  | 4 | 4 |  | - | 4 | - | 1160.3
2 | Dhaka (South) | 990.29 |  |  | 1 | 1 |  | - | 1 | - | 101.87
3 | Chattogram | 917 | - |  | 4 | 4 |  | - | 4 | - | 470.4
4 | Khulna | 1238.4 | - | 2 | 1 | 3 | 2 |  | 1 |  | 366.5
5 | HVDC | 1325 | - |  | 2 | 2 | - | - | 2 | - | 431.13
6 | Bogura | 1803.3 | - | 1 | 2 | 3 | 1 |  | 2 | - | 174.6
7 | Cumilla | 1648.16 | - |  | 5 | 5 |  |  | 5 | - | 444.6
8 | Others | - |  |  | - | - | - | - | - | - | -
| Total | 10176.6215 | [8 empty] | 3149.4
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 99.96%
2 | Dhaka (South) | 99.88%
3 | Chattogram | 99.94%
4 | Khulna | 99.97%
5 | Bheramara (HVDC) | 99.97% | [7 empty] | Executive Engineer
6 | Bogura | 99.97% | [7 empty] | Information Management Division
7 | Cumilla | 99.83% | [7 empty] | LDC, PGCB, Dhaka.

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month:January 2023
Type of | Power failure due to | [7 empty] | Partial |  | Total Grid failure
fault | Trouble In |  | Trouble In Grid S/S |  | Trouble In |  | Lightning in |  | Grid failure |  |  |  | Remarks
| Generation |  | Equipment |  | Transmission Line |  | Transmission Line/Thunder Storm
Period | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration
| No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min.
2023-01-01 | 10 | - | 11 | 21hr35 min | - | - | - | - | - | - | - | - | -
* Tripping of a generator is accounted in the category "Trouble in Generation ". Not all tripping cause power interruption.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-32
Page: 1/2 |  |  |  |  | QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the Systems
Month:January 2023
| Total Nos.of | Total | Unserved | Total | Remarks
Sub-station | Interruption | Duration of | Load | Unserved
|  | Interruption | (MW) | Energy
|  | Hrs./Mins. |  | (MWH)
| Total Nos.of | Total | Unserved | Total | Remarks
Sub-station | Interruption | Duration of | Load | Unserved
|  | Interruption | (MW) | Energy
|  | Hrs./Mins. |  | (MWH)
Jamalpur | 1 | 2:12 | 10 | 22 | Due red-hot maint.of 132/33 kV transformer T-3 LT & HT
Kishoreganj | 1 | 0:11 | 10 | 1.8333 | Due to tripping of 132/33 kV transformer T1 (404T) LT & T2
Tangail | 1 | 3:53 | 70 | 271.8333 | Due to S/D of Tangail-RPCL 132 kV Ckt-1
Aminbazar | 1 | 3:41 | 8 | 29.4667 | Due to S/D of Aminbazar-Manikganj P/P 132 kV Ckt-2
Manikganj P.S | 1 | 10:05 | 60 | 605 | Due to S/D of Manikganj P.S -Savar 132 kV Ckt-2
Kaliakoir | 1 | 6:21 | 40 | 254 | Due to S/D Kaliakoir-Tongi 230 kV Ckr-2
Kodda | 1 | 6:23 | 28 | 178.7333 | Due to S/D of 132/33 kV transformer Tr-1(406) LT
| 1 | 6:21 | 28 | 177.8 | Due to S/D of 132/33 kV transformer Tr-1(406) HT
|  | 6:20 | 28 | 177.3333 | Due to S/D of 132/33 kV transformer Tr-2(406) HT
| 1 | 4:36 | 30 | 138 | Due to S/D of 132/33 kV transformer Tr-4(436)LT
| 1 | 0:23 | 20 | 7.6667 | Due to S/D of 132/33 kV transformer Tr-5(446)LT
| 1 | 4:36 | 30 | 138 | Due to S/D of 132/33 kV transformer Tr-3(426T) LT
| 1 | 4:33 | 30 | 136.5 | Due to S/D of 132/33 kV transformer Tr-3(426T) HT
| 1 | 0:21 | 20 | 7 | Due to S/D of 132/33 kV transformer Tr-5(426T) HT
| 1 | 4:33 | 30 | 136.5 | Due to S/D of 132/33 kV transformer Tr-4(436) HT
| 1 | 0:18 | 54 | 16.2 | Due to S/D of 132/33 kV transformer Tr-5(446)LT
| 1 | 0:16 | 54 | 14.4 | Due to S/D of132/33 kV transformer Tr-5(446)LT
Dhamrai | 1 | 9:51 | 25 | 246.25 | Due to S/D of 132/33 kV transformer T-1 LT
| 1 | 9:16 | 25 | 231.6667 | Due to S/D of132/33 kV transformer T-1 HT
Tangail | 1 | 4:59 | 130 | 647.8333 | Due to S/D of 132 kV main Bus
Sonargaon |  | 3:35 | 30 | 107.5 | Due to Oil leakage.
| 1 | 3:14 | 30 | 97 | Due to Oil leakage.
Nawabganj | 1 | 5:03 | 30 | 151.5 | Due to Oil leakage.at 33 kV CT
Sonargaon | 1 | 1:38 | 30 | 49 | Due to red hot maintanance.
Keraniganj | 1 | 3:11 | 32 | 101.8667 | Due to S/D of Haripur-Madanganj 132 kV Ckt-1
Munshiganj | 1 | 6:38 | 10 | 66.3333 | Due to S/D of 132/33 kV transformer T-1 LT
Srinagar | 1 | 4:21 | 12 | 52.2 | Due to S/D of 132/33 kV transformer T-01 LT
| 1 | 7:57 | 4 | 31.8 | Due to S/D of 132/33 kV transformer T-02 LT
Sonargaon | 1 | 11:48 | 5 | 59 | Due to S/D of 132/33 kV transformer T-2 HT
| 1 | 11:52 | 5 | 59.3333 | Due to S/D of132/33 kV transformer T-2 LT
|  | 4:49 | 30 | 144.5 | Due to S/D of 132/33 kV transformer T-r2 LT
| 1 | 4:49 | 30 | 144.5 | Due to S/D of 132/33 kV transformer T-r2 HT
Madunaghat | 1 | 1:09 | 21 | 24.15 | Due to 33 kV Breaker fault
Sikalbaha(O) |  | 0:44 | 18 | 13.2 | Due to red-hot maint.at 33 kV bside
Cox'sbazar |  | 8:17 | 20 | 165.6667 | Due to S/D of Cox'sbazar-Dohazari 132 kV Ckt-1
Bakulia | 1 | 7:26 | 14 | 104.0667 | Due to S/D of Bakulia-Khulshi 132 kV Ckt-1
Khulshi | 1 | 3:29 | 10 | 34.8333 | Due to S/D of Khulshi-Halishahar 132 kV Ckt-3
Juldah | 1 | 6:38 | 25 | 165.8333 | Due to S/D of Juldah-Juldah P/S 132 kV Ckt-1
Chandraghona | 1 | 0:46 | 7 | 5.3667 | Due to S/D of 132/33 kV transformer TR-01(406T)LT
| 1 | 1:51 | 7 | 12.95 | Due to S/D of 132/33 kV transformer TR-02(406T)LT
| 1 | 0:45 | 7 | 5.25 | Due to S/D of 132/33 kV transformer TR-01(406T)HT
| 1 | 1:50 | 7 | 12.8333 | Due to S/D of 132/33 kV transformer TR-02(416T) HT
Halishahar | 1 | 5:17 | 40 | 211.3333 | Due to S/D of 132/33 kV transformer T-03 HT
Cox'sbazar | 1 | 5:09 | 17 | 87.55 | Due to S/D of 132/33 kV transformer( 415T) T2 HT
Shahjibazar | 1 | 0:08 | 19 | 2.5333 | Due to 33 kV feeder fault
Chattak | 1 | 0:30 | 6 | 3 | Due to Emergency maint.work
Daudkandi | 1 | 3:55 | 20 | 78.3333 | Due to Emergency maint.work
Kulaura | 1 | 1:11 | 7 | 8.2833 | Due to S/D of 132/33 kV transformer T1 LT
Sreemongal | 1 | 0:10 | 16 | 2.6667 | Due to tripping of 132/33 kV transformer T-3 HT
| 1 | 0:10 | 16 | 2.6667 | Due to tripping of 132/33 kV transformer T-3 LT
| 1 | 0:10 | 16 | 2.6667 | Due to tripping of 132/33 kV transformer T-2 HT
Cumilla(S) | 1 | 0:40 | 31 | 20.6667 | Due to tripping of 132/33 kV transformer TR1-LT
Shahjibazar | 1 | 15:22 | 14 | 215.1333 | Due to tripping of 132/33 kV transformer TR-06 HT & LT
Chowmuhani | 1 | 6:19 | 23 | 145.2833 | Due to S/D of Chowmuhani-Feni 132 kV Ckt-1
| 1 | 5:58 | 16 | 95.4667 | Due to S/D of Chowmuhani-Ramganj 132 kV Ckt-1
| 1 | 3:57 | 22 | 86.9 | Due to S/D of Chowmuhani-HFPL 132 kV Ckt
| 1 | 5:57 | 16 | 95.2 | Due to S/D of Chowmuhani-Ramganj 132 kV Ckt-2
| 1 | 2:25 | 9 | 21.75 | Due to S/D of Chowmuhani-HFPL 132 kV Ckt
Sunamganj | 1 | 7:59 | 18 | 143.7 | Due to S/D of 132 kV Bus-2
Cumilla(S) | 1 | 3:55 | 16 | 62.6667 | Due to S/D of 132/33 kV transformer TR-1 LT
Cumilla(N) | 1 | 6:03 | 20 | 121 | Due to S/D of 230/132 kV transformer T02 HT
Sylhet | 1 | 8:15 | 14 | 115.5 | Due to S/D of 132/33 kV transformer T-2 LT
Fenchuganj | 1 | 0:27 | 18 | 8.1 | Due to S/D of 132/33 kV transformer 422T LT
Shahjibazar | 1 | 6:05 | 13 | 79.0833 | Due to S/D of 132/33 kV transformer T06 LT
Page: 2/2 |  |  |  |  | QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the Systems
Month:January 2023
| Total Nos.of | Total | Unserved | Total | Remarks
Sub-station | Interruption | Duration of | Load | Unserved
|  | Interruption | (MW) | Energy
|  | Hrs./Mins. |  | (MWH)
| Total Nos.of | Total | Unserved | Total | Remarks
Sub-station | Interruption | Duration of | Load | Unserved
|  | Interruption | (MW) | Energy
|  | Hrs./Mins. |  | (MWH)
Chowmuhani | 1 | 6:22 | 30 | 191 | Due to S/D of 132/33 kV transformer TR-1-415TLT
| 1 | 6:28 | 30 | 194 | Due to S/D of 132/33 kV transformer TR-1-415THT
| 1 | 8:57 | 34 | 304.3 | Due to S/D of 132/33 kV transformer TR-2-425T LT
| 1 | 8:57 | 34 | 304.3 | Due to S/D of 132/33 kV transformer TR-2-425THT
| 1 | 2:42 | 22 | 59.4 | Due to S/D of 132/33 kV transformer TR-2-435T LT
| 1 | 2:40 | 22 | 58.6667 | Due to S/D of 132/33 kV transformer TR-2-435T LT
| 1 | 8:47 | 86 | 755.3667 | Due to S/D of 132 kV main Bus
Chandpur | 1 | 6:49 | 5.5 | 37.4917 | Due to S/D of 132/33 kV transformer TR-402 LT
| 1 | 6:48 | 5.5 | 37.4 | Due to S/D of 132/33 kV transformer TR-402 HT
Sylhet | 1 | 5:17 | 9 | 47.55
Barishal | 1 | 6:20 | 58 | 367.3333 | Due to tripping of 132/33 kV transformer Tr 1(405T) HT
| 1 | 0:30 | 58 | 29 | Due to tripping of 132/33 kV transformer Tr 1(405T) LT
| 1 | 6:25 | 58 | 372.1667 | Due to tripping of 132/33 kV transformer Tr 1(405T) LT
Shariatpur | 1 | 0:15 | 23 | 5.75 | Due to tripping of 132/33 kV transformerT1 406T) LT & T2
| 1 | 0:15 | 23 | 5.75 | Due to tripping of 132/33 kV transformerT2 406T) LT
| 1 | 0:22 | 15 | 5.5 | Due to 33 kV Breaker fault
Barishal | 1 | 0:11 | 74 | 13.5667 | Due to tripping of Barishal-Patuakhali(Barguna) 132 kV Ckt
| 1 | 0:28 | 112 | 52.2667 | Due to tripping of Barishal-Madaripur 132 kV Ckt-2
Magura | 1 | 7:31 | 40 | 300.6667 | Due to S/D of Magura-Narail 132 kV Ckt-1
Patuakhali | 1 | 0:26 | 8 | 3.4667 | Due to S/D of 132/33 kV transformer T1 HT & LT
Faridpur | 1 | 6:30 | 19 | 123.5 | Due to S/D of 132/33 kV transformer T1 LT
| 1 | 6:29 | 19 | 123.1833 | Due to S/D of 132/33 kV transformer T1 HT
Benapole | 1 | 1:53 | 16 | 30.1333 | Due to red-hot maint.132/33 kV transformer T01(406) LT
Jashore | 1 | 1:51 | 16 | 29.6 | Due to red-hot maint.of 132/33 kV transformer T01(406) HT
Shahjadpur | 1 | 0:55 | 14 | 12.8333 | Due to red-hot maint.of 132/33 kV transformer T04(435T) LT
Ishurdi | 1 | 1:42 | 15 | 25.5 | Due to Breaker maint. Of 132/33 kV transformer T01 HT
| 1 | 0:41 | 15 | 10.25 | Due to emergency maint.of 132/33 kV transformer T01 HT
| 1 | 1:07 | 25 | 27.9167 | Due to red-hot maint.of 132/33 kV transformer T02 LT
Baghabari | 1 | 7:18 | 6 | 43.8 | Due to S/D of Baghabari-Bhangura 132 kV Ckt-01
Chuadanga | 1 | 6:55 | 56 | 387.3333 | Due to S/D of Chuadanga-Jhenaidah 132 kV Ckt-1
HVDC | 1 | 6:52 | 16 | 109.8667 | Due to S/D of 132/33 kV transformer T3 LT
| 1 | 6:49 | 16 | 109.0667 | Due to S/D of 132/33 kV transformer T3 HT
Pabna | 1 | 6:07 | 35 | 214.0833 | Due to S/D of 132 kV main Bus
Shahjadpur | 1 | 6:49 | 40 | 272.6667
Naogaon | 1 | 0:34 | 10 | 5.6667 | Due to red-hot maint.of 132/33 kV transformer T02 LT
| 1 | 0:32 | 10 | 5.3333 | Due to red-hot maint.of 132/33 kV transformer T02 HT
| 1 | 1:01 | 10 | 10.1667 | Due to red-hot.of 132/33 kV transformer T02 LT
Rajshahi | 1 | 9:46 | 23 | 224.6333 | Due to emergency maint.of 132/33 kV transformer T01 HT
Naogaon | 1 | 0:42 | 15 | 10.5 | Due to red-hot maint.of 132/33 kV transformer T02 LT
| 1 | 0:40 | 15 | 10 | Due to red-hot maint.of 132/33 kV transformer T02 HT
Jaldhaka | 1 | 0:22 | 15 | 5.5 | Due to tripping of Jaldhaka-Saidpur 132 kV Ckt-1
Lalmonirhat | 1 | 8:10 | 12 | 98 | Due to S/D of Lalmonirhat-Rangpur 132 kV Ckt-2
| 1 | 7:54 | 9 | 71.1
Rajshahi | 1 | 1:09 | 8 | 9.2 | Due to S/D of 132/33 kV transformer T1-405 HT
| 1 | 1:36 | 12 | 19.2 | Due to S/D of 132/33 kV transformerT3 (425T) LT
C.nawabganj | 1 | 11:24 | 25 | 285 | Due to S/D of 132/33 kV transformer T1 (405) HT
| 1 | 11:25 | 25 | 285.4167 | Due to S/D of 132/33 kV transformer T1-405 HT
| 1 | 10:14 | 25 | 255.8333 | Due to S/D of 132 kV main Bus
Naogaon | 1 | 5:32 | 33 | 182.6 | Due to S/D of 132/33 kV transformer T1 HT
| 1 | 5:33 | 23 | 127.65 | Due to S/D of 132/33 kV transformer T2 HT
| 1 | 5:38 | 23 | 129.5667 | Due to S/D of 132/33 kV transformer T3 LT
C.nawabganj | 1 | 8:40 | 25 | 216.6667 | Due to S/D of 132/33 kV transformer T2(405) HT
| 1 | 8:40 | 25 | 216.6667 | Due to S/D of 132/33 kV transformer T3 LT
| 1 | 8:39 | 5 | 43.25 | Due to S/D of 132/33 kV transformer T4 HT
Rajshahi | 1 | 2:04 | 17 | 35.1333 | Due to S/D of 132/33 kV transformer T3 425T HT
| 1 | 2:04 | 17 | 35.1333 | Due to S/D of 132/33 kV transformer T3 425T LT
| 1 | 1:49 | 6 | 10.9 | Due to S/D of 132/33 kV transformer T1 405T HT
| 1 | 1:47 | 6 | 10.7 | Due to S/D of 132/33 kV transformer T1 405T LT
|  |  |  | 13624.675 | MWH
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.
0

## QF-LDC-33
Page: 1/3 |  |  | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:January '2023
Sl. No | Sub-station | Date and time | Load (MW)
1 | Aftabnagar 132/33kV Grid Sub-Station | 2023-01-31 18:00 | 24
2 | Agargaon 230/132kV Grid Sub-Station | 2023-01-21 13:00 | 69
3 | Banani 132/33kV Grid Sub-Station | 2023-01-31 13:00 | 28
4 | Bangabhaban 132/33kV Grid Sub-Station | 2023-01-31 12:00 | 12
5 | Bashundhara 132/33kV Grid Sub-Station | 2023-01-30 16:00 | 129
6 | BashundharaCement 132/33kV Sub-Station | 2023-01-04 07:00 | 12
7 | Bhulta 132/33kV Grid Sub-Station | 2023-01-08 12:00 | 219
8 | Cantonment 132/33kV GIS Grid Sub-Station | 2023-01-31 13:00 | 99
9 | Charsaidpur 132/33kV Sub-Station | 2023-01-29 16:00 | 51
10 | Dhaka University 132/33kV Grid Sub-Station | 2023-01-03 13:00 | 26
11 | Dhamrai 132/33kV Grid Sub-Station | 2023-01-12 15:00 | 128
12 | Dhanmondi 132/33kV Grid Sub-Station | 2023-01-26 13:00 | 98
13 | Fatullah 132/33kV Grid Sub-Station | 2023-01-26 12:00 | 55
14 | Ghorashal 132/33kV Sub-Station | 2023-01-29 18:00 | 66
15 | Gulshan 132/33kV Grid Sub-Station | 2023-01-31 13:00 | 76
16 | HaripurSBU 132/33kV Sub-Station | 2023-01-14 13:00 | 152
17 | Hasnabad 132/33kV Grid Substation | 2023-01-07 12:00 | 99
18 | Joydebpur 132/33kV Grid Sub-Station | 2023-01-10 12:00 | 144
19 | Kabirpur 132/33kV Grid Sub-Station | 2023-01-29 10:00 | 236
20 | Kallyanpur 132/33kV Grid Sub-Station | 2023-01-14 04:00 | 90
21 | Kamrangirchar 132/33kV Grid Sub-Station | 2023-01-25 13:00 | 68
22 | Kazla 132/33kV Grid Sub-Station | 2023-01-10 13:00 | 86
23 | Keranigonj 230/132/33kV Grid Sub-Station | 2023-01-11 13:00 | 68
24 | Kodda 132/33kV Grid Sub-Station | 2023-01-25 15:00 | 250
25 | Lalbag 132/33kV Grid Sub-Station | 2023-01-19 18:00 | 76
26 | Madanganj 132/33kV Grid Sub-Station | 2023-01-09 18:00 | 46
27 | Madartek 132/33kV Grid Sub-Station | 2023-01-27 13:00 | 54
28 | Manikganj 132/33kV Grid Sub-Station | 2023-01-08 18:00 | 84
29 | Maniknagar 132/33kV Grid Sub-Station | 2023-01-22 13:00 | 43
30 | Matuail 132/33kV Grid Sub-Station | 2023-01-26 15:00 | 60
31 | Millgate Tongi 132/33kV Grid Sub-Station | 2023-01-18 10:00 | 60
32 | Mirpur 132/33kV Grid Sub-Station | 2023-01-02 11:00 | 91
33 | Mogbazar 132/33kV Grid Sub-Station | 2023-01-30 13:00 | 91
34 | Motijheel 132/33kV Grid Sub-Station | 2023-01-31 13:00 | 24
35 | Munshiganj 132/33kV Grid Sub-Station | 2023-01-19 21:00 | 76
36 | Narinda 132/33kV Grid Sub-Station | 2023-01-24 14:00 | 50
37 | Narshingdi 132/33kV Grid Sub-Station | 2023-01-29 19:00 | 145
38 | Nawabganj 132/33kV Grid Sub-Station | 2023-01-08 20:00 | 33.9
39 | New Tongi 132/33kV Grid Sub-Station | 2023-01-31 12:00 | 62
40 | Postogola 132/33kV Grid Sub-Station | 2023-01-22 13:00 | 34
41 | Purbachal 132/33kV Grid Sub-Station | 2023-01-09 18:30 | 16
42 | Rahim Steel 132/33kV Sub-Station | 2023-01-24 11:00 | 40
43 | Rajendrapur 132/33kV Grid Sub-Station | 2023-01-23 19:30 | 98
44 | Satmasjid 132/33kV Grid Sub-Station | 2023-01-20 13:00 | 80
45 | Savar 132/33kV Grid Sub-Station | 2023-01-11 12:00 | 148
46 | Shitalakhya 132/33kV Grid Sub-Station | 2023-01-26 12:00 | 115
47 | Shyampur 132/33kV Grid Sub-Station | 2023-01-28 12:00 | 170
48 | Siddhirganj 132/33kV Grid Sub-Station | 2023-01-14 12:00 | 102
49 | Sonargaon 132/33kV Grid Sub-Station | 2023-01-17 18:30 | 96
50 | Srinagar 132/33kV Grid Sub-Station | 2023-01-27 11:00 | 37.1
51 | Tongi 230/132/33kV Grid Sub-Station | 2023-01-14 12:00 | 107
52 | Ullon 132/33kV Grid Sub-Station | 2023-01-20 13:00 | 43
53 | Uttara 132/33kV Grid Sub-Station | 2023-01-17 13:00 | 62
Page: 2/3 |  |  | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:January '2023
Sl. No | Sub-station | Date and time | Load (MW)
54 | UttaraNew 132/33kV Grid Sub-Station | 2023-01-23 11:00 | 16
56 | Zigatola 132/33kV Grid Sub-Station | 2023-01-31 13:00 | 60
57 | Agrabad 132/33kV Grid Sub-Station | 2023-01-03 18:30 | 50
58 | AKS 132/33kV Grid Sub-Station | 2023-01-30 11:00 | 10
59 | AKSML 230/33kV Grid Sub-Station | 2023-01-15 09:00 | 117
60 | Bakulia 132/33kV Grid Sub-Station | 2023-01-18 13:00 | 83
61 | Baroaulia 132/33kV Grid Sub-Station | 2023-01-19 12:00 | 69
62 | Baroirhat 132/33kV Grid Sub-Station | 2023-01-16 19:30 | 37
63 | BSRM 230/33kV Grid Sub-Station | 2023-01-01 02:00 | 152
64 | Chandraghona 132/33kV Grid Sub-Station | 2023-01-15 13:00 | 38
65 | Coxsbazar 132/33kV Grid Sub-Station | 2023-01-28 21:00 | 102
66 | Dohazari 132/33kV Grid Sub-Station | 2023-01-21 18:30 | 78
67 | GPH 230/33kV Grid Sub-Station | 2023-01-01 16:00 | 96
68 | Halishahar 132/33kV Grid Sub-Station | 2023-01-30 15:00 | 87
69 | Hathazari 230/132/33kV Grid Sub-Station | 2023-01-09 19:30 | 46
70 | Juldah 132/33kV Grid Sub-Station | 2023-01-15 05:00 | 51
71 | Kalurghat 132/33kV Grid Sub-Station | 2023-01-29 10:00 | 28
72 | Kaptai 132/33kV Sub-Station | 2023-01-03 04:00 | 28
73 | Khagrachori 132/33kV Grid Sub-Station | 2023-01-07 18:00 | 30
74 | Khulshi 132/33kV Grid Sub-Station | 2023-01-29 18:30 | 154
75 | KSRM 132/33kV Grid Sub-Station | 2023-01-19 14:00 | 68
76 | Madunaghat 132/33kV Grid Sub-Station | 2023-01-07 19:30 | 62
77 | Matarbari 132/33kV Sub-Station | 2023-01-29 18:30 | 39
78 | Mirsorai 230/33kV Grid Sub-Station | 2023-01-23 18:30 | 3.5
79 | Modern Steel 132/11kV Grid Sub-Station | 2023-01-01 | 0
80 | Rampur 230/132/33 kV GIS Grid Sub-Station | 2023-01-25 19:00 | 19
81 | Rangamati 132/33kV Grid Sub-Station | 2023-01-01 18:00 | 10
82 | Shahmirpur 132/33kV Grid Sub-Station | 2023-01-21 16:00 | 39.7
83 | Shikalbaha 132/33kV Sub-Station | 2023-01-17 11:00 | 26
84 | Sholosohor 132/33kV Grid Sub-Station | 2023-01-07 10:00 | 27
85 | SSM 132/33kV Grid Sub-Station | 2023-01-25 19:00 | 40
86 | TK chemical 132kV Grid Sub-Station | 2023-01-17 18:30 | 21.5
87 | Ashuganj 230/132/33kV Sub-Station | 2023-01-08 12:00 | 51
88 | Brahmanbaria 132/33kV Grid Sub-Station | 2023-01-29 17:00 | 152
89 | Chandpur 132/33kV Grid Sub-Station | 2023-01-19 20:00 | 47
90 | Chauddagram 132/33kV Grid Sub-Station | 2023-01-07 14:00 | 34
91 | Chowmuhani 132/33kV Grid Sub-Station | 2023-01-08 20:00 | 140
92 | Cumilla(N) 230/132/33kV Grid Sub-Station | 2023-01-24 18:30 | 108
93 | Cumilla(S) 132/33kV Grid Sub-Station | 2023-01-29 14:00 | 138
94 | Daudkandi 132/33kV Grid Sub-Station | 2023-01-02 19:30 | 104
95 | Feni 132/33kV Grid Sub-Station | 2023-01-26 18:30 | 90
96 | Kachua 132/33kV Grid Sub-Station | 2023-01-26 19:00 | 52
97 | PHP 132/33kV Sub-Station | 2023-01-14 14:00 | 11
98 | Ramganj 132/33kV Grid Sub-Station | 2023-01-07 18:00 | 74
99 | Bhaluka 132/33kV Grid Sub-Station | 2023-01-01 21:00 | 196
100 | Jamalpur 132/33kV Grid Sub-Station | 2023-01-30 20:00 | 128
101 | Kishoreganj 132/33kV Grid Sub-Station | 2023-01-21 19:30 | 120
101 | Mymensingh 132/33kV Grid Sub-Station | 2023-01-21 18:00 | 196
102 | Netrakona 132/33kV Grid Sub-Station | 2023-01-20 08:00 | 130
Page: 3/3 |  |  | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:January '2023
Sl. No | Sub-station | Date and time | Load (MW)
103 | Sherpur 132/33kV Grid Sub-Station | 2023-01-21 20:00 | 126
104 | Tangail 132/33kV Grid Sub-Station | 2023-01-18 20:00 | 186
105 | Beanibazar 132/33kV Grid Sub-Station | 2023-01-30 18:30 | 41
106 | Chhatak 132/33kV Grid Sub-Station | 2023-01-07 18:00 | 21
107 | Fenchuganj 230/132/33kV Grid Sub-Station | 2023-01-02 18:00 | 30
108 | Kulaura 132/33kV Grid Sub-Station | 2023-01-14 18:30 | 34
109 | Shahjibazar 132/33kV Grid Sub-Station | 2023-01-17 18:30 | 92
110 | Sreemongol 132/33kV Grid Sub-Station | 2023-01-10 17:00 | 46
111 | Sunamganj 132/33kV Grid Sub-Station | 2023-01-02 19:00 | 38
112 | Sylhet 132/33kV Grid Sub-Station | 2023-01-10 18:00 | 99
113 | Bagerhat 132/33kV Grid Sub-Station | 2023-01-03 18:00 | 83
114 | Benapole 132/33kV Grid Sub-Station | 2023-01-11 12:00 | 52
115 | Bheramara(GK) 132/33kV Grid Sub-Station | 2023-01-10 18:30 | 40
116 | Chuadanga 132/33kV Grid Sub-Station | 2023-01-07 18:00 | 82
117 | Faridpur 132/33kV Grid Sub-Station | 2023-01-17 20:00 | 106
118 | Goalpara 132/33kV Grid Sub-Station | 2023-01-20 13:00 | 26
119 | Gollamari 132/33kV Grid Sub-Station | 2023-01-22 10:00 | 56
120 | Gopalganj 132/33kV Grid Sub-Station | 2023-01-25 18:30 | 78.8
121 | Jashore 132/33kV Grid Sub-Station | 2023-01-21 13:00 | 110
122 | Jhenaidah 132/33kV Grid Sub-Station | 2023-01-11 20:00 | 106
123 | Khulna (C) 132/33kV Grid Sub-Station | 2023-01-02 13:00 | 84
124 | Kushtia 132/33kV Grid Sub-Station | 2023-01-07 18:00 | 106
125 | Madaripur 132/33kV Grid Sub-Station | 2023-01-14 21:00 | 71
126 | Magura 132/33kV Grid Sub-Station | 2023-01-13 21:00 | 54
127 | Mongla 132/33kV Grid Sub-Station | 2023-01-07 09:00 | 32
128 | Narail 132/33kV Grid Sub-Station | 2023-01-10 18:30 | 42
129 | Noapara 132/33kV Grid Sub-Station | 2023-01-07 19:30 | 38
130 | Rajbari 132/33kV Grid Sub-Station | 2023-01-07 18:30 | 52
131 | Satkhira 132/33kV Grid Sub-Station | 2023-01-31 19:00 | 90
132 | Shariatpur 132/33kV Grid Sub-Station | 2023-01-25 21:00 | 50
133 | Barguna 132/33kV Grid Sub-Station | 2023-01-07 18:00 | 14
134 | Barishal 132/33kV Grid Sub-Station | 2023-01-14 13:00 | 90
135 | Barishal 230/132kV Grid Sub-Station | 2023-01-25 18:30 | 62
136 | Bhandaria 132/33kV Grid Sub-Station | 2023-01-15 21:00 | 40
137 | Borhanuddin 230/33kV Grid Sub-Station | 2023-01-09 11:00 | 47
138 | Patuakhali 132/33kV Grid Sub-Station | 2023-01-04 20:00 | 58
139 | Payra 400/132/33kV Grid Sub-Station | 2023-01-08 22:00 | 14
140 | Amnura 132/33kV Grid Sub-Station | 2023-01-26 20:00 | 50
141 | Bhangura 132/33kV Grid Sub-Station | 2023-01-14 21:00 | 39
142 | Bog-Sherpur 132/33kV Grid Sub-Station | 2023-01-25 17:00 | 56
143 | Bogura 132/33kV Grid Sub-Station | 2023-01-29 18:30 | 117
144 | Chapai 132/33kV Grid Sub-Station | 2023-01-26 11:00 | 58
145 | Ishurdi 132/33kV Grid Sub-Station | 2023-01-04 18:00 | 69
146 | Joypurhat 132/33kV Grid Sub-Station | 2023-01-14 09:00 | 45
147 | Mahasthangarh 132/33kV Grid Sub-Station | 2023-01-30 18:30 | 46
148 | Naogaon 132/33kV Grid Sub-Station | 2023-01-25 13:00 | 108
149 | Natore 132/33kV Grid Sub-Station | 2023-01-23 18:30 | 110
150 | Niamatpur 132/33kV Grid Sub-Station | 2023-01-28 18:30 | 92
151 | Pabna 132/33kV Grid Sub-Station | 2023-01-08 18:30 | 82
152 | Rahanpur_I 400/132kV Grid Sub-Station | 2023-01-02 18:00 | 37
153 | Rajshahi 132/33kV Grid Sub-Station | 2023-01-17 20:00 | 104
154 | Rajshahi 230/132/33kV Grid Sub-Station | 2023-01-29 18:30 | 36
155 | Ruppur 132/11kV Grid Sub-Station | 2023-01-09 11:00 | 4
156 | Shahjadpur 132/33kV Grid Sub-Station | 2023-01-04 18:00 | 81
157 | Sirajganj 132/33kV Grid Sub-Station | 2023-01-31 19:30 | 88
158 | Barapukuria 230/132/33kV Grid Sub-Station | 2023-01-29 10:00 | 57
159 | Jaldhaka 132/33kV Grid Sub-Station | 2023-01-31 18:30 | 61
160 | Kurigram 132/33kV Grid Sub-Station | 2023-01-22 19:30 | 78
161 | Lalmonirhat 132/33kV Grid Sub-Station | 2023-01-05 10:00 | 60.5
162 | Mithapukur 132/33kV Grid Sub-Station | 2023-01-31 13:00 | 42
163 | Palashbari 132/33kV Grid Sub-Station | 2023-01-28 18:30 | 110
164 | Panchagarh 132/33kV Grid Sub-Station | 2023-01-05 18:30 | 54
165 | Purbasadipur 132/33kV Grid Sub-Station | 2023-01-30 18:30 | 112
166 | Rangpur 132/33kV Grid Sub-Station | 2023-01-30 18:30 | 128
167 | Saidpur 132/33kV Grid Sub-Station | 2023-01-30 11:00 | 100
168 | Thakurgaon 132/33kV Grid Sub-Station | 2023-01-29 18:30 | 73
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID COMPANY OF BANGLADESH LTD. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month:January 2023
Area | MW | Date | Hour | Remarks
Dhaka | 3644.9 | 30/01/2023 | 19:00
Chattogram | 1099.5 | 24/01/2023 | 18:00
Cumilla | 893 | 26/01/2023 | 19:30
Mymensingh | 922 | 21/01/2023 | 19:30
Sylhet | 376 | 2023-10-01 | 18:30
Khulna | 1214.1 | 2023-10-01 | 18:30
Barishal | 292.24 | 29/01/2023 | 20:00
Rajshahi | 1069.4 | 29/01/2023 | 18:30
Rangpur | 806 | 30/01/2023 | 18:30
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-35
| Page: 1/3 | [5 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: January '2023
SL. | 400 KV Substation | Rated | Maxm |  | Minm | Date and Time
No. |  | Voltage | Voltage | Date and Time | Voltage |  | Remarks
|  | kV | kV |  | kV
1 | Aminbazar 400/230/132kV Grid Sub-Station | 400 | 422 | 2023-01-13 05:00 | 380 | 2023-01-16 20:00
2 | Bhulta 400/230kV Grid Sub-Station | 400 | 404 | 2023-01-19 04:00 | 375 | 2023-01-25 14:00
3 | Bibiana 400/230kV Sub-Station | 400 | 411 | 2023-01-14 13:00 | 391 | 2023-01-04 12:00
4 | BIPTC | 400 | 408 | 2023-01-01 03:00 | 388 | 2023-01-03 10:00
5 | Gopalganj 400/132kV Grid Sub-Station | 400 | 426 | 2023-01-24 18:00 | 392 | 2023-01-30 12:00
| Kaliakoir 400/230/132kV Grid Sub-Station | 400 | 407 | 2023-01-19 04:00 | 370 | 2023-01-25 12:00
|  | Rated | Maxm |  | Minm | Date and Time
SL. | Substation | Voltage | Voltage | Date and Time | Voltage |  | Remarks
No. | 230 KV Substation | kV | kV |  | kV
1 | Agargaon 230/132kV Grid Sub-Station | 230 | 244 | 2023-01-06 06:00 | 225 | 2023-01-16 12:00
2 | AKSML 230/33kV Grid Sub-Station | 230 | 247 | 2023-01-19 18:00 | 200 | 2023-01-28 01:00
3 | Baghabari 230/132kV Grid Sub-Station | 230 | 242 | 2023-01-19 03:00 | 226 | 2023-01-11 12:00
4 | Barapukuria 230/132/33kV Grid Sub-Station | 230 | 233 | 2023-01-02 06:00 | 212 | 2023-01-31 08:00
5 | Barishal 230/132kV Grid Sub-Station | 230 | 249 | 2023-01-03 17:00 | 232 | 2023-01-28 13:00
6 | Bheramara 230/132kV Grid Sub-Station | 230 | 244 | 2023-01-02 | 221 | 2023-01-11 12:00
7 | Bogura 230/132kV Grid Sub-Station | 230 | 237 | 2023-01-01 21:00 | 216 | 2023-01-31 08:00
8 | BSRM 230/33kV Grid Sub-Station | 230 | 245 | 2023-01-19 18:00 | 211 | 2023-01-28 01:00
9 | Cumilla(N) 230/132/33kV Grid Sub-Station | 230 | 243 | 2023-01-19 18:00 | 223 | 2023-01-28 01:00
10 | Fenchuganj 230/132/33kV Grid Sub-Station | 230 | 247 | 2023-01-20 09:00 | 233 | 2023-01-26 10:00
11 | GPH 230/33kV Grid Sub-Station | 230 | 245 | 2023-01-19 18:00 | 205 | 2023-01-28 01:00
12 | Haripur 230/132kV Grid Sub-Station | 230 | 240 | 2023-01-06 18:00 | 223 | 2023-01-30 16:00
13 | Hasnabad 230/132kV Grid Sub-Station | 230 | 244 | 2023-01-07 06:00 | 224 | 2023-01-15 12:00
14 | Hathazari 230/132/33kV Grid Sub-Station | 230 | 245 | 2023-01-15 19:00 | 222 | 2023-01-10 15:00
15 | Ishurdi 230/132kV Grid Sub-Station | 230 | 246 | 2023-01-02 | 225 | 2023-01-11 12:00
16 | Jhenaidah 230/132kV Grid Sub-Station | 230 | 244 | 2023-01-02 | 221 | 2023-01-15 12:00
17 | Keranigonj 230/132/33kV Grid Sub-Station | 230 | 243 | 2023-01-07 05:00 | 223 | 2023-01-30 16:00
18 | Khulna(S) 230/132kV Grid Sub-Station | 230 | 247 | 2023-01-14 02:00 | 223 | 2023-01-15 12:00
19 | Maniknagar 230/132kV Grid Sub-Station | 230 | 242 | 2023-01-07 06:00 | 224 | 2023-01-30 16:00
20 | Meghnaghat 230/132kV Grid Sub-Station | 230 | 246 | 2023-01-06 19:00 | 232 | 2023-01-11 11:00
21 | Mirsorai 230/33kV Grid Sub-Station | 230 | 248 | 2023-01-28 19:30 | 220 | 2023-01-11 12:00
22 | Rajshahi 230/132/33kV Grid Sub-Station | 230 | 251 | 2023-01-16 20:00 | 223 | 2023-01-31 07:00
23 | Rampura 230/132kV Grid Sub-Station | 230 | 241 | 2023-01-20 09:00 | 225 | 2023-01-30 16:00
24 | Shikalbaha 230/132kV Grid Sub-Station | 230 | 245 | 2023-01-19 19:30 | 218 | 2023-01-28 02:00
25 | Shyampur 230/132kV Grid Sub-Station | 230 | 242 | 2023-01-07 05:00 | 223 | 2023-01-30 15:00
26 | Siddhirganj 230/132kV Grid Sub-Station | 230 | 243 | 2023-01-06 18:30 | 228 | 2023-01-25 12:00
27 | Sirajgonj 230 kV Switching Station | 230 | 241 | 2023-01-18 09:00 | 224 | 2023-01-31 08:00
28 | Tongi 230/132/33kV Grid Sub-Station | 230 | 243 | 2023-01-17 19:30 | 218 | 2023-01-31 15:00
QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: January '2023
|  | Rated | Maxm |  | Minm | Date and Time
SL. | Substation | Voltage | Voltage | Date and Time | Voltage |  | Remarks
No. | 132 KV Substation | kV | kV |  | kV
11 | Aftabnagar 132/33kV Grid Sub-Station | 132 | 141 | 2023-01-19 04:00 | 129 | 2023-01-30 16:00
12 | Agrabad 132/33kV Grid Sub-Station | 132 | 142 | 2023-01-19 18:00 | 126 | 2023-01-10 14:00
13 | AKS 132/33kV Grid Sub-Station | 132 | 142 | 2023-01-06 09:00 | 118 | 2023-01-28 01:00
14 | Amnura 132/33kV Grid Sub-Station | 132 | 140 | 2023-01-09 18:00 | 121 | 2023-01-11 13:00
15 | Ashuganj 230/132/33kV Sub-Station | 132 | 141 | 2023-01-09 06:00 | 130 | 2023-01-31 12:00
16 | Bagerhat 132/33kV Grid Sub-Station | 132 | 140 | 2023-01-14 03:00 | 124 | 2023-01-22 08:00
17 | Bakulia 132/33kV Grid Sub-Station | 132 | 143 | 2023-01-16 18:00 | 118 | 2023-01-28 01:00
18 | Banani 132/33kV Grid Sub-Station | 132 | 142 | 2023-01-02 | 124 | 2023-01-29 12:00
19 | Bangabhaban 132/33kV Grid Sub-Station | 132 | 141 | 2023-01-19 05:00 | 128 | 2023-01-28 12:00
20 | Barguna 132/33kV Grid Sub-Station | 132 | 142 | 2023-01-16 09:00 | 125 | 2023-01-27 12:00
21 | Barishal 132/33kV Grid Sub-Station | 132 | 141 | 2023-01-02 05:00 | 127 | 2023-01-04 13:00
22 | Baroaulia 132/33kV Grid Sub-Station | 132 | 144 | 2023-01-19 22:00 | 125 | 2023-01-09 13:00
23 | Baroirhat 132/33kV Grid Sub-Station | 132 | 143 | 2023-01-16 22:00 | 121 | 2023-01-28 01:00
24 | Bashundhara 132/33kV Grid Sub-Station | 132 | 141 | 2023-01-02 | 124 | 2023-01-29 12:00
25 | BashundharaCement 132/33kV Sub-Station | 132 | 143 | 2023-01-06 18:00 | 128 | 2023-01-12 12:00
26 | Beanibazar 132/33kV Grid Sub-Station | 132 | 140 | 2023-01-20 03:00 | 126 | 2023-01-21 07:00
27 | Benapole 132/33kV Grid Sub-Station | 132 | 140 | 2023-01-14 03:00 | 122 | 2023-01-15 12:00
28 | Bhaluka 132/33kV Grid Sub-Station | 132 | 133 | 2023-01-01 05:00 | 113 | 2023-01-10 07:00
29 | Bhandaria 132/33kV Grid Sub-Station | 132 | 142 | 2023-01-02 05:00 | 130 | 2023-01-09 17:00
30 | Bhangura 132/33kV Grid Sub-Station | 132 | 146 | 2023-01-02 11:00 | 121 | 2023-01-28 21:00
31 | Bheramara(GK) 132/33kV Grid Sub-Station | 132 | 141 | 2023-01-01 04:00 | 129 | 2023-01-26 12:00
32 | Bhulta 132/33kV Grid Sub-Station | 132 | 135 | 2023-01-06 14:00 | 123 | 2023-01-25 14:00
33 | Bog-Sherpur 132/33kV Grid Sub-Station | 132 | 141 | 2023-01-01 13:00 | 124 | 2023-01-31 08:00
34 | Bogura 132/33kV Grid Sub-Station | 132 | 141 | 2023-01-16 21:00 | 123 | 2023-01-31 08:00
35 | Brahmanbaria 132/33kV Grid Sub-Station | 132 | 137 | 2023-01-06 04:00 | 126 | 2023-01-31 12:00
36 | Cantonment 132/33kV GIS Grid Sub-Station | 132 | 142 | 2023-01-06 06:00 | 129 | 2023-01-16 12:00
37 | Chandpur 132/33kV Grid Sub-Station | 132 | 143 | 2023-01-02 17:00 | 121 | 2023-01-28 01:00
38 | Chandraghona 132/33kV Grid Sub-Station | 132 | 144 | 2023-01-19 18:00 | 127 | 2023-01-28 02:00
39 | Chapai 132/33kV Grid Sub-Station | 132 | 140 | 2023-01-24 18:00 | 120 | 2023-01-11 13:00
40 | Charsaidpur 132/33kV Sub-Station | 132 | 144 | 2023-01-09 19:30 | 129 | 2023-01-12 12:00
41 | Chauddagram 132/33kV Grid Sub-Station | 132 | 143 | 2023-01-01 18:30 | 127 | 2023-01-10 13:00
42 | Chhatak 132/33kV Grid Sub-Station | 132 | 138 | 2023-01-20 02:00 | 128 | 2023-01-25 12:00
43 | Chowmuhani 132/33kV Grid Sub-Station | 132 | 143 | 2023-01-01 17:00 | 120 | 2023-01-28 01:00
44 | Chuadanga 132/33kV Grid Sub-Station | 132 | 140 | 2023-01-02 | 121 | 2023-01-15 12:00
45 | Coxsbazar 132/33kV Grid Sub-Station | 132 | 138 | 2023-01-20 17:00 | 114 | 2023-01-03 18:30
46 | Cumilla(S) 132/33kV Grid Sub-Station | 132 | 144 | 2023-01-17 22:00 | 123 | 2023-01-05 12:00
47 | Daudkandi 132/33kV Grid Sub-Station | 132 | 144 | 2023-01-09 20:00 | 128 | 2023-01-04 16:00
48 | Dhaka University 132/33kV Grid Sub-Station | 132 | 141 | 2023-01-20 01:00 | 130 | 2023-01-16 12:00
49 | Dhamrai 132/33kV Grid Sub-Station | 132 | 141 | 2023-01-06 06:00 | 128 | 2023-01-29 11:00
50 | Dhanmondi 132/33kV Grid Sub-Station | 132 | 142 | 2023-01-06 18:30 | 131.5 | 2023-01-25 14:00
51 | Dohazari 132/33kV Grid Sub-Station | 132 | 141 | 2023-01-18 13:00 | 126 | 2023-01-11 12:00
52 | Faridpur 132/33kV Grid Sub-Station | 132 | 139 | 2023-01-06 06:00 | 121 | 2023-01-26 12:00
53 | Fatullah 132/33kV Grid Sub-Station | 132 | 141 | 2023-01-06 18:30 | 126 | 2023-01-11 19:30
54 | Feni 132/33kV Grid Sub-Station | 132 | 145 | 2023-01-15 22:00 | 123 | 2023-01-28 01:00
55 | Ghorashal 132/33kV Sub-Station | 132 | 145 | 2023-01-06 03:00 | 133 | 2023-01-14 14:00
56 | Goalpara 132/33kV Grid Sub-Station | 132 | 142 | 2023-01-14 02:00 | 128 | 2023-01-15 12:00
57 | Gollamari 132/33kV Grid Sub-Station | 132 | 141 | 2023-01-15 19:00 | 128 | 2023-01-10 15:00
58 | Gopalganj 132/33kV Grid Sub-Station | 132 | 143 | 2023-01-30 19:00 | 127 | 2023-01-11 12:00
59 | Gulshan 132/33kV Grid Sub-Station | 132 | 140 | 2023-01-07 07:00 | 129 | 2023-01-25 14:00
60 | Halishahar 132/33kV Grid Sub-Station | 132 | 142 | 2023-01-20 13:00 | 127 | 2023-01-10 13:00
61 | HaripurSBU 132/33kV Sub-Station | 132 | 147 | 2023-01-30 21:00 | 129 | 2023-01-01 03:00
62 | Hasnabad 132/33kV Grid Substation | 132 | 139 | 2023-01-06 17:00 | 129 | 2023-01-16 12:00
63 | Ishurdi 132/33kV Grid Sub-Station | 132 | 143 | 2023-01-02 | 130 | 2023-01-29 11:00
64 | Jaldhaka 132/33kV Grid Sub-Station | 132 | 144 | 2023-01-31 08:00 | 114 | 2023-01-31 07:00
65 | Jamalpur 132/33kV Grid Sub-Station | 132 | 140 | 2023-01-09 09:00 | 113 | 2023-01-20 08:00
66 | Jashore 132/33kV Grid Sub-Station | 132 | 140 | 2023-01-15 22:00 | 122 | 2023-01-16 13:00
67 | Jhenaidah 132/33kV Grid Sub-Station | 132 | 142 | 2023-01-02 | 127 | 2023-01-15 12:00
68 | Joydebpur 132/33kV Grid Sub-Station | 132 | 144 | 2023-01-01 21:00 | 130 | 2023-01-30 16:00
69 | Joypurhat 132/33kV Grid Sub-Station | 132 | 138 | 2023-01-02 | 115 | 2023-01-31 08:00
70 | Juldah 132/33kV Grid Sub-Station | 132 | 142 | 2023-01-20 13:00 | 117 | 2023-01-28 01:00
71 | Kabirpur 132/33kV Grid Sub-Station | 132 | 138 | 2023-01-09 09:00 | 119 | 2023-01-25 12:00
| Page: 3/3 | [5 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: January '2023
Rated
SL. | Substation | Rated | Maxm |  | Minm | Date and Time
No. | 132 KV Substation | Voltage | Voltage | Date and Time | Voltage |  | Remarks
|  | kV | kV |  | kV
72 | Kachua 132/33kV Grid Sub-Station | 132 | 143 | 2023-01-16 22:00 | 127 | 2023-01-28 01:00
73 | Kallyanpur 132/33kV Grid Sub-Station | 132 | 142 | 2023-01-19 18:00 | 128 | 2023-01-11 12:00
74 | Kalurghat 132/33kV Grid Sub-Station | 132 | 143 | 2023-01-18 18:00 | 118 | 2023-01-28 01:00
75 | Kamrangirchar 132/33kV Grid Sub-Station | 132 | 138 | 2023-01-07 06:00 | 125 | 2023-01-16 12:00
76 | Kaptai 132/33kV Sub-Station | 132 | 142 | 2023-01-01 17:00 | 126 | 2023-01-13 02:00
77 | Kazla 132/33kV Grid Sub-Station | 132 | 141 | 2023-01-19 05:00 | 128 | 2023-01-28 14:00
78 | Khagrachori 132/33kV Grid Sub-Station | 132 | 142 | 2023-01-07 07:00 | 126 | 2023-01-28 02:00
79 | Khulna (C) 132/33kV Grid Sub-Station | 132 | 141 | 2023-01-15 22:00 | 127 | 2023-01-15 12:00
80 | Khulshi 132/33kV Grid Sub-Station | 132 | 140 | 2023-01-06 17:00 | 126 | 2023-01-28 01:00
81 | Kishoreganj 132/33kV Grid Sub-Station | 132 | 136 | 2023-01-01 06:00 | 118 | 2023-01-31 12:00
82 | Kodda 132/33kV Grid Sub-Station | 132 | 144 | 2023-01-09 09:00 | 119 | 2023-01-25 12:00
83 | KSRM 132/33kV Grid Sub-Station | 132 | 142 | 2023-01-14 18:00 | 118 | 2023-01-28 01:00
84 | Kulaura 132/33kV Grid Sub-Station | 132 | 140 | 2023-01-20 | 132 | 2023-01-30 16:00
85 | Kurigram 132/33kV Grid Sub-Station | 132 | 135 | 2023-01-12 15:00 | 114 | 2023-01-30 07:00
86 | Kushtia 132/33kV Grid Sub-Station | 132 | 142 | 2023-01-02 | 128 | 2023-01-11 12:00
87 | Lalbag 132/33kV Grid Sub-Station | 132 | 139 | 2023-01-07 05:00 | 125 | 2023-01-01 06:00
88 | Lalmonirhat 132/33kV Grid Sub-Station | 132 | 135 | 2023-01-02 06:00 | 115 | 2023-01-31 08:00
89 | Madanganj 132/33kV Grid Sub-Station | 132 | 143 | 2023-01-06 18:00 | 128 | 2023-01-12 12:00
90 | Madaripur 132/33kV Grid Sub-Station | 132 | 139 | 2023-01-01 04:00 | 128 | 2023-01-15 12:00
91 | Madartek 132/33kV Grid Sub-Station | 132 | 141 | 2023-01-20 04:00 | 129 | 2023-01-25 14:00
92 | Madunaghat 132/33kV Grid Sub-Station | 132 | 143 | 2023-01-15 18:00 | 119 | 2023-01-28 01:00
93 | Magura 132/33kV Grid Sub-Station | 132 | 141 | 2023-01-02 | 125 | 2023-01-15 12:00
94 | Mahasthangarh 132/33kV Grid Sub-Station | 132 | 139 | 2023-01-02 | 122 | 2023-01-31 08:00
95 | Manikganj 132/33kV Grid Sub-Station | 132 | 137 | 2023-01-02 | 120 | 2023-01-29 12:00
96 | Maniknagar 132/33kV Grid Sub-Station | 132 | 140 | 2023-01-08 07:00 | 129 | 2023-01-26 12:00
97 | Matarbari 132/33kV Sub-Station | 132 | 141 | 2023-01-18 20:00 | 113 | 2023-01-03 19:30
98 | Matuail 132/33kV Grid Sub-Station | 132 | 141 | 2023-01-06 21:00 | 130 | 2023-01-21 12:00
99 | Millgate Tongi 132/33kV Grid Sub-Station | 132 | 140 | 2023-01-01 01:00 | 125 | 2023-01-25 14:00
100 | Mirpur 132/33kV Grid Sub-Station | 132 | 141 | 2023-01-07 07:00 | 126 | 2023-01-05 08:00
101 | Mithapukur 132/33kV Grid Sub-Station | 132 | 138 | 2023-01-05 17:00 | 119 | 2023-01-31 07:00
102 | Modern Steel 132/11kV Grid Sub-Station | 132 | 142 | 2023-01-14 17:00 | 118 | 2023-01-28 01:00
103 | Mogbazar 132/33kV Grid Sub-Station | 132 | 143 | 2023-01-13 07:00 | 127 | 2023-01-10 10:00
104 | Mongla 132/33kV Grid Sub-Station | 132 | 140 | 2023-01-09 09:00 | 124 | 2023-01-22 08:00
105 | Motijheel 132/33kV Grid Sub-Station | 132 | 141 | 2023-01-19 05:00 | 128 | 2023-01-28 12:00
106 | Munshiganj 132/33kV Grid Sub-Station | 132 | 143 | 2023-01-06 18:00 | 127 | 2023-01-04 12:00
107 | Mymensingh 132/33kV Grid Sub-Station | 132 | 138 | 2023-01-09 09:00 | 113 | 2023-01-10 19:00
108 | Naogaon 132/33kV Grid Sub-Station | 132 | 139 | 2023-01-06 06:00 | 116 | 2023-01-31 08:00
109 | Narail 132/33kV Grid Sub-Station | 132 | 140 | 2023-01-02 | 124 | 2023-01-15 12:00
110 | Narshingdi 132/33kV Grid Sub-Station | 132 | 140 | 2023-01-07 03:00 | 113 | 2023-01-20 05:00
111 | Natore 132/33kV Grid Sub-Station | 132 | 138 | 2023-01-02 | 125 | 2023-01-31 08:00
112 | Nawabganj 132/33kV Grid Sub-Station | 132 | 138 | 2023-01-06 06:00 | 125 | 2023-01-16 12:00
113 | Netrakona 132/33kV Grid Sub-Station | 132 | 132 | 2023-01-02 04:00 | 113 | 2023-01-04 18:30
114 | New Tongi 132/33kV Grid Sub-Station | 132 | 141 | 2023-01-01 | 124 | 2023-01-25 13:00
115 | Niamatpur 132/33kV Grid Sub-Station | 132 | 137 | 2023-01-06 06:00 | 113 | 2023-01-31 09:00
116 | Noapara 132/33kV Grid Sub-Station | 132 | 142 | 2023-01-15 22:00 | 124 | 2023-01-20 13:00
117 | Pabna 132/33kV Grid Sub-Station | 132 | 142 | 2023-01-01 | 129 | 2023-01-26 10:00
118 | Palashbari 132/33kV Grid Sub-Station | 132 | 137 | 2023-01-05 22:00 | 116 | 2023-01-31 07:00
119 | Panchagarh 132/33kV Grid Sub-Station | 132 | 140 | 2023-01-16 09:00 | 113 | 2023-01-31 07:00
120 | Patuakhali 132/33kV Grid Sub-Station | 132 | 142 | 2023-01-16 10:00 | 124 | 2023-01-27 11:00
121 | PHP 132/33kV Sub-Station | 132 | 143 | 2023-01-17 23:00 | 128 | 2023-01-10 15:00
122 | Postogola 132/33kV Grid Sub-Station | 132 | 140 | 2023-01-07 07:00 | 127 | 2023-01-16 12:00
123 | Purbachal 132/33kV Grid Sub-Station | 132 | 142 | 2023-01-01 06:00 | 126 | 2023-01-25 14:00
124 | Purbasadipur 132/33kV Grid Sub-Station | 132 | 138 | 2023-01-05 22:00 | 113 | 2023-01-31 07:00
125 | Rahim Steel 132/33kV Sub-Station | 132 | 141 | 2023-01-06 17:00 | 124 | 2023-01-28 16:00
126 | Rajbari 132/33kV Grid Sub-Station | 132 | 139 | 2023-01-02 | 121 | 2023-01-26 13:00
127 | Rajendrapur 132/33kV Grid Sub-Station | 132 | 143 | 2023-01-09 18:00 | 116 | 2023-01-25 15:00
128 | Rajshahi 132/33kV Grid Sub-Station | 132 | 138 | 2023-01-24 18:00 | 124 | 2023-01-08 12:00
129 | Ramganj 132/33kV Grid Sub-Station | 132 | 142 | 2023-01-15 18:00 | 127 | 2023-01-11 12:00
130 | Rangamati 132/33kV Grid Sub-Station | 132 | 142 | 2023-01-15 18:00 | 127 | 2023-01-10 12:00
131 | Rangpur 132/33kV Grid Sub-Station | 132 | 137 | 2023-01-05 17:00 | 120 | 2023-01-31 07:00
132 | Ruppur 132/11kV Grid Sub-Station | 132 | 142 | 2023-01-05 17:00 | 130 | 2023-01-15 12:00
133 | Saidpur 132/33kV Grid Sub-Station | 132 | 136 | 2023-01-05 17:00 | 114 | 2023-01-31 07:00
134 | Satkhira 132/33kV Grid Sub-Station | 132 | 141 | 2023-01-14 03:00 | 125 | 2023-01-22 08:00
135 | Satmasjid 132/33kV Grid Sub-Station | 132 | 142 | 2023-01-06 06:00 | 130 | 2023-01-30 16:00
136 | Savar 132/33kV Grid Sub-Station | 132 | 142 | 2023-01-09 18:00 | 124 | 2023-01-11 12:00
137 | Shahjadpur 132/33kV Grid Sub-Station | 132 | 147 | 2023-01-01 | 135 | 2023-01-22 12:00
138 | Shahjibazar 132/33kV Grid Sub-Station | 132 | 138 | 2023-01-01 | 129 | 2023-01-28 12:00
139 | Shariatpur 132/33kV Grid Sub-Station | 132 | 139 | 2023-01-02 | 128 | 2023-01-15 12:00
140 | Sherpur 132/33kV Grid Sub-Station | 132 | 139 | 2023-01-09 09:00 | 113 | 2023-01-12 08:00
141 | Shikalbaha 132/33kV Sub-Station | 132 | 143 | 2023-01-16 15:00 | 127 | 2023-01-19 10:00
142 | Shitalakhya 132/33kV Grid Sub-Station | 132 | 139 | 2023-01-07 07:00 | 125 | 2023-01-16 12:00
143 | Sholosohor 132/33kV Grid Sub-Station | 132 | 142 | 2023-01-19 18:00 | 118 | 2023-01-28 01:00
144 | Shyampur 132/33kV Grid Sub-Station | 132 | 138 | 2023-01-01 20:00 | 128 | 2023-01-16 12:00
145 | Siddhirganj 132/33kV Grid Sub-Station | 132 | 141 | 2023-01-06 18:30 | 131 | 2023-01-25 14:00
146 | Sirajganj 132/33kV Grid Sub-Station | 132 | 144 | 2023-01-02 | 126 | 2023-01-31 07:00
147 | Sonargaon 132/33kV Grid Sub-Station | 132 | 141 | 2023-01-09 20:00 | 129 | 2023-01-05 11:00
148 | Sreemongol 132/33kV Grid Sub-Station | 132 | 140 | 2023-01-01 | 128 | 2023-01-28 11:00
149 | Srinagar 132/33kV Grid Sub-Station | 132 | 138 | 2023-01-07 07:00 | 125 | 2023-01-15 12:00
150 | SSM 132/33kV Grid Sub-Station | 132 | 146 | 2023-01-18 14:00 | 129 | 2023-01-10 13:00
151 | Sunamganj 132/33kV Grid Sub-Station | 132 | 137 | 2023-01-20 03:00 | 127 | 2023-01-25 14:00
152 | Sylhet 132/33kV Grid Sub-Station | 132 | 139 | 2023-01-20 02:00 | 129 | 2023-01-25 14:00
153 | Tangail 132/33kV Grid Sub-Station | 132 | 136 | 2023-01-02 | 117 | 2023-01-25 12:00
154 | Thakurgaon 132/33kV Grid Sub-Station | 132 | 141 | 2023-01-05 17:00 | 117 | 2023-01-05 09:00
155 | TK chemical 132kV Grid Sub-Station | 132 | 142 | 2023-01-09 20:00 | 129 | 2023-01-11 12:00
156 | Ullon 132/33kV Grid Sub-Station | 132 | 140 | 2023-01-13 05:00 | 129 | 2023-01-25 14:00
157 | Uttara 132/33kV Grid Sub-Station | 132 | 140 | 2023-01-02 | 126 | 2023-01-25 12:00
158 | UttaraNew 132/33kV Grid Sub-Station | 132 | 140 | 2023-01-01 17:00 | 127 | 2023-01-11 12:00
159 | Zigatola 132/33kV Grid Sub-Station | 132 | 138 | 2023-01-06 07:00 | 125 | 2023-01-16 12:00

## QF-LDC-36
Page: 1/2
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
Month: January 2023
Substation | transformer | mw | mva | date_time
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-1 ( 705T1) | 195 | 198.6681 | 2023-01-08 13:00
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-2 ( 715T2) | 203 | 209.5543 | 2023-01-03 14:00
Aminbazar 400/230/132kV Grid Sub-Station | 230/132kv Tr-01 | 173 | 176.1193 | 2023-01-11 12:00
Aminbazar 400/230/132kV Grid Sub-Station | 230/132kv Tr-02 | 168 | 170.8362 | 2023-01-29 09:00
Aminbazar 400/230/132kV Grid Sub-Station | 230/132kv Tr-03 | 179 | 182.0165 | 2023-01-11 12:00
Baghabari 230/132kV Grid Sub-Station | T-1 | 238 | 241.3379 | 2023-01-10 20:00
Baghabari 230/132kV Grid Sub-Station | T-2 Bank | 60 | 208.8061 | 2023-01-11 22:00
Barishal 230/132kV Grid Sub-Station | ATR-1 | 194 | 194.1649 | 2023-01-22 09:00
Barishal 230/132kV Grid Sub-Station | ATR-2 | 194 | 194.1649 | 2023-01-22 09:00
Bheramara 230/132kV Grid Sub-Station | Transformer-1 | 135 | 155.4156 | 2023-01-19 07:00
Bheramara 230/132kV Grid Sub-Station | Transformer-2 | -101 | 101.005 | 2023-01-26 13:00
Bogura 230/132kV Grid Sub-Station | T-01 | 91 | 122.4949 | 2023-01-31 01:00
Bogura 230/132kV Grid Sub-Station | T-02 | 91 | 122.4949 | 2023-01-31 01:00
Bogura 230/132kV Grid Sub-Station | T-03 | 153 | 166.2348 | 2023-01-31 08:00
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV T-01 | 187 | 188.2897 | 2023-01-06 13:00
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV T-02 | 169 | 202.7437 | 2023-01-04 15:00
Fenchuganj 230/132/33kV Grid Sub-Station | AT-02 | 162 | 166.6283 | 2023-01-10 13:00
Haripur 230/132kV Grid Sub-Station | Auto TR-1 | 92 | 115 | 2023-01-28 08:00
Haripur 230/132kV Grid Sub-Station | Auto TR-2 | 92 | 115 | 2023-01-28 08:00
Haripur 230/132kV Grid Sub-Station | Auto TR-3 | 92 | 115 | 2023-01-28 08:00
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-1 | 65 | 67.1863 | 2023-01-07 12:00
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-2 | 65 | 67.1863 | 2023-01-07 12:00
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-3 | 65 | 67.1863 | 2023-01-07 12:00
Hathazari 230/132/33kV Grid Sub-Station | MT-01 | 88 | 92.6553 | 2023-01-21 17:00
Hathazari 230/132/33kV Grid Sub-Station | MT-02 | 88 | 92.6553 | 2023-01-21 17:00
Hathazari 230/132/33kV Grid Sub-Station | MT-03 | 88 | 92.6553 | 2023-01-21 17:00
Hathazari 230/132/33kV Grid Sub-Station | MT-04 | 88 | 92.6553 | 2023-01-21 17:00
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-01 | 97 | 102.4597 | 2023-01-28 19:00
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-02 | 104 | 111.072 | 2023-01-04 18:30
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-03 | 58 | 230.4192 | 2023-01-20 04:00
Jhenaidah 230/132kV Grid Sub-Station | Transformer- 1 | -231 | 232.5726 | 2023-01-19 20:00
Jhenaidah 230/132kV Grid Sub-Station | Transformer- 2 | -225 | 226.6142 | 2023-01-19 21:00
Keranigonj 230/132/33kV Grid Sub-Station | ATR-1 | 120 | 123.2234 | 2023-01-11 13:00
Keranigonj 230/132/33kV Grid Sub-Station | ATR-2 | 39 | 55.1543 | 2023-01-01 06:00
Keranigonj 230/132/33kV Grid Sub-Station | ATR-3 | 202 | 205.5432 | 2023-01-01 19:00
Khulna(S) 230/132kV Grid Sub-Station | TR-1 | -144 | 144.7791 | 2023-01-25 20:00
Khulna(S) 230/132kV Grid Sub-Station | TR-2 | -205 | 205.1975 | 2023-01-28 18:00
Khulna(S) 230/132kV Grid Sub-Station | TR-3 | -265 | 265.4242 | 2023-01-28 18:00
Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-01(705T) | 15 | 237.4742 | 2023-01-12 05:00
Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-02 (715T) | 180 | 190.7066 | 2023-01-28 12:00
Rajshahi 230/132/33kV Grid Sub-Station | ATR-01 (704T) | -99 | 100.8067 | 2023-01-27 09:00
Rajshahi 230/132/33kV Grid Sub-Station | ATR-02 (714T) | -73 | 103.9471 | 2023-01-23 01:00
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-01 (706T) | 1 | 1.4142 | 2023-01-01 10:00
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-02 (716T) | 1 | 1 | 2023-01-01 18:30
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 01 | 198 | 199.3314 | 2023-01-08 14:00
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 02 | 198 | 199.3314 | 2023-01-08 14:00
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 03 | 165 | 165.9789 | 2023-01-08 18:30
Shikalbaha 230/132kV Grid Sub-Station | ATR 01 | 209 | 220.7306 | 2023-01-21 17:00
Shikalbaha 230/132kV Grid Sub-Station | ATR 02 | 209 | 220.7306 | 2023-01-21 17:00
Shyampur 230/132kV Grid Sub-Station | Auto TR-1 | 62 | 242.0744 | 2023-01-10 05:00
Shyampur 230/132kV Grid Sub-Station | Auto TR-2 | 104 | 111.4271 | 2023-01-12 12:00
Siddhirganj 230/132kV Grid Sub-Station | MTR 1 | 243 | 244.8448 | 2023-01-18 03:00
Siddhirganj 230/132kV Grid Sub-Station | MTR 2 | 75 | 184.8946 | 2023-01-15 23:00
Tongi 230/132/33kV Grid Sub-Station | T-01 | 205 | 205.9733 | 2023-01-10 12:00
Tongi 230/132/33kV Grid Sub-Station | T-02 | 205 | 205.9733 | 2023-01-10 11:00
Tongi 230/132/33kV Grid Sub-Station | T-03 | 205 | 205.9733 | 2023-01-10 11:00
Information Management Division, LDC, Dhaka
Maximum load of 400/230 & 400/132 kV Transformer
Month: January 2023
Substation | transformer | mw | mva | date_time
Aminbazar 400/230/132kV Grid Sub-Station | ATR-02 | 376 | 385.9339 | 2023-01-04 01:00
Aminbazar 400/230/132kV Grid Sub-Station | ATR-03 | 428 | 444.5042 | 2023-01-20 16:00
Bhulta 400/230kV Grid Sub-Station | ATR-01 | -383 | 389.7089 | 2023-01-29 10:00
Bhulta 400/230kV Grid Sub-Station | ATR-02 | -30600 | 30600.1181 | 2023-01-31 01:00
Bibiana 400/230kV Sub-Station | ICT-01 | -276 | 276.306 | 2023-01-24 10:00
Bibiana 400/230kV Sub-Station | ICT-02 | -266 | 266.0677 | 2023-01-24 10:00
Kaliakoir 400/230/132kV Grid Sub-Station | 400/230kV TR1 | 217 | 220.6558 | 2023-01-16 12:00
Kaliakoir 400/230/132kV Grid Sub-Station | 400/230kV TR2 | 217 | 220.6558 | 2023-01-16 12:00
Gopalganj 400/132kV Grid Sub-Station | ATR-01 | 102 | 112.3076 | 2023-01-28 11:00
Gopalganj 400/132kV Grid Sub-Station | ATR-02 | 0 | 0 | 2023-01-23 18:00
Gopalganj 400/132kV Grid Sub-Station | ATR-03 | 102 | 112.3076 | 2023-01-28 11:00
Kaliakoir 400/230/132kV Grid Sub-Station | 400/132kV TR1 | 299 | 318.5922 | 2023-01-27 07:00
Kaliakoir 400/230/132kV Grid Sub-Station | 400/132kV TR2 | 299 | 318.5922 | 2023-01-27 07:00
Payra 400/132/33kV Grid Sub-Station | 400/132/33 kV Auto Transformer-01 | -153 | 158.3982 | 2023-01-03 21:00
Payra 400/132/33kV Grid Sub-Station | 400/132/33 kV Auto Transformer-02 | -84 | 106.827 | 2023-01-30 19:00
Rahanpur_I 400/132kV Grid Sub-Station | AT-1 -Gen | 0 | 0 | 2023-01-04 10:00

## QF-LDC-37
|  |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
[6 empty] | Report on load shedding | [13 empty] | Report on load shedding
Month:January-2023 | [6 empty] | (For Evening Peak) | [7 empty] | Month:January-2023 | [6 empty] | (For Day Peak)
| Peak Hour |  | Total load shed (SS end) | [12 empty] | Peak Hour |  | Total load shed (SS end)
Date | Generation (Gen End) | Demand (Gen End) |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks | Date | Generation | Demand (Gen End) |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur
2023-01-01 | 9239 | 9239 | 0 | 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-01-01 | 8127 | 8127 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-01-02 | 9425 | 9425 | 0 | 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-01-02 | 8126 | 8126 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-01-03 | 9706 | 9706 | 0 | 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2023-01-03 | 8371 | 8371 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-01-04 | 9797 | 9797 | 0 | 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-01-04 | 8640 | 8640 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-01-05 | 9839 | 9839 | 0 | 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-01-05 | 8652 | 8652 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-01-06 | 8810 | 8810 | 0 | 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-01-06 | 7986 | 7986 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-01-07 | 9795 | 9795 | 0 | 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-01-07 | 7958 | 7958 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-01-08 | 9340 | 9861 | 480 | 20:00 | 134 | 35 | 47 | 17 | 0 | 101 | 62 | 0 | 84 | - | 2023-01-08 | 8582 | 8853 | 250 | 12:00 | 0 | 70 | 0 | 55 | 30 | 55 | 25 | 0 | 15 | -
2023-01-09 | 8939 | 9972 | 952 | 20:00 | 401 | 90 | 107 | 59 | 32 | 101 | 62 | 0 | 100 | - | 2023-01-09 | 7776 | 8800 | 944 | 12:00 | 325 | 85 | 170 | 130 | 36 | 123 | 0 | 0 | 75 | -
2023-01-10 | 9606 | 9800 | 179 | 20:00 | 0 | 0 | 0 | 100 | 0 | 24 | 0 | 0 | 55 | - | 2023-01-10 | 8152 | 8761 | 561 | 12:00 | 35 | 0 | 202 | 110 | 10 | 80 | 29 | 0 | 95 | -
2023-01-11 | 9767 | 9767 | 0 | 20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-01-11 | 8503 | 9065 | 518 | 12:00 | 43 | 98 | 0 | 102 | 73 | 117 | 30 | 0 | 55 | -
2023-01-12 | 9375 | 9808 | 399 | 20:00 | 120 | 0 | 12 | 0 | 0 | 155 | 0 | 0 | 112 | - | 2023-01-12 | 8733 | 8733 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-01-13 | 8929 | 8929 | 0 | 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-01-13 | 8148 | 8148 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-01-14 | 9446 | 9700 | 234 | 19:30 | 53 | 0 | 43 | 37 | 38 | 39 | 0 | 0 | 24 | - | 2023-01-14 | 8153 | 8449 | 273 | 12:00 | 0 | 0 | 149 | 46 | 0 | 37 | 0 | 0 | 41 | -
2023-01-15 | 9122 | 9660 | 496 | 20:00 | 0 | 0 | 136 | 107 | 0 | 87 | 53 | 0 | 113 | - | 2023-01-15 | 8501 | 8800 | 276 | 12:00 | 0 | 10 | 15 | 29 | 11 | 146 | 0 | 0 | 65 | -
2023-01-16 | 8937 | 9970 | 952 | 20:00 | 314 | 10 | 237 | 138 | 0 | 62 | 58 | 0 | 133 | - | 2023-01-16 | 7973 | 8992 | 939 | 12:00 | 202 | 149 | 31 | 107 | 110 | 216 | 49 | 0 | 75 | -
2023-01-17 | 9472 | 10094 | 573 | 20:00 | 102 | 0 | 171 | 78 | 0 | 107 | 0 | 0 | 115 | - | 2023-01-17 | 7983 | 7983 | 684 | 12:00 | 242 | 0 | 0 | 133 | 25 | 150 | 45 | 0 | 89 | -
2023-01-18 | 9460 | 10094 | 584 | 20:00 | 81 | 0 | 132 | 134 | 0 | 90 | 40 | 0 | 107 | - | 2023-01-18 | 8263 | 9000 | 679 | 12:00 | 190 | 115 | 34 | 130 | 42 | 110 | 18 | 0 | 40 | -
2023-01-19 | 9554 | 10000 | 411 | 19:00 | 41 | 0 | 40 | 180 | 0 | 150 | 0 | 0 | 0 | - | 2023-01-19 | 8415 | 9089 | 621 | 12:00 | 187 | 0 | 158 | 133 | 0 | 81 | 0 | 0 | 62 | -
2023-01-20 | 9186 | 9239 | 49 | 19:30 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | - | 2023-01-20 | 8171 | 8500 | 303 | 12:00 | 90 | 0 | 0 | 80 | 0 | 83 | 0 | 0 | 50 | -
2023-01-21 | 9768 | 9801 | 30 | 20:00 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | - | 2023-01-21 | 8385 | 8683 | 275 | 12:00 | 40 | 0 | 0 | 0 | 0 | 235 | 0 | 0 | 0 | -
2023-01-22 | 9673 | 10000 | 301 | 19:30 | 0 | 0 | 0 | 101 | 0 | 150 | 0 | 0 | 50 | - | 2023-01-22 | 8728 | 8950 | 205 | 12:00 | 105 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | -
2023-01-23 | 9927 | 10050 | 113 | 20:00 | 0 | 0 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | - | 2023-01-23 | 8596 | 9100 | 864 | 12:00 | 85 | 100 | 0 | 58 | 17 | 127 | 17 | 0 | 60 | -
2023-01-24 | 10098 | 10293 | 180 | 20:00 | 30 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | - | 2023-01-24 | 8675 | 9100 | 530 | 12:00 | 170 | 0 | 0 | 100 | 30 | 160 | 20 | 0 | 50 | -
2023-01-25 | 10048 | 10336 | 265 | 20:00 | 105 | 0 | 0 | 0 | 0 | 109 | 51 | 0 | 0 | - | 2023-01-25 | 9231 | 9567 | 310 | 12:00 | 75 | 66 | 0 | 0 | 70 | 99 | 0 | 0 | 0 | -
2023-01-26 | 10308 | 10485 | 163 | 19:30 | 22 | 0 | 0 | 0 | 0 | 141 | 0 | 0 | 0 | - | 2023-01-26 | 8821 | 9550 | 672 | 12:00 | 220 | 140 | 0 | 0 | 90 | 160 | 12 | 0 | 50 | -
2023-01-27 | 9356 | 9405 | 45 | 19:30 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | - | 2023-01-27 | 8508 | 8781 | 252 | 12:00 | 59 | 0 | 0 | 10 | 30 | 125 | 21 | 0 | 7 | -
2023-01-28 | 10111 | 10209 | 90 | 20:00 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | - | 2023-01-28 | 8603 | 9200 | 550 | 12:00 | 190 | 116 | 0 | 43 | 55 | 99 | 0 | 0 | 47 | -
2023-01-29 | 10300 | 10455 | 143 | 19:00 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 0 | 0 |  | 2023-01-29 | 9332 | 9560 | 160 | 12:00 | 106 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0
2023-01-30 | 10330 | 10496 | 153 | 19:00 | 0 | 0 | 0 | 0 | 0 | 153 | 0 | 0 | 0 |  | 2023-01-30 | 9051 | 9550 | 460 | 12:00 | 180 | 14 | 0 | 0 | 47 | 148 | 34 | 0 | 37
2023-01-31 | 10187 | 10350 | 150 | 19:30 | 30 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 |  | 2023-01-31 | 9296 | 9550 | 234 | 12:00 | 138 | 0 | 0 | 0 | 0 | 96 | 0 | 0 | 0
15456
| Max. L/S | - | 1537 | - | [10 empty] | Max. L/S | - |  | 1638
| Min. L/S | - | 54 | - | [10 empty] | Min. L/S | - |  | 0
| No. of Days | - | 31 | - | [10 empty] | No. of Days | - | 31
| Average L/S |  | 21566 | [11 empty] | Average L/S |  | 19669

## QF-LDC-38
Page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month:January 2023
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 10330 | 2023-01-30 | 19:00
2 | Maximum Day Peak Genaration | MW | 9332 | 2023-01-29 | 12:00
3 | Maximum Evening Peak Demand | MW | 10496 | 2023-01-30 | 19:00
4 | Minimum Generation | MW | 5671 | 2023-01-07 | 6:00
5 | Average of the daily evening peak Genaration | MW | 9608.0645 | - | -
6 | Average of the daily day peak Genaration | MW | 8465.7742 | - | -
7 | Maximum load shed | MW | 952 | 2023-01-09 | 20:00
8 | Minimum load shed | MW | 0 | 2023-01-07 | 20:00
9 | Total nos. of load shed days | Day | 22 | - | -
10 | Average load shed ( Avg. of the 30 days in the month) | MW/Day | 223.9355 | - | -
11 | Total Generation | MkWh | 5927.4643 | - | -
12 | Total Generation by BPDB | MkWh | 1441.7073 | % of total Gen. | 24.32%
13 | Total Generation by IPP | MkWh | 1488.6477 | '' | 25.11%
14 | A) Total Generation by Generation Companies | MkWh | 1962.9574 | '' | 33.12%
| B) Total Generation by REB | MkWh | 122.7522 | " | 2.071%
| C) Total Generation by RENTAL | MkWh | 264.3287 | " | 4.459%
| D) Total Imported from India (BIPTC) | MkWh | 575.0298 | " | 9.701%
| E) Total Imported from Tripura, India (A.C) | MkWh | 72.0413 | " | 1.215%
15 | Fuel wise Generation.
| A) Gas | MkWh | 3400.0318 | % of total Gen. | 57.36%
| B) Oil | MkWh | 999.5429 | '' | 16.86%
| C) Hydro | MkWh | 22.1863 | '' | 0.3743%
| D) Solar | MkWh | 29.9075 | '' | 0.5046%
| E) Coal | MkWh | 828.7249 | '' | 13.98%
| F) BIPTC (Import from India) | MkWh | 575.0298 | '' | 9.701%
| G) A.C (Import from Tripura, India) | MkWh | 72.0413 | '' | 1.215%
16 | Maximun of the daily total Generation . | MkWh | 209.3512 | 2023-01-26
17 | Monthly Load factor | % | 87.0884 | - | -
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 23676.9755 | - | -
| A) Gas | M.Taka | 3565.8479 | - | -
| B) Liquid fuel | M.Taka | 11864.1496 | - | -
| C) Coal | M.Taka | 5215.4007 | - | -
| D) BIPTC (Import from India) | M.Taka | 2512.8803 | - | -
| E) Tripura(Import from India) | M.Taka | 518.6971 | - | -
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 885.1796 | 2023-01-19
| A) Gas | M.Taka | 126.3014 | 2023-01-13
| B) Liquid fuel | M.Taka | 515.2739 | 2023-01-01
| C) Coal | M.Taka | 309.9503 | 2023-01-19
| D) BIPTC (Import from India) | M.Taka | 91.9416 | 2023-01-22
20 | Average fuel cost of per unit Generation
| A) Including Hydro & Solar | Taka/kWhR | 4.7844
| B) Excluding Hydro & Solar | Taka/kWhR | 4.8254
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 97.2 | 31/1/2023 | 06:00
b) | Actual | FT (MSL) | 83.67 | 31/1/2023 | 06:00
22 | Peak Genaration of January 2022 | MW | 10021 | 2022-01-25 | 19:00
23 | Peak Demand of January 2022 | MW | 10021 | 2022-01-25 | 19:00
24 | Maximum peak Generation recorded upto 31/1/2023 | MW | 14782 | 16/04/2022 | 21:00
25 | Maximum peak Demand recorded upto 31/1/2023 | MW | 14782 | 16/04/2022 | 21:00
26 | Maximum load shed recorded upto 31/1/2023 | MW | 4395 | 2022-10-04 | 21:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## FGMO
Power Grid Company Of Bangladesh Ltd.
NLDC, Aftabnagar, Dhaka.
Monthly status of Free Governor Mode of Operation (FGMO) Power Plants
SL | Plant Name | Owner | Installed capacity | FGMO Status
|  |  | (MW) | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
1 | Bibiana-II 341 MW CCPP (Summit) | IPP | 341 | [7 empty] | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
2 | Shahjibazar GTPP Unit 8 & 9 | BPDB | 70
3 | Sirajgonj 400 MW CCPP Unit-4 | IPP | 414
4 | Sirajgonj 225MW CCPP Unit-3 | NWPGCL | 220
5 | Sirajgonj 225MW CCPP Unit-2 | NWPGCL | 220
6 | Meghnaghat CCPP(Summit) | IPP | 335
7 | Ashuganj 450 MW CCPP(North) | APSCL | 360 | √ | √ |  |  |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
8 | Ashuganj 225 MW CCPP | APSCL | 221 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
9 | Bheramara 410 MW CCPP | NWPGCL | 410
10 | Haripur 412 MW CCPP | EGCB | 412
11 | Fenchugonj CCPP Phase-1 | BPDB | 97
12 | Chandpur 150 MW CCPP | BPDB | 163
13 | Siddhirganj 2x120 MW GTPP | EGCB | 210
14 | Shikalbaha 225 MW CCPP | BPDB | 225
15 | Shikalbaha Peaking GT | BPDB | 150
16 | Shahjibazar 330 MW CCPP | BPDB | 330
17 | Ashuganj 450 MW CCPP(South) | APSCL | 360
18 | Fenchugonj CCPP Phase-2 | BPDB | 104
19 | Bhola 225 MW CCPP | BPDB | 194
20 | Ghorasal 365 MW CCPP Unit-7 | BPDB | 365
21 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | 210
22 | Siddhirganj 335 MW CCPP | EGCB | 335
23 | Bibiyana-III 400 MW CCPP | BPDB | 400 | [26 empty] | √ | √ | √ | √ | √
24 | Sylhet 225 MW CCPP | BPDB | 231
25 | RPCL 210 MW CCPP | IPP | 210
26 | Khulna 225 MW CCPP | NWPGCL | 230
27 | a) Baghabari 71 MW GTPP | BPDB | 71
| b) Baghabari 100 MW GTPP | BPDB | 100
28 | Karnaphuli Hydro PP Unit: 1 | BPDB | 40
| Karnaphuli Hydro PP Unit: 2 | BPDB | 40
| Karnaphuli Hydro PP Unit: 3 | BPDB | 50
| Karnaphuli Hydro PP Unit: 4 | BPDB | 50
| Karnaphuli Hydro PP Unit: 5 | BPDB | 50
29 | a) Ghorasal Repowered CCPP Unit-3 | BPDB | 416
| b) Ghorasal Repowered CCPP Unit-4 | BPDB | 410
30 | Bibiyana South 400 MW CCPP | BPDB | 383
31 | Barapukuria 275 MW TPP Unit-3 | BPDB | 274
32 | Shajibazar 100 MW PP | BPDB | 100
33 | Payra 1320 MW Unit-1 | BCPCL | 622
34 | Kushiara 163 MW CCPP (KP) | IPP | 163
35 | Haripur 360MW CCPP(HPL) | IPP | 360
36 | Meghnaghat 450 MW CCPP(MPL) | IPP | 450
due to gas shortage