## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2023-04-03 | Monday
|  | Date (day): | 2023-04-03 |  | Monday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 12259.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14121 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2023-04-02 | 2023-04-03 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 | 365 |  | Under maint.
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 79 | 81 | 79 | 81 | 27 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 410 | 400 | 400 | 400 | 12
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 342 | 332 | 340 | 340 | 20
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 1 | 8 | 75 | 90 |  | 10 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 255 | 288 | 285 | 285 | 50 |  | FGMO
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 2 | 30 | 80 | 100
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 15 | 40 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 22 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 6 | 0 | 92 | 92 |  | 10 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 221 | 221 | 170 | 200 |  | 118 | ST under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 5 | 0 | 102 | 102
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 35 | 17 | 0 | 35 | 19 |  | Fuel shortage
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 16 | 0 | 64 | 150
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 35 | 35 | 35 | 20 |  | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 24 | 55 | 17 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 49 | 49 | 48 | 49 |  | 31 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 16 | 16 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 25 | 50 | 25 | 51
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 30 | 15 | 280 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 0 | 300 |  | Fuel shortage
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Fuel shortage
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Fuel shortage
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 52 | 144 | 115 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 17 | 51 | 70 | 105
37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 27 | 32 | 72 | 72 | 32 |  | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 54 | 54 | 162 | 162
39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 34 | 0 | 30 | 0
40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 35 | 35 | 35 | 20 |  | Fuel shortage
| Dhaka area Total |  |  |  |  | 6263 | 5847 | 2449 | 2638 | 3349 | 3661 | 1506 | 669
41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 0 | 8 | 25 | 25
43 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 0 | 0 | 20 | 0
44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 6 | 3 | 20 | 20 | 30 |  | Fuel shortage
45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 25 | 25 | 25 | 25 | 205 |  | Low Water Level
46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 224 | 213 | 225 | 225
47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 17 | 34 | 17 | 17 | 88 |  | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 48 |  | 50 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 34 | 0 | 65 |  | 37 | Engine problem
51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 44 | 64 | 55 | 66 |  | 34 | Engine problem
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 76 | 100 | 100 | 100
53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 8 | 8 | 5 | 5 | 17 |  | Gas shortage
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 38 | 5 | 20
54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 8 | 3 | 6 | 6 | 102 |  | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 3 | 0 | 5 | 0
56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 48 | 120 | 230 | 70 |  | Fuel shortge
57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 17 | 54 | 0 | 54
58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 67 | 54 | 54 | 54 | 56 |  | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 80 | 25 | 100 | 100
60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 107 | 107 | 107 | 107 |  | 9 | Engine problem
| Mirsharai 150 MW |  | Gas/HSD | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0
| Chattogram area Total |  |  |  |  | 2442 | 2382 | 684 | 818 | 889 | 1167 | 928 | 280
61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Contract Expired
62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 184 | 181 | 200 | 200 |  |  | FGMO
63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 280 | 305 | 280 | 300 |  |  | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Gas shortage
65 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 320 | 300 | 320 | 300 |  |  | FGMO
66 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 35 | 50 | 45 | 45
67 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 55 | 5 | 5 | 5 | 5 | 50 |  | Gas shortage
68 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
69 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 43 | 43 | 43 |  | 8 | Engine problem
70 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 10 | 10 | 100 | 150
71 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 35 |  | 17 | Engine problem
72 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under Maint.
73 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 159 | 200 | 160 | 200
74 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 18 | 18 | 18 |  | 4 | Engine problem
75 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 130 | 148 | 135 | 153
76 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 0 | 33 | 33 | 33
77 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 20 | 52 | 30 | 52
78 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 12 | 21 | 18 | 21 |  | 4 | Engine problem
79 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel shortage
80 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114
81 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 9 | 9 | 9 | 104 |  | Fuel shortage
82 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 17 |  | 18 | Engine problem
83 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 36 | 115 | 36 | 115 | 21
| Cumilla Area Total |  |  |  |  | 3309 | 3285 | 1297 | 1526 | 1582 | 1829 | 696 | 574
84 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 33 | 59 | 44 | 80 | 122 |  | Gas shortage
85 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 16 | 19 | 16 | 16 | 6 |  | Gas shortage
86 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0
87 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
88 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 55 | 173 | 150 | 180 |  | 20 | Engine problem
89 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 107 | 115 | 115 | 115
90 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 31 | 0 | 50 | 0
91 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 18 | 12 | 18 |  | 4 | Engine problem
| Mymensingh Area Total |  |  |  |  | 717 | 614 | 256 | 384 | 388.6 | 409 | 128 | 24
92 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 41 | 41 | 41 | 41 |  | 29 | Machine problem.
93 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 21 | 42 | 42 | 42 |  | 48 | Machine problem
94 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 112 | 112 | 112 | 112 |  | 51 | ST U/M.
95 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
96 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 48 | 53 | 48 | 51
97 | Fenchuganj 44MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 50 | 50 | 50 | 50
98 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 8 | 8 | 8 |  | 3 | Engine problem
99 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 61 | 64 | 65 | 65
100 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 88 | 86 | 86 | 86
101 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
102 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 212 | 209 | 210 | 210 |  | 21 | Machine problem
103 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18
104 | Sylhet 50MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
105 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 16 | 16 | 16 | 9 |  | Gas shortage
106 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 260 | 275 | 280 | 280 |  |  | FGMO
107 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 367 | 366 | 366 | 366 |  |  | FGMO
108 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 9 | 9 | 10 | 10
109 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 400 | 400 | 400 | 400
| Sylhet Area Total |  |  |  |  | 2472 | 2427 | 1703 | 1749 | 1752 | 1755 | 9 | 582
110 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 905 | 792 | 909 | 909
111 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 0 | 16 | 66 | 99 |  | 16 | Engine problem
112 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 40 | 50
113 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
114 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 40 | 65 |  | 44 | Engine problem
115 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 200 | 265 | 170 | 200 | 210 |  | Gas shortage
116 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 8 | 8 | 40
117 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Fuel shortage
118 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 17 | 53 | 53 | 52 |  | Fuel shortage
119 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 15 | 0 | 100
120 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 102 | 0 | 100 | 0
| Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 660*2 | 617 | 617 | 0 | 0 | 0 | 0 |  |  | Under maintenance
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3005 | 3001 | 1207 | 1113 | 1386 | 1516 | 608 | 60
121 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 16 | 48 | 48 | 62 |  | Fuel shortage
122 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 10 | 24 | 20 | 25 |  | 15 | Engine problem
123 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 153 | 171 | 170 | 170 | 24 |  | Gas shortage
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
124 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 640 | 1060 | 900 | 1200
125 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 0 | 0 | 0 | 0 |  | 220 | Under maintenance
126 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 0 | 0 |  |  | Line O/L
127 | Barisal 307 MW |  | Coal | BCPCL | 307*1 | 307 | 307 | 152 | 152 | 150 | 180 |  |  | Line O/L
| Barisal Area Total |  |  |  |  | 2265 | 2265 | 955 | 1423 | 1288 | 1623 | 86 | 235
128 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
129 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 32 |  | 20 | Engine problem
130 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 40 |  | 31 | Engine problem
131 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
132 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 0 | 42 |  | 8 | Engine problem
133 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 40 |  | 10 | Engine problem
134 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 130 | 204 | 180 | 180 | 30 |  | Gas shortage
135 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
136 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
137 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 254 | 420 | 290 | 300 | 114 |  | Gas shortage
138 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 23 | 0 | 28 | 36 |  | 14 | Engine problem
139 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 3 | 21 | 22 | 22
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
140 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
141 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 34 | 18 |  | Fuel shortage
142 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 50 | 100
143 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel shortage
144 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 113 | 50 | 113
145 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 50 | 113
146 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
| Adani Power Jharkhanda Ltd |  | Coal | Import | 0 | 0 | 0 | 766 | 752 | 500 | 700 |  |  | On test.
| Rajshahi Area Total |  |  |  |  | 2179 | 2129 | 1192 | 1521 | 1187 | 1763 | 973 | 83
147 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
148 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 170 | 170 | 170 | 104 |  | Coal Shortage.
149 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
150 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
151 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 34 | 50 | 113
152 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 6 | 0 | 8 | 0
153 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 0 | 36 | 50 | 115
154 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 37 | 0 | 30 | 0
| Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 0 | 0 | 166 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 830 | 750 | 359 | 240 | 438 | 398 | 229 | 85
| Total |  |  |  |  | 23482 | 22700 | 10102 | 11412 | 12259.6 | 14121 | 5163 | 2592
A. |  | 2023-04-02 | (Yesterday) |  |  |  |  | Sunday
1 | Highest Generation : |  |  | 11412 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 7408 | MW at | 6:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 11412 | MW
3 | Day peak Generation : |  |  | 10102 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 10922.88 | MW
4 | Evening peak Generation : |  |  | 11412 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 237.8648 | MKWHr | By Solar | 3.0462 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Gas : | 134.1951 | MKWHr |  | By Oil: | 29.8614 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 46.1026 | MKWHr |  | By Hydro: | 0.49342 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 5163 | MW | Dhaka | 4075.7 | 4075.7 |  | 0 |  | 18:00 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 2592 | MW | Chittagong | 1156.5 | 1156.5 |  | 0 |  | 19:00 |  | 0
|  |  | Total = |  |  | 7755 | MW | Khulna | 1381 | 1381 |  | 0 |  | 19:30 |  | 0
7 | Total Gas Supplied : |  |  | 1028.65 | MMCFD |  |  | Rajshahi | 1120.8 | 1120.8 |  | 0 |  | 20:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 142354998.49 | ii) Oil : | Taka | 385686072.18 | Comilla | 997 | 997 |  | 0 |  | 21:00 |  | 0
|  | iii) Coal : | Taka | 202535678 | Total | Taka | 730576748.67 | Mymensingh | 877 | 877 |  | 0 |  | 22:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0 | MKWHr. | Sylhet | 336 | 336 |  | 0 |  | 23:00 |  | 0
| ii) During Peak Demand : |  |  | 470 | MW (E to W) at | 21:00 | hrs | Barisal | 335.88 | 335.88 |  | 0 |  | 24:00 |  | 0
| iii) Maximum : |  |  | 76 | MW at | 19:30 | hrs | Rangpur | 643 | 643 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 32.0° C |  |  | Total | 10922.88 | 10922.88 |  | 0
B. |  | 2023-04-03 | (Today) |  |  |  | Monday |  |  | Probable max. temperature in Dhaka |  |  | 34.3° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 12100 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 14121 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 10800 | MW
4 | Reserve(Generation end) |  |  |  | 2021 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 252.2051 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 8001 | MW at | 6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.2582 | MKWHr. | ii) HVDC Flow at Peak Time |  | 792 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.9078 | MKWHr. | iii) Maximum HVDC Flow : |  | 905 | MW at | 11:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 75.98 |  | (b) Today: | 76.01 |  | (c) Rule Curve: |  | 87.6
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2023-04-02 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 0 | 55 | 0 | 374 | 262 |  | 0 | 360 | 222 | 0 | 0 | 0 | 136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 0 | 19 | 23 | 26 | 33 | 16 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 176 | 0 | 0 | 0 |  | 10 | 0 | 17 | 52 | 0 | 6 | 7 | 40 | 0 | 0 | 0 | 280 | 0 | 181 | 0 | 0 | 50 | 5 | 0 | 30 | 0 | 0 | 0 | 18 | 11 | 33 | 21 | 108 | 84 | 0 | 14 | 0 | 41 | 31 | 11 | 50 | 80 | 0 | 40 | 20 | 0 | 212 | 18 | 0 | 10 | 260 | 8 | 8 | 0 | 0 | 0 | 0 | 46 | 0 | 71 | 0 | 50 | 51 | 0 | 366 | 57 | 0 | 17 | 0 | 0 | 0 | 54 | 0 | 9 | 0 | 360 | 0 | 0 | 0 | 107 | 0 | 17 | 0 | 38 | 17 | 250 | 0 | 0 |  | 904 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 860 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 239 | 755 | 0 | 0 |  | 5225 | 3704 | 8929 | 3532 | 904 | 1685 | 0 | 654 | 2004 | 25 | 0 | 17 | 108 | 0 | 0 | 75.97
2:00 | 0 | 0 | 0 | 180 | 0 | 53 | 0 | 383 | 262 |  | 0 | 370 | 236 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 19 | 23 | 26 | 33 | 16 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 177 | 0 | 0 | 0 |  | 12 | 0 | 17 | 52 | 0 | 6 | 7 | 41 | 0 | 0 | 0 | 280 | 0 | 181 | 0 | 0 | 25 | 5 | 0 | 30 | 0 | 0 | 0 | 18 | 11 | 33 | 21 | 106 | 84 | 0 | 14 | 0 | 41 | 31 | 11 | 10 | 80 | 0 | 40 | 20 | 0 | 212 | 18 | 0 | 9 | 265 | 8 | 8 | 0 | 0 | 0 | 0 | 28 | 0 | 70 | 0 | 50 | 51 | 0 | 339 | 68 | 0 | 17 | 0 | 0 | 0 | 54 | 0 | 9 | 0 | 360 | 0 | 0 | 0 | 107 | 0 | 17 | 0 | 47 | 17 | 250 | 0 | 0 |  | 904 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 750 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 209 | 761 | 0 | 0 |  | 5162 | 3549 | 8711 | 3498 | 904 | 1652 | 0 | 639 | 1870 | 25 | 0 | 17 | 106 | 0 | 0 | 75.97
3:00 | 0 | 0 | 0 | 180 | 0 | 81 | 0 | 394 | 272 |  | 0 | 380 | 254 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 19 | 23 | 26 | 33 | 16 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 176 | 0 | 0 | 0 |  | 12 | 0 | 17 | 55 | 0 | 6 | 7 | 41 | 0 | 0 | 0 | 280 | 0 | 181 | 0 | 0 | 25 | 5 | 0 | 36 | 0 | 0 | 0 | 18 | 11 | 33 | 21 | 100 | 83 | 0 | 14 | 0 | 41 | 31 | 44 | 20 | 112 | 0 | 64 | 60 | 0 | 213 | 18 | 0 | 10 | 270 | 8 | 8 | 0 | 0 | 0 | 0 | 19 | 0 | 70 | 0 | 60 | 51 | 0 | 328 | 47 | 0 | 17 | 0 | 0 | 0 | 54 | 0 | 9 | 0 | 400 | 0 | 0 | 0 | 107 | 0 | 17 | 0 | 35 | 17 | 250 | 0 | 0 |  | 904 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 790 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 758 | 0 | 0 |  | 5388 | 3632 | 9020 | 3582 | 904 | 1902 | 0 | 610 | 1880 | 25 | 0 | 17 | 100 | 0 | 0 | 75.97
4:00 | 0 | 0 | 0 | 180 | 0 | 81 | 0 | 386 | 272 |  | 0 | 330 | 257 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 19 | 23 | 26 | 33 | 16 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 172 | 0 | 0 | 0 |  | 12 | 0 | 17 | 55 | 0 | 6 | 7 | 41 | 0 | 0 | 0 | 280 | 0 | 181 | 0 | 0 | 25 | 5 | 0 | 43 | 0 | 0 | 0 | 18 | 11 | 33 | 21 | 112 | 72 | 0 | 14 | 0 | 41 | 31 | 51 | 47 | 112 | 0 | 64 | 60 | 0 | 212 | 18 | 0 | 10 | 270 | 8 | 8 | 0 | 0 | 0 | 0 | 32 | 0 | 78 | 0 | 75 | 51 | 0 | 332 | 47 | 0 | 17 | 0 | 0 | 0 | 54 | 0 | 9 | 0 | 380 | 0 | 0 | 0 | 107 | 0 | 17 | 0 | 37 | 34 | 250 | 0 | 0 |  | 904 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 810 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 758 | 0 | 0 |  | 5419 | 3703 | 9122 | 3589 | 904 | 1910 | 0 | 665 | 1900 | 25 | 0 | 17 | 112 | 0 | 0 | 75.97
5:00 | 0 | 0 | 0 | 180 | 0 | 22 | 0 | 345 | 292 |  | 0 | 300 | 228 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 26 | 33 | 16 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 171 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 0 | 6 | 7 | 41 | 0 | 0 | 0 | 280 | 0 | 182 | 0 | 0 | 10 | 5 | 0 | 5 | 0 | 0 | 0 | 18 | 11 | 33 | 19 | 98 | 72 | 0 | 14 | 0 | 41 | 31 | 5 | 5 | 80 | 0 | 40 | 10 | 0 | 211 | 19 | 0 | 10 | 255 | 16 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 17 | 0 | 76 | 34 | 0 | 302 | 24 | 0 | 17 | 0 | 0 | 0 | 54 | 0 | 9 | 0 | 310 | 0 | 0 | 0 | 107 | 0 | 0 | 0 | 36 | 17 | 250 | 0 | 0 |  | 904 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 580 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 756 | 0 | 0 |  | 4594 | 3299 | 7893 | 3293 | 904 | 1520 | 0 | 415 | 1638 | 25 | 0 | 0 | 98 | 0 | 0 | 75.98
6:00 | 0 | 0 | 0 | 180 | 0 | 22 | 0 | 301 | 263 |  | 0 | 300 | 245 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 26 | 33 | 16 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 172 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 0 | 6 | 7 | 41 | 0 | 0 | 0 | 280 | 0 | 153 | 0 | 0 | 10 | 5 | 0 | 5 | 0 | 0 | 0 | 18 | 11 | 33 | 12 | 92 | 74 | 0 | 14 | 0 | 41 | 31 | 5 | 5 | 80 | 0 | 40 | 10 | 0 | 210 | 19 | 0 | 0 | 250 | 16 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 40 | 17 | 0 | 305 | 8 | 0 | 17 | 0 | 0 | 0 | 54 | 0 | 9 | 0 | 310 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 36 | 0 | 250 | 0 | 0 |  | 848 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 560 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 610 | 0 | 0 |  | 4277 | 3131 | 7408 | 3168 | 848 | 1547 | 0 | 256 | 1472 | 25 | 0 | 0 | 92 | 0 | 0 | 75.98
7:00 | 0 | 0 | 0 | 180 | 0 | 22 | 0 | 301 | 263 |  | 0 | 300 | 244 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 26 | 33 | 16 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 172 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 0 | 6 | 5 | 25 | 0 | 0 | 0 | 280 | 0 | 152 | 0 | 0 | 10 | 5 | 0 | 5 | 0 | 0 | 0 | 18 | 8 | 33 | 12 | 90 | 36 | 0 | 14 | 0 | 41 | 31 | 5 | 5 | 80 | 0 | 40 | 10 | 0 | 211 | 18 | 0 | 0 | 265 | 16 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 40 | 17 | 0 | 304 | 8 | 0 | 17 | 0 | 0 | 0 | 54 | 0 | 8 | 0 | 350 | 0 | 8 | 0 | 51 | 0 | 0 | 5 | 35 | 0 | 250 | 0 | 0 |  | 848 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 298 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 560 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 3 | 153 | 756 | 27 | 0 |  | 4279 | 3322 | 7601 | 3163 | 848 | 1544 | 0 | 254 | 1619 | 25 | 0 | 0 | 90 | 58 | 0 | 75.98
8:00 | 0 | 0 | 0 | 180 | 0 | 22 | 0 | 325 | 262 |  | 0 | 300 | 270 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 26 | 33 | 16 | 3 | 0 | 25 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 |  | 1 | 0 | 0 | 10 | 0 | 6 | 7 | 18 | 0 | 0 | 0 | 275 | 0 | 184 | 0 | 0 | 10 | 5 | 0 | 5 | 0 | 0 | 1 | 18 | 0 | 0 | 0 | 100 | 35 | 0 | 14 | 1 | 41 | 31 | 5 | 5 | 112 | 0 | 40 | 10 | 0 | 211 | 18 | 0 | 0 | 280 | 16 | 8 | 0 | 0 | 0 | 0 | 24 | 0 | 9 | 0 | 40 | 38 | 0 | 364 | 47 | 0 | 17 | 1 | 0 | 0 | 54 | 0 | 9 | 9 | 350 | 0 | 20 | 4 | 51 | 0 | 0 | 13 | 36 | 5 | 250 | 0 | 0 |  | 843 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 298 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 590 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 0 | 8 | 154 | 759 | 80 | 0 |  | 4562 | 3438 | 8000 | 3223 | 843 | 1610 | 0 | 364 | 1653 | 25 | 0 | 16 | 100 | 166 | 0 | 75.99
9:00 | 0 | 0 | 0 | 180 | 0 | 67 | 0 | 399 | 282 |  | 0 | 340 | 295 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 26 | 33 | 16 | 16 | 0 | 25 | 0 | 0 | 0 | 0 | 201 | 0 | 0 | 0 |  | 12 | 0 | 0 | 10 | 0 | 6 | 8 | 18 | 0 | 0 | 0 | 285 | 0 | 192 | 0 | 0 | 10 | 5 | 0 | 5 | 0 | 0 | 8 | 18 | 0 | 33 | 15 | 104 | 35 | 0 | 19 | 2 | 41 | 31 | 22 | 20 | 112 | 0 | 40 | 40 | 0 | 212 | 18 | 0 | 9 | 280 | 16 | 8 | 0 | 0 | 0 | 0 | 47 | 0 | 51 | 14 | 40 | 68 | 0 | 370 | 47 | 25 | 17 | 3 | 0 | 16 | 54 | 0 | 9 | 12 | 400 | 0 | 14 | 17 | 51 | 0 | 0 | 23 | 36 | 17 | 320 | 0 | 0 |  | 856 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 620 | 0 | 0 | 0 | 2 | 48 | 0 | 0 | 0 | 0 | 24 | 152 | 761 | 87 | 0 |  | 5344 | 3462 | 8806 | 3584 | 856 | 1760 | 0 | 559 | 1683 | 25 | 0 | 16 | 104 | 219 | 0 | 75.99
10:00 | 0 | 0 | 0 | 180 | 0 | 75 | 0 | 409 | 352 |  | 0 | 450 | 280 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 35 | 17 | 0 | 0 | 23 | 26 | 33 | 16 | 25 | 0 | 25 | 0 | 0 | 0 | 0 | 199 | 0 | 0 | 0 |  | 12 | 0 | 0 | 36 | 3 | 6 | 8 | 4 | 0 | 0 | 0 | 280 | 0 | 184 | 0 | 0 | 10 | 5 | 0 | 25 | 0 | 0 | 8 | 18 | 8 | 0 | 12 | 118 | 35 | 0 | 16 | 2 | 41 | 31 | 48 | 44 | 112 | 0 | 61 | 86 | 0 | 211 | 18 | 0 | 9 | 270 | 16 | 0 | 0 | 12 | 0 | 0 | 37 | 0 | 51 | 11 | 76 | 72 | 5 | 367 | 49 | 17 | 21 | 4 | 0 | 17 | 54 | 0 | 5 | 12 | 400 | 1 | 43 | 54 | 62 | 0 | 1 | 30 | 35 | 17 | 320 | 0 | 0 |  | 857 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 620 | 0 | 0 | 0 | 4 | 83 | 0 | 0 | 0 | 0 | 34 | 152 | 765 | 160 | 0 |  | 5811 | 3593 | 9404 | 3563 | 857 | 2024 | 0 | 740 | 1687 | 25 | 0 | 16 | 118 | 374 | 0 | 75.99
11:00 | 0 | 0 | 0 | 180 | 0 | 75 | 0 | 408 | 342 |  | 0 | 450 | 288 | 0 | 0 | 7 | 140 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 35 | 17 | 8 | 19 | 23 | 26 | 33 | 16 | 25 | 0 | 25 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 |  | 12 | 0 | 0 | 44 | 8 | 6 | 8 | 6 | 0 | 0 | 0 | 280 | 0 | 182 | 8 | 0 | 20 | 5 | 0 | 43 | 0 | 0 | 8 | 18 | 11 | 0 | 12 | 132 | 35 | 0 | 16 | 2 | 41 | 20 | 49 | 50 | 80 | 0 | 60 | 89 | 0 | 212 | 18 | 0 | 9 | 260 | 16 | 0 | 0 | 30 | 0 | 0 | 55 | 0 | 52 | 14 | 76 | 120 | 10 | 367 | 75 | 17 | 17 | 5 | 0 | 17 | 61 | 0 | 9 | 12 | 400 | 16 | 53 | 72 | 107 | 0 | 17 | 22 | 36 | 17 | 320 | 0 | 0 |  | 905 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 590 | 0 | 0 | 0 | 5 | 98 | 0 | 0 | 0 | 0 | 23 | 153 | 768 | 95 | 0 |  | 6114 | 3563 | 9677 | 3606 | 905 | 2023 | 0 | 986 | 1661 | 25 | 0 | 16 | 132 | 323 | 0 | 76
12:00 | 0 | 0 | 0 | 180 | 0 | 79 | 0 | 410 | 342 |  | 0 | 450 | 255 | 1 | 2 | 15 | 221 | 0 | 0 | 6 | 5 | 16 | 0 | 0 | 0 | 0 | 35 | 35 | 24 | 19 | 23 | 26 | 33 | 16 | 25 | 0 | 25 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 |  | 12 | 0 | 0 | 44 | 8 | 6 | 8 | 2 | 0 | 0 | 0 | 280 | 0 | 184 | 8 | 0 | 35 | 5 | 0 | 43 | 0 | 0 | 20 | 18 | 11 | 0 | 12 | 130 | 33 | 0 | 16 | 2 | 41 | 21 | 48 | 50 | 112 | 0 | 61 | 88 | 0 | 212 | 18 | 0 | 9 | 260 | 16 | 0 | 0 | 30 | 0 | 0 | 55 | 0 | 52 | 0 | 76 | 159 | 10 | 367 | 107 | 17 | 17 | 3 | 0 | 17 | 67 | 0 | 9 | 80 | 400 | 27 | 31 | 54 | 107 | 0 | 17 | 34 | 36 | 17 | 320 | 0 | 0 |  | 905 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 3 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 254 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 640 | 0 | 0 | 0 | 5 | 102 | 0 | 0 | 0 | 0 | 37 | 152 | 766 | 166 | 0 |  | 6389 | 3713 | 10102 | 3699 | 905 | 2018 | 0 | 1192 | 1708 | 25 | 0 | 39 | 130 | 386 | 0 | 76
13:00 | 0 | 0 | 0 | 180 | 0 | 80 | 0 | 408 | 211 |  | 0 | 450 | 290 | 8 | 17 | 26 | 215 | 0 | 0 | 9 | 32 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 41 | 19 | 23 | 26 | 33 | 16 | 25 | 0 | 25 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 |  | 12 | 0 | 0 | 44 | 6 | 6 | 8 | 8 | 0 | 0 | 0 | 290 | 0 | 200 | 8 | 0 | 35 | 5 | 0 | 43 | 0 | 0 | 52 | 18 | 11 | 0 | 18 | 136 | 33 | 0 | 19 | 2 | 41 | 20 | 51 | 50 | 112 | 0 | 60 | 84 | 0 | 212 | 18 | 0 | 9 | 275 | 16 | 3 | 0 | 30 | 0 | 0 | 62 | 0 | 73 | 9 | 76 | 183 | 10 | 370 | 115 | 17 | 17 | 3 | 0 | 17 | 66 | 0 | 9 | 75 | 400 | 48 | 17 | 90 | 107 | 0 | 17 | 34 | 36 | 17 | 320 | 18 | 0 |  | 904 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 3 | 0 | 11 | 0 | 0 | 163 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 286 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 700 | 0 | 0 | 0 | 5 | 98 | 0 | 0 | 0 | 0 | 37 | 154 | 764 | 190 | 0 |  | 6567 | 3860 | 10427 | 3737 | 904 | 1977 | 0 | 1395 | 1781 | 25 | 18 | 52 | 136 | 402 | 0 | 76
14:00 | 0 | 0 | 0 | 180 | 0 | 80 | 0 | 409 | 254 |  | 0 | 450 | 275 | 25 | 24 | 47 | 216 | 0 | 0 | 30 | 33 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 55 | 19 | 23 | 26 | 33 | 16 | 25 | 0 | 25 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 |  | 12 | 0 | 0 | 44 | 5 | 6 | 8 | 2 | 0 | 0 | 0 | 280 | 0 | 182 | 8 | 0 | 39 | 5 | 0 | 43 | 0 | 0 | 41 | 13 | 11 | 33 | 21 | 136 | 33 | 0 | 19 | 2 | 41 | 42 | 51 | 50 | 112 | 0 | 62 | 82 | 0 | 207 | 18 | 0 | 8 | 260 | 16 | 3 | 0 | 30 | 0 | 0 | 75 | 0 | 91 | 7 | 76 | 200 | 10 | 367 | 115 | 22 | 17 | 4 | 100 | 17 | 54 | 0 | 9 | 85 | 400 | 66 | 11 | 108 | 107 | 0 | 17 | 30 | 35 | 18 | 320 | 0 | 0 |  | 905 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 20 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 286 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 800 | 0 | 0 | 0 | 5 | 77 | 0 | 0 | 0 | 0 | 33 | 153 | 763 | 145 | 0 |  | 6823 | 3933 | 10756 | 3782 | 905 | 1998 | 0 | 1651 | 1886 | 25 | 0 | 52 | 136 | 321 | 0 | 76
15:00 | 0 | 0 | 0 | 180 | 0 | 80 | 0 | 410 | 341 |  | 0 | 450 | 277 | 24 | 51 | 55 | 160 | 0 | 0 | 20 | 33 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 55 | 7 | 23 | 26 | 33 | 16 | 34 | 0 | 25 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 |  | 12 | 0 | 0 | 44 | 5 | 6 | 8 | 2 | 0 | 0 | 0 | 280 | 0 | 181 | 8 | 0 | 46 | 5 | 0 | 5 | 0 | 0 | 42 | 15 | 11 | 33 | 21 | 140 | 33 | 0 | 19 | 2 | 41 | 42 | 51 | 50 | 112 | 0 | 60 | 82 | 0 | 210 | 18 | 0 | 8 | 270 | 16 | 3 | 0 | 30 | 0 | 0 | 75 | 0 | 100 | 5 | 88 | 200 | 10 | 375 | 115 | 46 | 17 | 3 | 100 | 17 | 54 | 0 | 9 | 86 | 395 | 60 | 39 | 108 | 107 | 0 | 17 | 23 | 35 | 35 | 321 | 7 | 0 |  | 903 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 18 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 740 | 0 | 0 | 0 | 4 | 70 | 0 | 0 | 0 | 0 | 30 | 153 | 761 | 148 | 0 |  | 6948 | 3800 | 10748 | 3686 | 903 | 2038 | 0 | 1742 | 1824 | 25 | 7 | 52 | 140 | 331 | 0 | 76.01
16:00 | 0 | 0 | 0 | 180 | 0 | 80 | 0 | 407 | 346 |  | 0 | 450 | 290 | 8 | 20 | 40 | 160 | 0 | 0 | 8 | 33 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 55 | 15 | 23 | 26 | 33 | 16 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 |  | 12 | 0 | 0 | 46 | 6 | 6 | 8 | 3 | 0 | 0 | 0 | 315 | 0 | 202 | 8 | 0 | 45 | 5 | 0 | 5 | 0 | 0 | 50 | 0 | 11 | 33 | 21 | 128 | 33 | 0 | 19 | 1 | 41 | 42 | 53 | 50 | 80 | 0 | 60 | 84 | 0 | 210 | 18 | 0 | 8 | 275 | 16 | 3 | 0 | 30 | 0 | 0 | 75 | 0 | 104 | 5 | 88 | 200 | 10 | 397 | 88 | 52 | 17 | 2 | 65 | 17 | 54 | 0 | 9 | 38 | 400 | 34 | 20 | 108 | 107 | 0 | 17 | 14 | 47 | 35 | 345 | 11 | 0 |  | 904 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 3 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 263 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 700 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 17 | 154 | 760 | 101 | 0 |  | 6806 | 3631 | 10437 | 3771 | 904 | 2017 | 0 | 1571 | 1784 | 0 | 11 | 51 | 128 | 200 | 0 | 76.01
17:00 | 0 | 0 | 0 | 180 | 0 | 81 | 0 | 408 | 332 |  | 0 | 450 | 292 | 8 | 17 | 40 | 214 | 0 | 0 | 8 | 33 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 55 | 22 | 23 | 24 | 33 | 16 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 |  | 12 | 0 | 0 | 47 | 6 | 8 | 8 | 12 | 0 | 0 | 0 | 280 | 0 | 180 | 8 | 0 | 45 | 5 | 0 | 5 | 0 | 0 | 52 | 0 | 11 | 33 | 21 | 126 | 30 | 0 | 16 | 0 | 41 | 42 | 53 | 50 | 112 | 0 | 60 | 84 | 0 | 210 | 18 | 0 | 9 | 270 | 16 | 3 | 0 | 30 | 0 | 0 | 96 | 0 | 123 | 2 | 88 | 200 | 10 | 364 | 88 | 52 | 17 | 1 | 65 | 17 | 54 | 0 | 9 | 38 | 400 | 17 | 10 | 108 | 107 | 0 | 11 | 6 | 75 | 35 | 300 | 0 | 0 |  | 904 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 3 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 318 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 700 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 8 | 153 | 764 | 40 | 0 |  | 6773 | 3645 | 10418 | 3732 | 904 | 2098 | 0 | 1628 | 1787 | 0 | 0 | 50 | 126 | 93 | 0 | 76.01
18:00 | 0 | 0 | 0 | 180 | 0 | 81 | 0 | 403 | 302 |  | 0 | 450 | 285 | 18 | 20 | 41 | 214 | 0 | 0 | 21 | 33 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 55 | 22 | 23 | 24 | 33 | 16 | 50 | 0 | 0 | 25 | 0 | 0 | 0 | 225 | 0 | 0 | 0 |  | 17 | 0 | 0 | 60 | 6 | 6 | 8 | 24 | 0 | 0 | 0 | 300 | 0 | 179 | 8 | 0 | 47 | 5 | 0 | 5 | 0 | 0 | 52 | 18 | 11 | 33 | 21 | 142 | 30 | 0 | 16 | 0 | 41 | 42 | 22 | 20 | 80 | 0 | 40 | 86 | 0 | 210 | 18 | 0 | 9 | 275 | 16 | 5 | 0 | 42 | 0 | 0 | 120 | 0 | 147 | 0 | 88 | 200 | 10 | 342 | 92 | 62 | 30 | 0 | 100 | 27 | 54 | 0 | 9 | 85 | 400 | 35 | 1 | 108 | 107 | 0 | 17 | 1 | 75 | 35 | 250 | 0 | 0 |  | 904 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 3 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 0 | 0 | 9 | 0 | 40 | 0 | 1 | 35 | 600 | 0 | 0 | 0 | 0 | 1 | 35 | 0 | 0 | 0 | 1 | 154 | 756 | 4 | 0 |  | 6878 | 3563 | 10441 | 3689 | 904 | 1951 | 0 | 1993 | 1680 | 25 | 0 | 48 | 142 | 9 | 0 | 76.01
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 0 | 81 | 0 | 337 | 352 |  | 0 | 400 | 282 | 42 | 51 | 40 | 88 | 0 | 0 | 40 | 33 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 55 | 0 | 23 | 16 | 33 | 8 | 3 | 0 | 0 | 25 | 0 | 0 | 8 | 226 | 0 | 0 | 0 |  | 18 | 36 | 51 | 60 | 5 | 6 | 8 | 35 | 0 | 0 | 0 | 280 | 0 | 180 | 8 | 0 | 47 | 5 | 0 | 16 | 0 | 25 | 52 | 18 | 11 | 33 | 21 | 144 | 33 | 0 | 16 | 0 | 41 | 42 | 32 | 35 | 112 | 0 | 64 | 86 | 0 | 216 | 18 | 0 | 9 | 280 | 16 | 8 | 0 | 95 | 0 | 0 | 172 | 0 | 149 | 0 | 100 | 200 | 33 | 363 | 115 | 105 | 34 | 0 | 100 | 54 | 54 | 17 | 9 | 85 | 400 | 35 | 0 | 108 | 107 | 0 | 17 | 0 | 75 | 34 | 270 | 0 | 0 |  | 904 | 0 | 180 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 171 | 22 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 8 | 34 | 21 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 294 | 17 | 0 | 35 | 15 | 40 | 0 | 0 | 35 | 620 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 186 | 748 | 0 | 0 |  | 7189 | 3742 | 10931 | 3506 | 904 | 2070 | 0 | 2396 | 1724 | 25 | 0 | 162 | 144 | 0 | 0 | 76.01
19:30 | 0 | 0 | 0 | 180 | 0 | 81 | 0 | 400 | 342 |  | 0 | 400 | 260 | 41 | 51 | 40 | 88 | 0 | 0 | 40 | 33 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 55 | 0 | 23 | 26 | 33 | 8 | 33 | 0 | 0 | 25 | 0 | 0 | 8 | 229 | 0 | 0 | 0 |  | 18 | 18 | 51 | 60 | 5 | 6 | 8 | 35 | 0 | 0 | 0 | 280 | 0 | 182 | 8 | 0 | 49 | 5 | 0 | 43 | 0 | 38 | 52 | 18 | 11 | 33 | 21 | 136 | 49 | 0 | 19 | 0 | 41 | 42 | 48 | 50 | 112 | 0 | 65 | 86 | 0 | 216 | 18 | 0 | 9 | 275 | 16 | 8 | 0 | 95 | 0 | 0 | 172 | 0 | 149 | 0 | 100 | 200 | 100 | 365 | 115 | 105 | 34 | 0 | 100 | 54 | 54 | 17 | 9 | 85 | 400 | 35 | 0 | 108 | 107 | 0 | 17 | 0 | 80 | 35 | 270 | 0 | 0 |  | 791 | 0 | 220 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 162 | 21 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 29 | 21 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 17 | 0 | 98 | 15 | 40 | 0 | 0 | 35 | 820 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 202 | 750 | 0 | 0 |  | 7401 | 4003 | 11404 | 3702 | 791 | 2103 | 0 | 2553 | 1942 | 25 | 0 | 152 | 136 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 180 | 0 | 81 | 0 | 398 | 341 |  | 0 | 400 | 285 | 33 | 46 | 40 | 100 | 0 | 0 | 30 | 33 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 55 | 22 | 23 | 26 | 33 | 16 | 35 | 0 | 0 | 25 | 0 | 0 | 8 | 225 | 0 | 0 | 0 |  | 18 | 0 | 51 | 62 | 5 | 6 | 8 | 38 | 0 | 0 | 0 | 280 | 0 | 182 | 8 | 0 | 49 | 5 | 0 | 43 | 0 | 39 | 52 | 18 | 11 | 33 | 21 | 138 | 50 | 0 | 19 | 0 | 41 | 42 | 53 | 50 | 112 | 0 | 64 | 86 | 0 | 216 | 18 | 0 | 9 | 270 | 16 | 8 | 0 | 15 | 0 | 0 | 173 | 0 | 149 | 0 | 100 | 200 | 50 | 370 | 115 | 70 | 34 | 0 | 65 | 54 | 54 | 0 | 9 | 50 | 400 | 35 | 0 | 72 | 107 | 0 | 17 | 0 | 88 | 35 | 270 | 0 | 0 |  | 792 | 0 | 220 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 171 | 22 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 308 | 17 | 0 | 85 | 15 | 34 | 0 | 0 | 0 | 820 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 160 | 755 | 0 | 0 |  | 7156 | 3889 | 11045 | 3753 | 792 | 2132 | 0 | 2194 | 1905 | 25 | 0 | 106 | 138 | 0 | 0 | 76.01
21:00 | 0 | 0 | 0 | 180 | 0 | 81 | 0 | 400 | 332 |  | 0 | 450 | 288 | 8 | 30 | 40 | 221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 55 | 22 | 23 | 26 | 33 | 16 | 50 | 0 | 0 | 25 | 0 | 0 | 8 | 213 | 0 | 0 | 0 |  | 18 | 0 | 34 | 64 | 3 | 3 | 8 | 38 | 0 | 0 | 0 | 305 | 0 | 181 | 8 | 0 | 50 | 5 | 0 | 43 | 0 | 0 | 52 | 18 | 11 | 33 | 21 | 148 | 59 | 0 | 19 | 0 | 41 | 42 | 53 | 50 | 112 | 0 | 64 | 86 | 0 | 209 | 18 | 0 | 9 | 275 | 16 | 8 | 0 | 15 | 0 | 0 | 173 | 0 | 144 | 0 | 100 | 200 | 10 | 366 | 115 | 51 | 34 | 0 | 48 | 54 | 54 | 0 | 9 | 25 | 400 | 32 | 0 | 54 | 107 | 0 | 17 | 0 | 115 | 35 | 300 | 0 | 0 |  | 792 | 0 | 265 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 171 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 17 | 0 | 113 | 15 | 34 | 0 | 0 | 0 | 1060 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 152 | 752 | 0 | 0 |  | 7115 | 4297 | 11412 | 3954 | 792 | 2295 | 0 | 2030 | 2134 | 25 | 0 | 34 | 148 | 0 | 0 | 76.01
22:00 | 0 | 0 | 0 | 180 | 0 | 81 | 0 | 399 | 333 |  | 0 | 450 | 266 | 0 | 8 | 30 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 55 | 22 | 23 | 26 | 33 | 16 | 33 | 0 | 0 | 25 | 0 | 0 | 8 | 215 | 0 | 0 | 0 |  | 18 | 0 | 34 | 65 | 0 | 6 | 8 | 38 | 0 | 0 | 0 | 310 | 0 | 182 | 8 | 0 | 50 | 5 | 0 | 43 | 0 | 0 | 52 | 18 | 11 | 33 | 21 | 142 | 102 | 0 | 0 | 0 | 41 | 42 | 53 | 50 | 112 | 0 | 65 | 86 | 0 | 209 | 18 | 0 | 9 | 280 | 16 | 8 | 0 | 0 | 0 | 0 | 150 | 0 | 84 | 0 | 100 | 200 | 10 | 366 | 115 | 34 | 34 | 0 | 48 | 35 | 54 | 0 | 9 | 25 | 400 | 17 | 0 | 35 | 107 | 0 | 17 | 0 | 115 | 35 | 352 | 0 | 0 |  | 904 | 0 | 285 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 303 | 17 | 0 | 113 | 0 | 34 | 0 | 0 | 0 | 1140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 198 | 750 | 0 | 0 |  | 6952 | 4297 | 11249 | 3993 | 904 | 2162 | 0 | 1731 | 2258 | 25 | 0 | 34 | 142 | 0 | 0 | 76.01
23:00 | 0 | 0 | 0 | 180 | 0 | 81 | 0 | 398 | 333 |  | 0 | 450 | 313 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 22 | 23 | 25 | 33 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 200 | 0 | 0 | 0 |  | 18 | 0 | 34 | 65 | 0 | 6 | 8 | 38 | 0 | 0 | 0 | 345 | 0 | 203 | 8 | 0 | 50 | 5 | 0 | 43 | 0 | 0 | 8 | 18 | 11 | 33 | 21 | 136 | 96 | 0 | 0 | 0 | 41 | 42 | 53 | 50 | 80 | 0 | 40 | 86 | 0 | 209 | 18 | 0 | 9 | 270 | 16 | 2 | 0 | 0 | 0 | 0 | 87 | 0 | 52 | 0 | 100 | 160 | 10 | 398 | 115 | 17 | 32 | 0 | 30 | 35 | 54 | 0 | 9 | 25 | 400 | 0 | 0 | 0 | 107 | 0 | 17 | 0 | 115 | 35 | 374 | 0 | 0 |  | 904 | 0 | 270 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 304 | 0 | 0 | 70 | 0 | 34 | 0 | 0 | 0 | 1210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 755 | 0 | 0 |  | 6519 | 4258 | 10777 | 3975 | 904 | 2167 | 0 | 1258 | 2303 | 0 | 0 | 34 | 136 | 0 | 0 | 76.01
24:00 | 0 | 0 | 0 | 180 | 0 | 53 | 0 | 404 | 332 |  | 0 | 450 | 291 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 22 | 23 | 20 | 33 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 188 | 0 | 0 | 0 |  | 12 | 0 | 34 | 56 | 0 | 6 | 8 | 38 | 0 | 0 | 0 | 305 | 0 | 183 | 8 | 0 | 50 | 5 | 0 | 10 | 0 | 0 | 8 | 18 | 11 | 33 | 21 | 128 | 93 | 0 | 0 | 0 | 41 | 42 | 51 | 49 | 112 | 0 | 64 | 30 | 0 | 209 | 18 | 0 | 9 | 270 | 16 | 5 | 0 | 0 | 0 | 0 | 48 | 0 | 52 | 0 | 100 | 85 | 10 | 368 | 49 | 17 | 34 | 0 | 30 | 17 | 54 | 0 | 9 | 25 | 400 | 0 | 0 | 0 | 107 | 0 | 17 | 0 | 107 | 35 | 346 | 0 | 0 |  | 905 | 0 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 416 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 1190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 151 | 550 | 0 | 0 |  | 6125 | 4039 | 10164 | 3916 | 905 | 2167 | 0 | 953 | 2061 | 0 | 0 | 34 | 128 | 0 | 0 | 76.01
KWH | 0 | 0 | 0 | 4378500 | 0 | 1580727 | 0 | 9334780 | 7162000 |  | 0 | 8933050 | 6466764 | 171840 | 258518 | 481488 | 3898711 | 0 | 0 | 168960 | 270432 | 206400 | 0 | 0 | 0 | 0 | 372960 | 553585 | 597580 | 312120 | 552000 | 572940 | 834600 | 396500 | 481440 | 0 | 381420 | 112000 | 0 | 0 | 49419 | 4884834 | 0 | 0 | 0 |  | 291120 | 21840 | 286252 | 1038120 | 72000 | 151200 | 177120 | 604320 | 0 | 0 | 0 | 7269000 | 0 | 4455000 | 133818 | 0 | 793584 | 145440 | 0 | 804793 | 0 | 57344 | 588091 | 383328 | 218700 | 633100 | 420340 | 2907840 | 1272000 | 0 | 336060 | 15050 | 970000 | 774360 | 891000 | 887760 | 2425664 | 0 | 1314432 | 1471680 | 0 | 5263840 | 434000 | 0 | 180180 | 6572500 | 363120 | 110880 | 0 | 474218 | 0 | 0 | 1749600 | 0 | 1829232 | 74385 | 1802880 | 2979840 | 322836 | 8546000 | 1782000 | 705706 | 539454 | 31438 | 828000 | 462383 | 1366612 | 25080 | 225960 | 776640 | 9117800 | 490560 | 320550 | 1118880 | 2335964 | 0 | 337680 | 218715 | 1379520 | 594000 | 6991700 | 31781 | 0 |  | 21258181 | 0 | 5382720 | 0 | 85440 | 0 | 0 | 0 | 0 | 0 | 28500 | 3980263 | 406700 | 48192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9327 | 0 | 12096 | 269041 | 269760 | 0 | 200970 | 0 | 0 | 3890800 | 0 | 0 | 3760582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6925090 | 97920 | 0 | 527232 | 49680 | 234748 | 0 | 51590 | 74208 | 20194600 | 0 | 0 | 0 | 34920 | 735840 | 147648 | 0 | 0 | 0 | 230254 | 4058200 | 17959000 | 1333440 | 0 |  | 145607858 | 92256942 | 237864800 | 88333884 | 21258181 | 45861246 | 0 | 28988789 | 46102600 | 493420 | 31781 | 840877 | 2907840 | 3046182 | 0
Fuel Cost | 0 | 0 | 0 | 6523965 | 0 | 2102366.91 | 0 | 9801519 | 7734960 |  | 0 | 9737024.5 | 7178108.04 | 1921171.2 | 3425363.5 | 6379716 | 4366556.32 | 0 | 0 | 2470195.2 | 3804978.24 | 3345744 | 0 | 0 | 0 | 0 | 4744051.2 | 7473397.5 | 8013547.8 | 234090 | 414000 | 0 | 0 | 0 | 8189294.4 | 0 | 102983.4 | 30240 | 0 | 0 | 808000.65 | 5080227.36 | 0 | 0 | 0 |  | 3799116 | 364291.2 | 4872009.04 | 14025001.2 | 912960 | 1749384 | 224942.4 | 2012385.6 | 0 | 0 | 0 | 8068590 | 0 | 5167800 | 172625.22 | 0 | 896749.92 | 216705.6 | 0 | 1344004.31 | 0 | 990330.88 | 7909823.95 | 525159.36 | 164025 | 1107925 | 315255 | 20878291.2 | 1386480 | 0 | 457041.6 | 239897 | 1328900 | 1022155.2 | 1550340 | 1535824.8 | 2789513.6 | 0 | 2549998.08 | 3355430.4 | 0 | 5316478.4 | 933100 | 0 | 356756.4 | 6572500 | 272340 | 84268.8 | 0 | 6473075.7 | 0 | 0 | 23584608 | 0 | 25334863.2 | 869560.65 | 18605721.6 | 40704614.4 | 4284033.72 | 7862320 | 21669120 | 10204508.76 | 6824093.1 | 0 | 9720720 | 5035350.87 | 14527085.56 | 340335.6 | 2912624.4 | 9148819.2 | 8388376 | 6352752 | 4631947.5 | 14198587.2 | 26583270.32 | 0 | 4410100.8 | 2613644.25 | 20651414.4 | 7822980 | 0 | 0 | 0 |  | 63774543 | 0 | 6028646.4 | 0 | 889430.4 | 0 | 0 | 0 | 0 | 0 | 409545 | 4457894.56 | 788998 | 525292.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 154455.12 | 0 | 164868.48 | 4538721.67 | 558403.2 | 0 | 152134.29 | 0 | 0 | 20582332 | 0 | 0 | 4362275.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6855839.1 | 1316044.8 | 0 | 6237154.56 | 717876 | 2981299.6 | 0 | 570069.5 | 900885.12 | 181953346 | 0 | 0 | 0 | 394945.2 | 8631403.2 | 2263443.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 513104426.61 | 320209846.96 | 833314273.57 | 87493212.81 | 63774543 | 54861785.68 | 0 | 371574975.39 | 202535678 | 133223.4 | 0 | 14111096.79 | 20878291.2 | 17951467.3 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 0 | 79 | 0 | 410 | 342 |  | 0 | 450 | 255 | 1 | 2 | 15 | 221 | 0 | 0 | 6 | 5 | 16 | 0 | 0 | 0 | 0 | 35 | 35 | 24 | 19 | 23 | 26 | 33 | 16 | 25 | 0 | 25 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 |  | 12 | 0 | 0 | 44 | 8 | 6 | 8 | 2 | 0 | 0 | 0 | 280 | 0 | 184 | 8 | 0 | 35 | 5 | 0 | 43 | 0 | 0 | 20 | 18 | 11 | 0 | 12 | 130 | 33 | 0 | 16 | 2 | 41 | 21 | 48 | 50 | 112 | 0 | 61 | 88 | 0 | 212 | 18 | 0 | 9 | 260 | 16 | 0 | 0 | 30 | 0 | 0 | 55 | 0 | 52 | 0 | 76 | 159 | 10 | 367 | 107 | 17 | 17 | 3 | 0 | 17 | 67 | 0 | 9 | 80 | 400 | 27 | 31 | 54 | 107 | 0 | 17 | 34 | 36 | 17 | 320 | 0 | 0 |  | 905 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 3 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 254 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 640 | 0 | 0 | 0 | 5 | 102 | 0 | 0 | 0 | 0 | 37 | 152 | 766 | 166 | 0 |  | 10102 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 0 | 81 | 0 | 400 | 332 | 0 | 0 | 450 | 288 | 8 | 30 | 40 | 221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 55 | 22 | 23 | 26 | 33 | 16 | 50 | 0 | 0 | 25 | 0 | 0 | 8 | 213 | 0 | 0 | 0 | 0 | 18 | 0 | 34 | 64 | 3 | 3 | 8 | 38 | 0 | 0 | 0 | 305 | 0 | 181 | 8 | 0 | 50 | 5 | 0 | 43 | 0 | 0 | 52 | 18 | 11 | 33 | 21 | 148 | 59 | 0 | 19 | 0 | 41 | 42 | 53 | 50 | 112 | 0 | 64 | 86 | 0 | 209 | 18 | 0 | 9 | 275 | 16 | 8 | 0 | 15 | 0 | 0 | 173 | 0 | 144 | 0 | 100 | 200 | 10 | 366 | 115 | 51 | 34 | 0 | 48 | 54 | 54 | 0 | 9 | 25 | 400 | 32 | 0 | 54 | 107 | 0 | 17 | 0 | 115 | 35 | 300 | 0 | 0 |  | 792 | 0 | 265 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 171 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 17 | 0 | 113 | 15 | 34 | 0 | 0 | 0 | 1060 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 152 | 752 | 0 | 0 |  | 11412 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 0 | 81 | 0 | 400 | 340 | 0 | 0 | 450 | 285 | 90 | 100 | 55 | 200 | 0 | 0 | 92 | 102 | 150 | 0 | 0 | 0 | 0 | 35 | 35 | 55 | 22 | 23 | 26 | 33 | 33 | 51 | 0 | 25 | 0 | 0 | 0 | 25 | 225 | 0 | 0 | 0 | 0 | 18 | 48 | 65 | 66 | 6 | 20 | 5 | 20 | 0 | 0 | 0 | 300 | 0 | 200 | 8 | 0 | 45 | 5 | 0 | 43 | 0 | 35 | 52 | 18 | 11 | 33 | 21 | 153 | 80 | 0 | 16 | 0 | 41 | 42 | 51 | 50 | 112 | 0 | 65 | 86 | 0 | 210 | 18 | 0 | 10 | 280 | 16 | 8 |  | 300 | 0 | 0 | 180 | 0 | 149 | 0 | 100 | 200 | 150 | 366 | 115 | 105 | 17 | 0 | 230 | 54 | 54 | 114 | 9 | 100 | 400 | 72 | 0 | 162 | 107 | 0 | 17 |  | 115 | 35 | 300 |  |  |  | 909 | 0 | 200 |  | 99 | 0 | 0 | 0 | 50 | 65 | 40 | 170 | 25 | 48 | 0 | 0 | 0 | 32 | 40 | 100 | 0 | 42 | 40 | 34 | 36 | 22 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 180 |  | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 53 | 0 | 113 | 100 | 113 | 0 | 0 | 113 | 1200 | 0 |  | 0 |  |  | 115 | 0 |  | 0 |  | 180 | 700 |  | 0
Forecast for Day | 0 | 0 | 0 | 180 | 0 | 79 | 0 | 400 | 340 | 0 | 0 | 450 | 285 | 75 | 80 | 55 | 170 | 0 | 0 | 92 | 102 | 64 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 22 | 23 | 25 | 33 | 33 | 25 | 0 | 25 | 0 | 0 | 0 | 25 | 225 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 55 | 6 | 20 | 5 | 5 | 0 | 0 | 0 | 280 | 0 | 200 | 8 | 0 | 45 | 5 | 0 | 43 | 0 | 0 | 30 | 18 | 11 | 33 | 18 | 135 | 44 | 0 | 16 | 1.6 | 41 | 42 | 48 | 50 | 112 | 0 | 65 | 86 | 0 | 210 | 18 | 0 | 10 | 280 | 16 | 8 | 0 | 280 | 0 | 0 | 150 | 0 | 115 | 20 | 100 | 160 | 100 | 366 | 115 | 70 | 17 | 5 | 120 | 0 | 54 | 114 | 9 | 100 | 400 | 72 | 50 | 162 | 107 | 0 | 17 | 30 | 36 | 35 | 320 |  |  |  | 909 | 0 | 170 | 0 | 66 | 0 | 0 | 0 | 40 | 40 | 8 | 170 | 20 | 48 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 28 | 22 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 53 | 0 | 50 | 0 | 50 | 0 | 8 | 50 | 900 | 0 |  | 0 | 6 | 100 | 50 | 0 |  | 0 | 30 | 150 | 500 | 130 | 0 |  |  |  |  | g | h | o | c | h | t | s
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 0 | 68 | 0 | 390 | 342 | 0 | 0 | 400 | 285 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 23 | 20 | 33 | 16 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 33 | 0 | 0 | 8 | 18 | 0 | 0 | 0 | 280 | 0 | 185 | 8 | 0 | 46 | 5 | 0 | 23 | 0 | 0 | 0 | 18 | 11 | 33 | 17 | 108 | 44 | 0 | 0 | 1 | 41 | 42 | 48 | 30 | 80 | 0 | 40 | 5 | 0 | 209 | 18 | 0 | 9 | 280 | 16 | 0 | 0 | 0 | 0 | 0 | 47 | 0 | 5 | 0 | 100 | 17 | 0 | 325 | 49 | 0 | 17 | 2 | 0 | 0 | 22 | 0 | 9 | 0 | 400 | 0 | 16 | 0 | 107 | 0 | 0 | 15 | 27 | 35 | 300 | 0 | 0 | 0 | 797 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 22 | 0 | 5 | 0 | 0 | 169 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 600 | 0 | 0 | 0 | 2 | 31 | 0 | 0 | 0 | 0 | 12 | 152 | 512 | 84 | 0 | 0 |  |  |  | 134.1951 | 21.2582 | 29.8614 | 46.1026 | 0.49342 | 2.9078 | 3.0462
237.8648
| Minimum Generation |  | 7408 | 6:00
| Highest Generation |  | 11412 | 21:00
| Day Peak Generation |  | 10102 | 12:00
| Evening Peak Generation |  | 11412 | 21:00
| HVDC Max Flow |  | 905 | 11:00
| HVDC EvPeak Flow |  | 792 | 21:00
| Load factor L.F |  | 86.85% | [161 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2023-04-03
Till now the maximum generation is : - |  |  |  | 14782 | 21:00 | Hrs on | 2022-04-16
The Summary of Yesterday's |  |  | 2023-04-02 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 10102 | MW Hour : | 12:00 | Min. Gen. at | 6:00 | 8001
Evening Peak Generation : |  |  | 11412 | MW Hour : | 21:00 | Available Max Generation : |  | 14121
E.P. Demand (at gen end) : |  |  | 11412 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 12100
Maximum Generation : |  |  | 11412 | MW Hour : | 21:00 | Reserve(Generation end) |  | 2021
Total Gen. (MKWH) : |  |  | 237.8648 | System Load Factor : | 86.85% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 76 | MW at | 19:30 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2023-04-03
Actual : |  | 76.01 | Ft.(MSL) , | Rule curve : | 87.6 | Ft.( MSL )
Gas Consumed : |  | Total = | 1028.65 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 142354998.49
: |  |  | Coal : | 202535678 | Oil : | 385686072.18 | Total : | 730576748.67
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 0 | 0:00 | 3948.8334 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 1090.4778 |  |  | 0 | 0%
Khulna Area |  | 0 | 0:00 | 1432.9418 |  |  | 0 | 0%
Rajshahi Area |  | 0 | 0:00 | 1263.6312 |  |  | 0 | 0%
Cumilla Area |  | 0 | 0:00 | 1079.1812 |  |  | 0 | 0%
Mymensingh Area |  | 0 | 0:00 | 886.6511 |  |  | 0 | 0%
Sylhet Area |  | 0 | 0:00 | 401.0597 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 323.2277 |  |  | 0 | 0%
Rangpur Area |  | 0 | 0:00 | 700.1211 |  |  | 0 | 0%
Total |  | 0 |  | 11126.125 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 1,2
2) Ghorasal-3,7
3) Kushiara 163 MW ST
4) Baghabari-100 MW & 71 MW
5) Raozan unit-1,2
6) Siddhirganj 210 MW .
7) Shajibazar 330 MW
8) Sirajganj-2 & 3
9) Bhula Nuton Biddut
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
09:07 |  | Ashuganj South- Ghorashal 230kV ckt-1 was shutdown.
| 09:19 | Maniknagar 132/33kV S/S Haripur Ckt-2 is restored.
| 09:22 | Haripur 230/132kV S/S Ullon (Maniknagar-2) is restored.
| 09:50 | Maniknagar-Matuail 132kV Ckt-1 is restored.
10:04 | 21:02 | BIPTC S/S Baharampur-3 Scheduled S/D Due to Shutdown is taken from Berhampore substation end for maintenance work.
10:24 | 11:53 | Cumilla(N) 230/132/33kV S/S 132KV T-04 HT Scheduled S/D Due to 33KV Balutopa Feeder BUS Isulator Problem.
10:24 | 11:53 | Cumilla(N) 230/132/33kV S/S 132KV T-04 LT Scheduled S/D Due to 33KV Balutopa Feeder BUS Isulator Problem.
| 11:50 | Chandpur 132/33kV S/S 50MW(ST) Power Plant Incomer(T3) is restored.
12:39 | 13:16 | Khulna(C )-Noapara 132kV Ckt-2 Tripped from Noapara 132/33kV end showing Distance Relay(ZIV Relay) relays Due
to Distance Relay Tripping and from Khulna (C) end showing Distance Relay -22.1km zone-2, B- phase.
14:25 |  | Bibiana 400/230kV S/S Bibiyana-III (Back feed) Tripped showing -General trip-Trafo PROT trip -Power station inter trip relays Due to Inter
trip From power station.
| 17:24 | Bogura(New)-Naogaon 132 kV Ckt-1 is restored.
| 17:37 | Ghorashal-Ashugonj south 230 kV CKT-1 was switched on.
18:26 |  | Bhulta-Rampura 230 kV Ckt-1 Tripped from Bhulta 400/230kV end showing REL670 relays Due to Y-Phase trip, 67N trip,
CR/DTT Received, General Trip and from Rampura 230/132kV end showing Distance z1, ABN relays.
20:22 | 20:29 | Shahjibazar 132/33kV S/S TR-02 LT Tripped showing TR-02 33 kV OC/EF relays Due to Due to shaistaganj feeder fault. | [5 empty] | 25 MW load interrup.
04:46 | 04:57 | Shahjibazar-Sreemangal 132kV Ckt-2 Tripped from Sreemongol 132/33kV end showing distance relay relays Due to heavy
raining and thunder and from Shahjibazar 132/33kV end showing Distance Relay Due to Stormy Wether.
05:35 | 07:54 | Kodda 132/33kV S/S Tr-2 (416T) LT Forced S/D Due to Bus DS Maintenance. | [5 empty] | 15 MW load interrup.
05:35 | 07:49 | Kodda 132/33kV S/S Tr-2 (416T) HT Forced S/D Due to 33kV Bus DS maintenance
06:39 |  | Bogura(New)-Naogaon 132 kV Ckt-1 Project Work S/D from Bogura 230/132kV end.
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2023-04-02 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4378500
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 81 | 1580727 | Engine problem
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 400 | 9334780 | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 332 | 7162000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 8933050
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 8 | 171840 | High Voltage
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 288 | 6466764 | FGMO
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 30 | 258518 | High Voltage
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 40 | 481488 | High Voltage
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 312120
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 0 | 168960 | Reserve.
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 221 | 3898711 | ST U/M.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 270432 | Reserve.
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 17 | 372960 | Engine problem
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 0 | 206400 | Reserve.
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 35 | 553585 | Engine problem
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 597580
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 49 | 1124940 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 834600
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 16 | 396500 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 50 | 481440 | 0:00
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 15 | 474218 | Low demand
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Fuel shortage
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 0 | 0 | Fuel shortage
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Fuel shortage
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 144 | 1829232
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 51 | 705706 | Low demand
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 32 | 490560 | Low demand
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 54 | 1118880 | Low demand
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 218715
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 594000 | Engine problem
| Dhaka area Total |  |  |  | 5847 | 2638 | 53417206
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 8 | 49419 | Low demand
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 74385
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 3 | 151200 | Fuel shortage
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 25 | 493420 | Low Water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 213 | 4884834
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 34 | 539454 | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 21840 | Reserve.
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 34 | 286252 | Low demand
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 64 | 1038120 | Engine problem
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 100 | 1802880
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 8 | 177120 | Gas shortage
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 38 | 604320
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 3 | 72000 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 31438
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 48 | 828000 | Low demand
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 462383
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 54 | 1366612 | Low demand
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 25 | 776640
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 107 | 2335964 | Engine problem
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 31781 | On test.
| Chattogram area Total |  |  |  | 2382 | 818 | 16028062
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 181 | 4455000 | FGMO
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 305 | 7269000 | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | Gas shortage
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 300 | 6991700 | FGMO
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 50 | 793584
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 5 | 145440 | Gas shortage
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 133818 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 804793 | Engine problem
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 10 | 322836 | Low demand
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 57344 | Reserve.
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 200 | 2979840
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 383328 | Engine problem
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 218700
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 148 | 2907840
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 633100
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 588091
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 21 | 420340 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Fuel shortage
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 25080 | Reserve.
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 9 | 225960 | Fuel shortage
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 337680 | Engine problem
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 115 | 1379520
| Cumilla Area Total |  |  |  | 3285 | 1526 | 31072994
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 59 | 1272000 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 336060 | Engine problem
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 15050
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 173 | 1749600 | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 115 | 1782000
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 320550
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 18 | 291120 | Engine problem
| Mymensingh Area Total |  |  |  | 614 | 384 | 5766380
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 41 | 970000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 42 | 774360 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 112 | 2425664 | ST U/M.
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 891000
| Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 50 | 887760
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 8 | 110880 | Engine problem
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 64 | 1314432
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 86 | 1471680
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 209 | 5263840
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 434000
| Sylhet 50MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 363120 | Engine problem
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 275 | 6572500 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 366 | 8546000 | FGMO
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 9 | 180180
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 400 | 9117800
| Sylhet Area Total |  |  |  | 2427 | 1749 | 39323216
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Fuel shortage
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 792 | 21258181
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 16 | 85440 | Low demand
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve.
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel conservation
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve.
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 265 | 5382720 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 8 | 28500 | Low demand
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve.
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 97920 | Fuel shortage
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 15 | 49680 | Transformer O/L
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 735840
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 0 | 0 | 0 | On test.
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 660*2 | 617 | 0 | 0 | On test.
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3001 | 1113 | 27638281
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 16 | 48192 | Line O/L
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 24 | 406700 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 171 | 3980263 | Machine problem
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1060 | 20194600 | Line O/L
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 0 | 0 | Under maint.
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Line O/L
| Barisal 307 MW |  | BCPCL | 307*1 | 307 | 152 | 4058200 | On test.
| Barisal Area Total |  |  |  | 2265 | 1423 | 28687955
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve.
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve.
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contract Expired
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 9327 | Reserve.
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 204 | 3760582
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 420 | 6925090
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 269041 | Reserve.
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 21 | 269760
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 200970
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 12096 | Reserve.
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Reserve.
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Fuel shortage
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 527232
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 74208 | Reserve.
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 34920
| Adani Power Jharkhanda Ltd |  | Import | 0 | 0 | 752 | 17959000 | On test.
| Rajshahi Area Total |  |  |  | 2129 | 1521 | 30042226
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 170 | 3890800 | Machine problem
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 34 | 234748 | Low demand
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 51590
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 36 | 147648 | Low demand
| Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 230254
| Teesta Solar Limited |  | BPCL | 16*12.5 | 0 | 0 | 1333440
| Rangpur Area Total |  |  |  | 750 | 240 | 5888480
| Total |  |  |  | 22700 | 11412 | 237864800
| Eastern Grid Total |  |  |  | 14555 | 7115 | 145607858
| Western Grid Total |  |  |  | 8145 | 4297 | 92256942
| National Grid Total |  |  |  | 22700 | 11412 | 237864800
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2023-04-02
| (a) ENTIRE EASTERN GRID : |  | 7442.2 | MW | (b) ENTIRE WESTERN GRID : |  | 3480.68 | MW
| i) Dhaka area |  | 4075.7 | MW | i) Khulna area |  | 1381 | MW
| ii) Chittagong area |  | 1156.5 | MW | ii) Rajshahi area |  | 1120.8 | MW
| iii) Comilla area |  | 997 | MW | iii) Barisal area |  | 335.88 | MW
| iv) Mymensingh area |  | 877 | MW | iv) Rangpur area |  | 643 | MW
| v) Sylhet area |  | 336 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 10922.88 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 16 | 14:00 | Chhatak | 21 | 19:00 | Kamrangirchar | 53 | 16:00 | Natore | 115 | 21:00 | Shitalakhya | 112 | 12:00
2 | AKSML | 71.8 | 08:00 | Chowmuhani | 152 | 21:00 | Kaptai | 4 | 19:30 | Nawabganj | 34.9 | 19:30 | Sholosohor | 27 | 15:00
3 | Aftabnagar | 28 | 13:00 | Chuadanga | 89 | 21:00 | Kazla | 79 | 00:00 | Netrakona | 94 | 18:00 | Shyampur | 176 | 00:00
4 | Agargaon | 67 | 14:00 | Coxsbazar | 106 | 00:00 | Keranigonj | 60 | 19:30 | New | 69 | 14:00 | Siddhirganj | 104 | 14:00
5 | Agrabad | 54 | 14:00 | Cumilla(N) | 124 | 19:00 | Khagrachori | 28 | 19:00 | Niamatpur | 82 | 19:30 | Sirajganj | 88 | 19:30
6 | Amnura | 67 | 20:00 | Cumilla(S) | 148 | 21:00 | Khulna | 97 | 19:30 | Noapara | 42 | 19:00 | Sonargaon | 84 | 23:00
7 | Ashuganj | 49 | 00:00 | Daudkandi | 140 | 19:00 | Khulshi | 162 | 15:00 | PHP | 4 | 01:00 | Sreemongol | 35 | 00:00
8 | BIPTC | N/A | N/A | Dhaka | 34 | 13:00 | Kishoreganj | 112 | 22:00 | Pabna | 94 | 19:30 | Srinagar | 35.2 | 19:00
9 | BSRM | 111 | 21:00 | Dhamrai | 110 | 12:00 | Kodda | 291 | 14:00 | Palashbari | 85 | 19:00 | Sunamganj | 32 | 21:00
10 | Bagerhat | 75 | 19:30 | Dhanmondi | 119 | 13:00 | Kulaura | 24 | 00:00 | Panchagarh | 42 | 19:00 | Sylhet | 99 | 14:00
11 | Bakulia | 82 | 19:00 | Dohazari | 82 | 18:30 | Kurigram | 46 | 19:30 | Patuakhali | 78 | 21:00 | TK | 18.5 | 00:00
12 | Banani | 38 | 11:00 | Faridpur | 123 | 19:30 | Kushtia | 102 | 19:00 | Payra | 13 | 22:00 | Tangail | 165 | 21:00
13 | Bangabhaban | 18 | 10:00 | Fatullah | 62 | 10:00 | Lalbag | 76 | 13:00 | Postogola | 33 | 23:00 | Thakurgaon | 70 | 19:00
14 | Barapukuria | 43 | 19:00 | Fenchuganj | 26 | 21:00 | Lalmonirhat | 35 | 19:00 | Purbachal | 16 | 16:00 | Tongi | 116 | 11:00
15 | Barguna | 14 | 19:00 | Feni | 109 | 19:00 | Madanganj | 44 | 14:00 | Purbasadipur | 95 | 19:30 | Ullon | 35 | 19:30
16 | Barishal | 90 | 19:00 | GPH | 94 | 00:00 | Madaripur | 77 | 22:00 | Rahanpur_I | 0 | 00:00 | Uttara | 69 | 14:00
17 | Barishal-230 | 68 | 19:00 | Ghorashal | 58 | 22:00 | Madartek | 66 | 21:00 | Rahim | 32 | 00:00 | UttaraNew | 17 | 09:00
18 | Baroaulia | 50 | 00:00 | Goalpara | 36 | 21:00 | Madunaghat | 46 | 19:00 | Rajbari | 52 | 19:30 | Zigatola | 49 | 14:00
19 | Baroirhat | 38 | 19:00 | Gollamari | 32 | 19:00 | Magura | 50 | 19:30 | Rajendrapur | 98 | 16:00
20 | Bashundhara | 135 | 14:00 | Gopalganj | 79.4 | 19:30 | Mahasthangarh | 66 | 03:00 | Rajshahi | 108 | 19:30
21 | BashundharaCement | 0 | 00:00 | Gulshan | 92 | 13:00 | Manikganj | 85 | 19:30 | Rajshahi-230 | 29 | 17:00
22 | Beanibazar | 45 | 18:30 | Halishahar | 75 | 14:00 | Maniknagar | 54 | 14:00 | Ramganj | 94 | 21:00
23 | Benapole | 50 | 19:00 | HaripurSBU | 144 | 13:00 | Matarbari | 37 | 21:00 | Rampur | 29 | 21:00
24 | Bhaluka | 110 | 21:00 | Hasnabad | 77 | 18:00 | Matuail | 62 | 15:00 | Rangamati | 14 | 18:30
25 | Bhandaria | 40 | 21:00 | Hathazari | 50 | 18:30 | Millgate | 74 | 14:00 | Rangpur | 115 | 18:00
26 | Bhangura | 28 | 03:00 | Ishurdi | 51 | 19:30 | Mirpur | 111.5 | 14:00 | Ruppur | 4.6 | 11:00
27 | Bheramara(GK) | 44 | 19:30 | Jaldhaka | 48 | 19:00 | Mirsorai | 3 | 14:00 | SSM | 3 | 00:00
28 | Bhulta | 249 | 00:00 | Jamalpur | 131 | 19:30 | Mithapukur | 26 | 18:00 | Saidpur | 85 | 19:30
29 | Bog-Sherpur | 48 | 03:00 | Jashore | 116 | 19:30 | Modern | 0 | 00:00 | Satkhira | 111 | 19:00
30 | Bogura | 131 | 21:00 | Jhenaidah | 104 | 19:00 | Mogbazar | 108 | 13:00 | Satmasjid | 94 | 18:00
31 | Borhanuddin | 39 | 21:00 | Joydebpur | 146 | 16:00 | Mongla | 28 | 21:00 | Savar | 172 | 15:00
32 | Brahmanbaria | 136 | 19:00 | Joypurhat | 53 | 21:00 | Motijheel | 31 | 14:00 | Shahjadpur | 85 | 10:00
33 | Cantonment | 114 | 14:00 | Juldah | 27 | 07:00 | Munshiganj | 87 | 14:00 | Shahjibazar | 85 | 20:00
34 | Chandpur | 50 | 18:30 | KSRM | 25 | 23:00 | Mymensingh | 178 | 19:30 | Shahmirpur | 36.5 | 00:00
35 | Chandraghona | 24 | 18:30 | Kabirpur | 282 | 12:00 | Naogaon | 88 | 21:00 | Shariatpur | 56 | 19:00
36 | Chapai | 56 | 19:30 | Kachua | 61 | 19:30 | Narail | 47 | 19:00 | Sherpur | 116 | 19:00
37 | Charsaidpur | 41 | 02:00 | Kallyanpur | 78 | 15:00 | Narinda | 64 | 13:00 | Shikalbaha | 29 | 12:00
38 | Chauddagram | 37 | 18:30 | Kalurghat | 30 | 11:00 | Narshingdi | 143 | 23:00 | Shikalbaha-230 | N/A | N/A
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2023-04-02 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 407 | 18:30 | 388 | 00:00 | Kaliakoir | 388 | 04:00 | 382 | 00:00
| Bhulta | 393 | 18:30 | 380 | 10:00 | Madunaghat_I | 408 | 18:30 | 381 | 09:00
| Bibiana | 406 | 18:00 | 395 | 10:00 | Payra | 417 | 06:00 | 409 | 00:00
| BIPTC | 401 | 06:00 | 389 | 11:00 | Rahanpur_I | 418 | 06:00 | 402 | 14:00
| Gopalganj | 420 | 06:00 | 388 | 23:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 235 | 18:30 | 223 | 11:00 | Hasnabad | 235 | 18:30 | 225 | 00:00
| AKSML | 235 | 18:00 | 210 | 00:00 | Hathazari | 237 | 18:00 | 223 | 00:00
| Aminbazar | 234 | 18:30 | 225 | 12:00 | Ishurdi | 234 | 05:00 | 226 | 11:00
| Ashuganj | 237 | 18:30 | 228 | 11:00 | Jhenaidah | 235 | 06:00 | 221 | 13:00
| Baghabari | 231 | 04:00 | 224 | 11:00 | Kaliakoir | 232 | 04:00 | 225 | 00:00
| Barapukuria | 227 | 00:00 | 215 | 17:00 | Keranigonj | 236 | 18:30 | 223 | 11:00
| Barishal | 237 | 06:00 | 228 | 13:00 | Khulna(S) | 242 | 06:00 | 226 | 22:00
| Bheramara | 233 | 06:00 | 222 | 11:00 | Madunaghat_I | 238 | 18:30 | 222 | 09:00
| Bhulta | 236 | 18:30 | 224 | 11:00 | Maniknagar | 233 | 18:30 | 223 | 13:00
| Bibiana | 240 | 05:00 | 234 | 00:00 | Meghnaghat | 239 | 18:30 | 228 | 12:00
| BIPTC | 235 | 06:00 | 223 | 11:00 | Mirsorai | 237 | 18:00 | 220 | 00:00
| Bogura | 228 | 05:00 | 219 | 13:00 | Rajshahi | 233 | 06:00 | 221 | 11:00
| Borhanuddin | 240 | 05:00 | 231 | 13:00 | Rampur | N/A | N/A | N/A | N/A
| BSRM | 238 | 18:30 | 220 | 00:00 | Rampura | 234 | 18:30 | 222 | 12:00
| Cumilla(N) | 235 | 19:00 | 224 | 23:00 | Shikalbaha | 238 | 19:00 | 221 | 00:00
| Fenchuganj | 245 | 19:30 | 237 | 10:00 | Shyampur | 236 | 18:30 | 223 | 11:00
| Ghorashal | N/A | N/A | N/A | N/A | Siddhirganj | 237 | 18:30 | 228 | 00:00
| GPH | 236 | 20:00 | 220 | 06:00 | Sirajgonj | 230 | 06:00 | 224 | 11:00
| Haripur | 232 | 19:00 | 224 | 10:00 | Sreepur | N/A | N/A | N/A | N/A
| 132 kV | KV |  | KV |  | Tongi | 230 | 18:30 | 217 | 13:00
| Aftabnagar | 134 | 03:00 | 126 | 11:00 | Lalbag | 137 | 18:30 | 125 | 12:00
| Agargaon | 136 | 18:30 | 128 | 11:00 | Lalmonirhat | 134 | 00:00 | 123 | 17:00
| Agrabad | 135 | 18:30 | 127 | 00:00 | Madanganj | 138 | 18:30 | 127 | 10:00
| AKS | 134 | 18:00 | 127 | 00:00 | Madaripur | 135 | 06:00 | 128 | 14:00
| Aminbazar | 135 | 18:00 | 128 | 11:00 | Madartek | 135 | 18:30 | 126 | 11:00
| Amnura | 131 | 04:00 | 127 | 12:00 | Madunaghat | 138 | 19:00 | 130 | 00:00
| Ashuganj | 139 | 18:30 | 135 | 00:00 | Magura | 140 | 06:00 | 129 | 19:00
| Bagerhat | 136 | 05:00 | 124 | 21:00 | Mahasthangarh | 134 | 01:00 | 126 | 13:00
| Bakulia | 137 | 18:30 | 127 | 23:00 | Manikganj | 137 | 18:30 | 127 | 10:00
| Banani | 135 | 18:30 | 126 | 14:00 | Maniknagar | 135 | 18:30 | 128 | 11:00
| Bangabhaban | 133 | 08:00 | 128 | 11:00 | Matarbari | 134 | 07:00 | 114 | 23:00
| Barapukuria | 138 | 00:00 | 129 | 17:00 | Matuail | 137 | 18:30 | 129 | 00:00
| Barguna | 130 | 05:00 | 125 | 20:00 | Millgate | 136 | 18:30 | 126 | 10:00
| Barishal | 134 | 05:00 | 127 | 14:00 | Mirpur | 135 | 18:30 | 127 | 23:00
| Barishal-230 | 135 | 06:00 | 129 | 13:00 | Mithapukur | 135 | 01:00 | 124 | 17:00
| Baroaulia | 140 | 19:00 | 128 | 00:00 | Modern | 137 | 18:30 | 126 | 09:00
| Baroirhat | 133 | 19:00 | 127 | 00:00 | Mogbazar | 136 | 18:30 | 128 | 15:00
| Bashundhara | 135 | 04:00 | 126 | 10:00 | Mongla | 133 | 05:00 | 124 | 21:00
| BashundharaCement | 138 | 18:30 | 121 | 22:00 | Motijheel | 133 | 06:00 | 128 | 11:00
| Beanibazar | 136 | 05:00 | 132 | 00:00 | Munshiganj | 137 | 18:30 | 127 | 08:00
| Benapole | 137 | 06:00 | 124 | 13:00 | Mymensingh | 136 | 18:30 | 117 | 20:00
| Bhaluka | 131 | 18:30 | 115 | 20:00 | Naogaon | 133 | 05:00 | 120 | 09:00
| Bhandaria | 134 | 06:00 | 124 | 21:00 | Narail | 138 | 05:00 | 126 | 19:00
| Bhangura | 138 | 02:00 | 132 | 11:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bheramara | 137 | 06:00 | 131 | 13:00 | Narshingdi | 135 | 18:30 | 130 | 02:00
| Bheramara(GK) | 138 | 04:00 | 134 | 10:00 | Natore | 135 | 06:00 | 127 | 12:00
| Bhulta | 130 | 18:30 | 120 | 00:00 | Nawabganj | 135 | 18:30 | 127 | 11:00
| Bog-Sherpur | 136 | 06:00 | 128 | 12:00 | Netrakona | 131 | 04:00 | 121 | 14:00
| Bogura | 136 | 05:00 | 127 | 12:00 | New | 137 | 18:00 | 126 | 11:00
| Bogura-230 | 135 | 05:00 | 127 | 17:00 | Niamatpur | 130 | 03:00 | 116 | 09:00
| Brahmanbaria | 134 | 03:00 | 130 | 00:00 | Noapara | 137 | 05:00 | 127 | 21:00
| Cantonment | 135 | 18:30 | 127 | 11:00 | Pabna | 136 | 05:00 | 129 | 13:00
| Chandpur | 139 | 17:00 | 130 | 00:00 | Palashbari | 132 | 02:00 | 122 | 17:00
| Chandraghona | 138 | 19:30 | 129 | 00:00 | Panchagarh | 135 | 18:30 | 121 | 17:00
| Chapai | 135 | 06:00 | 128 | 10:00 | Patuakhali | 130 | 05:00 | 125 | 22:00
| Charsaidpur | 137 | 18:30 | 128 | 11:00 | Payra | 130 | 04:00 | 127 | 20:00
| Chauddagram | 136 | 19:30 | 128 | 23:00 | PHP | 134 | 18:30 | 125 | 00:00
| Chhatak | 135 | 04:00 | 132 | 00:00 | Postogola | 137 | 18:30 | 128 | 10:00
| Chowmuhani | 131 | 12:00 | 125 | 00:00 | Purbachal | 136 | 18:00 | 127 | 11:00
| Chuadanga | 138 | 05:00 | 124 | 22:00 | Purbasadipur | 132 | 00:00 | 118 | 16:00
| Coxsbazar | 130 | 08:00 | 113 | 23:00 | Rahim | 136 | 19:00 | 120 | 10:00
| Cumilla(N) | 139 | 19:30 | 130 | 23:00 | Rajbari | 134 | 06:00 | 127 | 13:00
| Cumilla(S) | 137 | 18:30 | 127 | 15:00 | Rajendrapur | 137 | 18:30 | 125 | 11:00
| Daudkandi | 136 | 19:30 | 127 | 23:00 | Rajshahi | 134 | 06:00 | 127 | 11:00
| Dhaka | 135 | 18:30 | 127 | 11:00 | Rajshahi-230 | 134 | 05:00 | 126 | 12:00
| Dhamrai | 135 | 18:30 | 125 | 10:00 | Ramganj | 134 | 12:00 | 126 | 23:00
| Dhanmondi | 137 | 18:30 | 129 | 10:00 | Rampur | 135 | 19:30 | 125 | 14:00
| Dohazari | 133 | 19:00 | 125 | 00:00 | Rampura | 135 | 18:30 | 126 | 12:00
| Faridpur | 133 | 04:00 | 128 | 13:00 | Rangamati | 137 | 19:30 | 128 | 00:00
| Fatullah | 137 | 18:30 | 128 | 10:00 | Rangpur | 136 | 01:00 | 122 | 17:00
| Fenchuganj | 139 | 19:00 | 135 | 10:00 | Ruppur | 137 | 06:00 | 131 | 13:00
| Feni | 135 | 07:00 | 126 | 23:00 | Saidpur | 136 | 06:00 | 122 | 17:00
| Ghorashal | 137 | 01:00 | 133 | 21:00 | Satkhira | 137 | 06:00 | 124 | 22:00
| Goalpara | 138 | 06:00 | 128 | 13:00 | Satmasjid | 136 | 18:30 | 127 | 13:00
| Gollamari | 133 | 04:00 | 127 | 22:00 | Savar | 136 | 18:30 | 126 | 09:00
| Gopalganj | 133 | 04:00 | 126 | 13:00 | Shahjadpur | 143 | 00:00 | 134 | 10:00
| Gopalganj-400 | 134 | 05:00 | 129 | 15:00 | Shahjibazar | 137 | 18:30 | 132 | 09:00
| Gulshan | 134 | 18:30 | 127 | 11:00 | Shahmirpur | 138 | 18:00 | 128 | 00:00
| Halishahar | 137 | 19:00 | 128 | 00:00 | Shariatpur | 135 | 05:00 | 128 | 00:00
| Haripur | 136 | 19:00 | 130 | 16:00 | Sherpur | 139 | 02:00 | 124 | 10:00
| HaripurSBU | 136 | 19:00 | 130 | 00:00 | Shikalbaha | 139 | 18:30 | 127 | 00:00
| Hasnabad | 134 | 19:30 | 128 | 10:00 | Shikalbaha-230 | 137 | 19:30 | 126 | 00:00
| Hathazari | 140 | 18:30 | 130 | 00:00 | Shitalakhya | 137 | 18:30 | 128 | 00:00
| Ishurdi | 137 | 05:00 | 132 | 11:00 | Sholosohor | 137 | 19:30 | 128 | 00:00
| Jaldhaka | 135 | 00:00 | 120 | 17:00 | Shyampur | 137 | 18:30 | 127 | 11:00
| Jamalpur | 140 | 02:00 | 126 | 07:00 | Shyampur-230 | 136 | 18:30 | 122 | 05:00
| Jashore | 136 | 03:00 | 125 | 22:00 | Siddhirganj | 137 | 18:30 | 129 | 11:00
| Jhenaidah | 141 | 06:00 | 131 | 15:00 | Sirajganj | 136 | 05:00 | 128 | 13:00
| Jhenaidah-230 | 140 | 06:00 | 130 | 22:00 | Sonargaon | 132 | 18:30 | 129 | 00:00
| Joydebpur | 141 | 19:30 | 129 | 10:00 | Sreemongol | 135 | 18:00 | 133 | 00:00
| Joypurhat | 131 | 06:00 | 118 | 09:00 | Sreepur | N/A | N/A | N/A | N/A
| Juldah | 136 | 19:00 | 128 | 00:00 | Srinagar | 135 | 18:30 | 127 | 12:00
| Kabirpur | 138 | 18:30 | 124 | 11:00 | SSM | 141 | 18:00 | 130 | 09:00
| Kachua | 139 | 19:30 | 129 | 00:00 | Sunamganj | 134 | 04:00 | 131 | 00:00
| Kaliakoir | 140 | 04:00 | 130 | 00:00 | Sylhet | 135 | 03:00 | 133 | 15:00
| Kallyanpur | 136 | 18:30 | 128 | 12:00 | Tangail | 135 | 02:00 | 128 | 07:00
| Kalurghat | 138 | 19:30 | 129 | 23:00 | Thakurgaon | 132 | 00:00 | 118 | 17:00
| Kamrangirchar | 133 | 04:00 | 127 | 13:00 | TK | 138 | 19:00 | 127 | 10:00
| Kaptai | 134 | 13:00 | 132 | 00:00 | Tongi | 137 | 18:30 | 129 | 11:00
| Kazla | 135 | 18:30 | 127 | 13:00 | Ullon | 133 | 03:00 | 126 | 13:00
| Keranigonj | 136 | 18:30 | 128 | 00:00 | Uttara | 137 | 18:30 | 127 | 23:00
| Khagrachori | 136 | 18:30 | 126 | 00:00 | UttaraNew | 137 | 18:30 | 127 | 23:00
| Khulna | 137 | 05:00 | 128 | 19:00 | Zigatola | 134 | 18:30 | 126 | 13:00
| Khulna(S) | 139 | 06:00 | 129 | 21:00
| Khulshi | 136 | 03:00 | 126 | 09:00
| Kishoreganj | 134 | 06:00 | 127 | 14:00
| Kodda | 139 | 18:30 | 127 | 10:00
| KSRM | 137 | 18:00 | 129 | 11:00
| Kulaura | 138 | 05:00 | 135 | 16:00
| Kurigram | 135 | 00:00 | 120 | 17:00
| Kushtia | 139 | 06:00 | 131 | 15:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2023-04-02
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 800 | 6125 | 4039 | 10164 |  |  |  | QF-LDC-11
0:30 | 1052 | 5675 | 3871.5 | 9546.5 | Date: | 2023-04-02
1:00 | 1304 | 5225 | 3704 | 8929
1:30 | 1302 | 5193.5 | 3626.5 | 8820
2:00 | 1300 | 5162 | 3549 | 8711
2:30 | 1210 | 5275 | 3590.5 | 8865.5 | [5 empty] | Gen. at Eve. Peak | 11412 | 11412 MW (21:00 )
3:00 | 1120 | 5388 | 3632 | 9020 | [6 empty] | 21:00
3:30 | 1095 | 5403.5 | 3667.5 | 9071 | [5 empty] | Gen. at Day Peak | 10102 | 10102 MW (12:00 )
4:00 | 1070 | 5419 | 3703 | 9122 | [6 empty] | 12:00
4:30 | 1110 | 5006.5 | 3501 | 8507.5 | [5 empty] | Highest Generation | 11412
5:00 | 1150 | 4594 | 3299 | 7893 | [6 empty] | 21:00
5:30 | 1195 | 4435.5 | 3215 | 7650.5
6:00 | 1240 | 4277 | 3131 | 7408
6:30 | 1220 | 4278 | 3226.5 | 7504.5
7:00 | 1200 | 4279 | 3322 | 7601
7:30 | 1195 | 4420.5 | 3380 | 7800.5
8:00 | 1190 | 4562 | 3438 | 8000
8:30 | 1145 | 4953 | 3450 | 8403
9:00 | 1100 | 5344 | 3462 | 8806
9:30 | 1115 | 5577.5 | 3527.5 | 9105
10:00 | 1130 | 5811 | 3593 | 9404
10:30 | 1105 | 5962.5 | 3578 | 9540.5
11:00 | 1080 | 6114 | 3563 | 9677
11:30 | 1050 | 6251.5 | 3638 | 9889.5
12:00 | 1020 | 6389 | 3713 | 10102
12:30 | 935 | 6478 | 3786.5 | 10264.5
13:00 | 850 | 6567 | 3860 | 10427
13:30 | 840 | 6695 | 3896.5 | 10591.5
14:00 | 830 | 6823 | 3933 | 10756
14:30 | 820 | 6885.5 | 3866.5 | 10752
15:00 | 810 | 6948 | 3800 | 10748
15:30 | 735 | 6877 | 3715.5 | 10592.5
16:00 | 660 | 6806 | 3631 | 10437
16:30 | 505 | 6789.5 | 3638 | 10427.5
17:00 | 350 | 6773 | 3645 | 10418
17:30 | 340 | 6825.5 | 3604 | 10429.5
18:00 | 330 | 6878 | 3563 | 10441
18:30 | 260 | 7033.5 | 3652.5 | 10686
19:00 | 190 | 7189 | 3742 | 10931
19:30 | 76 | 7401 | 4003 | 11404
20:00 | 170 | 7156 | 3889 | 11045 |  |  |  | Executive Engineer
20:30 | 320 | 7135.5 | 4093 | 11228.5 |  |  |  | Network Operation Division
21:00 | 470 | 7115 | 4297 | 11412
21:30 | 565 | 7033.5 | 4297 | 11330.5
22:00 | 660 | 6952 | 4297 | 11249 |  |  |  |  | Page 6 of 7
22:30 | 725 | 6735.5 | 4277.5 | 11013
23:00 | 790 | 6519 | 4258 | 10777
23:30 | 795 | 6322 | 4148.5 | 10470.5
24:00 | 800 | 6125 | 4039 | 10164
11412 MW (21:00 )
10102 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2023-04-02 |  | Energy |  | 237864800
[13 empty] | 2023-04-02 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 3916 | 905 | 2167 | 0 | 953 | 2061 | 0 | 0 | 34 | 128 | 0 | 0
0:30 | 3724 | 904.5 | 1926 | 0 | 803.5 | 2032.5 | 12.5 | 0 | 25.5 | 118 | 0 | 0 |  | Date: | 43556
1:00 | 3532 | 904 | 1685 | 0 | 654 | 2004 | 25 | 0 | 17 | 108 | 0 | 0
1:30 | 3515 | 904 | 1668.5 | 0 | 646.5 | 1937 | 25 | 0 | 17 | 107 | 0 | 0 | [7 empty] | Total Energy | 237.8648 | Total Energy Gen MKWHr Energy Not Served MKWHr Energy Requirement MKWHr | Total Energy Gen 237.865 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 237.865 MKWHr
2:00 | 3498 | 904 | 1652 | 0 | 639 | 1870 | 25 | 0 | 17 | 106 | 0 | 0 | [7 empty] | Energy not Served | 0
2:30 | 3540 | 904 | 1777 | 0 | 624.5 | 1875 | 25 | 0 | 17 | 103 | 0 | 0 | [7 empty] | Energy Requirement | 237.8648
3:00 | 3582 | 904 | 1902 | 0 | 610 | 1880 | 25 | 0 | 17 | 100 | 0 | 0
3:30 | 3585.5 | 904 | 1906 | 0 | 637.5 | 1890 | 25 | 0 | 17 | 106 | 0 | 0
4:00 | 3589 | 904 | 1910 | 0 | 665 | 1900 | 25 | 0 | 17 | 112 | 0 | 0
4:30 | 3441 | 904 | 1715 | 0 | 540 | 1769 | 25 | 0 | 8.5 | 105 | 0 | 0
5:00 | 3293 | 904 | 1520 | 0 | 415 | 1638 | 25 | 0 | 0 | 98 | 0 | 0
5:30 | 3230.5 | 876 | 1533.5 | 0 | 335.5 | 1555 | 25 | 0 | 0 | 95 | 0 | 0
6:00 | 3168 | 848 | 1547 | 0 | 256 | 1472 | 25 | 0 | 0 | 92 | 0 | 0
6:30 | 3165.5 | 848 | 1545.5 | 0 | 255 | 1545.5 | 25 | 0 | 0 | 91 | 29 | 0 | [6 empty] | Coal
7:00 | 3163 | 848 | 1544 | 0 | 254 | 1619 | 25 | 0 | 0 | 90 | 58 | 0
7:30 | 3193 | 845.5 | 1577 | 0 | 309 | 1636 | 25 | 0 | 8 | 95 | 112 | 0 | [5 empty] | Oil
8:00 | 3223 | 843 | 1610 | 0 | 364 | 1653 | 25 | 0 | 16 | 100 | 166 | 0
8:30 | 3403.5 | 849.5 | 1685 | 0 | 461.5 | 1668 | 25 | 0 | 16 | 102 | 192.5 | 0
9:00 | 3584 | 856 | 1760 | 0 | 559 | 1683 | 25 | 0 | 16 | 104 | 219 | 0
9:30 | 3573.5 | 856.5 | 1892 | 0 | 649.5 | 1685 | 25 | 0 | 16 | 111 | 296.5 | 0
10:00 | 3563 | 857 | 2024 | 0 | 740 | 1687 | 25 | 0 | 16 | 118 | 374 | 0
10:30 | 3584.5 | 881 | 2023.5 | 0 | 863 | 1674 | 25 | 0 | 16 | 125 | 348.5 | 0
11:00 | 3606 | 905 | 2023 | 0 | 986 | 1661 | 25 | 0 | 16 | 132 | 323 | 0
11:30 | 3652.5 | 905 | 2020.5 | 0 | 1089 | 1684.5 | 25 | 0 | 27.5 | 131 | 354.5 | 0
12:00 | 3699 | 905 | 2018 | 0 | 1192 | 1708 | 25 | 0 | 39 | 130 | 386 | 0
12:30 | 3718 | 904.5 | 1997.5 | 0 | 1293.5 | 1744.5 | 25 | 9 | 45.5 | 133 | 394 | 0
13:00 | 3737 | 904 | 1977 | 0 | 1395 | 1781 | 25 | 18 | 52 | 136 | 402 | 0
13:30 | 3737 | 904 | 1977 | 0 | 1395 | 1781 | 25 | 18 | 52 | 136 | 402 | 0
14:00 | 3737 | 904 | 1977 | 0 | 1395 | 1781 | 25 | 18 | 52 | 136 | 402 | 0
14:30 | 3711.5 | 903.5 | 2007.5 | 0 | 1568.5 | 1802.5 | 25 | 12.5 | 52 | 138 | 366.5 | 0
15:00 | 3686 | 903 | 2038 | 0 | 1742 | 1824 | 25 | 7 | 52 | 140 | 331 | 0
15:30 | 3728.5 | 903.5 | 2027.5 | 0 | 1656.5 | 1804 | 12.5 | 9 | 51.5 | 134 | 265.5 | 0
16:00 | 3771 | 904 | 2017 | 0 | 1571 | 1784 | 0 | 11 | 51 | 128 | 200 | 0
16:30 | 3751.5 | 904 | 2057.5 | 0 | 1599.5 | 1785.5 | 0 | 5.5 | 50.5 | 127 | 146.5 | 0
17:00 | 3732 | 904 | 2098 | 0 | 1628 | 1787 | 0 | 0 | 50 | 126 | 93 | 0
17:30 | 3710.5 | 904 | 2024.5 | 0 | 1810.5 | 1733.5 | 12.5 | 0 | 49 | 134 | 51 | 0
18:00 | 3689 | 904 | 1951 | 0 | 1993 | 1680 | 25 | 0 | 48 | 142 | 9 | 0
18:30 | 3597.5 | 904 | 2010.5 | 0 | 2194.5 | 1702 | 25 | 0 | 105 | 143 | 4.5 | 0
19:00 | 3506 | 904 | 2070 | 0 | 2396 | 1724 | 25 | 0 | 162 | 144 | 0 | 0
19:30 | 3702 | 791 | 2103 | 0 | 2553 | 1942 | 25 | 0 | 152 | 136 | 0 | 0
20:00 | 3753 | 792 | 2132 | 0 | 2194 | 1905 | 25 | 0 | 106 | 138 | 0 | 0
20:30 | 3853.5 | 792 | 2213.5 | 0 | 2112 | 2019.5 | 25 | 0 | 70 | 143 | 0 | 0
21:00 | 3954 | 792 | 2295 | 0 | 2030 | 2134 | 25 | 0 | 34 | 148 | 0 | 0
21:30 | 3973.5 | 848 | 2228.5 | 0 | 1880.5 | 2196 | 25 | 0 | 34 | 145 | 0 | 0
22:00 | 3993 | 904 | 2162 | 0 | 1731 | 2258 | 25 | 0 | 34 | 142 | 0 | 0
22:30 | 3984 | 904 | 2164.5 | 0 | 1494.5 | 2280.5 | 12.5 | 0 | 34 | 139 | 0 | 0
23:00 | 3975 | 904 | 2167 | 0 | 1258 | 2303 | 0 | 0 | 34 | 136 | 0 | 0
23:30 | 3945.5 | 904.5 | 2167 | 0 | 1105.5 | 2182 | 0 | 0 | 34 | 132 | 0 | 0 |  | Max Temp. in Dhaka |  | 32.0° C
24:00 | 3916 | 905 | 2167 | 0 | 953 | 2061 | 0 | 0 | 34 | 128 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 237.865 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 237.865 MKWHr
Note on W13: Author:

## Generation
g | 2023-04-02
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 0 | [10 empty] | 381420
2 | Karnaphuli Hydro PP Unit-4 & 5 | [16 empty] | 0 | 25 |  | 25 | 25 | 25 | 25 | 25 | 0 |  | 112000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [19 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 49419
| Teknaf 20MW PP (Solartech) | [8 empty] | 14 | 11 | 14 |  | 9 | 7 | 5 | 5 | 2 | 0 | [8 empty] | 74385
6 | Sikalbaha 225MW CCPP (Gas) | 176 | 177 | 176 | 172 | 171 | 172 | 172 | 173 | 201 | 199 | 224 | 224 | 224 | 224 | 222 | 222 | 223 | 225 |  | 226 | 229 | 225 | 213 | 215 | 200 | 188 | 4884834
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 17 | 17 | 17 | 17 | [15 empty] | 51 | 51 | 51 | 34 | 34 | 34 | 34 | 286252
12 | Hathazari 100 MW peaking PP | [19 empty] | 36 | 18 | 0 |  |  |  |  | 21840
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 21 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 30 |  | 34 | 34 | 34 | 34 | 34 | 32 | 34 | 539454
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP | [19 empty] | 25 | 38 | 39 | 0 |  |  |  | 57344
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 136 | 145 | 150 | 160 | 130 | 80 | 80 | 80 | 140 | 140 | 140 | 221 | 215 | 216 | 160 | 160 | 214 | 214 |  | 88 | 88 | 100 | 221 | 220 | 170 | 219 | 3898711
18 | Kodda 300 MW PP Unit-2 (Summit) | [9 empty] | 12 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 42 |  | 95 | 95 | 15 | 15 | 0 |  |  | 474218
19 | Ashuganj 195MW PP (APSCL-United) | [10 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 133818
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4378500
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 50 | 25 | 25 | 25 | 10 | 10 | 10 | 10 | 10 | 10 | 20 | 35 | 35 | 39 | 46 | 45 | 45 | 47 |  | 47 | 49 | 49 | 50 | 50 | 50 | 50 | 793584
33 | Ashuganj 225 MW CCPP | 181 | 181 | 181 | 181 | 182 | 153 | 152 | 184 | 192 | 184 | 182 | 184 | 200 | 182 | 181 | 202 | 180 | 179 |  | 180 | 182 | 182 | 181 | 182 | 203 | 183 | 4455000
34 | Ashuganj 450 MW CCPP(South)
| Ashuganj 450 MW CCPP(North) | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 275 | 285 | 280 | 280 | 280 | 290 | 280 | 280 | 315 | 280 | 300 |  | 280 | 280 | 280 | 305 | 310 | 345 | 305 | 7269000
| Ashuganj 420 MW CCPP(East) | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 320 | 320 | 320 | 320 | 320 | 320 | 321 | 345 | 300 | 250 |  | 270 | 270 | 270 | 300 | 352 | 374 | 346 | 6991700
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 145440
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 374 | 383 | 394 | 386 | 345 | 301 | 301 | 325 | 399 | 409 | 408 | 410 | 408 | 409 | 410 | 407 | 408 | 403 |  | 337 | 400 | 398 | 400 | 399 | 398 | 404 | 9334780
40 | Meghnaghat 450 MW CCPP(MPL) | 360 | 370 | 380 | 330 | 300 | 300 | 300 | 300 | 340 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 |  | 400 | 400 | 400 | 450 | 450 | 450 | 450 | 8933050
41 | Haripur 360MW CCPP(HPL) | 262 | 262 | 272 | 272 | 292 | 263 | 263 | 262 | 282 | 352 | 342 | 342 | 211 | 254 | 341 | 346 | 332 | 302 |  | 352 | 342 | 341 | 332 | 333 | 333 | 332 | 7162000
42 | RPCL 210MW CCPP | 84 | 84 | 83 | 72 | 72 | 74 | 36 | 35 | 35 | 35 | 35 | 33 | 33 | 33 | 33 | 33 | 30 | 30 |  | 33 | 49 | 50 | 59 | 102 | 96 | 93 | 1272000
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 0 | 8 | 20 | 14 | 43 | 53 | 31 | 17 | 11 | 39 | 20 | 10 | 1 |  | 0 | [6 empty] | 320550
44 | Fenchugonj CCPP Phase-1 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 |  | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 970000
45 | Fenchugonj CCPP Phase-2 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 20 | 21 | 20 | 42 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 774360
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 40 | 40 | 64 | 64 | 40 | 40 | 40 | 40 | 40 | 61 | 60 | 61 | 60 | 62 | 60 | 60 | 60 | 40 |  | 64 | 65 | 64 | 64 | 65 | 40 | 64 | 1314432
48 | Shahjibazar 86MW PP (Shahjibazar) | 20 | 20 | 60 | 60 | 10 | 10 | 10 | 10 | 40 | 86 | 89 | 88 | 84 | 82 | 82 | 84 | 84 | 86 |  | 86 | 86 | 86 | 86 | 86 | 86 | 30 | 1471680
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 212 | 212 | 213 | 212 | 211 | 210 | 211 | 211 | 212 | 211 | 212 | 212 | 212 | 207 | 210 | 210 | 210 | 210 |  | 216 | 216 | 216 | 209 | 209 | 209 | 209 | 5263840
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 19 | 19 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 434000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 9 | 10 | 10 | 10 |  |  |  | 9 | 9 | 9 | 9 | 9 | 8 | 8 | 8 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 180180
54 | Hobiganj 11MW PP Cofidence-E | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  |  |  | 3 | 3 | 3 | 3 | 3 | 5 |  | 8 | 8 | 8 | 8 | 8 | 2 | 5 | 110880
55 | Fenchugonj 51 MW PP (Barakatullah) | 11 | 11 | 44 | 51 | 5 | 5 | 5 | 5 | 22 | 48 | 49 | 48 | 51 | 51 | 51 | 53 | 53 | 22 |  | 32 | 48 | 53 | 53 | 53 | 53 | 51 | 891000
56 | Shahjahanulla 25 MW PP | 8 | 8 | 8 | 8 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 363120
57 | Bibiana-II 341 MW CCPP (Summit) | 260 | 265 | 270 | 270 | 255 | 250 | 265 | 280 | 280 | 270 | 260 | 260 | 275 | 260 | 270 | 275 | 270 | 275 |  | 280 | 275 | 270 | 275 | 280 | 270 | 270 | 6572500
| Bibiyana South 400 MW | 360 | 360 | 400 | 380 | 310 | 310 | 350 | 350 | 400 | 400 | 400 | 400 | 400 | 400 | 395 | 400 | 400 | 400 |  | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 9117800
58 | Nababganj 55 MW PP (Southern power ) | [10 empty] | 8 | 24 | 41 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 0 |  | 597580
59 | Tangail Palli Power Gen 22 MW | 10 | 12 | 12 | 12 |  |  |  | 1 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 17 |  | 18 | 18 | 18 | 18 | 18 | 18 | 12 | 291120
60 | Barabkunda 22 MW PP (Regent) | 7 | 7 | 7 | 7 | 7 | 7 | 5 | 7 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 177120
61 | Narshingdi 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | [6 empty] | 19 | 19 | 19 | 19 | 7 | 15 | 22 | 22 |  | 0 | 0 | 22 | 22 | 22 | 22 | 22 | 312120
62 | Tangail 22 MW PP (Doreen) | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 19 | 16 | 16 | 16 | 19 | 19 | 19 | 19 | 16 | 16 |  | 16 | 19 | 19 | 19 |  |  |  | 336060
63 | Impoprt (Tripura) | 108 | 106 | 100 | 112 | 98 | 92 | 90 | 100 | 104 | 118 | 132 | 130 | 136 | 136 | 140 | 128 | 126 | 142 |  | 144 | 136 | 138 | 148 | 142 | 136 | 128 | 2907840
64 | Malancha, Ctg. EPZ (United) | 40 | 41 | 41 | 41 | 41 | 41 | 25 | 18 | 18 | 4 | 6 | 2 | 8 | 2 | 2 | 3 | 12 | 24 |  | 35 | 35 | 38 | 38 | 38 | 38 | 38 | 604320
65 | Feni 22MW PP (Doreen) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 13 | 15 |  | 0 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 383328
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 8 |  |  | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 218700
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 |  |  |  |  | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 633100
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 19 | 12 | 12 |  | 15 | 12 | 12 | 12 | 18 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 420340
69 | Summit Ashulia | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 |  | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 552000
70 | Summit Madhabdi | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 24 | 24 |  | 16 | 26 | 26 | 26 | 26 | 25 | 20 | 572940
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 834600
72 | Rupganj 33 MW PP(Summit) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 8 | 8 | 16 | 16 | 16 | 16 | 16 | 396500
73 | Ghorashal 108MW PP (Regent) | 55 | 53 | 81 | 81 | 22 | 22 | 22 | 22 | 67 | 75 | 75 | 79 | 80 | 80 | 80 | 80 | 81 | 81 |  | 81 | 81 | 81 | 81 | 81 | 81 | 53 | 1580727
| Feni Lanka Power | [19 empty] | 17 | 17 | 0 |  |  |  |  | 25080
| Chowmuhani 113 MW | 9 | 9 | 9 | 9 | 9 | 9 | 8 | 9 | 9 | 5 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 225960
| Manikgonj 162MW PP(MPGL) | [7 empty] | 4 | 17 | 54 | 72 | 54 | 90 | 108 | 108 | 108 | 108 | 108 |  | 108 | 108 | 72 | 54 | 35 | 0 |  | 1118880
77 | Siddhirganj 100 PP(Dutch Bangla) | [11 empty] | 6 | 9 | 30 | 20 | 8 | 8 | 21 |  | 40 | 40 | 30 | 0 |  |  |  | 168960
78 | Gazipur 52 MW PP | [7 empty] | 3 | 16 | 25 | 25 | 25 | 25 | 25 | 34 | 40 | 50 | 50 |  | 3 | 33 | 35 | 50 | 33 | 16 | 16 | 481440
79 | Kodda 150 MW PP | [7 empty] | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 0 |  |  |  | 206400
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | [7 empty] | 1 | 8 | 8 | 8 | 20 | 52 | 41 | 42 | 50 | 52 | 52 |  | 52 | 52 | 52 | 52 | 52 | 8 | 8 | 588091
| Gazipur 100 MW PP | [8 empty] | 25 | 17 | 17 | 17 | 17 | 22 | 46 | 52 | 52 | 62 |  | 105 | 105 | 70 | 51 | 34 | 17 | 17 | 705706
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 1 | 3 | 4 | 5 | 3 | 3 | 4 | 3 | 2 | 1 | 0 | [8 empty] | 31438
| Jodiac Power | [8 empty] | 16 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 27 |  | 54 | 54 | 54 | 54 | 35 | 35 | 17 | 462383
| Karnaphuli Power Ltd. | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 61 | 67 | 66 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1366612
82 | Madanganj 102 PP(Summit) | [11 empty] | 2 | 17 | 24 | 51 | 20 | 17 | 20 |  | 51 | 51 | 46 | 30 | 8 | 0 |  | 258518
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP ( Summit) | 222 | 236 | 254 | 257 | 228 | 245 | 244 | 270 | 295 | 280 | 288 | 255 | 290 | 275 | 277 | 290 | 292 | 285 |  | 282 | 260 | 285 | 288 | 266 | 313 | 291 | 6466764
87 | Meghnaghat 100 MW(IEL) | [11 empty] | 1 | 8 | 25 | 24 | 8 | 8 | 18 |  | 42 | 41 | 33 | 8 | 0 |  |  | 171840
| Meghnaghat 104 MW PP (OPCL) | [9 empty] | 1 | 16 | 27 | 48 | 66 | 60 | 34 | 17 | 35 |  | 35 | 35 | 35 | 32 | 17 | 0 |  | 490560
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 52 | 52 | 55 | 55 | 10 | 10 | 10 | 10 | 10 | 36 | 44 | 44 | 44 | 44 | 44 | 46 | 47 | 60 |  | 60 | 60 | 62 | 64 | 65 | 65 | 56 | 1038120
92 | Fenchuganj 44MW (Energyprima) | 50 | 10 | 20 | 47 | 5 | 5 | 5 | 5 | 20 | 44 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 20 |  | 35 | 50 | 50 | 50 | 50 | 50 | 49 | 887760
93 | Ashuganj 51 MW PP (Midland) | 30 | 30 | 36 | 43 | 5 | 5 | 5 | 5 | 5 | 25 | 43 | 43 | 43 | 43 | 5 | 5 | 5 | 5 |  | 16 | 43 | 43 | 43 | 43 | 43 | 10 | 804793
94 | Gagnagar 102 MW PP (Digital Power) | [11 empty] | 5 | 32 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 0 |  |  |  | 270432
95 | Patenga 50MW PP (Baraka) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 8 | 6 |  | 6 | 6 | 6 | 3 | 6 | 6 | 6 | 151200
96 | Chattogram 108 MW PP (ECPV) | [9 empty] | 3 | 8 | 8 | 6 | 5 | 5 | 6 | 6 | 6 |  | 5 | 5 | 5 | 3 | 0 |  |  | 72000
97 | katpotti 52 MW
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [10 empty] | 7 | 15 | 26 | 47 | 55 | 40 | 40 | 41 |  | 40 | 40 | 40 | 40 | 30 | 0 |  | 481488
100 | Manikganj 55 MW PP (Northern) | 17 | 17 | 17 | 17 | [5 empty] | 17 | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 17 | 17 | 553585
101 | Kushiara 163 MW CCPP (KP) | 80 | 80 | 112 | 112 | 80 | 80 | 80 | 112 | 112 | 112 | 80 | 112 | 112 | 112 | 112 | 80 | 112 | 80 |  | 112 | 112 | 112 | 112 | 112 | 80 | 112 | 2425664
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 0 | 0 | [8 empty] | 15050
103 | Kamalaghat 54 MW PP(Banco Energy) | 35 | 17 | 17 | 17 | [5 empty] | 35 | 35 | 35 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 0 |  | 372960
104 | Keranigonj 300 MW PP (APR) | [26 empty] | 0
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 46 | 28 | 19 | 32 | 8 | 8 | 8 | 24 | 47 | 37 | 55 | 55 | 62 | 75 | 75 | 75 | 96 | 120 |  | 172 | 172 | 173 | 173 | 150 | 87 | 48 | 1749600
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 71 | 70 | 70 | 78 | 17 |  |  | 9 | 51 | 51 | 52 | 52 | 73 | 91 | 100 | 104 | 123 | 147 |  | 149 | 149 | 149 | 144 | 84 | 52 | 52 | 1829232
115 | Juldah 100 MW PP Unit-3 (Acorn) | 50 | 50 | 60 | 75 | 76 | 40 | 40 | 40 | 40 | 76 | 76 | 76 | 76 | 76 | 88 | 88 | 88 | 88 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1802880
116 | Chandpur 200MW (Desh energy) | 51 | 51 | 51 | 51 | 34 | 17 | 17 | 38 | 68 | 72 | 120 | 159 | 183 | 200 | 200 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 160 | 85 | 2979840
117 | Ashuganj 150MW PP (Midland) | [9 empty] | 5 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 33 | 100 | 50 | 10 | 10 | 10 | 10 | 322836
118 | Bibiyana-III 400 MW CCPP | 366 | 339 | 328 | 332 | 302 | 305 | 304 | 364 | 370 | 367 | 367 | 367 | 370 | 367 | 375 | 397 | 364 | 342 |  | 363 | 365 | 370 | 366 | 366 | 398 | 368 | 8546000
| Jamalpur 115 MW PP (United) | 57 | 68 | 47 | 47 | 24 | 8 | 8 | 47 | 47 | 49 | 75 | 107 | 115 | 115 | 115 | 88 | 88 | 92 |  | 115 | 115 | 115 | 115 | 115 | 115 | 49 | 1782000
| Anwara 300 MW PP (United) | [13 empty] | 100 | 100 | 65 | 65 | 100 |  | 100 | 100 | 65 | 48 | 48 | 30 | 30 | 828000
| Juldah unit-2 (Acorn) | [7 empty] | 9 | 12 | 12 | 12 | 80 | 75 | 85 | 86 | 38 | 38 | 85 |  | 85 | 85 | 50 | 25 | 25 | 25 | 25 | 776640
| Anlima Energy Ltd. | 107 | 107 | 107 | 107 | 107 | 51 | 51 | 51 | 51 | 62 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 |  | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 2335964
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | [5 empty] | 1 | 17 | 17 | 17 | 17 | 17 | 17 | 11 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 337680
| Spectra Solar Plant Ltd. | [5 empty] | 0 | 5 | 13 | 23 | 30 | 22 | 34 | 34 | 30 | 23 | 14 | 6 | 1 |  | 0 | [6 empty] | 218715
| Chandpur 115(Doreen) | 38 | 47 | 35 | 37 | 36 | 36 | 35 | 36 | 36 | 35 | 36 | 36 | 36 | 35 | 35 | 47 | 75 | 75 |  | 75 | 80 | 88 | 115 | 115 | 115 | 107 | 1379520
| Kanchan Purbachal Power Generation Ltd. | 17 | 17 | 17 | 34 | 17 |  |  | 5 | 17 | 17 | 17 | 17 | 17 | 18 | 35 | 35 | 35 | 35 |  | 34 | 35 | 35 | 35 | 35 | 35 | 35 | 594000
| Mirsharai 150 MW (Oil) | [12 empty] | 18 | 0 | 7 | 11 | 0 | [9 empty] | 31781
Mirsharai 150 MW (Gas)
120 | Eastern Zone Total | 5225 | 5162 | 5388 | 5419 | 4594 | 4277 | 4279 | 4562 | 5344 | 5811 | 6114 | 6389 | 6567 | 6823 | 6948 | 6806 | 6773 | 6878 |  | 7189 | 7401 | 7156 | 7115 | 6952 | 6519 | 6125 | 145607858
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | [19 empty] | 16 | 16 | 16 | 16 | 16 | 16 | 0 | 85440
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | [19 empty] | 17 | 17 | 17 | 17 | 17 | 0 |  | 97920
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 0 | 14 | 41 | 48 | 83 | 98 | 102 | 98 | 77 | 70 | 34 | 22 | 1 |  | 0 | [6 empty] | 735840
131 | Rampal 1320 MW (BIFPCL)
132 | United Payra Power Ltd. | [26 empty] | 0
133 | Bhola Nutan Biddut BD LTD (GAS)
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [19 empty] | 16 | 16 | 16 | 16 | 0 |  |  | 48192
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW | 239 | 209 | 182 | 182 | 152 | 152 | 153 | 154 | 152 | 152 | 153 | 152 | 154 | 153 | 153 | 154 | 153 | 154 |  | 186 | 202 | 160 | 152 | 198 | 168 | 151 | 4058200
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 171 | 170 | 171 | 171 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 153 | 160 | 160 | 160 | 160 | 160 | 171 |  | 171 | 162 | 171 | 171 | 171 | 172 | 171 | 3980263
140 | Bhola 33 MW PP (Venture) | 21 | 20 | 20 | 22 | 19 | 16 | 14 | 15 | 9 | 8 | 11 | 10 | 12 | 12 | 14 | 14 | 14 | 20 |  | 22 | 21 | 22 | 24 | 23 | 22 | 21 | 406700
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali) | [19 empty] | 8 | 8 | 8 | 8 | 0 |  |  | 28500
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | [19 empty] | 15 | 15 | 15 | 15 | 0 |  |  | 49680
146 | Bheramara HVDC | 904 | 904 | 904 | 904 | 904 | 848 | 848 | 843 | 856 | 857 | 905 | 905 | 904 | 905 | 903 | 904 | 904 | 904 |  | 904 | 791 | 792 | 792 | 904 | 904 | 905 | 21258181
147 | Bheramara 410 MW CCPP | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 180 | 180 | 210 | 210 |  | 180 | 220 | 220 | 265 | 285 | 270 | 255 | 5382720
148 | Payra 1320 MW | 860 | 750 | 790 | 810 | 580 | 560 | 560 | 590 | 620 | 620 | 590 | 640 | 700 | 800 | 740 | 700 | 700 | 600 |  | 620 | 820 | 820 | 1060 | 1140 | 1210 | 1190 | 20194600
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 163 | 170 | 170 | 170 | 170 | 170 |  | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 3890800
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [26 empty] | 0
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 0 | 2 | 4 | 5 | 5 | 5 | 5 | 4 | 0 | 0 | 0 | [8 empty] | 34920
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 140 | 140 | 155 | 192 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 150 | 130 | 130 | 130 | 130 |  | 148 | 211 | 212 | 204 | 140 | 130 | 149 | 3760582
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 237 | 235 | 287 | 287 | 240 | 297 | 298 | 298 | 253 | 253 | 255 | 254 | 286 | 286 | 265 | 263 | 318 | 276 |  | 294 | 307 | 308 | 420 | 303 | 304 | 416 | 6925090
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 22 | 5 | 10 | 22 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 20 | 18 | 3 | 3 | 3 |  | 21 | 21 | 21 | 21 | 22 | 22 | 22 | 269760
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 5 | 200970
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | [19 empty] | 8 | 0 | [5 empty] | 9327
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP | [11 empty] | 23 | 36 | 36 | 36 | 35 | 34 | 32 |  | 34 | 29 | 0 |  |  |  |  | 269041
169 | Natore 52 MW PP (Rajlanka) | [19 empty] | 8 | 8 | 0 |  |  |  |  | 12096
170 | Chapainawabganj 100 MW Peaking PP
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [16 empty] | 0 | 9 |  | 35 | 98 | 85 | 113 | 113 | 70 |  | 527232
172 | Confidence Power Bogura Unit-1 113 MW | [16 empty] | 0 | 35 |  | 35 | 35 | 0 |  |  |  |  | 74208
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [16 empty] | 0 | 40 |  | 40 | 40 | 34 | 34 | 34 | 34 | 34 | 234748
177 | Sympa Solar Power 8MW | [6 empty] | 1 | 2 | 2 | 3 | 6 | 6 | 7 | 7 | 7 | 6 | 4 | 1 |  | 0 | [6 empty] | 51590
178 | Energypac Power Venture Thakurgaon Ltd. | [16 empty] | 0 | 35 |  | 35 | 35 | 36 | 36 | 0 |  |  | 147648
| Intraco Solar 30 MW | [6 empty] | 3 | 8 | 24 | 34 | 23 | 37 | 37 | 33 | 30 | 17 | 8 | 1 |  | 0 | [6 empty] | 230254
| Adani Power Jharkhanda Ltd | 755 | 761 | 758 | 758 | 756 | 610 | 756 | 759 | 761 | 765 | 768 | 766 | 764 | 763 | 761 | 760 | 764 | 756 |  | 748 | 750 | 755 | 752 | 750 | 755 | 550 | 17959000
178 | Teesta Solar Limited | [6 empty] | 27 | 80 | 87 | 160 | 95 | 166 | 190 | 145 | 148 | 101 | 40 | 4 |  | 0 | [6 empty] | 1333440