## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2023-04-05 | Wednesday
|  | Date (day): | 2023-04-05 |  | Wednesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13034.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14279 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2023-04-04 | 2023-04-05 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 | 365 |  | Under maint.
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 78 | 81 | 78 | 81 | 27 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 351 | 400 | 400 | 400 | 12 |  | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 302 | 347 | 340 | 340 | 20 |  | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 17 | 77 | 75 | 90 |  | 10 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 283 | 245 | 280 | 300 | 35 |  | FGMO
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 50 | 95 | 68 | 95
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 47 | 55 | 48 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 16 | 90 | 92 | 92 |  | 8 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 215 | 192 | 220 | 220 |  | 115 | ST under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 50 | 102 | 102 | 102
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 35 | 0 | 35 | 19 |  | Fuel shortage
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 48 | 150 | 150 | 150
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 35 | 35 | 35 | 20 |  | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 35 | 17 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 29 | 47 | 48 | 49 |  | 31 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 30 | 32 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 33 | 49 | 50 | 50
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 132 | 296 | 280 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 0 | 300 |  | Fuel shortage
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Fuel shortage
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Fuel shortage
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 149 | 149 | 115 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 88 | 70 | 105
37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 34 | 71 | 72 | 72 | 32 |  | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 54 | 162 | 162 | 162
39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 33 | 0 | 30 | 0
40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 20 | 35 | 35 | 35 | 20 |  | Fuel shortage
| Dhaka area Total |  |  |  |  | 6263 | 5847 | 2778 | 3553 | 3485 | 3690 | 1491 | 664
41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 0 | 8 | 25 | 25
43 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 16 | 0 | 20 | 0
44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 6 | 19 | 6 | 6 | 44 |  | Fuel shortage
45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 25 | 25 | 25 | 25 | 205 |  | Low Water Level
46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 214 | 214 | 225 | 225
47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 17 | 34 | 17 | 17 | 88 |  | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 12 | 40 | 0 | 48 |  | 50 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 85 | 0 | 85 |  | 17 | Engine problem
51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 44 | 66 | 44 | 66 |  | 34 | Engine problem
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 62 | 88 | 100 | 100
53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 10 | 10 | 10 | 10 | 12 |  | Gas shortage
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 0 | 36 | 7 | 20
54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 14 | 0 | 0 | 0 | 108 |  | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 1 | 0 | 5 | 0
56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 45 | 230 | 120 | 230 | 70 |  | Fuel shortge
57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 54 | 0 | 54
58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 54 | 54 | 54 | 54 | 56 |  | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 90 | 90 | 100 | 100
60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 107 | 107 | 107 | 107 |  | 9
| Mirsharai 150 MW |  | Gas/HSD | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0
| Chattogram area Total |  |  |  |  | 2442 | 2382 | 717 | 1160 | 865 | 1172 | 943 | 260
61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 |  |  | Contract Expired
62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 209 | 217 | 200 | 200 |  |  | FGMO
63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 310 | 290 | 300 | 300 |  |  | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Gas shortage
65 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 356 | 250 | 320 | 300 |  |  | FGMO
66 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 41 | 49 | 45 | 45
67 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 55 | 15 | 40 | 50 | 50 | 5 |  | Gas shortage
68 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 16 | 0 | 0 | 0 | 195 |  | Gas shortage
69 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 43 | 43 | 43 |  | 8 | Engine problem
70 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 90 | 147 | 100 | 150
71 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 24 | 0 | 35 |  | 17 | Engine problem
72 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under Maint.
73 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 170 | 179 | 200 | 200
74 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 18 | 18 | 18 |  | 4 | Engine problem
75 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 138 | 164 | 135 | 153
76 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
77 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 52 | 30 | 52
78 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 21 | 21 | 21 | 21 |  | 4 | Engine problem
79 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel shortage
80 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 88 | 114 | 114
81 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 31 | 9 | 9 | 104 |  | Fuel shortage
82 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 17 |  | 37 | Engine problem
83 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 35 | 115 | 36 | 115
| Cumilla Area Total |  |  |  |  | 3309 | 3285 | 1537 | 1789 | 1682 | 1866 | 504 | 593
84 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 34 | 100 | 50 | 100 | 102 |  | Gas shortage
85 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 16 | 19 | 19 | 19 | 3 |  | Gas shortage
86 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0
87 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
88 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 154 | 173 | 150 | 170 |  | 30 | Engine problem
89 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 89 | 115 | 100 | 115
90 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 25 | 0 | 50 | 0
91 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 19 | 19 | 12 | 19 |  | 3 | Engine problem
| Mymensingh Area Total |  |  |  |  | 717 | 614 | 339 | 426 | 382.6 | 423 | 105 | 33
92 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 39 | 40 | 41 | 41 |  | 29 | Machine problem.
93 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 42 | 43 | 42 | 42 |  | 48 | Machine problem
94 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 80 | 80 | 112 | 112 |  | 51 | ST U/M.
95 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
96 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 51 | 53 | 51 | 51
97 | Fenchuganj 44MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 47 | 50 | 50 | 50
98 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 8 | 8 |  | 3 | Engine problem
99 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 60 | 62 | 65 | 65
100 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 79 | 84 | 86 | 86
101 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
102 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 206 | 208 | 210 | 210 |  | 21 | Machine problem
103 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 18 | 18
104 | Sylhet 50MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
105 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 8 | 16 | 16 | 9 |  | Gas shortage
106 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 280 | 260 | 280 | 280 |  |  | FGMO
107 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 367 | 330 | 375 | 375 |  |  | FGMO
108 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 9 | 9 | 9 | 9
109 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 390 | 400 | 400 | 400
| Sylhet Area Total |  |  |  |  | 2472 | 2427 | 1666 | 1627 | 1763 | 1763 | 9 | 582
110 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 894 | 799 | 905 | 905
111 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 46 | 77 | 66 | 99 |  | 16 | Engine problem
112 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 40 | 50
113 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
114 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 40 | 65 |  | 44 | Engine problem
115 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 150 | 150 | 170 | 200 | 210 |  | Gas shortage
116 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 24 | 8 | 40
117 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Fuel shortage
118 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 7 | 55 | 53 | 53 | 52 |  | Fuel shortage
119 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 50 | 0 | 100
120 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 102 | 0 | 100 | 0
| Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 660*2 | 617 | 617 | 369 | 364 | 370 | 370
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3005 | 3001 | 1568 | 1519 | 1752 | 1882 | 608 | 60
121 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 16 | 48 | 48 | 62 |  | Fuel shortage
122 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 19 | 27 | 20 | 25 |  | 15 | Engine problem
123 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 171 | 163 | 170 | 170 | 24 |  | Gas shortage
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
124 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 730 | 932 | 900 | 900
125 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 0 | 0 | 0 | 0 |  | 220 | Under maintenance
126 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 0 | 0 |  |  | Line O/L
127 | Barisal 307 MW |  | Coal | BCPCL | 307*1 | 307 | 307 | 230 | 263 | 150 | 180 |  |  | Line O/L
| Barisal Area Total |  |  |  |  | 2265 | 2265 | 1150 | 1401 | 1288 | 1323 | 86 | 235
128 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
129 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 32 | 0 | 32 |  | 20 | Engine problem
130 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 40 |  | 31 | Engine problem
131 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 7 | 0 | 0 | 0 |  |  | Contract Expired
132 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 8 | 0 | 42 |  | 8 | Engine problem
133 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 40 | 0 | 40 |  | 10 | Engine problem
134 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 130 | 135 | 180 | 180 | 30 |  | Gas shortage
135 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
136 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
137 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 265 | 262 | 332 | 300 | 114 |  | Gas shortage
138 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 28 | 33 | 28 | 36 |  | 14 | Engine problem
139 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 18 | 21 | 22 | 22
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
140 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
141 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 8 | 0 | 43 | 9 |  | Fuel shortage
142 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 46 | 40 | 90
143 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel shortage
144 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 70 | 95 | 50 | 113
145 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 35 | 113 | 50 | 113
146 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 4 | 0 | 6 | 0
| Adani Power Jharkhanda Ltd |  | Coal | Import | 0 | 0 | 0 | 666 | 695 | 660 | 700 |  |  | On test.
| Rajshahi Area Total |  |  |  |  | 2179 | 2129 | 1234 | 1499 | 1379 | 1762 | 964 | 83
147 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
148 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 170 | 220 | 170 | 170 | 104 |  | Coal Shortage.
149 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
150 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
151 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 51 | 113 | 50 | 113
152 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 7 | 0 | 8 | 0
153 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 35 | 55 | 50 | 115
154 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 33 | 0 | 30 | 0
| Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 0 | 0 | 200 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 830 | 750 | 496 | 388 | 438 | 398 | 229 | 85
| Total |  |  |  |  | 23482 | 22700 | 11485 | 13362 | 13034.6 | 14279 | 4939 | 2595
A. |  | 2023-04-04 | (Yesterday) |  |  |  |  | Tuesday
1 | Highest Generation : |  |  | 13362 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 8871 | MW at | 6:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 13378 | MW
3 | Day peak Generation : |  |  | 11485 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 12889.8 | MW
4 | Evening peak Generation : |  |  | 13362 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 15 | MW
5 | Total Energy Generation : |  | 275.4691 | MKWHr | By Solar | 3.1529 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Gas : | 136.3614 | MKWHr |  | By Oil: | 55.8353 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 55.178 | MKWHr |  | By Hydro: | 0.32772 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 4939 | MW | Dhaka | 4614.2 | 4614.2 |  | 0 |  | 18:00 |  | 58
|  |  | For Plants S/D or M/C prob = |  |  | 2595 | MW | Chittagong | 1294.6 | 1294.6 |  | 0 |  | 19:00 |  | 17
|  |  | Total = |  |  | 7534 | MW | Khulna | 1688.2 | 1688.2 |  | 0 |  | 19:30 |  | 18
7 | Total Gas Supplied : |  |  | 1039 | MMCFD |  |  | Rajshahi | 1407.2 | 1407.2 |  | 0 |  | 20:00 |  | 20
8 | Fuel Cost : | i) Gas : | Taka | 144677911.408 | ii) Oil : | Taka | 739994596.21 | Comilla | 1245 | 1245 |  | 0 |  | 21:00 |  | 15
|  | iii) Coal : | Taka | 211811533 | Total | Taka | 1096484040.618 | Mymensingh | 1088 | 1073 |  | 15 |  | 22:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0.033 | MKWHr. | Sylhet | 409 | 409 |  | 0 |  | 23:00 |  | 0
| ii) During Peak Demand : |  |  | 128 | MW (E to W) at | 21:00 | hrs | Barisal | 401.6 | 401.6 |  | 0 |  | 24:00 |  | 0
| iii) Maximum : |  |  | 56 | MW at | 20:00 | hrs | Rangpur | 742 | 742 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 33.4° C |  |  | Total | 12889.8 | 12874.8 |  | 15
B. |  | 2023-04-05 | (Today) |  |  |  | Wednesday |  |  | Probable max. temperature in Dhaka |  |  | 34.2° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 13800 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 14279 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 11800 | MW
4 | Reserve(Generation end) |  |  |  | 479 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 284.4989 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 9961 | MW at | 6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.2567 | MKWHr. | ii) HVDC Flow at Peak Time |  | 799 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.3571 | MKWHr. | iii) Maximum HVDC Flow : |  | 894 | MW at | 4:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 76.04 |  | (b) Today: | 76.07 |  | (c) Rule Curve: |  | 87.2
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2023-04-04 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 0 | 81 | 0 | 381 | 302 |  | 0 | 450 | 266 | 8 | 17 | 30 | 190 | 0 | 0 | 8 | 8 | 32 | 0 | 0 | 0 | 0 | 0 | 35 | 35 | 22 | 23 | 25 | 33 | 22 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 |  | 19 | 0 | 51 | 55 | 0 | 6 | 8 | 31 | 0 | 0 | 0 | 280 | 0 | 191 | 8 | 0 | 50 | 15 | 0 | 43 | 0 | 0 | 8 | 18 | 11 | 33 | 21 | 138 | 94 | 0 | 19 | 0 | 41 | 42 | 53 | 50 | 112 | 0 | 40 | 50 | 0 | 207 | 18 | 0 | 9 | 260 | 16 | 8 | 0 | 15 | 0 | 0 | 48 | 0 | 133 | 0 | 62 | 200 | 80 | 367 | 49 | 34 | 17 | 0 | 80 | 17 | 54 | 0 | 9 | 30 | 360 | 17 | 0 | 35 | 107 | 0 | 17 | 0 | 46 | 35 | 330 | 0 | 0 |  | 893 | 0 | 145 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 156 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 169 | 0 | 0 | 166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 241 | 55 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 870 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 182 | 651 | 0 | 0 |  | 6507 | 4081 | 10588 | 3692 | 893 | 2015 | 0 | 1514 | 2253 | 0 | 0 | 83 | 138 | 0 | 0 | 76.04
2:00 | 0 | 0 | 0 | 180 | 0 | 81 | 0 | 354 | 302 |  | 0 | 350 | 269 | 9 | 17 | 30 | 170 | 0 | 0 | 8 | 8 | 32 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 22 | 23 | 25 | 33 | 22 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 0 | 0 | 0 |  | 19 | 0 | 51 | 55 | 0 | 6 | 5 | 40 | 0 | 0 | 0 | 280 | 0 | 199 | 8 | 0 | 50 | 15 | 0 | 43 | 0 | 0 | 8 | 18 | 11 | 33 | 21 | 132 | 96 | 0 | 19 | 0 | 41 | 42 | 53 | 50 | 80 | 0 | 40 | 50 | 0 | 209 | 18 | 0 | 9 | 265 | 16 | 8 | 0 | 15 | 0 | 0 | 48 | 0 | 133 | 0 | 62 | 200 | 80 | 317 | 49 | 17 | 17 | 0 | 80 | 17 | 54 | 0 | 9 | 30 | 390 | 17 | 0 | 35 | 107 | 0 | 17 | 0 | 35 | 35 | 300 | 0 | 0 |  | 893 | 0 | 145 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 169 | 0 | 0 | 166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 247 | 17 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 820 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 182 | 641 | 0 | 0 |  | 6255 | 3997 | 10252 | 3621 | 893 | 1906 | 0 | 1431 | 2186 | 0 | 0 | 83 | 132 | 0 | 0 | 76.04
3:00 | 0 | 0 | 0 | 180 | 0 | 81 | 0 | 364 | 342 |  | 0 | 400 | 290 | 8 | 17 | 30 | 170 | 0 | 0 | 8 | 8 | 32 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 22 | 23 | 25 | 33 | 32 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 0 | 0 |  | 19 | 0 | 51 | 55 | 0 | 6 | 8 | 40 | 0 | 0 | 0 | 280 | 0 | 197 | 8 | 0 | 50 | 15 | 0 | 43 | 0 | 0 | 8 | 18 | 11 | 33 | 21 | 128 | 94 | 0 | 19 | 0 | 41 | 42 | 53 | 50 | 80 | 0 | 40 | 86 | 0 | 208 | 18 | 0 | 9 | 275 | 16 | 8 | 0 | 15 | 0 | 0 | 57 | 0 | 139 | 0 | 62 | 200 | 80 | 355 | 68 | 17 | 17 | 0 | 30 | 17 | 54 | 0 | 9 | 60 | 390 | 17 | 0 | 35 | 107 | 0 | 17 | 0 | 36 | 35 | 300 | 0 | 0 |  | 892 | 0 | 150 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 259 | 17 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 830 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 182 | 659 | 0 | 0 |  | 6471 | 4042 | 10513 | 3676 | 892 | 2074 | 0 | 1445 | 2215 | 0 | 0 | 83 | 128 | 0 | 0 | 76.04
4:00 | 0 | 0 | 0 | 180 | 0 | 81 | 0 | 386 | 342 |  | 0 | 400 | 245 | 8 | 17 | 15 | 170 | 0 | 0 | 8 | 8 | 32 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 22 | 23 | 25 | 33 | 32 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 0 | 0 |  | 19 | 0 | 17 | 44 | 0 | 6 | 8 | 40 | 0 | 0 | 0 | 280 | 0 | 204 | 8 | 0 | 50 | 15 | 0 | 43 | 0 | 0 | 8 | 18 | 11 | 33 | 21 | 134 | 84 | 0 | 19 | 0 | 41 | 42 | 53 | 50 | 112 | 0 | 40 | 86 | 0 | 207 | 18 | 0 | 9 | 270 | 16 | 8 | 0 | 15 | 0 | 0 | 57 | 0 | 149 | 0 | 62 | 200 | 80 | 366 | 70 | 17 | 17 | 0 | 100 | 28 | 54 | 0 | 9 | 60 | 390 | 17 | 0 | 35 | 107 | 0 | 17 | 0 | 36 | 35 | 300 | 0 | 0 |  | 894 | 0 | 150 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 169 | 0 | 0 | 167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 263 | 17 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 373 | 0 | 182 | 655 | 0 | 0 |  | 6522 | 4013 | 10535 | 3706 | 894 | 2061 | 0 | 1512 | 2179 | 0 | 0 | 49 | 134 | 0 | 0 | 76.04
5:00 | 0 | 0 | 0 | 180 | 0 | 23 | 0 | 383 | 302 |  | 0 | 400 | 250 | 0 | 2 | 0 | 170 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 23 | 25 | 33 | 32 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 0 | 0 |  | 19 | 0 | 0 | 44 | 0 | 6 | 5 | 40 | 0 | 0 | 0 | 280 | 0 | 209 | 8 | 0 | 50 | 15 | 0 | 10 | 0 | 0 | 0 | 18 | 11 | 33 | 21 | 112 | 84 | 0 | 19 | 0 | 41 | 42 | 11 | 10 | 80 | 0 | 40 | 10 | 0 | 208 | 19 | 0 | 9 | 265 | 16 | 8 | 0 | 0 | 0 | 0 | 58 | 0 | 128 | 0 | 62 | 136 | 10 | 355 | 69 | 17 | 17 | 0 | 30 | 35 | 54 | 0 | 9 | 60 | 400 | 0 | 0 | 0 | 107 | 0 | 0 | 0 | 35 | 35 | 300 | 0 | 0 |  | 893 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 169 | 0 | 0 | 164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 720 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 182 | 666 | 0 | 0 |  | 5712 | 3843 | 9555 | 3703 | 893 | 1745 | 0 | 975 | 2111 | 0 | 0 | 16 | 112 | 0 | 0 | 76.04
6:00 | 0 | 0 | 0 | 180 | 0 | 23 | 0 | 342 | 263 |  | 0 | 360 | 245 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 23 | 25 | 33 | 32 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 0 |  | 19 | 0 | 0 | 44 | 0 | 6 | 5 | 40 | 0 | 0 | 0 | 280 | 0 | 168 | 8 | 0 | 20 | 15 | 0 | 10 | 0 | 0 | 0 | 18 | 11 | 33 | 21 | 106 | 84 | 0 | 19 | 0 | 41 | 42 | 11 | 10 | 80 | 0 | 40 | 10 | 0 | 209 | 19 | 0 | 9 | 270 | 16 | 8 | 0 | 0 | 0 | 0 | 48 | 0 | 78 | 0 | 62 | 68 | 10 | 319 | 49 | 17 | 17 | 0 | 15 | 17 | 54 | 0 | 9 | 12 | 340 | 0 | 0 | 0 | 92 | 0 | 0 | 0 | 35 | 35 | 250 | 0 | 0 |  | 846 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 169 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 700 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 181 | 661 | 1 | 0 |  | 5148 | 3723 | 8871 | 3423 | 846 | 1676 | 0 | 734 | 2085 | 0 | 0 | 0 | 106 | 1 | 0 | 76.04
7:00 | 0 | 0 | 0 | 180 | 0 | 23 | 0 | 318 | 261 |  | 0 | 330 | 310 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 23 | 6 | 33 | 32 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 0 |  | 19 | 0 | 0 | 44 | 0 | 6 | 5 | 21 | 0 | 0 | 0 | 325 | 0 | 205 | 8 | 0 | 20 | 15 | 0 | 10 | 0 | 0 | 0 | 18 | 11 | 33 | 21 | 108 | 47 | 0 | 19 | 0 | 41 | 42 | 11 | 10 | 80 | 0 | 64 | 10 | 0 | 209 | 0 | 0 | 9 | 270 | 16 | 8 | 0 | 0 | 0 | 0 | 48 | 0 | 55 | 4 | 62 | 68 | 10 | 417 | 49 | 17 | 17 | 1 | 15 | 0 | 54 | 0 | 9 | 12 | 400 | 0 | 5 | 0 | 107 | 0 | 0 | 3 | 36 | 35 | 250 | 0 | 0 |  | 823 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 650 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 374 | 5 | 183 | 612 | 30 | 0 |  | 5288 | 3661 | 8949 | 3561 | 823 | 1694 | 0 | 710 | 1989 | 0 | 0 | 0 | 108 | 64 | 0 | 0
8:00 | 0 | 0 | 0 | 180 | 0 | 30 | 0 | 389 | 352 |  | 0 | 450 | 280 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 23 | 23 | 33 | 32 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 0 |  | 19 | 0 | 0 | 44 | 0 | 6 | 5 | 9 | 0 | 0 | 0 | 280 | 0 | 213 | 8 | 0 | 20 | 15 | 0 | 10 | 0 | 0 | 0 | 18 | 11 | 33 | 21 | 124 | 47 | 0 | 16 | 1 | 41 | 42 | 11 | 10 | 80 | 0 | 40 | 10 | 0 | 207 | 0 | 0 | 9 | 275 | 16 | 8 | 0 | 0 | 0 | 0 | 48 | 0 | 56 | 4 | 62 | 68 | 10 | 366 | 49 | 40 | 17 | 1 | 15 | 0 | 54 | 0 | 9 | 72 | 400 | 0 | 8 | 0 | 107 | 0 | 0 | 14 | 35 | 35 | 300 | 0 | 0 |  | 762 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 22 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 287 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 650 | 0 | 0 | 0 | 2 | 34 | 0 | 0 | 0 | 370 | 12 | 182 | 615 | 83 | 0 |  | 5705 | 3691 | 9396 | 3664 | 762 | 1874 | 0 | 796 | 1987 | 0 | 0 | 28 | 124 | 161 | 0 | 76.05
9:00 | 0 | 0 | 0 | 180 | 0 | 65 | 0 | 415 | 309 |  | 0 | 450 | 255 | 0 | 2 | 0 | 206 | 0 | 0 | 2 | 8 | 36 | 0 | 0 | 0 | 0 | 0 | 17 | 2 | 22 | 23 | 5 | 33 | 32 | 42 | 0 | 25 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 0 |  | 19 | 0 | 0 | 44 | 5 | 6 | 5 | 6 | 0 | 0 | 0 | 280 | 0 | 216 | 16 | 0 | 20 | 15 | 0 | 27 | 0 | 0 | 0 | 18 | 11 | 33 | 20 | 134 | 47 | 0 | 16 | 0 | 38 | 42 | 51 | 50 | 80 | 0 | 62 | 81 | 0 | 209 | 0 | 0 | 9 | 270 | 16 | 8 | 0 | 0 | 0 | 0 | 48 | 0 | 97 | 9 | 62 | 90 | 11 | 367 | 49 | 52 | 17 | 3 | 45 | 0 | 54 | 0 | 9 | 90 | 360 | 17 | 19 | 54 | 107 | 0 | 0 | 15 | 36 | 35 | 450 | 0 | 0 |  | 752 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 19 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 0 | 0 | 9 | 0 | 54 | 0 | 3 | 0 | 670 | 0 | 0 | 0 | 3 | 63 | 0 | 0 | 0 | 375 | 22 | 229 | 600 | 137 | 0 |  | 6294 | 3895 | 10189 | 3816 | 752 | 1997 | 0 | 1083 | 2044 | 25 | 0 | 64 | 134 | 274 | 0 | 76.05
10:00 | 0 | 0 | 0 | 180 | 0 | 70 | 0 | 378 | 303 |  | 0 | 450 | 281 | 14 | 37 | 32 | 210 | 0 | 0 | 16 | 16 | 48 | 0 | 0 | 0 | 0 | 0 | 35 | 23 | 22 | 23 | 5 | 33 | 32 | 42 | 0 | 25 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 |  | 19 | 0 | 0 | 44 | 7 | 6 | 5 | 6 | 0 | 0 | 0 | 305 | 0 | 213 | 16 | 0 | 20 | 15 | 0 | 43 | 0 | 0 | 1 | 18 | 11 | 33 | 18 | 134 | 34 | 0 | 16 | 2 | 39 | 42 | 51 | 50 | 80 | 0 | 61 | 81 | 0 | 208 | 0 | 0 | 9 | 280 | 16 | 0 | 0 | 27 | 0 | 0 | 48 | 0 | 120 | 0 | 62 | 194 | 25 | 367 | 58 | 52 | 17 | 3 | 45 | 0 | 54 | 0 | 9 | 90 | 360 | 33 | 24 | 54 | 107 | 0 | 1 | 25 | 36 | 35 | 320 | 0 | 0 |  | 845 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 22 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 271 | 0 | 0 | 70 | 0 | 51 | 0 | 5 | 0 | 680 | 0 | 0 | 0 | 5 | 90 | 0 | 0 | 0 | 374 | 26 | 230 | 607 | 167 | 0 |  | 6538 | 4119 | 10657 | 3644 | 845 | 2045 | 0 | 1480 | 2061 | 25 | 0 | 76 | 134 | 347 | 0 | 76.05
11:00 | 0 | 0 | 0 | 180 | 0 | 72 | 0 | 351 | 302 |  | 0 | 450 | 273 | 17 | 50 | 47 | 210 | 0 | 0 | 16 | 16 | 48 | 0 | 0 | 0 | 0 | 0 | 35 | 35 | 22 | 23 | 17 | 33 | 30 | 42 | 0 | 25 | 0 | 0 | 0 | 0 | 213 | 0 | 0 | 0 |  | 19 | 0 | 0 | 44 | 11 | 6 | 8 | 6 | 0 | 0 | 0 | 315 | 0 | 210 | 16 | 0 | 20 | 15 | 0 | 43 | 0 | 0 | 6 | 18 | 8 | 33 | 20 | 144 | 34 | 0 | 16 | 2 | 39 | 42 | 51 | 50 | 80 | 0 | 60 | 80 | 0 | 208 | 0 | 0 | 9 | 280 | 16 | 0 | 0 | 32 | 0 | 0 | 67 | 0 | 126 | 11 | 62 | 185 | 58 | 372 | 79 | 52 | 17 | 0 | 45 | 0 | 54 | 0 | 9 | 90 | 370 | 34 | 50 | 54 | 107 | 0 | 17 | 32 | 36 | 30 | 320 | 0 | 0 |  | 893 | 0 | 150 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 18 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 267 | 0 | 0 | 70 | 0 | 51 | 0 | 7 | 0 | 700 | 0 | 0 | 0 | 5 | 98 | 0 | 0 | 0 | 374 | 26 | 230 | 625 | 189 | 0 |  | 6725 | 4242 | 10967 | 3650 | 893 | 2031 | 0 | 1623 | 2099 | 25 | 0 | 82 | 144 | 420 | 0 | 76.05
12:00 | 0 | 0 | 0 | 180 | 0 | 78 | 0 | 351 | 302 |  | 0 | 450 | 283 | 17 | 50 | 47 | 215 | 0 | 0 | 16 | 50 | 48 | 0 | 0 | 0 | 0 | 0 | 35 | 35 | 22 | 23 | 6 | 33 | 30 | 33 | 0 | 25 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 |  | 19 | 12 | 0 | 44 | 14 | 6 | 10 | 0 | 0 | 0 | 0 | 310 | 0 | 209 | 16 | 0 | 41 | 15 | 0 | 43 | 0 | 0 | 8 | 18 | 8 | 33 | 21 | 138 | 34 | 0 | 16 | 2 | 39 | 42 | 51 | 47 | 80 | 0 | 60 | 79 | 0 | 206 | 0 | 0 | 9 | 280 | 16 | 0 | 0 | 132 | 0 | 0 | 154 | 0 | 149 | 16 | 62 | 170 | 90 | 367 | 89 | 52 | 17 | 1 | 45 | 0 | 54 | 0 | 9 | 90 | 390 | 34 | 25 | 54 | 107 | 0 | 17 | 33 | 35 | 20 | 356 | 0 | 0 |  | 894 | 0 | 150 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 28 | 18 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 265 | 7 | 0 | 70 | 0 | 51 | 0 | 7 | 35 | 730 | 0 | 0 | 0 | 4 | 102 | 35 | 0 | 0 | 369 | 33 | 230 | 666 | 200 | 0 |  | 7037 | 4448 | 11485 | 3712 | 894 | 2035 | 0 | 2005 | 2165 | 25 | 0 | 88 | 138 | 423 | 0 | 76.05
13:00 | 0 | 0 | 0 | 180 | 0 | 81 | 0 | 381 | 302 |  | 0 | 450 | 284 | 14 | 50 | 47 | 210 | 0 | 0 | 17 | 102 | 115 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 23 | 20 | 33 | 30 | 42 | 0 | 25 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 |  | 19 | 34 | 0 | 44 | 14 | 6 | 7 | 2 | 0 | 0 | 0 | 310 | 0 | 210 | 16 | 0 | 40 | 15 | 0 | 43 | 0 | 0 | 8 | 18 | 8 | 33 | 20 | 148 | 34 | 0 | 16 | 2 | 37 | 42 | 50 | 47 | 90 | 0 | 60 | 81 | 0 | 206 | 0 | 0 | 8 | 285 | 16 | 0 | 0 | 145 | 0 | 0 | 154 | 0 | 149 | 20 | 62 | 160 | 95 | 364 | 89 | 52 | 17 | 2 | 115 | 0 | 54 | 70 | 9 | 90 | 396 | 35 | 53 | 54 | 107 | 0 | 17 | 29 | 36 | 35 | 356 | 0 | 0 |  | 893 | 0 | 150 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 28 | 18 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 254 | 17 | 0 | 70 | 0 | 49 | 0 | 7 | 35 | 760 | 0 | 0 | 0 | 5 | 74 | 35 | 0 | 0 | 376 | 34 | 230 | 662 | 194 | 0 |  | 7463 | 4466 | 11929 | 3766 | 893 | 2046 | 0 | 2256 | 2198 | 25 | 0 | 177 | 148 | 420 | 0 | 76.05
14:00 | 0 | 0 | 0 | 180 | 0 | 81 | 0 | 400 | 340 |  | 0 | 450 | 301 | 14 | 60 | 47 | 206 | 0 | 0 | 36 | 102 | 115 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 23 | 19 | 33 | 29 | 45 | 0 | 25 | 0 | 0 | 0 | 0 | 216 | 0 | 0 | 0 |  | 19 | 24 | 74 | 44 | 18 | 6 | 7 | 2 | 0 | 0 | 0 | 335 | 0 | 182 | 16 | 0 | 42 | 15 | 0 | 43 | 0 | 8 | 8 | 18 | 8 | 33 | 20 | 158 | 33 | 0 | 19 | 2 | 39 | 42 | 50 | 50 | 90 | 0 | 50 | 81 | 0 | 206 | 0 | 0 | 8 | 280 | 16 | 0 | 0 | 183 | 0 | 0 | 154 | 0 | 90 | 17 | 62 | 160 | 97 | 390 | 98 | 56 | 17 | 4 | 130 | 0 | 54 | 99 | 8 | 90 | 385 | 49 | 46 | 72 | 107 | 0 | 17 | 30 | 36 | 35 | 328 | 0 | 0 |  | 893 | 0 | 150 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 30 | 17 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 232 | 32 | 0 | 80 | 0 | 49 | 0 | 7 | 35 | 790 | 0 | 0 | 0 | 5 | 85 | 35 | 0 | 0 | 373 | 32 | 203 | 657 | 164 | 0 |  | 7691 | 4462 | 12153 | 3777 | 893 | 2078 | 0 | 2386 | 2193 | 25 | 0 | 251 | 158 | 392 | 22 | 76.05
15:00 | 0 | 0 | 0 | 180 | 0 | 78 | 0 | 401 | 323 |  | 0 | 450 | 280 | 38 | 80 | 47 | 207 | 0 | 0 | 70 | 102 | 150 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 23 | 19 | 33 | 15 | 0 | 0 | 25 | 0 | 0 | 0 | 18 | 216 | 0 | 0 | 0 |  | 19 | 24 | 81 | 55 | 18 | 6 | 10 | 3 | 0 | 0 | 0 | 280 | 0 | 204 | 0 | 0 | 42 | 5 | 0 | 43 | 0 | 15 | 16 | 18 | 8 | 33 | 21 | 154 | 31 | 0 | 19 | 1 | 39 | 42 | 50 | 46 | 90 | 0 | 55 | 81 | 0 | 205 | 0 | 0 | 8 | 285 | 16 | 3 | 0 | 223 | 0 | 0 | 144 | 0 | 52 | 9 | 62 | 160 | 97 | 367 | 97 | 70 | 17 | 3 | 139 | 0 | 54 | 114 | 8 | 90 | 395 | 66 | 28 | 72 | 107 | 0 | 17 | 19 | 36 | 35 | 316 | 0 | 0 |  | 893 | 0 | 145 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 36 | 17 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 223 | 17 | 0 | 113 | 0 | 80 | 0 | 6 | 50 | 850 | 0 | 0 | 0 | 1 | 75 | 35 | 0 | 0 | 369 | 26 | 201 | 707 | 136 | 0 |  | 7687 | 4573 | 12260 | 3711 | 893 | 2004 | 0 | 2566 | 2297 | 25 | 0 | 306 | 154 | 304 | 40 | 76.06
16:00 | 0 | 0 | 0 | 180 | 0 | 81 | 0 | 400 | 327 |  | 0 | 420 | 287 | 51 | 95 | 47 | 160 | 0 | 0 | 70 | 60 | 150 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 23 | 19 | 33 | 15 | 21 | 0 | 25 | 0 | 0 | 0 | 8 | 220 | 0 | 0 | 0 |  | 19 | 31 | 83 | 55 | 18 | 6 | 10 | 13 | 0 | 0 | 0 | 285 | 0 | 207 | 0 | 0 | 42 | 5 | 0 | 43 | 0 | 29 | 25 | 18 | 8 | 33 | 15 | 144 | 30 | 0 | 19 | 1 | 37 | 42 | 53 | 49 | 112 | 0 | 60 | 82 | 0 | 204 | 0 | 0 | 8 | 265 | 16 | 8 | 0 | 242 | 0 | 0 | 96 | 0 | 51 | 7 | 62 | 174 | 102 | 366 | 68 | 105 | 17 | 1 | 138 | 16 | 54 | 88 | 9 | 90 | 395 | 71 | 13 | 72 | 107 | 0 | 17 | 15 | 45 | 35 | 317 | 0 | 0 |  | 892 | 0 | 145 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 17 | 0 | 11 | 0 | 0 | 169 | 0 | 0 | 164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 217 | 17 | 0 | 35 | 0 | 70 | 0 | 5 | 35 | 830 | 0 | 0 | 0 | 2 | 37 | 35 | 0 | 0 | 374 | 17 | 201 | 704 | 85 | 0 |  | 7649 | 4305 | 11954 | 3674 | 892 | 2000 | 0 | 2429 | 2278 | 25 | 0 | 329 | 144 | 183 | 42 | 76.06
17:00 | 0 | 0 | 0 | 180 | 0 | 43 | 0 | 401 | 327 |  | 0 | 420 | 270 | 42 | 95 | 55 | 160 | 0 | 0 | 40 | 58 | 150 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 23 | 19 | 33 | 15 | 49 | 0 | 25 | 0 | 0 | 0 | 8 | 221 | 0 | 0 | 0 |  | 19 | 34 | 84 | 44 | 19 | 6 | 10 | 26 | 0 | 0 | 0 | 290 | 0 | 182 | 0 | 0 | 47 | 5 | 0 | 10 | 0 | 23 | 34 | 18 | 8 | 33 | 21 | 138 | 31 | 0 | 19 | 0 | 37 | 42 | 22 | 49 | 112 | 0 | 52 | 82 | 0 | 203 | 0 | 0 | 8 | 270 | 16 | 8 | 0 | 257 | 0 | 0 | 97 | 0 | 51 | 2 | 62 | 178 | 112 | 366 | 68 | 105 | 25 | 1 | 140 | 35 | 54 | 88 | 9 | 90 | 400 | 72 | 5 | 72 | 107 | 0 | 17 | 6 | 89 | 35 | 316 | 18 | 0 |  | 893 | 0 | 140 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 17 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 216 | 17 | 0 | 35 | 0 | 70 | 0 | 4 | 35 | 800 | 0 | 0 | 0 | 0 | 19 | 35 | 0 | 0 | 374 | 6 | 201 | 708 | 33 | 0 |  | 7622 | 4191 | 11813 | 3658 | 893 | 1898 | 0 | 2527 | 2253 | 25 | 18 | 327 | 138 | 76 | 60 | 76.06
18:00 | 0 | 0 | 0 | 180 | 0 | 33 | 0 | 364 | 307 |  | 0 | 420 | 274 | 45 | 95 | 55 | 160 | 0 | 0 | 46 | 74 | 150 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 23 | 17 | 33 | 26 | 49 | 0 | 25 | 0 | 0 | 0 | 8 | 224 | 0 | 0 | 0 |  | 19 | 40 | 84 | 66 | 14 | 7 | 10 | 35 | 0 | 0 | 0 | 290 | 0 | 213 | 0 | 0 | 47 | 8 | 0 | 10 | 0 | 31 | 51 | 18 | 8 | 33 | 21 | 158 | 31 | 0 | 19 | 0 | 37 | 42 | 22 | 20 | 112 | 0 | 40 | 40 | 0 | 203 | 0 | 0 | 9 | 280 | 8 | 8 | 0 | 260 | 0 | 0 | 117 | 0 | 74 | 0 | 88 | 178 | 139 | 318 | 98 | 105 | 34 | 0 | 141 | 36 | 54 | 88 | 8 | 90 | 400 | 71 | 1 | 108 | 107 | 0 | 17 | 1 | 95 | 35 | 323 | 0 | 0 |  | 894 | 0 | 135 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 16 | 170 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 34 | 8 | 35 | 16 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 205 | 17 | 0 | 35 | 15 | 108 | 0 | 1 | 35 | 750 | 0 | 0 | 0 | 0 | 2 | 48 | 0 | 0 | 367 | 1 | 202 | 653 | 0 | 0 |  | 7737 | 4143 | 11880 | 3564 | 894 | 1813 | 0 | 2873 | 2142 | 25 | 0 | 405 | 158 | 6 | 58 | 76.06
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 0 | 81 | 0 | 348 | 312 |  | 0 | 420 | 305 | 54 | 95 | 55 | 160 | 0 | 0 | 62 | 84 | 150 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 22 | 23 | 12 | 33 | 26 | 49 | 0 | 25 | 0 | 0 | 0 | 11 | 223 | 0 | 0 | 0 |  | 19 | 40 | 84 | 66 | 13 | 19 | 10 | 35 | 0 | 0 | 0 | 310 | 0 | 212 | 0 | 0 | 47 | 20 | 0 | 25 | 0 | 31 | 51 | 18 | 8 | 33 | 21 | 166 | 34 | 0 | 19 | 0 | 38 | 42 | 53 | 35 | 112 | 0 | 61 | 82 | 0 | 203 | 0 | 0 | 9 | 270 | 8 | 8 | 0 | 293 | 0 | 0 | 163 | 0 | 149 | 0 | 88 | 179 | 138 | 395 | 108 | 105 | 34 | 0 | 226 | 36 | 54 | 99 | 9 | 90 | 400 | 71 | 0 | 126 | 107 | 0 | 17 | 0 | 96 | 35 | 270 | 0 | 0 |  | 838 | 0 | 130 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 32 | 171 | 27 | 8 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 40 | 8 | 36 | 19 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 204 | 31 | 0 | 35 | 25 | 113 | 0 | 0 | 95 | 760 | 0 | 0 | 0 | 0 | 0 | 79 | 0 | 0 | 374 | 0 | 206 | 701 | 0 | 0 |  | 8325 | 4369 | 12694 | 3616 | 838 | 2009 | 0 | 3387 | 2241 | 25 | 0 | 412 | 166 | 0 | 17 | 76.06
19:30 | 0 | 0 | 0 | 180 | 0 | 81 | 0 | 400 | 312 |  | 0 | 450 | 240 | 84 | 95 | 55 | 160 | 0 | 0 | 90 | 102 | 150 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 22 | 23 | 17 | 33 | 32 | 49 | 0 | 25 | 0 | 0 | 0 | 25 | 221 | 0 | 0 | 0 |  | 19 | 40 | 84 | 66 | 12 | 19 | 10 | 38 | 0 | 0 | 0 | 290 | 0 | 217 | 0 | 0 | 47 | 30 | 0 | 43 | 0 | 24 | 51 | 18 | 8 | 33 | 21 | 162 | 50 | 0 | 19 | 0 | 38 | 42 | 48 | 50 | 80 | 0 | 62 | 83 | 0 | 203 | 0 | 0 | 9 | 265 | 8 | 8 | 0 | 294 | 0 | 0 | 173 | 0 | 149 | 0 | 88 | 180 | 142 | 366 | 108 | 105 | 34 | 0 | 226 | 54 | 54 | 114 | 9 | 90 | 354 | 71 | 0 | 162 | 107 | 0 | 17 | 0 | 115 | 35 | 270 | 0 | 0 |  | 799 | 0 | 135 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 40 | 170 | 27 | 16 | 0 | 0 | 0 | 32 | 0 | 31 | 0 | 24 | 40 | 25 | 35 | 21 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 208 | 45 | 0 | 50 | 67 | 113 | 0 | 0 | 113 | 850 | 0 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 366 | 0 | 260 | 706 | 0 | 0 |  | 8465 | 4724 | 13189 | 3628 | 799 | 1985 | 0 | 3772 | 2382 | 25 | 0 | 436 | 162 | 0 | 18 | 0
20:00 | 0 | 0 | 0 | 180 | 0 | 78 | 0 | 394 | 311 |  | 0 | 450 | 245 | 76 | 95 | 55 | 140 | 0 | 0 | 90 | 102 | 150 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 22 | 23 | 24 | 33 | 32 | 49 | 0 | 25 | 0 | 0 | 0 | 25 | 214 | 0 | 0 | 0 |  | 19 | 40 | 84 | 66 | 12 | 19 | 10 | 36 | 0 | 0 | 0 | 290 | 0 | 217 | 0 | 0 | 49 | 30 | 0 | 43 | 0 | 30 | 52 | 18 | 11 | 33 | 21 | 162 | 78 | 0 | 19 | 0 | 38 | 42 | 53 | 50 | 80 | 0 | 62 | 83 | 0 | 203 | 0 | 0 | 9 | 270 | 8 | 0 | 0 | 296 | 0 | 0 | 173 | 0 | 149 | 0 | 88 | 179 | 140 | 319 | 108 | 105 | 34 | 0 | 229 | 54 | 54 | 114 | 9 | 90 | 360 | 71 | 0 | 162 | 107 | 0 | 17 | 0 | 115 | 35 | 250 | 0 | 0 |  | 799 | 0 | 140 | 0 | 69 | 0 | 0 | 0 | 0 | 0 | 40 | 162 | 28 | 16 | 0 | 0 | 0 | 32 | 0 | 31 | 0 | 24 | 40 | 25 | 35 | 21 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 232 | 45 | 0 | 80 | 67 | 113 | 0 | 0 | 113 | 930 | 0 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 367 | 0 | 220 | 704 | 0 | 0 |  | 8413 | 4789 | 13202 | 3533 | 799 | 2019 | 0 | 3801 | 2421 | 25 | 0 | 442 | 162 | 0 | 20 | 76.06
21:00 | 0 | 0 | 0 | 180 | 0 | 81 | 0 | 400 | 347 |  | 0 | 450 | 245 | 77 | 95 | 55 | 192 | 0 | 0 | 90 | 102 | 150 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 22 | 23 | 24 | 33 | 32 | 49 | 0 | 25 | 0 | 0 | 0 | 8 | 214 | 0 | 0 | 0 |  | 19 | 40 | 85 | 66 | 0 | 19 | 10 | 36 | 0 | 0 | 0 | 290 | 0 | 217 | 0 | 0 | 49 | 40 | 0 | 43 | 0 | 24 | 52 | 18 | 11 | 33 | 21 | 164 | 100 | 0 | 19 | 0 | 40 | 43 | 53 | 50 | 80 | 0 | 62 | 84 | 0 | 208 | 0 | 0 | 9 | 260 | 8 | 0 | 0 | 296 | 0 | 0 | 173 | 0 | 149 | 0 | 88 | 179 | 147 | 330 | 115 | 88 | 34 | 0 | 230 | 54 | 54 | 88 | 31 | 90 | 400 | 71 | 0 | 162 | 107 | 0 | 17 | 0 | 115 | 35 | 250 | 0 | 0 |  | 799 | 0 | 150 | 0 | 77 | 0 | 0 | 0 | 0 | 0 | 24 | 163 | 27 | 16 | 0 | 0 | 0 | 32 | 0 | 46 | 0 | 8 | 40 | 8 | 33 | 21 | 0 | 11 | 0 | 0 | 220 | 0 | 0 | 135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 262 | 55 | 0 | 95 | 50 | 113 | 0 | 0 | 113 | 932 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 364 | 0 | 263 | 695 | 0 | 0 |  | 8555 | 4807 | 13362 | 3688 | 799 | 2088 | 0 | 3674 | 2474 | 25 | 0 | 450 | 164 | 0 | 15 | 76.06
22:00 | 0 | 0 | 0 | 180 | 0 | 81 | 0 | 361 | 341 |  | 0 | 450 | 255 | 83 | 95 | 55 | 222 | 0 | 0 | 85 | 102 | 150 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 23 | 24 | 33 | 32 | 49 | 0 | 25 | 0 | 0 | 0 | 8 | 207 | 0 | 0 | 0 |  | 19 | 40 | 85 | 66 | 0 | 19 | 5 | 36 | 0 | 0 | 0 | 285 | 0 | 218 | 0 | 0 | 49 | 47 | 0 | 43 | 0 | 0 | 52 | 18 | 11 | 33 | 21 | 162 | 101 | 0 | 19 | 0 | 40 | 42 | 53 | 50 | 80 | 0 | 62 | 83 | 0 | 208 | 0 | 0 | 9 | 265 | 8 | 8 | 0 | 260 | 0 | 0 | 173 | 0 | 149 | 0 | 88 | 179 | 149 | 366 | 115 | 88 | 34 | 0 | 230 | 36 | 54 | 51 | 56 | 90 | 400 | 71 | 0 | 110 | 107 | 0 | 17 | 0 | 115 | 35 | 250 | 0 | 0 |  | 832 | 0 | 150 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 24 | 170 | 29 | 16 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 36 | 21 | 0 | 11 | 0 | 0 | 220 | 0 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 275 | 55 | 0 | 95 | 15 | 113 | 0 | 0 | 113 | 952 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 364 | 0 | 259 | 704 | 0 | 0 |  | 8430 | 4786 | 13216 | 3747 | 832 | 2118 | 0 | 3476 | 2499 | 25 | 0 | 357 | 162 | 0 | 0 | 76.06
23:00 | 0 | 0 | 0 | 180 | 0 | 81 | 0 | 351 | 336 |  | 0 | 450 | 275 | 85 | 95 | 55 | 180 | 0 | 0 | 85 | 102 | 150 | 0 | 0 | 0 | 0 | 17 | 35 | 0 | 22 | 23 | 27 | 33 | 32 | 42 | 0 | 0 | 0 | 0 | 0 | 8 | 202 | 0 | 0 | 0 |  | 19 | 40 | 85 | 70 | 0 | 19 | 5 | 36 | 0 | 0 | 0 | 290 | 0 | 182 | 0 | 0 | 49 | 48 | 0 | 43 | 0 | 0 | 52 | 18 | 11 | 33 | 21 | 164 | 101 | 0 | 19 | 0 | 40 | 42 | 53 | 50 | 80 | 0 | 61 | 84 | 0 | 208 | 0 | 0 | 9 | 270 | 16 | 0 | 0 | 195 | 0 | 0 | 174 | 0 | 144 | 0 | 88 | 180 | 48 | 367 | 108 | 88 | 34 | 0 | 230 | 36 | 54 | 34 | 57 | 90 | 400 | 71 | 0 | 21 | 107 | 0 | 17 | 0 | 96 | 35 | 250 | 0 | 0 |  | 893 | 0 | 155 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 26 | 16 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 31 | 22 | 0 | 11 | 0 | 0 | 220 | 0 | 0 | 169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 281 | 55 | 0 | 95 | 15 | 113 | 0 | 0 | 113 | 952 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 371 | 0 | 259 | 690 | 0 | 0 |  | 8008 | 4822 | 12830 | 3668 | 893 | 2144 | 0 | 3117 | 2492 | 0 | 0 | 352 | 164 | 0 | 0 | 76.07
24:00 | 0 | 0 | 0 | 180 | 0 | 78 | 0 | 351 | 336 |  | 0 | 450 | 260 | 84 | 95 | 55 | 180 | 0 | 0 | 85 | 102 | 150 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 22 | 23 | 27 | 33 | 33 | 42 | 0 | 0 | 0 | 0 | 0 | 12 | 200 | 0 | 0 | 0 |  | 19 | 40 | 85 | 55 | 0 | 9 | 10 | 38 | 0 | 0 | 0 | 285 | 0 | 182 | 0 | 0 | 49 | 50 | 0 | 43 | 0 | 0 | 52 | 18 | 11 | 33 | 21 | 154 | 86 | 0 | 19 | 0 | 40 | 42 | 53 | 50 | 112 | 0 | 62 | 83 | 0 | 208 | 0 | 0 | 9 | 260 | 16 | 8 | 0 | 195 | 0 | 0 | 47 | 0 | 112 | 0 | 88 | 179 | 27 | 367 | 49 | 70 | 17 | 0 | 86 | 17 | 54 | 70 | 9 | 90 | 400 | 71 | 0 | 17 | 107 | 0 | 17 | 0 | 76 | 35 | 270 | 0 | 0 |  | 892 | 0 | 155 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 26 | 16 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 281 | 55 | 0 | 95 | 15 | 113 | 0 | 0 | 113 | 962 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 370 | 0 | 247 | 707 | 0 | 0 |  | 7505 | 4786 | 12291 | 3683 | 892 | 2151 | 0 | 2604 | 2486 | 0 | 0 | 321 | 154 | 0 | 0 | 76.07
KWH | 0 | 0 | 0 | 4347000 | 0 | 1567136 | 0 | 9105410 | 7534000 |  | 0 | 9447000 | 6832756 | 737280 | 1152710 | 921519 | 4554838 | 0 | 0 | 799027 | 1183968 | 1947360 | 0 | 0 | 0 | 0 | 259920 | 648499 | 670184 | 469260 | 552000 | 440820 | 822900 | 685700 | 935040 | 0 | 327720 | 0 | 0 | 0 | 141291 | 4869769 | 0 | 0 | 0 |  | 463440 | 402624 | 1065058 | 1245480 | 169920 | 216480 | 170352 | 595200 | 0 | 0 | 0 | 7494100 | 0 | 4877000 | 184000 | 0 | 948816 | 499200 | 0 | 892502 | 0 | 182752 | 513730 | 416988 | 227340 | 814100 | 482140 | 3357120 | 1387200 | 0 | 428184 | 11600 | 933000 | 962640 | 1001400 | 985824 | 2229954 | 0 | 1247328 | 1558080 | 0 | 5191320 | 124000 | 0 | 200700 | 6636000 | 341952 | 129504 | 0 | 3199089 | 0 | 0 | 2390400 | 0 | 2714832 | 108945 | 1661760 | 3906240 | 1915272 | 8712000 | 1816800 | 1462493 | 544472 | 26641 | 2604436 | 491171 | 1336500 | 963300 | 343560 | 2007360 | 9178500 | 973440 | 324130 | 1330560 | 2566800 | 0 | 347040 | 224394 | 1400640 | 845280 | 7312400 | 13381 | 0 |  | 21256727 | 0 | 3734208 | 0 | 721920 | 0 | 0 | 0 | 0 | 0 | 138750 | 4101299 | 509600 | 81696 | 0 | 0 | 0 | 69521 | 0 | 261784 | 23280 | 34157 | 186241 | 55627 | 484404 | 458400 | 0 | 249174 | 0 | 0 | 4303500 | 0 | 0 | 3843055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6075345 | 555840 | 0 | 1328928 | 211536 | 1424956 | 0 | 53255 | 1063968 | 20981800 | 0 | 0 | 0 | 36300 | 701280 | 701568 | 0 | 0 | 8909091 | 246096 | 5040000 | 15943636 | 1420230 | 0 |  | 170261971 | 105207172 | 275469143 | 89154297 | 21256727 | 47207097 | 0 | 51222159 | 55178027 | 327720 | 13381 | 4599744 | 3357120 | 3152871 | 0
Fuel Cost | 0 | 0 | 0 | 6477030 | 0 | 2084290.88 | 0 | 9560680.5 | 8136720 |  | 0 | 10297230 | 7584359.16 | 8242790.4 | 15273407.5 | 12210126.75 | 5101418.56 | 0 | 0 | 11681774.74 | 16658429.76 | 31566705.6 | 0 | 0 | 0 | 0 | 3306182.4 | 8754736.5 | 8987167.44 | 351945 | 414000 | 0 | 0 | 0 | 15905030.4 | 0 | 88484.4 | 0 | 0 | 0 | 2310107.85 | 5064559.76 | 0 | 0 | 0 |  | 6047892 | 6715768.32 | 18127287.16 | 16826434.8 | 2154585.6 | 2504673.6 | 216347.04 | 1982016 | 0 | 0 | 0 | 8318451 | 0 | 5657320 | 237360 | 0 | 1072162.08 | 743808 | 0 | 1490478.34 | 0 | 3156127.04 | 6909668.5 | 571273.56 | 170505 | 1424675 | 361605 | 24104121.6 | 1512048 | 0 | 582330.24 | 184904 | 1278210 | 1270684.8 | 1742436 | 1705475.52 | 2564447.1 | 0 | 2419816.32 | 3552422.4 | 0 | 5243233.2 | 266600 | 0 | 397386 | 6636000 | 256464 | 98423.04 | 0 | 43667564.85 | 0 | 0 | 32222592 | 0 | 37600423.2 | 1273567.05 | 17149363.2 | 53359238.4 | 25415659.44 | 8015040 | 22092288 | 21147648.78 | 6887570.8 | 0 | 30576078.64 | 5348852.19 | 14206995 | 13071981 | 4428488.4 | 23646700.8 | 8444220 | 12606048 | 4683678.5 | 16884806.4 | 29210184 | 0 | 4532342.4 | 2681508.3 | 20967580.8 | 11132337.6 | 0 | 0 | 0 |  | 63770181 | 0 | 4182312.96 | 0 | 7515187.2 | 0 | 0 | 0 | 0 | 0 | 1993837.5 | 4593454.88 | 988624 | 890486.4 | 0 | 0 | 0 | 1165867.17 | 0 | 4094301.76 | 179256 | 565639.92 | 3149335.31 | 758196.01 | 8171895.48 | 948888 | 0 | 188624.718 | 0 | 0 | 22765515 | 0 | 0 | 4457943.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6014591.55 | 7470489.6 | 0 | 15721218.24 | 3056695.2 | 18096941.2 | 0 | 588467.75 | 12916571.52 | 189046018 | 0 | 0 | 0 | 410553 | 8226014.4 | 10755037.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 799813375.61 | 402682145.008 | 1202495520.618 | 87571378.458 | 63770181 | 57106532.95 | 0 | 663847308.37 | 211811533 | 88484.4 | 0 | 76147287.84 | 24104121.6 | 18048693 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 0 | 78 | 0 | 351 | 302 |  | 0 | 450 | 283 | 17 | 50 | 47 | 215 | 0 | 0 | 16 | 50 | 48 | 0 | 0 | 0 | 0 | 0 | 35 | 35 | 22 | 23 | 6 | 33 | 30 | 33 | 0 | 25 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 |  | 19 | 12 | 0 | 44 | 14 | 6 | 10 | 0 | 0 | 0 | 0 | 310 | 0 | 209 | 16 | 0 | 41 | 15 | 0 | 43 | 0 | 0 | 8 | 18 | 8 | 33 | 21 | 138 | 34 | 0 | 16 | 2 | 39 | 42 | 51 | 47 | 80 | 0 | 60 | 79 | 0 | 206 | 0 | 0 | 9 | 280 | 16 | 0 | 0 | 132 | 0 | 0 | 154 | 0 | 149 | 16 | 62 | 170 | 90 | 367 | 89 | 52 | 17 | 1 | 45 | 0 | 54 | 0 | 9 | 90 | 390 | 34 | 25 | 54 | 107 | 0 | 17 | 33 | 35 | 20 | 356 | 0 | 0 |  | 894 | 0 | 150 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 28 | 18 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 265 | 7 | 0 | 70 | 0 | 51 | 0 | 7 | 35 | 730 | 0 | 0 | 0 | 4 | 102 | 35 | 0 | 0 | 369 | 33 | 230 | 666 | 200 | 0 |  | 11485 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 0 | 81 | 0 | 400 | 347 | 0 | 0 | 450 | 245 | 77 | 95 | 55 | 192 | 0 | 0 | 90 | 102 | 150 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 22 | 23 | 24 | 33 | 32 | 49 | 0 | 25 | 0 | 0 | 0 | 8 | 214 | 0 | 0 | 0 | 0 | 19 | 40 | 85 | 66 | 0 | 19 | 10 | 36 | 0 | 0 | 0 | 290 | 0 | 217 | 0 | 0 | 49 | 40 | 0 | 43 | 0 | 24 | 52 | 18 | 11 | 33 | 21 | 164 | 100 | 0 | 19 | 0 | 40 | 43 | 53 | 50 | 80 | 0 | 62 | 84 | 0 | 208 | 0 | 0 | 9 | 260 | 8 | 0 | 0 | 296 | 0 | 0 | 173 | 0 | 149 | 0 | 88 | 179 | 147 | 330 | 115 | 88 | 34 | 0 | 230 | 54 | 54 | 88 | 31 | 90 | 400 | 71 | 0 | 162 | 107 | 0 | 17 | 0 | 115 | 35 | 250 | 0 | 0 |  | 799 | 0 | 150 | 0 | 77 | 0 | 0 | 0 | 0 | 0 | 24 | 163 | 27 | 16 | 0 | 0 | 0 | 32 | 0 | 46 | 0 | 8 | 40 | 8 | 33 | 21 | 0 | 11 | 0 | 0 | 220 | 0 | 0 | 135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 262 | 55 | 0 | 95 | 50 | 113 | 0 | 0 | 113 | 932 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 364 | 0 | 263 | 695 | 0 | 0 |  | 13362 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 0 | 81 | 0 | 400 | 340 | 0 | 0 | 450 | 300 | 90 | 95 | 55 | 220 | 0 | 0 | 92 | 102 | 150 | 0 | 0 | 0 | 0 | 35 | 35 | 55 | 22 | 23 | 26 | 33 | 33 | 50 | 0 | 25 | 0 | 0 | 0 | 25 | 225 | 0 | 0 | 0 | 0 | 19 | 48 | 85 | 66 | 0 | 6 | 10 | 20 | 0 | 0 | 0 | 300 | 0 | 200 | 0 | 0 | 45 | 50 | 0 | 43 | 0 | 35 | 52 | 18 | 11 | 33 | 21 | 153 | 100 | 0 | 19 | 0 | 41 | 42 | 51 | 50 | 112 | 0 | 65 | 86 | 0 | 210 | 18 | 0 | 9 | 280 | 16 | 8 |  | 300 | 0 | 0 | 170 | 0 | 149 | 0 | 100 | 200 | 150 | 375 | 115 | 105 | 17 | 0 | 230 | 54 | 54 | 114 | 9 | 100 | 400 | 72 | 0 | 162 | 107 | 0 | 17 |  | 115 | 35 | 300 |  |  |  | 905 | 0 | 200 |  | 99 | 0 | 0 | 0 | 50 | 65 | 40 | 170 | 25 | 48 | 0 | 0 | 0 | 32 | 40 | 90 | 0 | 42 | 40 | 43 | 36 | 22 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 180 |  | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 53 | 0 | 113 | 100 | 113 | 0 | 0 | 113 | 900 | 0 |  | 0 |  |  | 115 | 0 |  | 370 |  | 180 | 700 |  | 0
Forecast for Day | 0 | 0 | 0 | 180 | 0 | 78 | 0 | 400 | 340 | 0 | 0 | 450 | 280 | 75 | 68 | 48 | 220 | 0 | 0 | 92 | 102 | 150 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 22 | 23 | 25 | 33 | 33 | 50 | 0 | 25 | 0 | 0 | 0 | 25 | 225 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 44 | 0 | 6 | 10 | 7 | 0 | 0 | 0 | 300 | 0 | 200 | 0 | 0 | 45 | 50 | 0 | 43 | 0 | 0 | 30 | 18 | 11 | 33 | 21 | 135 | 50 | 0 | 19 | 1.6 | 41 | 42 | 51 | 50 | 112 | 0 | 65 | 86 | 0 | 210 | 18 | 0 | 9 | 280 | 16 | 8 | 0 | 280 | 0 | 0 | 150 | 0 | 115 | 20 | 100 | 200 | 100 | 375 | 100 | 70 | 17 | 5 | 120 | 0 | 54 | 114 | 9 | 100 | 400 | 72 | 50 | 162 | 107 | 0 | 17 | 30 | 36 | 35 | 320 |  |  |  | 905 | 0 | 170 | 0 | 66 | 0 | 0 | 0 | 40 | 40 | 8 | 170 | 20 | 48 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 28 | 22 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 332 | 53 | 0 | 50 | 0 | 50 | 0 | 8 | 50 | 900 | 0 |  | 0 | 6 | 100 | 50 | 0 |  | 370 | 30 | 150 | 660 | 130 | 0 |  |  |  |  | g | h | o | c | h | t | s
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 0 | 78 | 0 | 392 | 346 | 0 | 0 | 420 | 298 | 17 | 24 | 20 | 218 | 0 | 0 | 17 | 24 | 133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 23 | 27 | 33 | 16 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 208 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 44 | 0 | 6 | 10 | 2 | 0 | 0 | 0 | 300 | 0 | 192 | 0 | 0 | 48 | 50 | 0 | 43 | 0 | 0 | 0 | 18 | 11 | 33 | 18 | 112 | 49 | 0 | 19 | 1 | 40 | 42 | 53 | 50 | 112 | 0 | 60 | 83 | 0 | 207 | 0 | 0 | 9 | 275 | 16 | 8 | 0 | 30 | 0 | 0 | 48 | 0 | 71 | 9 | 62 | 179 | 20 | 376 | 49 | 34 | 17 | 2 | 86 | 0 | 54 | 51 | 9 | 38 | 400 | 50 | 8 | 17 | 107 | 0 | 0 | 12 | 36 | 0 | 270 | 0 | 0 | 0 | 774 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 35 | 0 | 34 | 0 | 1 | 0 | 670 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 376 | 14 | 172 | 660 | 40 | 0 | 0 |  |  |  | 136.3614 | 21.2567 | 55.8353 | 55.178 | 0.32772 | 3.3571 | 3.1529
275.4691
| Minimum Generation |  | 8871 | 6:00
| Highest Generation |  | 13362 | 21:00
| Day Peak Generation |  | 11485 | 12:00
| Evening Peak Generation |  | 13362 | 21:00
| HVDC Max Flow |  | 894 | 4:00
| HVDC EvPeak Flow |  | 799 | 21:00
| Load factor L.F |  | 85.9% | [161 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2023-04-05
Till now the maximum generation is : - |  |  |  | 14782 | 21:00 | Hrs on | 2022-04-16
The Summary of Yesterday's |  |  | 2023-04-04 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 11485 | MW Hour : | 12:00 | Min. Gen. at | 6:00 | 9961
Evening Peak Generation : |  |  | 13362 | MW Hour : | 21:00 | Available Max Generation : |  | 14279
E.P. Demand (at gen end) : |  |  | 13378 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 13800
Maximum Generation : |  |  | 13362 | MW Hour : | 21:00 | Reserve(Generation end) |  | 479
Total Gen. (MKWH) : |  |  | 275.4691 | System Load Factor : | 85.9% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 56 | MW at | 20:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2023-04-05
Actual : |  | 76.07 | Ft.(MSL) , | Rule curve : | 87.2 | Ft.( MSL )
Gas Consumed : |  | Total = | 1039 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 144677911.408
: |  |  | Coal : | 211811533 | Oil : | 739994596.21 | Total : | 1096484040.618
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 0 | 0:00 | 4376.0059 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 1211.4883 |  |  | 0 | 0%
Khulna Area |  | 0 | 0:00 | 1592.6656 |  |  | 0 | 0%
Rajshahi Area |  | 0 | 0:00 | 1405.3461 |  |  | 0 | 0%
Cumilla Area |  | 0 | 0:00 | 1199.8191 |  |  | 0 | 0%
Mymensingh Area |  | 15 | 360:00 | 986.316 |  |  | 0 | 0%
Sylhet Area |  | 0 | 0:00 | 445.6056 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 359.5404 |  |  | 0 | 0%
Rangpur Area |  | 0 | 0:00 | 778.813 |  |  | 0 | 0%
Total |  | 15 |  | 12355.6 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 1,2
2) Ghorasal-3,7
3) Kushiara 163 MW ST
4) Baghabari-100 MW & 71 MW
5) Raozan unit-1,2
6) Siddhirganj 210 MW .
7) Shajibazar 330 MW
8) Sirajganj-2 & 3
9) Bhula Nuton Biddut
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
08:12 | 12:05 | Tongi 230/132/33kV S/S 230 kV Bus-2 Scheduled S/D Due to maintenance work.
08:12 | 08:32 | Kaliakoir-Tongi 230kV Ckt-2 Tripped from Tongi end showing No relay operate relays Due to None
| 08:18 | Kodda 132/33kV S/S Tr-3 (426T) LT is restored.
09:35 | 12:44 | Bibiyana-Kaliakoir 400 kV Ckt-2 Scheduled S/D from Kaliakoir end due to Maintenance work .
09:43 | 10:42 | Sreepur 230/132/33kV S/S TRAFO-1 HT Project Work S/D Due to Project work .
10:03 | 20:03 | BIPTC S/S Baharampur-4 Forced S/D Due to Shutdown is taken from Baharampur S/S end at 10:03 BST
10:12 | 12:28 | Khulna(S)-PDB 330MW CCPP 230kV Ckt-1 Scheduled S/D from Khulna(S) end Due to SCADA Operation work by BPDB,Khulna.
10:12 | 13:29 | Aminbazar 400/230/132kV S/S Gopalganj-2 Scheduled S/D Due to CSD Commissioning .
10:42 | 13:09 | Ruppur 132/11kV S/S TR-02 HT Scheduled S/D Due to 11kV annual maintenance.
10:45 | 12:25 | Sreepur 230/132/33kV S/S TRAFO-2 LT Project Work S/D Due to Project Work .
11:33 | 12:23 | Sherpur(Bogura)-Sirajgonj 132 kV Ckt-2 Forced S/D from Bog-Sherpur 132/33kV end.
11:35 | 12:23 | Sirajganj 132/33kV S/S Sherpur-2 Forced S/D Due to a kite has been stuck to Sirajgonj- Sherpur ckt-02. For removing
this kite Sirajgonj- Sherpur ckt-02
11:44 | 12:32 | Kulaura 132/33kV S/S TR-1 HT Scheduled S/D Due to Red hot maintenance of REB Feeder-2.
12:29 | 12:41 | Sirajganj 132/33kV S/S Sherpur-1 Forced S/D Due to a kite removing.
13:05 | 14:11 | Chandraghona 132/33kV S/S TR-01(406T) LT Project Work S/D Due to Spare transformer T1 25/41 MVA Transfer.
13:06 | 14:10 | Chandraghona 132/33kV S/S TR-01(406T) HT Project Work S/D
13:12 | 14:35 | Shahjadpur 132/33kV S/S T-3(425T) LT Forced S/D Due to Red hot maintenance. | [5 empty] | 22 MW power interruption.
13:23 | 14:41 | Ruppur 132/11kV S/S TR-01 HT Scheduled S/D Due to 11kv annual maintenance .
13:25 | 14:15 | Khulna(S)-PDB 330MW CCPP 230kV Ckt-1 S/D from Khulna(S) end Due to SCADA work by BPDB,Khulna.
13:46 | 17:19 | Aminbazar 400/230/132kV S/S Gopalganj-2 Project Work S/D Due to CSD Test .
14:13 | 14:40 | Chandraghona 132/33kV S/S TR-02(416T) LT Project Work S/D
05:34 | 06:58 | Moghbazar-Rampura 132kV Ckt-1 Scheduled S/D from Rampura end Due to Shutdown by NLDC.
06:03 |  | Aminbazar 400/230kV T-3 was scheduled shutdown.
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2023-04-04 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4347000
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 81 | 1567136 | Engine problem
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 400 | 9105410
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 347 | 7534000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 9447000
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 77 | 737280 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 245 | 6832756 | FGMO
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 95 | 1152710 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 55 | 921519
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 469260
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 90 | 799027 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 192 | 4554838 | ST U/M.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 102 | 1183968
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 35 | 259920 | Engine problem
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 150 | 1947360
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 35 | 648499 | Engine problem
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 670184 | Engine problem
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 47 | 992820 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 822900
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 32 | 685700
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 49 | 935040 | 0:00
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 296 | 3199089
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Fuel shortage
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 0 | 0 | Fuel shortage
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Fuel shortage
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 2714832
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 88 | 1462493 | Engine problem
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 71 | 973440 | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 1330560
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 224394
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 845280 | Engine problem
| Dhaka area Total |  |  |  | 5847 | 3553 | 66364415
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 8 | 141291 | Low demand
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 108945
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 216480 | Fuel shortage
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 25 | 327720 | Low Water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 214 | 4869769
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 34 | 544472 | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 40 | 402624 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 85 | 1065058 | Engine problem
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 66 | 1245480 | Engine problem
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 88 | 1661760 | Engine problem
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 10 | 170352 | Gas shortage
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 36 | 595200
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 169920 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 26641
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 230 | 2604436 | Fuel shortage
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 491171
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 54 | 1336500 | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 90 | 2007360
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 107 | 2566800 | Engine problem
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 13381 | On test.
| Chattogram area Total |  |  |  | 2382 | 1160 | 20565360
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 217 | 4877000 | FGMO
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 290 | 7494100 | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | Gas shortage
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 250 | 7312400 | FGMO
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 49 | 948816
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 40 | 499200 | Gas shortage
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 0 | 184000 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 892502 | Engine problem
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 147 | 1915272
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 24 | 182752
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 179 | 3906240 | Engine problem
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 416988 | Engine problem
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 227340
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 164 | 3357120
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 814100
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 513730
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 21 | 482140 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Fuel shortage
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 88 | 963300 | Engine problem
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 31 | 343560 | Fuel shortage
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 347040 | Engine problem
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 115 | 1400640
| Cumilla Area Total |  |  |  | 3285 | 1789 | 37078240
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 100 | 1387200 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 428184 | Engine problem
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 11600
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 173 | 2390400 | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 115 | 1816800
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 324130
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 19 | 463440 | Engine problem
| Mymensingh Area Total |  |  |  | 614 | 426 | 6821754
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 40 | 933000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 43 | 962640 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 80 | 2229954 | ST U/M.
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 1001400
| Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 50 | 985824
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 0 | 129504 | Engine problem
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 62 | 1247328
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 84 | 1558080
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 208 | 5191320 | Machine problem
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 124000
| Sylhet 50MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 8 | 341952 | Engine problem
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 260 | 6636000 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 330 | 8712000 | FGMO
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 9 | 200700
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 400 | 9178500
| Sylhet Area Total |  |  |  | 2427 | 1627 | 39432202
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Fuel shortage
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 799 | 21256727
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 77 | 721920 | Engine problem
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve.
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel conservation
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve.
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 150 | 3734208 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 24 | 138750 | Engine problem
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve.
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 55 | 555840 | Fuel shortage
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 50 | 211536 | Transformer O/L
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 701280
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 0 | 0 | 0 | On test.
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 660*2 | 617 | 364 | 8909091 | On test.
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3001 | 1519 | 36229352
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 16 | 81696 | Line O/L
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 27 | 509600 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 163 | 4101299 | Machine problem
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 932 | 20981800 | Line O/L
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 0 | 0 | Under maint.
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Line O/L
| Barisal 307 MW |  | BCPCL | 307*1 | 307 | 263 | 5040000 | On test.
| Barisal Area Total |  |  |  | 2265 | 1401 | 30714395
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 32 | 69521 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve.
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 23280 | Contract Expired
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 8 | 34157 | Low demand
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 40 | 186241 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 135 | 3843055 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 262 | 6075345 | Gas shortage
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 33 | 484404 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 21 | 458400
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 249174
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 8 | 55627 | Low demand
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 46 | 261784 | Low demand
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Fuel shortage
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 95 | 1328928 | Engine problem
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 1063968
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 36300
| Adani Power Jharkhanda Ltd |  | Import | 0 | 0 | 695 | 15943636 | On test.
| Rajshahi Area Total |  |  |  | 2129 | 1499 | 30113820
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 220 | 4303500 | Machine problem
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 1424956
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 53255
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 55 | 701568 | Low demand
| Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 246096
| Teesta Solar Limited |  | BPCL | 16*12.5 | 0 | 0 | 1420230
| Rangpur Area Total |  |  |  | 750 | 388 | 8149605
| Total |  |  |  | 22700 | 13362 | 275469143
| Eastern Grid Total |  |  |  | 14555 | 8555 | 170261971
| Western Grid Total |  |  |  | 8145 | 4807 | 105207172
| National Grid Total |  |  |  | 22700 | 13362 | 275469143
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2023-04-04
| (a) ENTIRE EASTERN GRID : |  | 8635.8 | MW | (b) ENTIRE WESTERN GRID : |  | 4239 | MW
| i) Dhaka area |  | 4614.2 | MW | i) Khulna area |  | 1688.2 | MW
| ii) Chittagong area |  | 1294.6 | MW | ii) Rajshahi area |  | 1407.2 | MW
| iii) Comilla area |  | 1245 | MW | iii) Barisal area |  | 401.6 | MW
| iv) Mymensingh area |  | 1073 | MW | iv) Rangpur area |  | 742 | MW
| v) Sylhet area |  | 409 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 12874.8 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 10 | 08:00 | Chhatak | 26 | 21:00 | Kamrangirchar | 56 | 13:00 | Natore | 144 | 19:30 | Shitalakhya | 121 | 14:00
2 | AKSML | 94 | 12:00 | Chowmuhani | 195 | 21:00 | Kaptai | 3.8 | 19:00 | Nawabganj | 43.2 | 21:00 | Sholosohor | 32 | 13:00
3 | Aftabnagar | 34 | 20:00 | Chuadanga | 108 | 22:00 | Kazla | 92 | 22:00 | Netrakona | 104 | 17:00 | Shyampur | 144 | 00:00
4 | Agargaon | 79 | 14:00 | Coxsbazar | 120 | 21:00 | Keranigonj | 64 | 19:30 | New | 76 | 14:00 | Siddhirganj | 114 | 15:00
5 | Agrabad | 62 | 14:00 | Cumilla(N) | 138 | 21:00 | Khagrachori | 26 | 18:30 | Niamatpur | 97 | 21:00 | Sirajganj | 112 | 19:30
6 | Amnura | 81 | 21:00 | Cumilla(S) | 165 | 19:00 | Khulna | 106 | 20:00 | Noapara | 49 | 19:30 | Sonargaon | 80 | 01:00
7 | Ashuganj | 55 | 21:00 | Daudkandi | 141 | 21:00 | Khulshi | 170 | 14:00 | PHP | 4 | 22:00 | Sreemongol | 49 | 21:00
8 | BIPTC | N/A | N/A | Dhaka | 40 | 13:00 | Kishoreganj | 130 | 20:00 | Pabna | 106 | 19:30 | Sreepur | 22 | 09:00
9 | BSRM | 111 | 18:00 | Dhamrai | 116 | 11:00 | Kodda | 298 | 14:00 | Palashbari | 114 | 19:30 | Srinagar | 42.15 | 20:00
10 | Bagerhat | 89 | 20:00 | Dhanmondi | 126.2 | 13:00 | Kulaura | 30 | 13:00 | Panchagarh | 45 | 18:00 | Sunamganj | 40 | 21:00
11 | Bakulia | 94 | 19:30 | Dohazari | 82 | 19:00 | Kurigram | 61 | 18:30 | Patuakhali | 95 | 21:00 | Sylhet | 108 | 21:00
12 | Banani | 44 | 13:00 | Faridpur | 143 | 20:00 | Kushtia | 124 | 19:30 | Payra | 14.6 | 21:00 | TK | 28 | 21:00
13 | Bangabhaban | 19 | 11:00 | Fatullah | 64 | 15:00 | Lalbag | 80 | 13:00 | Postogola | 39 | 13:00 | Tangail | 226 | 19:30
14 | Barapukuria | 52 | 19:00 | Fenchuganj | 28 | 21:00 | Lalmonirhat | 40 | 18:00 | Purbachal | 20 | 22:00 | Thakurgaon | 78 | 19:00
15 | Barguna | 18 | 21:00 | Feni | 128 | 21:00 | Madanganj | 38 | 20:00 | Purbasadipur | 109 | 19:30 | Tongi | 130 | 15:00
16 | Barishal | 96 | 19:00 | GPH | 91 | 03:00 | Madaripur | 101 | 21:00 | Rahanpur_I | 0 | 00:00 | Ullon | 49 | 20:00
17 | Barishal-230 | 82 | 19:30 | Ghorashal | 64 | 19:00 | Madartek | 77 | 21:00 | Rahim | 36 | 08:00 | Uttara | 81 | 13:00
18 | Baroaulia | 61 | 07:00 | Goalpara | 38 | 19:30 | Madunaghat | 50 | 18:30 | Rajbari | 65 | 21:00 | UttaraNew | 17 | 13:00
19 | Baroirhat | 44 | 19:30 | Gollamari | 47 | 19:00 | Magura | 62 | 19:30 | Rajendrapur | 106 | 20:00 | Zigatola | 58 | 15:00
20 | Bashundhara | 156 | 15:00 | Gopalganj | 95.8 | 19:30 | Mahasthangarh | 86 | 19:30 | Rajshahi | 141 | 20:00
21 | BashundharaCement | 0 | 00:00 | Gulshan | 106 | 13:00 | Manikganj | 107 | 21:00 | Rajshahi-230 | 34 | 19:30
22 | Beanibazar | 50 | 21:00 | Halishahar | 77 | 14:00 | Maniknagar | 61 | 13:00 | Ramganj | 140 | 06:00
23 | Benapole | 62 | 19:30 | HaripurSBU | 156 | 13:00 | Matarbari | 39 | 22:00 | Rampur | 34 | 19:00
24 | Bhaluka | 106 | 01:00 | Hasnabad | 84 | 23:00 | Matuail | 64 | 13:00 | Rangamati | 14 | 18:30
25 | Bhandaria | 46 | 21:00 | Hathazari | 60 | 21:00 | Millgate | 77 | 11:00 | Rangpur | 133 | 18:00
26 | Bhangura | 34 | 19:00 | Ishurdi | 63 | 19:30 | Mirpur | 121.5 | 19:30 | Ruppur | 5 | 10:00
27 | Bheramara(GK) | 53 | 19:00 | Jaldhaka | 54 | 18:30 | Mirsorai | 4 | 21:00 | SSM | 14 | 13:00
28 | Bhulta | 253 | 11:00 | Jamalpur | 165 | 19:30 | Mithapukur | 36 | 19:00 | Saidpur | 95 | 17:00
29 | Bog-Sherpur | 50 | 03:00 | Jashore | 142 | 19:30 | Modern | 0 | 00:00 | Satkhira | 135 | 21:00
30 | Bogura | 147 | 21:00 | Jhenaidah | 130 | 21:00 | Mogbazar | 131 | 14:00 | Satmasjid | 107 | 21:00
31 | Borhanuddin | 57 | 23:00 | Joydebpur | 157 | 21:00 | Mongla | 27 | 10:00 | Savar | 192 | 14:00
32 | Brahmanbaria | 132 | 22:00 | Joypurhat | 47 | 21:00 | Motijheel | 34 | 12:00 | Shahjadpur | 106 | 20:00
33 | Cantonment | 125 | 15:00 | Juldah | 30 | 11:00 | Munshiganj | 107 | 21:00 | Shahjibazar | 96 | 16:00
34 | Chandpur | 61 | 19:30 | KSRM | 32.5 | 02:00 | Mymensingh | 220 | 20:00 | Shahmirpur | 34.5 | 06:00
35 | Chandraghona | 28 | 21:00 | Kabirpur | 297 | 15:00 | Naogaon | 119 | 21:00 | Shariatpur | 74 | 21:00
36 | Chapai | 65 | 23:00 | Kachua | 74 | 21:00 | Narail | 56 | 19:30 | Sherpur | 142 | 19:30
37 | Charsaidpur | 48.8 | 11:00 | Kallyanpur | 90 | 19:30 | Narinda | 70 | 13:00 | Shikalbaha | 29 | 23:00
38 | Chauddagram | 45 | 18:30 | Kalurghat | 32 | 14:00 | Narshingdi | 171 | 22:00 | Shikalbaha-230 | N/A | N/A
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2023-04-04 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 402 | 05:00 | 381 | 12:00 | Kaliakoir | 393 | 18:30 | 381 | 15:00
| Bhulta | 394 | 19:30 | 376 | 12:00 | Madunaghat_I | 412 | 19:00 | 378 | 12:00
| Bibiana | 406 | 04:00 | 397 | 05:00 | Payra | 420 | 19:30 | 407 | 14:00
| BIPTC | 400 | 08:00 | 387 | 16:00 | Rahanpur_I | 407 | 04:00 | 403 | 12:00
| Gopalganj | 415 | 20:00 | 385 | 12:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 234 | 18:30 | 218 | 12:00 | Hathazari | 240 | 18:00 | 221 | 12:00
| AKSML | 235 | 18:00 | 218 | 12:00 | Ishurdi | 235 | 18:30 | 225 | 12:00
| Aminbazar | 233 | 18:00 | 222 | 10:00 | Jhenaidah | 232 | 06:00 | 221 | 11:00
| Ashuganj | 237 | 19:30 | 226 | 12:00 | Kaliakoir | 233 | 18:30 | 224 | 15:00
| Baghabari | 231 | 03:00 | 224 | 11:00 | Keranigonj | 235 | 18:30 | 218 | 12:00
| Barapukuria | 223 | 05:00 | 214 | 17:00 | Khulna(S) | 237 | 06:00 | 227 | 11:00
| Barishal | 237 | 06:00 | 226 | 19:00 | Madunaghat_I | 240 | 19:00 | 218 | 12:00
| Bheramara | 234 | 20:00 | 222 | 12:00 | Maniknagar | 233 | 18:30 | 221 | 12:00
| Bhulta | 235 | 18:30 | 222 | 11:00 | Meghnaghat | 236 | 00:00 | 226 | 11:00
| Bibiana | 242 | 20:00 | 233 | 10:00 | Mirsorai | 236 | 19:30 | 219 | 12:00
| BIPTC | 235 | 20:00 | 224 | 11:00 | Rajshahi | 234 | 19:30 | 223 | 11:00
| Bogura | 227 | 19:30 | 220 | 17:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 238 | 07:00 | 229 | 22:00 | Rampura | 232 | 19:30 | 220 | 11:00
| BSRM | 238 | 19:30 | 218 | 12:00 | Shikalbaha | 238 | 18:30 | 222 | 12:00
| Cumilla(N) | 235 | 19:30 | 221 | 12:00 | Shyampur | 232 | 04:00 | 220 | 12:00
| Fenchuganj | 245 | 17:00 | 238 | 07:00 | Siddhirganj | 235 | 18:00 | 223 | 11:00
| Ghorashal | N/A | N/A | N/A | N/A | Sirajgonj | 230 | 19:30 | 225 | 10:00
| GPH | 238 | 19:30 | 218 | 12:00 | Sreepur | 235 | 19:30 | 230 | 09:00
| Haripur | 232 | 20:00 | 221 | 11:00 | Tongi | 232 | 19:30 | 216 | 11:00
| Hasnabad | 231 | 18:00 | 224 | 15:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 136 | 18:30 | 124 | 12:00 | Lalbag | 137 | 18:30 | 127 | 10:00
| Agargaon | 134 | 04:00 | 125 | 12:00 | Lalmonirhat | 130 | 00:00 | 124 | 17:00
| Agrabad | 137 | 18:00 | 124 | 12:00 | Madanganj | 136 | 20:00 | 127 | 12:00
| AKS | 134 | 18:30 | 126 | 22:00 | Madaripur | 133 | 08:00 | 127 | 22:00
| Aminbazar | 134 | 02:00 | 126 | 10:00 | Madartek | 136 | 18:30 | 124 | 11:00
| Amnura | 131 | 02:00 | 127 | 10:00 | Madunaghat | 140 | 19:30 | 126 | 12:00
| Ashuganj | 137 | 04:00 | 134 | 15:00 | Magura | 136 | 05:00 | 127 | 12:00
| Bagerhat | 132 | 02:00 | 125 | 11:00 | Mahasthangarh | 131 | 00:00 | 125 | 17:00
| Bakulia | 138 | 18:30 | 124 | 12:00 | Manikganj | 136 | 04:00 | 128 | 10:00
| Banani | 135 | 18:30 | 124 | 11:00 | Maniknagar | 135 | 18:30 | 125 | 12:00
| Bangabhaban | 132 | 01:00 | 125 | 11:00 | Matarbari | 126 | 18:30 | 112 | 23:00
| Barapukuria | 136 | 05:00 | 129 | 17:00 | Matuail | 136 | 19:30 | 127 | 12:00
| Barguna | 129 | 05:00 | 126 | 00:00 | Millgate | 134 | 05:00 | 123 | 10:00
| Barishal | 134 | 06:00 | 126 | 19:00 | Mirpur | 133 | 01:00 | 123 | 12:00
| Barishal-230 | 135 | 06:00 | 127 | 14:00 | Mithapukur | 133 | 05:00 | 125 | 17:00
| Baroaulia | 138 | 19:30 | 128 | 04:00 | Modern | 137 | 17:00 | 125 | 12:00
| Baroirhat | 135 | 18:00 | 124 | 12:00 | Mogbazar | 135 | 02:00 | 125 | 11:00
| Bashundhara | 134 | 06:00 | 123 | 11:00 | Mongla | 132 | 01:00 | 124 | 11:00
| BashundharaCement | 138 | 08:00 | 127 | 12:00 | Motijheel | 132 | 01:00 | 125 | 11:00
| Beanibazar | 135 | 07:00 | 131 | 13:00 | Munshiganj | 137 | 18:30 | 127 | 12:00
| Benapole | 133 | 06:00 | 122 | 14:00 | Mymensingh | 135 | 23:00 | 110 | 19:00
| Bhaluka | 130 | 06:00 | 111 | 14:00 | Naogaon | 129 | 01:00 | 119 | 12:00
| Bhandaria | 132 | 06:00 | 120 | 21:00 | Narail | 134 | 05:00 | 124 | 19:00
| Bhangura | 137 | 04:00 | 130 | 11:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bheramara | 135 | 05:00 | 130 | 11:00 | Narshingdi | 134 | 18:30 | 122 | 12:00
| Bheramara(GK) | 135 | 04:00 | 131 | 11:00 | Natore | 133 | 05:00 | 127 | 10:00
| Bhulta | 130 | 18:00 | 120 | 11:00 | Nawabganj | 138 | 18:30 | 127 | 10:00
| Bog-Sherpur | 134 | 01:00 | 127 | 17:00 | Netrakona | 130 | 05:00 | 110 | 19:00
| Bogura | 134 | 19:30 | 129 | 16:00 | New | 134 | 06:00 | 124 | 10:00
| Bogura-230 | 134 | 19:30 | 128 | 17:00 | Niamatpur | 126 | 01:00 | 120 | 18:00
| Brahmanbaria | 133 | 04:00 | 128 | 15:00 | Noapara | 134 | 06:00 | 126 | 11:00
| Cantonment | 133 | 04:00 | 123 | 12:00 | Pabna | 135 | 04:00 | 129 | 11:00
| Chandpur | 139 | 17:00 | 127 | 08:00 | Palashbari | 130 | 00:00 | 121 | 17:00
| Chandraghona | 138 | 17:00 | 126 | 12:00 | Panchagarh | 135 | 18:30 | 121 | 17:00
| Chapai | 132 | 04:00 | 129 | 10:00 | Patuakhali | 129 | 06:00 | 126 | 22:00
| Charsaidpur | 138 | 18:30 | 127 | 12:00 | Payra | 131 | 06:00 | 129 | 00:00
| Chauddagram | 135 | 18:00 | 125 | 12:00 | PHP | 134 | 16:00 | 123 | 12:00
| Chhatak | 134 | 03:00 | 132 | 13:00 | Postogola | 135 | 18:00 | 126 | 12:00
| Chowmuhani | 130 | 16:00 | 120 | 12:00 | Purbachal | 136 | 18:30 | 124 | 11:00
| Chuadanga | 132 | 05:00 | 120 | 21:00 | Purbasadipur | 133 | 20:00 | 122 | 17:00
| Coxsbazar | 125 | 09:00 | 112 | 13:00 | Rahim | 136 | 18:00 | 129 | 11:00
| Cumilla(N) | 137 | 18:00 | 128 | 12:00 | Rajbari | 131 | 04:00 | 125 | 11:00
| Cumilla(S) | 137 | 17:00 | 124 | 15:00 | Rajendrapur | 137 | 04:00 | 126 | 11:00
| Daudkandi | 137 | 20:00 | 125 | 12:00 | Rajshahi | 133 | 04:00 | 127 | 11:00
| Dhaka | 136 | 18:30 | 125 | 11:00 | Rajshahi-230 | 134 | 05:00 | 127 | 12:00
| Dhamrai | 133 | 18:30 | 120 | 12:00 | Ramganj | 133 | 15:00 | 122 | 12:00
| Dhanmondi | 137 | 18:30 | 128 | 12:00 | Rampur | 135 | 18:00 | 124 | 12:00
| Dohazari | 135 | 17:00 | 123 | 12:00 | Rampura | 134 | 19:30 | 124 | 11:00
| Faridpur | 132 | 04:00 | 126 | 11:00 | Rangamati | 138 | 19:30 | 127 | 12:00
| Fatullah | 138 | 18:30 | 127 | 12:00 | Rangpur | 133 | 20:00 | 124 | 17:00
| Fenchuganj | 139 | 20:00 | 135 | 05:00 | Ruppur | 137 | 05:00 | 130 | 11:00
| Feni | 135 | 17:00 | 124 | 12:00 | Saidpur | 132 | 06:00 | 122 | 17:00
| Ghorashal | 139 | 00:00 | 131 | 12:00 | Satkhira | 133 | 06:00 | 125 | 18:30
| Goalpara | 136 | 06:00 | 129 | 11:00 | Satmasjid | 134 | 18:30 | 124 | 11:00
| Gollamari | 132 | 07:00 | 125 | 12:00 | Savar | 135 | 19:30 | 124 | 12:00
| Gopalganj | 132 | 06:00 | 124 | 12:00 | Shahjadpur | 140 | 02:00 | 134 | 11:00
| Gopalganj-400 | 135 | 06:00 | 128 | 12:00 | Shahjibazar | 135 | 20:00 | 132 | 08:00
| Gulshan | 135 | 18:30 | 124 | 11:00 | Shahmirpur | 139 | 18:00 | 127 | 12:00
| Halishahar | 138 | 18:00 | 125 | 12:00 | Shariatpur | 134 | 06:00 | 126 | 22:00
| Haripur | 136 | 18:00 | 129 | 11:00 | Sherpur | 136 | 22:00 | 115 | 17:00
| HaripurSBU | 136 | 18:00 | 129 | 11:00 | Shikalbaha | 139 | 18:30 | 126 | 12:00
| Hasnabad | 135 | 18:00 | 127 | 11:00 | Shikalbaha-230 | 138 | 18:30 | 126 | 13:00
| Hathazari | 140 | 18:00 | 129 | 12:00 | Shitalakhya | 136 | 18:30 | 127 | 11:00
| Ishurdi | 136 | 05:00 | 130 | 12:00 | Sholosohor | 138 | 18:30 | 125 | 12:00
| Jaldhaka | 131 | 05:00 | 120 | 17:00 | Shyampur | 135 | 18:30 | 126 | 12:00
| Jamalpur | 139 | 22:00 | 119 | 16:00 | Shyampur-230 | 134 | 18:00 | 127 | 11:00
| Jashore | 132 | 05:00 | 125 | 11:00 | Siddhirganj | 136 | 18:00 | 128 | 11:00
| Jhenaidah | 137 | 05:00 | 129 | 11:00 | Sirajganj | 135 | 05:00 | 128 | 11:00
| Jhenaidah-230 | 137 | 05:00 | 129 | 12:00 | Sonargaon | 137 | 20:00 | 128 | 11:00
| Joydebpur | 139 | 17:00 | 128 | 12:00 | Sreemongol | 135 | 19:30 | 132 | 08:00
| Joypurhat | 128 | 01:00 | 116 | 12:00 | Sreepur | 132.5 | 15:00 | 130 | 09:00
| Juldah | 137 | 18:00 | 128 | 13:00 | Srinagar | 135 | 19:30 | 126 | 12:00
| Kabirpur | 138 | 13:00 | 120 | 11:00 | SSM | 140 | 18:00 | 130 | 10:00
| Kachua | 137 | 17:00 | 128 | 06:00 | Sunamganj | 132 | 00:00 | 130 | 12:00
| Kaliakoir | 140 | 18:00 | 128 | 15:00 | Sylhet | 135 | 03:00 | 133 | 11:00
| Kallyanpur | 134 | 02:00 | 124 | 12:00 | Tangail | 136 | 06:00 | 126 | 16:00
| Kalurghat | 139 | 18:30 | 126 | 12:00 | Thakurgaon | 135 | 20:00 | 120 | 17:00
| Kamrangirchar | 136 | 18:30 | 127 | 10:00 | TK | 137 | 18:00 | 125 | 12:00
| Kaptai | 136 | 17:00 | 126 | 12:00 | Tongi | 136 | 04:00 | 126 | 11:00
| Kazla | 133 | 00:00 | 124 | 13:00 | Ullon | 136 | 18:00 | 124 | 11:00
| Keranigonj | 138 | 18:30 | 127 | 10:00 | Uttara | 135 | 18:30 | 124 | 12:00
| Khagrachori | 138 | 18:30 | 125 | 12:00 | UttaraNew | 133 | 01:00 | 123 | 12:00
| Khulna | 135 | 01:00 | 128 | 11:00 | Zigatola | 136 | 19:00 | 125 | 11:00
| Khulna(S) | 137 | 06:00 | 129 | 11:00
| Khulshi | 136 | 18:30 | 124 | 12:00
| Kishoreganj | 131 | 05:00 | 120 | 21:00
| Kodda | 139 | 06:00 | 128 | 12:00
| KSRM | 136 | 17:00 | 128 | 12:00
| Kulaura | 138 | 03:00 | 135 | 13:00
| Kurigram | 133 | 05:00 | 121 | 17:00
| Kushtia | 136 | 06:00 | 130 | 10:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2023-04-04
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 570 | 7505 | 4786 | 12291 |  |  |  | QF-LDC-11
0:30 | 665 | 7006 | 4433.5 | 11439.5 | Date: | 2023-04-04
1:00 | 760 | 6507 | 4081 | 10588
1:30 | 750 | 6381 | 4039 | 10420
2:00 | 740 | 6255 | 3997 | 10252
2:30 | 730 | 6363 | 4019.5 | 10382.5 | [5 empty] | Gen. at Eve. Peak | 13362 | 13362 MW (21:00 )
3:00 | 720 | 6471 | 4042 | 10513 | [6 empty] | 21:00
3:30 | 722 | 6496.5 | 4027.5 | 10524 | [5 empty] | Gen. at Day Peak | 11485 | 11485 MW (12:00 )
4:00 | 724 | 6522 | 4013 | 10535 | [6 empty] | 12:00
4:30 | 772 | 6117 | 3928 | 10045 | [5 empty] | Highest Generation | 13362
5:00 | 820 | 5712 | 3843 | 9555 | [6 empty] | 21:00
5:30 | 845 | 5430 | 3783 | 9213
6:00 | 870 | 5148 | 3723 | 8871
6:30 | 810 | 5218 | 3692 | 8910
7:00 | 750 | 5288 | 3661 | 8949
7:30 | 725 | 5496.5 | 3676 | 9172.5
8:00 | 700 | 5705 | 3691 | 9396
8:30 | 758 | 5999.5 | 3793 | 9792.5
9:00 | 816 | 6294 | 3895 | 10189
9:30 | 823 | 6416 | 4007 | 10423
10:00 | 830 | 6538 | 4119 | 10657
10:30 | 850 | 6631.5 | 4180.5 | 10812
11:00 | 870 | 6725 | 4242 | 10967
11:30 | 805 | 6881 | 4345 | 11226
12:00 | 740 | 7037 | 4448 | 11485
12:30 | 735 | 7250 | 4457 | 11707
13:00 | 730 | 7463 | 4466 | 11929
13:30 | 815 | 7577 | 4464 | 12041
14:00 | 900 | 7691 | 4462 | 12153
14:30 | 825 | 7689 | 4517.5 | 12206.5
15:00 | 750 | 7687 | 4573 | 12260
15:30 | 725 | 7668 | 4439 | 12107
16:00 | 700 | 7649 | 4305 | 11954
16:30 | 645 | 7635.5 | 4248 | 11883.5
17:00 | 590 | 7622 | 4191 | 11813
17:30 | 410 | 7679.5 | 4167 | 11846.5
18:00 | 230 | 7737 | 4143 | 11880
18:30 | 153 | 8031 | 4256 | 12287
19:00 | 76 | 8325 | 4369 | 12694
19:30 | 80 | 8465 | 4724 | 13189
20:00 | 56 | 8413 | 4789 | 13202 |  |  |  | Executive Engineer
20:30 | 92 | 8484 | 4798 | 13282 |  |  |  | Network Operation Division
21:00 | 128 | 8555 | 4807 | 13362
21:30 | 180 | 8492.5 | 4796.5 | 13289
22:00 | 232 | 8430 | 4786 | 13216 |  |  |  |  | Page 6 of 7
22:30 | 316 | 8219 | 4804 | 13023
23:00 | 400 | 8008 | 4822 | 12830
23:30 | 485 | 7756.5 | 4804 | 12560.5
24:00 | 570 | 7505 | 4786 | 12291
13362 MW (21:00 )
11485 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2023-04-04 |  | Energy |  | 275469143
[13 empty] | 2023-04-04 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 3683 | 892 | 2151 | 0 | 2604 | 2486 | 0 | 0 | 321 | 154 | 0 | 0
0:30 | 3687.5 | 892.5 | 2083 | 0 | 2059 | 2369.5 | 0 | 0 | 202 | 146 | 0 | 0 |  | Date: | 43558
1:00 | 3692 | 893 | 2015 | 0 | 1514 | 2253 | 0 | 0 | 83 | 138 | 0 | 0
1:30 | 3656.5 | 893 | 1960.5 | 0 | 1472.5 | 2219.5 | 0 | 0 | 83 | 135 | 0 | 0 | [8 empty] | Total Energy | 275.4691 | Total Energy Gen MKWHr Energy Not Served MKWHr Energy Requirement MKWHr | Total Energy Gen 275.469 MKWHr Energy Not Served 0.284 MKWHr Energy Requirement 275.753 MKWHr
2:00 | 3621 | 893 | 1906 | 0 | 1431 | 2186 | 0 | 0 | 83 | 132 | 0 | 0 | [8 empty] | Energy not Served | 0.28416
2:30 | 3648.5 | 892.5 | 1990 | 0 | 1438 | 2200.5 | 0 | 0 | 83 | 130 | 0 | 0 | [8 empty] | Energy Requirement | 275.7533
3:00 | 3676 | 892 | 2074 | 0 | 1445 | 2215 | 0 | 0 | 83 | 128 | 0 | 0
3:30 | 3691 | 893 | 2067.5 | 0 | 1478.5 | 2197 | 0 | 0 | 66 | 131 | 0 | 0 | [7 empty] | Shortage
4:00 | 3706 | 894 | 2061 | 0 | 1512 | 2179 | 0 | 0 | 49 | 134 | 0 | 0
4:30 | 3704.5 | 893.5 | 1903 | 0 | 1243.5 | 2145 | 0 | 0 | 32.5 | 123 | 0 | 0
5:00 | 3703 | 893 | 1745 | 0 | 975 | 2111 | 0 | 0 | 16 | 112 | 0 | 0
5:30 | 3563 | 869.5 | 1710.5 | 0 | 854.5 | 2098 | 0 | 0 | 8 | 109 | 0.5 | 0
6:00 | 3423 | 846 | 1676 | 0 | 734 | 2085 | 0 | 0 | 0 | 106 | 1 | 0
6:30 | 3492 | 834.5 | 1685 | 0 | 722 | 2037 | 0 | 0 | 0 | 107 | 32.5 | 0 | [6 empty] | Coal
7:00 | 3561 | 823 | 1694 | 0 | 710 | 1989 | 0 | 0 | 0 | 108 | 64 | 0
7:30 | 3612.5 | 792.5 | 1784 | 0 | 753 | 1988 | 0 | 0 | 14 | 116 | 112.5 | 0 | [5 empty] | Oil
8:00 | 3664 | 762 | 1874 | 0 | 796 | 1987 | 0 | 0 | 28 | 124 | 161 | 0
8:30 | 3740 | 757 | 1935.5 | 0 | 939.5 | 2015.5 | 12.5 | 0 | 46 | 129 | 217.5 | 0
9:00 | 3816 | 752 | 1997 | 0 | 1083 | 2044 | 25 | 0 | 64 | 134 | 274 | 0
9:30 | 3730 | 798.5 | 2021 | 0 | 1281.5 | 2052.5 | 25 | 0 | 70 | 134 | 310.5 | 0
10:00 | 3644 | 845 | 2045 | 0 | 1480 | 2061 | 25 | 0 | 76 | 134 | 347 | 0
10:30 | 3647 | 869 | 2038 | 0 | 1551.5 | 2080 | 25 | 0 | 79 | 139 | 383.5 | 0
11:00 | 3650 | 893 | 2031 | 0 | 1623 | 2099 | 25 | 0 | 82 | 144 | 420 | 0
11:30 | 3681 | 893.5 | 2033 | 0 | 1814 | 2132 | 25 | 0 | 85 | 141 | 421.5 | 0
12:00 | 3712 | 894 | 2035 | 0 | 2005 | 2165 | 25 | 0 | 88 | 138 | 423 | 0
12:30 | 3739 | 893.5 | 2040.5 | 0 | 2130.5 | 2181.5 | 25 | 0 | 132.5 | 143 | 421.5 | 11
13:00 | 3766 | 893 | 2046 | 0 | 2256 | 2198 | 25 | 0 | 177 | 148 | 420 | 22
13:30 | 3766 | 893 | 2046 | 0 | 2256 | 2198 | 25 | 0 | 177 | 148 | 420 | 22
14:00 | 3766 | 893 | 2046 | 0 | 2256 | 2198 | 25 | 0 | 177 | 148 | 420 | 22
14:30 | 3738.5 | 893 | 2025 | 0 | 2411 | 2247.5 | 25 | 0 | 241.5 | 151 | 362 | 31
15:00 | 3711 | 893 | 2004 | 0 | 2566 | 2297 | 25 | 0 | 306 | 154 | 304 | 40
15:30 | 3692.5 | 892.5 | 2002 | 0 | 2497.5 | 2287.5 | 25 | 0 | 317.5 | 149 | 243.5 | 41
16:00 | 3674 | 892 | 2000 | 0 | 2429 | 2278 | 25 | 0 | 329 | 144 | 183 | 42
16:30 | 3666 | 892.5 | 1949 | 0 | 2478 | 2265.5 | 25 | 9 | 328 | 141 | 129.5 | 51
17:00 | 3658 | 893 | 1898 | 0 | 2527 | 2253 | 25 | 18 | 327 | 138 | 76 | 60
17:30 | 3611 | 893.5 | 1855.5 | 0 | 2700 | 2197.5 | 25 | 9 | 366 | 148 | 41 | 59
18:00 | 3564 | 894 | 1813 | 0 | 2873 | 2142 | 25 | 0 | 405 | 158 | 6 | 58
18:30 | 3590 | 866 | 1911 | 0 | 3130 | 2191.5 | 25 | 0 | 408.5 | 162 | 3 | 37.5
19:00 | 3616 | 838 | 2009 | 0 | 3387 | 2241 | 25 | 0 | 412 | 166 | 0 | 17
19:30 | 3628 | 799 | 1985 | 0 | 3772 | 2382 | 25 | 0 | 436 | 162 | 0 | 18.5
20:00 | 3533 | 799 | 2019 | 0 | 3801 | 2421 | 25 | 0 | 442 | 162 | 0 | 20
20:30 | 3610.5 | 799 | 2053.5 | 0 | 3737.5 | 2447.5 | 25 | 0 | 446 | 163 | 0 | 17.5
21:00 | 3688 | 799 | 2088 | 0 | 3674 | 2474 | 25 | 0 | 450 | 164 | 0 | 15
21:30 | 3717.5 | 815.5 | 2103 | 0 | 3575 | 2486.5 | 25 | 0 | 403.5 | 163 | 0 | 7.5
22:00 | 3747 | 832 | 2118 | 0 | 3476 | 2499 | 25 | 0 | 357 | 162 | 0 | 0
22:30 | 3707.5 | 862.5 | 2131 | 0 | 3296.5 | 2495.5 | 12.5 | 0 | 354.5 | 163 | 0 | 0
23:00 | 3668 | 893 | 2144 | 0 | 3117 | 2492 | 0 | 0 | 352 | 164 | 0 | 0
23:30 | 3675.5 | 892.5 | 2147.5 | 0 | 2860.5 | 2489 | 0 | 0 | 336.5 | 159 | 0 | 0 |  | Max Temp. in Dhaka |  | 33.4° C
24:00 | 3683 | 892 | 2151 | 0 | 2604 | 2486 | 0 | 0 | 321 | 154 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 275.469 MKWHr Energy Not Served 0.284 MKWHr Energy Requirement 275.753 MKWHr
Shortage
Note on W13: Author:

## Generation
g | 2023-04-04
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | [8 empty] | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 |  |  | 327720
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [13 empty] | 0 | 18 | 8 | 8 | 8 |  | 11 | 25 | 25 | 8 | 8 | 8 | 12 | 141291
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 4 | 4 | 9 |  | 11 | 16 | 20 | 17 | 9 | 7 | 2 | 0 | [8 empty] | 108945
6 | Sikalbaha 225MW CCPP (Gas) | 187 | 189 | 182 | 183 | 183 | 184 | 184 | 184 | 215 | 214 | 213 | 214 | 214 | 216 | 216 | 220 | 221 | 224 |  | 223 | 221 | 214 | 214 | 207 | 202 | 200 | 4869769
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 51 | 51 | 51 | 17 | [9 empty] | 74 | 81 | 83 | 84 | 84 |  | 84 | 84 | 84 | 85 | 85 | 85 | 85 | 1065058
12 | Hathazari 100 MW peaking PP | [11 empty] | 12 | 34 | 24 | 24 | 31 | 34 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 402624
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 25 | 34 |  | 34 | 34 | 34 | 34 | 34 | 34 | 17 | 544472
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP | [13 empty] | 8 | 15 | 29 | 23 | 31 |  | 31 | 24 | 30 | 24 |  |  |  | 182752
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 190 | 170 | 170 | 170 | 170 | 170 | 140 | 222 | 206 | 210 | 210 | 215 | 210 | 206 | 207 | 160 | 160 | 160 |  | 160 | 160 | 140 | 192 | 222 | 180 | 180 | 4554838
18 | Kodda 300 MW PP Unit-2 (Summit) | 15 | 15 | 15 | 15 | [5 empty] | 27 | 32 | 132 | 145 | 183 | 223 | 242 | 257 | 260 |  | 293 | 294 | 296 | 296 | 260 | 195 | 195 | 3199089
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 16 | 16 | 16 | 16 | 16 | 16 | [12 empty] | 184000
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4347000
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 50 | 50 | 50 | 50 | 50 | 20 | 20 | 20 | 20 | 20 | 20 | 41 | 40 | 42 | 42 | 42 | 47 | 47 |  | 47 | 47 | 49 | 49 | 49 | 49 | 49 | 948816
33 | Ashuganj 225 MW CCPP | 191 | 199 | 197 | 204 | 209 | 168 | 205 | 213 | 216 | 213 | 210 | 209 | 210 | 182 | 204 | 207 | 182 | 213 |  | 212 | 217 | 217 | 217 | 218 | 182 | 182 | 4877000
34 | Ashuganj 450 MW CCPP(South) | [26 empty] | 0
| Ashuganj 450 MW CCPP(North) | 280 | 280 | 280 | 280 | 280 | 280 | 325 | 280 | 280 | 305 | 315 | 310 | 310 | 335 | 280 | 285 | 290 | 290 |  | 310 | 290 | 290 | 290 | 285 | 290 | 285 | 7494100
| Ashuganj 420 MW CCPP(East) | 330 | 300 | 300 | 300 | 300 | 250 | 250 | 300 | 450 | 320 | 320 | 356 | 356 | 328 | 316 | 317 | 316 | 323 |  | 270 | 270 | 250 | 250 | 250 | 250 | 270 | 7312400
35 | Ashuganj 55 MW PP (Precision) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 5 | 5 | 5 | 8 |  | 20 | 30 | 30 | 40 | 47 | 48 | 50 | 499200
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 381 | 354 | 364 | 386 | 383 | 342 | 318 | 389 | 415 | 378 | 351 | 351 | 381 | 400 | 401 | 400 | 401 | 364 |  | 348 | 400 | 394 | 400 | 361 | 351 | 351 | 9105410
40 | Meghnaghat 450 MW CCPP(MPL) | 450 | 350 | 400 | 400 | 400 | 360 | 330 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 420 | 420 | 420 |  | 420 | 450 | 450 | 450 | 450 | 450 | 450 | 9447000
41 | Haripur 360MW CCPP(HPL) | 302 | 302 | 342 | 342 | 302 | 263 | 261 | 352 | 309 | 303 | 302 | 302 | 302 | 340 | 323 | 327 | 327 | 307 |  | 312 | 312 | 311 | 347 | 341 | 336 | 336 | 7534000
42 | RPCL 210MW CCPP | 94 | 96 | 94 | 84 | 84 | 84 | 47 | 47 | 47 | 34 | 34 | 34 | 34 | 33 | 31 | 30 | 31 | 31 |  | 34 | 50 | 78 | 100 | 101 | 101 | 86 | 1387200
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 0 | 5 | 8 | 19 | 24 | 50 | 25 | 53 | 46 | 28 | 13 | 5 | 1 | [8 empty] | 324130
44 | Fenchugonj CCPP Phase-1 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 38 | 39 | 39 | 39 | 37 | 39 | 39 | 37 | 37 | 37 |  | 38 | 38 | 38 | 40 | 40 | 40 | 40 | 933000
45 | Fenchugonj CCPP Phase-2 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 43 | 42 | 42 | 42 | 962640
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 40 | 40 | 40 | 40 | 40 | 40 | 64 | 40 | 62 | 61 | 60 | 60 | 60 | 50 | 55 | 60 | 52 | 40 |  | 61 | 62 | 62 | 62 | 62 | 61 | 62 | 1247328
48 | Shahjibazar 86MW PP (Shahjibazar) | 50 | 50 | 86 | 86 | 10 | 10 | 10 | 10 | 81 | 81 | 80 | 79 | 81 | 81 | 81 | 82 | 82 | 40 |  | 82 | 83 | 83 | 84 | 83 | 84 | 83 | 1558080
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 207 | 209 | 208 | 207 | 208 | 209 | 209 | 207 | 209 | 208 | 208 | 206 | 206 | 206 | 205 | 204 | 203 | 203 |  | 203 | 203 | 203 | 208 | 208 | 208 | 208 | 5191320
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 19 | 19 | [20 empty] | 124000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 8 | 8 | 8 | 8 | 8 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 200700
54 | Hobiganj 11MW PP Cofidence-E | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | [5 empty] | 3 | 8 | 8 | 8 |  | 8 | 8 |  |  | 8 |  | 8 | 129504
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 53 | 53 | 53 | 11 | 11 | 11 | 11 | 51 | 51 | 51 | 51 | 50 | 50 | 50 | 53 | 22 | 22 |  | 53 | 48 | 53 | 53 | 53 | 53 | 53 | 1001400
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 8 |  | 8 | 8 | 8 | 8 | 8 | 16 | 16 | 341952
57 | Bibiana-II 341 MW CCPP (Summit) | 260 | 265 | 275 | 270 | 265 | 270 | 270 | 275 | 270 | 280 | 280 | 280 | 285 | 280 | 285 | 265 | 270 | 280 |  | 270 | 265 | 270 | 260 | 265 | 270 | 260 | 6636000
| Bibiyana South 400 MW | 360 | 390 | 390 | 390 | 400 | 340 | 400 | 400 | 360 | 360 | 370 | 390 | 396 | 385 | 395 | 395 | 400 | 400 |  | 400 | 354 | 360 | 400 | 400 | 400 | 400 | 9178500
58 | Nababganj 55 MW PP (Southern power ) | 35 | 35 | 35 | 35 | 0 |  |  |  | 2 | 23 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 |  |  | 670184
59 | Tangail Palli Power Gen 22 MW | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 463440
60 | Barabkunda 22 MW PP (Regent) | 8 | 5 | 8 | 8 | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 10 | 7 | 7 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 5 | 5 | 10 | 170352
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 469260
62 | Tangail 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 16 | 16 | 16 | 16 | 16 | 16 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 428184
63 | Impoprt (Tripura) | 138 | 132 | 128 | 134 | 112 | 106 | 108 | 124 | 134 | 134 | 144 | 138 | 148 | 158 | 154 | 144 | 138 | 158 |  | 166 | 162 | 162 | 164 | 162 | 164 | 154 | 3357120
64 | Malancha, Ctg. EPZ (United) | 31 | 40 | 40 | 40 | 40 | 40 | 21 | 9 | 6 | 6 | 6 | 0 | 2 | 2 | 3 | 13 | 26 | 35 |  | 35 | 38 | 36 | 36 | 36 | 36 | 38 | 595200
65 | Feni 22MW PP (Doreen) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 416988
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 227340
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 814100
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 20 | 18 | 20 | 21 | 20 | 20 | 21 | 15 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 482140
69 | Summit Ashulia | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 |  | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 552000
70 | Summit Madhabdi | 25 | 25 | 25 | 25 | 25 | 25 | 6 | 23 | 5 | 5 | 17 | 6 | 20 | 19 | 19 | 19 | 19 | 17 |  | 12 | 17 | 24 | 24 | 24 | 27 | 27 | 440820
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 822900
72 | Rupganj 33 MW PP(Summit) | 22 | 22 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 30 | 30 | 30 | 29 | 15 | 15 | 15 | 26 |  | 26 | 32 | 32 | 32 | 32 | 32 | 33 | 685700
73 | Ghorashal 108MW PP (Regent) | 81 | 81 | 81 | 81 | 23 | 23 | 23 | 30 | 65 | 70 | 72 | 78 | 81 | 81 | 78 | 81 | 43 | 33 |  | 81 | 81 | 78 | 81 | 81 | 81 | 78 | 1567136
| Feni Lanka Power | [12 empty] | 70 | 99 | 114 | 88 | 88 | 88 |  | 99 | 114 | 114 | 88 | 51 | 34 | 70 | 963300
| Chowmuhani 113 MW | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 8 | 8 | 9 | 9 | 8 |  | 9 | 9 | 9 | 31 | 56 | 57 | 9 | 343560
| Manikgonj 162MW PP(MPGL) | 35 | 35 | 35 | 35 |  |  |  |  | 54 | 54 | 54 | 54 | 54 | 72 | 72 | 72 | 72 | 108 |  | 126 | 162 | 162 | 162 | 110 | 21 | 17 | 1330560
77 | Siddhirganj 100 PP(Dutch Bangla) | 8 | 8 | 8 | 8 |  |  |  |  | 2 | 16 | 16 | 16 | 17 | 36 | 70 | 70 | 40 | 46 |  | 62 | 90 | 90 | 90 | 85 | 85 | 85 | 799027
78 | Gazipur 52 MW PP | 25 | 25 | 25 | 25 | 8 | 47 | 47 | 50 | 42 | 42 | 42 | 33 | 42 | 45 |  | 21 | 49 | 49 |  | 49 | 49 | 49 | 49 | 49 | 42 | 42 | 935040
79 | Kodda 150 MW PP | 32 | 32 | 32 | 32 | 16 |  |  | 16 | 36 | 48 | 48 | 48 | 115 | 115 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 1947360
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 8 | 8 | 8 | 8 | [5 empty] | 1 | 6 | 8 | 8 | 8 | 16 | 25 | 34 | 51 |  | 51 | 51 | 52 | 52 | 52 | 52 | 52 | 513730
| Gazipur 100 MW PP | 34 | 17 | 17 | 17 | 17 | 17 | 17 | 40 | 52 | 52 | 52 | 52 | 52 | 56 | 70 | 105 | 105 | 105 |  | 105 | 105 | 105 | 88 | 88 | 88 | 70 | 1462493
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 1 | 3 | 3 | 0 | 1 | 2 | 4 | 3 | 1 | 1 | [9 empty] | 26641
| Jodiac Power | 17 | 17 | 17 | 28 | 35 | 17 | [9 empty] | 16 | 35 | 36 |  | 36 | 54 | 54 | 54 | 36 | 36 | 17 | 491171
| Karnaphuli Power Ltd. | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1336500
82 | Madanganj 102 PP(Summit) | 17 | 17 | 17 | 17 | 2 |  |  |  | 2 | 37 | 50 | 50 | 50 | 60 | 80 | 95 | 95 | 95 |  | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 1152710
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP ( Summit) | 266 | 269 | 290 | 245 | 250 | 245 | 310 | 280 | 255 | 281 | 273 | 283 | 284 | 301 | 280 | 287 | 270 | 274 |  | 305 | 240 | 245 | 245 | 255 | 275 | 260 | 6832756
87 | Meghnaghat 100 MW(IEL) | 8 | 9 | 8 | 8 | [5 empty] | 14 | 17 | 17 | 14 | 14 | 38 | 51 | 42 | 45 |  | 54 | 84 | 76 | 77 | 83 | 85 | 84 | 737280
| Meghnaghat 104 MW PP (OPCL) | 17 | 17 | 17 | 17 |  |  |  |  | 17 | 33 | 34 | 34 | 35 | 49 | 66 | 71 | 72 | 71 |  | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 973440
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 55 | 55 | 55 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 55 | 55 | 44 | 66 |  | 66 | 66 | 66 | 66 | 66 | 70 | 55 | 1245480
92 | Fenchuganj 44MW (Energyprima) | 50 | 50 | 50 | 50 | 10 | 10 | 10 | 10 | 50 | 50 | 50 | 47 | 47 | 50 | 46 | 49 | 49 | 20 |  | 35 | 50 | 50 | 50 | 50 | 50 | 50 | 985824
93 | Ashuganj 51 MW PP (Midland) | 43 | 43 | 43 | 43 | 10 | 10 | 10 | 10 | 27 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 10 | 10 |  | 25 | 43 | 43 | 43 | 43 | 43 | 43 | 892502
94 | Gagnagar 102 MW PP (Digital Power) | 8 | 8 | 8 | 8 |  |  |  |  | 8 | 16 | 16 | 50 | 102 | 102 | 102 | 60 | 58 | 74 |  | 84 | 102 | 102 | 102 | 102 | 102 | 102 | 1183968
95 | Patenga 50MW PP (Baraka) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 7 |  | 19 | 19 | 19 | 19 | 19 | 19 | 9 | 216480
96 | Chattogram 108 MW PP (ECPV) | [8 empty] | 5 | 7 | 11 | 14 | 14 | 18 | 18 | 18 | 19 | 14 |  | 13 | 12 | 12 |  |  |  |  | 169920
97 | katpotti 52 MW
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 30 | 30 | 30 | 15 | [5 empty] | 32 | 47 | 47 | 47 | 47 | 47 | 47 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 921519
100 | Manikganj 55 MW PP (Northern) | 35 | 17 | 17 | 17 |  |  |  |  | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 648499
101 | Kushiara 163 MW CCPP (KP) | 112 | 80 | 80 | 112 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 90 | 90 | 90 | 112 | 112 | 112 |  | 112 | 80 | 80 | 80 | 80 | 80 | 112 | 2229954
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 1 |  | 2 | 2 | 2 | 2 | 2 | 1 | 1 | 0 | 0 | [8 empty] | 11600
103 | Kamalaghat 54 MW PP(Banco Energy) | [12 empty] | 17 | 17 | 17 | 17 | 17 | 17 |  | 35 | 35 | 35 | 35 | 17 | 17 |  | 259920
104 | Keranigonj 300 MW PP (APR) | [26 empty] | 0
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 48 | 48 | 57 | 57 | 58 | 48 | 48 | 48 | 48 | 48 | 67 | 154 | 154 | 154 | 144 | 96 | 97 | 117 |  | 163 | 173 | 173 | 173 | 173 | 174 | 47 | 2390400
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 133 | 133 | 139 | 149 | 128 | 78 | 55 | 56 | 97 | 120 | 126 | 149 | 149 | 90 | 52 | 51 | 51 | 74 |  | 149 | 149 | 149 | 149 | 149 | 144 | 112 | 2714832
115 | Juldah 100 MW PP Unit-3 (Acorn) | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 88 |  | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 1661760
116 | Chandpur 200MW (Desh energy) | 200 | 200 | 200 | 200 | 136 | 68 | 68 | 68 | 90 | 194 | 185 | 170 | 160 | 160 | 160 | 174 | 178 | 178 |  | 179 | 180 | 179 | 179 | 179 | 180 | 179 | 3906240
117 | Ashuganj 150MW PP (Midland) | 80 | 80 | 80 | 80 | 10 | 10 | 10 | 10 | 11 | 25 | 58 | 90 | 95 | 97 | 97 | 102 | 112 | 139 |  | 138 | 142 | 140 | 147 | 149 | 48 | 27 | 1915272
118 | Bibiyana-III 400 MW CCPP | 367 | 317 | 355 | 366 | 355 | 319 | 417 | 366 | 367 | 367 | 372 | 367 | 364 | 390 | 367 | 366 | 366 | 318 |  | 395 | 366 | 319 | 330 | 366 | 367 | 367 | 8712000
| Jamalpur 115 MW PP (United) | 49 | 49 | 68 | 70 | 69 | 49 | 49 | 49 | 49 | 58 | 79 | 89 | 89 | 98 | 97 | 68 | 68 | 98 |  | 108 | 108 | 108 | 115 | 115 | 108 | 49 | 1816800
| Anwara 300 MW PP (United) | 80 | 80 | 30 | 100 | 30 | 15 | 15 | 15 | 45 | 45 | 45 | 45 | 115 | 130 | 139 | 138 | 140 | 141 |  | 226 | 226 | 229 | 230 | 230 | 230 | 86 | 2604436
| Juldah unit-2 (Acorn) | 30 | 30 | 60 | 60 | 60 | 12 | 12 | 72 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 2007360
| Anlima Energy Ltd. | 107 | 107 | 107 | 107 | 107 | 92 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 |  | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 2566800
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | [5 empty] | 1 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 347040
| Spectra Solar Plant Ltd. | [5 empty] | 0 | 3 | 14 | 15 | 25 | 32 | 33 | 29 | 30 | 19 | 15 | 6 | 1 | [8 empty] | 224394
| Chandpur 115(Doreen) | 46 | 35 | 36 | 36 | 35 | 35 | 36 | 35 | 36 | 36 | 36 | 35 | 36 | 36 | 36 | 45 | 89 | 95 |  | 96 | 115 | 115 | 115 | 115 | 96 | 76 | 1400640
| Kanchan Purbachal Power Generation Ltd. | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 30 | 20 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 845280
| Mirsharai 150 MW (Oil) | [16 empty] | 18 | [9 empty] | 13381
Mirsharai 150 MW (Gas)
120 | Eastern Zone Total | 6507 | 6255 | 6471 | 6522 | 5712 | 5148 | 5288 | 5705 | 6294 | 6538 | 6725 | 7037 | 7463 | 7691 | 7687 | 7649 | 7622 | 7737 |  | 8325 | 8465 | 8413 | 8555 | 8430 | 8008 | 7505 | 170261971
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | 16 | 16 | 16 | 16 | [6 empty] | 4 | 46 | 48 | 48 | 48 | 16 | 16 | 32 |  | 55 | 65 | 69 | 77 | 83 | 83 | 83 | 721920
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | 55 | 17 | 17 | 17 | [7 empty] | 7 | 17 | 32 | 17 | 17 | 17 | 17 |  | 31 | 45 | 45 | 55 | 55 | 55 | 55 | 555840
130 | Mongla Orion 100 MW Solar PP | [6 empty] | 16 | 34 | 63 | 90 | 98 | 102 | 74 | 85 | 75 | 37 | 19 | 2 | [8 empty] | 701280
131 | Rampal 1320 MW (BIFPCL) | 381 | 374 | 374 | 373 | 374 | 374 | 374 | 370 | 375 | 374 | 374 | 369 | 376 | 373 | 369 | 374 | 374 | 367 |  | 374 | 366 | 367 | 364 | 364 | 371 | 370 | 8909091
132 | United Payra Power Ltd. | [26 empty] | 0
133 | Bhola Nutan Biddut BD LTD (GAS)
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [19 empty] | 8 | 16 | 16 | 16 | 16 | 16 | 16 | 81696
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW | 182 | 182 | 182 | 182 | 182 | 181 | 183 | 182 | 229 | 230 | 230 | 230 | 230 | 203 | 201 | 201 | 201 | 202 |  | 206 | 260 | 220 | 263 | 259 | 259 | 247 | 5040000
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 156 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 166 | 170 | 171 | 171 | 171 | 171 | 171 | 170 | 170 | 170 |  | 171 | 170 | 162 | 163 | 170 | 170 | 170 | 4101299
140 | Bhola 33 MW PP (Venture) | 22 | 22 | 21 | 22 | 20 | 18 | 16 | 16 | 17 | 17 | 19 | 19 | 20 | 22 | 22 | 21 | 21 | 22 |  | 27 | 27 | 28 | 27 | 29 | 26 | 26 | 509600
141 | Noapara 100 MW PP (Bangla Trac) | [9 empty] | 0 | [16 empty] | 0
142 | Noapara 40 MW PP (Khanjahan Ali) | [17 empty] | 16 |  | 32 | 40 | 40 | 24 | 24 |  |  | 138750
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | [17 empty] | 15 |  | 25 | 67 | 67 | 50 | 15 | 15 | 15 | 211536
146 | Bheramara HVDC | 893 | 893 | 892 | 894 | 893 | 846 | 823 | 762 | 752 | 845 | 893 | 894 | 893 | 893 | 893 | 892 | 893 | 894 |  | 838 | 799 | 799 | 799 | 832 | 893 | 892 | 21256727
147 | Bheramara 410 MW CCPP | 145 | 145 | 150 | 150 | 150 | 160 | 160 | 160 | 160 | 150 | 150 | 150 | 150 | 150 | 145 | 145 | 140 | 135 |  | 130 | 135 | 140 | 150 | 150 | 155 | 155 | 3734208
148 | Payra 1320 MW | 870 | 820 | 830 | 800 | 720 | 700 | 650 | 650 | 670 | 680 | 700 | 730 | 760 | 790 | 850 | 830 | 800 | 750 |  | 760 | 850 | 930 | 932 | 952 | 952 | 962 | 20981800
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 169 | 169 | 170 | 169 | 169 | 169 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 169 | 170 | 170 |  | 200 | 200 | 200 | 220 | 220 | 220 | 200 | 4303500
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [20 empty] | 32 | 32 | 32 |  |  |  | 69521
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 0 | 2 | 3 | 5 | 5 | 4 | 5 | 5 | 1 | 2 | 0 | 0 | [8 empty] | 36300
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 166 | 166 | 167 | 167 | 164 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 148 | 164 | 164 | 164 | 164 | 130 |  | 140 | 160 | 130 | 135 | 168 | 169 | 171 | 3843055
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 241 | 247 | 259 | 263 | 270 | 282 | 288 | 287 | 277 | 271 | 267 | 265 | 254 | 232 | 223 | 217 | 216 | 205 |  | 204 | 208 | 232 | 262 | 275 | 281 | 281 | 6075345
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 22 | 18 | 18 | 18 | 17 | 17 | 17 | 17 | 16 |  | 19 | 21 | 21 | 21 | 21 | 22 | 22 | 458400
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 249174
165 | Amnura 50 MW PP(Sinha) | [11 empty] | 7 | 7 | 7 | 7 | [11 empty] | 23280
166 | Katakhali 50 MW PP (Northern) | [20 empty] | 24 | 24 | 8 |  |  |  | 34157
167 | Katakhali 50 MW Peaking PP | [17 empty] | 34 |  | 40 | 40 | 40 | 40 |  |  |  | 186241
168 | Santahar 50 MW Peaking PP | [7 empty] | 12 | 28 | 28 | 34 | 28 | 28 | 30 | 36 | 36 | 36 | 35 |  | 36 | 35 | 35 | 33 | 36 | 31 |  | 484404
169 | Natore 52 MW PP (Rajlanka) | [17 empty] | 8 |  | 8 | 25 | 25 | 8 |  |  |  | 55627
170 | Chapainawabganj 100 MW Peaking PP | [17 empty] | 31 |  | 31 | 31 | 31 | 46 | 46 | 46 | 46 | 261784
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 35 | 35 | 35 | 35 |  |  |  |  | 9 | 70 | 70 | 70 | 70 | 80 | 113 | 35 | 35 | 35 |  | 35 | 50 | 80 | 95 | 95 | 95 | 95 | 1328928
172 | Confidence Power Bogura Unit-1 113 MW | 35 | 35 | 35 | 35 | [7 empty] | 35 | 35 | 35 | 50 | 35 | 35 | 35 |  | 95 | 113 | 113 | 113 | 113 | 113 | 113 | 1063968
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | 34 | 34 | 34 | 34 | 34 |  |  |  | 54 | 51 | 51 | 51 | 49 | 49 | 80 | 70 | 70 | 108 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 1424956
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 2 | 3 | 5 | 7 | 7 | 7 | 7 | 6 | 5 | 4 | 1 | [8 empty] | 53255
178 | Energypac Power Venture Thakurgaon Ltd. | [11 empty] | 35 | 35 | 35 | 35 | 35 | 35 | 48 |  | 79 | 115 | 115 | 55 | 35 | 36 | 36 | 701568
| Intraco Solar 30 MW | [5 empty] | 0 | 5 | 12 | 22 | 26 | 26 | 33 | 34 | 32 | 26 | 17 | 6 | 1 | [8 empty] | 246096
| Adani Power Jharkhanda Ltd | 651 | 641 | 659 | 655 | 666 | 661 | 612 | 615 | 600 | 607 | 625 | 666 | 662 | 657 | 707 | 704 | 708 | 653 |  | 701 | 706 | 704 | 695 | 704 | 690 | 707 | 15943636
178 | Teesta Solar Limited | [5 empty] | 1 | 30 | 83 | 137 | 167 | 189 | 200 | 194 | 164 | 136 | 85 | 33 | 0 | [8 empty] | 1420230