## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2023-04-18 | Tuesday
|  | Date (day): | 2023-04-18 |  | Tuesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13862.6 | MW |  |  | (b) At Evening Peak Hour : |  | 15617 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2023-04-17 | 2023-04-18 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 120 | 120 | 120 | 120 | 245 |  | ST under Main. & Gas shortage
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 70 | 70 | 75 | 76 | 32 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 409 | 399 | 400 | 400
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 328 | 326 | 340 | 330 | 30 |  | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 66 | 96 | 80 | 97 |  | 3 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 300 | 308 | 300 | 300 | 35 |  | FGMO
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 94 | 63 | 90 | 85 |  | 17 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 15 | 55 | 15 | 55 |  |  | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 19 | 19 | 20
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 95 | 84 | 95 | 95 | 115 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 62 | 85 | 90 | 90 |  | 10 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 211 | 212 | 215 | 215 | 120 |  | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 64 | 82 | 64 | 92 |  | 10 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 54 | 17 | 54
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 82 | 48 | 32 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 35 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 35 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 41 | 41 | 46 | 46 |  | 34 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 28 | 16 | 31 | 31 |  | 2
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 35 | 48 | 48 | 48
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 244 | 263 | 300 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 250 | 290 | 300 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 50 | 65 | 50 | 65 |  | 35 | Engine problem
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 50 | 53 | 0 | 70 | 30 |  | Fuel shortage
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 132 | 131 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 82 | 105 | 88 | 105
37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 72 | 89 | 54 | 90 |  | 14 | Engine problem
38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 90 | 162 | 108 | 162
39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 29 | 0 | 30 | 0
40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 34 | 54 | 35 | 54
| Dhaka area Total |  |  |  |  | 6263 | 5847 | 3803 | 4111 | 3924 | 4371 | 838 | 625
41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 120 | 90 | 90 | 90 | 90 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 17 | 25 | 25 | 25
43 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 16 | 0 | 20 | 0
44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 26 | 39 | 26 | 40 | 10 |  | Fuel shortage
45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 25 | 25 | 25 | 25 | 205 |  | Low Water Level
46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 44 | 225 | 225 | 225
47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 51 | 100 | 51 | 105
49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 29 | 57 | 48 | 60 |  | 38 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 62 | 67 | 66 | 66 |  | 36 | Engine problem
51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 55 | 80 | 55 | 77 | 23 |  | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 62 | 100 | 50 | 100
53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 14 | 14 | 14 | 14 | 8 |  | Gas shortage
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 30 | 5 | 20
54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 7 | 108 | 0 | 108 | 0 |  | DCT & Fuel shortage
55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 122 | 228 | 120 | 230 | 70 |  | Fuel shortge
57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 17 | 54 | 17 | 54
58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 72 | 86 | 68 | 105 |  | 5 | Engine problem
59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 63 | 90 | 63 | 90 | 10 |  | Fuel shortage
60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 107 | 107 | 107 | 107 |  | 9 | Engine problem
| Mirsharai 150 MW |  | Gas/HSD | BPDB-RPCL | 18.5*9 | 0 | 0 | 145 | 36 | 0 | 0
| Chattogram area Total |  |  |  |  | 2442 | 2382 | 1060 | 1561 | 1080 | 1541 | 596 | 238
61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 204 | 207 | 200 | 210 |  |  | FGMO
63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 | 360 |  | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 340 | 345 | 345 | 345 |  |  | FGMO
65 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Under maint.
66 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 33 | 41 | 41 | 41
67 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 55 | 0 | 0 | 0 | 0 |  |  | Contract Expired
68 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 184 | 180 | 167 | 167 | 28 |  | Gas shortage
69 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
70 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 42 | 133 | 50 | 150
71 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 32 | 43 | 40 | 43 |  | 9 | Engine problem
72 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under Maint.
73 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 180 | 182 | 195 | 195 |  | 5
74 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 18 | 17 | 17 |  | 5 | Engine problem
75 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 9 | 9 | 9 | 9 |  | 2 | Engine problem
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 132 | 152 | 135 | 153
76 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 31 | 33 | 33 | 33
77 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 52 | 0 | 52
78 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 20 | 20 |  | 5 | Engine problem
79 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 125 | 128 | 130 | 130 | 70 |  | Fuel shortage
80 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 114 | 0 | 114
81 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 115 | 9 | 113
82 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 35 | 35 | 35 | 35 |  | 19 | Engine problem
83 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 75 | 93 | 72 | 92 | 23 |  | Fuel shortage
| Cumilla Area Total |  |  |  |  | 3159 | 3151 | 1519 | 1951 | 1549 | 1970 | 481 | 608
84 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 33 | 100 | 33 | 90 | 112 |  | Gas shortage
85 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 14 | 18 | 19 | 19 | 3 |  | Gas shortage
86 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0
87 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
88 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 143 | 174 | 150 | 180 | 20 |  | Fuel shortage
89 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 96 | 104 | 100 | 100 | 15 |  | Fuel shortage
90 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 45 | 0 | 50 | 0
91 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 24 | 25 | 25 | 25
| Mymensingh Area Total |  |  |  |  | 717 | 614 | 357 | 421 | 378.6 | 414 | 115 | 0
92 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 34 | 32 | 34 | 34 |  | 36 | Machine problem.
93 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 40 | 40 | 40 | 41 |  | 49 | Machine problem
94 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 112 | 0 | 0 | 0 |  | 163 | Under maint
95 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
96 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 50 | 53 | 50 | 51
97 | Fenchuganj 44MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 42 | 46 | 44 | 49
98 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 8 | 8 |  | 3 | Engine problem
99 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 50 | 60 | 60 | 60
100 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 84 | 84 | 84 | 85
101 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
102 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 197 | 195 | 200 | 200 |  | 31 | Machine problem
103 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 17 | 17 | 18 | 18
104 | Sylhet 50MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
105 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 0 | 16 | 16 | 9 |  | Gas shortage
106 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 255 | 285 | 280 | 290 |  |  | FGMO
107 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 375 | 402 | 400 | 400
108 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 8 | 10 | 10 | 10
109 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 372 | 385 | 400 | 400
| Sylhet Area Total |  |  |  |  | 2472 | 2427 | 1660 | 1617 | 1644 | 1662 | 9 | 712
110 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 924 | 854 | 943 | 943
111 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 72 | 98 | 98 | 98 |  | 17 | Engine problem
112 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 19 | 27 | 20 | 35 |  | 19 | Engine problem
113 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 158 | 0 | 0 | 230 |  | Fuel shortage
114 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 35 | 73 | 52 | 60 |  | 49 | Engine problem
115 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 195 | 230 | 215 | 215 | 195 |  | Gas shortage
116 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 32 | 32 | 40 | 40
117 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Fuel shortage
118 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 36 | 36 | 36 | 36 | 69 |  | Fuel shortage
119 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 105 | 0 | 0
120 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 90 | 0 | 100 | 0
| Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 0 | 0 | 0 | 175 | 0 | 0 |  |  | On test.
| Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 660*2 | 617 | 617 | 0 | 0 | 0 | 0
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3005 | 3001 | 1403 | 1788 | 1504 | 1427 | 610 | 85
121 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 16 | 110 | 16 | 110
122 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 25 | 36 | 24 | 37
123 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 166 | 169 | 170 | 170 | 24 |  | Gas shortage
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
124 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 1244 | 1244 | 1244 | 1244
125 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 0 | 0 | 0 | 0 |  | 220 | Under maintenance
126 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 150 | 17 | 150
127 | Barisal 307 MW |  | Coal | BCPCL | 307*1 | 307 | 307 | 0 | 0 | 0 | 0 | 307 |  | Coal Shortage.
| Barisal Area Total |  |  |  |  | 2265 | 2265 | 1468 | 1709 | 1471 | 1711 | 331 | 220
128 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
129 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 28 | 28 | 28 | 28 |  | 24 | Engine problem
130 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 4 | 40 | 0 | 45 |  | 26 | Engine problem
131 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 21 | 21 | 21 | 21
132 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 25 | 42 | 42 | 42 |  | 8 | Engine problem
133 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 40 | 40 | 40 | 40 |  | 10 | Engine problem
134 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 177 | 197 | 160 | 160 | 50 |  | Gas shortage
135 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
136 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 72 | 180 | 180 | 40 |  | Gas shortage
137 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 414 | 414 | 414 | 414
138 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 35 | 35 | 35 | 35 |  | 15 | Engine problem
139 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 15 | 20 | 21 | 21
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
140 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 8 | 8 | 8 |  | 3 | Engine problem
141 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 43 | 0 | 43 | 9 |  | Fuel shortage
142 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 83 | 71 | 80 | 80 |  | 14 | Enginr problem
143 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel shortage
144 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 35 | 95 | 35 | 95 | 18 |  | Fuel shortage
145 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 35 | 95 | 35 | 95 | 18 |  | Fuel shortage
146 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 4 | 0 | 6 | 0
| Adani Power Jharkhanda Ltd |  | Coal | Import | 0 | 0 | 0 | 756 | 753 | 755 | 755 |  |  | On test.
| Rajshahi Area Total |  |  |  |  | 2179 | 2129 | 1672 | 1974 | 1860 | 2062 | 726 | 100
147 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
148 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 204 | 250 | 250 | 250 | 24 |  | Coal Shortage.
149 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 17 | 0 | 0 | 20 |  | Fuel conservation
150 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
151 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 35 | 93 | 34 | 95 | 18 |  | Fuel shortage
152 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5 | 0 | 8 | 0
153 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 0 | 112 | 0 | 114
154 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 30 | 0 | 30 | 0
| Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 0 | 0 | 176 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 830 | 750 | 450 | 472 | 452 | 459 | 167 | 85
| Total |  |  |  |  | 23332 | 22566 | 13392 | 15604 | 13862.6 | 15617 | 3873 | 2673
A. |  | 2023-04-17 | (Yesterday) |  |  |  |  | Monday
1 | Highest Generation : |  |  | 15604 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 11702 | MW at | 9:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 16221 | MW
3 | Day peak Generation : |  |  | 13392 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 15499.37 | MW
4 | Evening peak Generation : |  |  | 15604 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 589 | MW
5 | Total Energy Generation : |  | 335.9571 | MKWHr | By Solar | 2.8323 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Gas : | 146.5515 | MKWHr |  | By Oil: | 106.8358 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 54.8029 | MKWHr |  | By Hydro: | 0.42348 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 3873 | MW | Dhaka | 5312.27 | 5237.27 |  | 75 |  | 18:00 |  | 460.7875
|  |  | For Plants S/D or M/C prob = |  |  | 2673 | MW | Chittagong | 1430.5 | 1430.5 |  | 0 |  | 19:00 |  | 758.4562
|  |  | Total = |  |  | 6546 | MW | Khulna | 2015 | 2005 |  | 10 |  | 19:30 |  | 864.4374
7 | Total Gas Supplied : |  |  | 1143.54 | MMCFD |  |  | Rajshahi | 1737.6 | 1737.6 |  | 0 |  | 20:00 |  | 796.2408
8 | Fuel Cost : | i) Gas : | Taka | 168748114.388 | ii) Oil : | Taka | 1490938180.63 | Comilla | 1576 | 1512 |  | 64 |  | 21:00 |  | 589
|  | iii) Coal : | Taka | 311772022 | Total | Taka | 1971458317.018 | Mymensingh | 1257 | 982 |  | 275 |  | 22:00 |  | 500.42
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0.3465 | MKWHr. | Sylhet | 626 | 611 |  | 15 |  | 23:00 |  | 912.025
| ii) During Peak Demand : |  |  | 268 | MW (E to W) at | 21:00 | hrs | Barisal | 512 | 512 |  | 0 |  | 24:00 |  | 1596.76
| iii) Maximum : |  |  | 146 | MW at | 19:00 | hrs | Rangpur | 1033 | 883 |  | 150
10 | Maximum Temperature in Dhaka was |  |  |  | 38.1° C |  |  | Total | 15499.37 | 14910.37 |  | 589
B. |  | 2023-04-18 | (Today) |  |  |  | Tuesday |  |  | Probable max. temperature in Dhaka |  |  | 42.3° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 16000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 360 | MW
2 | Maximum Generation (Generation end) |  |  |  | 15617 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 14000 | MW
4 | Reserve(Generation end) |  |  |  | - | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 344.4831 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 11656 | MW at | 7:00 | 40 | 40 | 60 | 60 | 50 | 60 | 15 | 0 | 35
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.3258 | MKWHr. | ii) HVDC Flow at Peak Time |  | 854 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.1853 | MKWHr. | iii) Maximum HVDC Flow : |  | 924 | MW at | 4:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 75.96 |  | (b) Today: | 75.89 |  | (c) Rule Curve: |  | 84.8
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2023-04-17 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 40 | 76 | 0 | 400 | 323 |  | 0 | 450 | 297 | 41 | 80 | 15 | 214 | 0 | 96 | 50 | 50 | 48 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 19 | 23 | 23 | 33 | 32 | 48 | 0 | 25 | 0 | 120 | 0 | 25 | 0 | 0 | 0 | 0 |  | 23 | 45 | 67 | 55 | 8 | 6 | 14 | 26 | 0 | 0 | 0 | 0 | 340 | 208 | 184 | 0 | 45 | 0 | 0 | 51 | 0 | 45 | 0 | 18 | 9 | 32 | 15 | 136 | 93 | 0 | 18 | 0 | 34 | 41 | 53 | 49 | 112 | 0 | 60 | 83 | 0 | 195 | 17 | 0 | 10 | 285 | 16 | 8 | 105 | 160 | 290 | 49 | 48 | 51 | 34 | 0 | 63 | 192 | 18 | 397 | 48 | 105 | 17 | 0 | 87 | 17 | 44 | 114 | 8 | 50 | 390 | 64 | 0 | 54 | 107 | 0 | 35 | 0 | 58 | 35 | 0 | 0 | 0 |  | 663 | 0 | 210 | 0 | 81 | 0 | 0 | 0 | 30 | 43 | 40 | 160 | 36 | 16 | 0 | 0 | 0 | 30 | 25 | 80 | 21 | 34 | 32 | 0 | 35 | 21 | 0 | 8 | 0 | 0 | 170 | 15 | 0 | 182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 36 | 0 | 35 | 105 | 34 | 0 | 0 | 35 | 1244 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 751 | 0 | 0 |  | 7818 | 4736 | 12554 | 3690 | 663 | 2470 | 495 | 2415 | 2165 | 25 | 15 | 480 | 136 | 0 | 2254.1725 | 75.97
2:00 | 0 | 0 | 0 | 180 | 40 | 76 | 0 | 394 | 323 |  | 0 | 450 | 304 | 41 | 65 | 15 | 215 | 0 | 96 | 50 | 50 | 48 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 19 | 23 | 23 | 33 | 32 | 48 | 0 | 25 | 0 | 120 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 45 | 67 | 55 | 8 | 6 | 14 | 31 | 0 | 0 | 0 | 0 | 340 | 208 | 184 | 0 | 45 | 0 | 0 | 43 | 0 | 45 | 0 | 18 | 9 | 32 | 20 | 130 | 94 | 0 | 19 | 0 | 34 | 41 | 53 | 49 | 112 | 0 | 60 | 81 | 0 | 197 | 17 | 0 | 10 | 275 | 16 | 8 | 103 | 97 | 298 | 49 | 48 | 50 | 34 | 0 | 63 | 192 | 20 | 379 | 48 | 105 | 17 | 0 | 88 | 22 | 51 | 114 | 3 | 38 | 390 | 53 | 0 | 54 | 107 | 0 | 35 | 0 | 35 | 35 | 0 | 0 | 0 |  | 740 | 0 | 210 | 0 | 81 | 0 | 0 | 0 | 30 | 43 | 40 | 160 | 36 | 16 | 0 | 0 | 0 | 30 | 30 | 80 | 21 | 34 | 32 | 0 | 35 | 21 | 0 | 8 | 0 | 0 | 170 | 15 | 0 | 182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 36 | 0 | 35 | 105 | 34 | 0 | 0 | 35 | 1244 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 753 | 0 | 0 |  | 7682 | 4820 | 12502 | 3676 | 740 | 2462 | 500 | 2302 | 2167 | 25 | 15 | 485 | 130 | 0 | 2025.6218 | 75.97
3:00 | 0 | 0 | 0 | 180 | 40 | 76 | 0 | 394 | 323 |  | 0 | 450 | 309 | 42 | 70 | 15 | 219 | 0 | 98 | 50 | 50 | 48 | 0 | 0 | 0 | 0 | 17 | 35 | 20 | 19 | 23 | 23 | 33 | 32 | 48 | 0 | 25 | 0 | 120 | 0 | 25 | 0 | 0 | 0 | 0 |  | 25 | 45 | 67 | 55 | 12 | 6 | 14 | 31 | 0 | 0 | 0 | 0 | 350 | 210 | 184 | 0 | 45 | 0 | 0 | 43 | 0 | 45 | 0 | 18 | 9 | 32 | 20 | 128 | 95 | 0 | 19 | 0 | 34 | 41 | 53 | 49 | 112 | 0 | 60 | 81 | 0 | 197 | 17 | 0 | 10 | 270 | 16 | 8 | 103 | 97 | 300 | 48 | 67 | 50 | 41 | 0 | 63 | 192 | 18 | 340 | 58 | 105 | 17 | 0 | 88 | 36 | 51 | 114 | 8 | 38 | 400 | 53 | 0 | 54 | 107 | 0 | 35 | 0 | 36 | 35 | 0 | 0 | 0 |  | 827 | 0 | 215 | 0 | 81 | 0 | 0 | 0 | 30 | 43 | 40 | 169 | 35 | 16 | 0 | 0 | 0 | 30 | 40 | 80 | 21 | 34 | 32 | 0 | 35 | 21 | 0 | 8 | 0 | 0 | 170 | 15 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 423 | 36 | 0 | 58 | 105 | 90 | 0 | 0 | 94 | 1244 | 0 | 0 | 137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 756 | 0 | 0 |  | 7739 | 5066 | 12805 | 3679 | 827 | 2470 | 501 | 2495 | 2170 | 25 | 15 | 495 | 128 | 0 | 2022.8571 | 75.97
4:00 | 0 | 0 | 0 | 180 | 40 | 74 | 0 | 392 | 330 |  | 0 | 450 | 305 | 41 | 84 | 15 | 214 | 0 | 95 | 50 | 50 | 48 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 23 | 23 | 33 | 32 | 50 | 0 | 0 | 0 | 120 | 0 | 25 | 0 | 0 | 0 | 0 |  | 25 | 45 | 67 | 55 | 12 | 6 | 14 | 37 | 0 | 0 | 0 | 0 | 340 | 207 | 184 | 0 | 45 | 0 | 0 | 43 | 0 | 45 | 0 | 18 | 9 | 32 | 20 | 136 | 95 | 0 | 19 | 0 | 34 | 41 | 53 | 49 | 112 | 0 | 60 | 81 | 0 | 196 | 17 | 0 | 10 | 270 | 16 | 8 | 103 | 97 | 300 | 46 | 67 | 50 | 119 | 0 | 63 | 192 | 20 | 397 | 59 | 105 | 17 | 0 | 88 | 36 | 51 | 114 | 9 | 38 | 390 | 53 | 0 | 54 | 107 | 0 | 35 | 0 | 36 | 35 | 0 | 0 | 0 |  | 924 | 0 | 210 | 0 | 81 | 0 | 0 | 0 | 30 | 44 | 40 | 169 | 36 | 16 | 0 | 0 | 0 | 30 | 38 | 80 | 21 | 34 | 24 | 0 | 35 | 21 | 0 | 8 | 0 | 0 | 170 | 15 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 36 | 0 | 95 | 105 | 92 | 0 | 0 | 95 | 1244 | 0 | 0 | 137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 754 | 0 | 0 |  | 7862 | 5178 | 13040 | 3696 | 924 | 2469 | 499 | 2647 | 2168 | 0 | 15 | 486 | 136 | 0 | 1621.972 | 75.97
5:00 | 0 | 0 | 0 | 180 | 40 | 74 | 0 | 395 | 326 |  | 0 | 450 | 308 | 41 | 94 | 15 | 214 | 0 | 97 | 50 | 50 | 48 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 23 | 19 | 33 | 32 | 50 | 0 | 0 | 0 | 120 | 0 | 25 | 0 | 0 | 0 | 0 |  | 25 | 45 | 67 | 55 | 8 | 6 | 14 | 23 | 0 | 0 | 0 | 0 | 345 | 210 | 184 | 0 | 45 | 0 | 0 | 43 | 0 | 44 | 0 | 18 | 9 | 32 | 20 | 132 | 94 | 0 | 19 | 0 | 34 | 41 | 53 | 49 | 112 | 0 | 60 | 81 | 0 | 196 | 18 | 0 | 10 | 275 | 16 | 8 | 70 | 97 | 240 | 48 | 67 | 51 | 132 | 0 | 50 | 184 | 20 | 393 | 59 | 105 | 17 | 0 | 87 | 36 | 53 | 114 | 9 | 38 | 390 | 61 | 0 | 54 | 107 | 0 | 35 | 0 | 36 | 35 | 0 | 0 | 0 |  | 924 | 0 | 210 | 0 | 81 | 0 | 0 | 0 | 30 | 44 | 40 | 169 | 33 | 16 | 0 | 0 | 0 | 30 | 38 | 80 | 21 | 34 | 24 | 0 | 35 | 21 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 36 | 0 | 95 | 105 | 92 | 0 | 0 | 95 | 1244 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 754 | 0 | 0 |  | 7769 | 5047 | 12816 | 3702 | 924 | 2462 | 409 | 2534 | 2168 | 0 | 0 | 485 | 132 | 0 | 1367.6173 | 75.96
6:00 | 0 | 0 | 0 | 180 | 50 | 74 | 0 | 398 | 326 |  | 0 | 450 | 311 | 40 | 94 | 15 | 211 | 0 | 100 | 50 | 50 | 48 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 23 | 19 | 33 | 32 | 50 | 0 | 0 | 0 | 120 | 0 | 25 | 0 | 0 | 0 | 0 |  | 25 | 45 | 67 | 55 | 6 | 6 | 14 | 24 | 0 | 0 | 0 | 0 | 350 | 210 | 184 | 0 | 45 | 0 | 0 | 43 | 0 | 44 | 0 | 18 | 9 | 32 | 20 | 122 | 83 | 0 | 19 | 0 | 34 | 41 | 53 | 49 | 112 | 0 | 60 | 81 | 0 | 196 | 18 | 0 | 10 | 275 | 16 | 8 | 0 | 97 | 155 | 25 | 48 | 25 | 47 | 0 | 50 | 175 | 18 | 345 | 49 | 105 | 17 | 0 | 87 | 36 | 54 | 114 | 9 | 38 | 390 | 72 | 1 | 54 | 107 | 0 | 35 | 0 | 35 | 35 | 0 | 0 | 0 |  | 924 | 0 | 215 | 0 | 80 | 0 | 0 | 0 | 26 | 44 | 40 | 169 | 30 | 16 | 0 | 0 | 0 | 30 | 0 | 80 | 21 | 34 | 24 | 0 | 35 | 21 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 421 | 36 | 0 | 50 | 105 | 49 | 0 | 0 | 55 | 1244 | 0 | 0 | 17 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 750 | 0 | 0 |  | 7402 | 4878 | 12280 | 3668 | 924 | 2464 | 205 | 2288 | 2164 | 0 | 0 | 443 | 122 | 2 | 1308.6365 | 75.96
7:00 | 0 | 0 | 0 | 180 | 50 | 74 | 0 | 397 | 326 |  | 0 | 450 | 309 | 42 | 94 | 15 | 218 | 0 | 98 | 50 | 50 | 48 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 23 | 19 | 33 | 32 | 50 | 0 | 0 | 0 | 120 | 0 | 25 | 0 | 0 | 0 | 0 |  | 25 | 45 | 67 | 55 | 6 | 6 | 14 | 2 | 0 | 0 | 0 | 0 | 355 | 211 | 184 | 0 | 45 | 0 | 0 | 43 | 0 | 43 | 0 | 18 | 9 | 32 | 20 | 126 | 35 | 0 | 19 | 0 | 34 | 41 | 53 | 49 | 112 | 0 | 61 | 81 | 0 | 196 | 17 | 0 | 10 | 280 | 16 | 8 | 0 | 97 | 104 | 25 | 48 | 25 | 34 | 3 | 50 | 175 | 20 | 363 | 49 | 89 | 17 | 0 | 87 | 17 | 54 | 114 | 9 | 38 | 396 | 72 | 5 | 54 | 107 | 0 | 35 | 5 | 35 | 35 | 0 | 0 | 0 |  | 924 | 0 | 210 | 0 | 80 | 0 | 0 | 0 | 20 | 45 | 40 | 169 | 26 | 16 | 0 | 0 | 0 | 30 | 0 | 80 | 21 | 34 | 24 | 0 | 35 | 21 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 423 | 36 | 0 | 35 | 105 | 34 | 0 | 1 | 35 | 1244 | 0 | 0 | 17 | 0 | 14 | 0 | 0 | 0 | 0 | 5 | 0 | 750 | 30 | 0 |  | 7289 | 4866 | 12155 | 3650 | 924 | 2443 | 154 | 2194 | 2164 | 0 | 0 | 437 | 126 | 63 | 1193.4396 | 75.96
8:00 | 0 | 0 | 0 | 180 | 0 | 68 | 0 | 395 | 326 |  | 0 | 450 | 315 | 39 | 94 | 15 | 219 | 0 | 98 | 50 | 50 | 48 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 0 | 23 | 19 | 33 | 16 | 42 | 0 | 0 | 0 | 120 | 0 | 0 | 25 | 0 | 0 | 0 |  | 25 | 45 | 66 | 55 | 9 | 6 | 14 | 2 | 0 | 0 | 0 | 0 | 355 | 213 | 184 | 0 | 43 | 0 | 0 | 43 | 0 | 45 | 0 | 18 | 9 | 32 | 20 | 124 | 35 | 0 | 19 | 1 | 34 | 41 | 53 | 49 | 112 | 0 | 61 | 81 | 0 | 196 | 17 | 0 | 10 | 270 | 16 | 0 | 0 | 97 | 0 | 0 | 48 | 0 | 34 | 7 | 50 | 174 | 42 | 344 | 49 | 89 | 17 | 1 | 87 | 17 | 54 | 61 | 9 | 38 | 400 | 72 | 8 | 54 | 107 | 0 | 35 | 12 | 36 | 35 | 0 | 0 | 0 |  | 924 | 0 | 215 | 0 | 65 | 0 | 0 | 0 | 20 | 45 | 40 | 169 | 24 | 16 | 0 | 0 | 0 | 30 | 0 | 73 | 21 | 34 | 24 | 0 | 35 | 20 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 415 | 36 | 0 | 35 | 30 | 34 | 0 | 2 | 35 | 1244 | 0 | 0 | 17 | 1 | 33 | 0 | 0 | 0 | 0 | 11 | 0 | 748 | 68 | 0 |  | 6992 | 4826 | 11818 | 3571 | 924 | 2422 | 0 | 2040 | 2162 | 0 | 0 | 431 | 124 | 144 | 1504.0104 | 75.96
9:00 | 0 | 0 | 0 | 180 | 0 | 68 | 0 | 401 | 339 |  | 0 | 450 | 289 | 40 | 94 | 15 | 180 | 0 | 97 | 50 | 50 | 82 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 23 | 19 | 33 | 16 | 49 | 0 | 0 | 0 | 120 | 0 | 9 | 26 | 0 | 0 | 0 |  | 25 | 44 | 67 | 55 | 7 | 0 | 14 | 2 | 0 | 0 | 0 | 0 | 340 | 209 | 184 | 0 | 40 | 0 | 0 | 43 | 0 | 45 | 0 | 18 | 9 | 30 | 20 | 120 | 35 | 0 | 18 | 1 | 34 | 31 | 53 | 49 | 80 | 0 | 60 | 81 | 0 | 196 | 17 | 0 | 9 | 260 | 16 | 5 | 0 | 97 | 0 | 0 | 48 | 0 | 34 | 13 | 50 | 174 | 45 | 335 | 57 | 89 | 17 | 3 | 87 | 17 | 54 | 0 | 9 | 38 | 385 | 72 | 21 | 54 | 107 | 0 | 35 | 19 | 36 | 35 | 0 | 0 | 0 |  | 924 | 0 | 200 | 0 | 65 | 0 | 0 | 0 | 16 | 38 | 40 | 168 | 23 | 16 | 0 | 0 | 0 | 30 | 0 | 74 | 21 | 34 | 24 | 0 | 35 | 19 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 376 | 36 | 0 | 35 | 0 | 34 | 0 | 3 | 35 | 1244 | 0 | 0 | 17 | 3 | 59 | 0 | 0 | 0 | 0 | 19 | 0 | 759 | 111 | 0 |  | 6884 | 4818 | 11702 | 3484 | 924 | 2325 | 0 | 1969 | 2173 | 0 | 0 | 455 | 120 | 252 | 1795.2281 | 75.95
10:00 | 0 | 0 | 0 | 180 | 0 | 67 | 0 | 406 | 329 |  | 0 | 450 | 307 | 52 | 94 | 15 | 205 | 0 | 97 | 50 | 42 | 82 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 23 | 19 | 33 | 30 | 49 | 0 | 25 | 0 | 120 | 0 | 17 | 29 | 0 | 0 | 0 |  | 25 | 44 | 66 | 55 | 6 | 7 | 14 | 2 | 0 | 0 | 0 | 0 | 345 | 210 | 184 | 0 | 36 | 0 | 0 | 43 | 0 | 44 | 0 | 15 | 9 | 31 | 20 | 136 | 33 | 0 | 15 | 2 | 34 | 22 | 53 | 47 | 0 | 0 | 60 | 84 | 0 | 196 | 17 | 0 | 9 | 270 | 16 | 5 | 106 | 97 | 155 | 50 | 71 | 25 | 34 | 17 | 50 | 175 | 36 | 341 | 64 | 89 | 17 | 4 | 87 | 17 | 54 | 0 | 9 | 38 | 385 | 72 | 38 | 90 | 107 | 0 | 35 | 24 | 57 | 35 | 0 | 0 | 0 |  | 924 | 0 | 200 | 0 | 64 | 0 | 0 | 0 | 16 | 38 | 40 | 167 | 23 | 16 | 0 | 0 | 0 | 28 | 0 | 74 | 21 | 34 | 35 | 0 | 27 | 19 | 0 | 8 | 0 | 0 | 176 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 36 | 0 | 35 | 0 | 35 | 0 | 5 | 35 | 1244 | 0 | 0 | 17 | 4 | 77 | 0 | 0 | 0 | 0 | 26 | 0 | 759 | 145 | 0 |  | 7361 | 4922 | 12283 | 3520 | 924 | 2301 | 336 | 2066 | 2179 | 25 | 0 | 454 | 136 | 342 | 1582.3443 | 75.95
11:00 | 0 | 0 | 0 | 180 | 0 | 70 | 0 | 406 | 329 |  | 0 | 450 | 304 | 59 | 94 | 15 | 211 | 0 | 97 | 62 | 50 | 82 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 23 | 18 | 33 | 30 | 42 | 0 | 25 | 0 | 120 | 0 | 17 | 32 | 0 | 0 | 0 |  | 25 | 44 | 64 | 55 | 11 | 25 | 14 | 2 | 0 | 0 | 0 | 0 | 340 | 207 | 184 | 0 | 32 | 0 | 0 | 51 | 0 | 35 | 0 | 17 | 9 | 31 | 20 | 132 | 34 | 0 | 15 | 2 | 34 | 41 | 50 | 43 | 5 | 0 | 55 | 84 | 0 | 196 | 17 | 0 | 9 | 260 | 16 | 8 | 124 | 97 | 210 | 50 | 119 | 50 | 75 | 17 | 62 | 175 | 36 | 343 | 96 | 70 | 51 | 4 | 121 | 17 | 54 | 0 | 9 | 63 | 380 | 72 | 43 | 90 | 107 | 0 | 35 | 28 | 74 | 35 | 0 | 34 | 0 |  | 924 | 0 | 195 | 0 | 64 | 0 | 0 | 0 | 16 | 35 | 32 | 167 | 23 | 16 | 0 | 0 | 0 | 28 | 0 | 74 | 21 | 25 | 40 | 0 | 27 | 18 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 36 | 0 | 35 | 0 | 35 | 0 | 5 | 35 | 1244 | 0 | 0 | 17 | 4 | 86 | 0 | 0 | 0 | 0 | 29 | 0 | 764 | 165 | 0 |  | 7763 | 4951 | 12714 | 3517 | 924 | 2296 | 434 | 2316 | 2208 | 25 | 34 | 445 | 132 | 383 | 1415.5392 | 75.95
12:00 | 0 | 0 | 0 | 180 | 120 | 70 | 0 | 409 | 328 |  | 0 | 450 | 300 | 66 | 94 | 15 | 211 | 0 | 95 | 62 | 64 | 82 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 0 | 23 | 18 | 33 | 28 | 35 | 0 | 25 | 0 | 120 | 0 | 17 | 44 | 0 | 0 | 0 |  | 24 | 29 | 62 | 55 | 7 | 26 | 14 | 2 | 0 | 0 | 0 | 0 | 340 | 204 | 184 | 0 | 33 | 0 | 0 | 51 | 0 | 32 | 0 | 17 | 9 | 31 | 20 | 132 | 33 | 0 | 14 | 2 | 34 | 40 | 50 | 42 | 112 | 0 | 50 | 84 | 0 | 197 | 17 | 0 | 8 | 255 | 16 | 8 | 125 | 244 | 250 | 50 | 143 | 50 | 132 | 16 | 62 | 180 | 42 | 375 | 96 | 82 | 51 | 4 | 122 | 17 | 72 | 0 | 9 | 63 | 372 | 72 | 45 | 90 | 107 | 0 | 35 | 29 | 75 | 34 | 0 | 145 | 0 |  | 924 | 0 | 195 | 0 | 72 | 0 | 0 | 0 | 19 | 35 | 32 | 166 | 25 | 16 | 0 | 0 | 0 | 28 | 4 | 83 | 21 | 25 | 40 | 0 | 35 | 15 | 0 | 0 | 0 | 0 | 204 | 0 | 0 | 177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 36 | 0 | 35 | 0 | 35 | 0 | 5 | 35 | 1244 | 0 | 0 | 17 | 4 | 90 | 0 | 0 | 0 | 0 | 30 | 0 | 756 | 176 | 0 |  | 8399 | 4993 | 13392 | 3643 | 924 | 2390 | 475 | 2604 | 2204 | 25 | 145 | 449 | 132 | 401 | 1067.1839 | 75.95
13:00 | 0 | 0 | 0 | 180 | 120 | 64 | 0 | 396 | 319 |  | 0 | 450 | 285 | 58 | 94 | 15 | 200 | 0 | 94 | 64 | 74 | 80 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 23 | 18 | 33 | 28 | 35 | 0 | 25 | 0 | 100 | 0 | 17 | 73 | 0 | 0 | 0 |  | 24 | 29 | 61 | 55 | 16 | 26 | 14 | 2 | 0 | 0 | 0 | 0 | 320 | 204 | 182 | 0 | 35 | 0 | 0 | 51 | 0 | 32 | 0 | 15 | 9 | 31 | 20 | 134 | 33 | 0 | 12 | 2 | 34 | 40 | 53 | 44 | 112 | 0 | 54 | 83 | 0 | 197 | 17 | 0 | 8 | 270 | 16 | 8 | 125 | 165 | 293 | 50 | 156 | 50 | 63 | 17 | 62 | 178 | 48 | 355 | 94 | 89 | 68 | 4 | 122 | 17 | 85 | 0 | 9 | 63 | 375 | 70 | 41 | 90 | 107 | 0 | 35 | 28 | 60 | 34 | 0 | 163 | 0 |  | 924 | 0 | 200 | 0 | 77 | 0 | 0 | 0 | 16 | 38 | 32 | 165 | 27 | 16 | 0 | 0 | 0 | 28 | 6 | 68 | 21 | 25 | 32 | 0 | 35 | 14 | 0 | 8 | 0 | 0 | 230 | 0 | 0 | 178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 36 | 0 | 35 | 0 | 35 | 0 | 7 | 35 | 1244 | 0 | 0 | 17 | 4 | 87 | 0 | 0 | 0 | 0 | 28 | 0 | 751 | 167 | 0 |  | 8310 | 5000 | 13310 | 3624 | 924 | 2378 | 518 | 2509 | 2225 | 25 | 163 | 425 | 134 | 385 | 912.3592 | 75.94
14:00 | 0 | 0 | 0 | 180 | 115 | 66 | 0 | 402 | 318 |  | 0 | 450 | 287 | 56 | 86 | 15 | 204 | 0 | 92 | 64 | 82 | 80 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 23 | 18 | 33 | 28 | 37 | 0 | 25 | 0 | 90 | 0 | 17 | 118 | 0 | 0 | 0 |  | 24 | 49 | 64 | 55 | 55 | 25 | 14 | 2 | 0 | 0 | 0 | 0 | 320 | 199 | 182 | 0 | 35 | 0 | 0 | 51 | 0 | 32 | 0 | 0 | 5 | 30 | 20 | 154 | 33 | 0 | 16 | 2 | 34 | 40 | 53 | 41 | 112 | 0 | 54 | 81 | 0 | 197 | 17 | 0 | 8 | 260 | 16 | 8 | 124 | 97 | 250 | 50 | 149 | 51 | 35 | 15 | 62 | 192 | 51 | 392 | 93 | 85 | 68 | 3 | 123 | 17 | 91 | 0 | 15 | 63 | 330 | 71 | 40 | 108 | 107 | 0 | 35 | 24 | 70 | 33 | 0 | 163 | 0 |  | 924 | 0 | 205 | 0 | 77 | 0 | 0 | 0 | 17 | 38 | 32 | 160 | 28 | 16 | 0 | 0 | 0 | 24 | 23 | 60 | 21 | 25 | 32 | 0 | 35 | 14 | 0 | 8 | 0 | 0 | 230 | 0 | 0 | 178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 36 | 0 | 35 | 0 | 39 | 0 | 7 | 35 | 1244 | 0 | 0 | 17 | 4 | 76 | 0 | 175 | 0 | 0 | 26 | 0 | 753 | 149 | 0 |  | 8287 | 5157 | 13444 | 3633 | 924 | 2367 | 475 | 2501 | 2227 | 25 | 338 | 454 | 154 | 346 | 1157.4982 | 75.95
15:00 | 0 | 0 | 0 | 180 | 110 | 68 | 0 | 401 | 319 |  | 0 | 450 | 299 | 57 | 85 | 15 | 198 | 0 | 95 | 65 | 82 | 80 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 23 | 18 | 33 | 28 | 38 | 0 | 25 | 0 | 100 | 0 | 25 | 149 | 0 | 0 | 0 |  | 24 | 51 | 64 | 55 | 92 | 25 | 14 | 3 | 0 | 0 | 0 | 0 | 330 | 201 | 182 | 0 | 35 | 0 | 0 | 51 | 0 | 32 | 1 | 0 | 9 | 30 | 20 | 134 | 32 | 0 | 14 | 1 | 34 | 40 | 52 | 42 | 112 | 0 | 54 | 82 | 0 | 196 | 17 | 0 | 8 | 270 | 16 | 8 | 30 | 95 | 146 | 50 | 149 | 50 | 31 | 11 | 62 | 192 | 60 | 372 | 92 | 85 | 76 | 2 | 123 | 17 | 102 | 20 | 9 | 62 | 350 | 71 | 30 | 108 | 107 | 0 | 35 | 19 | 74 | 34 | 0 | 145 | 0 |  | 924 | 0 | 215 | 0 | 76 | 0 | 0 | 0 | 17 | 35 | 32 | 160 | 29 | 16 | 0 | 0 | 0 | 28 | 28 | 38 | 21 | 34 | 40 | 0 | 35 | 11 | 0 | 8 | 0 | 0 | 240 | 0 | 0 | 178 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 414 | 36 | 0 | 78 | 45 | 60 | 0 | 5 | 90 | 1244 | 0 | 0 | 17 | 3 | 60 | 0 | 175 | 0 | 0 | 21 | 0 | 754 | 110 | 0 |  | 8189 | 5279 | 13468 | 3689 | 924 | 2392 | 276 | 2760 | 2238 | 25 | 320 | 448 | 134 | 262 | 1227.5379 | 75.94
16:00 | 0 | 0 | 0 | 180 | 110 | 68 | 0 | 395 | 318 |  | 0 | 450 | 290 | 56 | 83 | 15 | 207 | 0 | 93 | 75 | 82 | 80 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 23 | 18 | 33 | 28 | 33 | 0 | 25 | 0 | 100 | 0 | 25 | 149 | 0 | 0 | 0 |  | 23 | 56 | 65 | 66 | 100 | 25 | 14 | 7 | 0 | 0 | 0 | 0 | 330 | 201 | 180 | 0 | 35 | 0 | 0 | 51 | 0 | 40 | 8 | 18 | 9 | 30 | 20 | 134 | 33 | 0 | 12 | 1 | 34 | 40 | 52 | 42 | 112 | 0 | 54 | 82 | 0 | 193 | 17 | 0 | 8 | 270 | 16 | 0 | 0 | 95 | 0 | 0 | 114 | 0 | 33 | 7 | 62 | 192 | 68 | 372 | 46 | 85 | 85 | 1 | 123 | 17 | 86 | 53 | 9 | 63 | 330 | 71 | 18 | 108 | 107 | 0 | 35 | 12 | 73 | 37 | 0 | 144 | 0 |  | 924 | 0 | 220 | 0 | 75 | 0 | 0 | 0 | 17 | 40 | 24 | 160 | 28 | 16 | 0 | 0 | 0 | 28 | 28 | 38 | 21 | 34 | 40 | 0 | 35 | 12 | 0 | 8 | 0 | 0 | 240 | 0 | 0 | 178 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 414 | 36 | 0 | 95 | 105 | 90 | 0 | 3 | 95 | 1244 | 0 | 0 | 17 | 2 | 38 | 0 | 175 | 0 | 0 | 13 | 0 | 755 | 68 | 0 |  | 7866 | 5319 | 13185 | 3682 | 924 | 2384 | 0 | 2848 | 2239 | 25 | 319 | 467 | 134 | 163 | 1211.8711 | 75.93
17:00 | 0 | 0 | 0 | 180 | 110 | 68 | 0 | 396 | 317 |  | 0 | 450 | 300 | 63 | 65 | 15 | 210 | 0 | 96 | 77 | 82 | 80 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 19 | 23 | 18 | 33 | 14 | 45 | 0 | 25 | 0 | 90 | 0 | 25 | 208 | 0 | 0 | 0 |  | 23 | 32 | 65 | 66 | 108 | 26 | 14 | 12 | 0 | 0 | 0 | 0 | 340 | 205 | 180 | 0 | 37 | 0 | 0 | 51 | 0 | 40 | 8 | 18 | 9 | 30 | 20 | 130 | 33 | 0 | 14 | 0 | 32 | 40 | 53 | 42 | 0 | 0 | 55 | 82 | 0 | 192 | 17 | 0 | 8 | 285 | 16 | 8 | 0 | 95 | 0 | 0 | 115 | 0 | 34 | 2 | 62 | 192 | 80 | 369 | 46 | 85 | 92 | 0 | 123 | 17 | 86 | 114 | 55 | 63 | 310 | 71 | 7 | 108 | 107 | 0 | 35 | 5 | 74 | 50 | 0 | 150 | 0 |  | 924 | 0 | 225 | 0 | 86 | 0 | 0 | 0 | 17 | 51 | 24 | 160 | 28 | 16 | 0 | 0 | 0 | 28 | 28 | 38 | 21 | 34 | 40 | 0 | 34 | 13 | 0 | 8 | 0 | 0 | 240 | 0 | 0 | 177 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 414 | 36 | 0 | 95 | 105 | 94 | 0 | 1 | 95 | 1244 | 0 | 0 | 20 | 0 | 16 | 0 | 175 | 0 | 0 | 6 | 0 | 753 | 32 | 0 |  | 7971 | 5280 | 13251 | 3728 | 924 | 2303 | 0 | 3057 | 2237 | 25 | 325 | 453 | 130 | 69 | 966.7322 | 75.93
18:00 | 0 | 0 | 0 | 180 | 110 | 68 | 0 | 405 | 324 |  | 0 | 450 | 305 | 78 | 58 | 15 | 212 | 0 | 96 | 79 | 82 | 110 | 0 | 0 | 0 | 0 | 54 | 35 | 40 | 19 | 23 | 24 | 33 | 28 | 46 | 0 | 25 | 0 | 90 | 0 | 25 | 224 | 0 | 0 | 0 |  | 24 | 56 | 67 | 80 | 107 | 38 | 14 | 25 | 0 | 0 | 0 | 0 | 345 | 206 | 182 | 0 | 37 | 0 | 0 | 51 | 0 | 41 | 10 | 18 | 9 | 30 | 20 | 134 | 32 | 0 | 17 | 0 | 32 | 40 | 53 | 42 | 0 | 0 | 55 | 83 | 0 | 192 | 17 | 0 | 9 | 270 | 16 | 8 | 0 | 148 | 0 | 0 | 162 | 0 | 105 | 0 | 75 | 192 | 87 | 369 | 80 | 105 | 105 | 0 | 123 | 32 | 86 | 114 | 55 | 90 | 300 | 74 | 1 | 108 | 107 | 0 | 35 | 1 | 74 | 51 | 0 | 23 | 0 |  | 924 | 0 | 225 | 0 | 92 | 0 | 0 | 0 | 22 | 52 | 24 | 160 | 27 | 16 | 0 | 0 | 0 | 28 | 35 | 38 | 21 | 42 | 38 | 8 | 35 | 17 | 0 | 8 | 0 | 0 | 240 | 0 | 0 | 189 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 414 | 36 | 0 | 95 | 105 | 95 | 0 | 0 | 95 | 1202 | 0 | 0 | 137 | 0 | 2 | 35 | 175 | 0 | 0 | 1 | 0 | 754 | 5 | 0 |  | 8300 | 5400 | 13700 | 3791 | 924 | 2320 | 0 | 3580 | 2196 | 25 | 198 | 522 | 134 | 10 | 460.7875 | 75.93
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 115 | 69 | 0 | 388 | 329 |  | 0 | 450 | 274 | 88 | 62 | 15 | 216 | 0 | 99 | 81 | 82 | 110 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 19 | 23 | 15 | 33 | 28 | 46 | 0 | 25 | 0 | 90 | 0 | 25 | 228 | 0 | 0 | 0 |  | 25 | 56 | 67 | 80 | 108 | 39 | 14 | 26 | 0 | 0 | 0 | 0 | 355 | 210 | 180 | 0 | 39 | 0 | 0 | 51 | 0 | 43 | 40 | 18 | 9 | 0 | 5 | 146 | 47 | 0 | 17 | 0 | 32 | 40 | 53 | 42 | 0 | 0 | 56 | 83 | 0 | 192 | 17 | 0 | 10 | 260 | 16 | 8 | 128 | 258 | 145 | 60 | 172 | 56 | 130 | 0 | 100 | 192 | 101 | 402 | 103 | 105 | 105 | 0 | 224 | 54 | 86 | 114 | 113 | 85 | 273 | 89 | 0 | 160 | 107 | 0 | 35 | 0 | 73 | 52 | 0 | 0 | 0 |  | 890 | 0 | 220 | 0 | 97 | 0 | 0 | 0 | 17 | 60 | 32 | 168 | 34 | 16 | 0 | 0 | 0 | 28 | 35 | 60 | 21 | 42 | 38 | 8 | 35 | 18 | 0 | 8 | 0 | 0 | 240 | 0 | 0 | 192 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 414 | 36 | 0 | 95 | 105 | 96 | 0 | 0 | 95 | 1212 | 0 | 0 | 137 | 0 | 0 | 36 | 175 | 0 | 0 | 0 | 0 | 754 | 0 | 0 |  | 9140 | 5437 | 14577 | 3795 | 890 | 2293 | 389 | 4109 | 2206 | 25 | 175 | 549 | 146 | 0 | 758.4562 | 75.92
19:30 | 0 | 0 | 0 | 180 | 115 | 69 | 0 | 397 | 334 |  | 0 | 450 | 277 | 89 | 62 | 55 | 217 | 0 | 95 | 81 | 83 | 110 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 19 | 23 | 15 | 33 | 30 | 46 | 0 | 25 | 0 | 90 | 0 | 25 | 222 | 0 | 0 | 0 |  | 25 | 56 | 67 | 80 | 108 | 39 | 14 | 29 | 0 | 0 | 0 | 0 | 350 | 210 | 180 | 0 | 40 | 0 | 0 | 51 | 0 | 43 | 52 | 18 | 9 | 16 | 20 | 148 | 46 | 0 | 18 | 0 | 32 | 40 | 53 | 42 | 0 | 0 | 61 | 83 | 0 | 192 | 17 | 0 | 10 | 260 | 16 | 8 | 20 | 262 | 15 | 25 | 173 | 27 | 144 | 0 | 100 | 192 | 120 | 405 | 103 | 105 | 105 | 0 | 224 | 54 | 86 | 114 | 113 | 90 | 320 | 89 | 0 | 162 | 107 | 0 | 0 | 0 | 73 | 52 | 0 | 0 | 0 |  | 853 | 0 | 230 | 0 | 96 | 0 | 0 | 0 | 21 | 64 | 40 | 168 | 34 | 16 | 0 | 0 | 0 | 28 | 35 | 70 | 21 | 42 | 40 | 8 | 35 | 18 | 0 | 8 | 0 | 0 | 250 | 0 | 0 | 192 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 414 | 36 | 0 | 95 | 105 | 92 | 0 | 0 | 95 | 1244 | 0 | 0 | 137 | 0 | 0 | 73 | 175 | 0 | 0 | 0 | 0 | 750 | 0 | 0 |  | 8999 | 5513 | 14512 | 3894 | 853 | 2304 | 87 | 4213 | 2244 | 25 | 175 | 569 | 148 | 0 | 864.4374 | 0
20:00 | 0 | 0 | 0 | 180 | 115 | 69 | 0 | 397 | 339 |  | 0 | 450 | 307 | 90 | 63 | 50 | 218 | 0 | 90 | 82 | 82 | 133 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 23 | 18 | 33 | 30 | 46 | 0 | 25 | 0 | 90 | 0 | 25 | 224 | 0 | 0 | 0 |  | 25 | 56 | 67 | 80 | 108 | 39 | 14 | 32 | 0 | 0 | 0 | 0 | 345 | 208 | 182 | 0 | 41 | 0 | 0 | 51 | 0 | 43 | 52 | 18 | 9 | 33 | 20 | 146 | 57 | 0 | 18 | 0 | 32 | 40 | 53 | 42 | 0 | 0 | 60 | 84 | 0 | 194 | 17 | 0 | 10 | 260 | 8 | 8 | 10 | 263 | 65 | 60 | 173 | 53 | 137 | 0 | 100 | 193 | 117 | 380 | 103 | 105 | 105 | 0 | 227 | 54 | 86 | 114 | 114 | 90 | 335 | 88 | 0 | 162 | 107 | 0 | 15 | 0 | 77 | 53 | 0 | 36 | 0 |  | 853 | 0 | 230 | 0 | 97 | 160 | 0 | 0 | 31 | 70 | 32 | 169 | 35 | 48 | 0 | 0 | 0 | 28 | 39 | 74 | 18 | 42 | 40 | 43 | 35 | 20 | 0 | 8 | 0 | 0 | 250 | 17 | 0 | 193 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 414 | 36 | 0 | 95 | 105 | 92 | 0 | 0 | 95 | 1244 | 0 | 0 | 150 | 0 | 0 | 74 | 175 | 0 | 0 | 0 | 0 | 753 | 0 | 0 |  | 9236 | 5800 | 15036 | 3909 | 853 | 2348 | 188 | 4316 | 2247 | 25 | 388 | 616 | 146 | 0 | 796.2408 | 75.92
21:00 | 0 | 0 | 0 | 180 | 120 | 70 | 0 | 399 | 326 |  | 0 | 450 | 308 | 96 | 63 | 55 | 212 | 0 | 84 | 85 | 82 | 48 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 23 | 18 | 33 | 16 | 48 | 0 | 25 | 0 | 90 | 0 | 25 | 225 | 0 | 0 | 0 |  | 25 | 57 | 67 | 80 | 108 | 39 | 14 | 30 | 0 | 0 | 0 | 0 | 345 | 207 | 180 | 0 | 41 | 0 | 0 | 51 | 0 | 43 | 52 | 18 | 9 | 33 | 20 | 152 | 100 | 0 | 18 | 0 | 32 | 40 | 53 | 46 | 0 | 0 | 60 | 84 | 0 | 195 | 17 | 0 | 10 | 285 | 0 | 8 | 128 | 263 | 290 | 65 | 174 | 53 | 131 | 0 | 100 | 182 | 133 | 402 | 104 | 105 | 100 | 0 | 228 | 54 | 86 | 114 | 115 | 90 | 385 | 89 | 0 | 162 | 107 | 0 | 35 | 0 | 93 | 54 | 0 | 36 | 0 |  | 854 | 0 | 230 | 0 | 98 | 158 | 0 | 0 | 27 | 73 | 32 | 169 | 36 | 110 | 0 | 0 | 0 | 28 | 40 | 71 | 21 | 42 | 40 | 43 | 35 | 20 | 0 | 8 | 0 | 0 | 250 | 17 | 0 | 197 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 414 | 36 | 0 | 95 | 105 | 93 | 0 | 0 | 95 | 1244 | 0 | 0 | 150 | 0 | 0 | 112 | 175 | 0 | 0 | 0 | 0 | 753 | 0 | 0 |  | 9661 | 5943 | 15604 | 4039 | 854 | 2363 | 536 | 4473 | 2247 | 25 | 386 | 529 | 152 | 0 | 589 | 75.92
22:00 | 0 | 0 | 0 | 180 | 120 | 70 | 0 | 398 | 326 |  | 0 | 450 | 269 | 96 | 63 | 55 | 220 | 0 | 83 | 85 | 82 | 48 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 23 | 11 | 33 | 30 | 48 | 0 | 25 | 0 | 90 | 0 | 25 | 227 | 0 | 0 | 0 |  | 25 | 48 | 67 | 80 | 108 | 39 | 14 | 24 | 0 | 0 | 0 | 0 | 355 | 211 | 180 | 0 | 42 | 0 | 0 | 51 | 0 | 44 | 52 | 18 | 9 | 33 | 20 | 146 | 93 | 0 | 18 | 0 | 32 | 40 | 53 | 47 | 0 | 0 | 61 | 84 | 0 | 194 | 17 | 0 | 10 | 270 | 8 | 8 | 50 | 273 | 260 | 68 | 174 | 53 | 131 | 0 | 100 | 175 | 150 | 403 | 104 | 105 | 105 | 0 | 228 | 54 | 86 | 114 | 107 | 90 | 395 | 89 | 0 | 162 | 107 | 0 | 35 | 0 | 93 | 54 | 0 | 36 | 0 |  | 852 | 0 | 230 | 0 | 98 | 160 | 0 | 0 | 25 | 66 | 32 | 169 | 36 | 110 | 0 | 0 | 0 | 28 | 40 | 78 | 21 | 42 | 40 | 43 | 35 | 20 | 0 | 8 | 0 | 0 | 250 | 15 | 0 | 198 | 0 | 0 | 0 | 0 | 0 | 84 | 0 | 415 | 36 | 0 | 95 | 105 | 92 | 0 | 0 | 95 | 1244 | 0 | 0 | 150 | 0 | 0 | 114 | 175 | 0 | 0 | 0 | 0 | 753 | 0 | 0 |  | 9522 | 5954 | 15476 | 4094 | 852 | 2305 | 431 | 4471 | 2247 | 25 | 386 | 519 | 146 | 0 | 500.42 | 75.91
23:00 | 0 | 0 | 0 | 180 | 120 | 72 | 0 | 398 | 326 |  | 0 | 450 | 262 | 94 | 63 | 15 | 214 | 0 | 79 | 85 | 50 | 30 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 19 | 23 | 19 | 33 | 30 | 48 | 0 | 25 | 0 | 90 | 0 | 25 | 229 | 0 | 0 | 0 |  | 25 | 48 | 67 | 80 | 108 | 39 | 14 | 26 | 0 | 0 | 0 | 0 | 355 | 212 | 184 | 0 | 43 | 0 | 0 | 51 | 0 | 44 | 52 | 18 | 9 | 33 | 20 | 148 | 93 | 0 | 18 | 0 | 33 | 41 | 53 | 47 | 0 | 0 | 61 | 85 | 0 | 196 | 17 | 0 | 10 | 280 | 16 | 8 | 129 | 273 | 302 | 48 | 174 | 50 | 70 | 0 | 100 | 174 | 150 | 400 | 96 | 105 | 90 | 0 | 212 | 54 | 86 | 114 | 79 | 76 | 390 | 72 | 0 | 162 | 107 | 0 | 35 | 0 | 93 | 52 | 0 | 0 | 0 |  | 824 | 0 | 235 | 0 | 98 | 100 | 0 | 0 | 25 | 66 | 32 | 168 | 37 | 16 | 0 | 0 | 0 | 28 | 40 | 73 | 21 | 42 | 40 | 8 | 35 | 20 | 0 | 8 | 0 | 0 | 250 | 15 | 0 | 198 | 0 | 0 | 0 | 0 | 0 | 98 | 0 | 415 | 36 | 0 | 95 | 105 | 92 | 0 | 0 | 95 | 1244 | 0 | 0 | 150 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 753 | 0 | 0 |  | 9330 | 5515 | 14845 | 4118 | 824 | 2318 | 529 | 4025 | 2247 | 25 | 115 | 496 | 148 | 0 | 912.025 | 75.91
24:00 | 0 | 0 | 0 | 180 | 120 | 72 | 0 | 397 | 326 |  | 0 | 450 | 271 | 95 | 51 | 15 | 218 | 0 | 64 | 85 | 50 | 32 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 23 | 19 | 33 | 30 | 49 | 0 | 0 | 0 | 90 | 0 | 25 | 230 | 0 | 0 | 0 |  | 25 | 42 | 67 | 80 | 0 | 6 | 14 | 27 | 0 | 0 | 0 | 0 | 355 | 204 | 184 | 0 | 44 | 0 | 0 | 43 | 0 | 39 | 52 | 18 | 9 | 33 | 20 | 136 | 93 | 0 | 18 | 0 | 34 | 41 | 53 | 44 | 0 | 0 | 61 | 85 | 0 | 208 | 17 | 0 | 10 | 260 | 16 | 8 | 129 | 273 | 268 | 48 | 174 | 23 | 33 | 0 | 88 | 191 | 150 | 402 | 97 | 88 | 53 | 0 | 87 | 54 | 59 | 114 | 30 | 90 | 400 | 72 | 0 | 126 | 107 | 0 | 35 | 0 | 94 | 35 | 0 | 0 | 0 |  | 824 | 0 | 235 | 0 | 98 | 0 | 0 | 0 | 20 | 66 | 32 | 161 | 37 | 16 | 0 | 0 | 0 | 28 | 40 | 73 | 21 | 42 | 40 | 0 | 35 | 20 | 0 | 8 | 0 | 0 | 250 | 15 | 0 | 197 | 0 | 0 | 0 | 0 | 0 | 117 | 0 | 308 | 36 | 0 | 50 | 105 | 49 | 0 | 0 | 50 | 1244 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 764 | 0 | 0 |  | 8697 | 5131 | 13828 | 4136 | 824 | 2190 | 468 | 3319 | 2258 | 0 | 15 | 482 | 136 | 0 | 1596.76 | 75.91
KWH | 0 | 0 | 0 | 4236750 | 1772800 | 1666454 | 0 | 9664510 | 7762000 |  | 0 | 10179000 | 7192727 | 1460160 | 1774265 | 491917 | 5190893 | 0 | 2360000 | 1515590 | 1513152 | 1573920 | 0 | 0 | 0 | 0 | 665640 | 889022 | 886600 | 375300 | 552000 | 443700 | 760700 | 681400 | 1083840 | 0 | 423480 | 0 | 2600000 | 0 | 541024 | 2183858 | 0 | 0 | 0 |  | 597840 | 1089648 | 1576416 | 1486440 | 1172160 | 489120 | 324384 | 382560 | 0 | 0 | 0 | 0 | 8280000 | 5017000 | 4365818 | 0 | 950256 | 0 | 0 | 1031044 | 0 | 996864 | 326611 | 381636 | 211140 | 738900 | 466280 | 3185280 | 1359360 | 0 | 381132 | 13750 | 789000 | 876360 | 1262400 | 1088208 | 1556263 | 0 | 1393248 | 1969920 | 0 | 4978120 | 401000 | 0 | 218160 | 6618500 | 320112 | 170131 | 1713600 | 3690873 | 4381510 | 932843 | 2656800 | 884853 | 1707120 | 122175 | 1682880 | 4439520 | 1553963 | 8948000 | 1764000 | 2308608 | 1328982 | 27359 | 3005891 | 782602 | 1700319 | 1911780 | 735840 | 1430400 | 8856400 | 1719360 | 295830 | 2322720 | 2581855 | 0 | 857160 | 204094 | 1510080 | 980280 | 0 | 1073890 | 0 |  | 21325818 | 0 | 5332608 | 0 | 1913280 | 565539 | 0 | 0 | 488160 | 1110016 | 822000 | 4003120 | 732454 | 604320 | 0 | 0 | 0 | 666608 | 455679 | 16249668 | 490420 | 782851 | 692170 | 129782 | 779050 | 403440 | 0 | 160254 | 0 | 0 | 5104000 | 134000 | 0 | 4654918 | 0 | 0 | 0 | 0 | 0 | 521782 | 0 | 9785455 | 864480 | 0 | 1589472 | 1816128 | 1503292 | 0 | 43093 | 1569696 | 31606200 | 0 | 0 | 1836000 | 34680 | 641520 | 419328 | 1565923 | 0 | 0 | 216488 | 0 | 18092727 | 1233340 | 0 |  | 195017350 | 140939759 | 335957109 | 90337052 | 21325818 | 56214403 | 7912806 | 69905463 | 54802927 | 423480 | 3339352 | 25678199 | 3185280 | 2832329 | 0
Fuel Cost | 0 | 0 | 0 | 6312757.5 | 1985536 | 2216383.82 | 0 | 10147735.5 | 8382960 |  | 0 | 11095110 | 7983926.97 | 16324588.8 | 23509011.25 | 6517900.25 | 5813800.16 | 0 | 4130000 | 22157925.8 | 21290048.64 | 25513243.2 | 0 | 0 | 0 | 0 | 8466940.8 | 12001797 | 11889306 | 281475 | 414000 | 0 | 0 | 0 | 18436118.4 | 0 | 114339.6 | 0 | 4914000 | 0 | 8845742.4 | 2271212.32 | 0 | 0 | 0 |  | 7801812 | 18175328.64 | 26830600.32 | 20081804.4 | 14862988.8 | 5659118.4 | 411967.68 | 1273924.8 | 0 | 0 | 0 | 0 | 9025200 | 5819720 | 5631905.22 | 0 | 1073789.28 | 0 | 0 | 1721843.48 | 0 | 17215841.28 | 4392917.95 | 522841.32 | 158355 | 1293075 | 349710 | 22870310.4 | 1481702.4 | 0 | 518339.52 | 219175 | 1080930 | 1156795.2 | 2196576 | 1882599.84 | 1789702.45 | 0 | 2702901.12 | 4491417.6 | 0 | 5027901.2 | 862150 | 0 | 431956.8 | 6618500 | 240084 | 129299.56 | 35917056 | 50380416.45 | 91836449.6 | 19281864.81 | 35813664 | 18289911.51 | 23643612 | 1428225.75 | 17367321.6 | 60643843.2 | 20621089.01 | 8232160 | 21450240 | 33382471.68 | 16811622.3 | 0 | 35289160.34 | 8522535.78 | 18074390.97 | 25942854.6 | 9484977.6 | 16850112 | 8147888 | 22265712 | 4274743.5 | 29475316.8 | 29381509.9 | 0 | 11194509.6 | 2438923.3 | 22605897.6 | 12910287.6 | 0 | 0 | 0 |  | 63977454 | 0 | 5972520.96 | 0 | 19917244.8 | 9331393.5 | 0 | 0 | 8791761.6 | 19980288 | 11812140 | 4483494.4 | 1420960.76 | 6587088 | 0 | 0 | 0 | 11179016.16 | 7969825.71 | 254144807.52 | 3776234 | 12964012.56 | 11704594.7 | 1768928.66 | 13142573.5 | 835120.8 | 0 | 121312.278 | 0 | 0 | 27000160 | 5630680 | 0 | 5399704.88 | 0 | 0 | 0 | 0 | 0 | 605267.12 | 0 | 9687600.45 | 11618611.2 | 0 | 18803453.76 | 26243049.6 | 19091808.4 | 0 | 476177.65 | 19056109.44 | 284771862 | 0 | 0 | 13586400 | 392230.8 | 7525029.6 | 6428298.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1148977711.57 | 926197215.048 | 2075174926.618 | 101087625.398 | 63977454 | 67660488.99 | 165325281.92 | 896002944.58 | 311772022 | 114339.6 | 14962073.5 | 414647880.63 | 22870310.4 | 16754505.6 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 120 | 70 | 0 | 409 | 328 |  | 0 | 450 | 300 | 66 | 94 | 15 | 211 | 0 | 95 | 62 | 64 | 82 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 0 | 23 | 18 | 33 | 28 | 35 | 0 | 25 | 0 | 120 | 0 | 17 | 44 | 0 | 0 | 0 |  | 24 | 29 | 62 | 55 | 7 | 26 | 14 | 2 | 0 | 0 | 0 | 0 | 340 | 204 | 184 | 0 | 33 | 0 | 0 | 51 | 0 | 32 | 0 | 17 | 9 | 31 | 20 | 132 | 33 | 0 | 14 | 2 | 34 | 40 | 50 | 42 | 112 | 0 | 50 | 84 | 0 | 197 | 17 | 0 | 8 | 255 | 16 | 8 | 125 | 244 | 250 | 50 | 143 | 50 | 132 | 16 | 62 | 180 | 42 | 375 | 96 | 82 | 51 | 4 | 122 | 17 | 72 | 0 | 9 | 63 | 372 | 72 | 45 | 90 | 107 | 0 | 35 | 29 | 75 | 34 | 0 | 145 | 0 |  | 924 | 0 | 195 | 0 | 72 | 0 | 0 | 0 | 19 | 35 | 32 | 166 | 25 | 16 | 0 | 0 | 0 | 28 | 4 | 83 | 21 | 25 | 40 | 0 | 35 | 15 | 0 | 0 | 0 | 0 | 204 | 0 | 0 | 177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 36 | 0 | 35 | 0 | 35 | 0 | 5 | 35 | 1244 | 0 | 0 | 17 | 4 | 90 | 0 | 0 | 0 | 0 | 30 | 0 | 756 | 176 | 0 |  | 13392 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 120 | 70 | 0 | 399 | 326 | 0 | 0 | 450 | 308 | 96 | 63 | 55 | 212 | 0 | 84 | 85 | 82 | 48 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 23 | 18 | 33 | 16 | 48 | 0 | 25 | 0 | 90 | 0 | 25 | 225 | 0 | 0 | 0 | 0 | 25 | 57 | 67 | 80 | 108 | 39 | 14 | 30 | 0 | 0 | 0 | 0 | 345 | 207 | 180 | 0 | 41 | 0 | 0 | 51 | 0 | 43 | 52 | 18 | 9 | 33 | 20 | 152 | 100 | 0 | 18 | 0 | 32 | 40 | 53 | 46 | 0 | 0 | 60 | 84 | 0 | 195 | 17 | 0 | 10 | 285 | 0 | 8 | 128 | 263 | 290 | 65 | 174 | 53 | 131 | 0 | 100 | 182 | 133 | 402 | 104 | 105 | 100 | 0 | 228 | 54 | 86 | 114 | 115 | 90 | 385 | 89 | 0 | 162 | 107 | 0 | 35 | 0 | 93 | 54 | 0 | 36 | 0 |  | 854 | 0 | 230 | 0 | 98 | 158 | 0 | 0 | 27 | 73 | 32 | 169 | 36 | 110 | 0 | 0 | 0 | 28 | 40 | 71 | 21 | 42 | 40 | 43 | 35 | 20 | 0 | 8 | 0 | 0 | 250 | 17 | 0 | 197 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 414 | 36 | 0 | 95 | 105 | 93 | 0 | 0 | 95 | 1244 | 0 | 0 | 150 | 0 | 0 | 112 | 175 | 0 | 0 | 0 | 0 | 753 | 0 | 0 |  | 15604 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 120 | 76 | 0 | 400 | 330 | 0 | 0 | 450 | 300 | 97 | 85 | 55 | 215 | 0 | 95 | 90 | 92 | 149 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 20 | 23 | 23 | 33 | 31 | 48 | 0 | 25 |  | 90 | 0 | 25 | 225 | 0 | 0 | 0 | 0 | 25 | 60 | 66 | 77 | 108 | 40 | 14 | 20 | 0 | 0 | 0 | 0 | 345 | 210 | 167 | 0 | 41 | 0 | 0 | 51 | 0 | 43 | 52 | 17 | 9 | 33 | 20 | 153 | 90 | 0 | 19 | 0 | 34 | 41 | 51 | 49 | 0 | 0 | 60 | 85 | 0 | 200 | 18 | 0 | 10 | 290 | 16 | 8 | 130 | 300 | 300 | 65 | 180 | 70 | 149 | 0 | 100 | 195 | 150 | 400 | 100 | 105 | 105 | 0 | 230 | 54 | 105 | 114 | 113 | 90 | 400 | 90 | 0 | 162 | 107 | 0 | 35 |  | 92 | 54 | 0 |  |  |  | 943 | 0 | 215 |  | 98 | 0 | 0 | 0 | 35 | 60 | 40 | 170 | 37 | 110 | 0 | 0 | 0 | 28 | 45 | 80 | 21 | 42 | 40 | 43 | 35 | 21 | 0 | 8 | 0 | 0 | 250 | 0 | 0 | 160 |  | 0 | 0 | 0 | 0 | 180 | 0 | 414 | 36 | 0 | 95 | 0 | 95 | 0 | 0 | 95 | 1244 | 0 |  | 150 |  |  | 114 | 0 |  | 0 |  | 0 | 755 |  | 0
Forecast for Day | 0 | 0 | 0 | 180 | 120 | 75 | 0 | 400 | 340 | 0 | 0 | 450 | 300 | 80 | 90 | 15 | 215 | 0 | 95 | 90 | 64 | 32 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 23 | 23 | 33 | 31 | 48 | 0 | 25 | 0 | 90 | 0 | 25 | 225 | 0 | 0 | 0 | 0 | 25 | 48 | 66 | 55 | 0 | 26 | 14 | 5 | 0 | 0 | 0 | 0 | 345 | 200 | 167 | 0 | 41 | 0 | 0 | 51 | 0 | 40 | 0 | 17 | 9 | 33 | 20 | 135 | 33 | 0 | 19 | 1.6 | 34 | 40 | 50 | 44 | 0 | 0 | 60 | 84 | 0 | 200 | 18 | 0 | 10 | 280 | 16 | 8 | 130 | 300 | 300 | 50 | 150 | 0 | 149 | 20 | 50 | 195 | 50 | 400 | 100 | 88 | 51 | 5 | 120 | 17 | 68 | 0 | 9 | 63 | 400 | 54 | 50 | 108 | 107 | 0 | 35 | 30 | 72 | 35 | 0 |  |  |  | 943 | 0 | 215 | 0 | 98 | 0 | 0 | 0 | 20 | 52 | 40 | 170 | 24 | 16 | 0 | 0 | 0 | 28 | 0 | 80 | 21 | 42 | 40 | 0 | 35 | 21 | 0 | 8 | 0 | 0 | 250 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 414 | 36 | 0 | 35 | 0 | 34 | 0 | 8 | 35 | 1244 | 0 |  | 17 | 6 | 100 | 0 | 0 |  | 0 | 30 | 0 | 755 | 130 | 0 |  |  |  |  | g | h | o | c | h | t | s
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 60 | 68 | 0 | 359 | 330 | 0 | 0 | 450 | 313 | 42 | 95 | 15 | 170 | 0 | 93 | 50 | 50 | 32 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 23 | 19 | 33 | 31 | 49 | 0 | 0 | 0 | 90 | 0 | 25 | 225 | 0 | 0 | 0 | 0 | 25 | 35 | 67 | 66 | 0 | 6 | 14 | 4 | 0 | 0 | 0 | 0 | 280 | 204 | 184 | 0 | 42 | 0 | 0 | 51 | 0 | 39 | 0 | 0 | 9 | 32 | 9 | 118 | 33 | 0 | 19 | 1 | 34 | 40 | 50 | 44 | 0 | 0 | 61 | 85 | 0 | 202 | 17 | 0 | 10 | 270 | 16 | 8 | 0 | 97 | 0 | 0 | 47 | 0 | 25 | 5 | 38 | 193 | 55 | 402 | 49 | 88 | 17 | 1 | 88 | 17 | 54 | 0 | 9 | 38 | 400 | 54 | 0 | 54 | 107 | 0 | 35 | 11 | 36 | 35 | 0 | 0 | 0 | 0 | 925 | 0 | 225 | 0 | 98 | 0 | 0 | 0 | 16 | 48 | 32 | 169 | 24 | 16 | 0 | 0 | 0 | 28 | 0 | 80 | 21 | 42 | 24 | 0 | 35 | 21 | 0 | 8 | 0 | 0 | 248 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 416 | 36 | 0 | 35 | 0 | 34 | 0 | 2 | 35 | 1244 | 0 | 0 | 17 | 1 | 33 | 0 | 0 | 0 | 0 | 5 | 0 | 678 | 40 | 0 | 0 |  |  |  | 146.5515 | 21.3258 | 106.8358 | 54.8029 | 0.42348 | 3.1853 | 2.8323
335.9571
| Minimum Generation |  | 11702 | 9:00
| Highest Generation |  | 15604 | 21:00
| Day Peak Generation |  | 13392 | 12:00
| Evening Peak Generation |  | 15604 | 21:00
| HVDC Max Flow |  | 924 | 4:00
| HVDC EvPeak Flow |  | 854 | 21:00
| Load factor L.F |  | 89.71% | [161 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2023-04-18
Till now the maximum generation is : - |  |  |  | 15304 | 21:00 | Hrs on | 2023-04-13
The Summary of Yesterday's |  |  | 2023-04-17 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 13392 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 11656
Evening Peak Generation : |  |  | 15604 | MW Hour : | 21:00 | Available Max Generation : |  | 15617
E.P. Demand (at gen end) : |  |  | 16221 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 16000
Maximum Generation : |  |  | 15604 | MW Hour : | 21:00 | Reserve(Generation end) |  | -
Total Gen. (MKWH) : |  |  | 335.9571 | System Load Factor : | 89.71% | Load Shed : |  | 360
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 146 | MW at | 19:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2023-04-18
Actual : |  | 75.89 | Ft.(MSL) , | Rule curve : | 84.8 | Ft.( MSL )
Gas Consumed : |  | Total = | 1143.54 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 168748114.388
: |  |  | Coal : | 311772022 | Oil : | 1490938180.63 | Total : | 1971458317.018
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 75 | 1800:00 | 4868.8972 |  |  | 40 | 0.8215%
Chittagong Area |  | 0 | 0:00 | 1351.1159 |  |  | 40 | 2.961%
Khulna Area |  | 10 | 240:00 | 1776.9624 |  |  | 60 | 3.377%
Rajshahi Area |  | 0 | 0:00 | 1568.8632 |  |  | 60 | 3.824%
Cumilla Area |  | 64 | 1536:00 | 1339.0166 |  |  | 50 | 3.734%
Mymensingh Area |  | 275 | 6600:00 | 1101.314 |  |  | 60 | 5.448%
Sylhet Area |  | 15 | 360:00 | 497.0047 |  |  | 15 | 3.018%
Barisal Area |  | 0 | 0:00 | 401.4396 |  |  | 0 | 0%
Rangpur Area |  | 150 | 3600:00 | 869.6114 |  |  | 35 | 4.025%
Total |  | 589 |  | 13774.225 |  |  | 360
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 1,2
2) Ghorasal-3
3) Bhula Nuton Biddut
4) Baghabari-100 MW & 71 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
7) Shajibazar 330 MW
8) Sirajganj- 3
9) Barishal 307 MW
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
08:00 | 17:05 | Hathazari-Madunaghat 132kV Ckt-1 Forced S/D from Hathazari 230/132/33kV end Due to CT Change. | [5 empty] | 22 MW load interrup.
08:15 | 08:43 | Barishal 132/33kV S/S T-1 (405T) HT Scheduled S/D Due to Red-hot remove at 33kv Jhalokathi feeder.
08:28 | 09:47 | Mymensingh 132/33kV S/S Transformer-3 (424T) HT Scheduled S/D Due to Maintanance Work.
08:32 | 12:09 | Ashuganj-Ghorasal 132kV ckt-1 S/D for project work.
| 08:43 | Barishal 132/33kV S/S T-1 (405T) LT is restored.
08:45 | 11:58 | Bogura 132/33kV S/S Transformer-1 LT Scheduled S/D Due to T-2 blast wall work.
08:45 | 11:58 | Bogura 132/33kV S/S Transformer-1 HT Scheduled S/D Due to T-2 blast wall work.
09:15 | 16:51 | Chattak-Sylhet 132 kV Ckt-1 Scheduled S/D from Chhatak 132/33kV end Due to Sylhet ckt-1 CB replace work. and from
Sylhet 132/33kV end Due to Due to CB Replace.
09:36 | 12:16 | Khulna(S)-PDB 330MW CCPP 230kV Ckt-1 Scheduled S/D from Khulna(S) 230/132kV end Due to SCADA test by BPDB.
9:42 |  | Kushiara 163MW GT tripped . | [5 empty] | 63 MW load interrup.
10:16 | 12:47 | Rampura 230/132kV S/S 132 kV Busbar-1 Scheduled S/D Due to Protection team testing work.
10:27 | 11:59 | Shahjadpur 132/33kV S/S T-4(435T) HT Forced S/D Due to 33 kV T-4 Incoming DS (B-Phase) Red-hot Maintenance.
| 10:52 | Kushiara 163MW GT was sync.
| 11:07 | Ghorasal Unit-7 365 MW GT was sync.
| 12:30 | Sikalbaha Gas 225MW ST was sync.
| 13:07 | Khulna 330 MW CCPP GT was sync.
14:09 | 16:03 | Bogura 132/33kV S/S Transformer-2 HT Scheduled S/D.
14:09 | 16:03 | Bogura 132/33kV S/S Transformer-2 HT Scheduled S/D.
14:09 | 16:03 | Bogura 132/33kV S/S Transformer-2 LT Scheduled S/D Due to 132kV CB r phase strand cutting
| 14:30 | Sirajganj Gas 225MW Unit-3 GT was sync.
14:52 | 18:07 | Aminbazar 400/230/132kV S/S Bus-2 Scheduled S/D Due to Interim 400/132 kV ATR testing.
16:01 |  | Shikalbaha 230/132kV S/S Interconnection-1 Forced S/D Due to Emergency maintenance at Shikalbaha 132 KV end.
| 16:28 | Niamatpur 132/33kV S/S 417T HT is restored.
16:30 |  | Kushiara 163MW GT tripped.
| 16:52 | Niamatpur 132/33kV S/S 417T LT is restored.
| 17:05 | Hathazari-Madunaghat 132kV Ckt-1 is restored.
| 17:30 | Sirajganj Gas 225MW Unit-3 ST was sync.
19:10 | 21:05 | Bashundhara-Tongi 132 kV Ckt-1 Scheduled S/D from Tongi 230/132/33kV end Due to Temperature rise Bashundhara end(Red hot).
| 19:36 | Khulna 225MW GT was sync.
| 20:24 | Aminbazar 400/132kV Interim transformer 132kV side switched on.
20:44 | 20:56 | Naogaon 132/33kV S/S T-1 LT Tripped showing A,B,C timing relays Due to trip. | [5 empty] | 67 MW load interrup.
21:22 | 22:12 | Satkhira 132/33kV S/S Transformer-2 (T-2) LT Tripped showing Over current relay relays Due to over current. | [5 empty] | 155 MW load interrup.
21:22 | 21:39 | Satkhira 132/33kV S/S Transformer-1 (T-1) LT Tripped showing Over current relay relays Due to Over current.
21:22 | 21:39 | Satkhira 132/33kV S/S Transformer-2 (T-2) HT Tripped showing Over current relay relays Due to Definite over current.
00:10 |  | Aftabnagar-Rampura 132kV Ckt-1 Forced S/D from Noapara 132/33kV end Due to Power Station Date Expired.
02:22 | 03:10 | Feni 132/33kV S/S T-1(405T) LT Tripped showing over current , Earth fault relays. | [5 empty] | 38 MW load interrup.
05:37 | 06:54 | Barishal 132/33kV S/S T-2 (415T) LT Scheduled S/D Due to Hot spot tightening work.
05:38 | 06:53 | Barishal 132/33kV S/S T-2 (415T) HT Scheduled S/D Due to Hot spot tightening work.
06:43 |  | Ghorashal U-7 CCPP GT was shut down due to air compressor maint.
06:55 |  | Mirpur, Uttara & Uttara 3rd phase have been shifted on Aminbazar 400/132 kv (interim) Transformer.
07:21 |  | Jhenaidah 132/33kV S/S Transformer T-1 HT Forced S/D due to Red hot maintenance. | [5 empty] | 25 MW load interrup.
7:21 |  | Jhenaidah 132/33kV S/S Transformer T-1 LT Forced S/D due to Red hot maintenance.
07:25 |  | Barishal 230/132kV S/S T-4 LT Scheduled S/D Due to Red Hot Maintenance.
07:26 |  | Barishal 230/132kV S/S T-4 HT Scheduled S/D Due to Red Hot Maintenance.
07:32 |  | Jamalpur 132/33kV S/S T-2 HT Scheduled S/D Due to Maintenance work due to temperature increase of 33kV CB connector. | [5 empty] | 6 MW load interrup.
07:32 |  | Jamalpur 132/33kV S/S T-2 LT Scheduled S/D Due to Maintenance work due to temperature increase of 33kv CB connector.
| 07:54 | Ghorashal Unit-7 365 MW GT was sync.
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2023-04-17 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4236750
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 120 | 1772800 | ST under S/D
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 70 | 1666454 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 399 | 9664510 | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 326 | 7762000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 10179000
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 96 | 1460160 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 308 | 7192727 | FGMO
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 63 | 1774265 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 55 | 491917
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 375300
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 84 | 2360000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 85 | 1515590 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 212 | 5190893
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 82 | 1513152 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 665640
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 48 | 1573920 | Fuel shortage
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 889022
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 886600
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 41 | 995700 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 760700
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 16 | 681400 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 48 | 1083840 | 0:00
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 263 | 3690873 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 290 | 4381510
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 65 | 932843 | Fuel shortage
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 53 | 884853 | Fuel shortage
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 131 | 1707120 | Engine problem
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 2308608
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 89 | 1719360 | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 2322720
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 204094
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 54 | 980280
| Dhaka area Total |  |  |  | 5847 | 4111 | 83824601
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 90 | 2600000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 25 | 541024
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 122175
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 39 | 489120 | Fuel shortage
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 25 | 423480 | Low Water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 225 | 2183858
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 100 | 1328982
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 57 | 1089648 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 67 | 1576416 | Engine problem
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 80 | 1486440 | Engine problem
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 100 | 1682880
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 14 | 324384 | Gas shortage
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 30 | 382560
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 108 | 1172160
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 27359
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 228 | 3005891 | Engine problem
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 782602
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 86 | 1700319 | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 90 | 1430400
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 107 | 2581855 | Engine problem
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 0 | 36 | 1073890 | On test.
| Chattogram area Total |  |  |  | 2382 | 1561 | 26005443
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 207 | 5017000 | FGMO
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 0 | 0 | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 345 | 8280000 | FGMO
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 0 | 0 | Under maint.
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 41 | 950256 | Gas shortage
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 0 | 0 | Gas shortage
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 180 | 4365818 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1031044
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 133 | 1553963 | Engine problem
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 43 | 996864 | Engine problem
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 182 | 4439520 | Engine problem
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 381636 | Engine problem
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 9 | 211140 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 152 | 3185280
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 738900
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 326611
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 20 | 466280 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 128 | 1713600 | Fuel shortage
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 1911780
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 115 | 735840
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 35 | 857160 | Engine problem
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 93 | 1510080 | Fuel shortage
| Cumilla Area Total |  |  |  | 3151 | 1951 | 38672772
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 100 | 1359360 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 381132 | Engine problem
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 13750
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 174 | 2656800 | Engine problem
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 104 | 1764000 | Engine problem
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 295830
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 25 | 597840 | Engine problem
| Mymensingh Area Total |  |  |  | 614 | 421 | 7068712
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 32 | 789000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 40 | 876360 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 1556263 | Gas shortage
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 1262400
| Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 46 | 1088208
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 8 | 170131 | Engine problem
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 60 | 1393248
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 84 | 1969920
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 195 | 4978120 | Machine problem
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 401000
| Sylhet 50MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 0 | 320112 | Engine problem
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 285 | 6618500 | Gas shortage
104 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 402 | 8948000 | FGMO
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 218160 | Engine problem
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 385 | 8856400
| Sylhet Area Total |  |  |  | 2427 | 1617 | 39445822
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Fuel shortage
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 854 | 21325818
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 98 | 1913280 | Engine problem
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 27 | 488160 | Engine problem
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 158 | 565539 | Fuel conservation
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 73 | 1110016 | Engine problem
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 230 | 5332608 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 32 | 822000
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Fuel shortage
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 36 | 864480 | Fuel shortage
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 105 | 1816128
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 641520
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 0 | 175 | 1565923 | On test.
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 660*2 | 617 | 0 | 0 | On test.
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3001 | 1788 | 36445472
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 110 | 604320
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 36 | 732454 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 169 | 4003120 | Machine problem
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1244 | 31606200
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 0 | 0 | Under maint.
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 150 | 1836000
| Barisal 307 MW |  | BCPCL | 307*1 | 307 | 0 | 0 | On test.
| Barisal Area Total |  |  |  | 2265 | 1709 | 38782094
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 28 | 666608 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 40 | 455679 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 21 | 490420 | Contract Expired
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 42 | 782851 | Engine problem
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 40 | 692170 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 197 | 4654918 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 72 | 521782 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 414 | 9785455
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 35 | 779050 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 20 | 403440
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 160254
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 43 | 129782 | Engine problem
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 71 | 16249668 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Fuel shortage
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 95 | 1589472 | Fuel shortage
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 95 | 1569696 | Fuel shortage
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 34680
| Adani Power Jharkhanda Ltd |  | Import | 0 | 0 | 753 | 18092727 | On test.
| Rajshahi Area Total |  |  |  | 2129 | 1974 | 57058652
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 250 | 5104000 | Coal shortage
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 134000
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 93 | 1503292 | Fuel shortage
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 43093
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 112 | 419328
| Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 216488
| Teesta Solar Limited |  | BPCL | 16*12.5 | 0 | 0 | 1233340
| Rangpur Area Total |  |  |  | 750 | 472 | 8653541
| Total |  |  |  | 22566 | 15604 | 335957109
| Eastern Grid Total |  |  |  | 14421 | 9661 | 195017350
| Western Grid Total |  |  |  | 8145 | 5943 | 140939759
| National Grid Total |  |  |  | 22566 | 15604 | 335957109
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2023-04-17
| (a) ENTIRE EASTERN GRID : |  | 9772.77 | MW | (b) ENTIRE WESTERN GRID : |  | 5137.6 | MW
| i) Dhaka area |  | 5237.27 | MW | i) Khulna area |  | 2005 | MW
| ii) Chittagong area |  | 1430.5 | MW | ii) Rajshahi area |  | 1737.6 | MW
| iii) Comilla area |  | 1512 | MW | iii) Barisal area |  | 512 | MW
| iv) Mymensingh area |  | 982 | MW | iv) Rangpur area |  | 883 | MW
| v) Sylhet area |  | 611 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 14910.37 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | Chhatak | 37 | 21:00 | Kamrangirchar | 56 | 11:00 | Natore | 176 | 22:00 | Shitalakhya | 138 | 15:00
2 | AKSML | 113 | 02:00 | Chowmuhani | 240 | 22:00 | Kaptai | 5 | 19:30 | Nawabganj | 56.6 | 21:00 | Sholosohor | 37 | 19:00
3 | Aftabnagar | 59 | 00:00 | Chuadanga | 115 | 21:00 | Kazla | 101 | 17:00 | Netrakona | 114 | 23:00 | Shyampur | 166 | 00:00
4 | Agargaon | 105 | 13:00 | Coxsbazar | 138.5 | 19:30 | Keranigonj | 64 | 23:00 | New | 80.6 | 11:00 | Siddhirganj | 124 | 14:00
5 | Agrabad | 82 | 11:00 | Cumilla(N) | 203 | 22:00 | Khagrachori | 34 | 21:00 | Niamatpur | 107 | 21:00 | Sirajganj | 130 | 22:00
6 | Amnura | 98 | 22:00 | Cumilla(S) | 201 | 21:00 | Khulna | 111 | 22:00 | Noapara | 54 | 20:00 | Sonargaon | 93 | 00:00
7 | Ashuganj | 69 | 00:00 | Daudkandi | 170 | 21:00 | Khulshi | 197 | 19:00 | PHP | 3 | 06:00 | Sreemongol | 72 | 21:00
8 | BIPTC | N/A | N/A | Dhaka | 44 | 13:00 | Kishoreganj | 100 | 10:00 | Pabna | 119 | 23:00 | Sreepur | 73.9 | 14:00
9 | BSRM | 104 | 10:00 | Dhamrai | 130 | 22:00 | Kodda | 285 | 20:00 | Palashbari | 146 | 21:00 | Srinagar | 52.27 | 21:00
10 | Bagerhat | 103 | 21:00 | Dhanmondi | 181 | 13:00 | Kulaura | 52 | 21:00 | Panchagarh | 54 | 20:00 | Sunamganj | 62 | 21:00
11 | Bakulia | 123 | 19:00 | Dohazari | 102 | 20:00 | Kurigram | 64 | 19:30 | Patuakhali | 124 | 22:00 | Sylhet | 147 | 20:00
12 | Banani | 89 | 12:00 | Faridpur | 180 | 20:00 | Kushtia | 152 | 20:00 | Payra | 22 | 00:00 | TK | 33 | 19:00
13 | Bangabhaban | 28 | 12:00 | Fatullah | 70 | 16:00 | Lalbag | 80 | 13:00 | Postogola | 49 | 00:00 | Tangail | 228 | 20:00
14 | Barapukuria | 63 | 20:00 | Fenchuganj | 51 | 04:00 | Lalmonirhat | 58 | 19:00 | Purbachal | 24 | 23:00 | Thakurgaon | 91 | 19:00
15 | Barguna | 24 | 23:00 | Feni | 158 | 22:00 | Madanganj | 48 | 17:00 | Purbasadipur | 118 | 19:30 | Tongi | 145 | 19:30
16 | Barishal | 121 | 21:00 | GPH | 72 | 20:00 | Madaripur | 129 | 21:00 | Rahanpur_I | 0 | 00:00 | Ullon | 46 | 00:00
17 | Barishal-230 | 106 | 21:00 | Ghorashal | 81 | 19:00 | Madartek | 107 | 01:00 | Rahim | 41 | 17:00 | Uttara | 111 | 19:00
18 | Baroaulia | 70 | 13:00 | Goalpara | 44 | 21:00 | Madunaghat | 73 | 19:00 | Rajbari | 82 | 20:00 | UttaraNew | 42 | 23:00
19 | Baroirhat | 60 | 19:00 | Gollamari | 61 | 21:00 | Magura | 70 | 20:00 | Rajendrapur | 96 | 18:30 | Zigatola | 100 | 19:00
20 | Bashundhara | 202 | 19:00 | Gopalganj | 120 | 21:00 | Mahasthangarh | 92 | 21:00 | Rajshahi | 191 | 21:00
21 | BashundharaCement | 7 | 11:00 | Gulshan | 156 | 13:00 | Manikganj | 108 | 18:30 | Rajshahi-230 | 42 | 22:00
22 | Beanibazar | 81 | 21:00 | Halishahar | 102 | 11:00 | Maniknagar | 106 | 15:00 | Ramganj | 122 | 21:00
23 | Benapole | 78 | 20:00 | HaripurSBU | 155 | 18:00 | Matarbari | 48 | 21:00 | Rampur | 34 | 22:00
24 | Bhaluka | 96 | 09:00 | Hasnabad | 115 | 00:00 | Matuail | 70 | 15:00 | Rangamati | 20 | 19:00
25 | Bhandaria | 58 | 22:00 | Hathazari | 71 | 19:00 | Millgate | 86 | 10:00 | Rangpur | 129 | 22:00
26 | Bhangura | 53 | 23:00 | Ishurdi | 84 | 22:00 | Mirpur | 172 | 19:00 | Ruppur | 5.6 | 16:00
27 | Bheramara(GK) | 72 | 22:00 | Jaldhaka | 65 | 19:00 | Mirsorai | 6 | 20:00 | SSM | 18 | 05:00
28 | Bhulta | 244 | 01:00 | Jamalpur | 162 | 20:00 | Mithapukur | 40 | 21:00 | Saidpur | 102 | 18:00
29 | Bog-Sherpur | 74 | 22:00 | Jashore | 167 | 21:00 | Modern | 0 | 00:00 | Satkhira | 155 | 21:00
30 | Bogura | 196 | 22:00 | Jhenaidah | 156 | 22:00 | Mogbazar | 146 | 15:00 | Satmasjid | 149 | 19:00
31 | Borhanuddin | 62 | 02:00 | Joydebpur | 163 | 12:00 | Mongla | 28 | 04:00 | Savar | 198 | 12:00
32 | Brahmanbaria | 150 | 00:00 | Joypurhat | 72 | 21:00 | Motijheel | 54 | 15:00 | Shahjadpur | 139 | 22:00
33 | Cantonment | 178 | 19:00 | Juldah | 26 | 23:00 | Munshiganj | 120 | 21:00 | Shahjibazar | 130 | 20:00
34 | Chandpur | 76 | 21:00 | KSRM | 33 | 18:00 | Mymensingh | 267 | 00:00 | Shahmirpur | 49 | 23:00
35 | Chandraghona | 33 | 18:30 | Kabirpur | 265 | 21:00 | Naogaon | 155 | 20:00 | Shariatpur | 94 | 22:00
36 | Chapai | 87 | 22:00 | Kachua | 96 | 19:30 | Narail | 64 | 21:00 | Sherpur | 136 | 19:00
37 | Charsaidpur | 50.5 | 23:00 | Kallyanpur | 117 | 18:30 | Narinda | 83 | 13:00 | Shikalbaha | 37 | 19:00
38 | Chauddagram | 75 | 20:00 | Kalurghat | 38 | 11:00 | Narshingdi | 185 | 18:00 | Shikalbaha-230 | N/A | N/A
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2023-04-17 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 397 | 06:00 | 383 | 16:00 | Kaliakoir | N/A | N/A | N/A | N/A
| Bhulta | 380 | 19:00 | 365 | 16:00 | Madunaghat_I | 415 | 17:00 | 382 | 04:00
| Bibiana | 404 | 00:00 | 394 | 17:00 | Payra | 413 | 06:00 | 405 | 16:00
| BIPTC | 399 | 01:00 | 387 | 16:00 | Rahanpur_I | 418 | 00:00 | 403 | 21:00
| Gopalganj | 408 | 00:00 | 385 | 16:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 226 | 06:00 | 215 | 16:00 | Hathazari | 238 | 00:00 | 220 | 04:00
| AKSML | 239 | 17:00 | 204 | 04:00 | Ishurdi | 237 | 19:30 | 225 | 12:00
| Aminbazar | 228 | 19:00 | 218 | 15:00 | Jhenaidah | 228 | 01:00 | 214 | 12:00
| Ashuganj | 236 | 19:00 | 228 | 13:00 | Kaliakoir | N/A | N/A | N/A | N/A
| Baghabari | 232 | 00:00 | 202 | 03:00 | Keranigonj | 226 | 06:00 | 216 | 16:00
| Barapukuria | 219 | 08:00 | 209 | 06:00 | Khulna(S) | 235 | 02:00 | 221 | 12:00
| Barishal | 231 | 08:00 | 224 | 04:00 | Madunaghat_I | 239 | 17:00 | 223 | 05:00
| Bheramara | 235 | 00:00 | 222 | 12:00 | Maniknagar | 225 | 00:00 | 216 | 16:00
| Bhulta | 229 | 03:00 | 219 | 16:00 | Meghnaghat | 231 | 00:00 | 224 | 16:00
| Bibiana | 239 | 00:00 | 233 | 10:00 | Mirsorai | 239 | 17:00 | 219 | 04:00
| BIPTC | 237 | 19:30 | 222 | 12:00 | Rajshahi | 235 | 00:00 | 222 | 06:00
| Bogura | 226 | 05:00 | 216 | 22:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 231 | 05:00 | 228 | 12:00 | Rampura | 226 | 01:00 | 217 | 16:00
| BSRM | 239 | 17:00 | 221 | 05:00 | Shikalbaha | 237 | 17:00 | 223 | 04:00
| Cumilla(N) | 232 | 19:00 | 222 | 01:00 | Shyampur | 227 | 02:00 | 218 | 16:00
| Fenchuganj | 242 | 04:00 | 237 | 22:00 | Siddhirganj | 229 | 00:00 | 222 | 15:00
| Ghorashal | N/A | N/A | N/A | N/A | Sirajgonj | 238 | 00:00 | 230 | 05:00
| GPH | 240 | 17:00 | 220 | 04:00 | Sreepur | 234 | 00:00 | 228 | 12:00
| Haripur | 226 | 00:00 | 218 | 16:00 | Tongi | 225 | 23:00 | 214 | 13:00
| Hasnabad | 227 | 00:00 | 221 | 09:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 137 | 06:00 | 127 | 16:00 | Lalbag | 134 | 07:00 | 125 | 16:00
| Agargaon | 131 | 03:00 | 123 | 16:00 | Lalmonirhat | 127 | 05:00 | 117 | 18:00
| Agrabad | 138 | 17:00 | 126 | 03:00 | Madanganj | 134 | 03:00 | 126 | 16:00
| AKS | 136 | 17:00 | 124 | 03:00 | Madaripur | 134 | 02:00 | 128 | 11:00
| Aminbazar | 133 | 23:00 | 125 | 15:00 | Madartek | 136 | 06:00 | 127 | 12:00
| Amnura | 135 | 09:00 | 125 | 22:00 | Madunaghat | 140 | 17:00 | 125 | 04:00
| Ashuganj | 138 | 18:30 | 135 | 07:00 | Magura | 137 | 00:00 | 123 | 21:00
| Bagerhat | 138 | 01:00 | 125 | 21:00 | Mahasthangarh | 131 | 00:00 | 120 | 22:00
| Bakulia | 138 | 17:00 | 123 | 04:00 | Manikganj | 135 | 19:00 | 126 | 16:00
| Banani | 136 | 03:00 | 127 | 11:00 | Maniknagar | 134 | 05:00 | 126 | 16:00
| Bangabhaban | 134 | 03:00 | 126 | 15:00 | Matarbari | 130 | 17:00 | 108 | 18:00
| Barapukuria | 135 | 20:00 | 126 | 18:00 | Matuail | 133 | 18:30 | 126 | 16:00
| Barguna | 138 | 18:00 | 128 | 05:00 | Millgate | 133 | 08:00 | 124 | 16:00
| Barishal | 137 | 01:00 | 126 | 05:00 | Mirpur | 139 | 05:00 | 124 | 12:00
| Barishal-230 | 134 | 08:00 | 127 | 23:00 | Mithapukur | 129 | 20:00 | 119 | 07:00
| Baroaulia | 140 | 17:00 | 130 | 09:00 | Modern | 138 | 00:00 | 123 | 04:00
| Baroirhat | 135 | 17:00 | 123 | 21:00 | Mogbazar | 137 | 06:00 | 128 | 12:00
| Bashundhara | 134 | 08:00 | 123 | 15:00 | Mongla | 136 | 02:00 | 125 | 06:00
| BashundharaCement | 134 | 00:00 | 126 | 16:00 | Motijheel | 134 | 03:00 | 126 | 15:00
| Beanibazar | 134 | 23:00 | 124 | 21:00 | Munshiganj | 134 | 19:00 | 126 | 16:00
| Benapole | 136 | 01:00 | 120 | 21:00 | Mymensingh | 124 | 00:00 | 109 | 03:00
| Bhaluka | 125 | 18:30 | 105 | 03:00 | Naogaon | 128 | 01:00 | 109 | 22:00
| Bhandaria | 132 | 01:00 | 121 | 22:00 | Narail | 136 | 01:00 | 118 | 21:00
| Bhangura | 137 | 00:00 | 129 | 22:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bheramara | 135 | 00:00 | 129 | 12:00 | Narshingdi | 130 | 19:00 | 121 | 18:00
| Bheramara(GK) | 137 | 00:00 | 130 | 21:00 | Natore | 133 | 00:00 | 124 | 22:00
| Bhulta | 127 | 19:00 | 119 | 14:00 | Nawabganj | 133 | 01:00 | 124 | 16:00
| Bog-Sherpur | 133 | 00:00 | 123 | 22:00 | Netrakona | 121 | 06:00 | 109 | 08:00
| Bogura | 135 | 03:00 | 125 | 22:00 | New | 135 | 08:00 | 125 | 16:00
| Bogura-230 | 135 | 01:00 | 124 | 22:00 | Niamatpur | 126 | 01:00 | 101 | 22:00
| Brahmanbaria | 134 | 18:30 | 130 | 04:00 | Noapara | 138 | 00:00 | 127 | 21:00
| Cantonment | 131 | 06:00 | 122 | 16:00 | Pabna | 134 | 00:00 | 125 | 22:00
| Chandpur | 138 | 17:00 | 124 | 21:00 | Palashbari | 127 | 01:00 | 116 | 22:00
| Chandraghona | 140 | 00:00 | 128 | 12:00 | Panchagarh | 129 | 20:00 | 110 | 18:00
| Chapai | 135 | 00:00 | 126 | 22:00 | Patuakhali | 139 | 01:00 | 130 | 05:00
| Charsaidpur | 134 | 19:00 | 127 | 16:00 | Payra | 140 | 00:00 | 136 | 05:00
| Chauddagram | 135 | 19:30 | 124 | 04:00 | PHP | 136 | 17:00 | 123 | 21:00
| Chhatak | 132 | 00:00 | 126 | 21:00 | Postogola | 132 | 07:00 | 125 | 16:00
| Chowmuhani | 135 | 17:00 | 118 | 21:00 | Purbachal | 137 | 00:00 | 123 | 16:00
| Chuadanga | 134 | 01:00 | 113 | 21:00 | Purbasadipur | 128 | 20:00 | 112 | 07:00
| Coxsbazar | 129 | 17:00 | 107 | 21:00 | Rahim | 133 | 00:00 | 128 | 16:00
| Cumilla(N) | 136 | 19:00 | 128 | 04:00 | Rajbari | 133 | 00:00 | 124 | 21:00
| Cumilla(S) | 136 | 19:00 | 123 | 14:00 | Rajendrapur | 136 | 19:30 | 126 | 16:00
| Daudkandi | 135 | 19:00 | 126 | 20:00 | Rajshahi | 133 | 00:00 | 125 | 22:00
| Dhaka | 136 | 03:00 | 128 | 12:00 | Rajshahi-230 | 134 | 00:00 | 126 | 22:00
| Dhamrai | 134 | 00:00 | 128 | 18:00 | Ramganj | 136 | 23:00 | 119 | 21:00
| Dhanmondi | 132.5 | 07:00 | 125 | 16:00 | Rampur | 135 | 00:00 | 126 | 04:00
| Dohazari | 137 | 00:00 | 122 | 04:00 | Rampura | 135 | 23:00 | 127 | 16:00
| Faridpur | 133 | 00:00 | 125 | 12:00 | Rangamati | 138 | 17:00 | 127 | 04:00
| Fatullah | 135 | 18:30 | 127 | 16:00 | Rangpur | 129 | 19:30 | 118 | 19:00
| Fenchuganj | 137 | 10:00 | 135 | 04:00 | Ruppur | 135 | 00:00 | 129 | 22:00
| Feni | 137 | 00:00 | 123 | 21:00 | Saidpur | 127 | 04:00 | 117 | 19:00
| Ghorashal | 137 | 00:00 | 137 | 00:00 | Satkhira | 137 | 02:00 | 122 | 21:00
| Goalpara | 139 | 00:00 | 130 | 05:00 | Satmasjid | 131 | 06:00 | 123 | 16:00
| Gollamari | 136 | 00:00 | 123 | 12:00 | Savar | 134 | 19:00 | 123 | 12:00
| Gopalganj | 138 | 01:00 | 124 | 12:00 | Shahjadpur | 138 | 01:00 | 131 | 22:00
| Gopalganj-400 | 136 | 01:00 | 129 | 11:00 | Shahjibazar | 136 | 00:00 | 133 | 11:00
| Gulshan | 136 | 06:00 | 127 | 12:00 | Shahmirpur | 138 | 17:00 | 124 | 04:00
| Halishahar | 139 | 17:00 | 128 | 03:00 | Shariatpur | 132 | 01:00 | 125 | 12:00
| Haripur | 133 | 00:00 | 128 | 16:00 | Sherpur | 126 | 10:00 | 111 | 08:00
| HaripurSBU | 133 | 00:00 | 128 | 16:00 | Shikalbaha | 139 | 17:00 | 125 | 03:00
| Hasnabad | 132 | 04:00 | 126 | 15:00 | Shikalbaha-230 | 136 | 17:00 | 127 | 04:00
| Hathazari | 138 | 16:00 | 127 | 05:00 | Shitalakhya | 134 | 19:00 | 126 | 16:00
| Ishurdi | 136 | 00:00 | 129 | 22:00 | Sholosohor | 137 | 17:00 | 123 | 04:00
| Jaldhaka | 127 | 20:00 | 115 | 07:00 | Shyampur | 135 | 05:00 | 130 | 10:00
| Jamalpur | 129 | 00:00 | 113 | 08:00 | Shyampur-230 | 135 | 19:00 | 128 | 16:00
| Jashore | 136 | 02:00 | 122 | 21:00 | Siddhirganj | 133 | 19:00 | 127 | 16:00
| Jhenaidah | 140 | 02:00 | 125 | 21:00 | Sirajganj | 133 | 00:00 | 124 | 22:00
| Jhenaidah-230 | 140 | 01:00 | 126 | 21:00 | Sonargaon | 133 | 00:00 | 129 | 14:00
| Joydebpur | 140 | 00:00 | 133 | 12:00 | Sreemongol | 134 | 08:00 | 131 | 00:00
| Joypurhat | 125 | 00:00 | 104 | 22:00 | Sreepur | 132 | 00:00 | 129 | 09:00
| Juldah | 139 | 17:00 | 126 | 05:00 | Srinagar | 133 | 06:00 | 124 | 16:00
| Kabirpur | 137 | 19:00 | 122 | 14:00 | SSM | 141 | 02:00 | 132 | 06:00
| Kachua | 136 | 17:00 | 124 | 21:00 | Sunamganj | 131 | 08:00 | 123 | 21:00
| Kaliakoir | N/A | N/A | N/A | N/A | Sylhet | 134 | 00:00 | 130 | 21:00
| Kallyanpur | 133 | 00:00 | 126 | 13:00 | Tangail | 133 | 10:00 | 119 | 16:00
| Kalurghat | 139 | 17:00 | 128 | 04:00 | Thakurgaon | 128 | 20:00 | 110 | 13:00
| Kamrangirchar | 132 | 00:00 | 124 | 16:00 | TK | 138 | 17:00 | 128 | 12:00
| Kaptai | 140 | 00:00 | 130 | 21:00 | Tongi | 135 | 18:30 | 127 | 14:00
| Kazla | 133 | 04:00 | 125 | 16:00 | Ullon | 136 | 06:00 | 126 | 12:00
| Keranigonj | 133 | 03:00 | 126 | 16:00 | Uttara | 132 | 06:00 | 122 | 16:00
| Khagrachori | 138 | 00:00 | 125 | 04:00 | UttaraNew | 132 | 07:00 | 123 | 15:00
| Khulna | 139 | 01:00 | 128 | 12:00 | Zigatola | 133 | 00:00 | 124 | 16:00
| Khulna(S) | 139 | 01:00 | 130 | 11:00
| Khulshi | 136 | 23:00 | 121 | 04:00
| Kishoreganj | 129 | 00:00 | 120 | 18:00
| Kodda | 137 | 18:30 | 125 | 15:00
| KSRM | 139 | 17:00 | 126 | 03:00
| Kulaura | 136 | 00:00 | 131 | 21:00
| Kurigram | 130 | 20:00 | 114 | 19:00
| Kushtia | 137 | 00:00 | 126 | 21:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2023-04-17
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 500 | 8697 | 5131 | 13828 |  |  |  | QF-LDC-11
0:30 | 635 | 8257.5 | 4933.5 | 13191 | Date: | 2023-04-17
1:00 | 770 | 7818 | 4736 | 12554
1:30 | 695 | 7750 | 4778 | 12528
2:00 | 620 | 7682 | 4820 | 12502
2:30 | 610 | 7710.5 | 4943 | 12653.5 | [5 empty] | Gen. at Eve. Peak | 15604 | 15604 MW (21:00 )
3:00 | 600 | 7739 | 5066 | 12805 | [6 empty] | 21:00
3:30 | 570 | 7800.5 | 5122 | 12922.5 | [5 empty] | Gen. at Day Peak | 13392 | 13392 MW (12:00 )
4:00 | 540 | 7862 | 5178 | 13040 | [6 empty] | 12:00
4:30 | 580 | 7815.5 | 5112.5 | 12928 | [5 empty] | Highest Generation | 15604
5:00 | 620 | 7769 | 5047 | 12816 | [6 empty] | 21:00
5:30 | 590 | 7585.5 | 4962.5 | 12548
6:00 | 560 | 7402 | 4878 | 12280
6:30 | 460 | 7345.5 | 4872 | 12217.5
7:00 | 360 | 7289 | 4866 | 12155
7:30 | 490 | 7140.5 | 4846 | 11986.5
8:00 | 620 | 6992 | 4826 | 11818
8:30 | 690 | 6938 | 4822 | 11760
9:00 | 760 | 6884 | 4818 | 11702
9:30 | 658 | 7122.5 | 4870 | 11992.5
10:00 | 556 | 7361 | 4922 | 12283
10:30 | 648 | 7562 | 4936.5 | 12498.5
11:00 | 740 | 7763 | 4951 | 12714
11:30 | 732 | 8081 | 4972 | 13053
12:00 | 724 | 8399 | 4993 | 13392
12:30 | 622 | 8354.5 | 4996.5 | 13351
13:00 | 520 | 8310 | 5000 | 13310
13:30 | 552 | 8298.5 | 5078.5 | 13377
14:00 | 584 | 8287 | 5157 | 13444
14:30 | 632 | 8238 | 5218 | 13456
15:00 | 680 | 8189 | 5279 | 13468
15:30 | 745 | 8027.5 | 5299 | 13326.5
16:00 | 810 | 7866 | 5319 | 13185
16:30 | 730 | 7918.5 | 5299.5 | 13218
17:00 | 650 | 7971 | 5280 | 13251
17:30 | 532 | 8135.5 | 5340 | 13475.5
18:00 | 414 | 8300 | 5400 | 13700
18:30 | 280 | 8720 | 5418.5 | 14138.5
19:00 | 146 | 9140 | 5437 | 14577
19:30 | 149 | 8999 | 5513 | 14512
20:00 | 180 | 9236 | 5800 | 15036 |  |  |  | Executive Engineer
20:30 | 224 | 9448.5 | 5871.5 | 15320 |  |  |  | Network Operation Division
21:00 | 268 | 9661 | 5943 | 15604
21:30 | 454 | 9591.5 | 5948.5 | 15540
22:00 | 640 | 9522 | 5954 | 15476 |  |  |  |  | Page 6 of 7
22:30 | 578 | 9426 | 5734.5 | 15160.5
23:00 | 516 | 9330 | 5515 | 14845
23:30 | 508 | 9013.5 | 5323 | 14336.5
24:00 | 500 | 8697 | 5131 | 13828
15604 MW (21:00 )
13392 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2023-04-17 |  | Energy |  | 335957109
[13 empty] | 2023-04-17 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 4136 | 824 | 2190 | 468 | 3319 | 2258 | 0 | 15 | 482 | 136 | 0 | 0
0:30 | 3913 | 743.5 | 2330 | 481.5 | 2867 | 2211.5 | 12.5 | 15 | 481 | 136 | 0 | 1127.0862 |  | Date: | 43571
1:00 | 3690 | 663 | 2470 | 495 | 2415 | 2165 | 25 | 15 | 480 | 136 | 0 | 2254.1725
1:30 | 3683 | 701.5 | 2466 | 497.5 | 2358.5 | 2166 | 25 | 15 | 482.5 | 133 | 0 | 2139.8972 | [8 empty] | Total Energy | 335.9571 | Total Energy Gen MKWHr Energy Not Served MKWHr Energy Requirement MKWHr | Total Energy Gen 335.957 MKWHr Energy Not Served 28.890 MKWHr Energy Requirement 364.848 MKWHr
2:00 | 3676 | 740 | 2462 | 500 | 2302 | 2167 | 25 | 15 | 485 | 130 | 0 | 2025.6218 | [8 empty] | Energy not Served | 28.8905
2:30 | 3677.5 | 783.5 | 2466 | 500.5 | 2398.5 | 2168.5 | 25 | 15 | 490 | 129 | 0 | 2024.2395 | [8 empty] | Energy Requirement | 364.8476
3:00 | 3679 | 827 | 2470 | 501 | 2495 | 2170 | 25 | 15 | 495 | 128 | 0 | 2022.8571
3:30 | 3687.5 | 875.5 | 2469.5 | 500 | 2571 | 2169 | 12.5 | 15 | 490.5 | 132 | 0 | 1822.4146 | [7 empty] | Shortage
4:00 | 3696 | 924 | 2469 | 499 | 2647 | 2168 | 0 | 15 | 486 | 136 | 0 | 1621.972
4:30 | 3699 | 924 | 2465.5 | 454 | 2590.5 | 2168 | 0 | 7.5 | 485.5 | 134 | 0 | 1494.7946
5:00 | 3702 | 924 | 2462 | 409 | 2534 | 2168 | 0 | 0 | 485 | 132 | 0 | 1367.6173
5:30 | 3685 | 924 | 2463 | 307 | 2411 | 2166 | 0 | 0 | 464 | 127 | 1 | 1338.1269
6:00 | 3668 | 924 | 2464 | 205 | 2288 | 2164 | 0 | 0 | 443 | 122 | 2 | 1308.6365
6:30 | 3659 | 924 | 2453.5 | 179.5 | 2241 | 2164 | 0 | 0 | 440 | 124 | 32.5 | 1251.0381 | [6 empty] | Coal
7:00 | 3650 | 924 | 2443 | 154 | 2194 | 2164 | 0 | 0 | 437 | 126 | 63 | 1193.4396
7:30 | 3610.5 | 924 | 2432.5 | 77 | 2117 | 2163 | 0 | 0 | 434 | 125 | 103.5 | 1348.725 | [5 empty] | Oil
8:00 | 3571 | 924 | 2422 | 0 | 2040 | 2162 | 0 | 0 | 431 | 124 | 144 | 1504.0104
8:30 | 3527.5 | 924 | 2373.5 | 0 | 2004.5 | 2167.5 | 0 | 0 | 443 | 122 | 198 | 1649.6192
9:00 | 3484 | 924 | 2325 | 0 | 1969 | 2173 | 0 | 0 | 455 | 120 | 252 | 1795.2281
9:30 | 3502 | 924 | 2313 | 168 | 2017.5 | 2176 | 12.5 | 0 | 454.5 | 128 | 297 | 1688.7862
10:00 | 3520 | 924 | 2301 | 336 | 2066 | 2179 | 25 | 0 | 454 | 136 | 342 | 1582.3443
10:30 | 3518.5 | 924 | 2298.5 | 385 | 2191 | 2193.5 | 25 | 17 | 449.5 | 134 | 362.5 | 1498.9417
11:00 | 3517 | 924 | 2296 | 434 | 2316 | 2208 | 25 | 34 | 445 | 132 | 383 | 1415.5392
11:30 | 3580 | 924 | 2343 | 454.5 | 2460 | 2206 | 25 | 89.5 | 447 | 132 | 392 | 1241.3615
12:00 | 3643 | 924 | 2390 | 475 | 2604 | 2204 | 25 | 145 | 449 | 132 | 401 | 1067.1839
12:30 | 3633.5 | 924 | 2384 | 496.5 | 2556.5 | 2214.5 | 25 | 154 | 437 | 133 | 393 | 1112.341
13:00 | 3624 | 924 | 2378 | 518 | 2509 | 2225 | 25 | 163 | 425 | 134 | 385 | 1157.4982
13:30 | 3624 | 924 | 2378 | 518 | 2509 | 2225 | 25 | 163 | 425 | 134 | 385 | 1157.4982
14:00 | 3624 | 924 | 2378 | 518 | 2509 | 2225 | 25 | 163 | 425 | 134 | 385 | 1157.4982
14:30 | 3656.5 | 924 | 2385 | 397 | 2634.5 | 2231.5 | 25 | 241.5 | 436.5 | 134 | 323.5 | 1192.5181
15:00 | 3689 | 924 | 2392 | 276 | 2760 | 2238 | 25 | 320 | 448 | 134 | 262 | 1227.5379
15:30 | 3685.5 | 924 | 2388 | 138 | 2804 | 2238.5 | 25 | 319.5 | 457.5 | 134 | 212.5 | 1219.7045
16:00 | 3682 | 924 | 2384 | 0 | 2848 | 2239 | 25 | 319 | 467 | 134 | 163 | 1211.8711
16:30 | 3705 | 924 | 2343.5 | 0 | 2952.5 | 2238 | 25 | 322 | 460 | 132 | 116 | 1089.3016
17:00 | 3728 | 924 | 2303 | 0 | 3057 | 2237 | 25 | 325 | 453 | 130 | 69 | 966.7322
17:30 | 3759.5 | 924 | 2311.5 | 0 | 3318.5 | 2216.5 | 25 | 261.5 | 487.5 | 132 | 39.5 | 713.7598
18:00 | 3791 | 924 | 2320 | 0 | 3580 | 2196 | 25 | 198 | 522 | 134 | 10 | 460.7875
18:30 | 3793 | 907 | 2306.5 | 194.5 | 3844.5 | 2201 | 25 | 186.5 | 535.5 | 140 | 5 | 609.6219
19:00 | 3795 | 890 | 2293 | 389 | 4109 | 2206 | 25 | 175 | 549 | 146 | 0 | 758.4562
19:30 | 3894 | 853 | 2304 | 87 | 4213 | 2244 | 25 | 175 | 569 | 148 | 0 | 777.3485
20:00 | 3909 | 853 | 2348 | 188 | 4316 | 2247 | 25 | 388 | 616 | 146 | 0 | 796.2408
20:30 | 3974 | 853.5 | 2355.5 | 362 | 4394.5 | 2247 | 25 | 387 | 572.5 | 149 | 0 | 692.6204
21:00 | 4039 | 854 | 2363 | 536 | 4473 | 2247 | 25 | 386 | 529 | 152 | 0 | 589
21:30 | 4066.5 | 853 | 2334 | 483.5 | 4472 | 2247 | 25 | 386 | 524 | 149 | 0 | 544.71
22:00 | 4094 | 852 | 2305 | 431 | 4471 | 2247 | 25 | 386 | 519 | 146 | 0 | 500.42
22:30 | 4106 | 838 | 2311.5 | 480 | 4248 | 2247 | 25 | 250.5 | 507.5 | 147 | 0 | 706.2225
23:00 | 4118 | 824 | 2318 | 529 | 4025 | 2247 | 25 | 115 | 496 | 148 | 0 | 912.025
23:30 | 4127 | 824 | 2254 | 498.5 | 3672 | 2252.5 | 12.5 | 65 | 489 | 142 | 0 | 1254.3925 |  | Max Temp. in Dhaka |  | 38.1° C
24:00 | 4136 | 824 | 2190 | 468 | 3319 | 2258 | 0 | 15 | 482 | 136 | 0 | 1596.76
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 335.957 MKWHr Energy Not Served 28.890 MKWHr Energy Requirement 364.848 MKWHr
Shortage
Note on W13: Author:

## Generation
g | 2023-04-17
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 25 | 25 | 25 | 0 | [5 empty] | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 0 | 423480
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 100 | 90 | 100 | 100 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 2600000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 9 | 17 | 17 | 17 | 17 | 17 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 541024
| Teknaf 20MW PP (Solartech) |  |  |  |  | 0 | 0 | 3 | 7 | 13 | 17 | 17 | 16 | 17 | 15 | 11 | 7 | 2 | 0 | [8 empty] | 122175
6 | Sikalbaha 225MW CCPP (Gas) | [7 empty] | 25 | 26 | 29 | 32 | 44 | 73 | 118 | 149 | 149 | 208 | 224 |  | 228 | 222 | 224 | 225 | 227 | 229 | 230 | 2183858
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 66 | 67 | 66 | 64 | 62 | 61 | 64 | 64 | 65 | 65 | 67 |  | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 1576416
12 | Hathazari 100 MW peaking PP | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 44 | 44 | 44 | 29 | 29 | 49 | 51 | 56 | 32 | 56 |  | 56 | 56 | 56 | 57 | 48 | 48 | 42 | 1089648
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 51 | 51 | 68 | 68 | 76 | 85 | 92 | 105 |  | 105 | 105 | 105 | 100 | 105 | 90 | 53 | 1328982
| Daudkandi 200 MW PP (B.Trac) | 105 | 103 | 103 | 103 | 70 | 0 |  |  |  | 106 | 124 | 125 | 125 | 124 | 30 | 0 |  |  |  | 128 | 20 | 10 | 128 | 50 | 129 | 129 | 1713600
14 | Titas 50 MW Peaking PP | 45 | 45 | 45 | 45 | 44 | 44 | 43 | 45 | 45 | 44 | 35 | 32 | 32 | 32 | 32 | 40 | 40 | 41 |  | 43 | 43 | 43 | 43 | 44 | 44 | 39 | 996864
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 96 | 96 | 98 | 95 | 97 | 100 | 98 | 98 | 97 | 97 | 97 | 95 | 94 | 92 | 95 | 93 | 96 | 96 |  | 99 | 95 | 90 | 84 | 83 | 79 | 64 | 2360000
17 | Siddhirganj 335 MW CCPP | 214 | 215 | 219 | 214 | 214 | 211 | 218 | 219 | 180 | 205 | 211 | 211 | 200 | 204 | 198 | 207 | 210 | 212 |  | 216 | 217 | 218 | 212 | 220 | 214 | 218 | 5190893
18 | Kodda 300 MW PP Unit-2 (Summit) | 160 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 244 | 165 | 97 | 95 | 95 | 95 | 148 |  | 258 | 262 | 263 | 263 | 273 | 273 | 273 | 3690873
19 | Ashuganj 195MW PP (APSCL-United) | 184 | 184 | 184 | 184 | 184 | 184 | 184 | 184 | 184 | 184 | 184 | 184 | 182 | 182 | 182 | 180 | 180 | 182 |  | 180 | 180 | 182 | 180 | 180 | 184 | 184 | 4365818
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4236750
24
25 | Ghorasal 365 MW CCPP Unit-7 | 40 | 40 | 40 | 40 | 40 | 50 | 50 |  |  |  |  | 120 | 120 | 115 | 110 | 110 | 110 | 110 |  | 115 | 115 | 115 | 120 | 120 | 120 | 120 | 1772800
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 43 | 40 | 36 | 32 | 33 | 35 | 35 | 35 | 35 | 37 | 37 |  | 39 | 40 | 41 | 41 | 42 | 43 | 44 | 950256
33 | Ashuganj 225 MW CCPP | 208 | 208 | 210 | 207 | 210 | 210 | 211 | 213 | 209 | 210 | 207 | 204 | 204 | 199 | 201 | 201 | 205 | 206 |  | 210 | 210 | 208 | 207 | 211 | 212 | 204 | 5017000
34 | Ashuganj 450 MW CCPP(South) | 340 | 340 | 350 | 340 | 345 | 350 | 355 | 355 | 340 | 345 | 340 | 340 | 320 | 320 | 330 | 330 | 340 | 345 |  | 355 | 350 | 345 | 345 | 355 | 355 | 355 | 8280000
| Ashuganj 450 MW CCPP(North) | [26 empty] | 0
Ashuganj 420 MW CCPP(East)
35 | Ashuganj 55 MW PP (Precision)
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 400 | 394 | 394 | 392 | 395 | 398 | 397 | 395 | 401 | 406 | 406 | 409 | 396 | 402 | 401 | 395 | 396 | 405 |  | 388 | 397 | 397 | 399 | 398 | 398 | 397 | 9664510
40 | Meghnaghat 450 MW CCPP(MPL) | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 |  | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 10179000
41 | Haripur 360MW CCPP(HPL) | 323 | 323 | 323 | 330 | 326 | 326 | 326 | 326 | 339 | 329 | 329 | 328 | 319 | 318 | 319 | 318 | 317 | 324 |  | 329 | 334 | 339 | 326 | 326 | 326 | 326 | 7762000
42 | RPCL 210MW CCPP | 93 | 94 | 95 | 95 | 94 | 83 | 35 | 35 | 35 | 33 | 34 | 33 | 33 | 33 | 32 | 33 | 33 | 32 |  | 47 | 46 | 57 | 100 | 93 | 93 | 93 | 1359360
43 | Sutiakhali 50 MW Solar PP |  |  |  |  | 0 | 1 | 5 | 8 | 21 | 38 | 43 | 45 | 41 | 40 | 30 | 18 | 7 | 1 | [8 empty] | 295830
44 | Fenchugonj CCPP Phase-1 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 32 | 32 |  | 32 | 32 | 32 | 32 | 32 | 33 | 34 | 789000
45 | Fenchugonj CCPP Phase-2 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 31 | 22 | 41 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 41 | 41 | 876360
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 60 | 60 | 60 | 60 | 60 | 60 | 61 | 61 | 60 | 60 | 55 | 50 | 54 | 54 | 54 | 54 | 55 | 55 |  | 56 | 61 | 60 | 60 | 61 | 61 | 61 | 1393248
48 | Shahjibazar 86MW PP (Shahjibazar) | 83 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 84 | 84 | 84 | 83 | 81 | 82 | 82 | 82 | 83 |  | 83 | 83 | 84 | 84 | 84 | 85 | 85 | 1969920
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 195 | 197 | 197 | 196 | 196 | 196 | 196 | 196 | 196 | 196 | 196 | 197 | 197 | 197 | 196 | 193 | 192 | 192 |  | 192 | 192 | 194 | 195 | 194 | 196 | 208 | 4978120
51 | Sylhet 20 MW GTPP | 17 | 17 | 17 | 17 | 18 | 18 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 401000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 9 | 9 | 9 | 8 | 8 | 8 | 8 | 8 | 8 | 9 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 218160
54 | Hobiganj 11MW PP Cofidence-E | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 5 | 5 | 8 | 8 | 8 | 8 | 8 | 0 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 170131
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 50 | 50 | 53 | 53 | 52 | 52 | 53 | 53 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 1262400
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 8 | 0 | 8 | 16 | 16 | 320112
57 | Bibiana-II 341 MW CCPP (Summit) | 285 | 275 | 270 | 270 | 275 | 275 | 280 | 270 | 260 | 270 | 260 | 255 | 270 | 260 | 270 | 270 | 285 | 270 |  | 260 | 260 | 260 | 285 | 270 | 280 | 260 | 6618500
| Bibiyana South 400 MW | 390 | 390 | 400 | 390 | 390 | 390 | 396 | 400 | 385 | 385 | 380 | 372 | 375 | 330 | 350 | 330 | 310 | 300 |  | 273 | 320 | 335 | 385 | 395 | 390 | 400 | 8856400
58 | Nababganj 55 MW PP (Southern power ) | 17 | 17 | 20 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 40 |  | 55 | 55 | 55 | 55 | 35 | 35 | 35 | 886600
59 | Tangail Palli Power Gen 22 MW | 23 | 24 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 24 | 24 | 24 | 24 | 23 | 23 | 24 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 597840
60 | Barabkunda 22 MW PP (Regent) | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 |  | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 324384
61 | Narshingdi 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 375300
62 | Tangail 22 MW PP (Doreen) | 18 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 18 | 15 | 15 | 14 | 12 | 16 | 14 | 12 | 14 | 17 |  | 17 | 18 | 18 | 18 | 18 | 18 | 18 | 381132
63 | Impoprt (Tripura) | 136 | 130 | 128 | 136 | 132 | 122 | 126 | 124 | 120 | 136 | 132 | 132 | 134 | 154 | 134 | 134 | 130 | 134 |  | 146 | 148 | 146 | 152 | 146 | 148 | 136 | 3185280
64 | Malancha, Ctg. EPZ (United) | 26 | 31 | 31 | 37 | 23 | 24 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 7 | 12 | 25 |  | 26 | 29 | 32 | 30 | 24 | 26 | 27 | 382560
65 | Feni 22MW PP (Doreen) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 15 | 17 | 17 | 15 |  |  | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 381636
66 | Feni 11 MW PP (Doreen) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 5 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 211140
67 | Jangalia 33MW PP (Summit) | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 30 | 31 | 31 | 31 | 31 | 30 | 30 | 30 | 30 | 30 |  | 0 | 16 | 33 | 33 | 33 | 33 | 33 | 738900
68 | Cumilla 25 MW PP (Summit) | 15 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 5 | 20 | 20 | 20 | 20 | 20 | 20 | 466280
69 | Summit Ashulia | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 |  | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 552000
70 | Summit Madhabdi | 23 | 23 | 23 | 23 | 19 | 19 | 19 | 19 | 19 | 19 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 24 |  | 15 | 15 | 18 | 18 | 11 | 19 | 19 | 443700
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 760700
72 | Rupganj 33 MW PP(Summit) | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 16 | 16 | 30 | 30 | 28 | 28 | 28 | 28 | 28 | 14 | 28 |  | 28 | 30 | 30 | 16 | 30 | 30 | 30 | 681400
73 | Ghorashal 108MW PP (Regent) | 76 | 76 | 76 | 74 | 74 | 74 | 74 | 68 | 68 | 67 | 70 | 70 | 64 | 66 | 68 | 68 | 68 | 68 |  | 69 | 69 | 69 | 70 | 70 | 72 | 72 | 1666454
| Feni Lanka Power | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 61 | [6 empty] | 20 | 53 | 114 | 114 |  | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 1911780
| Chowmuhani 113 MW | 8 | 3 | 8 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 15 | 9 | 9 | 55 | 55 |  | 113 | 113 | 114 | 115 | 107 | 79 | 30 | 735840
| Manikgonj 162MW PP(MPGL) | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 90 | 90 | 90 | 90 | 108 | 108 | 108 | 108 | 108 |  | 160 | 162 | 162 | 162 | 162 | 162 | 126 | 2322720
77 | Siddhirganj 100 PP(Dutch Bangla) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 62 | 62 | 64 | 64 | 65 | 75 | 77 | 79 |  | 81 | 81 | 82 | 85 | 85 | 85 | 85 | 1515590
78 | Gazipur 52 MW PP | 48 | 48 | 48 | 50 | 50 | 50 | 50 | 42 | 49 | 49 | 42 | 35 | 35 | 37 | 38 | 33 | 45 | 46 |  | 46 | 46 | 46 | 48 | 48 | 48 | 49 | 1083840
79 | Kodda 150 MW PP | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 82 | 82 | 82 | 82 | 80 | 80 | 80 | 80 | 80 | 110 |  | 110 | 110 | 133 | 48 | 48 | 30 | 32 | 1573920
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | [14 empty] | 1 | 8 | 8 | 10 |  | 40 | 52 | 52 | 52 | 52 | 52 | 52 | 326611
| Gazipur 100 MW PP | 105 | 105 | 105 | 105 | 105 | 105 | 89 | 89 | 89 | 89 | 70 | 82 | 89 | 85 | 85 | 85 | 85 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 88 | 2308608
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 0 | 1 | 3 | 4 | 4 | 4 | 4 | 3 | 2 | 1 | 0 | [9 empty] | 27359
| Jodiac Power | 17 | 22 | 36 | 36 | 36 | 36 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 32 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 782602
| Karnaphuli Power Ltd. | 44 | 51 | 51 | 51 | 53 | 54 | 54 | 54 | 54 | 54 | 54 | 72 | 85 | 91 | 102 | 86 | 86 | 86 |  | 86 | 86 | 86 | 86 | 86 | 86 | 59 | 1700319
82 | Madanganj 102 PP(Summit) | 80 | 65 | 70 | 84 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 86 | 85 | 83 | 65 | 58 |  | 62 | 62 | 63 | 63 | 63 | 63 | 51 | 1774265
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP ( Summit) | 297 | 304 | 309 | 305 | 308 | 311 | 309 | 315 | 289 | 307 | 304 | 300 | 285 | 287 | 299 | 290 | 300 | 305 |  | 274 | 277 | 307 | 308 | 269 | 262 | 271 | 7192727
87 | Meghnaghat 100 MW(IEL) | 41 | 41 | 42 | 41 | 41 | 40 | 42 | 39 | 40 | 52 | 59 | 66 | 58 | 56 | 57 | 56 | 63 | 78 |  | 88 | 89 | 90 | 96 | 96 | 94 | 95 | 1460160
| Meghnaghat 104 MW PP (OPCL) | 64 | 53 | 53 | 53 | 61 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 70 | 71 | 71 | 71 | 71 | 74 |  | 89 | 89 | 88 | 89 | 89 | 72 | 72 | 1719360
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 66 | 66 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1486440
92 | Fenchuganj 44MW (Energyprima) | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 47 | 43 | 42 | 44 | 41 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 46 | 47 | 47 | 44 | 1088208
93 | Ashuganj 51 MW PP (Midland) | 51 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 43 | 1031044
94 | Gagnagar 102 MW PP (Digital Power) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 42 | 50 | 64 | 74 | 82 | 82 | 82 | 82 | 82 |  | 82 | 83 | 82 | 82 | 82 | 50 | 50 | 1513152
95 | Patenga 50MW PP (Baraka) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 |  | 7 | 25 | 26 | 26 | 25 | 25 | 25 | 26 | 38 |  | 39 | 39 | 39 | 39 | 39 | 39 | 6 | 489120
96 | Chattogram 108 MW PP (ECPV) | 8 | 8 | 12 | 12 | 8 | 6 | 6 | 9 | 7 | 6 | 11 | 7 | 16 | 55 | 92 | 100 | 108 | 107 |  | 108 | 108 | 108 | 108 | 108 | 108 | 0 | 1172160
97 | katpotti 52 MW
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 55 | 50 | 55 | 55 | 15 | 15 | 491917
100 | Manikganj 55 MW PP (Northern) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 55 | 55 | 55 | 35 | 35 | 889022
101 | Kushiara 163 MW CCPP (KP) | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 80 |  | 5 | 112 | 112 | 112 | 112 | 112 | [10 empty] | 1556263
102 | Sarishabari 3 MW Solar Plant |  |  |  |  | 0 | 0 | 0 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 1 | 1 | 0 | 0 | [8 empty] | 13750
103 | Kamalaghat 54 MW PP(Banco Energy) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 17 | 665640
104 | Keranigonj 300 MW PP (APR) | 290 | 298 | 300 | 300 | 240 | 155 | 104 |  |  | 155 | 210 | 250 | 293 | 250 | 146 | 0 |  |  |  | 145 | 15 | 65 | 290 | 260 | 302 | 268 | 4381510
105 | Bramhangoan 100 MW PP (Aggreko) | 49 | 49 | 48 | 46 | 48 | 25 | 25 |  |  | 50 | 50 | 50 | 50 | 50 | 50 | 0 |  |  |  | 60 | 25 | 60 | 65 | 68 | 48 | 48 | 932843
106 | Mymensingh 200 MW PP (United) | 48 | 48 | 67 | 67 | 67 | 48 | 48 | 48 | 48 | 71 | 119 | 143 | 156 | 149 | 149 | 114 | 115 | 162 |  | 172 | 173 | 173 | 174 | 174 | 174 | 174 | 2656800
112 | Aurahati 100MW PP (Aggreko) | 51 | 50 | 50 | 50 | 51 | 25 | 25 |  |  | 25 | 50 | 50 | 50 | 51 | 50 | 0 |  |  |  | 56 | 27 | 53 | 53 | 53 | 50 | 23 | 884853
114 | Kodda 149 MW PP Unit-1 (Summit) | 34 | 34 | 41 | 119 | 132 | 47 | 34 | 34 | 34 | 34 | 75 | 132 | 63 | 35 | 31 | 33 | 34 | 105 |  | 130 | 144 | 137 | 131 | 131 | 70 | 33 | 1707120
115 | Juldah 100 MW PP Unit-3 (Acorn) | 63 | 63 | 63 | 63 | 50 | 50 | 50 | 50 | 50 | 50 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 75 |  | 100 | 100 | 100 | 100 | 100 | 100 | 88 | 1682880
116 | Chandpur 200MW (Desh energy) | 192 | 192 | 192 | 192 | 184 | 175 | 175 | 174 | 174 | 175 | 175 | 180 | 178 | 192 | 192 | 192 | 192 | 192 |  | 192 | 192 | 193 | 182 | 175 | 174 | 191 | 4439520
117 | Ashuganj 150MW PP (Midland) | 18 | 20 | 18 | 20 | 20 | 18 | 20 | 42 | 45 | 36 | 36 | 42 | 48 | 51 | 60 | 68 | 80 | 87 |  | 101 | 120 | 117 | 133 | 150 | 150 | 150 | 1553963
118 | Bibiyana-III 400 MW CCPP | 397 | 379 | 340 | 397 | 393 | 345 | 363 | 344 | 335 | 341 | 343 | 375 | 355 | 392 | 372 | 372 | 369 | 369 |  | 402 | 405 | 380 | 402 | 403 | 400 | 402 | 8948000
| Jamalpur 115 MW PP (United) | 48 | 48 | 58 | 59 | 59 | 49 | 49 | 49 | 57 | 64 | 96 | 96 | 94 | 93 | 92 | 46 | 46 | 80 |  | 103 | 103 | 103 | 104 | 104 | 96 | 97 | 1764000
| Anwara 300 MW PP (United) | 87 | 88 | 88 | 88 | 87 | 87 | 87 | 87 | 87 | 87 | 121 | 122 | 122 | 123 | 123 | 123 | 123 | 123 |  | 224 | 224 | 227 | 228 | 228 | 212 | 87 | 3005891
| Juldah unit-2 (Acorn) | 50 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 63 | 63 | 63 | 63 | 62 | 63 | 63 | 90 |  | 85 | 90 | 90 | 90 | 90 | 76 | 90 | 1430400
| Anlima Energy Ltd. | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 |  | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 2581855
| Bhairob 54.5 MW | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 0 | 15 | 35 | 35 | 35 | 35 | 857160
| Spectra Solar Plant Ltd. |  |  |  |  | 0 | 0 | 5 | 12 | 19 | 24 | 28 | 29 | 28 | 24 | 19 | 12 | 5 | 1 | [8 empty] | 204094
| Chandpur 115(Doreen) | 58 | 35 | 36 | 36 | 36 | 35 | 35 | 36 | 36 | 57 | 74 | 75 | 60 | 70 | 74 | 73 | 74 | 74 |  | 73 | 73 | 77 | 93 | 93 | 93 | 94 | 1510080
| Kanchan Purbachal Power Generation Ltd. | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 34 | 34 | 33 | 34 | 37 | 50 | 51 |  | 52 | 52 | 53 | 54 | 54 | 52 | 35 | 980280
| Mirsharai 150 MW (Oil) | [10 empty] | 34 | 145 | 163 | 163 | 145 | 144 | 150 | 23 |  |  | 0 | 36 | 36 | 36 | 0 |  | 1073890
Mirsharai 150 MW (Gas)
120 | Eastern Zone Total | 7818 | 7682 | 7739 | 7862 | 7769 | 7402 | 7289 | 6992 | 6884 | 7361 | 7763 | 8399 | 8310 | 8287 | 8189 | 7866 | 7971 | 8300 |  | 9140 | 8999 | 9236 | 9661 | 9522 | 9330 | 8697 | 195017350
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | 81 | 81 | 81 | 81 | 81 | 80 | 80 | 65 | 65 | 64 | 64 | 72 | 77 | 77 | 76 | 75 | 86 | 92 |  | 97 | 96 | 97 | 98 | 98 | 98 | 98 | 1913280
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL) | [13 empty] | 175 | 175 | 175 | 175 | 175 |  | 175 | 175 | 175 | 175 | 175 | 0 |  | 1565923
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 30 | 30 | 30 | 30 | 30 | 26 | 20 | 20 | 16 | 16 | 16 | 19 | 16 | 17 | 17 | 17 | 17 | 22 |  | 17 | 21 | 31 | 27 | 25 | 25 | 20 | 488160
| Khulna 225 MW CCPP | [21 empty] | 160 | 158 | 160 | 100 | 0 | 565539
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 |  | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 864480
130 | Mongla Orion 100 MW Solar PP |  |  |  |  | 0 | 1 | 14 | 33 | 59 | 77 | 86 | 90 | 87 | 76 | 60 | 38 | 16 | 2 |  | 0 | [6 empty] | 641520
131 | Rampal 1320 MW (BIFPCL)
132 | United Payra Power Ltd. | 150 | 150 | 137 | 137 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 20 | 137 |  | 137 | 137 | 150 | 150 | 150 | 150 | 150 | 1836000
133 | Bhola Nutan Biddut BD LTD (GAS)
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 48 | 110 | 110 | 16 | 16 | 604320
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 160 | 160 | 169 | 169 | 169 | 169 | 169 | 169 | 168 | 167 | 167 | 166 | 165 | 160 | 160 | 160 | 160 | 160 |  | 168 | 168 | 169 | 169 | 169 | 168 | 161 | 4003120
140 | Bhola 33 MW PP (Venture) | 36 | 36 | 35 | 36 | 33 | 30 | 26 | 24 | 23 | 23 | 23 | 25 | 27 | 28 | 29 | 28 | 28 | 27 |  | 34 | 34 | 35 | 36 | 36 | 37 | 37 | 732454
141 | Noapara 100 MW PP (Bangla Trac) | [9 empty] | 0 | [16 empty] | 0
142 | Noapara 40 MW PP (Khanjahan Ali) | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 32 | 32 | 32 | 32 | 32 | 24 | 24 | 24 |  | 32 | 40 | 32 | 32 | 32 | 32 | 32 | 822000
143 | Gopalganj 100 MW Peaking PP | 43 | 43 | 43 | 44 | 44 | 44 | 45 | 45 | 38 | 38 | 35 | 35 | 38 | 38 | 35 | 40 | 51 | 52 |  | 60 | 64 | 70 | 73 | 66 | 66 | 66 | 1110016
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 30 | [6 empty] | 45 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 1816128
146 | Bheramara HVDC | 663 | 740 | 827 | 924 | 924 | 924 | 924 | 924 | 924 | 924 | 924 | 924 | 924 | 924 | 924 | 924 | 924 | 924 |  | 890 | 853 | 853 | 854 | 852 | 824 | 824 | 21325818
147 | Bheramara 410 MW CCPP | 210 | 210 | 215 | 210 | 210 | 215 | 210 | 215 | 200 | 200 | 195 | 195 | 200 | 205 | 215 | 220 | 225 | 225 |  | 220 | 230 | 230 | 230 | 230 | 235 | 235 | 5332608
148 | Payra 1320 MW | 1244 | 1244 | 1244 | 1244 | 1244 | 1244 | 1244 | 1244 | 1244 | 1244 | 1244 | 1244 | 1244 | 1244 | 1244 | 1244 | 1244 | 1202 |  | 1212 | 1244 | 1244 | 1244 | 1244 | 1244 | 1244 | 31606200
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 176 | 200 | 204 | 230 | 230 | 240 | 240 | 240 | 240 |  | 240 | 250 | 250 | 250 | 250 | 250 | 250 | 5104000
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 28 | 28 | 28 | 28 | 24 | 28 | 28 | 28 | 28 |  | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 666608
| Sirajgonj 6.55 MW Solar |  |  |  |  | 0 | 0 | 0 | 1 | 3 | 4 | 4 | 4 | 4 | 4 | 3 | 2 | 0 | 0 | [8 empty] | 34680
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 182 | 182 | 181 | 180 | 181 | 183 | 184 | 184 | 182 | 180 | 177 | 177 | 178 | 178 | 178 | 178 | 177 | 189 |  | 192 | 192 | 193 | 197 | 198 | 198 | 197 | 4654918
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | [14 empty] | 2 | 3 | 2 | 8 |  | 23 | 28 | 35 | 72 | 84 | 98 | 117 | 521782
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 414 | 414 | 423 | 414 | 420 | 421 | 423 | 415 | 376 | 414 | 414 | 414 | 414 | 414 | 414 | 414 | 414 | 414 |  | 414 | 414 | 414 | 414 | 415 | 415 | 308 | 9785455
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | 25 | 30 | 40 | 38 | 38 | 0 | [5 empty] | 4 | 6 | 23 | 28 | 28 | 28 | 35 |  | 35 | 35 | 39 | 40 | 40 | 40 | 40 | 455679
162 | Bogra 22 MW PP (GBB) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 20 | 19 | 19 | 18 | 15 | 14 | 14 | 11 | 12 | 13 | 17 |  | 18 | 18 | 20 | 20 | 20 | 20 | 20 | 403440
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  |  | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 160254
165 | Amnura 50 MW PP(Sinha) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 18 | 21 | 21 | 21 | 21 | 490420
166 | Katakhali 50 MW PP (Northern) | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 25 | 25 | 25 | 25 | 34 | 34 | 34 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 782851
167 | Katakhali 50 MW Peaking PP | 32 | 32 | 32 | 24 | 24 | 24 | 24 | 24 | 24 | 35 | 40 | 40 | 32 | 32 | 40 | 40 | 40 | 38 |  | 38 | 40 | 40 | 40 | 40 | 40 | 40 | 692170
168 | Santahar 50 MW Peaking PP | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 27 | 27 | 35 | 35 | 35 | 35 | 35 | 34 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 779050
169 | Natore 52 MW PP (Rajlanka) | [17 empty] | 8 |  | 8 | 8 | 43 | 43 | 43 | 8 | 0 | 129782
170 | Chapainawabganj 100 MW Peaking PP | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 73 | 74 | 74 | 74 | 83 | 68 | 60 | 38 | 38 | 38 | 38 |  | 60 | 70 | 74 | 71 | 78 | 73 | 73 | 16249668
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 35 | 35 | 58 | 95 | 95 | 50 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 78 | 95 | 95 | 95 |  | 95 | 95 | 95 | 95 | 95 | 95 | 50 | 1589472
172 | Confidence Power Bogura Unit-1 113 MW | 35 | 35 | 94 | 95 | 95 | 55 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 90 | 95 | 95 | 95 |  | 95 | 95 | 95 | 95 | 95 | 95 | 50 | 1569696
173 | Rangpur 20 MW GTPP | 15 | 15 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 17 | 17 | 15 | 15 | 15 | 134000
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 34 | 34 | 90 | 92 | 92 | 49 | 34 | 34 | 34 | 35 | 35 | 35 | 35 | 39 | 60 | 90 | 94 | 95 |  | 96 | 92 | 92 | 93 | 92 | 92 | 49 | 1503292
177 | Sympa Solar Power 8MW | [6 empty] | 1 | 2 | 3 | 5 | 5 | 5 | 7 | 7 | 5 | 3 | 1 | 0 | [8 empty] | 43093
178 | Energypac Power Venture Thakurgaon Ltd. | [17 empty] | 35 |  | 36 | 73 | 74 | 112 | 114 | 53 | 0 | 419328
| Intraco Solar 30 MW |  |  |  |  | 0 | 0 | 5 | 11 | 19 | 26 | 29 | 30 | 28 | 26 | 21 | 13 | 6 | 1 | [8 empty] | 216488
| Adani Power Jharkhanda Ltd | 751 | 753 | 756 | 754 | 754 | 750 | 750 | 748 | 759 | 759 | 764 | 756 | 751 | 753 | 754 | 755 | 753 | 754 |  | 754 | 750 | 753 | 753 | 753 | 753 | 764 | 18092727
178 | Teesta Solar Limited |  |  |  |  | 0 | 0 | 30 | 68 | 111 | 145 | 165 | 176 | 167 | 149 | 110 | 68 | 32 | 5 | [8 empty] | 1233340