## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2023-04-19 | Wednesday
|  | Date (day): | 2023-04-19 |  | Wednesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 14221.6 | MW |  |  | (b) At Evening Peak Hour : |  | 15948 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2023-04-18 | 2023-04-19 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 120 | 120 | 120 | 120 | 245 |  | ST under Main. & Gas shortage
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 66 | 74 | 75 | 76 | 32 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 396 | 394 | 400 | 400
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 334 | 330 | 340 | 330 | 30 |  | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 88 | 89 | 80 | 92 |  | 8 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 305 | 325 | 300 | 300 | 35 |  | FGMO
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 92 | 95 | 90 | 95 |  | 7 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 14 | 55 | 15 | 55 |  |  | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 0 | 19 | 19
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 62 | 35 | 64 | 64 | 146 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 72 | 80 | 90 | 90 |  | 10 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 214 | 216 | 216 | 216 | 119 |  | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 58 | 91 | 64 | 92 |  | 10 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 54 | 17 | 54
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 32 | 146 | 32 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 35 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 35 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 41 | 46 | 46 | 46 |  | 34 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 30 | 30 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 12 | 32 | 32 | 32 |  | 1
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 41 | 48 | 48 | 48
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 264 | 270 | 300 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 280 | 295 | 300 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 50 | 70 | 50 | 70 |  | 30 | Engine problem
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 75 | 0 | 75 | 25 |  | Fuel shortage
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 119 | 148 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 88 | 105 | 88 | 105
37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 53 | 88 | 54 | 90 |  | 14 | Engine problem
38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 108 | 162 | 108 | 162
39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 30 | 0 | 30 | 0
40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 35 | 54 | 35 | 54
| Dhaka area Total |  |  |  |  | 6263 | 5847 | 3740 | 4267 | 3895 | 4356 | 863 | 614
41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 90 | 110 | 110 | 110 | 70 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 17 | 25 | 25 | 25
43 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 19 | 0 | 20 | 0
44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 25 | 39 | 26 | 40 | 10 |  | Fuel shortage
45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 25 | 25 | 25 | 25 | 205 |  | Low Water Level
46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 225 | 226 | 225 | 225
47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 68 | 105 | 51 | 105
49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 36 | 63 | 48 | 60 |  | 38 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 49 | 66 | 66 | 66 |  | 36 | Engine problem
51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 66 | 77 | 55 | 77 | 23 |  | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 50 | 100 | 50 | 100
53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 14 | 14 | 14 | 14 | 8 |  | Gas shortage
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 15 | 5 | 15
54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 52 | 0 | 52 | 56 |  | DCT & Fuel shortage
55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 122 | 228 | 120 | 230 | 70 |  | Fuel shortge
57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 17 | 54 | 17 | 54
58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 68 | 107 | 68 | 105 |  | 5 | Engine problem
59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 63 | 88 | 63 | 90 | 10 |  | Fuel shortage
60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 107 | 107 | 107 | 107 |  | 9 | Engine problem
| Mirsharai 150 MW |  | Gas/HSD | BPDB-RPCL | 18.5*9 | 0 | 0 | 134 | 54 | 0 | 0
| Chattogram area Total |  |  |  |  | 2442 | 2382 | 1201 | 1555 | 1100 | 1500 | 632 | 238
61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 206 | 204 | 200 | 210 |  |  | FGMO
63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 | 360 |  | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 305 | 350 | 350 | 350 |  |  | FGMO
65 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Under maint.
66 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 36 | 41 | 41 | 41
67 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 55 | 0 | 0 | 0 | 0 |  |  | Contract Expired
68 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 167 | 155 | 155 | 155 | 40 |  | Gas shortage
69 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 43 | 51 | 51
70 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 50 | 147 | 53 | 150
71 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 35 | 44 | 40 | 44 |  | 8 | Engine problem
72 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under Maint.
73 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 193 | 192 | 195 | 195 |  | 5
74 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 18 | 18 | 18 |  | 4 | Engine problem
75 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 7 | 9 | 9 |  | 2 | Engine problem
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 140 | 136 | 135 | 153
76 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 32 | 32 | 33 | 33
77 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 52 | 0 | 52
78 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 20 | 20 |  | 5 | Engine problem
79 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 115 | 129 | 130 | 130 | 70 |  | Fuel shortage
80 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 114 | 0 | 114
81 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 109 | 9 | 113
82 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 35 | 6 | 35 | 35 |  | 19 | Engine problem
83 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 62 | 93 | 62 | 92 | 23 |  | Fuel shortage
| Cumilla Area Total |  |  |  |  | 3159 | 3151 | 1473 | 1892 | 1536 | 1965 | 493 | 606
84 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 16 | 94 | 33 | 90 | 112 |  | Gas shortage
85 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 15 | 15 | 18 | 18 | 4 |  | Gas shortage
86 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0
87 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
88 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 125 | 164 | 140 | 165 | 35 |  | Fuel shortage
89 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 68 | 97 | 100 | 100 | 15 |  | Fuel shortage
90 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 41 | 0 | 50 | 0
91 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 24 | 25 | 25 | 25
| Mymensingh Area Total |  |  |  |  | 717 | 614 | 291 | 395 | 367.6 | 398 | 116 | 0
92 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 34 | 32 | 33 | 33 |  | 37 | Machine problem.
93 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 40 | 40 | 41 | 41 |  | 49 | Machine problem
94 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 112 | 112 | 112 |  | 51 | ST Under maint
95 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
96 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 48 | 53 | 50 | 51
97 | Fenchuganj 44MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 43 | 45 | 44 | 49
98 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 8 | 8 |  | 3 | Engine problem
99 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 60 | 60 | 60 | 60
100 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 83 | 83 | 84 | 85
101 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
102 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 199 | 200 | 200 | 200 |  | 31 | Machine problem
103 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 17 | 17 | 17 | 17
104 | Sylhet 50MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
105 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 16 | 16 | 16 | 9 |  | Gas shortage
106 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 275 | 275 | 280 | 290 |  |  | FGMO
107 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 367 | 403 | 400 | 400
108 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
109 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 395 | 393 | 400 | 400
| Sylhet Area Total |  |  |  |  | 2472 | 2427 | 1595 | 1747 | 1755 | 1772 | 9 | 601
110 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 925 | 850 | 943 | 943
111 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 77 | 85 | 85 | 98 |  | 17 | Engine problem
112 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 17 | 24 | 22 | 35 |  | 19 | Engine problem
113 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 160 | 0 | 0 | 230 |  | Fuel shortage
114 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 48 | 72 | 66 | 72 |  | 37 | Engine problem
115 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 200 | 190 | 210 | 210 | 200 |  | Gas shortage
116 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 24 | 32 | 40 | 40
117 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Fuel shortage
118 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 36 | 55 | 55 | 55 | 50 |  | Fuel shortage
119 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 0
120 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 85 | 0 | 100 | 0
| Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 0 | 0 | 0 | 175 | 0 | 0 |  |  | On test.
| Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 660*2 | 617 | 617 | 0 | 0 | 335 | 335
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3005 | 3001 | 1412 | 1643 | 1856 | 1788 | 596 | 73
121 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 16 | 110 | 16 | 110
122 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 25 | 35 | 25 | 35
123 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 168 | 170 | 170 | 170 | 24 |  | Gas shortage
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
124 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 1244 | 1244 | 1244 | 1244
125 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 0 | 0 | 0 | 0 |  | 220 | Under maintenance
126 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 150 | 17 | 150
127 | Barisal 307 MW |  | Coal | BCPCL | 307*1 | 307 | 307 | 0 | 0 | 0 | 0 | 307 |  | Coal Shortage.
| Barisal Area Total |  |  |  |  | 2265 | 2265 | 1470 | 1709 | 1472 | 1709 | 331 | 220
128 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
129 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 28 | 20 | 27 | 27 |  | 25 | Engine problem
130 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 4 | 28 | 0 | 32 |  | 39 | Engine problem
131 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 21 | 21 | 21 | 21
132 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 34 | 42 | 42 | 42 |  | 8 | Engine problem
133 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 40 | 42 | 40 | 42 |  | 8 | Engine problem
134 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 173 | 159 | 160 | 160 | 50 |  | Gas shortage
135 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
136 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 176 | 168 | 180 | 180 | 40 |  | Gas shortage
137 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 414 | 414 | 414 | 414
138 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 34 | 31 | 35 | 35 |  | 15 | Engine problem
139 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 16 | 19 | 22 | 22
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
140 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 8 | 8 |  | 3 | Engine problem
141 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 43 | 0 | 43 | 9 |  | Fuel shortage
142 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 69 | 80 | 80 | 80 |  | 14 | Enginr problem
143 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel shortage
144 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 35 | 95 | 35 | 95 | 18 |  | Fuel shortage
145 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 35 | 95 | 35 | 95 | 18 |  | Fuel shortage
146 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
| Adani Power Jharkhanda Ltd |  | Coal | Import | 0 | 0 | 0 | 585 | 750 | 755 | 755 |  |  | On test.
| Rajshahi Area Total |  |  |  |  | 2179 | 2129 | 1677 | 2015 | 1860 | 2051 | 726 | 112
147 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
148 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 200 | 200 | 170 | 200 | 74 |  | Coal Shortage.
149 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
150 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
151 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 42 | 92 | 42 | 95 | 18 |  | Fuel shortage
152 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 6 | 0 | 8 | 0
153 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 0 | 111 | 0 | 114
154 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 30 | 0 | 30 | 0
| Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 0 | 0 | 170 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 830 | 750 | 448 | 403 | 380 | 409 | 217 | 85
| Total |  |  |  |  | 23332 | 22566 | 13307 | 15626 | 14221.6 | 15948 | 3983 | 2549
A. |  | 2023-04-18 | (Yesterday) |  |  |  |  | Tuesday
1 | Highest Generation : |  |  | 15626 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 11656 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 16131 | MW
3 | Day peak Generation : |  |  | 13307 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 15384.62 | MW
4 | Evening peak Generation : |  |  | 15626 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 482 | MW
5 | Total Energy Generation : |  | 337.8275 | MKWHr | By Solar | 2.5134 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Gas : | 150.8018 | MKWHr |  | By Oil: | 105.7905 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 53.4862 | MKWHr |  | By Hydro: | 0.30708 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 3983 | MW | Dhaka | 5265.7 | 5265.7 |  | 0 |  | 18:00 |  | 486.095
|  |  | For Plants S/D or M/C prob = |  |  | 2549 | MW | Chittagong | 1428.56 | 1428.56 |  | 0 |  | 19:00 |  | 537.665
|  |  | Total = |  |  | 6532 | MW | Khulna | 1986.2 | 1986.2 |  | 0 |  | 19:30 |  | 456.49
7 | Total Gas Supplied : |  |  | 1174.57 | MMCFD |  |  | Rajshahi | 1802.6 | 1777.6 |  | 25 |  | 20:00 |  | 473.68
8 | Fuel Cost : | i) Gas : | Taka | 172690021.71 | ii) Oil : | Taka | 1436626785.19 | Comilla | 1568 | 1541 |  | 27 |  | 21:00 |  | 482.275
|  | iii) Coal : | Taka | 311027386 | Total | Taka | 1920344192.9 | Mymensingh | 1231 | 1031 |  | 200 |  | 22:00 |  | 436.435
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0 | MKWHr. | Sylhet | 599 | 519 |  | 80 |  | 23:00 |  | 1028.535
| ii) During Peak Demand : |  |  | 240 | MW (E to W) at | 21:00 | hrs | Barisal | 488.56 | 488.56 |  | 0 |  | 24:00 |  | 1653.105
| iii) Maximum : |  |  | 150 | MW at | 20:00 | hrs | Rangpur | 1015 | 865 |  | 150
10 | Maximum Temperature in Dhaka was |  |  |  | 37.1° C |  |  | Total | 15384.62 | 14902.62 |  | 482
B. |  | 2023-04-19 | (Today) |  |  |  | Wednesday |  |  | Probable max. temperature in Dhaka |  |  | 42.6° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 15500 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 15948 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 13700 | MW
4 | Reserve(Generation end) |  |  |  | 448 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 335.1035 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 12354 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.6742 | MKWHr. | ii) HVDC Flow at Peak Time |  | 850 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.2544 | MKWHr. | iii) Maximum HVDC Flow : |  | 926 | MW at | 5:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 75.89 |  | (b) Today: | 75.77 |  | (c) Rule Curve: |  | 84.4
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2023-04-18 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 120 | 72 | 0 | 397 | 330 |  | 0 | 450 | 307 | 60 | 51 | 15 | 218 | 0 | 65 | 55 | 50 | 32 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 19 | 23 | 19 | 33 | 31 | 49 | 0 | 0 | 0 | 90 | 0 | 18 | 228 | 0 | 0 | 0 |  | 23 | 42 | 67 | 70 | 0 | 6 | 14 | 17 | 0 | 0 | 0 | 0 | 345 | 186 | 184 | 0 | 44 | 0 | 0 | 51 | 0 | 37 | 52 | 18 | 9 | 33 | 15 | 136 | 93 | 0 | 19 | 0 | 34 | 40 | 53 | 47 | 0 | 0 | 60 | 85 | 0 | 205 | 17 | 0 | 10 | 260 | 16 | 8 | 129 | 158 | 301 | 48 | 47 | 0 | 33 | 0 | 50 | 193 | 150 | 390 | 49 | 105 | 17 | 0 | 88 | 17 | 59 | 114 | 9 | 50 | 390 | 72 | 0 | 54 | 107 | 0 | 35 | 0 | 81 | 35 | 0 | 0 | 0 |  | 853 | 0 | 235 | 0 | 98 | 0 | 0 | 0 | 15 | 66 | 32 | 169 | 36 | 16 | 0 | 0 | 0 | 28 | 40 | 77 | 21 | 42 | 32 | 0 | 35 | 20 | 0 | 8 | 0 | 0 | 250 | 0 | 0 | 197 | 0 | 0 | 0 | 0 | 0 | 136 | 0 | 414 | 36 | 0 | 35 | 105 | 34 | 0 | 0 | 35 | 1244 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 761 | 0 | 0 |  | 8058 | 5220 | 13278 | 4104 | 853 | 2336 | 478 | 2645 | 2255 | 0 | 0 | 471 | 136 | 0 | 1644.51 | 75.9
2:00 | 0 | 0 | 0 | 180 | 120 | 72 | 0 | 398 | 330 |  | 0 | 450 | 304 | 41 | 51 | 15 | 217 | 0 | 65 | 50 | 50 | 32 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 19 | 23 | 11 | 33 | 32 | 49 | 0 | 0 | 0 | 90 | 0 | 25 | 223 | 0 | 0 | 0 |  | 25 | 42 | 67 | 70 | 0 | 6 | 14 | 34 | 0 | 0 | 0 | 0 | 335 | 178 | 184 | 0 | 44 | 0 | 0 | 51 | 0 | 39 | 52 | 18 | 9 | 33 | 20 | 134 | 93 | 0 | 19 | 0 | 34 | 40 | 53 | 48 | 0 | 0 | 61 | 85 | 0 | 204 | 17 | 0 | 10 | 270 | 16 | 8 | 127 | 91 | 299 | 48 | 47 | 0 | 52 | 0 | 50 | 192 | 150 | 403 | 49 | 105 | 17 | 0 | 88 | 17 | 54 | 114 | 9 | 38 | 390 | 54 | 0 | 54 | 107 | 0 | 35 | 0 | 63 | 35 | 0 | 0 | 0 |  | 853 | 0 | 230 | 0 | 82 | 0 | 0 | 0 | 15 | 66 | 32 | 169 | 35 | 16 | 0 | 0 | 0 | 28 | 10 | 77 | 21 | 42 | 32 | 0 | 35 | 20 | 0 | 8 | 0 | 0 | 240 | 0 | 0 | 195 | 0 | 0 | 0 | 0 | 0 | 156 | 0 | 414 | 36 | 0 | 35 | 105 | 34 | 0 | 0 | 35 | 1244 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 762 | 0 | 0 |  | 7950 | 5177 | 13127 | 4105 | 853 | 2360 | 474 | 2512 | 2246 | 0 | 0 | 443 | 134 | 0 | 1502.215 | 75.9
3:00 | 0 | 0 | 0 | 180 | 120 | 72 | 0 | 398 | 330 |  | 0 | 450 | 311 | 42 | 51 | 15 | 218 | 0 | 65 | 50 | 50 | 32 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 19 | 23 | 19 | 33 | 32 | 49 | 0 | 0 | 0 | 90 | 0 | 25 | 224 | 0 | 0 | 0 |  | 25 | 42 | 67 | 70 | 0 | 6 | 14 | 35 | 0 | 0 | 0 | 0 | 350 | 176 | 184 | 0 | 43 | 0 | 0 | 51 | 0 | 39 | 52 | 0 | 0 | 33 | 20 | 132 | 94 | 0 | 19 | 0 | 34 | 40 | 53 | 48 | 0 | 0 | 61 | 85 | 0 | 202 | 17 | 0 | 10 | 275 | 16 | 8 | 126 | 97 | 300 | 48 | 57 | 0 | 121 | 0 | 38 | 193 | 150 | 395 | 69 | 105 | 17 | 0 | 88 | 23 | 61 | 114 | 9 | 38 | 400 | 54 | 0 | 54 | 107 | 0 | 35 | 0 | 35 | 35 | 0 | 0 | 0 |  | 854 | 0 | 230 | 0 | 98 | 0 | 0 | 0 | 15 | 66 | 32 | 169 | 35 | 16 | 0 | 0 | 0 | 28 | 12 | 77 | 21 | 42 | 24 | 0 | 35 | 21 | 0 | 8 | 0 | 0 | 240 | 0 | 0 | 193 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 418 | 36 | 0 | 57 | 105 | 92 | 0 | 0 | 90 | 1244 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 760 | 0 | 0 |  | 8037 | 5335 | 13372 | 4110 | 854 | 2378 | 474 | 2743 | 2244 | 0 | 0 | 437 | 132 | 0 | 1554.74 | 75.9
4:00 | 0 | 0 | 0 | 180 | 120 | 72 | 0 | 397 | 330 |  | 0 | 450 | 305 | 42 | 60 | 15 | 218 | 0 | 65 | 50 | 50 | 32 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 23 | 19 | 33 | 32 | 49 | 0 | 0 | 0 | 90 | 0 | 23 | 224 | 0 | 0 | 0 |  | 25 | 42 | 67 | 70 | 0 | 6 | 14 | 36 | 0 | 0 | 0 | 0 | 335 | 173 | 184 | 0 | 43 | 0 | 0 | 51 | 0 | 38 | 0 | 0 | 0 | 33 | 20 | 136 | 82 | 0 | 19 | 0 | 34 | 40 | 53 | 48 | 0 | 0 | 60 | 85 | 0 | 202 | 17 | 0 | 10 | 265 | 16 | 8 | 125 | 97 | 300 | 48 | 57 | 0 | 131 | 0 | 38 | 193 | 63 | 403 | 68 | 105 | 17 | 0 | 88 | 36 | 54 | 114 | 9 | 38 | 390 | 54 | 0 | 54 | 107 | 0 | 35 | 0 | 36 | 35 | 0 | 0 | 0 |  | 925 | 0 | 230 | 0 | 98 | 0 | 0 | 0 | 15 | 66 | 32 | 169 | 35 | 16 | 0 | 0 | 0 | 28 | 12 | 78 | 21 | 42 | 24 | 0 | 35 | 21 | 0 | 8 | 0 | 0 | 240 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 171 | 0 | 414 | 36 | 0 | 94 | 0 | 93 | 0 | 0 | 95 | 1244 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 755 | 0 | 0 |  | 7892 | 5337 | 13229 | 4077 | 925 | 2359 | 473 | 2583 | 2239 | 0 | 0 | 437 | 136 | 0 | 1500.305 | 75.89
5:00 | 0 | 0 | 0 | 180 | 120 | 72 | 0 | 398 | 330 |  | 0 | 450 | 310 | 41 | 70 | 15 | 220 | 0 | 64 | 50 | 50 | 32 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 23 | 19 | 33 | 32 | 49 | 0 | 0 | 0 | 90 | 0 | 25 | 228 | 0 | 0 | 0 |  | 25 | 42 | 67 | 67 | 0 | 6 | 14 | 36 | 0 | 0 | 0 | 0 | 350 | 164 | 184 | 0 | 43 | 0 | 0 | 43 | 0 | 38 | 0 | 0 | 9 | 33 | 15 | 124 | 87 | 0 | 19 | 0 | 34 | 40 | 53 | 48 | 0 | 0 | 60 | 85 | 0 | 202 | 18 | 0 | 10 | 260 | 16 | 8 | 100 | 97 | 240 | 48 | 47 | 0 | 97 | 0 | 38 | 193 | 46 | 401 | 49 | 105 | 17 | 0 | 87 | 36 | 54 | 114 | 9 | 38 | 400 | 54 | 0 | 54 | 107 | 0 | 35 | 0 | 36 | 35 | 0 | 0 | 0 |  | 926 | 0 | 225 | 0 | 97 | 0 | 0 | 0 | 16 | 62 | 32 | 169 | 31 | 16 | 0 | 0 | 0 | 28 | 12 | 78 | 21 | 42 | 24 | 0 | 35 | 21 | 0 | 8 | 0 | 0 | 240 | 0 | 0 | 189 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 417 | 36 | 0 | 95 | 0 | 92 | 0 | 0 | 95 | 1244 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 743 | 0 | 0 |  | 7744 | 5189 | 12933 | 4108 | 926 | 2350 | 388 | 2376 | 2227 | 0 | 0 | 434 | 124 | 0 | 1305.485 | 75.89
6:00 | 0 | 0 | 0 | 180 | 120 | 72 | 0 | 390 | 330 |  | 0 | 400 | 288 | 42 | 88 | 15 | 220 | 0 | 64 | 50 | 50 | 32 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 23 | 19 | 33 | 32 | 49 | 0 | 0 | 0 | 90 | 0 | 25 | 228 | 0 | 0 | 0 |  | 25 | 42 | 67 | 67 | 0 | 6 | 14 | 35 | 0 | 0 | 0 | 0 | 310 | 165 | 184 | 0 | 43 | 0 | 0 | 43 | 0 | 39 | 0 | 0 | 9 | 33 | 15 | 116 | 86 | 0 | 19 | 0 | 34 | 40 | 53 | 47 | 0 | 0 | 62 | 85 | 0 | 202 | 18 | 0 | 10 | 265 | 16 | 8 | 0 | 97 | 0 | 0 | 47 | 0 | 34 | 0 | 38 | 193 | 51 | 401 | 49 | 90 | 17 | 0 | 87 | 36 | 37 | 0 | 9 | 38 | 400 | 54 | 1 | 54 | 94 | 0 | 35 | 0 | 35 | 35 | 0 | 0 | 0 |  | 925 | 0 | 225 | 0 | 98 | 0 | 0 | 0 | 16 | 62 | 0 | 169 | 29 | 16 | 0 | 0 | 0 | 28 | 0 | 78 | 21 | 42 | 24 | 0 | 35 | 21 | 0 | 8 | 0 | 0 | 240 | 0 | 0 | 188 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 300 | 36 | 0 | 50 | 0 | 48 | 0 | 0 | 55 | 1244 | 0 | 0 | 17 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 741 | 0 | 0 |  | 7036 | 4900 | 11936 | 4066 | 925 | 2162 | 0 | 2017 | 2225 | 0 | 0 | 423 | 116 | 2 | 1684.62 | 75.89
7:00 | 0 | 0 | 0 | 180 | 0 | 72 | 0 | 344 | 285 |  | 0 | 370 | 311 | 41 | 95 | 15 | 180 | 0 | 93 | 50 | 50 | 32 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 0 | 23 | 19 | 33 | 32 | 49 | 0 | 0 | 0 | 90 | 0 | 25 | 225 | 0 | 0 | 0 |  | 25 | 42 | 67 | 67 | 0 | 6 | 14 | 10 | 0 | 0 | 0 | 0 | 280 | 193 | 184 | 0 | 43 | 0 | 0 | 51 | 0 | 39 | 0 | 0 | 9 | 33 | 15 | 118 | 33 | 0 | 19 | 0 | 34 | 40 | 53 | 47 | 0 | 0 | 61 | 85 | 0 | 202 | 17 | 0 | 10 | 265 | 16 | 8 | 0 | 97 | 0 | 0 | 47 | 0 | 34 | 0 | 38 | 193 | 51 | 377 | 49 | 88 | 17 | 1 | 88 | 17 | 52 | 0 | 9 | 38 | 370 | 54 | 0 | 54 | 107 | 0 | 35 | 4 | 36 | 35 | 0 | 0 | 0 |  | 926 | 0 | 225 | 0 | 98 | 0 | 0 | 0 | 16 | 62 | 32 | 169 | 26 | 16 | 0 | 0 | 0 | 28 | 0 | 80 | 21 | 42 | 24 | 0 | 35 | 21 | 0 | 8 | 0 | 0 | 240 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 346 | 36 | 0 | 35 | 0 | 34 | 0 | 1 | 35 | 1244 | 0 | 0 | 17 | 0 | 14 | 0 | 0 | 0 | 0 | 4 | 0 | 752 | 21 | 0 |  | 6678 | 4978 | 11656 | 3755 | 926 | 2136 | 0 | 2015 | 2236 | 0 | 0 | 425 | 118 | 45 | 1665.52 | 75.88
8:00 | 0 | 0 | 0 | 180 | 60 | 68 | 0 | 359 | 330 |  | 0 | 450 | 313 | 42 | 95 | 15 | 170 | 0 | 93 | 50 | 50 | 32 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 23 | 19 | 33 | 31 | 49 | 0 | 0 | 0 | 90 | 0 | 25 | 225 | 0 | 0 | 0 |  | 25 | 35 | 67 | 66 | 0 | 6 | 14 | 4 | 0 | 0 | 0 | 0 | 280 | 204 | 184 | 0 | 42 | 0 | 0 | 51 | 0 | 39 | 0 | 0 | 9 | 32 | 9 | 118 | 33 | 0 | 19 | 1 | 34 | 40 | 50 | 44 | 0 | 0 | 61 | 85 | 0 | 202 | 17 | 0 | 10 | 270 | 16 | 8 | 0 | 97 | 0 | 0 | 47 | 0 | 25 | 5 | 38 | 193 | 55 | 402 | 49 | 88 | 17 | 1 | 88 | 17 | 54 | 0 | 9 | 38 | 400 | 54 | 0 | 54 | 107 | 0 | 35 | 11 | 36 | 35 | 0 | 0 | 0 |  | 925 | 0 | 225 | 0 | 98 | 0 | 0 | 0 | 16 | 48 | 32 | 169 | 24 | 16 | 0 | 0 | 0 | 28 | 0 | 80 | 21 | 42 | 24 | 0 | 35 | 21 | 0 | 8 | 0 | 0 | 248 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 416 | 36 | 0 | 35 | 0 | 34 | 0 | 2 | 35 | 1244 | 0 | 0 | 17 | 1 | 33 | 0 | 0 | 0 | 0 | 5 | 0 | 678 | 40 | 0 |  | 6938 | 5006 | 11944 | 3896 | 925 | 2320 | 0 | 2012 | 2170 | 0 | 0 | 404 | 118 | 99 | 1676.98 | 75.88
9:00 | 0 | 0 | 0 | 180 | 120 | 68 | 0 | 395 | 333 |  | 0 | 450 | 305 | 41 | 95 | 15 | 218 | 0 | 95 | 50 | 50 | 32 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 23 | 19 | 33 | 30 | 43 | 0 | 0 | 0 | 90 | 0 | 17 | 223 | 0 | 0 | 0 |  | 25 | 35 | 66 | 66 | 0 | 6 | 14 | 2 | 0 | 0 | 0 | 0 | 320 | 198 | 184 | 0 | 37 | 0 | 0 | 51 | 0 | 39 | 0 | 9 | 9 | 32 | 18 | 128 | 34 | 0 | 19 | 1 | 34 | 40 | 50 | 46 | 0 | 0 | 61 | 85 | 0 | 203 | 17 | 0 | 10 | 260 | 16 | 8 | 0 | 97 | 0 | 0 | 48 | 0 | 34 | 7 | 38 | 193 | 51 | 403 | 49 | 88 | 17 | 3 | 88 | 17 | 54 | 0 | 9 | 38 | 400 | 52 | 21 | 54 | 107 | 0 | 35 | 17 | 36 | 35 | 0 | 0 | 0 |  | 924 | 0 | 220 | 0 | 96 | 0 | 0 | 0 | 19 | 48 | 32 | 167 | 23 | 16 | 0 | 0 | 0 | 28 | 0 | 80 | 21 | 42 | 24 | 0 | 35 | 20 | 0 | 8 | 0 | 0 | 220 | 0 | 0 | 171 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 421 | 36 | 0 | 35 | 0 | 35 | 0 | 3 | 35 | 1244 | 0 | 0 | 17 | 1 | 56 | 0 | 0 | 0 | 0 | 7 | 0 | 549 | 35 | 0 |  | 7145 | 4852 | 11997 | 4067 | 924 | 2308 | 0 | 2000 | 2013 | 0 | 0 | 406 | 128 | 151 | 1721.865 | 75.87
10:00 | 0 | 0 | 0 | 180 | 120 | 68 | 0 | 395 | 334 |  | 0 | 450 | 305 | 61 | 95 | 14 | 214 | 0 | 83 | 50 | 50 | 32 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 23 | 19 | 25 | 30 | 41 | 0 | 0 | 0 | 90 | 0 | 17 | 224 | 0 | 0 | 0 |  | 25 | 44 | 66 | 55 | 0 | 18 | 14 | 2 | 0 | 0 | 0 | 0 | 305 | 199 | 167 | 0 | 39 | 0 | 0 | 51 | 0 | 44 | 0 | 16 | 9 | 32 | 19 | 132 | 21 | 0 | 15 | 2 | 34 | 40 | 50 | 46 | 0 | 0 | 60 | 84 | 0 | 201 | 17 | 0 | 10 | 275 | 16 | 8 | 114 | 95 | 266 | 50 | 48 | 0 | 34 | 12 | 38 | 193 | 53 | 367 | 71 | 88 | 17 | 2 | 88 | 17 | 54 | 0 | 5 | 38 | 395 | 53 | 36 | 90 | 107 | 0 | 35 | 25 | 35 | 35 | 0 | 8 | 0 |  | 924 | 0 | 215 | 0 | 72 | 0 | 0 | 0 | 19 | 48 | 32 | 169 | 23 | 16 | 0 | 0 | 0 | 28 | 0 | 70 | 21 | 42 | 24 | 0 | 33 | 19 | 0 | 8 | 0 | 0 | 220 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 417 | 36 | 0 | 35 | 0 | 35 | 0 | 5 | 35 | 1244 | 0 | 0 | 17 | 3 | 72 | 0 | 0 | 0 | 0 | 22 | 0 | 477 | 106 | 0 |  | 7611 | 4852 | 12463 | 3986 | 924 | 2301 | 430 | 2048 | 1941 | 0 | 8 | 408 | 132 | 285 | 1467.835 | 75.87
11:00 | 0 | 0 | 0 | 180 | 120 | 68 | 0 | 393 | 334 |  | 0 | 450 | 295 | 74 | 92 | 14 | 211 | 0 | 80 | 65 | 50 | 32 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 23 | 18 | 30 | 0 | 41 | 0 | 25 | 0 | 90 | 0 | 17 | 226 | 0 | 0 | 0 |  | 25 | 44 | 49 | 55 | 0 | 25 | 14 | 2 | 0 | 0 | 0 | 0 | 305 | 208 | 167 | 0 | 34 | 0 | 0 | 51 | 0 | 37 | 0 | 17 | 9 | 32 | 20 | 132 | 21 | 0 | 15 | 2 | 34 | 40 | 53 | 43 | 0 | 0 | 61 | 84 | 0 | 201 | 17 | 0 | 10 | 280 | 16 | 8 | 50 | 124 | 120 | 50 | 99 | 0 | 45 | 13 | 62 | 193 | 51 | 367 | 78 | 88 | 51 | 4 | 121 | 17 | 58 | 0 | 12 | 63 | 397 | 53 | 38 | 90 | 107 | 0 | 35 | 29 | 53 | 26 | 0 | 93 | 0 |  | 925 | 0 | 215 | 0 | 71 | 0 | 0 | 0 | 20 | 48 | 24 | 159 | 24 | 16 | 0 | 0 | 0 | 28 | 4 | 69 | 21 | 42 | 27 | 0 | 33 | 18 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 421 | 36 | 0 | 35 | 0 | 36 | 0 | 5 | 35 | 1244 | 0 | 0 | 17 | 4 | 83 | 0 | 0 | 0 | 0 | 20 | 0 | 547 | 134 | 0 |  | 7732 | 4925 | 12657 | 3944 | 925 | 2300 | 220 | 2304 | 1991 | 25 | 93 | 391 | 132 | 332 | 1473.565 | 75.86
12:00 | 0 | 0 | 0 | 180 | 120 | 66 | 0 | 396 | 334 |  | 0 | 450 | 305 | 88 | 92 | 14 | 214 | 0 | 62 | 72 | 58 | 32 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 23 | 18 | 30 | 12 | 41 | 0 | 25 | 0 | 90 | 0 | 17 | 225 | 0 | 0 | 0 |  | 24 | 36 | 49 | 66 | 0 | 25 | 14 | 2 | 0 | 0 | 0 | 0 | 305 | 206 | 167 | 0 | 36 | 0 | 0 | 43 | 0 | 35 | 0 | 17 | 8 | 32 | 20 | 140 | 16 | 0 | 15 | 2 | 34 | 40 | 48 | 43 | 0 | 0 | 60 | 83 | 0 | 199 | 17 | 0 | 10 | 275 | 16 | 8 | 115 | 264 | 280 | 50 | 125 | 0 | 119 | 19 | 50 | 193 | 50 | 367 | 68 | 88 | 68 | 4 | 122 | 17 | 68 | 0 | 9 | 63 | 395 | 53 | 41 | 108 | 107 | 0 | 35 | 30 | 62 | 35 | 0 | 134 | 0 |  | 925 | 0 | 200 | 0 | 77 | 0 | 0 | 0 | 17 | 48 | 24 | 168 | 25 | 16 | 0 | 0 | 0 | 28 | 4 | 69 | 21 | 34 | 40 | 0 | 34 | 16 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 173 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 414 | 36 | 0 | 35 | 0 | 42 | 0 | 6 | 35 | 1244 | 0 | 0 | 17 | 5 | 85 | 0 | 0 | 0 | 0 | 30 | 0 | 585 | 170 | 0 |  | 8300 | 5007 | 13307 | 3919 | 925 | 2281 | 445 | 2625 | 2029 | 25 | 134 | 392 | 140 | 392 | 1043.815 | 75.86
13:00 | 0 | 0 | 0 | 180 | 120 | 71 | 0 | 396 | 321 |  | 0 | 450 | 300 | 90 | 90 | 14 | 212 | 0 | 79 | 72 | 58 | 32 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 0 | 23 | 18 | 30 | 17 | 41 | 0 | 25 | 0 | 90 | 0 | 17 | 225 | 0 | 0 | 0 |  | 24 | 45 | 51 | 64 | 0 | 25 | 14 | 2 | 0 | 0 | 0 | 0 | 305 | 200 | 167 | 0 | 33 | 0 | 0 | 43 | 0 | 35 | 0 | 16 | 8 | 30 | 20 | 136 | 21 | 0 | 15 | 1 | 33 | 40 | 53 | 0 | 0 | 0 | 60 | 82 | 0 | 195 | 17 | 0 | 10 | 275 | 16 | 8 | 126 | 130 | 294 | 50 | 143 | 0 | 72 | 17 | 50 | 193 | 40 | 368 | 78 | 105 | 68 | 4 | 124 | 17 | 68 | 0 | 9 | 63 | 384 | 52 | 36 | 108 | 107 | 0 | 35 | 28 | 89 | 33 | 0 | 145 | 0 |  | 925 | 0 | 200 | 0 | 81 | 0 | 0 | 0 | 11 | 25 | 24 | 168 | 27 | 16 | 0 | 0 | 0 | 28 | 20 | 67 | 21 | 34 | 40 | 0 | 34 | 14 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 169 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 414 | 36 | 0 | 35 | 0 | 42 | 0 | 6 | 35 | 1232 | 0 | 0 | 17 | 4 | 82 | 0 | 150 | 0 | 0 | 26 | 0 | 614 | 162 | 0 |  | 8138 | 5141 | 13279 | 3892 | 925 | 2229 | 470 | 2507 | 2046 | 25 | 295 | 388 | 136 | 366 | 1118.305 | 75.85
14:00 | 0 | 0 | 0 | 180 | 120 | 71 | 0 | 396 | 321 |  | 0 | 450 | 290 | 89 | 90 | 14 | 209 | 0 | 81 | 72 | 66 | 32 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 0 | 23 | 18 | 30 | 26 | 39 | 0 | 25 | 0 | 90 | 0 | 17 | 227 | 0 | 0 | 0 |  | 24 | 45 | 50 | 64 | 0 | 25 | 14 | 2 | 0 | 0 | 0 | 0 | 305 | 202 | 163 | 0 | 34 | 0 | 0 | 43 | 0 | 35 | 0 | 17 | 8 | 31 | 20 | 140 | 31 | 0 | 15 | 2 | 32 | 40 | 53 | 0 | 0 | 0 | 60 | 82 | 0 | 192 | 17 | 0 | 10 | 270 | 16 | 8 | 120 | 95 | 260 | 50 | 145 | 0 | 34 | 15 | 62 | 193 | 48 | 367 | 77 | 85 | 68 | 3 | 124 | 17 | 72 | 0 | 9 | 63 | 377 | 68 | 37 | 108 | 107 | 0 | 35 | 25 | 92 | 27 | 0 | 145 | 0 |  | 924 | 0 | 200 | 0 | 81 | 0 | 0 | 0 | 15 | 21 | 24 | 156 | 29 | 16 | 0 | 0 | 0 | 28 | 27 | 67 | 14 | 34 | 40 | 0 | 33 | 13 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 166 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 414 | 36 | 0 | 35 | 0 | 42 | 0 | 7 | 35 | 1222 | 0 | 0 | 17 | 4 | 71 | 0 | 175 | 0 | 0 | 26 | 0 | 745 | 115 | 0 |  | 8041 | 5210 | 13251 | 3886 | 924 | 2211 | 430 | 2450 | 2167 | 25 | 320 | 393 | 140 | 305 | 1240.545 | 75.86
15:00 | 0 | 0 | 0 | 180 | 120 | 71 | 0 | 398 | 321 |  | 0 | 450 | 300 | 88 | 88 | 15 | 209 | 0 | 63 | 75 | 66 | 62 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 0 | 23 | 19 | 30 | 26 | 39 | 0 | 25 | 0 | 90 | 0 | 21 | 221 | 0 | 0 | 0 |  | 24 | 30 | 48 | 64 | 0 | 26 | 14 | 2 | 0 | 0 | 0 | 0 | 305 | 203 | 163 | 0 | 32 | 0 | 0 | 43 | 0 | 35 | 6 | 17 | 9 | 31 | 20 | 150 | 31 | 0 | 14 | 2 | 34 | 40 | 53 | 40 | 0 | 0 | 58 | 82 | 0 | 196 | 17 | 0 | 10 | 270 | 16 | 8 | 10 | 95 | 40 | 0 | 145 | 0 | 33 | 12 | 62 | 191 | 50 | 369 | 77 | 105 | 92 | 2 | 124 | 17 | 86 | 0 | 9 | 63 | 370 | 72 | 27 | 108 | 107 | 0 | 35 | 19 | 92 | 36 | 0 | 153 | 0 |  | 920 | 0 | 195 | 0 | 61 | 0 | 0 | 0 | 12 | 26 | 24 | 154 | 29 | 16 | 0 | 0 | 0 | 28 | 28 | 67 | 14 | 34 | 40 | 0 | 33 | 13 | 0 | 8 | 0 | 0 | 178 | 0 | 0 | 166 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 414 | 36 | 0 | 77 | 0 | 80 | 0 | 5 | 90 | 1222 | 0 | 0 | 17 | 3 | 53 | 0 | 175 | 0 | 0 | 19 | 0 | 760 | 113 | 0 |  | 7781 | 5278 | 13059 | 3854 | 920 | 2261 | 50 | 2647 | 2160 | 25 | 328 | 409 | 150 | 255 | 1567.155 | 75.85
16:00 | 0 | 0 | 0 | 180 | 120 | 71 | 0 | 399 | 321 |  | 0 | 450 | 300 | 89 | 88 | 15 | 210 | 0 | 47 | 80 | 66 | 62 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 23 | 18 | 30 | 26 | 39 | 0 | 25 | 0 | 90 | 0 | 25 | 223 | 0 | 0 | 0 |  | 24 | 38 | 48 | 64 | 0 | 26 | 14 | 7 | 0 | 0 | 0 | 0 | 305 | 204 | 163 | 0 | 34 | 0 | 0 | 43 | 0 | 42 | 13 | 16 | 9 | 31 | 20 | 144 | 31 | 0 | 14 | 1 | 32 | 40 | 53 | 45 | 112 | 0 | 59 | 82 | 0 | 196 | 17 | 0 | 10 | 275 | 16 | 8 | 0 | 97 | 0 | 0 | 117 | 0 | 34 | 7 | 62 | 193 | 50 | 367 | 49 | 105 | 105 | 1 | 124 | 17 | 86 | 34 | 9 | 63 | 388 | 71 | 18 | 108 | 107 | 0 | 35 | 12 | 92 | 34 | 0 | 163 | 0 |  | 921 | 0 | 195 | 0 | 61 | 0 | 0 | 0 | 15 | 26 | 24 | 162 | 25 | 16 | 0 | 0 | 0 | 28 | 28 | 46 | 21 | 25 | 40 | 0 | 33 | 15 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 164 | 0 | 0 | 0 | 0 | 0 | 169 | 0 | 414 | 36 | 0 | 95 | 0 | 90 | 0 | 3 | 95 | 1224 | 0 | 0 | 17 | 1 | 33 | 0 | 175 | 0 | 0 | 11 | 0 | 758 | 68 | 0 |  | 7887 | 5222 | 13109 | 3884 | 921 | 2386 | 0 | 2688 | 2162 | 25 | 338 | 406 | 144 | 155 | 1376.155 | 75.84
17:00 | 0 | 0 | 0 | 180 | 120 | 71 | 0 | 396 | 322 |  | 0 | 450 | 305 | 88 | 88 | 15 | 208 | 0 | 63 | 80 | 66 | 62 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 19 | 23 | 23 | 30 | 26 | 39 | 0 | 25 | 0 | 90 | 0 | 25 | 222 | 0 | 0 | 0 |  | 24 | 57 | 65 | 64 | 0 | 28 | 14 | 10 | 0 | 0 | 0 | 0 | 325 | 203 | 163 | 0 | 34 | 0 | 0 | 51 | 0 | 42 | 49 | 16 | 7 | 30 | 20 | 132 | 31 | 0 | 14 | 0 | 33 | 40 | 53 | 45 | 112 | 0 | 58 | 83 | 0 | 196 | 17 | 0 | 10 | 275 | 16 | 8 | 0 | 97 | 0 | 0 | 117 | 0 | 36 | 3 | 62 | 191 | 60 | 383 | 49 | 105 | 105 | 1 | 124 | 17 | 86 | 58 | 55 | 63 | 377 | 72 | 7 | 108 | 107 | 0 | 35 | 6 | 92 | 48 | 0 | 74 | 0 |  | 921 | 0 | 190 | 0 | 61 | 0 | 0 | 0 | 17 | 40 | 24 | 164 | 29 | 16 | 0 | 0 | 0 | 27 | 28 | 46 | 21 | 25 | 40 | 0 | 33 | 16 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 161 | 0 | 0 | 0 | 0 | 0 | 169 | 0 | 414 | 36 | 0 | 95 | 0 | 90 | 0 | 1 | 95 | 1222 | 0 | 0 | 17 | 0 | 14 | 0 | 175 | 0 | 0 | 4 | 0 | 759 | 27 | 0 |  | 8023 | 5165 | 13188 | 3914 | 921 | 2409 | 0 | 2857 | 2161 | 25 | 249 | 457 | 132 | 63 | 918.71 | 75.83
18:00 | 0 | 0 | 0 | 180 | 120 | 72 | 0 | 396 | 328 |  | 0 | 450 | 307 | 82 | 92 | 15 | 208 | 0 | 64 | 80 | 75 | 62 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 19 | 23 | 23 | 30 | 26 | 39 | 0 | 25 | 0 | 110 | 0 | 25 | 221 | 0 | 0 | 0 |  | 24 | 60 | 66 | 77 | 50 | 39 | 14 | 20 | 0 | 0 | 0 | 0 | 315 | 205 | 163 | 0 | 37 | 0 | 0 | 51 | 0 | 42 | 52 | 17 | 7 | 31 | 20 | 138 | 31 | 0 | 14 | 0 | 32 | 40 | 53 | 44 | 112 | 0 | 60 | 83 | 0 | 195 | 18 | 0 | 10 | 280 | 16 | 8 | 0 | 135 | 0 | 0 | 162 | 0 | 120 | 0 | 80 | 192 | 112 | 380 | 75 | 105 | 105 | 0 | 124 | 46 | 107 | 100 | 53 | 88 | 380 | 75 | 1 | 108 | 107 | 0 | 35 | 1 | 93 | 52 | 0 | 54 | 0 |  | 922 | 0 | 190 | 0 | 78 | 0 | 0 | 0 | 19 | 59 | 24 | 170 | 29 | 16 | 0 | 0 | 0 | 27 | 30 | 46 | 21 | 42 | 40 | 8 | 33 | 18 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 158 | 0 | 0 | 0 | 0 | 0 | 169 | 0 | 414 | 36 | 0 | 95 | 0 | 92 | 0 | 0 | 95 | 1222 | 0 | 0 | 150 | 0 | 2 | 35 | 175 | 0 | 0 | 1 | 0 | 754 | 3 | 0 |  | 8530 | 5361 | 13891 | 3935 | 922 | 2434 | 0 | 3560 | 2156 | 25 | 229 | 484 | 138 | 8 | 486.095 | 75.83
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 120 | 74 | 0 | 395 | 333 |  | 0 | 450 | 276 | 81 | 95 | 15 | 215 | 0 | 34 | 80 | 82 | 64 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 0 | 23 | 12 | 30 | 28 | 39 | 0 | 25 | 0 | 110 | 0 | 25 | 226 | 0 | 0 | 0 |  | 25 | 60 | 66 | 77 | 51 | 39 | 14 | 29 | 0 | 0 | 0 | 0 | 350 | 204 | 180 | 0 | 39 | 0 | 0 | 43 | 0 | 42 | 43 | 16 | 7 | 30 | 20 | 140 | 50 | 0 | 15 | 0 | 33 | 40 | 53 | 44 | 112 | 0 | 61 | 83 | 0 | 196 | 17 | 0 | 10 | 280 | 16 | 8 | 118 | 273 | 120 | 50 | 163 | 74 | 132 | 0 | 100 | 193 | 130 | 400 | 105 | 105 | 105 | 0 | 224 | 54 | 107 | 114 | 103 | 88 | 318 | 89 | 0 | 162 | 107 | 0 | 35 | 0 | 93 | 53 | 0 | 54 | 0 |  | 920 | 0 | 190 | 0 | 79 | 0 | 0 | 0 | 19 | 60 | 24 | 151 | 34 | 16 | 0 | 0 | 0 | 27 | 32 | 46 | 21 | 42 | 40 | 8 | 33 | 18 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 156 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 381 | 55 | 0 | 95 | 0 | 92 | 0 | 0 | 95 | 1232 | 0 | 0 | 150 | 0 | 0 | 45 | 175 | 0 | 0 | 0 | 0 | 757 | 0 | 0 |  | 9318 | 5369 | 14687 | 3880 | 920 | 2400 | 362 | 4053 | 2189 | 25 | 229 | 489 | 140 | 0 | 537.665 | 75.82
19:30 | 0 | 0 | 0 | 180 | 120 | 74 | 0 | 403 | 333 |  | 0 | 450 | 307 | 89 | 95 | 55 | 215 | 0 | 37 | 80 | 82 | 82 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 0 | 23 | 23 | 30 | 30 | 48 | 0 | 25 | 0 | 110 | 0 | 25 | 226 | 0 | 0 | 0 |  | 25 | 60 | 66 | 77 | 51 | 39 | 14 | 28 | 0 | 0 | 0 | 0 | 350 | 206 | 153 | 0 | 40 | 0 | 0 | 43 | 0 | 42 | 43 | 16 | 7 | 30 | 20 | 136 | 60 | 0 | 15 | 0 | 33 | 40 | 53 | 45 | 112 | 0 | 60 | 83 | 0 | 197 | 17 | 0 | 10 | 280 | 16 | 8 | 128 | 275 | 300 | 65 | 164 | 74 | 132 | 0 | 100 | 193 | 133 | 400 | 95 | 105 | 105 | 0 | 224 | 54 | 107 | 114 | 104 | 88 | 395 | 90 | 0 | 162 | 107 | 0 | 35 | 0 | 93 | 54 | 0 | 54 | 0 |  | 850 | 0 | 190 | 0 | 79 | 100 | 0 | 0 | 19 | 61 | 24 | 162 | 34 | 16 | 0 | 0 | 0 | 27 | 32 | 46 | 21 | 42 | 40 | 8 | 33 | 18 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 156 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 395 | 55 | 0 | 95 | 0 | 92 | 0 | 0 | 95 | 1244 | 0 | 0 | 150 | 0 | 0 | 73 | 175 | 0 | 0 | 0 | 0 | 753 | 0 | 0 |  | 9711 | 5461 | 15172 | 4005 | 850 | 2418 | 567 | 4137 | 2197 | 25 | 329 | 508 | 136 | 0 | 456.49 | 0
20:00 | 0 | 0 | 0 | 180 | 120 | 74 | 0 | 396 | 334 |  | 0 | 450 | 285 | 85 | 95 | 45 | 216 | 0 | 36 | 80 | 82 | 146 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 23 | 23 | 30 | 30 | 48 | 0 | 25 | 0 | 110 | 0 | 25 | 226 | 0 | 0 | 0 |  | 25 | 60 | 66 | 77 | 51 | 39 | 15 | 17 | 0 | 0 | 0 | 0 | 345 | 204 | 155 | 0 | 40 | 0 | 0 | 43 | 0 | 43 | 44 | 16 | 7 | 30 | 20 | 138 | 59 | 0 | 15 | 0 | 32 | 40 | 53 | 45 | 112 | 0 | 61 | 83 | 0 | 198 | 17 | 0 | 10 | 275 | 16 | 8 | 129 | 265 | 254 | 40 | 164 | 44 | 132 | 0 | 100 | 192 | 130 | 404 | 96 | 105 | 105 | 0 | 226 | 54 | 107 | 114 | 100 | 88 | 394 | 90 | 0 | 162 | 107 | 0 | 35 | 0 | 93 | 54 | 0 | 54 | 0 |  | 849 | 0 | 190 | 0 | 79 | 100 | 0 | 0 | 29 | 61 | 32 | 170 | 34 | 64 | 0 | 0 | 0 | 27 | 21 | 46 | 21 | 42 | 40 | 43 | 31 | 18 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 157 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 414 | 55 | 0 | 95 | 0 | 92 | 0 | 0 | 95 | 1244 | 0 | 0 | 150 | 0 | 0 | 75 | 175 | 0 | 0 | 0 | 0 | 754 | 0 | 0 |  | 9625 | 5579 | 15204 | 4004 | 849 | 2402 | 467 | 4222 | 2198 | 25 | 329 | 570 | 138 | 0 | 473.68 | 75.82
21:00 | 0 | 0 | 0 | 180 | 120 | 74 | 0 | 394 | 330 |  | 0 | 450 | 325 | 89 | 95 | 55 | 216 | 0 | 35 | 80 | 91 | 146 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 23 | 23 | 30 | 32 | 48 | 0 | 25 | 0 | 110 | 0 | 25 | 226 | 0 | 0 | 0 |  | 25 | 63 | 66 | 77 | 52 | 39 | 14 | 15 | 0 | 0 | 0 | 0 | 350 | 204 | 155 | 0 | 41 | 0 | 0 | 43 | 0 | 44 | 52 | 18 | 7 | 32 | 20 | 136 | 94 | 0 | 15 | 0 | 32 | 40 | 53 | 45 | 112 | 0 | 60 | 83 | 0 | 200 | 17 | 0 | 10 | 275 | 16 | 8 | 129 | 270 | 295 | 70 | 164 | 75 | 148 | 0 | 100 | 192 | 147 | 403 | 97 | 105 | 105 | 0 | 228 | 54 | 107 | 114 | 109 | 88 | 393 | 88 | 0 | 162 | 107 | 0 | 6 | 0 | 93 | 54 | 0 | 54 | 0 |  | 850 | 0 | 190 | 0 | 85 | 160 | 0 | 0 | 24 | 72 | 32 | 170 | 35 | 110 | 0 | 0 | 0 | 20 | 28 | 80 | 21 | 42 | 42 | 43 | 31 | 19 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 159 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 414 | 55 | 0 | 95 | 0 | 92 | 0 | 0 | 95 | 1244 | 0 | 0 | 150 | 0 | 0 | 111 | 175 | 0 | 0 | 0 | 0 | 750 | 0 | 0 |  | 9856 | 5770 | 15626 | 4048 | 850 | 2438 | 569 | 4361 | 2194 | 25 | 389 | 616 | 136 | 0 | 482.275 | 75.82
22:00 | 0 | 0 | 0 | 180 | 120 | 74 | 0 | 394 | 330 |  | 0 | 450 | 326 | 90 | 85 | 55 | 213 | 0 | 38 | 85 | 91 | 146 | 2 | 0 | 0 | 0 | 54 | 55 | 35 | 0 | 23 | 16 | 30 | 16 | 48 | 0 | 25 | 0 | 110 | 0 | 25 | 225 | 0 | 0 | 0 |  | 25 | 54 | 67 | 77 | 53 | 39 | 14 | 17 | 0 | 0 | 0 | 0 | 340 | 198 | 155 | 0 | 42 | 0 | 0 | 51 | 0 | 44 | 52 | 18 | 7 | 32 | 20 | 140 | 93 | 0 | 15 | 0 | 33 | 40 | 53 | 46 | 112 | 0 | 60 | 84 | 0 | 203 | 17 | 0 | 10 | 280 | 16 | 5 | 129 | 281 | 292 | 68 | 164 | 70 | 149 | 0 | 100 | 192 | 149 | 400 | 107 | 105 | 105 | 0 | 228 | 54 | 105 | 114 | 113 | 88 | 390 | 87 | 0 | 162 | 107 | 0 | 35 | 0 | 93 | 54 | 0 | 26 | 0 |  | 850 | 0 | 190 | 0 | 98 | 100 | 0 | 0 | 24 | 65 | 32 | 170 | 37 | 110 | 0 | 0 | 0 | 20 | 22 | 81 | 21 | 42 | 40 | 43 | 31 | 21 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 169 | 0 | 414 | 55 | 0 | 95 | 0 | 92 | 0 | 0 | 95 | 1244 | 0 | 0 | 150 | 0 | 0 | 115 | 175 | 0 | 0 | 0 | 0 | 754 | 0 | 0 |  | 9820 | 5723 | 15543 | 4005 | 850 | 2460 | 559 | 4411 | 2198 | 25 | 301 | 594 | 140 | 0 | 436.435 | 75.81
23:00 | 0 | 0 | 0 | 180 | 120 | 75 | 0 | 394 | 330 |  | 0 | 450 | 324 | 84 | 85 | 15 | 213 | 0 | 40 | 85 | 50 | 146 | 7 | 0 | 0 | 0 | 35 | 35 | 35 | 0 | 23 | 16 | 30 | 16 | 48 | 0 | 0 | 0 | 110 | 0 | 25 | 228 | 0 | 0 | 0 |  | 20 | 54 | 67 | 77 | 0 | 39 | 12 | 22 | 0 | 0 | 0 | 0 | 350 | 193 | 155 | 0 | 42 | 0 | 0 | 51 | 0 | 44 | 52 | 16 | 7 | 32 | 20 | 140 | 94 | 0 | 15 | 0 | 34 | 40 | 53 | 47 | 112 | 0 | 60 | 84 | 0 | 200 | 17 | 0 | 10 | 275 | 16 | 8 | 130 | 291 | 231 | 48 | 165 | 60 | 77 | 0 | 100 | 192 | 150 | 402 | 107 | 105 | 105 | 0 | 228 | 54 | 105 | 114 | 73 | 77 | 382 | 72 | 0 | 162 | 107 | 0 | 35 | 0 | 93 | 53 | 0 | 0 | 0 |  | 822 | 0 | 200 | 0 | 98 | 0 | 0 | 0 | 24 | 67 | 32 | 170 | 37 | 16 | 0 | 0 | 0 | 14 | 22 | 81 | 21 | 42 | 40 | 8 | 31 | 21 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 161 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 414 | 55 | 0 | 95 | 0 | 92 | 0 | 0 | 95 | 1244 | 0 | 0 | 150 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 751 | 0 | 0 |  | 9375 | 5198 | 14573 | 4019 | 822 | 2460 | 469 | 3878 | 2195 | 0 | 0 | 590 | 140 | 0 | 1028.535 | 75.8
24:00 | 0 | 0 | 0 | 180 | 120 | 75 | 0 | 394 | 330 |  | 0 | 450 | 295 | 48 | 85 | 6 | 215 | 0 | 40 | 85 | 50 | 146 | 12 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 23 | 22 | 30 | 31 | 48 | 0 | 0 | 0 | 110 | 0 | 25 | 228 | 0 | 0 | 0 |  | 25 | 48 | 67 | 66 | 0 | 6 | 12 | 28 | 0 | 0 | 0 | 0 | 350 | 190 | 155 | 0 | 43 | 0 | 0 | 51 | 0 | 42 | 52 | 16 | 7 | 33 | 20 | 130 | 82 | 0 | 18 | 0 | 34 | 40 | 53 | 47 | 112 | 0 | 60 | 84 | 0 | 199 | 17 | 0 | 10 | 270 | 16 | 8 | 30 | 287 | 104 | 25 | 165 | 25 | 34 | 0 | 88 | 192 | 150 | 372 | 107 | 105 | 76 | 0 | 87 | 54 | 64 | 114 | 9 | 77 | 390 | 55 | 0 | 108 | 107 | 0 | 35 | 0 | 87 | 17 | 0 | 0 | 0 |  | 822 | 0 | 205 | 0 | 98 | 0 | 0 | 0 | 22 | 66 | 32 | 168 | 37 | 16 | 0 | 0 | 0 | 14 | 22 | 85 | 21 | 42 | 40 | 0 | 31 | 21 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 161 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 415 | 55 | 0 | 50 | 0 | 49 | 0 | 0 | 57 | 1244 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 759 | 0 | 0 |  | 8509 | 5060 | 13569 | 4031 | 822 | 2433 | 184 | 3183 | 2203 | 0 | 0 | 583 | 130 | 0 | 1653.105 | 75.8
KWH | 0 | 0 | 0 | 4268250 | 2637900 | 1673772 | 0 | 9535490 | 7760000 |  | 0 | 10065000 | 7293091 | 1604160 | 1907349 | 479088 | 5141130 | 0 | 1634000 | 1522560 | 1439424 | 1401120 | 24124 | 0 | 0 | 0 | 648000 | 891436 | 890057 | 285516 | 552000 | 426060 | 775900 | 623800 | 1067040 | 0 | 307080 | 0 | 2200000 | 0 | 548199 | 5350301 | 0 | 0 | 0 |  | 593520 | 1061424 | 1478023 | 1628280 | 261120 | 504960 | 313296 | 391680 | 0 | 0 | 0 | 0 | 7917000 | 4709000 | 4131636 | 0 | 933048 | 0 | 0 | 1048182 | 0 | 961760 | 571800 | 280404 | 196560 | 777300 | 435890 | 3254400 | 1271040 | 0 | 376820 | 11700 | 788000 | 911520 | 1262400 | 999648 | 884454 | 0 | 1336928 | 2016000 | 0 | 4075400 | 409000 | 0 | 232920 | 6593500 | 379152 | 189408 | 1824384 | 3783545 | 4195787 | 855967 | 2534400 | 343272 | 17821290 | 100440 | 1462080 | 4624800 | 2166181 | 9312000 | 1695600 | 2377123 | 1422655 | 26039 | 3051055 | 778257 | 1785628 | 1448940 | 691320 | 1385280 | 9296200 | 1560960 | 274670 | 2322720 | 2568055 | 0 | 850320 | 202855 | 1656000 | 956520 | 0 | 1179272 | 0 |  | 21674181 | 0 | 5305824 | 0 | 2010240 | 383715 | 0 | 0 | 389280 | 1250048 | 675750 | 4011140 | 737042 | 609984 | 0 | 0 | 0 | 633808 | 341807 | 1683032 | 474900 | 883070 | 695340 | 131112 | 767650 | 440640 | 0 | 159660 | 0 | 0 | 5092000 | 3000 | 0 | 4389345 | 0 | 0 | 0 | 0 | 0 | 4392455 | 0 | 9675054 | 942240 | 0 | 1590240 | 370080 | 1552992 | 0 | 42285 | 1570176 | 31530600 | 0 | 0 | 1916400 | 31080 | 597600 | 411840 | 1678916 | 0 | 0 | 183114 | 0 | 16863636 | 1043630 | 0 |  | 210692635 | 127134906 | 337827541 | 95596737 | 21674181 | 55205019 | 7219410 | 84662870 | 53486236 | 307080 | 3244903 | 10663292 | 3254400 | 2513413 | 0
Fuel Cost | 0 | 0 | 0 | 6359692.5 | 2954448 | 2226116.76 | 0 | 10012264.5 | 8380800 |  | 0 | 10970850 | 8095331.01 | 17934508.8 | 25272374.25 | 6347916 | 5758065.6 | 0 | 2859500 | 22259827.2 | 20252695.68 | 22712155.2 | 222423.28 | 0 | 0 | 0 | 8242560 | 12034386 | 11935664.37 | 214137 | 414000 | 0 | 0 | 0 | 18150350.4 | 0 | 82911.6 | 0 | 4158000 | 0 | 8963053.65 | 5564313.04 | 0 | 0 | 0 |  | 7745436 | 17704552.32 | 25155951.46 | 21998062.8 | 3311001.6 | 5842387.2 | 397885.92 | 1304294.4 | 0 | 0 | 0 | 0 | 8629530 | 5462440 | 5329810.44 | 0 | 1054344.24 | 0 | 0 | 1750463.94 | 0 | 16609595.2 | 7690710 | 384153.48 | 147420 | 1360275 | 326917.5 | 23366592 | 1385433.6 | 0 | 512475.2 | 186498 | 1079560 | 1203206.4 | 2196576 | 1729391.04 | 1017122.1 | 0 | 2593640.32 | 4596480 | 0 | 4116154 | 879350 | 0 | 461181.6 | 6593500 | 284364 | 143950.08 | 38239088.64 | 51645389.25 | 87943695.52 | 17692837.89 | 34163712 | 7095432.24 | 246824866.5 | 1174143.6 | 15088665.6 | 63174768 | 28745221.87 | 8567040 | 20618496 | 34373198.58 | 17996585.75 | 0 | 35819385.7 | 8475218.73 | 18981225.64 | 19662115.8 | 8911114.8 | 16318598.4 | 8552504 | 20214432 | 3968981.5 | 29475316.8 | 29224465.9 | 0 | 11105179.2 | 2424117.25 | 24790320 | 12597368.4 | 0 | 0 | 0 |  | 65022543 | 0 | 5942522.88 | 0 | 20926598.4 | 6331297.5 | 0 | 0 | 7010932.8 | 22500864 | 9710527.5 | 4492476.8 | 1429861.48 | 6648825.6 | 0 | 0 | 0 | 10628960.16 | 5978204.43 | 26322620.48 | 3656730 | 14623639.2 | 11758199.4 | 1787056.56 | 12950255.5 | 912124.8 | 0 | 120862.62 | 0 | 0 | 26936680 | 126060 | 0 | 5091640.2 | 0 | 0 | 0 | 0 | 0 | 5095247.8 | 0 | 9578303.46 | 12663705.6 | 0 | 18812539.2 | 5347656 | 19722998.4 | 0 | 467249.25 | 19061936.64 | 284090706 | 0 | 0 | 14181360 | 351514.8 | 7009848 | 6313507.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1350792536.24 | 673606055.66 | 2024398591.9 | 106117814.68 | 65022543 | 66572207.03 | 150971054.29 | 1099866082.45 | 311027386 | 82911.6 | 6457357.5 | 179332290.95 | 23366592 | 15582352.4 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 120 | 66 | 0 | 396 | 334 |  | 0 | 450 | 305 | 88 | 92 | 14 | 214 | 0 | 62 | 72 | 58 | 32 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 23 | 18 | 30 | 12 | 41 | 0 | 25 | 0 | 90 | 0 | 17 | 225 | 0 | 0 | 0 |  | 24 | 36 | 49 | 66 | 0 | 25 | 14 | 2 | 0 | 0 | 0 | 0 | 305 | 206 | 167 | 0 | 36 | 0 | 0 | 43 | 0 | 35 | 0 | 17 | 8 | 32 | 20 | 140 | 16 | 0 | 15 | 2 | 34 | 40 | 48 | 43 | 0 | 0 | 60 | 83 | 0 | 199 | 17 | 0 | 10 | 275 | 16 | 8 | 115 | 264 | 280 | 50 | 125 | 0 | 119 | 19 | 50 | 193 | 50 | 367 | 68 | 88 | 68 | 4 | 122 | 17 | 68 | 0 | 9 | 63 | 395 | 53 | 41 | 108 | 107 | 0 | 35 | 30 | 62 | 35 | 0 | 134 | 0 |  | 925 | 0 | 200 | 0 | 77 | 0 | 0 | 0 | 17 | 48 | 24 | 168 | 25 | 16 | 0 | 0 | 0 | 28 | 4 | 69 | 21 | 34 | 40 | 0 | 34 | 16 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 173 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 414 | 36 | 0 | 35 | 0 | 42 | 0 | 6 | 35 | 1244 | 0 | 0 | 17 | 5 | 85 | 0 | 0 | 0 | 0 | 30 | 0 | 585 | 170 | 0 |  | 13307 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 120 | 74 | 0 | 394 | 330 | 0 | 0 | 450 | 325 | 89 | 95 | 55 | 216 | 0 | 35 | 80 | 91 | 146 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 23 | 23 | 30 | 32 | 48 | 0 | 25 | 0 | 110 | 0 | 25 | 226 | 0 | 0 | 0 | 0 | 25 | 63 | 66 | 77 | 52 | 39 | 14 | 15 | 0 | 0 | 0 | 0 | 350 | 204 | 155 | 0 | 41 | 0 | 0 | 43 | 0 | 44 | 52 | 18 | 7 | 32 | 20 | 136 | 94 | 0 | 15 | 0 | 32 | 40 | 53 | 45 | 112 | 0 | 60 | 83 | 0 | 200 | 17 | 0 | 10 | 275 | 16 | 8 | 129 | 270 | 295 | 70 | 164 | 75 | 148 | 0 | 100 | 192 | 147 | 403 | 97 | 105 | 105 | 0 | 228 | 54 | 107 | 114 | 109 | 88 | 393 | 88 | 0 | 162 | 107 | 0 | 6 | 0 | 93 | 54 | 0 | 54 | 0 |  | 850 | 0 | 190 | 0 | 85 | 160 | 0 | 0 | 24 | 72 | 32 | 170 | 35 | 110 | 0 | 0 | 0 | 20 | 28 | 80 | 21 | 42 | 42 | 43 | 31 | 19 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 159 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 414 | 55 | 0 | 95 | 0 | 92 | 0 | 0 | 95 | 1244 | 0 | 0 | 150 | 0 | 0 | 111 | 175 | 0 | 0 | 0 | 0 | 750 | 0 | 0 |  | 15626 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 120 | 76 | 0 | 400 | 330 | 0 | 0 | 450 | 300 | 92 | 95 | 55 | 216 | 0 | 64 | 90 | 92 | 149 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 23 | 23 | 33 | 32 | 48 | 0 | 25 |  | 110 | 0 | 25 | 225 | 0 | 0 | 0 | 0 | 25 | 60 | 66 | 77 | 52 | 40 | 14 | 15 | 0 | 0 | 0 | 0 | 350 | 210 | 155 | 0 | 41 | 0 | 0 | 51 | 0 | 44 | 52 | 18 | 9 | 33 | 20 | 153 | 90 | 0 | 18 | 0 | 33 | 41 | 51 | 49 | 112 | 0 | 60 | 85 | 0 | 200 | 17 | 0 | 10 | 290 | 16 | 8 | 130 | 300 | 300 | 70 | 165 | 75 | 149 | 0 | 100 | 195 | 150 | 400 | 100 | 105 | 105 | 0 | 230 | 54 | 105 | 114 | 113 | 90 | 400 | 90 | 0 | 162 | 107 | 0 | 35 |  | 92 | 54 | 0 |  |  |  | 943 | 0 | 210 |  | 98 | 0 | 0 | 0 | 35 | 72 | 40 | 170 | 35 | 110 | 0 | 0 | 0 | 27 | 32 | 80 | 21 | 42 | 42 | 43 | 35 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 160 |  | 0 | 0 | 0 | 0 | 180 | 0 | 414 | 55 | 0 | 95 | 0 | 95 | 0 | 0 | 95 | 1244 | 0 |  | 150 |  |  | 114 | 0 |  | 335 |  | 0 | 755 |  | 0
Forecast for Day | 0 | 0 | 0 | 180 | 120 | 75 | 0 | 400 | 340 | 0 | 0 | 450 | 300 | 80 | 90 | 15 | 216 | 0 | 64 | 90 | 64 | 32 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 23 | 23 | 33 | 32 | 48 | 0 | 25 | 0 | 110 | 0 | 25 | 225 | 0 | 0 | 0 | 0 | 25 | 48 | 66 | 55 | 0 | 26 | 14 | 5 | 0 | 0 | 0 | 0 | 350 | 200 | 155 | 0 | 41 | 0 | 0 | 51 | 0 | 40 | 0 | 18 | 9 | 33 | 20 | 135 | 33 | 0 | 18 | 1.6 | 33 | 41 | 50 | 44 | 112 | 0 | 60 | 84 | 0 | 200 | 17 | 0 | 10 | 280 | 16 | 8 | 130 | 300 | 300 | 50 | 140 | 0 | 149 | 20 | 50 | 195 | 53 | 400 | 100 | 88 | 51 | 5 | 120 | 17 | 68 | 0 | 9 | 63 | 400 | 54 | 50 | 108 | 107 | 0 | 35 | 30 | 62 | 35 | 0 |  |  |  | 943 | 0 | 210 | 0 | 85 | 0 | 0 | 0 | 22 | 66 | 40 | 170 | 25 | 16 | 0 | 0 | 0 | 27 | 0 | 80 | 21 | 42 | 40 | 0 | 35 | 22 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 414 | 55 | 0 | 35 | 0 | 42 | 0 | 8 | 35 | 1244 | 0 |  | 17 | 6 | 100 | 0 | 0 |  | 335 | 30 | 0 | 755 | 130 | 0 |  |  |  |  | g | h | o | c | h | t | s
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 120 | 75 | 0 | 393 | 344 | 0 | 0 | 450 | 250 | 34 | 67 | 15 | 219 | 0 | 64 | 33 | 24 | 64 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 23 | 8 | 33 | 32 | 49 | 0 | 0 | 0 | 110 | 0 | 25 | 228 | 0 | 0 | 0 | 0 | 23 | 38 | 50 | 55 | 0 | 6 | 11 | 2 | 0 | 0 | 0 | 0 | 355 | 191 | 155 | 0 | 43 | 0 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 30 | 15 | 116 | 35 | 0 | 18 | 0 | 33 | 41 | 50 | 45 | 112 | 0 | 61 | 75 | 0 | 198 | 17 | 0 | 10 | 270 | 16 | 8 | 0 | 95 | 0 | 0 | 47 | 0 | 34 | 8 | 38 | 157 | 53 | 405 | 49 | 105 | 17 | 2 | 87 | 17 | 54 | 114 | 9 | 38 | 400 | 52 | 15 | 54 | 107 | 0 | 35 | 8 | 35 | 17 | 0 | 0 | 0 | 0 | 923 | 0 | 210 | 0 | 65 | 0 | 0 | 0 | 22 | 66 | 24 | 169 | 25 | 16 | 0 | 0 | 0 | 0 | 0 | 78 | 14 | 34 | 0 | 0 | 32 | 22 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 166 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 423 | 55 | 0 | 35 | 0 | 42 | 0 | 2 | 35 | 1244 | 0 | 0 | 17 | 1 | 24 | 0 | 0 | 0 | 335 | 10 | 0 | 755 | 57 | 0 | 0 |  |  |  | 150.8018 | 21.6742 | 105.7905 | 53.4862 | 0.30708 | 3.2544 | 2.5134
337.8275
| Minimum Generation |  | 11656 | 7:00
| Highest Generation |  | 15626 | 21:00
| Day Peak Generation |  | 13307 | 12:00
| Evening Peak Generation |  | 15626 | 21:00
| HVDC Max Flow |  | 926 | 5:00
| HVDC EvPeak Flow |  | 850 | 21:00
| Load factor L.F |  | 90.08% | [161 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2023-04-19
Till now the maximum generation is : - |  |  |  | 15304 | 21:00 | Hrs on | 2023-04-13
The Summary of Yesterday's |  |  | 2023-04-18 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 13307 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 12354
Evening Peak Generation : |  |  | 15626 | MW Hour : | 21:00 | Available Max Generation : |  | 15948
E.P. Demand (at gen end) : |  |  | 16131 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 15500
Maximum Generation : |  |  | 15626 | MW Hour : | 21:00 | Reserve(Generation end) |  | 448
Total Gen. (MKWH) : |  |  | 337.8275 | System Load Factor : | 90.08% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 150 | MW at | 20:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2023-04-19
Actual : |  | 75.77 | Ft.(MSL) , | Rule curve : | 84.4 | Ft.( MSL )
Gas Consumed : |  | Total = | 1174.57 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 172690021.71
: |  |  | Coal : | 311027386 | Oil : | 1436626785.19 | Total : | 1920344192.9
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 0 | 0:00 | 4868.8972 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 1351.1159 |  |  | 0 | 0%
Khulna Area |  | 0 | 0:00 | 1776.9624 |  |  | 0 | 0%
Rajshahi Area |  | 25 | 600:00 | 1568.8632 |  |  | 0 | 0%
Cumilla Area |  | 27 | 648:00 | 1339.0166 |  |  | 0 | 0%
Mymensingh Area |  | 200 | 4800:00 | 1101.314 |  |  | 0 | 0%
Sylhet Area |  | 80 | 1920:00 | 497.0047 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 401.4396 |  |  | 0 | 0%
Rangpur Area |  | 150 | 3600:00 | 869.6114 |  |  | 0 | 0%
Total |  | 482 |  | 13774.225 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 1,2
2) Ghorasal-3
3) Bhula Nuton Biddut
4) Baghabari-100 MW & 71 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
7) Shajibazar 330 MW
8) Sirajganj- 3
9) Barishal 307 MW
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
08:04 | 08:22 | Aminbazar-Mirpur 132kV Ckt-2 Tripped from Mirpur 132/33kV end showing General Trip. relays Due to Amin Bazer 400KV | [5 empty] | 67.0MW load interrup.
|  | X-former Comissioning Effect. | [5 empty] | Mirpur 132/33 KV end.
08:23 | 22:12 | Chattak-Sylhet 132 kV Ckt-1 Scheduled S/D from Chhatak 132/33kV end Due to Sylhet-chhatak Ckt-1 CB replace work.
and from Sylhet 132/33kV end Due to work of chhatak end
| 08:37 | Jamalpur 132/33kV S/S T-2 LT is restored.
| 08:37 | Jamalpur 132/33kV S/S T-2 HT is restored.
| 09:02 | Jhenaidah 132/33kV S/S Transformer T-1 HT is restored.
| 09:02 | Jhenaidah 132/33kV S/S Transformer T-1 LT is restored.
09:17 | 10:48 | Chapai 132/33kV S/S T-1 (405T) HT Scheduled S/D Due to 33kV CT High Junction Temperature
09:17 | 10:49 | Chapai 132/33kV S/S T-1 (405T) LT Scheduled S/D Due to Same
09:18 | 13:43 | Aminbazar 400/230/132kV S/S 132 kv Bus 01 Forced S/D Due to Cable loop repairung of 132 kv side of 400/132 kv
transforner
| 10:42 | Shikalbaha 230/132kV S/S Interconnection-1 is restored.
11:02 | 12:51 | Ishurdi 132/33kV S/S 132 kV Bus-2 Scheduled S/D Due to Red hot Maintenance
12:00 | 13:03 | Chauddagram 132/33kV S/S 132 kv T-1 HT Forced S/D Due to 33 kv Bus-01 red hot | [5 empty] | 20.0MW load interrup.
12:00 |  | Day peak Generation: 13307 MW load shed about 1044 MW
12:01 | 13:03 | Chauddagram 132/33kV S/S 132 kv T-1 LT Forced S/D Due to 33 kv Bus-01 Red Hot. | [5 empty] | 20.0MW load interrup.
| 12:51 | Barishal 230/132kV S/S T-4 HT is restored.
| 12:53 | Barishal 230/132kV S/S T-4 LT is restored.
14:10 |  | Aminbazar 400/132kV Interim transformer was switched on.
| 14:30 | Sreemongol 132/33kV S/S 132/33kv T-3 HT is restored.
| 14:30 | Sreemongol 132/33kV S/S 132/33kv T-3 LT is restored.
15:15 | 15:25 | Kallyanpur 132/33kV S/S GT-2 (132kV) HT Project Work S/D Due to Sf6 gas pressure checking
15:19 |  | Kushiara 163MW GT was sync.
19:06 |  | Khulna 225MW GT was sync.
21:00 |  | Evening peak generation15626 MW
21:05 | 07:38 | Sirajganj 132/33kV S/S Sherpur-1 Forced S/D Due to ALDC Bogura instruction Sirajgonj-Sherpur line (Ckt-1) CB off | [5 empty] | 14.0MW load interrup.
due to Pabna-Shahjadpur 132KV TL overload.
23:11 | 23:59 | Shahjibazar 132/33kV S/S TR-04 LT Forced S/D Due to 33 kv Hobigonj old feeder red hot maintenance. | [5 empty] | 45.0MW load interrup.
23:14 | 23:56 | Shahjibazar 132/33kV S/S TR-04 HT Forced S/D Due to TR-04 33 kv side bus shutdown due to hobigonj old feeder red hot | [5 empty] | 45.0MW load interrup.
maintenance.
02:06 |  | Rampal P/S Synchronize.
07:00 |  | Minimum generation 12354MW
07:05 | 07:30 | Sirajganj 132/33kV S/S T2-(425) LT Forced S/D Due to Red Hot has become visible/measured at 33kV T2+T3 connecting | [5 empty] | 25.0MW load interrup.
bus isolator. all operation has been conducted by the instruction of ALDC, Bogura with the permission of NLDC Dhaka.
07:10 |  | Baroaulia-Hathazari 132 kV Ckt-1 Forced S/D from Baroaulia 132/33kV end Due to Red Hot in Line Isolator | [5 empty] | 40.0MW load interrup.
Baroaulia
07:14 |  | Chattak-Sylhet 132 kV Ckt-1 Scheduled S/D from Chhatak 132/33kV end Due to New Breaker Replacement and from Sylhet
132/33kV end Due to Maintenance for Chhatak SS end.
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2023-04-18 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4268250
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 120 | 2637900 | ST under S/D
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 74 | 1673772 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 394 | 9535490 | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 330 | 7760000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 10065000
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 89 | 1604160 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 325 | 7293091 | FGMO
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 95 | 1907349 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 55 | 479088
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 24124 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 285516 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 35 | 1634000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 80 | 1522560 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 216 | 5141130
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 91 | 1439424 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 648000
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 146 | 1401120
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 891436
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 890057
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 46 | 978060 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 30 | 775900
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 32 | 623800
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 48 | 1067040 | 0:00
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 270 | 3783545 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 295 | 4195787
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 70 | 855967 | Fuel shortage
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 75 | 343272 | Fuel shortage
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 148 | 17821290
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 2377123
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 88 | 1560960 | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 2322720
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 202855
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 54 | 956520
| Dhaka area Total |  |  |  | 5847 | 4267 | 98966306
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 110 | 2200000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 25 | 548199
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 100440
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 39 | 504960 | Fuel shortage
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 25 | 307080 | Low Water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 226 | 5350301
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 105 | 1422655
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 63 | 1061424 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 66 | 1478023 | Engine problem
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 77 | 1628280 | Engine problem
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 100 | 1462080
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 14 | 313296 | Gas shortage
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 15 | 391680
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 52 | 261120 | Engine problem
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 26039
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 228 | 3051055 | Engine problem
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 778257
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 107 | 1785628
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 88 | 1385280
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 107 | 2568055 | Engine problem
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 0 | 54 | 1179272 | On test.
| Chattogram area Total |  |  |  | 2382 | 1555 | 27803124
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 204 | 4709000 | FGMO
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 0 | 0 | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 350 | 7917000 | FGMO
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 0 | 0 | Under maint.
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 41 | 933048 | Gas shortage
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 0 | 0 | Gas shortage
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 155 | 4131636 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 1048182 | Engine problem
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 147 | 2166181
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 44 | 961760 | Engine problem
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 192 | 4624800
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 280404 | Engine problem
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 7 | 196560 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 136 | 3254400
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 32 | 777300
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 571800
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 20 | 435890 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 129 | 1824384 | Fuel shortage
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 1448940
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 109 | 691320
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 6 | 850320 | Engine problem
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 93 | 1656000 | Fuel shortage
| Cumilla Area Total |  |  |  | 3151 | 1892 | 38478925
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 94 | 1271040 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 15 | 376820 | Engine problem
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 11700
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 164 | 2534400 | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 97 | 1695600 | Fuel shortage
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 274670
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 25 | 593520
| Mymensingh Area Total |  |  |  | 614 | 395 | 6757750
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 32 | 788000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 40 | 911520 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 112 | 884454 | Gas shortage
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 1262400
| Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 45 | 999648
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 8 | 189408 | Engine problem
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 60 | 1336928
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 83 | 2016000
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 200 | 4075400 | Machine problem
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 409000
| Sylhet 50MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 379152 | Engine problem
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 275 | 6593500 | Gas shortage
104 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 403 | 9312000 | FGMO
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 232920
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 393 | 9296200
| Sylhet Area Total |  |  |  | 2427 | 1747 | 38686530
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Fuel shortage
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 850 | 21674181
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 85 | 2010240 | Engine problem
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 24 | 389280 | Engine problem
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 160 | 383715 | Fuel conservation
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 72 | 1250048 | Engine problem
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 190 | 5305824 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 32 | 675750 | Fuel shortage
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Fuel shortage
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 55 | 942240 | Fuel shortage
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 370080
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 597600
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 0 | 175 | 1678916 | On test.
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 660*2 | 617 | 0 | 0 | On test.
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3001 | 1643 | 35277874
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 110 | 609984
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 35 | 737042 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 170 | 4011140 | Machine problem
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1244 | 31530600
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 0 | 0 | Under maint.
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 150 | 1916400
| Barisal 307 MW |  | BCPCL | 307*1 | 307 | 0 | 0 | On test.
| Barisal Area Total |  |  |  | 2265 | 1709 | 38805166
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 20 | 633808 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 28 | 341807 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 21 | 474900
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 42 | 883070 | Engine problem
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 42 | 695340 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 159 | 4389345 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 168 | 4392455 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 414 | 9675054
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 31 | 767650 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 19 | 440640
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 159660
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 43 | 131112 | Engine problem
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 80 | 1683032 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Fuel shortage
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 95 | 1590240 | Fuel shortage
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 95 | 1570176 | Fuel shortage
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 31080
| Adani Power Jharkhanda Ltd |  | Import | 0 | 0 | 750 | 16863636 | On test.
| Rajshahi Area Total |  |  |  | 2129 | 2015 | 44723005
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 200 | 5092000 | Coal shortage
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 3000
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 92 | 1552992 | Fuel shortage
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 42285
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 111 | 411840
| Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 183114
| Teesta Solar Limited |  | BPCL | 16*12.5 | 0 | 0 | 1043630
| Rangpur Area Total |  |  |  | 750 | 403 | 8328861
| Total |  |  |  | 22566 | 15626 | 337827541
| Eastern Grid Total |  |  |  | 14421 | 9856 | 210692635
| Western Grid Total |  |  |  | 8145 | 5770 | 127134906
| National Grid Total |  |  |  | 22566 | 15626 | 337827541
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2023-04-18
| (a) ENTIRE EASTERN GRID : |  | 9785.26 | MW | (b) ENTIRE WESTERN GRID : |  | 5117.36 | MW
| i) Dhaka area |  | 5265.7 | MW | i) Khulna area |  | 1986.2 | MW
| ii) Chittagong area |  | 1428.56 | MW | ii) Rajshahi area |  | 1777.6 | MW
| iii) Comilla area |  | 1541 | MW | iii) Barisal area |  | 488.56 | MW
| iv) Mymensingh area |  | 1031 | MW | iv) Rangpur area |  | 865 | MW
| v) Sylhet area |  | 519 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 14902.62 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | Chhatak | 20 | 16:00 | Kamrangirchar | 55 | 13:00 | Natore | 180 | 21:00 | Shitalakhya | 139 | 14:00
2 | AKSML | 123 | 14:00 | Chowmuhani | 252 | 22:00 | Kaptai | 4 | 00:00 | Nawabganj | 59.9 | 21:00 | Sholosohor | 34 | 09:00
3 | Aftabnagar | 44 | 19:00 | Chuadanga | 111 | 21:00 | Kazla | 100 | 17:00 | Netrakona | 128 | 19:00 | Shyampur | 156 | 06:00
4 | Agargaon | 100 | 13:00 | Coxsbazar | 125 | 19:00 | Keranigonj | 62 | 00:00 | New | 78 | 12:00 | Siddhirganj | 118 | 13:00
5 | Agrabad | 78 | 16:00 | Cumilla(N) | 202 | 21:00 | Khagrachori | 36 | 19:00 | Niamatpur | 99 | 22:00 | Sirajganj | 135 | 21:00
6 | Amnura | 95 | 21:00 | Cumilla(S) | 192 | 22:00 | Khulna | 114 | 19:30 | Noapara | 52 | 21:00 | Sonargaon | 84 | 01:00
7 | Ashuganj | 69 | 00:00 | Daudkandi | 174 | 21:00 | Khulshi | 191 | 18:00 | PHP | 2 | 04:00 | Sreemongol | 69 | 18:30
8 | BIPTC | N/A | N/A | Dhaka | 38 | 13:00 | Kishoreganj | 108 | 12:00 | Pabna | 137 | 22:00 | Sreepur | 69.78 | 11:00
9 | BSRM | 110 | 20:00 | Dhamrai | 128 | 19:00 | Kodda | 306 | 21:00 | Palashbari | 128 | 03:00 | Srinagar | 54.8 | 21:00
10 | Bagerhat | 108 | 20:00 | Dhanmondi | 169 | 13:00 | Kulaura | 38 | 18:30 | Panchagarh | 53 | 21:00 | Sunamganj | 40 | 23:00
11 | Bakulia | 123 | 19:00 | Dohazari | 104 | 19:00 | Kurigram | 62 | 19:00 | Patuakhali | 122 | 01:00 | Sylhet | 158 | 21:00
12 | Banani | 50 | 11:00 | Faridpur | 179 | 19:30 | Kushtia | 154 | 19:30 | Payra | 22.4 | 22:00 | TK | 32.5 | 19:00
13 | Bangabhaban | 28 | 10:00 | Fatullah | 67 | 00:00 | Lalbag | 78 | 13:00 | Postogola | 48 | 00:00 | Tangail | 222 | 22:00
14 | Barapukuria | 67 | 19:00 | Fenchuganj | 42 | 21:00 | Lalmonirhat | 56 | 18:00 | Purbachal | 23 | 00:00 | Thakurgaon | 92 | 20:00
15 | Barguna | 24 | 00:00 | Feni | 156 | 18:30 | Madanganj | 46 | 00:00 | Purbasadipur | 116 | 22:00 | Tongi | 140 | 20:00
16 | Barishal | 134 | 19:00 | GPH | 82 | 13:00 | Madaripur | 127 | 21:00 | Rahanpur_I | 0 | 00:00 | Ullon | 46 | 00:00
17 | Barishal-230 | 94 | 22:00 | Ghorashal | 78 | 23:00 | Madartek | 104 | 00:00 | Rahim | 48 | 17:00 | Uttara | 101 | 15:00
18 | Baroaulia | 72 | 09:00 | Goalpara | 40 | 04:00 | Madunaghat | 69 | 19:00 | Rajbari | 86 | 21:00 | UttaraNew | 42 | 00:00
19 | Baroirhat | 61 | 18:30 | Gollamari | 60 | 19:30 | Magura | 68 | 20:00 | Rajendrapur | 96 | 21:00 | Zigatola | 92 | 20:00
20 | Bashundhara | 199 | 19:00 | Gopalganj | 117.2 | 22:00 | Mahasthangarh | 88 | 22:00 | Rajshahi | 188 | 21:00
21 | BashundharaCement | 6 | 03:00 | Gulshan | 152 | 14:00 | Manikganj | 135 | 20:00 | Rajshahi-230 | 46 | 22:00
22 | Beanibazar | 68 | 21:00 | Halishahar | 86 | 14:00 | Maniknagar | 108 | 15:00 | Ramganj | 128 | 19:30
23 | Benapole | 76 | 21:00 | HaripurSBU | 164 | 13:00 | Matarbari | 47 | 19:30 | Rampur | 33 | 18:30
24 | Bhaluka | 86 | 03:00 | Hasnabad | 117 | 21:00 | Matuail | 72 | 10:00 | Rangamati | 18 | 18:00
25 | Bhandaria | 58 | 21:00 | Hathazari | 85 | 19:00 | Millgate | 82 | 10:00 | Rangpur | 147 | 22:00
26 | Bhangura | 51 | 22:00 | Ishurdi | 86 | 21:00 | Mirpur | 165 | 19:00 | Ruppur | 5.4 | 10:00
27 | Bheramara(GK) | 78 | 21:00 | Jaldhaka | 68 | 09:00 | Mirsorai | 5 | 00:00 | SSM | 16 | 11:00
28 | Bhulta | 241 | 21:00 | Jamalpur | 153 | 19:30 | Mithapukur | 42 | 18:30 | Saidpur | 112 | 11:00
29 | Bog-Sherpur | 70 | 21:00 | Jashore | 164 | 21:00 | Modern | 0 | 00:00 | Satkhira | 143 | 21:00
30 | Bogura | 198 | 21:00 | Jhenaidah | 166 | 19:30 | Mogbazar | 137 | 14:00 | Satmasjid | 141 | 19:00
31 | Borhanuddin | 68 | 22:00 | Joydebpur | 155 | 17:00 | Mongla | 36 | 04:00 | Savar | 175 | 21:00
32 | Brahmanbaria | 172 | 22:00 | Joypurhat | 72 | 21:00 | Motijheel | 50 | 15:00 | Shahjadpur | 116 | 22:00
33 | Cantonment | 169 | 19:00 | Juldah | 24 | 01:00 | Munshiganj | 121 | 00:00 | Shahjibazar | 110 | 23:00
34 | Chandpur | 77.5 | 22:00 | KSRM | 24 | 02:00 | Mymensingh | 258 | 22:00 | Shahmirpur | 47 | 00:00
35 | Chandraghona | 35 | 19:30 | Kabirpur | 284 | 19:00 | Naogaon | 151 | 14:00 | Shariatpur | 94 | 21:00
36 | Chapai | 85 | 01:00 | Kachua | 97 | 19:30 | Narail | 65 | 20:00 | Sherpur | 156 | 22:00
37 | Charsaidpur | 49 | 00:00 | Kallyanpur | 111 | 00:00 | Narinda | 81 | 15:00 | Shikalbaha | 38 | 20:00
38 | Chauddagram | 75 | 20:00 | Kalurghat | 32 | 08:00 | Narshingdi | 177 | 04:00 | Shikalbaha-230 | N/A | N/A
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2023-04-18 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 398 | 18:30 | 383 | 17:00 | Kaliakoir | 385 | 21:00 | 375 | 13:00
| Bhulta | 382 | 18:30 | 368 | 15:00 | Madunaghat_I | 413 | 14:00 | 390 | 04:00
| Bibiana | 404 | 10:00 | 395 | 14:00 | Payra | 413 | 21:00 | 406 | 15:00
| BIPTC | 402 | 06:00 | 389 | 16:00 | Rahanpur_I | 416 | 00:00 | 407 | 21:00
| Gopalganj | 412 | 08:00 | 386 | 21:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 228 | 06:00 | 218 | 17:00 | Hathazari | 236 | 14:00 | 224 | 04:00
| AKSML | 235 | 17:00 | 222 | 04:00 | Ishurdi | 237 | 00:00 | 225 | 21:00
| Aminbazar | 230 | 22:00 | 222 | 16:00 | Jhenaidah | 230 | 15:00 | 212 | 21:00
| Ashuganj | 237 | 00:00 | 229 | 15:00 | Kaliakoir | 228 | 21:00 | 219 | 15:00
| Baghabari | 233 | 00:00 | 222 | 21:00 | Keranigonj | 228 | 18:30 | 219 | 16:00
| Barapukuria | 215 | 05:00 | 206 | 14:00 | Khulna(S) | 239 | 08:00 | 222 | 21:00
| Barishal | 235 | 09:00 | 224 | 19:00 | Madunaghat_I | 238 | 14:00 | 225 | 05:00
| Bheramara | 235 | 00:00 | 22 | 05:00 | Maniknagar | 226 | 08:00 | 22 | 11:00
| Bhulta | 229 | 06:00 | 221 | 15:00 | Meghnaghat | 231 | 14:00 | 228 | 02:00
| Bibiana | 239 | 18:00 | 233 | 05:00 | Mirsorai | 237 | 14:00 | 224 | 09:00
| BIPTC | 236 | 00:00 | 223 | 21:00 | Rajshahi | 233 | 08:00 | 220 | 21:00
| Bogura | 225 | 16:00 | 214 | 22:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 233 | 03:00 | 227 | 18:30 | Rampura | 227 | 00:00 | 220 | 16:00
| BSRM | 236 | 14:00 | 222 | 04:00 | Shikalbaha | 234 | 14:00 | 226 | 10:00
| Cumilla(N) | 232 | 19:00 | 225 | 04:00 | Shyampur | 229 | 21:00 | 220 | 16:00
| Fenchuganj | 242 | 18:30 | 236 | 11:00 | Siddhirganj | 231 | 06:00 | 223 | 13:00
| Ghorashal | N/A | N/A | N/A | N/A | Sirajgonj | 238 | 16:00 | 232 | 21:00
| GPH | 235 | 14:00 | 223 | 04:00 | Sreepur | 233 | 00:00 | 230 | 07:00
| Haripur | 228 | 21:00 | 221 | 13:00 | Tongi | 227 | 21:00 | 217 | 17:00
| Hasnabad | 237 | 10:00 | 220 | 15:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 136 | 00:00 | 128 | 15:00 | Lalbag | 134 | 21:00 | 127 | 17:00
| Agargaon | 134 | 06:00 | 126 | 14:00 | Lalmonirhat | 125 | 04:00 | 112 | 14:00
| Agrabad | 135 | 17:00 | 127 | 23:00 | Madanganj | 134 | 19:00 | 129 | 15:00
| AKS | 134 | 14:00 | 126 | 02:00 | Madaripur | 136 | 07:00 | 126 | 21:00
| Aminbazar | 136 | 00:00 | 123 | 16:00 | Madartek | 137 | 06:00 | 127 | 15:00
| Amnura | 134 | 00:00 | 127 | 21:00 | Madunaghat | 137 | 13:00 | 130 | 18:00
| Ashuganj | 138 | 00:00 | 135 | 12:00 | Magura | 136 | 09:00 | 121 | 21:00
| Bagerhat | 138 | 08:00 | 124 | 20:00 | Mahasthangarh | 131 | 16:00 | 120 | 22:00
| Bakulia | 135 | 13:00 | 128 | 04:00 | Manikganj | 134 | 21:00 | 126 | 09:00
| Banani | 136 | 00:00 | 129 | 13:00 | Maniknagar | 135 | 08:00 | 128 | 13:00
| Bangabhaban | 134 | 03:00 | 128 | 14:00 | Matarbari | 131 | 14:00 | 106 | 18:30
| Barapukuria | 131 | 05:00 | 123 | 13:00 | Matuail | 133 | 19:30 | 128 | 17:00
| Barguna | 138 | 00:00 | 128 | 05:00 | Millgate | 132 | 07:00 | 125 | 16:00
| Barishal | 138 | 00:00 | 125 | 18:30 | Mirpur | 139 | 07:00 | 121 | 16:00
| Barishal-230 | 136 | 08:00 | 127 | 19:30 | Mithapukur | 127 | 04:00 | 117 | 12:00
| Baroaulia | 137 | 14:00 | 130 | 23:00 | Modern | 137 | 14:00 | 128 | 04:00
| Baroirhat | 134 | 00:00 | 125 | 21:00 | Mogbazar | 137 | 06:00 | 130 | 13:00
| Bashundhara | 132 | 05:00 | 125 | 15:00 | Mongla | 136 | 15:00 | 124 | 20:00
| BashundharaCement | 134 | 19:00 | 129 | 15:00 | Motijheel | 134 | 03:00 | 128 | 14:00
| Beanibazar | 133 | 00:00 | 128 | 21:00 | Munshiganj | 135 | 21:00 | 128 | 15:00
| Benapole | 133 | 08:00 | 119 | 21:00 | Mymensingh | 125 | 20:00 | 109 | 16:00
| Bhaluka | 124 | 20:00 | 108 | 16:00 | Naogaon | 126 | 16:00 | 107 | 21:00
| Bhandaria | 134 | 00:00 | 123 | 22:00 | Narail | 134 | 08:00 | 119 | 21:00
| Bhangura | 136 | 00:00 | 127 | 21:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bheramara | 135 | 16:00 | -73 | 00:00 | Narshingdi | 128 | 00:00 | 118 | 19:30
| Bheramara(GK) | 136 | 00:00 | 128 | 21:00 | Natore | 132 | 15:00 | 124 | 21:00
| Bhulta | 126 | 22:00 | 119 | 13:00 | Nawabganj | 133 | 19:30 | 126 | 17:00
| Bog-Sherpur | 133 | 16:00 | 123 | 21:00 | Netrakona | 121 | 07:00 | 108 | 16:00
| Bogura | 134 | 16:00 | 124 | 12:00 | New | 133 | 08:00 | 127 | 13:00
| Bogura-230 | 134 | 16:00 | 124 | 12:00 | Niamatpur | 122 | 16:00 | 96 | 21:00
| Brahmanbaria | 134 | 08:00 | 129 | 13:00 | Noapara | 137 | 15:00 | 125 | 20:00
| Cantonment | 133 | 06:00 | 124 | 17:00 | Pabna | 133 | 11:00 | 125 | 21:00
| Chandpur | 139 | 19:00 | 126 | 07:00 | Palashbari | 126 | 16:00 | 115 | 12:00
| Chandraghona | 137 | 14:00 | 130 | 03:00 | Panchagarh | 125 | 21:00 | 100 | 13:00
| Chapai | 133 | 00:00 | 126 | 22:00 | Patuakhali | 140 | 00:00 | 134 | 12:00
| Charsaidpur | 135 | 19:30 | 129 | 12:00 | Payra | 141 | 00:00 | 137 | 03:00
| Chauddagram | 134 | 17:00 | 125 | 04:00 | PHP | 134 | 17:00 | 122 | 18:00
| Chhatak | 133 | 00:00 | 13 | 22:00 | Postogola | 133 | 06:00 | 127 | 13:00
| Chowmuhani | 134 | 19:00 | 120 | 00:00 | Purbachal | 137 | 07:00 | 124 | 16:00
| Chuadanga | 131 | 15:00 | 113 | 21:00 | Purbasadipur | 125 | 18:30 | 106 | 14:00
| Coxsbazar | 128 | 14:00 | 104 | 18:00 | Rahim | 134 | 18:30 | 130 | 13:00
| Cumilla(N) | 135 | 00:00 | 124 | 20:00 | Rajbari | 133 | 00:00 | 122 | 21:00
| Cumilla(S) | 135 | 19:00 | 125 | 15:00 | Rajendrapur | 136 | 21:00 | 126 | 14:00
| Daudkandi | 135 | 18:30 | 129 | 04:00 | Rajshahi | 133 | 00:00 | 29 | 01:00
| Dhaka | 138 | 06:00 | 129 | 12:00 | Rajshahi-230 | 134 | 19:00 | 125 | 21:00
| Dhamrai | 138 | 00:00 | 126 | 17:00 | Ramganj | 133 | 23:00 | 122 | 05:00
| Dhanmondi | 133.6 | 06:00 | 128 | 13:00 | Rampur | 135 | 14:00 | 128 | 03:00
| Dohazari | 133 | 13:00 | 121 | 21:00 | Rampura | 136 | 03:00 | 129 | 12:00
| Faridpur | 133 | 09:00 | 122 | 20:00 | Rangamati | 136 | 14:00 | 128 | 18:30
| Fatullah | 136 | 21:00 | 129 | 15:00 | Rangpur | 127 | 05:00 | 116 | 12:00
| Fenchuganj | 138 | 00:00 | 134 | 13:00 | Ruppur | 134 | 00:00 | 128 | 21:00
| Feni | 135 | 19:00 | 125 | 04:00 | Saidpur | 124 | 15:00 | 113 | 08:00
| Ghorashal | 139 | 00:00 | 135 | 15:00 | Satkhira | 139 | 08:00 | 121 | 21:00
| Goalpara | 140 | 06:00 | 131 | 12:00 | Satmasjid | 133 | 06:00 | 125 | 15:00
| Gollamari | 136 | 00:00 | 121 | 20:00 | Savar | 135 | 07:00 | 123 | 15:00
| Gopalganj | 139 | 03:00 | 123 | 21:00 | Shahjadpur | 139 | 00:00 | 132 | 22:00
| Gopalganj-400 | 137 | 06:00 | 127 | 20:00 | Shahjibazar | 134 | 00:00 | 131 | 13:00
| Gulshan | 137 | 05:00 | 128 | 12:00 | Shahmirpur | 135 | 14:00 | 126 | 06:00
| Halishahar | 134 | 11:00 | 128 | 05:00 | Shariatpur | 135 | 06:00 | 123 | 21:00
| Haripur | 134 | 18:30 | 130 | 13:00 | Sherpur | 131 | 00:00 | 108 | 01:00
| HaripurSBU | 134 | 18:30 | 130 | 13:00 | Shikalbaha | 136 | 13:00 | 129 | 04:00
| Hasnabad | 132 | 08:00 | 127 | 13:00 | Shikalbaha-230 | 135 | 14:00 | 128 | 23:00
| Hathazari | 138 | 14:00 | 131 | 04:00 | Shitalakhya | 135 | 21:00 | 128 | 15:00
| Ishurdi | 136 | 16:00 | 128 | 21:00 | Sholosohor | 136 | 14:00 | 126 | 04:00
| Jaldhaka | 125 | 04:00 | 110 | 14:00 | Shyampur | 135 | 20:00 | 129 | 16:00
| Jamalpur | 133 | 00:00 | 112 | 06:00 | Shyampur-230 | 136 | 21:00 | 129 | 15:00
| Jashore | 134 | 08:00 | 121 | 21:00 | Siddhirganj | 134 | 21:00 | 129 | 15:00
| Jhenaidah | 137 | 08:00 | 124 | 20:00 | Sirajganj | 133 | 15:00 | 124 | 22:00
| Jhenaidah-230 | 138 | 09:00 | 125 | 21:00 | Sonargaon | 135 | 19:30 | 129 | 15:00
| Joydebpur | 142 | 06:00 | 136 | 16:00 | Sreemongol | 134 | 23:00 | 131 | 13:00
| Joypurhat | 122 | 16:00 | 100 | 22:00 | Sreepur | 130 | 06:00 | 129 | 00:00
| Juldah | 135 | 14:00 | 128 | 04:00 | Srinagar | 134 | 21:00 | 126 | 17:00
| Kabirpur | 136 | 21:00 | 123 | 16:00 | SSM | 140 | 01:00 | 132 | 23:00
| Kachua | 137 | 00:00 | 127 | 04:00 | Sunamganj | 131 | 00:00 | 127 | 14:00
| Kaliakoir | 137 | 07:00 | 131 | 16:00 | Sylhet | 133 | 00:00 | 132 | 01:00
| Kallyanpur | 135 | 07:00 | 124 | 15:00 | Tangail | 133 | 00:00 | 123 | 22:00
| Kalurghat | 137 | 16:00 | 130 | 09:00 | Thakurgaon | 126 | 19:30 | 100 | 14:00
| Kamrangirchar | 134 | 21:00 | 127 | 15:00 | TK | 136 | 13:00 | 130 | 04:00
| Kaptai | 132 | 07:00 | 130 | 00:00 | Tongi | 135 | 23:00 | 127 | 15:00
| Kazla | 134 | 06:00 | 126 | 16:00 | Ullon | 136 | 03:00 | 128 | 15:00
| Keranigonj | 134 | 06:00 | 127 | 15:00 | Uttara | 132 | 06:00 | 120 | 16:00
| Khagrachori | 135 | 14:00 | 128 | 04:00 | UttaraNew | 134 | 07:00 | 121 | 15:00
| Khulna | 140 | 08:00 | 129 | 21:00 | Zigatola | 133 | 06:00 | 126 | 16:00
| Khulna(S) | 141 | 08:00 | 130 | 20:00
| Khulshi | 136 | 14:00 | 126 | 04:00
| Kishoreganj | 130 | 23:00 | 119 | 13:00
| Kodda | 137 | 00:00 | 128 | 13:00
| KSRM | 136 | 17:00 | 129 | 18:00
| Kulaura | 135 | 00:00 | 134 | 04:00
| Kurigram | 124 | 05:00 | 110 | 13:00
| Kushtia | 138 | 15:00 | 32 | 05:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2023-04-18
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 312 | 8509 | 5060 | 13569 |  |  |  | QF-LDC-11
0:30 | 346 | 8283.5 | 5140 | 13423.5 | Date: | 2023-04-18
1:00 | 380 | 8058 | 5220 | 13278
1:30 | 360 | 8004 | 5198.5 | 13202.5
2:00 | 340 | 7950 | 5177 | 13127
2:30 | 340 | 7993.5 | 5256 | 13249.5 | [5 empty] | Gen. at Eve. Peak | 15626 | 15626 MW (21:00 )
3:00 | 340 | 8037 | 5335 | 13372 | [6 empty] | 21:00
3:30 | 405 | 7964.5 | 5336 | 13300.5 | [5 empty] | Gen. at Day Peak | 13307 | 13307 MW (12:00 )
4:00 | 470 | 7892 | 5337 | 13229 | [6 empty] | 12:00
4:30 | 475 | 7818 | 5263 | 13081 | [5 empty] | Highest Generation | 15626
5:00 | 480 | 7744 | 5189 | 12933 | [6 empty] | 21:00
5:30 | 510 | 7390 | 5044.5 | 12434.5
6:00 | 540 | 7036 | 4900 | 11936
6:30 | 610 | 6857 | 4939 | 11796
7:00 | 680 | 6678 | 4978 | 11656
7:30 | 705 | 6808 | 4992 | 11800
8:00 | 730 | 6938 | 5006 | 11944
8:30 | 675 | 7041.5 | 4929 | 11970.5
9:00 | 620 | 7145 | 4852 | 11997
9:30 | 500 | 7378 | 4852 | 12230
10:00 | 380 | 7611 | 4852 | 12463
10:30 | 375 | 7671.5 | 4888.5 | 12560
11:00 | 370 | 7732 | 4925 | 12657
11:30 | 335 | 8016 | 4966 | 12982
12:00 | 300 | 8300 | 5007 | 13307
12:30 | 370 | 8219 | 5074 | 13293
13:00 | 440 | 8138 | 5141 | 13279
13:30 | 445 | 8089.5 | 5175.5 | 13265
14:00 | 450 | 8041 | 5210 | 13251
14:30 | 610 | 7911 | 5244 | 13155
15:00 | 770 | 7781 | 5278 | 13059
15:30 | 855 | 7834 | 5250 | 13084
16:00 | 940 | 7887 | 5222 | 13109
16:30 | 830 | 7955 | 5193.5 | 13148.5
17:00 | 720 | 8023 | 5165 | 13188
17:30 | 655 | 8276.5 | 5263 | 13539.5
18:00 | 590 | 8530 | 5361 | 13891
18:30 | 425 | 8924 | 5365 | 14289
19:00 | 260 | 9318 | 5369 | 14687
19:30 | 168 | 9711 | 5461 | 15172
20:00 | 150 | 9625 | 5579 | 15204 |  |  |  | Executive Engineer
20:30 | 195 | 9740.5 | 5674.5 | 15415 |  |  |  | Network Operation Division
21:00 | 240 | 9856 | 5770 | 15626
21:30 | 225 | 9838 | 5746.5 | 15584.5
22:00 | 210 | 9820 | 5723 | 15543 |  |  |  |  | Page 6 of 7
22:30 | 225 | 9597.5 | 5460.5 | 15058
23:00 | 240 | 9375 | 5198 | 14573
23:30 | 276 | 8942 | 5129 | 14071
24:00 | 312 | 8509 | 5060 | 13569
15626 MW (21:00 )
13307 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2023-04-18 |  | Energy |  | 337827541
[13 empty] | 2023-04-18 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 4031 | 822 | 2433 | 184 | 3183 | 2203 | 0 | 0 | 583 | 130 | 0 | 0
0:30 | 4067.5 | 837.5 | 2384.5 | 331 | 2914 | 2229 | 0 | 0 | 527 | 133 | 0 | 822.255 |  | Date: | 43572
1:00 | 4104 | 853 | 2336 | 478 | 2645 | 2255 | 0 | 0 | 471 | 136 | 0 | 1644.51
1:30 | 4104.5 | 853 | 2348 | 476 | 2578.5 | 2250.5 | 0 | 0 | 457 | 135 | 0 | 1573.3625 | [8 empty] | Total Energy | 337.8275 | Total Energy Gen MKWHr Energy Not Served MKWHr Energy Requirement MKWHr | Total Energy Gen 337.828 MKWHr Energy Not Served 28.098 MKWHr Energy Requirement 365.926 MKWHr
2:00 | 4105 | 853 | 2360 | 474 | 2512 | 2246 | 0 | 0 | 443 | 134 | 0 | 1502.215 | [8 empty] | Energy not Served | 28.0983
2:30 | 4107.5 | 853.5 | 2369 | 474 | 2627.5 | 2245 | 0 | 0 | 440 | 133 | 0 | 1528.4775 | [8 empty] | Energy Requirement | 365.9259
3:00 | 4110 | 854 | 2378 | 474 | 2743 | 2244 | 0 | 0 | 437 | 132 | 0 | 1554.74
3:30 | 4093.5 | 889.5 | 2368.5 | 473.5 | 2663 | 2241.5 | 0 | 0 | 437 | 134 | 0 | 1527.5225 | [7 empty] | Shortage
4:00 | 4077 | 925 | 2359 | 473 | 2583 | 2239 | 0 | 0 | 437 | 136 | 0 | 1500.305
4:30 | 4092.5 | 925.5 | 2354.5 | 430.5 | 2479.5 | 2233 | 0 | 0 | 435.5 | 130 | 0 | 1402.895
5:00 | 4108 | 926 | 2350 | 388 | 2376 | 2227 | 0 | 0 | 434 | 124 | 0 | 1305.485
5:30 | 4087 | 925.5 | 2256 | 194 | 2196.5 | 2226 | 0 | 0 | 428.5 | 120 | 1 | 1495.0525
6:00 | 4066 | 925 | 2162 | 0 | 2017 | 2225 | 0 | 0 | 423 | 116 | 2 | 1684.62
6:30 | 3910.5 | 925.5 | 2149 | 0 | 2016 | 2230.5 | 0 | 0 | 424 | 117 | 23.5 | 1675.07 | [6 empty] | Coal
7:00 | 3755 | 926 | 2136 | 0 | 2015 | 2236 | 0 | 0 | 425 | 118 | 45 | 1665.52
7:30 | 3825.5 | 925.5 | 2228 | 0 | 2013.5 | 2203 | 0 | 0 | 414.5 | 118 | 72 | 1671.25 | [5 empty] | Oil
8:00 | 3896 | 925 | 2320 | 0 | 2012 | 2170 | 0 | 0 | 404 | 118 | 99 | 1676.98
8:30 | 3981.5 | 924.5 | 2314 | 0 | 2006 | 2091.5 | 0 | 0 | 405 | 123 | 125 | 1699.4225
9:00 | 4067 | 924 | 2308 | 0 | 2000 | 2013 | 0 | 0 | 406 | 128 | 151 | 1721.865
9:30 | 4026.5 | 924 | 2304.5 | 215 | 2024 | 1977 | 0 | 4 | 407 | 130 | 218 | 1594.85
10:00 | 3986 | 924 | 2301 | 430 | 2048 | 1941 | 0 | 8 | 408 | 132 | 285 | 1467.835
10:30 | 3965 | 924.5 | 2300.5 | 325 | 2176 | 1966 | 12.5 | 50.5 | 399.5 | 132 | 308.5 | 1470.7
11:00 | 3944 | 925 | 2300 | 220 | 2304 | 1991 | 25 | 93 | 391 | 132 | 332 | 1473.565
11:30 | 3931.5 | 925 | 2290.5 | 332.5 | 2464.5 | 2010 | 25 | 113.5 | 391.5 | 136 | 362 | 1258.69
12:00 | 3919 | 925 | 2281 | 445 | 2625 | 2029 | 25 | 134 | 392 | 140 | 392 | 1043.815
12:30 | 3905.5 | 925 | 2255 | 457.5 | 2566 | 2037.5 | 25 | 214.5 | 390 | 138 | 379 | 1142.18
13:00 | 3892 | 925 | 2229 | 470 | 2507 | 2046 | 25 | 295 | 388 | 136 | 366 | 1240.545
13:30 | 3892 | 925 | 2229 | 470 | 2507 | 2046 | 25 | 295 | 388 | 136 | 366 | 1240.545
14:00 | 3892 | 925 | 2229 | 470 | 2507 | 2046 | 25 | 295 | 388 | 136 | 366 | 1240.545
14:30 | 3873 | 922.5 | 2245 | 260 | 2577 | 2103 | 25 | 311.5 | 398.5 | 143 | 310.5 | 1403.85
15:00 | 3854 | 920 | 2261 | 50 | 2647 | 2160 | 25 | 328 | 409 | 150 | 255 | 1567.155
15:30 | 3869 | 920.5 | 2323.5 | 25 | 2667.5 | 2161 | 25 | 333 | 407.5 | 147 | 205 | 1471.655
16:00 | 3884 | 921 | 2386 | 0 | 2688 | 2162 | 25 | 338 | 406 | 144 | 155 | 1376.155
16:30 | 3899 | 921 | 2397.5 | 0 | 2772.5 | 2161.5 | 25 | 293.5 | 431.5 | 138 | 109 | 1147.4325
17:00 | 3914 | 921 | 2409 | 0 | 2857 | 2161 | 25 | 249 | 457 | 132 | 63 | 918.71
17:30 | 3924.5 | 921.5 | 2421.5 | 0 | 3208.5 | 2158.5 | 25 | 239 | 470.5 | 135 | 35.5 | 702.4025
18:00 | 3935 | 922 | 2434 | 0 | 3560 | 2156 | 25 | 229 | 484 | 138 | 8 | 486.095
18:30 | 3907.5 | 921 | 2417 | 181 | 3806.5 | 2172.5 | 25 | 229 | 486.5 | 139 | 4 | 511.88
19:00 | 3880 | 920 | 2400 | 362 | 4053 | 2189 | 25 | 229 | 489 | 140 | 0 | 537.665
19:30 | 4005 | 850 | 2418 | 567 | 4137 | 2197 | 25 | 329 | 508 | 136 | 0 | 505.6725
20:00 | 4004 | 849 | 2402 | 467 | 4222 | 2198 | 25 | 329 | 570 | 138 | 0 | 473.68
20:30 | 4026 | 849.5 | 2420 | 518 | 4291.5 | 2196 | 25 | 359 | 593 | 137 | 0 | 477.9775
21:00 | 4048 | 850 | 2438 | 569 | 4361 | 2194 | 25 | 389 | 616 | 136 | 0 | 482.275
21:30 | 4026.5 | 850 | 2449 | 564 | 4386 | 2196 | 25 | 345 | 605 | 138 | 0 | 459.355
22:00 | 4005 | 850 | 2460 | 559 | 4411 | 2198 | 25 | 301 | 594 | 140 | 0 | 436.435
22:30 | 4012 | 836 | 2460 | 514 | 4144.5 | 2196.5 | 12.5 | 150.5 | 592 | 140 | 0 | 732.485
23:00 | 4019 | 822 | 2460 | 469 | 3878 | 2195 | 0 | 0 | 590 | 140 | 0 | 1028.535
23:30 | 4025 | 822 | 2446.5 | 326.5 | 3530.5 | 2199 | 0 | 0 | 586.5 | 135 | 0 | 1340.82 |  | Max Temp. in Dhaka |  | 37.1° C
24:00 | 4031 | 822 | 2433 | 184 | 3183 | 2203 | 0 | 0 | 583 | 130 | 0 | 1653.105
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 337.828 MKWHr Energy Not Served 28.098 MKWHr Energy Requirement 365.926 MKWHr
Shortage
Note on W13: Author:

## Generation
g | 2023-04-18
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | [10 empty] | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 0 |  | 307080
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2200000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 18 | 25 | 25 | 23 | 25 | 25 | 25 | 25 | 17 | 17 | 17 | 17 | 17 | 17 | 21 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 548199
| Teknaf 20MW PP (Solartech) |  |  |  |  | 0 | 0 | 0 | 5 | 7 | 12 | 13 | 19 | 17 | 15 | 12 | 7 | 3 | 0 | [8 empty] | 100440
6 | Sikalbaha 225MW CCPP (Gas) | 228 | 223 | 224 | 224 | 228 | 228 | 225 | 225 | 223 | 224 | 226 | 225 | 225 | 227 | 221 | 223 | 222 | 221 |  | 226 | 226 | 226 | 226 | 225 | 228 | 228 | 5350301
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 66 | 66 | 49 | 49 | 51 | 50 | 48 | 48 | 65 | 66 |  | 66 | 66 | 66 | 66 | 67 | 67 | 67 | 1478023
12 | Hathazari 100 MW peaking PP | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 35 | 35 | 44 | 44 | 36 | 45 | 45 | 30 | 38 | 57 | 60 |  | 60 | 60 | 60 | 63 | 54 | 54 | 48 | 1061424
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 51 | 68 | 68 | 68 | 92 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 76 | 1422655
| Daudkandi 200 MW PP (B.Trac) | 129 | 127 | 126 | 125 | 100 | 0 |  |  |  | 114 | 50 | 115 | 126 | 120 | 10 | 0 |  | 0 |  | 118 | 128 | 129 | 129 | 129 | 130 | 30 | 1824384
14 | Titas 50 MW Peaking PP | 37 | 39 | 39 | 38 | 38 | 39 | 39 | 39 | 39 | 44 | 37 | 35 | 35 | 35 | 35 | 42 | 42 | 42 |  | 42 | 42 | 43 | 44 | 44 | 44 | 42 | 961760
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 65 | 65 | 65 | 65 | 64 | 64 | 93 | 93 | 95 | 83 | 80 | 62 | 79 | 81 | 63 | 47 | 63 | 64 |  | 34 | 37 | 36 | 35 | 38 | 40 | 40 | 1634000
17 | Siddhirganj 335 MW CCPP | 218 | 217 | 218 | 218 | 220 | 220 | 180 | 170 | 218 | 214 | 211 | 214 | 212 | 209 | 209 | 210 | 208 | 208 |  | 215 | 215 | 216 | 216 | 213 | 213 | 215 | 5141130
18 | Kodda 300 MW PP Unit-2 (Summit) | 158 | 91 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 95 | 124 | 264 | 130 | 95 | 95 | 97 | 97 | 135 |  | 273 | 275 | 265 | 270 | 281 | 291 | 287 | 3783545
19 | Ashuganj 195MW PP (APSCL-United) | 184 | 184 | 184 | 184 | 184 | 184 | 184 | 184 | 184 | 167 | 167 | 167 | 167 | 163 | 163 | 163 | 163 | 163 |  | 180 | 153 | 155 | 155 | 155 | 155 | 155 | 4131636
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4268250
24
25 | Ghorasal 365 MW CCPP Unit-7 | 120 | 120 | 120 | 120 | 120 | 120 | 0 | 60 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2637900
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 44 | 44 | 43 | 43 | 43 | 43 | 43 | 42 | 37 | 39 | 34 | 36 | 33 | 34 | 32 | 34 | 34 | 37 |  | 39 | 40 | 40 | 41 | 42 | 42 | 43 | 933048
33 | Ashuganj 225 MW CCPP | 186 | 178 | 176 | 173 | 164 | 165 | 193 | 204 | 198 | 199 | 208 | 206 | 200 | 202 | 203 | 204 | 203 | 205 |  | 204 | 206 | 204 | 204 | 198 | 193 | 190 | 4709000
34 | Ashuganj 450 MW CCPP(South) | 345 | 335 | 350 | 335 | 350 | 310 | 280 | 280 | 320 | 305 | 305 | 305 | 305 | 305 | 305 | 305 | 325 | 315 |  | 350 | 350 | 345 | 350 | 340 | 350 | 350 | 7917000
| Ashuganj 450 MW CCPP(North) | [26 empty] | 0
Ashuganj 420 MW CCPP(East)
35 | Ashuganj 55 MW PP (Precision)
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 397 | 398 | 398 | 397 | 398 | 390 | 344 | 359 | 395 | 395 | 393 | 396 | 396 | 396 | 398 | 399 | 396 | 396 |  | 395 | 403 | 396 | 394 | 394 | 394 | 394 | 9535490
40 | Meghnaghat 450 MW CCPP(MPL) | 450 | 450 | 450 | 450 | 450 | 400 | 370 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 |  | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 10065000
41 | Haripur 360MW CCPP(HPL) | 330 | 330 | 330 | 330 | 330 | 330 | 285 | 330 | 333 | 334 | 334 | 334 | 321 | 321 | 321 | 321 | 322 | 328 |  | 333 | 333 | 334 | 330 | 330 | 330 | 330 | 7760000
42 | RPCL 210MW CCPP | 93 | 93 | 94 | 82 | 87 | 86 | 33 | 33 | 34 | 21 | 21 | 16 | 21 | 31 | 31 | 31 | 31 | 31 |  | 50 | 60 | 59 | 94 | 93 | 94 | 82 | 1271040
43 | Sutiakhali 50 MW Solar PP |  |  |  |  | 0 | 1 | 0 |  | 21 | 36 | 38 | 41 | 36 | 37 | 27 | 18 | 7 | 1 |  | 0 | [6 empty] | 274670
44 | Fenchugonj CCPP Phase-1 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 33 | 32 | 34 | 32 | 33 | 32 |  | 33 | 33 | 32 | 32 | 33 | 34 | 34 | 788000
45 | Fenchugonj CCPP Phase-2 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 911520
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 60 | 61 | 61 | 60 | 60 | 62 | 61 | 61 | 61 | 60 | 61 | 60 | 60 | 60 | 58 | 59 | 58 | 60 |  | 61 | 60 | 61 | 60 | 60 | 60 | 60 | 1336928
48 | Shahjibazar 86MW PP (Shahjibazar) | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 84 | 84 | 83 | 82 | 82 | 82 | 82 | 83 | 83 |  | 83 | 83 | 83 | 83 | 84 | 84 | 84 | 2016000
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 205 | 204 | 202 | 202 | 202 | 202 | 202 | 202 | 203 | 201 | 201 | 199 | 195 | 192 | 196 | 196 | 196 | 195 |  | 196 | 197 | 198 | 200 | 203 | 200 | 199 | 4075400
51 | Sylhet 20 MW GTPP | 17 | 17 | 17 | 17 | 18 | 18 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 18 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 409000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 232920
54 | Hobiganj 11MW PP Cofidence-E | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 5 | 8 | 8 | 189408
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 50 | 50 | 50 | 53 | 48 | 53 | 53 | 53 | 53 | 53 | 53 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 1262400
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 379152
57 | Bibiana-II 341 MW CCPP (Summit) | 260 | 270 | 275 | 265 | 260 | 265 | 265 | 270 | 260 | 275 | 280 | 275 | 275 | 270 | 270 | 275 | 275 | 280 |  | 280 | 280 | 275 | 275 | 280 | 275 | 270 | 6593500
| Bibiyana South 400 MW | 390 | 390 | 400 | 390 | 400 | 400 | 370 | 400 | 400 | 395 | 397 | 395 | 384 | 377 | 370 | 388 | 377 | 380 |  | 318 | 395 | 394 | 393 | 390 | 382 | 390 | 9296200
58 | Nababganj 55 MW PP (Southern power ) | 17 | 17 | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 55 |  | 55 | 55 | 55 | 55 | 35 | 35 | 35 | 890057
59 | Tangail Palli Power Gen 22 MW | 23 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 25 | 25 | 25 | 25 | 25 | 20 | 25 | 593520
60 | Barabkunda 22 MW PP (Regent) | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 |  | 14 | 14 | 15 | 14 | 14 | 12 | 12 | 313296
61 | Narshingdi 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 0 | 19 | 19 | 19 | 19 | 19 |  |  | 0 | 19 | 19 | 19 |  | 0 | [5 empty] | 19 | 285516
62 | Tangail 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 15 | 15 | 15 | 15 | 15 | 14 | 14 | 14 | 14 |  | 15 | 15 | 15 | 15 | 15 | 15 | 18 | 376820
63 | Impoprt (Tripura) | 136 | 134 | 132 | 136 | 124 | 116 | 118 | 118 | 128 | 132 | 132 | 140 | 136 | 140 | 150 | 144 | 132 | 138 |  | 140 | 136 | 138 | 136 | 140 | 140 | 130 | 3254400
64 | Malancha, Ctg. EPZ (United) | 17 | 34 | 35 | 36 | 36 | 35 | 10 | 4 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 7 | 10 | 20 |  | 29 | 28 | 17 | 15 | 17 | 22 | 28 | 391680
65 | Feni 22MW PP (Doreen) | 18 | 18 | 0 | [5 empty] | 9 | 16 | 17 | 17 | 16 | 17 | 17 | 16 | 16 | 17 |  | 16 | 16 | 16 | 18 | 18 | 16 | 16 | 280404
66 | Feni 11 MW PP (Doreen) | 9 | 9 | 0 | 0 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 8 | 8 | 8 | 9 | 9 | 7 | 7 |  | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 196560
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 32 | 32 | 32 | 32 | 32 | 30 | 31 | 31 | 31 | 30 | 31 |  | 30 | 30 | 30 | 32 | 32 | 32 | 33 | 777300
68 | Cumilla 25 MW PP (Summit) | 15 | 20 | 20 | 20 | 15 | 15 | 15 | 9 | 18 | 19 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 435890
69 | Summit Ashulia | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 |  | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 552000
70 | Summit Madhabdi | 19 | 11 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 18 | 18 | 18 | 18 | 19 | 18 | 23 | 23 |  | 12 | 23 | 23 | 23 | 16 | 16 | 22 | 426060
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 775900
72 | Rupganj 33 MW PP(Summit) | 31 | 32 | 32 | 32 | 32 | 32 | 32 | 31 | 30 | 30 |  | 12 | 17 | 26 | 26 | 26 | 26 | 26 |  | 28 | 30 | 30 | 32 | 16 | 16 | 31 | 623800
73 | Ghorashal 108MW PP (Regent) | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 68 | 68 | 68 | 68 | 66 | 71 | 71 | 71 | 71 | 71 | 72 |  | 74 | 74 | 74 | 74 | 74 | 75 | 75 | 1673772
| Feni Lanka Power | 114 | 114 | 114 | 114 | 114 | 0 | [8 empty] | 0 | 34 | 58 | 100 |  | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 1448940
| Chowmuhani 113 MW | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 5 | 12 | 9 | 9 | 9 | 9 | 9 | 55 | 53 |  | 103 | 104 | 100 | 109 | 113 | 73 | 9 | 691320
| Manikgonj 162MW PP(MPGL) | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 90 | 90 | 108 | 108 | 108 | 108 | 108 | 108 | 108 |  | 162 | 162 | 162 | 162 | 162 | 162 | 108 | 2322720
77 | Siddhirganj 100 PP(Dutch Bangla) | 55 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 65 | 72 | 72 | 72 | 75 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 85 | 85 | 85 | 1522560
78 | Gazipur 52 MW PP | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 43 | 41 | 41 | 41 | 41 | 39 | 39 | 39 | 39 | 39 |  | 39 | 48 | 48 | 48 | 48 | 48 | 48 | 1067040
79 | Kodda 150 MW PP | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 62 | 62 | 62 | 62 |  | 64 | 82 | 146 | 146 | 146 | 146 | 146 | 1401120
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 52 | 52 | 52 | 0 | [10 empty] | 6 | 13 | 49 | 52 |  | 43 | 43 | 44 | 52 | 52 | 52 | 52 | 571800
| Gazipur 100 MW PP | 105 | 105 | 105 | 105 | 105 | 90 | 88 | 88 | 88 | 88 | 88 | 88 | 105 | 85 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2377123
| Kaptai 7 MW Solar PP |  |  |  |  | 0 | 0 | 1 | 1 | 3 | 2 | 4 | 4 | 4 | 3 | 2 | 1 | 1 | 0 | [8 empty] | 26039
| Jodiac Power | 17 | 17 | 23 | 36 | 36 | 36 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 46 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 778257
| Karnaphuli Power Ltd. | 59 | 54 | 61 | 54 | 54 | 37 | 52 | 54 | 54 | 54 | 58 | 68 | 68 | 72 | 86 | 86 | 86 | 107 |  | 107 | 107 | 107 | 107 | 105 | 105 | 64 | 1785628
82 | Madanganj 102 PP(Summit) | 51 | 51 | 51 | 60 | 70 | 88 | 95 | 95 | 95 | 95 | 92 | 92 | 90 | 90 | 88 | 88 | 88 | 92 |  | 95 | 95 | 95 | 95 | 85 | 85 | 85 | 1907349
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [23 empty] | 2 | 7 | 12 | 24124
86 | Meghnaghat CCPP ( Summit) | 307 | 304 | 311 | 305 | 310 | 288 | 311 | 313 | 305 | 305 | 295 | 305 | 300 | 290 | 300 | 300 | 305 | 307 |  | 276 | 307 | 285 | 325 | 326 | 324 | 295 | 7293091
87 | Meghnaghat 100 MW(IEL) | 60 | 41 | 42 | 42 | 41 | 42 | 41 | 42 | 41 | 61 | 74 | 88 | 90 | 89 | 88 | 89 | 88 | 82 |  | 81 | 89 | 85 | 89 | 90 | 84 | 48 | 1604160
| Meghnaghat 104 MW PP (OPCL) | 72 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 52 | 53 | 53 | 53 | 52 | 68 | 72 | 71 | 72 | 75 |  | 89 | 90 | 90 | 88 | 87 | 72 | 55 | 1560960
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 70 | 70 | 70 | 70 | 67 | 67 | 67 | 66 | 66 | 55 | 55 | 66 | 64 | 64 | 64 | 64 | 64 | 77 |  | 77 | 77 | 77 | 77 | 77 | 77 | 66 | 1628280
92 | Fenchuganj 44MW (Energyprima) | 47 | 48 | 48 | 48 | 48 | 47 | 47 | 44 | 46 | 46 | 43 | 43 |  |  | 40 | 45 | 45 | 44 |  | 44 | 45 | 45 | 45 | 46 | 47 | 47 | 999648
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 43 | 43 | 51 | 51 | 51 | 51 | 51 | 43 | 43 | 43 | 43 | 43 | 51 | 51 |  | 43 | 43 | 43 | 43 | 51 | 51 | 51 | 1048182
94 | Gagnagar 102 MW PP (Digital Power) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 58 | 58 | 66 | 66 | 66 | 66 | 75 |  | 82 | 82 | 82 | 91 | 91 | 50 | 50 | 1439424
95 | Patenga 50MW PP (Baraka) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 18 | 25 | 25 | 25 | 25 | 26 | 26 | 28 | 39 |  | 39 | 39 | 39 | 39 | 39 | 39 | 6 | 504960
96 | Chattogram 108 MW PP (ECPV) | [17 empty] | 50 |  | 51 | 51 | 51 | 52 | 53 | 0 |  | 261120
97 | katpotti 52 MW
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 14 | 14 | 14 | 14 | 14 | 15 | 15 | 15 | 15 |  | 15 | 55 | 45 | 55 | 55 | 15 | 6 | 479088
100 | Manikganj 55 MW PP (Northern) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 55 | 55 | 55 | 35 | 35 | 891436
101 | Kushiara 163 MW CCPP (KP) | [14 empty] | 0 | 112 | 112 | 112 |  | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 884454
102 | Sarishabari 3 MW Solar Plant |  |  |  |  | 0 | 0 | 0 | 1 | 1 | 2 | 2 | 2 | 1 | 2 | 2 | 1 | 0 | 0 | [8 empty] | 11700
103 | Kamalaghat 54 MW PP(Banco Energy) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 35 | 17 | 648000
104 | Keranigonj 300 MW PP (APR) | 301 | 299 | 300 | 300 | 240 | 0 |  |  |  | 266 | 120 | 280 | 294 | 260 | 40 | 0 |  | 0 |  | 120 | 300 | 254 | 295 | 292 | 231 | 104 | 4195787
105 | Bramhangoan 100 MW PP (Aggreko) | 48 | 48 | 48 | 48 | 48 | 0 |  |  |  | 50 | 50 | 50 | 50 | 50 | 0 |  |  | 0 |  | 50 | 65 | 40 | 70 | 68 | 48 | 25 | 855967
106 | Mymensingh 200 MW PP (United) | 47 | 47 | 57 | 57 | 47 | 47 | 47 | 47 | 48 | 48 | 99 | 125 | 143 | 145 | 145 | 117 | 117 | 162 |  | 163 | 164 | 164 | 164 | 164 | 165 | 165 | 2534400
112 | Aurahati 100MW PP (Aggreko) | [17 empty] | 0 |  | 74 | 74 | 44 | 75 | 70 | 60 | 25 | 343272
114 | Kodda 149 MW PP Unit-1 (Summit) | 33 | 52 | 121 | 131 | 97 | 34 | 34 | 25 | 34 | 34 | 45 | 119 | 72 | 34 | 33 | 34 | 36 | 120 |  | 132 | 132 | 132 | 148 | 149 | 77 | 34 | 17821290
115 | Juldah 100 MW PP Unit-3 (Acorn) | 50 | 50 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 62 | 50 | 50 | 62 | 62 | 62 | 62 | 80 |  | 100 | 100 | 100 | 100 | 100 | 100 | 88 | 1462080
116 | Chandpur 200MW (Desh energy) | 193 | 192 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 191 | 193 | 191 | 192 |  | 193 | 193 | 192 | 192 | 192 | 192 | 192 | 4624800
117 | Ashuganj 150MW PP (Midland) | 150 | 150 | 150 | 63 | 46 | 51 | 51 | 55 | 51 | 53 | 51 | 50 | 40 | 48 | 50 | 50 | 60 | 112 |  | 130 | 133 | 130 | 147 | 149 | 150 | 150 | 2166181
118 | Bibiyana-III 400 MW CCPP | 390 | 403 | 395 | 403 | 401 | 401 | 377 | 402 | 403 | 367 | 367 | 367 | 368 | 367 | 369 | 367 | 383 | 380 |  | 400 | 400 | 404 | 403 | 400 | 402 | 372 | 9312000
| Jamalpur 115 MW PP (United) | 49 | 49 | 69 | 68 | 49 | 49 | 49 | 49 | 49 | 71 | 78 | 68 | 78 | 77 | 77 | 49 | 49 | 75 |  | 105 | 95 | 96 | 97 | 107 | 107 | 107 | 1695600
| Anwara 300 MW PP (United) | 88 | 88 | 88 | 88 | 87 | 87 | 88 | 88 | 88 | 88 | 121 | 122 | 124 | 124 | 124 | 124 | 124 | 124 |  | 224 | 224 | 226 | 228 | 228 | 228 | 87 | 3051055
| Juldah unit-2 (Acorn) | 50 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 88 |  | 88 | 88 | 88 | 88 | 88 | 77 | 77 | 1385280
| Anlima Energy Ltd. | 107 | 107 | 107 | 107 | 107 | 94 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 |  | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 2568055
| Bhairob 54.5 MW | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 6 | 35 | 35 | 35 | 850320
| Spectra Solar Plant Ltd. |  |  |  |  | 0 | 0 | 4 | 11 | 17 | 25 | 29 | 30 | 28 | 25 | 19 | 12 | 6 | 1 |  | 0 | [6 empty] | 202855
| Chandpur 115(Doreen) | 81 | 63 | 35 | 36 | 36 | 35 | 36 | 36 | 36 | 35 | 53 | 62 | 89 | 92 | 92 | 92 | 92 | 93 |  | 93 | 93 | 93 | 93 | 93 | 93 | 87 | 1656000
| Kanchan Purbachal Power Generation Ltd. | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 26 | 35 | 33 | 27 | 36 | 34 | 48 | 52 |  | 53 | 54 | 54 | 54 | 54 | 53 | 17 | 956520
| Mirsharai 150 MW (Oil) | [9 empty] | 8 | 93 | 134 | 145 | 145 | 153 | 163 | 74 | 54 |  | 54 | 54 | 54 | 54 | 26 | 0 |  | 1179272
Mirsharai 150 MW (Gas)
120 | Eastern Zone Total | 8058 | 7950 | 8037 | 7892 | 7744 | 7036 | 6678 | 6938 | 7145 | 7611 | 7732 | 8300 | 8138 | 8041 | 7781 | 7887 | 8023 | 8530 |  | 9318 | 9711 | 9625 | 9856 | 9820 | 9375 | 8509 | 210692635
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | 98 | 82 | 98 | 98 | 97 | 98 | 98 | 98 | 96 | 72 | 71 | 77 | 81 | 81 | 61 | 61 | 61 | 78 |  | 79 | 79 | 79 | 85 | 98 | 98 | 98 | 2010240
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL) | [12 empty] | 150 | 175 | 175 | 175 | 175 | 175 |  | 175 | 175 | 175 | 175 | 175 | 0 |  | 1678916
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 15 | 15 | 15 | 15 | 16 | 16 | 16 | 16 | 19 | 19 | 20 | 17 | 11 | 15 | 12 | 15 | 17 | 19 |  | 19 | 19 | 29 | 24 | 24 | 24 | 22 | 389280
| Khulna 225 MW CCPP | [19 empty] | 0 | 100 | 100 | 160 | 100 | 0 |  | 383715
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 942240
130 | Mongla Orion 100 MW Solar PP |  |  |  |  | 0 | 1 | 14 | 33 | 56 | 72 | 83 | 85 | 82 | 71 | 53 | 33 | 14 | 2 |  | 0 | [6 empty] | 597600
131 | Rampal 1320 MW (BIFPCL)
132 | United Payra Power Ltd. | 150 | 150 | 150 | 150 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 1916400
133 | Bhola Nutan Biddut BD LTD (GAS)
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 64 | 110 | 110 | 16 | 16 | 609984
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 167 | 169 | 159 | 168 | 168 | 156 | 154 | 162 | 164 | 170 |  | 151 | 162 | 170 | 170 | 170 | 170 | 168 | 4011140
140 | Bhola 33 MW PP (Venture) | 36 | 35 | 35 | 35 | 31 | 29 | 26 | 24 | 23 | 23 | 24 | 25 | 27 | 29 | 29 | 25 | 29 | 29 |  | 34 | 34 | 34 | 35 | 37 | 37 | 37 | 737042
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali) | 32 | 32 | 32 | 32 | 32 | 0 | 32 | 32 | 32 | 32 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 32 | 32 | 32 | 32 | 32 | 675750
143 | Gopalganj 100 MW Peaking PP | 66 | 66 | 66 | 66 | 62 | 62 | 62 | 48 | 48 | 48 | 48 | 48 | 25 | 21 | 26 | 26 | 40 | 59 |  | 60 | 61 | 61 | 72 | 65 | 67 | 66 | 1250048
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | 105 | 105 | 105 | 0 | [22 empty] | 370080
146 | Bheramara HVDC | 853 | 853 | 854 | 925 | 926 | 925 | 926 | 925 | 924 | 924 | 925 | 925 | 925 | 924 | 920 | 921 | 921 | 922 |  | 920 | 850 | 849 | 850 | 850 | 822 | 822 | 21674181
147 | Bheramara 410 MW CCPP | 235 | 230 | 230 | 230 | 225 | 225 | 225 | 225 | 220 | 215 | 215 | 200 | 200 | 200 | 195 | 195 | 190 | 190 |  | 190 | 190 | 190 | 190 | 190 | 200 | 205 | 5305824
148 | Payra 1320 MW | 1244 | 1244 | 1244 | 1244 | 1244 | 1244 | 1244 | 1244 | 1244 | 1244 | 1244 | 1244 | 1232 | 1222 | 1222 | 1224 | 1222 | 1222 |  | 1232 | 1244 | 1244 | 1244 | 1244 | 1244 | 1244 | 31530600
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 250 | 240 | 240 | 240 | 240 | 240 | 240 | 248 | 220 | 220 | 200 | 200 | 200 | 200 | 178 | 180 | 180 | 180 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 5092000
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 27 | 27 |  | 27 | 27 | 27 | 20 | 20 | 14 | 14 | 633808
| Sirajgonj 6.55 MW Solar |  |  |  |  | 0 | 0 | 0 | 1 | 1 | 3 | 4 | 5 | 4 | 4 | 3 | 1 | 0 | 0 | [8 empty] | 31080
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 197 | 195 | 193 | 190 | 189 | 188 | 187 | 187 | 171 | 181 | 174 | 173 | 169 | 166 | 166 | 164 | 161 | 158 |  | 156 | 156 | 157 | 159 | 160 | 161 | 161 | 4389345
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 136 | 156 | 167 | 171 | 178 | 183 | 183 | 183 | 184 | 184 | 182 | 176 | 174 | 170 | 168 | 169 | 169 | 169 |  | 168 | 168 | 168 | 168 | 169 | 170 | 170 | 4392455
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 414 | 414 | 418 | 414 | 417 | 300 | 346 | 416 | 421 | 417 | 421 | 414 | 414 | 414 | 414 | 414 | 414 | 414 |  | 381 | 395 | 414 | 414 | 414 | 414 | 415 | 9675054
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | 40 | 10 | 12 | 12 | 12 | 0 |  |  |  |  | 4 | 4 | 20 | 27 | 28 | 28 | 28 | 30 |  | 32 | 32 | 21 | 28 | 22 | 22 | 22 | 341807
162 | Bogra 22 MW PP (GBB) | 20 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 20 | 19 | 18 | 16 | 14 | 13 | 13 | 15 | 16 | 18 |  | 18 | 18 | 18 | 19 | 21 | 21 | 21 | 440640
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 159660
165 | Amnura 50 MW PP(Sinha) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 14 | 14 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 474900
166 | Katakhali 50 MW PP (Northern) | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 34 | 34 | 34 | 34 | 25 | 25 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 883070
167 | Katakhali 50 MW Peaking PP | 32 | 32 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 27 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 42 | 40 | 40 | 40 | 695340
168 | Santahar 50 MW Peaking PP | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 33 | 33 | 34 | 34 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 31 | 31 | 31 | 31 | 31 | 767650
169 | Natore 52 MW PP (Rajlanka) | [17 empty] | 8 |  | 8 | 8 | 43 | 43 | 43 | 8 | 0 | 131112
170 | Chapainawabganj 100 MW Peaking PP | 77 | 77 | 77 | 78 | 78 | 78 | 80 | 80 | 80 | 70 | 69 | 69 | 67 | 67 | 67 | 46 | 46 | 46 |  | 46 | 46 | 46 | 80 | 81 | 81 | 85 | 1683032
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 35 | 35 | 57 | 94 | 95 | 50 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 77 | 95 | 95 | 95 |  | 95 | 95 | 95 | 95 | 95 | 95 | 50 | 1590240
172 | Confidence Power Bogura Unit-1 113 MW | 35 | 35 | 90 | 95 | 95 | 55 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 90 | 95 | 95 | 95 |  | 95 | 95 | 95 | 95 | 95 | 95 | 57 | 1570176
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3000
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 34 | 34 | 92 | 93 | 92 | 48 | 34 | 34 | 35 | 35 | 36 | 42 | 42 | 42 | 80 | 90 | 90 | 92 |  | 92 | 92 | 92 | 92 | 92 | 92 | 49 | 1552992
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1 | 2 | 3 | 5 | 5 | 6 | 6 | 7 | 5 | 3 | 1 | 0 | [8 empty] | 42285
178 | Energypac Power Venture Thakurgaon Ltd. | [17 empty] | 35 |  | 45 | 73 | 75 | 111 | 115 | 17 | 0 | 411840
| Intraco Solar 30 MW |  |  |  |  | 0 | 0 | 4 | 5 | 7 | 22 | 20 | 30 | 26 | 26 | 19 | 11 | 4 | 1 |  | 0 | [6 empty] | 183114
| Adani Power Jharkhanda Ltd | 761 | 762 | 760 | 755 | 743 | 741 | 752 | 678 | 549 | 477 | 547 | 585 | 614 | 745 | 760 | 758 | 759 | 754 |  | 757 | 753 | 754 | 750 | 754 | 751 | 759 | 16863636
178 | Teesta Solar Limited |  |  |  |  | 0 | 0 | 21 | 40 | 35 | 106 | 134 | 170 | 162 | 115 | 113 | 68 | 27 | 3 |  | 0 | [6 empty] | 1043630