## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2023-04-25 | Tuesday
|  | Date (day): | 2023-04-25 |  | Tuesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13294.6 | MW |  |  | (b) At Evening Peak Hour : |  | 15462 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2023-04-24 | 2023-04-25 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 120 | 160 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 12 | 16 | 64 |  | 44 | Engine problem
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 344 | 398 | 400 | 400
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 275 | 334 | 300 | 330
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 320 | 450 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 0 | 0 | 16 | 50 |  | 50 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 301 | 298 | 300 | 300 |  |  | FGMO
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 0 | 0 | 90 | 90 |  | 12 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 0 | 0 | 15 | 15 | 40 |  | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 14 | 19 | 19
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 62 | 39 | 90 | 100 |  | 110 | GT-1 Under maint
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 0 | 0 | 50 | 50 |  | 50 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 100 | 208 | 218 | 218 |  | 117 | ST under S/D
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 48 | 92 |  | 10 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 0 | 35 | 54 |  |  | Fuel shortage
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 0 | 145 | 145
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 35 | 35 | 20 |  | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 35 | 35 | 20 |  | Fuel shortage
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 23 | 23 | 46 | 46 |  | 34 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 17 | 17 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 12 | 11 | 32 | 32
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 0 | 0 | 48 | 48
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 0 | 300 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 300 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 0 | 0 | 50 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 80 |  | 20 | Engine problem
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 0 | 0 | 35 | 70 | 79 |  | Fuel shortage
36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105
37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 0 | 17 | 54 | 90 |  | 14 | Engine problem
38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 0 | 0 | 108 | 162
39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 33 | 0 | 30 | 0
40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 17 | 54
| Dhaka area Total |  |  |  |  | 6263 | 5847 | 1787 | 2161 | 3600 | 4047 | 390 | 1326
41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 120 | 120 | 120 | 120 | 60 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
43 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 18 | 0 | 20 | 0
44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 10 | 33 | 26 | 40 | 10 |  | Fuel shortage
45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 0 | 25 | 25 | 25 | 205 |  | Low Water Level
46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 217 | 224 | 225 | 225
47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 17 | 105 | 105
49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 28 | 45 | 60 |  | 38 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 16 | 84 | 66 | 84 |  | 18 | Engine problem
51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 0 | 10 | 76 | 76 | 24 |  | Engine problem
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 70 | 50 | 100
53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 13 | 13 | 13 | 13 | 9 |  | Gas shortage
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 18 | 34 | 15 | 25
54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 0 | 51 | 57 |  | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5 | 0 | 5 | 0
56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 100 | 175 | 120 | 294 | 6 |  | Fuel shortage
57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 17 | 54
58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 17 | 51 | 17 | 51 | 59 |  | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 50 | 63 | 90 |  | 10 | Engine problem
60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 34 | 34 | 107 | 107 |  | 9 | Engine problem
| Mirsharai 150 MW |  | Gas/HSD | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 1 | 0 | 0
| Chattogram area Total |  |  |  |  | 2442 | 2382 | 568 | 969 | 1140 | 1545 | 610 | 225
61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 206 | 210 | 210 | 210 |  |  | FGMO
63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 345 | 290 | 300 | 330 |  |  | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 290 | 300 | 300 | 300 |  |  | FGMO
65 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 290 | 300 | 311 | 350
66 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 10 | 39 | 41 | 41
67 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 55 | 0 | 0 | 0 | 0 |  |  | Contract Expired
68 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 0 | 0 | 0 | 0 | 195 |  | Gas shortage
69 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 0 | 14 | 51 | 51
70 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 0 | 80 | 150
71 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 48 | 37 | 40 |  | 12 | Engine problem
72 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under Maint.
73 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 17 | 17 | 17 | 17 | 183 |  | Fuel shortage
74 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 18 | 18 | 18 |  | 4 | Engine problem
75 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 9 | 8 | 9 | 9 |  | 2 | Engine problem
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 116 | 142 | 143 | 166
76 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
77 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 16 | 25 | 52 | 52
78 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 20 | 20 |  | 5 | Engine problem
79 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 0 | 70 |  | Fuel shortage
80 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 34 | 17 | 114
81 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 26 | 55 | 9 | 94 | 19 |  | Fuel shortage
82 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 35 | 35 | 35 |  | 19 | Engine problem
83 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 55 | 93 | 94 | 94 | 21 |  | Fuel shortage
| Cumilla Area Total |  |  |  |  | 3159 | 3151 | 1460 | 1681 | 1777 | 2124 | 488 | 205
84 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 199 | 208 | 210 | 210
85 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 16 | 19 | 17 | 17 | 5 |  | Gas shortage
86 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0
87 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
88 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 141 | 150 | 160 | 180
89 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 94 | 115 | 100 | 115
90 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 53 | 0 | 50 | 0
91 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 19 | 0 | 22 | 22
| Mymensingh Area Total |  |  |  |  | 717 | 614 | 524 | 492 | 560.6 | 544 | 5 | 0
92 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 33 | 33 | 35 | 35 |  | 35 | Machine problem.
93 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 28 | 28 | 30 | 30 |  | 60 | Machine problem
94 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under maint
95 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
96 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 11 | 52 | 51 | 51
97 | Fenchuganj 44MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 10 | 49 | 44 | 44
98 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 8 | 8 |  | 3 | Engine problem
99 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 40 | 61 | 40 | 61
100 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 5 | 83 | 85 | 84
101 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
102 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 0 | 150 | 200
103 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 17 | 17 | 20 | 20
104 | Sylhet 50MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
105 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 0 | 12 | 12 | 12 | 13 |  | Gas shortage
106 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 280 | 290 | 280 | 290 |  |  | FGMO
107 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 240 | 241 | 400 | 400 |  |  | FGMO
108 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 0 | 10 | 10 | 10
109 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 370 | 400 | 400 | 400
| Sylhet Area Total |  |  |  |  | 2472 | 2427 | 1042 | 1284 | 1565 | 1645 | 13 | 691
110 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 928 | 856 | 942 | 942
111 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 0 | 0 | 85 | 98 |  | 17 | Engine problem
112 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 22 | 35 |  | 19 | Engine problem
113 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
114 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 55 | 75 |  | 34 | Engine problem
115 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 180 | 355 | 200 | 355
116 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 0 | 40 | 40
117 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Fuel shortage
118 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 17 | 17 | 88 |  | Fuel shortage
119 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 105
120 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 95 | 0 | 100 | 0
| Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 660*2 | 617 | 617 | 0 | 0 | 0 | 0 |  |  | Coal Shortage.
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3005 | 3001 | 1203 | 1211 | 1461 | 1667 | 434 | 70
121 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 16 | 16
122 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 22 | 30 | 25 | 35
123 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 160 | 170 | 170 | 170 | 24 |  | Gas shortage
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
124 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 560 | 680 | 750 | 1244
125 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 0 | 0 | 0 | 0 |  | 220 | Under maintenance
126 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 17 | 150
127 | Barisal 307 MW |  | Coal | BCPCL | 307*1 | 307 | 307 | 0 | 0 | 0 | 0 | 307 |  | Coal Shortage.
| Barisal Area Total |  |  |  |  | 2265 | 2265 | 742 | 880 | 978 | 1615 | 331 | 220
128 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 65 | 70 | 70 | 70
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
129 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 26 | 26 |  | 26 | Engine problem
130 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 34 |  | 37 | Engine problem
131 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 14 | 14
132 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 34 | 42 |  | 8 | Engine problem
133 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 24 | 42 |  | 8 | Engine problem
134 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 130 | 167 | 200 | 200
135 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
136 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 193 | 169 | 160 | 160 |  |  | FGMO
137 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 360 | 381 | 414 | 414 |  |  | FGMO
138 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 35 | 35 |  | 15 | Engine problem
139 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 0 | 22 | 22 | 22
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
140 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 0 | 8 | 8 |  | 3 | Engine problem
141 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 8 | 44 |  | Fuel shortage
142 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 80 | 80 |  | 24 | Enginr problem
143 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel shortage
144 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 35 | 70 | 43 |  | Fuel shortage
145 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 95 | 95 |  | 18 | Engine problem
146 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 4 | 0 | 6 | 0
| Adani Power Jharkhanda Ltd |  | Coal | Import | 0 | 0 | 0 | 519 | 459 | 500 | 500 |  |  | On test.
| Rajshahi Area Total |  |  |  |  | 2179 | 2129 | 1279 | 1268 | 1723 | 1820 | 607 | 139
147 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 75 | 76 | 75 | 75 | 10 |  | Coal Shortage.
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
148 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 170 | 170 | 170 | 170 | 104 |  | Coal Shortage.
149 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
150 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
151 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 39 | 42 | 95 | 18 |  | Fuel shortage
152 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 7 | 0 | 8 | 0
153 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 0 | 0 | 35 | 115
154 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 36 | 0 | 30 | 0
| Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 0 | 0 | 168 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 830 | 750 | 456 | 285 | 490 | 455 | 172 | 85
| Total |  |  |  |  | 23332 | 22566 | 9061 | 10231 | 13294.6 | 15462 | 3050 | 2961
A. |  | 2023-04-24 | (Yesterday) |  |  |  |  | Monday
1 | Highest Generation : |  |  | 10231 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 7059 | MW at | 6:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 10231 | MW
3 | Day peak Generation : |  |  | 9061 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 9725 | MW
4 | Evening peak Generation : |  |  | 10231 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 213.5109 | MKWHr | By Solar | 2.7845 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Gas : | 139.663 | MKWHr |  | By Oil: | 15.4385 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 32.5003 | MKWHr |  | By Hydro: | 0.12792 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 3050 | MW | Dhaka | 2662 | 2662 |  | 0 |  | 18:00 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 2961 | MW | Chittagong | 1117 | 1117 |  | 0 |  | 19:00 |  | 0
|  |  | Total = |  |  | 6011 | MW | Khulna | 1179.8 | 1179.8 |  | 0 |  | 19:30 |  | 0
7 | Total Gas Supplied : |  |  | 1096.1 | MMCFD |  |  | Rajshahi | 991.2 | 991.2 |  | 0 |  | 20:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 153605865.916 | ii) Oil : | Taka | 200831394.2 | Comilla | 1188 | 1188 |  | 0 |  | 21:00 |  | 0
|  | iii) Coal : | Taka | 169215136.13 | Total | Taka | 523652396.246 | Mymensingh | 998 | 998 |  | 0 |  | 22:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 1.089 | MKWHr. | Sylhet | 462 | 462 |  | 0 |  | 23:00 |  | 0
| ii) During Peak Demand : |  |  | 204 | MW (E to W) at | 21:00 | hrs | Barisal | 382 | 382 |  | 0 |  | 24:00 |  | 0
| iii) Maximum : |  |  | -74 | MW at | 7:00 | hrs | Rangpur | 745 | 745 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 35.1° C |  |  | Total | 9725 | 9725 |  | 0
B. |  | 2023-04-25 | (Today) |  |  |  | Tuesday |  |  | Probable max. temperature in Dhaka |  |  | 36.8° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 11000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 15462 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 9500 | MW
4 | Reserve(Generation end) |  |  |  | 4462 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 229.5592 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 7813 | MW at | 6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 20.0436 | MKWHr. | ii) HVDC Flow at Peak Time |  | 856 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.953 | MKWHr. | iii) Maximum HVDC Flow : |  | 928 | MW at | 12:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 75.35 |  | (b) Today: | 75.3 |  | (c) Rule Curve: |  | 83.2
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2023-04-24 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 120 | 0 | 0 | 386 | 305 |  | 0 | 320 | 273 | 0 | 0 | 0 | 90 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 6 | 17 | 12 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 228 | 0 | 0 | 0 |  | 0 | 0 | 67 | 0 | 0 | 6 | 13 | 42 | 0 | 0 | 0 | 290 | 275 | 183 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 47 | 34 | 18 | 9 | 33 | 18 | 132 | 215 | 0 | 16 | 0 | 34 | 29 | 22 | 41 | 0 | 0 | 40 | 5 | 0 | 0 | 18 | 0 | 0 | 270 | 0 | 2 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 50 | 17 | 0 | 240 | 35 | 0 | 0 | 0 | 105 | 0 | 17 | 0 | 9 | 0 | 400 | 0 | 0 | 0 | 34 | 0 | 17 | 0 | 73 | 0 | 250 | 0 | 0 |  | 696 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 27 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 75 | 0 | 170 | 0 | 0 | 155 | 0 | 0 | 0 | 0 | 0 | 156 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 570 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 514 | 0 | 0 |  | 5267 | 3252 | 8519 | 4233 | 696 | 1610 | 0 | 405 | 1329 | 0 | 0 | 114 | 132 | 0 | 0 | 75.35
2:00 | 0 | 0 | 0 | 180 | 120 | 0 | 0 | 386 | 265 |  | 0 | 320 | 271 | 0 | 0 | 0 | 90 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 10 | 17 | 12 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 227 | 0 | 0 | 0 |  | 0 | 0 | 67 | 0 | 0 | 6 | 13 | 34 | 0 | 0 | 0 | 290 | 275 | 183 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 47 | 8 | 18 | 9 | 33 | 18 | 126 | 216 | 0 | 16 | 0 | 34 | 29 | 11 | 10 | 0 | 0 | 40 | 5 | 0 | 0 | 18 | 0 | 0 | 270 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 12 | 17 | 0 | 240 | 35 | 0 | 0 | 0 | 100 | 0 | 17 | 0 | 9 | 0 | 400 | 0 | 0 | 0 | 34 | 0 | 17 | 0 | 72 | 0 | 250 | 0 | 0 |  | 678 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 26 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 75 | 0 | 170 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 514 | 0 | 0 |  | 5083 | 3111 | 8194 | 4173 | 678 | 1509 | 0 | 335 | 1259 | 0 | 0 | 114 | 126 | 0 | 0 | 75.35
3:00 | 0 | 0 | 0 | 180 | 120 | 0 | 0 | 337 | 265 |  | 0 | 320 | 277 | 0 | 0 | 0 | 50 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 10 | 17 | 12 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 227 | 0 | 0 | 0 |  | 0 | 0 | 67 | 0 | 0 | 6 | 13 | 34 | 0 | 0 | 0 | 290 | 275 | 183 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 47 | 8 | 18 | 9 | 33 | 18 | 124 | 216 | 0 | 16 | 0 | 34 | 29 | 11 | 10 | 0 | 0 | 40 | 5 | 0 | 0 | 18 | 0 | 0 | 275 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 12 | 17 | 0 | 240 | 35 | 0 | 0 | 0 | 65 | 0 | 17 | 0 | 9 | 0 | 400 | 0 | 0 | 0 | 34 | 0 | 17 | 0 | 50 | 0 | 250 | 0 | 0 |  | 678 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 25 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 75 | 0 | 170 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 514 | 0 | 0 |  | 4949 | 3015 | 7964 | 3975 | 678 | 1536 | 0 | 278 | 1259 | 0 | 0 | 114 | 124 | 0 | 0 | 75.35
4:00 | 0 | 0 | 0 | 180 | 120 | 0 | 0 | 316 | 265 |  | 0 | 290 | 271 | 0 | 0 | 0 | 50 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 17 | 12 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 227 | 0 | 0 | 0 |  | 0 | 0 | 67 | 0 | 0 | 6 | 13 | 34 | 0 | 0 | 0 | 290 | 275 | 151 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 47 | 0 | 18 | 9 | 33 | 18 | 118 | 216 | 0 | 16 | 0 | 34 | 29 | 11 | 10 | 0 | 0 | 40 | 5 | 0 | 0 | 18 | 0 | 0 | 245 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 12 | 17 | 0 | 240 | 16 | 0 | 0 | 0 | 65 | 0 | 17 | 0 | 9 | 0 | 360 | 0 | 0 | 0 | 34 | 0 | 17 | 0 | 34 | 0 | 250 | 0 | 0 |  | 678 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 22 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 76 | 0 | 170 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 496 | 0 | 0 |  | 4729 | 2951 | 7680 | 3870 | 678 | 1423 | 0 | 235 | 1242 | 0 | 0 | 114 | 118 | 0 | 0 | 75.35
5:00 | 0 | 0 | 0 | 180 | 120 | 0 | 0 | 286 | 241 |  | 0 | 290 | 274 | 0 | 0 | 0 | 50 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 17 | 12 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 227 | 0 | 0 | 0 |  | 0 | 0 | 67 | 0 | 0 | 6 | 13 | 34 | 0 | 0 | 0 | 290 | 280 | 151 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 9 | 33 | 18 | 115 | 187 | 0 | 16 | 0 | 34 | 29 | 11 | 10 | 0 | 0 | 40 | 5 | 0 | 0 | 18 | 0 | 0 | 275 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 12 | 17 | 0 | 240 | 16 | 0 | 0 | 0 | 65 | 0 | 17 | 0 | 9 | 0 | 320 | 0 | 0 | 0 | 34 | 0 | 17 | 0 | 17 | 0 | 250 | 0 | 0 |  | 738 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 21 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 76 | 0 | 170 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 411 | 0 | 0 |  | 4579 | 2865 | 7444 | 3728 | 738 | 1421 | 0 | 218 | 1157 | 0 | 0 | 67 | 115 | 0 | 0 | 75.35
6:00 | 0 | 0 | 0 | 180 | 120 | 0 | 0 | 278 | 243 |  | 0 | 290 | 281 | 0 | 0 | 0 | 50 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 17 | 12 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 180 | 0 | 0 | 0 |  | 0 | 0 | 4 | 0 | 0 | 6 | 13 | 34 | 0 | 0 | 0 | 280 | 250 | 130 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 9 | 25 | 18 | 104 | 149 | 0 | 16 | 0 | 34 | 29 | 11 | 10 | 0 | 0 | 40 | 5 | 0 | 0 | 18 | 0 | 0 | 190 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 1 | 12 | 17 | 0 | 240 | 16 | 0 | 0 | 0 | 30 | 0 | 17 | 0 | 9 | 0 | 320 | 0 | 1 | 0 | 34 | 0 | 17 | 1 | 17 | 0 | 250 | 0 | 0 |  | 738 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 17 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 75 | 0 | 170 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 413 | 4 | 0 |  | 4235 | 2824 | 7059 | 3546 | 738 | 1317 | 0 | 183 | 1158 | 0 | 0 | 4 | 104 | 9 | 0 | 75.35
7:00 | 0 | 0 | 0 | 180 | 120 | 0 | 0 | 278 | 246 |  | 0 | 290 | 277 | 0 | 0 | 0 | 50 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 17 | 12 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 181 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 6 | 13 | 36 | 0 | 0 | 0 | 280 | 250 | 131 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 9 | 25 | 18 | 96 | 214 | 0 | 16 | 0 | 34 | 29 | 11 | 10 | 0 | 0 | 40 | 5 | 0 | 0 | 18 | 0 | 0 | 230 | 0 | 5 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 5 | 12 | 17 | 0 | 240 | 47 | 0 | 0 | 1 | 30 | 0 | 17 | 0 | 9 | 0 | 320 | 0 | 11 | 0 | 34 | 0 | 17 | 7 | 17 | 0 | 250 | 0 | 0 |  | 737 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 16 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 76 | 0 | 170 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 234 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 500 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 7 | 0 | 413 | 37 | 0 |  | 4400 | 2871 | 7271 | 3601 | 737 | 1355 | 0 | 232 | 1159 | 0 | 0 | 0 | 96 | 91 | 0 | 75.35
8:00 | 0 | 0 | 0 | 180 | 120 | 0 | 0 | 269 | 246 |  | 0 | 290 | 282 | 0 | 0 | 0 | 50 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 17 | 12 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 181 | 0 | 0 | 0 |  | 3 | 0 | 0 | 0 | 0 | 6 | 13 | 36 | 0 | 0 | 0 | 290 | 250 | 181 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 9 | 20 | 0 | 92 | 213 | 0 | 16 | 1 | 34 | 29 | 11 | 10 | 0 | 0 | 40 | 5 | 0 | 0 | 18 | 0 | 0 | 285 | 0 | 5 | 0 | 0 | 0 | 0 | 46 | 0 | 0 | 9 | 0 | 17 | 0 | 240 | 47 | 0 | 0 | 1 | 30 | 0 | 17 | 0 | 0 | 0 | 320 | 0 | 27 | 0 | 34 | 0 | 17 | 15 | 17 | 0 | 250 | 0 | 0 |  | 737 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 18 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 75 | 0 | 170 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 263 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 500 | 0 | 0 | 0 | 2 | 43 | 0 | 0 | 0 | 0 | 15 | 0 | 429 | 68 | 0 |  | 4536 | 3014 | 7550 | 3683 | 737 | 1446 | 0 | 234 | 1174 | 0 | 0 | 0 | 92 | 184 | 0 | 75.34
9:00 | 0 | 0 | 0 | 180 | 120 | 0 | 0 | 275 | 254 |  | 0 | 290 | 296 | 0 | 0 | 0 | 50 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 17 | 12 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 201 | 0 | 0 | 0 |  | 18 | 0 | 0 | 0 | 0 | 6 | 13 | 33 | 0 | 0 | 0 | 290 | 250 | 151 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 9 | 21 | 12 | 100 | 210 | 0 | 16 | 2 | 34 | 28 | 11 | 10 | 0 | 0 | 40 | 5 | 0 | 0 | 17 | 0 | 0 | 280 | 0 | 5 | 0 | 0 | 0 | 0 | 46 | 0 | 0 | 11 | 0 | 17 | 0 | 240 | 47 | 0 | 0 | 3 | 30 | 0 | 17 | 0 | 0 | 0 | 320 | 0 | 40 | 0 | 34 | 0 | 17 | 23 | 17 | 0 | 250 | 0 | 0 |  | 738 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 17 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 75 | 0 | 170 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 156 | 0 | 264 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 500 | 0 | 0 | 0 | 3 | 66 | 0 | 0 | 0 | 0 | 26 | 0 | 515 | 86 | 0 |  | 4579 | 3179 | 7758 | 3686 | 738 | 1460 | 0 | 249 | 1260 | 0 | 0 | 0 | 100 | 265 | 0 | 75.34
10:00 | 0 | 0 | 0 | 180 | 120 | 0 | 0 | 342 | 254 |  | 0 | 290 | 307 | 0 | 0 | 0 | 50 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 17 | 12 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 223 | 0 | 0 | 0 |  | 19 | 0 | 0 | 0 | 0 | 6 | 13 | 20 | 0 | 0 | 0 | 290 | 250 | 152 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 9 | 25 | 18 | 104 | 205 | 0 | 16 | 2 | 34 | 28 | 11 | 10 | 0 | 0 | 40 | 5 | 0 | 0 | 18 | 0 | 0 | 300 | 0 | 5 | 0 | 0 | 0 | 0 | 46 | 0 | 0 | 11 | 0 | 17 | 0 | 240 | 47 | 0 | 0 | 4 | 30 | 0 | 17 | 0 | 0 | 0 | 320 | 0 | 49 | 0 | 34 | 0 | 17 | 28 | 17 | 0 | 250 | 0 | 0 |  | 926 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 18 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 75 | 0 | 170 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 263 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 500 | 0 | 0 | 0 | 4 | 90 | 0 | 0 | 0 | 0 | 28 | 0 | 519 | 143 | 0 |  | 4733 | 3421 | 8154 | 3766 | 926 | 1478 | 0 | 250 | 1264 | 0 | 0 | 0 | 104 | 366 | 0 | 75.34
11:00 | 0 | 0 | 0 | 180 | 120 | 0 | 0 | 344 | 254 |  | 0 | 290 | 305 | 0 | 0 | 0 | 100 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 17 | 12 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 219 | 0 | 0 | 0 |  | 19 | 0 | 0 | 0 | 0 | 6 | 13 | 20 | 0 | 0 | 0 | 325 | 250 | 152 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 1 | 18 | 9 | 25 | 20 | 116 | 204 | 0 | 16 | 2 | 33 | 28 | 11 | 10 | 0 | 0 | 40 | 5 | 0 | 0 | 18 | 0 | 0 | 285 | 0 | 8 | 0 | 0 | 0 | 0 | 139 | 0 | 0 | 15 | 0 | 17 | 0 | 240 | 94 | 0 | 0 | 5 | 100 | 0 | 17 | 0 | 27 | 0 | 320 | 0 | 53 | 0 | 34 | 0 | 17 | 30 | 45 | 0 | 290 | 0 | 0 |  | 926 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 20 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 75 | 0 | 170 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 264 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 500 | 0 | 0 | 0 | 4 | 94 | 0 | 0 | 0 | 0 | 35 | 0 | 500 | 163 | 0 |  | 5133 | 3436 | 8569 | 3894 | 926 | 1464 | 0 | 516 | 1245 | 0 | 0 | 0 | 116 | 408 | 0 | 75.34
12:00 | 0 | 0 | 0 | 180 | 120 | 0 | 0 | 344 | 275 |  | 0 | 320 | 301 | 0 | 0 | 0 | 100 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 17 | 12 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 217 | 0 | 0 | 0 |  | 19 | 0 | 16 | 0 | 0 | 10 | 13 | 18 | 0 | 0 | 0 | 345 | 290 | 206 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 16 | 18 | 9 | 25 | 20 | 116 | 199 | 0 | 16 | 2 | 33 | 28 | 11 | 10 | 0 | 0 | 40 | 5 | 0 | 0 | 17 | 0 | 0 | 280 | 0 | 8 | 0 | 0 | 0 | 0 | 141 | 0 | 0 | 18 | 0 | 17 | 0 | 240 | 94 | 0 | 0 | 5 | 100 | 0 | 17 | 0 | 26 | 0 | 370 | 0 | 53 | 0 | 34 | 0 | 17 | 33 | 55 | 0 | 290 | 0 | 0 |  | 928 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 22 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 75 | 0 | 170 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 193 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 560 | 0 | 0 | 0 | 4 | 95 | 0 | 0 | 0 | 0 | 36 | 0 | 519 | 168 | 0 |  | 5381 | 3680 | 9061 | 4108 | 928 | 1602 | 0 | 546 | 1324 | 0 | 0 | 16 | 116 | 421 | 0 | 75.34
13:00 | 0 | 0 | 0 | 180 | 120 | 13 | 0 | 381 | 308 |  | 0 | 350 | 299 | 0 | 0 | 0 | 170 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 17 | 12 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 219 | 0 | 0 | 0 |  | 18 | 0 | 16 | 0 | 0 | 16 | 13 | 18 | 0 | 0 | 0 | 300 | 290 | 206 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 34 | 18 | 8 | 25 | 20 | 124 | 197 | 0 | 16 | 2 | 33 | 28 | 11 | 37 | 0 | 0 | 59 | 30 | 0 | 0 | 17 | 0 | 0 | 275 | 0 | 8 | 0 | 0 | 0 | 0 | 152 | 0 | 0 | 14 | 12 | 17 | 0 | 240 | 94 | 0 | 0 | 4 | 100 | 0 | 17 | 0 | 28 | 0 | 400 | 0 | 51 | 0 | 34 | 0 | 17 | 32 | 71 | 0 | 320 | 0 | 0 |  | 928 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 24 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 8 | 75 | 0 | 170 | 0 | 0 | 158 | 0 | 0 | 0 | 0 | 0 | 212 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 650 | 0 | 0 | 0 | 4 | 31 | 0 | 0 | 0 | 0 | 34 | 0 | 518 | 162 | 0 |  | 5729 | 3807 | 9536 | 4364 | 928 | 1740 | 0 | 610 | 1413 | 0 | 0 | 16 | 124 | 341 | 0 | 75.34
14:00 | 0 | 0 | 0 | 180 | 160 | 13 | 0 | 401 | 328 |  | 0 | 350 | 272 | 0 | 0 | 0 | 208 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 17 | 12 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 221 | 0 | 0 | 0 |  | 18 | 0 | 16 | 0 | 0 | 16 | 13 | 19 | 0 | 0 | 0 | 290 | 290 | 209 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 41 | 18 | 8 | 25 | 20 | 132 | 202 | 0 | 16 | 2 | 33 | 28 | 45 | 37 | 0 | 0 | 60 | 30 | 0 | 0 | 17 | 0 | 8 | 270 | 0 | 8 | 0 | 0 | 0 | 0 | 153 | 0 | 0 | 16 | 30 | 17 | 0 | 240 | 94 | 0 | 0 | 4 | 139 | 0 | 19 | 34 | 28 | 12 | 395 | 0 | 46 | 0 | 34 | 0 | 17 | 21 | 84 | 0 | 320 | 0 | 0 |  | 927 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 25 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 8 | 75 | 0 | 170 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 195 | 0 | 307 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 710 | 0 | 0 | 0 | 3 | 6 | 0 | 0 | 0 | 0 | 31 | 0 | 513 | 140 | 0 |  | 5960 | 3895 | 9855 | 4579 | 927 | 1721 | 0 | 736 | 1468 | 0 | 0 | 16 | 132 | 276 | 0 | 75.34
15:00 | 0 | 0 | 0 | 180 | 160 | 13 | 0 | 396 | 329 |  | 0 | 350 | 281 | 0 | 0 | 0 | 140 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 17 | 12 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 220 | 0 | 0 | 0 |  | 0 | 0 | 16 | 0 | 0 | 18 | 13 | 20 | 0 | 0 | 0 | 290 | 290 | 209 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 52 | 16 | 8 | 33 | 15 | 132 | 201 | 0 | 16 | 2 | 33 | 28 | 52 | 36 | 0 | 0 | 60 | 30 | 0 | 0 | 17 | 0 | 10 | 280 | 0 | 8 | 0 | 0 | 0 | 0 | 85 | 0 | 0 | 10 | 50 | 17 | 0 | 247 | 89 | 0 | 0 | 3 | 139 | 0 | 51 | 34 | 28 | 12 | 395 | 0 | 37 | 0 | 34 | 0 | 17 | 10 | 94 | 0 | 320 | 0 | 0 |  | 924 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 23 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 8 | 75 | 0 | 170 | 0 | 0 | 167 | 0 | 0 | 0 | 0 | 0 | 177 | 0 | 313 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 650 | 0 | 0 | 0 | 2 | 5 | 0 | 0 | 0 | 0 | 15 | 0 | 515 | 114 | 0 |  | 5870 | 3758 | 9628 | 4471 | 924 | 1754 | 0 | 720 | 1410 | 0 | 0 | 16 | 132 | 201 | 0 | 75.33
16:00 | 0 | 0 | 0 | 180 | 130 | 13 | 0 | 367 | 304 |  | 0 | 320 | 233 | 0 | 0 | 0 | 140 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 17 | 12 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 220 | 0 | 0 | 0 |  | 0 | 0 | 16 | 0 | 0 | 18 | 13 | 20 | 0 | 0 | 0 | 290 | 290 | 208 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 52 | 18 | 8 | 33 | 20 | 128 | 201 | 0 | 16 | 1 | 33 | 28 | 52 | 41 | 0 | 0 | 60 | 30 | 0 | 0 | 17 | 0 | 10 | 275 | 0 | 8 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 8 | 30 | 17 | 0 | 240 | 75 | 0 | 0 | 2 | 141 | 0 | 34 | 34 | 28 | 12 | 340 | 0 | 20 | 0 | 34 | 0 | 17 | 0 | 70 | 0 | 270 | 0 | 0 |  | 922 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 23 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 8 | 75 | 0 | 170 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 237 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 510 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 13 | 0 | 422 | 64 | 0 |  | 5478 | 3287 | 8765 | 4162 | 922 | 1576 | 0 | 632 | 1177 | 0 | 0 | 16 | 128 | 152 | 0 | 75.33
17:00 | 0 | 0 | 0 | 180 | 130 | 0 | 0 | 326 | 252 |  | 0 | 300 | 231 | 0 | 0 | 0 | 140 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 23 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 221 | 0 | 0 | 0 |  | 0 | 0 | 17 | 0 | 0 | 12 | 13 | 20 | 0 | 0 | 0 | 290 | 270 | 208 | 0 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 52 | 18 | 8 | 33 | 20 | 122 | 203 | 0 | 16 | 0 | 33 | 28 | 24 | 20 | 0 | 0 | 40 | 30 | 0 | 0 | 17 | 0 | 10 | 265 | 0 | 8 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 3 | 12 | 17 | 0 | 240 | 75 | 0 | 0 | 0 | 142 | 0 | 34 | 17 | 28 | 12 | 320 | 0 | 5 | 0 | 34 | 0 | 17 | 1 | 51 | 0 | 250 | 0 | 0 |  | 923 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 22 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 0 | 170 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 234 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 500 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 9 | 0 | 422 | 34 | 0 |  | 5108 | 3071 | 8179 | 3913 | 923 | 1408 | 0 | 548 | 1168 | 0 | 0 | 17 | 122 | 80 | 0 | 75.33
18:00 | 0 | 0 | 0 | 180 | 130 | 0 | 0 | 304 | 254 |  | 0 | 300 | 230 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 23 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 221 | 0 | 0 | 0 |  | 0 | 0 | 17 | 0 | 0 | 6 | 13 | 20 | 0 | 0 | 0 | 290 | 270 | 195 | 0 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 16 | 18 | 8 | 33 | 20 | 120 | 146 | 0 | 16 | 0 | 33 | 28 | 6 | 5 | 0 | 0 | 40 | 10 | 0 | 0 | 17 | 0 | 10 | 250 | 0 | 8 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 12 | 17 | 0 | 247 | 75 | 0 | 0 | 0 | 142 | 0 | 34 | 17 | 28 | 12 | 320 | 0 | 1 | 0 | 34 | 0 | 17 | 0 | 51 | 0 | 250 | 0 | 0 |  | 893 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 0 | 170 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 213 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 500 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 1 | 0 | 414 | 5 | 0 |  | 4797 | 2915 | 7712 | 3676 | 893 | 1319 | 0 | 516 | 1160 | 0 | 0 | 17 | 120 | 11 | 0 | 75.33
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 160 | 12 | 0 | 361 | 343 |  | 0 | 450 | 275 | 7 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 23 | 0 | 17 | 0 | 2 | 0 | 25 | 0 | 120 | 0 | 0 | 225 | 0 | 0 | 0 |  | 1 | 0 | 73 | 44 | 7 | 9 | 13 | 26 | 0 | 0 | 0 | 290 | 280 | 210 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 27 | 26 | 18 | 8 | 33 | 20 | 144 | 207 | 0 | 16 | 0 | 33 | 28 | 52 | 25 | 0 | 0 | 61 | 83 | 0 | 0 | 17 | 0 | 10 | 290 | 5 | 8 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 60 | 17 | 0 | 241 | 115 | 4 | 6 | 0 | 225 | 0 | 40 | 70 | 94 | 90 | 400 | 30 | 0 | 0 | 34 | 0 | 17 | 0 | 72 | 0 | 250 | 0 | 0 |  | 922 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 75 | 0 | 170 | 0 | 0 | 162 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 294 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 550 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 441 | 0 | 0 |  | 6248 | 3372 | 9620 | 4208 | 922 | 1908 | 0 | 1077 | 1236 | 25 | 0 | 100 | 144 | 0 | 0 | 75.32
19:30 | 0 | 0 | 0 | 180 | 160 | 12 | 0 | 390 | 305 |  | 0 | 450 | 298 | 9 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 23 | 0 | 17 | 6 | 16 | 0 | 25 | 0 | 120 | 0 | 0 | 224 | 0 | 0 | 0 |  | 22 | 25 | 84 | 44 | 21 | 25 | 13 | 34 | 0 | 0 | 0 | 290 | 280 | 208 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 43 | 25 | 18 | 8 | 33 | 20 | 142 | 205 | 0 | 16 | 0 | 33 | 28 | 52 | 47 | 0 | 0 | 61 | 83 | 0 | 0 | 17 | 0 | 10 | 290 | 11 | 8 | 0 | 0 | 0 | 0 | 146 | 0 | 0 | 0 | 100 | 17 | 0 | 241 | 115 | 35 | 17 | 0 | 190 | 0 | 51 | 34 | 57 | 50 | 400 | 30 | 0 | 0 | 34 | 0 | 25 | 0 | 93 | 0 | 250 | 0 | 0 |  | 856 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 76 | 0 | 170 | 0 | 0 | 155 | 0 | 0 | 0 | 0 | 0 | 157 | 0 | 309 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 650 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 455 | 0 | 0 |  | 6518 | 3471 | 9989 | 4299 | 856 | 1939 | 0 | 1225 | 1351 | 25 | 0 | 152 | 142 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 180 | 160 | 12 | 0 | 392 | 304 |  | 0 | 450 | 300 | 9 | 0 | 0 | 150 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 23 | 0 | 17 | 11 | 0 | 0 | 25 | 0 | 120 | 0 | 0 | 225 | 0 | 0 | 0 |  | 21 | 28 | 84 | 44 | 0 | 30 | 13 | 34 | 0 | 0 | 0 | 290 | 280 | 212 | 0 | 0 | 38 | 0 | 0 | 11 | 0 | 48 | 25 | 18 | 8 | 33 | 20 | 142 | 207 | 0 | 16 | 0 | 33 | 28 | 52 | 47 | 0 | 0 | 61 | 83 | 0 | 0 | 17 | 0 | 10 | 275 | 12 | 8 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 70 | 17 | 0 | 241 | 118 | 17 | 17 | 0 | 190 | 0 | 51 | 34 | 55 | 50 | 400 | 17 | 0 | 0 | 34 | 0 | 31 | 0 | 94 | 0 | 250 | 1 | 0 |  | 857 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 28 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 75 | 0 | 170 | 0 | 0 | 153 | 0 | 0 | 0 | 0 | 0 | 157 | 0 | 300 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 650 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 0 | 0 | 0 | 470 | 0 | 0 |  | 6494 | 3552 | 10046 | 4389 | 857 | 1927 | 0 | 1180 | 1365 | 25 | 1 | 160 | 142 | 0 | 0 | 75.32
21:00 | 0 | 0 | 0 | 180 | 160 | 12 | 0 | 398 | 334 |  | 0 | 450 | 298 | 0 | 0 | 0 | 208 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 23 | 0 | 17 | 11 | 0 | 0 | 25 | 0 | 120 | 0 | 0 | 224 | 0 | 0 | 0 |  | 0 | 28 | 84 | 10 | 0 | 33 | 13 | 34 | 0 | 0 | 0 | 290 | 300 | 210 | 0 | 0 | 39 | 0 | 0 | 14 | 0 | 48 | 25 | 18 | 8 | 33 | 20 | 142 | 208 | 0 | 19 | 0 | 33 | 28 | 52 | 49 | 0 | 0 | 61 | 83 | 0 | 0 | 17 | 0 | 10 | 290 | 12 | 8 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 70 | 17 | 0 | 241 | 115 | 0 | 17 | 0 | 175 | 0 | 51 | 34 | 55 | 50 | 400 | 17 | 0 | 0 | 34 | 0 | 35 | 0 | 93 | 0 | 300 | 1 | 0 |  | 856 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 30 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 76 | 0 | 170 | 0 | 0 | 167 | 0 | 0 | 0 | 0 | 0 | 169 | 0 | 381 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 680 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 459 | 0 | 0 |  | 6587 | 3644 | 10231 | 4583 | 856 | 2059 | 0 | 1020 | 1385 | 25 | 1 | 160 | 142 | 0 | 0 | 75.32
22:00 | 0 | 0 | 0 | 180 | 160 | 11 | 0 | 394 | 343 |  | 0 | 450 | 281 | 0 | 0 | 0 | 209 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 23 | 0 | 17 | 11 | 0 | 0 | 25 | 0 | 120 | 0 | 0 | 226 | 0 | 0 | 0 |  | 0 | 28 | 84 | 10 | 0 | 33 | 13 | 35 | 0 | 0 | 0 | 290 | 300 | 212 | 0 | 0 | 40 | 0 | 0 | 14 | 0 | 48 | 43 | 18 | 8 | 33 | 20 | 146 | 209 | 0 | 16 | 0 | 33 | 28 | 52 | 49 | 0 | 0 | 62 | 83 | 0 | 100 | 17 | 0 | 10 | 275 | 14 | 8 | 0 | 0 | 0 | 0 | 95 | 0 | 0 | 0 | 70 | 17 | 0 | 241 | 115 | 0 | 17 | 0 | 175 | 0 | 51 | 52 | 55 | 50 | 400 | 20 | 0 | 0 | 34 | 0 | 35 | 0 | 94 | 0 | 300 | 0 | 0 |  | 839 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 30 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 76 | 0 | 170 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 299 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 650 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 459 | 0 | 0 |  | 6652 | 3513 | 10165 | 4687 | 839 | 1953 | 0 | 1000 | 1355 | 25 | 0 | 160 | 146 | 0 | 0 | 75.32
23:00 | 0 | 0 | 0 | 180 | 160 | 11 | 0 | 393 | 344 |  | 0 | 450 | 277 | 0 | 0 | 0 | 206 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 23 | 0 | 17 | 0 | 0 | 0 | 25 | 0 | 120 | 0 | 0 | 228 | 0 | 0 | 0 |  | 0 | 24 | 84 | 0 | 0 | 33 | 13 | 35 | 0 | 0 | 0 | 290 | 300 | 213 | 0 | 0 | 40 | 0 | 0 | 14 | 0 | 48 | 52 | 18 | 9 | 33 | 20 | 148 | 210 | 0 | 16 | 0 | 33 | 28 | 52 | 49 | 0 | 0 | 62 | 83 | 0 | 119 | 18 | 0 | 10 | 270 | 14 | 8 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | 70 | 17 | 0 | 241 | 115 | 0 | 17 | 0 | 155 | 0 | 54 | 52 | 22 | 25 | 400 | 34 | 0 | 0 | 34 | 0 | 35 | 0 | 93 | 0 | 270 | 0 | 0 |  | 839 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 32 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 76 | 0 | 170 | 0 | 0 | 155 | 0 | 0 | 0 | 0 | 0 | 158 | 0 | 303 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 650 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 459 | 0 | 0 |  | 6539 | 3493 | 10032 | 4640 | 839 | 1952 | 0 | 917 | 1355 | 25 | 0 | 156 | 148 | 0 | 0 | 75.32
24:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 396 | 344 |  | 0 | 450 | 299 | 0 | 0 | 0 | 206 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 23 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 228 | 0 | 0 | 0 |  | 0 | 24 | 84 | 0 | 0 | 11 | 13 | 36 | 0 | 0 | 0 | 290 | 300 | 213 | 0 | 0 | 40 | 0 | 0 | 14 | 0 | 48 | 52 | 18 | 9 | 33 | 20 | 146 | 210 | 0 | 16 | 0 | 33 | 28 | 52 | 49 | 0 | 0 | 63 | 83 | 0 | 120 | 18 | 0 | 10 | 290 | 15 | 8 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 70 | 17 | 0 | 241 | 115 | 0 | 17 | 0 | 87 | 0 | 54 | 52 | 9 | 25 | 400 | 34 | 0 | 0 | 34 | 0 | 35 | 0 | 93 | 0 | 270 | 0 | 0 |  | 882 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 31 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 75 | 0 | 170 | 0 | 0 | 157 | 0 | 0 | 0 | 0 | 0 | 159 | 0 | 322 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 460 | 0 | 0 |  | 6282 | 3406 | 9688 | 4492 | 882 | 2013 | 0 | 794 | 1205 | 0 | 0 | 156 | 146 | 0 | 0 | 75.32
KWH | 0 | 0 | 0 | 4268250 | 3121400 | 116045 | 0 | 8480770 | 6898000 |  | 0 | 8215500 | 6735069 | 17280 | 0 | 0 | 2754147 | 0 | 1069000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112392 | 552000 | 29160 | 418740 | 266200 | 11040 | 0 | 127920 | 0 | 2800000 | 0 | 0 | 5126173 | 0 | 0 | 0 |  | 163200 | 120864 | 939305 | 100920 | 14400 | 322080 | 295824 | 726720 | 0 | 0 | 0 | 7411100 | 6805000 | 4493000 | 0 | 0 | 606024 | 0 | 0 | 290494 | 0 | 475504 | 561782 | 411480 | 211680 | 726900 | 455550 | 2952960 | 4788480 | 0 | 377640 | 14950 | 785000 | 634560 | 600600 | 641664 | 0 | 0 | 1182528 | 739200 | 0 | 291710 | 407000 | 0 | 100620 | 6619000 | 62016 | 175008 | 0 | 0 | 0 | 0 | 1740000 | 0 | 0 | 127170 | 755520 | 430560 | 0 | 5776000 | 1718400 | 28877 | 100364 | 31559 | 2627018 | 0 | 735160 | 389880 | 551880 | 343680 | 8697200 | 142080 | 389310 | 0 | 839291 | 0 | 530280 | 205777 | 1470720 | 0 | 6582600 | 6690 | 0 |  | 20043636 | 0 | 6815520 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4018518 | 569561 | 0 | 0 | 0 | 1285000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173040 | 0 | 131778 | 1786473 | 0 | 4173600 | 0 | 0 | 3781409 | 0 | 0 | 0 | 0 | 0 | 3966845 | 0 | 7063927 | 0 | 0 | 0 | 0 | 192662 | 0 | 48884 | 0 | 15178400 | 0 | 0 | 0 | 29760 | 497520 | 109056 | 0 | 0 | 0 | 247014 | 0 | 11361818 | 1192600 | 0 |  | 130843865 | 82667021 | 213510886 | 100173602 | 20043636 | 39489440 | 0 | 13896130 | 32500291 | 127920 | 6690 | 1535673 | 2952960 | 2784544 | 0
Fuel Cost | 0 | 0 | 0 | 6359692.5 | 3495968 | 154339.85 | 0 | 8904808.5 | 7449840 |  | 0 | 8954895 | 7475926.59 | 193190.4 | 0 | 0 | 3084644.64 | 0 | 1870750 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84294 | 414000 | 0 | 0 | 0 | 187790.4 | 0 | 34538.4 | 0 | 5292000 | 0 | 0 | 5331219.92 | 0 | 0 | 0 |  | 2129760 | 2016011.52 | 15986971.1 | 1363429.2 | 182592 | 3726465.6 | 375696.48 | 2419977.6 | 0 | 0 | 0 | 8226321 | 7417450 | 5211880 | 0 | 0 | 684807.12 | 0 | 0 | 485124.98 | 0 | 8211954.08 | 7555967.9 | 563727.6 | 158760 | 1272075 | 341662.5 | 21202252.8 | 5219443.2 | 0 | 513590.4 | 238303 | 1075450 | 837619.2 | 1045044 | 1110078.72 | 0 | 0 | 2294104.32 | 1685376 | 0 | 294627.1 | 875050 | 0 | 199227.6 | 6619000 | 46512 | 133006.08 | 0 | 0 | 0 | 0 | 23455200 | 0 | 0 | 1486617.3 | 7796966.4 | 5881449.6 | 0 | 5313920 | 20895744 | 417561.42 | 1269604.6 | 0 | 30841191.32 | 0 | 7814750.8 | 5290671.6 | 7113733.2 | 4048550.4 | 8001424 | 1839936 | 5625529.5 | 0 | 9551131.58 | 0 | 6925456.8 | 2459035.15 | 22016678.4 | 0 | 0 | 0 | 0 |  | 60130908 | 0 | 7633382.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4500740.16 | 1104948.34 | 0 | 0 | 0 | 2634250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 358192.8 | 0 | 99755.946 | 10379408.13 | 0 | 22078344 | 0 | 0 | 4386434.44 | 0 | 0 | 0 | 0 | 0 | 4601540.2 | 0 | 6993287.73 | 0 | 0 | 0 | 0 | 2446807.4 | 0 | 540168.2 | 0 | 136757384 | 0 | 0 | 0 | 336585.6 | 5835909.6 | 1671828.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 349052368.37 | 272489875.426 | 621542243.796 | 107550606.706 | 60130908 | 46055259.21 | 0 | 174616457.5 | 169215136.13 | 34538.4 | 0 | 26214936.7 | 21202252.8 | 16522148.35 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 120 | 0 | 0 | 344 | 275 |  | 0 | 320 | 301 | 0 | 0 | 0 | 100 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 17 | 12 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 217 | 0 | 0 | 0 |  | 19 | 0 | 16 | 0 | 0 | 10 | 13 | 18 | 0 | 0 | 0 | 345 | 290 | 206 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 16 | 18 | 9 | 25 | 20 | 116 | 199 | 0 | 16 | 2 | 33 | 28 | 11 | 10 | 0 | 0 | 40 | 5 | 0 | 0 | 17 | 0 | 0 | 280 | 0 | 8 | 0 | 0 | 0 | 0 | 141 | 0 | 0 | 18 | 0 | 17 | 0 | 240 | 94 | 0 | 0 | 5 | 100 | 0 | 17 | 0 | 26 | 0 | 370 | 0 | 53 | 0 | 34 | 0 | 17 | 33 | 55 | 0 | 290 | 0 | 0 |  | 928 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 22 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 75 | 0 | 170 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 193 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 560 | 0 | 0 | 0 | 4 | 95 | 0 | 0 | 0 | 0 | 36 | 0 | 519 | 168 | 0 |  | 9061 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 160 | 12 | 0 | 398 | 334 | 0 | 0 | 450 | 298 | 0 | 0 | 0 | 208 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 23 | 0 | 17 | 11 | 0 | 0 | 25 | 0 | 120 | 0 | 0 | 224 | 0 | 0 | 0 | 0 | 0 | 28 | 84 | 10 | 0 | 33 | 13 | 34 | 0 | 0 | 0 | 290 | 300 | 210 | 0 | 0 | 39 | 0 | 0 | 14 | 0 | 48 | 25 | 18 | 8 | 33 | 20 | 142 | 208 | 0 | 19 | 0 | 33 | 28 | 52 | 49 | 0 | 0 | 61 | 83 | 0 | 0 | 17 | 0 | 10 | 290 | 12 | 8 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 70 | 17 | 0 | 241 | 115 | 0 | 17 | 0 | 175 | 0 | 51 | 34 | 55 | 50 | 400 | 17 | 0 | 0 | 34 | 0 | 35 | 0 | 93 | 0 | 300 | 1 | 0 |  | 856 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 30 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 76 | 0 | 170 | 0 | 0 | 167 | 0 | 0 | 0 | 0 | 0 | 169 | 0 | 381 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 680 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 459 | 0 | 0 |  | 10231 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 0 | 64 | 0 | 400 | 330 | 0 | 0 | 450 | 300 | 50 | 90 | 15 | 218 | 0 | 100 | 50 | 92 | 145 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 19 | 23 | 23 | 33 | 32 | 48 | 0 | 25 |  | 120 | 0 | 25 | 225 | 0 | 0 | 0 | 0 | 22 | 60 | 84 | 76 | 51 | 40 | 13 | 25 | 0 | 0 | 0 | 330 | 300 | 210 | 0 | 0 | 41 | 0 | 0 | 51 | 0 | 40 | 52 | 18 | 9 | 33 | 20 | 166 | 210 | 0 | 17 | 0 | 35 | 30 | 51 | 44 | 0 | 0 | 61 | 84 | 0 | 200 | 20 | 0 | 10 | 290 | 12 | 8 | 0 | 300 | 300 | 100 | 180 | 80 | 70 | 0 | 100 | 17 | 150 | 400 | 115 | 105 | 105 | 0 | 294 | 54 | 51 | 114 | 94 | 90 | 400 | 90 | 0 | 162 | 107 | 0 | 35 |  | 94 | 54 | 350 |  |  |  | 942 | 0 | 355 |  | 98 | 0 | 0 | 0 | 35 | 75 | 40 | 170 | 35 | 16 | 0 | 0 | 70 | 26 | 34 | 80 | 14 | 42 | 42 | 8 | 35 | 22 | 0 | 8 | 75 | 0 | 170 | 0 | 0 | 200 |  | 0 | 0 | 0 | 0 | 160 | 0 | 414 | 17 | 0 | 70 | 105 | 95 | 0 | 0 | 95 | 1244 | 0 |  | 150 |  |  | 115 | 0 |  | 0 |  | 0 | 500 |  | 0
Forecast for Day | 0 | 0 | 0 | 180 | 0 | 16 | 0 | 400 | 300 | 0 | 0 | 450 | 300 | 16 | 90 | 15 | 218 | 0 | 90 | 50 | 48 | 145 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 19 | 23 | 23 | 33 | 32 | 48 | 0 | 25 | 0 | 120 | 0 | 25 | 225 | 0 | 0 | 0 | 0 | 22 | 45 | 66 | 76 | 0 | 26 | 13 | 15 | 0 | 0 | 0 | 300 | 300 | 210 | 0 | 0 | 41 | 0 | 0 | 51 | 0 | 37 | 52 | 18 | 9 | 33 | 20 | 143 | 210 | 0 | 17 | 1.6 | 35 | 30 | 51 | 44 | 0 | 0 | 40 | 85 | 0 | 150 | 20 | 0 | 10 | 280 | 12 | 8 | 0 | 300 | 300 | 50 | 160 | 0 | 35 | 20 | 50 | 17 | 80 | 400 | 100 | 105 | 105 | 5 | 120 | 17 | 17 | 17 | 9 | 63 | 400 | 54 | 50 | 108 | 107 | 0 | 35 | 30 | 94 | 17 | 311 |  |  |  | 942 | 0 | 200 | 0 | 85 | 0 | 0 | 0 | 22 | 55 | 40 | 170 | 25 | 16 | 0 | 0 | 70 | 26 | 0 | 80 | 14 | 34 | 24 | 0 | 35 | 22 | 0 | 8 | 75 | 0 | 170 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 414 | 17 | 0 | 35 | 0 | 42 | 0 | 8 | 95 | 750 | 0 |  | 17 | 6 | 100 | 35 | 0 |  | 0 | 30 | 0 | 500 | 130 | 0 |  |  |  |  | g | h | o | c | h | t | s
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 298 | 248 | 0 | 0 | 300 | 298 | 0 | 0 | 0 | 90 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 9 | 17 | 4 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 9 | 40 | 0 | 0 | 0 | 310 | 260 | 150 | 0 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 9 | 33 | 21 | 106 | 208 | 0 | 0 | 1 | 33 | 28 | 0 | 0 | 0 | 0 | 61 | 30 | 0 | 120 | 18 | 0 | 10 | 305 | 16 | 8 | 0 | 0 | 0 | 0 | 47 | 0 | 0 | 9 | 12 | 17 | 0 | 240 | 49 | 0 | 17 | 2 | 50 | 0 | 17 | 0 | 28 | 12 | 360 | 0 | 25 | 0 | 34 | 0 | 17 | 13 | 36 | 0 | 260 | 0 | 0 | 0 | 924 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 160 | 18 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 75 | 0 | 170 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 500 | 0 | 0 | 0 | 1 | 47 | 0 | 0 | 0 | 0 | 16 | 0 | 425 | 73 | 0 | 0 |  |  |  | 139.663 | 20.0436 | 15.4385 | 32.5003 | 0.12792 | 2.953 | 2.7845
213.5109
| Minimum Generation |  | 7059 | 6:00
| Highest Generation |  | 10231 | 21:00
| Day Peak Generation |  | 9061 | 12:00
| Evening Peak Generation |  | 10231 | 21:00
| HVDC Max Flow |  | 928 | 12:00
| HVDC EvPeak Flow |  | 856 | 21:00
| Load factor L.F |  | 86.95% | [161 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2023-04-25
Till now the maximum generation is : - |  |  |  | 15648 | 21:00 | Hrs on | 2023-04-19
The Summary of Yesterday's |  |  | 2023-04-24 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 9061 | MW Hour : | 12:00 | Min. Gen. at | 6:00 | 7813
Evening Peak Generation : |  |  | 10231 | MW Hour : | 21:00 | Available Max Generation : |  | 15462
E.P. Demand (at gen end) : |  |  | 10231 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 11000
Maximum Generation : |  |  | 10231 | MW Hour : | 21:00 | Reserve(Generation end) |  | 4462
Total Gen. (MKWH) : |  |  | 213.5109 | System Load Factor : | 86.95% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | -74 | MW at | 7:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2023-04-25
Actual : |  | 75.3 | Ft.(MSL) , | Rule curve : | 83.2 | Ft.( MSL )
Gas Consumed : |  | Total = | 1096.1 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 153605865.916
: |  |  | Coal : | 169215136.13 | Oil : | 200831394.2 | Total : | 523652396.246
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 0 | 0:00 | 3784.5363 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 1043.9353 |  |  | 0 | 0%
Khulna Area |  | 0 | 0:00 | 1371.5095 |  |  | 0 | 0%
Rajshahi Area |  | 0 | 0:00 | 1209.1255 |  |  | 0 | 0%
Cumilla Area |  | 0 | 0:00 | 1032.782 |  |  | 0 | 0%
Mymensingh Area |  | 0 | 0:00 | 848.3185 |  |  | 0 | 0%
Sylhet Area |  | 0 | 0:00 | 383.9267 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 309.2613 |  |  | 0 | 0%
Rangpur Area |  | 0 | 0:00 | 669.8549 |  |  | 0 | 0%
Total |  | 0 |  | 10653.25 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 2
2) Ghorasal-3
3) Bhula Nuton Biddut
4) Baghabari-100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
7) Shajibazar 330 MW
8) Sirajganj- 3
9) Barishal 307 MW
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
- | 10:49 | Kachua 132/33kV S/S TR-2 HT is restored.
- | 10:51 | Kachua 132/33kV S/S TR-2 LT is restored.
15:10 | 15:47 | Jhenaidah 132/33kV S/S Transformer T-1 LT Tripped showing Over current Earth fault relays Due to 33 pbs feeder loop Y phase disconnect. | [5 empty] | 40.0MW load interrup.
15:10 | 15:47 | Jhenaidah 132/33kV S/S Transformer T-2 LT Tripped showing Over current earth fault relays Due to 33 kv pbs feeder Y phase Disconnect. | [5 empty] | 40.0MW load interrup.
17:27 | 17:44 | Sirajganj 132/33kV S/S T1-(415) LT Tripped showing MICOM P 142 & Lockout Relay relays Due to T1,33KV VCB trip due to PBS-1, | [5 empty] | 3.0MW load interrup.
33KV Raygonj feeder fault.
17:27 | 17:43 | Sirajganj 132/33kV S/S T1-(415) HT Tripped showing MICOM P-142, MICOM 632, Lockout Relay relays Due to T1,132KV VCB trip | [5 empty] | 3.0MW load interrup.
due to PBS-1,33KV Raygonj feeder fault.
17:27 | 17:42 | Sirajganj 132/33kV S/S T2-(425) LT Tripped showing MICOM P 142 & Lockout. relays Due to T2,33KV VCB trip due to PBS-1, | [5 empty] | 3.0MW load interrup.
33KV Raygonj feeder fault.
18:48 | 19:51 | Mongla 132/33kV S/S T-1 LT Tripped showing 50/51 relays Due to 33 kv BICL feeder fault. | [5 empty] | 6.0MW load interrup.
18:48 | 20:14 | Mongla 132/33kV S/S T-2 LT Tripped showing 50/51 relays Due to 33 kv BICL feeder fault. | [5 empty] | 6.0MW load interrup.
19:12 | 19:23 | Ishwardi-Natore 132kV Ckt-2 Tripped from Ishurdi 132/33kV end showing LZ32 relays Due to C PHASE TO GROUND FAULT and from
Natore 132/33kV end showing Zone 1trip, General trip,blocck A/R, sync. Fail relays Due to Wather cluudy,thandaring.
- | 20:03 | Bhulta-Rampura 230 kV Ckt-2 is restored.
- | 20:03 | Bhulta-Rampura 230 kV Ckt-2 is restored.
- | 20:03 | Bhulta-Rampura 230 kV Ckt-2 is restored.
- | 20:03 | Bhulta-Rampura 230 kV Ckt-2 is restored.
- | 21:07 | Sylhet CCPP 225 MW GT was sync.
22:55 | 1:33 | Rajshahi 132/33kV S/S Transformer T-3 (425T) LT Forced S/D Due to T-3 33KV B phase TDS red hot maintenance .
23:25 | - | Ghorasal Unit-7 365 MW was forced shutdown due to problem in air compressor.
23:44 | 1:25 | Rajshahi 132/33kV S/S Transformer T-3 (425T) HT Forced S/D Due to T-3 33KV B phase TDS red hot maintenance.
7:01 | - | Khulna (C) S/S TR-1 425T LT Scheduled S/D Due to Transformer oil leakage.
7:02 | - | Khulna (C) S/S TR-1 425T HT Scheduled S/D Due to Transformer oil leakage.
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2023-04-24 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4268250
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 160 | 3121400 | ST under S/D
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 12 | 116045 | Transformer overload.
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 398 | 8480770
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 334 | 6898000 | Machine problem
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 8215500
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 0 | 17280 | Reserve
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 298 | 6735069 | FGMO
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 0 | 0 | Reserve
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 0 | 0 | Reserve
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 14 | 112392 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 39 | 1069000 | Frequency control
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 0 | 0 | Reserve
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 208 | 2754147 | ST Under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Reserve
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 0 | 0 | Reserve
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 0 | 0 | Reserve
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 0 | 0 | Reserve
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 0 | 0 | Reserve
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 23 | 581160 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 17 | 418740 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 11 | 266200 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 0 | 11040 | Reserve
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 0 | 0 | Reserve
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 0 | 0 | Reserve
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 0 | 0 | Reserve
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 0 | 28877 | Reserve
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 17 | 142080 | Low Demand
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 0 | 0 | Reserve
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 205777
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 0 | Reserve
| Dhaka area Total |  |  |  | 5847 | 2161 | 43441727
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 120 | 2800000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 0 | 0 | Reserve
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 127170
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 33 | 322080 | Low Demand
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 25 | 127920 | Low Water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 224 | 5126173
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 17 | 100364 | Low Demand
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 28 | 120864 | Low Demand
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 84 | 939305 | Engine problem
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 10 | 100920 | Low Demand
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 70 | 755520 | Low Demand
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 13 | 295824 | Gas shortage
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 34 | 726720
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 14400 | Reserve
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 31559
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 175 | 2627018 | Low Demand
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 0 | Reserve
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 51 | 735160 | Low Demand
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 50 | 343680 | Reserve
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 34 | 839291 | Low Demand
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 0 | 1 | 6690 | On test.
| Chattogram area Total |  |  |  | 2382 | 969 | 16140658
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 210 | 4493000 | FGMO
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 290 | 7411100 | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 300 | 6805000 | FGMO
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 300 | 6582600
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 39 | 606024
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 0 | 0 | Contract Expired
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 0 | 0 | Under S/D
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 14 | 290494 | Transformer overload.
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 0 | 0 | Reserve
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 48 | 475504
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 17 | 430560 | Low Demand
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 411480 | Engine problem
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 211680 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 142 | 2952960
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 726900
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 25 | 561782 | Low Demand
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 20 | 455550 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Fuel shortage
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 34 | 389880 | Low Demand
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 55 | 551880 | Low Demand
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 35 | 530280 | Low Demand
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 93 | 1470720 | Engine problem
| Cumilla Area Total |  |  |  | 3151 | 1681 | 35357394
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 208 | 4788480
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 377640 | Engine problem
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 14950
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 150 | 1740000 | Low Demand
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 115 | 1718400
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 389310
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 163200
| Mymensingh Area Total |  |  |  | 614 | 492 | 9191980
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 33 | 785000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 28 | 634560 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Under maint.
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 52 | 600600
| Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 49 | 641664
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 8 | 175008 | Engine problem
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 61 | 1182528
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 83 | 739200
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 0 | 291710 | Gas Line work by JGTDSL
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 407000
| Sylhet 50MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 12 | 62016 | Engine problem
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 6619000 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 241 | 5776000 | FGMO
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 100620
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 400 | 8697200
| Sylhet Area Total |  |  |  | 2427 | 1284 | 26712106
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Fuel shortage
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 856 | 20043636
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 0 | 0 | Reserve
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel conservation
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 355 | 6815520 | FGMO
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 0 | 0 | Reserve
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Reserve
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Reserve
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 497520
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 0 | 0 | 0 | On test.
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 660*2 | 617 | 0 | 0 | On test.
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3001 | 1211 | 27356676
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 30 | 569561 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 170 | 4018518 | Machine problem
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 680 | 15178400 | Low Demand
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 0 | 0 | Under maint.
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Reserve
| Barisal 307 MW |  | BCPCL | 307*1 | 307 | 0 | 0 | Coal shortage
| Barisal Area Total |  |  |  | 2265 | 880 | 19766479
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 70 | 1285000 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Reserve
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 167 | 3781409 | FGMO
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 169 | 3966845 | FGMO
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 381 | 7063927 | FGMO
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 173040
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 0 | 131778 | Reserve
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Reserve
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Reserve
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | Reserve
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | Reserve
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 29760
| Adani Power Jharkhanda Ltd |  | Import | 0 | 0 | 459 | 11361818 | On test.
| Rajshahi Area Total |  |  |  | 2129 | 1268 | 27793577
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 76 | 1786473 | Coal shortage
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 170 | 4173600 | Coal shortage
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 39 | 192662 | Low Demand
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 48884
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 0 | 109056 | Reserve
| Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 247014
| Teesta Solar Limited |  | BPCL | 16*12.5 | 0 | 0 | 1192600
| Rangpur Area Total |  |  |  | 750 | 285 | 7750289
| Total |  |  |  | 22566 | 10231 | 213510886
| Eastern Grid Total |  |  |  | 14421 | 6587 | 130843865
| Western Grid Total |  |  |  | 8145 | 3644 | 82667021
| National Grid Total |  |  |  | 22566 | 10231 | 213510886
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2023-04-24
| (a) ENTIRE EASTERN GRID : |  | 6427 | MW | (b) ENTIRE WESTERN GRID : |  | 3298 | MW
| i) Dhaka area |  | 2662 | MW | i) Khulna area |  | 1179.8 | MW
| ii) Chittagong area |  | 1117 | MW | ii) Rajshahi area |  | 991.2 | MW
| iii) Comilla area |  | 1188 | MW | iii) Barisal area |  | 382 | MW
| iv) Mymensingh area |  | 998 | MW | iv) Rangpur area |  | 745 | MW
| v) Sylhet area |  | 462 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 9725 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | Chhatak | 28 | 23:00 | Kamrangirchar | 20 | 00:00 | Natore | 120 | 14:00 | Shitalakhya | 54 | 23:00
2 | AKSML | 6 | 17:00 | Chowmuhani | 201 | 22:00 | Kaptai | 4 | 18:30 | Nawabganj | 35.9 | 14:00 | Sholosohor | 21 | 19:00
3 | Aftabnagar | 24 | 19:00 | Chuadanga | 86 | 14:00 | Kazla | 38 | 22:00 | Netrakona | 144 | 19:00 | Shyampur | 42 | 23:00
4 | Agargaon | 61 | 13:00 | Coxsbazar | 121 | 21:00 | Keranigonj | 42 | 20:00 | New | 32 | 22:00 | Siddhirganj | 58 | 22:00
5 | Agrabad | 50 | 13:00 | Cumilla(N) | 142 | 21:00 | Khagrachori | 28 | 19:00 | Niamatpur | 95 | 13:00 | Sirajganj | 82 | 14:00
6 | Amnura | 77 | 00:00 | Cumilla(S) | 148 | 23:00 | Khulna | 64 | 19:00 | Noapara | 39 | 19:00 | Sonargaon | 44 | 20:00
7 | Ashuganj | 59 | 22:00 | Daudkandi | 118 | 21:00 | Khulshi | 119 | 22:00 | PHP | 3 | 20:00 | Sreemongol | 64 | 19:30
8 | BIPTC | N/A | N/A | Dhaka | 16 | 11:00 | Kishoreganj | 146 | 20:00 | Pabna | 82 | 14:00 | Sreepur | 31.5 | 21:00
9 | BSRM | 103 | 14:00 | Dhamrai | 70 | 14:00 | Kodda | 126 | 14:00 | Palashbari | 122 | 19:30 | Srinagar | 38.09 | 14:00
10 | Bagerhat | 75 | 19:30 | Dhanmondi | 80 | 13:00 | Kulaura | 38 | 19:30 | Panchagarh | 47 | 19:00 | Sunamganj | 48 | 22:00
11 | Bakulia | 74 | 14:00 | Dohazari | 86 | 22:00 | Kurigram | 66 | 19:00 | Patuakhali | 95 | 23:00 | Sylhet | 114 | 20:00
12 | Banani | 28 | 13:00 | Faridpur | 105 | 19:30 | Kushtia | 84 | 14:00 | Payra | 20 | 23:00 | TK | 27 | 00:00
13 | Bangabhaban | 21 | 10:00 | Fatullah | 30 | 16:00 | Lalbag | 17 | 13:00 | Postogola | 34 | 22:00 | Tangail | 202 | 14:00
14 | Barapukuria | 58 | 19:30 | Fenchuganj | 40 | 23:00 | Lalmonirhat | 44 | 19:30 | Purbachal | 13 | 22:00 | Thakurgaon | 83 | 19:30
15 | Barguna | 18 | 22:00 | Feni | 111 | 18:30 | Madanganj | 22 | 22:00 | Purbasadipur | 100 | 19:30 | Tongi | 69 | 14:00
16 | Barishal | 81 | 22:00 | GPH | 71 | 23:00 | Madaripur | 87 | 21:00 | Rahanpur_I | 0 | 00:00 | Ullon | 29 | 18:30
17 | Barishal-230 | 80 | 21:00 | Ghorashal | 56 | 23:00 | Madartek | 56 | 22:00 | Rahim | 0 | 00:00 | Uttara | 53 | 14:00
18 | Baroaulia | 51 | 20:00 | Goalpara | 32 | 13:00 | Madunaghat | 52 | 19:00 | Rajbari | 50 | 14:00 | UttaraNew | 21 | 12:00
19 | Baroirhat | 55 | 19:00 | Gollamari | 37 | 13:00 | Magura | 48 | 14:00 | Rajendrapur | 62 | 19:30 | Zigatola | 49 | 14:00
20 | Bashundhara | 100 | 15:00 | Gopalganj | 81.8 | 19:30 | Mahasthangarh | 62 | 15:00 | Rajshahi | 121 | 00:00
21 | BashundharaCement | 0 | 00:00 | Gulshan | 80 | 13:00 | Manikganj | 69 | 12:00 | Rajshahi-230 | 32 | 00:00
22 | Beanibazar | 56 | 18:30 | Halishahar | 62 | 18:30 | Maniknagar | 60 | 13:00 | Ramganj | 120 | 19:00
23 | Benapole | 46 | 13:00 | HaripurSBU | 45 | 21:00 | Matarbari | 45 | 21:00 | Rampur | 26 | 00:00
24 | Bhaluka | 100 | 15:00 | Hasnabad | 54 | 19:00 | Matuail | 27 | 23:00 | Rangamati | 16 | 19:00
25 | Bhandaria | 45 | 22:00 | Hathazari | 60 | 19:00 | Millgate | 28 | 13:00 | Rangpur | 123 | 19:00
26 | Bhangura | 33 | 11:00 | Ishurdi | 48 | 14:00 | Mirpur | 82 | 21:00 | Ruppur | 3.6 | 11:00
27 | Bheramara(GK) | 51 | 00:00 | Jaldhaka | 67 | 19:00 | Mirsorai | 4.5 | 19:00 | SSM | 0 | 00:00
28 | Bhulta | 93 | 22:00 | Jamalpur | 171 | 14:00 | Mithapukur | 41 | 19:00 | Saidpur | 93 | 19:30
29 | Bog-Sherpur | 48 | 13:00 | Jashore | 99 | 13:00 | Modern | 0 | 00:00 | Satkhira | 105 | 00:00
30 | Bogura | 123 | 15:00 | Jhenaidah | 104 | 14:00 | Mogbazar | 73 | 13:00 | Satmasjid | 72 | 14:00
31 | Borhanuddin | 59 | 22:00 | Joydebpur | 75 | 14:00 | Mongla | 14 | 00:00 | Savar | 90 | 19:00
32 | Brahmanbaria | 161 | 22:00 | Joypurhat | 59 | 22:00 | Motijheel | 23 | 11:00 | Shahjadpur | 88 | 13:00
33 | Cantonment | 87 | 19:00 | Juldah | 20 | 00:00 | Munshiganj | 82 | 15:00 | Shahjibazar | 94 | 22:00
34 | Chandpur | 62 | 22:00 | KSRM | 3 | 07:00 | Mymensingh | 168 | 12:00 | Shahmirpur | 30 | 00:00
35 | Chandraghona | 28 | 19:30 | Kabirpur | 122 | 15:00 | Naogaon | 101 | 14:00 | Shariatpur | 67 | 21:00
36 | Chapai | 58 | 00:00 | Kachua | 74 | 22:00 | Narail | 43 | 19:30 | Sherpur | 156 | 18:30
37 | Charsaidpur | 18 | 16:00 | Kallyanpur | 63 | 21:00 | Narinda | 32 | 13:00 | Shikalbaha | 29 | 19:00
38 | Chauddagram | 57 | 19:00 | Kalurghat | 20 | 00:00 | Narshingdi | 130 | 20:00 | Shikalbaha-230 | N/A | N/A
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2023-04-24 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 421 | 04:00 | 411 | 13:00 | Kaliakoir | 403 | 07:00 | 394 | 15:00
| Bhulta | 402 | 02:00 | 394 | 15:00 | Madunaghat_I | 406 | 19:00 | 380 | 11:00
| Bibiana | 411 | 08:00 | 402 | 01:00 | Payra | 425 | 04:00 | 420 | 18:30
| BIPTC | 407 | 01:00 | 393 | 12:00 | Rahanpur_I | 423 | 18:00 | 410 | 13:00
| Gopalganj | 423 | 01:00 | 393 | 19:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 242 | 04:00 | 229 | 11:00 | Hathazari | 233 | 19:00 | 219 | 10:00
| AKSML | 236 | 19:00 | 216 | 13:00 | Ishurdi | 237 | 17:00 | 226 | 12:00
| Aminbazar | 243 | 07:00 | 211 | 03:00 | Jhenaidah | 235 | 16:00 | 214 | 13:00
| Ashuganj | 242 | 02:00 | 238 | 10:00 | Kaliakoir | 240 | 08:00 | 234 | 13:00
| Baghabari | 235 | 17:00 | 227 | 12:00 | Keranigonj | 240 | 02:00 | 235 | 13:00
| Barapukuria | 220 | 00:00 | 217 | 07:00 | Khulna(S) | 241 | 16:00 | 221 | 19:30
| Barishal | 235 | 09:00 | 226 | 13:00 | Madunaghat_I | 236 | 19:00 | 220 | 11:00
| Bheramara | 235 | 18:00 | 223 | 12:00 | Maniknagar | 240 | 06:00 | 235 | 12:00
| Bhulta | 242 | 04:00 | 236 | 13:00 | Meghnaghat | 244 | 07:00 | 240 | 13:00
| Bibiana | 243 | 03:00 | 235 | 16:00 | Mirsorai | 234 | 19:00 | 222 | 12:00
| BIPTC | 237 | 17:00 | 223 | 12:00 | Rajshahi | 236 | 18:00 | 221 | 13:00
| Bogura | 230 | 06:00 | 223 | 12:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 237 | 06:00 | 226 | 20:00 | Rampura | 241 | 04:00 | 235 | 12:00
| BSRM | 234 | 19:00 | 222 | 13:00 | Shikalbaha | 230 | 19:30 | 219 | 11:00
| Cumilla(N) | 236 | 04:00 | 231 | 10:00 | Shyampur | 239 | 02:00 | 235 | 14:00
| Fenchuganj | 244 | 08:00 | 237 | 18:30 | Siddhirganj | 242 | 03:00 | 237 | 13:00
| Ghorashal | N/A | N/A | N/A | N/A | Sirajgonj | 241 | 18:00 | 235 | 13:00
| GPH | 232 | 19:00 | 219 | 10:00 | Sreepur | 239 | 18:00 | 235 | 00:00
| Haripur | 238 | 00:00 | 234 | 10:00 | Tongi | 236 | 07:00 | 232 | 09:00
| Hasnabad | 241 | 07:00 | 236 | 15:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 140 | 02:00 | 135 | 13:00 | Lalbag | 140 | 06:00 | 134 | 12:00
| Agargaon | 140 | 02:00 | 136 | 12:00 | Lalmonirhat | 131 | 05:00 | 120 | 18:30
| Agrabad | 136 | 19:00 | 125 | 10:00 | Madanganj | 139 | 07:00 | 135 | 13:00
| AKS | 132 | 18:30 | 125 | 10:00 | Madaripur | 139 | 16:00 | 128 | 19:30
| Aminbazar | 138 | 07:00 | 135 | 13:00 | Madartek | 140 | 04:00 | 135 | 12:00
| Amnura | 136 | 18:00 | 126 | 01:00 | Madunaghat | 137 | 19:00 | 127 | 10:00
| Ashuganj | 142 | 02:00 | 139 | 15:00 | Magura | 142 | 05:00 | 128 | 19:30
| Bagerhat | 140 | 16:00 | 123 | 19:30 | Mahasthangarh | 133 | 04:00 | 127 | 13:00
| Bakulia | 137 | 19:00 | 127 | 13:00 | Manikganj | 136 | 04:00 | 130 | 11:00
| Banani | 140 | 02:00 | 136 | 12:00 | Maniknagar | 141 | 06:00 | 137 | 12:00
| Bangabhaban | 140 | 00:00 | 137 | 12:00 | Matarbari | 121 | 19:00 | 112 | 10:00
| Barapukuria | 138 | 03:00 | 132 | 07:00 | Matuail | 140 | 05:00 | 136 | 13:00
| Barguna | 138 | 08:00 | 131 | 19:00 | Millgate | 139 | 01:00 | 135 | 12:00
| Barishal | 137 | 08:00 | 127 | 19:00 | Mirpur | 137 | 05:00 | 133 | 13:00
| Barishal-230 | 140 | 05:00 | 133 | 13:00 | Mithapukur | 132 | 03:00 | 125 | 14:00
| Baroaulia | 136 | 19:00 | 126 | 13:00 | Modern | 137 | 19:00 | 126 | 13:00
| Baroirhat | 134 | 13:00 | 123 | 23:00 | Mogbazar | 141 | 03:00 | 137 | 12:00
| Bashundhara | 140 | 06:00 | 135 | 12:00 | Mongla | 139 | 05:00 | 125 | 13:00
| BashundharaCement | 139 | 07:00 | 135 | 13:00 | Motijheel | 140 | 00:00 | 137 | 12:00
| Beanibazar | 134 | 06:00 | 125 | 18:30 | Munshiganj | 138 | 00:00 | 135 | 13:00
| Benapole | 140 | 05:00 | 125 | 13:00 | Mymensingh | 131 | 02:00 | 119 | 07:00
| Bhaluka | 131 | 04:00 | 118 | 10:00 | Naogaon | 129 | 18:00 | 120 | 13:00
| Bhandaria | 135 | 08:00 | 122 | 22:00 | Narail | 140 | 05:00 | 127 | 13:00
| Bhangura | 140 | 17:00 | 135 | 00:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bheramara | 137 | 16:00 | 132 | 12:00 | Narshingdi | 138 | 05:00 | 133 | 13:00
| Bheramara(GK) | 137 | 16:00 | 131 | 12:00 | Natore | 136 | 18:00 | 127 | 08:00
| Bhulta | 133 | 02:00 | 130 | 12:00 | Nawabganj | 139 | 04:00 | 132 | 12:00
| Bog-Sherpur | 137 | 18:00 | 130 | 12:00 | Netrakona | 131 | 06:00 | 120 | 10:00
| Bogura | 136 | 18:00 | 130 | 12:00 | New | 140 | 00:00 | 136 | 08:00
| Bogura-230 | 136 | 18:00 | 130 | 12:00 | Niamatpur | 127 | 02:00 | 114 | 13:00
| Brahmanbaria | 139 | 05:00 | 133 | 22:00 | Noapara | 141 | 06:00 | 127 | 13:00
| Cantonment | 140 | 02:00 | 135 | 13:00 | Pabna | 138 | 16:00 | 129 | 12:00
| Chandpur | 131 | 19:00 | 120 | 23:00 | Palashbari | 130 | 02:00 | 120 | 18:30
| Chandraghona | 136 | 19:00 | 127 | 13:00 | Panchagarh | 134 | 04:00 | 123 | 07:00
| Chapai | 137 | 18:00 | 129 | 12:00 | Patuakhali | 138 | 06:00 | 133 | 19:00
| Charsaidpur | 140 | 04:00 | 136 | 13:00 | Payra | 141 | 06:00 | 130 | 01:00
| Chauddagram | 132 | 19:00 | 125 | 23:00 | PHP | 131 | 19:00 | 123 | 10:00
| Chhatak | 134 | 03:00 | 125 | 18:30 | Postogola | 139 | 05:00 | 135 | 13:00
| Chowmuhani | 128 | 19:00 | 116 | 23:00 | Purbachal | 140 | 00:00 | 135 | 13:00
| Chuadanga | 141 | 15:00 | 123 | 19:30 | Purbasadipur | 132 | 05:00 | 120 | 13:00
| Coxsbazar | 120 | 19:00 | 112 | 00:00 | Rahim | 140 | 03:00 | 130 | 17:00
| Cumilla(N) | 137 | 19:00 | 131 | 18:30 | Rajbari | 136 | 16:00 | 126 | 13:00
| Cumilla(S) | 134 | 08:00 | 128 | 13:00 | Rajendrapur | 138 | 04:00 | 131 | 14:00
| Daudkandi | 136 | 03:00 | 129 | 13:00 | Rajshahi | 136 | 17:00 | 127 | 12:00
| Dhaka | 140 | 02:00 | 136 | 12:00 | Rajshahi-230 | 136 | 17:00 | 127 | 13:00
| Dhamrai | 144 | 04:00 | 132 | 15:00 | Ramganj | 126 | 19:00 | 118 | 01:00
| Dhanmondi | 140 | 02:00 | 130 | 23:00 | Rampur | 137 | 19:00 | 125 | 13:00
| Dohazari | 128 | 19:30 | 124 | 10:00 | Rampura | 140 | 02:00 | 135 | 13:00
| Faridpur | 136 | 15:00 | 128 | 13:00 | Rangamati | 135 | 19:00 | 126 | 13:00
| Fatullah | 140 | 04:00 | 136 | 15:00 | Rangpur | 130 | 03:00 | 124 | 19:00
| Fenchuganj | 139 | 06:00 | 133 | 21:00 | Ruppur | 139 | 16:00 | 131 | 13:00
| Feni | 132 | 19:00 | 123 | 23:00 | Saidpur | 132 | 03:00 | 122 | 19:00
| Ghorashal | 144 | 01:00 | 141 | 21:00 | Satkhira | 138 | 16:00 | 124 | 19:30
| Goalpara | 142 | 06:00 | 130 | 12:00 | Satmasjid | 140 | 04:00 | 135 | 13:00
| Gollamari | 137 | 16:00 | 127 | 13:00 | Savar | 136 | 07:00 | 132 | 13:00
| Gopalganj | 136 | 06:00 | 126 | 19:30 | Shahjadpur | 144 | 17:00 | 137 | 08:00
| Gopalganj-400 | 139 | 16:00 | 129 | 19:00 | Shahjibazar | 138 | 05:00 | 134 | 15:00
| Gulshan | 139 | 04:00 | 135 | 12:00 | Shahmirpur | 135 | 19:00 | 125 | 14:00
| Halishahar | 137 | 19:00 | 126 | 13:00 | Shariatpur | 138 | 16:00 | 127 | 19:30
| Haripur | 140 | 03:00 | 137 | 13:00 | Sherpur | 128 | 11:00 | 107 | 10:00
| HaripurSBU | 140 | 03:00 | 137 | 13:00 | Shikalbaha | 138 | 19:00 | 127 | 10:00
| Hasnabad | 138 | 06:00 | 135 | 15:00 | Shikalbaha-230 | 136 | 19:30 | 128 | 14:00
| Hathazari | 139 | 11:00 | 128 | 10:00 | Shitalakhya | 139 | 04:00 | 134 | 16:00
| Ishurdi | 138 | 16:00 | 131 | 12:00 | Sholosohor | 136 | 19:00 | 127 | 10:00
| Jaldhaka | 131 | 04:00 | 121 | 07:00 | Shyampur | 139 | 06:00 | 136 | 12:00
| Jamalpur | 131 | 11:00 | 112 | 10:00 | Shyampur-230 | 139 | 02:00 | 136 | 13:00
| Jashore | 138 | 15:00 | 124 | 13:00 | Siddhirganj | 139 | 03:00 | 136 | 13:00
| Jhenaidah | 143 | 16:00 | 130 | 13:00 | Sirajganj | 139 | 18:00 | 131 | 12:00
| Jhenaidah-230 | 142 | 16:00 | 130 | 19:30 | Sonargaon | 138 | 00:00 | 134 | 10:00
| Joydebpur | 144 | 03:00 | 138 | 13:00 | Sreemongol | 136 | 00:00 | 131 | 18:30
| Joypurhat | 128 | 18:00 | 115 | 13:00 | Sreepur | 133 | 00:00 | 129 | 17:00
| Juldah | 138 | 18:30 | 127 | 04:00 | Srinagar | 138 | 01:00 | 133 | 12:00
| Kabirpur | 138 | 00:00 | 132 | 15:00 | SSM | 138 | 19:30 | 128 | 13:00
| Kachua | 130 | 19:00 | 122 | 23:00 | Sunamganj | 133 | 06:00 | 122 | 21:00
| Kaliakoir | 141 | 03:00 | 134 | 14:00 | Sylhet | 136 | 06:00 | 129 | 19:30
| Kallyanpur | 137 | 01:00 | 132 | 00:00 | Tangail | 133 | 02:00 | 126 | 15:00
| Kalurghat | 135 | 19:30 | 127 | 11:00 | Thakurgaon | 131 | 04:00 | 120 | 07:00
| Kamrangirchar | 139 | 04:00 | 134 | 12:00 | TK | 137 | 19:00 | 127 | 13:00
| Kaptai | 132 | 07:00 | 120 | 14:00 | Tongi | 141 | 07:00 | 136 | 15:00
| Kazla | 139 | 00:00 | 137 | 14:00 | Ullon | 140 | 05:00 | 135 | 13:00
| Keranigonj | 139 | 02:00 | 133 | 13:00 | Uttara | 137 | 08:00 | 134 | 00:00
| Khagrachori | 134 | 19:00 | 127 | 10:00 | UttaraNew | 138 | 04:00 | 133 | 13:00
| Khulna | 140 | 06:00 | 126 | 19:30 | Zigatola | 139 | 06:00 | 133 | 14:00
| Khulna(S) | 141 | 05:00 | 128 | 19:30
| Khulshi | 135 | 19:00 | 124 | 13:00
| Kishoreganj | 134 | 00:00 | 127 | 10:00
| Kodda | 141 | 03:00 | 131 | 13:00
| KSRM | 134 | 20:00 | 127 | 12:00
| Kulaura | 138 | 06:00 | 133 | 18:30
| Kurigram | 130 | 04:00 | 120 | 07:00
| Kushtia | 140 | 16:00 | 130 | 13:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2023-04-24
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 120 | 6282 | 3406 | 9688 |  |  |  | QF-LDC-11
0:30 | 170 | 5774.5 | 3329 | 9103.5 | Date: | 2023-04-24
1:00 | 220 | 5267 | 3252 | 8519
1:30 | 243 | 5175 | 3181.5 | 8356.5
2:00 | 266 | 5083 | 3111 | 8194
2:30 | 273 | 5016 | 3063 | 8079 | [5 empty] | Gen. at Eve. Peak | 10231 | 10231 MW (21:00 )
3:00 | 280 | 4949 | 3015 | 7964 | [6 empty] | 21:00
3:30 | 288 | 4839 | 2983 | 7822 | [5 empty] | Gen. at Day Peak | 9061 | 9061 MW (12:00 )
4:00 | 296 | 4729 | 2951 | 7680 | [6 empty] | 12:00
4:30 | 308 | 4654 | 2908 | 7562 | [5 empty] | Highest Generation | 10231
5:00 | 320 | 4579 | 2865 | 7444 | [6 empty] | 21:00
5:30 | 330 | 4407 | 2844.5 | 7251.5
6:00 | 340 | 4235 | 2824 | 7059
6:30 | 207 | 4317.5 | 2847.5 | 7165
7:00 | 74 | 4400 | 2871 | 7271
7:30 | 39 | 4468 | 2942.5 | 7410.5
8:00 | 4 | 4536 | 3014 | 7550
8:30 | 50 | 4557.5 | 3096.5 | 7654
9:00 | 96 | 4579 | 3179 | 7758
9:30 | 173 | 4656 | 3300 | 7956
10:00 | 250 | 4733 | 3421 | 8154
10:30 | 278 | 4933 | 3428.5 | 8361.5
11:00 | 306 | 5133 | 3436 | 8569
11:30 | 278 | 5257 | 3558 | 8815
12:00 | 250 | 5381 | 3680 | 9061
12:30 | 215 | 5555 | 3743.5 | 9298.5
13:00 | 180 | 5729 | 3807 | 9536
13:30 | 198 | 5844.5 | 3851 | 9695.5
14:00 | 216 | 5960 | 3895 | 9855
14:30 | 263 | 5915 | 3826.5 | 9741.5
15:00 | 310 | 5870 | 3758 | 9628
15:30 | 355 | 5674 | 3522.5 | 9196.5
16:00 | 400 | 5478 | 3287 | 8765
16:30 | 440 | 5293 | 3179 | 8472
17:00 | 480 | 5108 | 3071 | 8179
17:30 | 475 | 4952.5 | 2993 | 7945.5
18:00 | 470 | 4797 | 2915 | 7712
18:30 | 340 | 5522.5 | 3143.5 | 8666
19:00 | 210 | 6248 | 3372 | 9620
19:30 | 200 | 6518 | 3471 | 9989
20:00 | 220 | 6494 | 3552 | 10046 |  |  |  | Executive Engineer
20:30 | 212 | 6540.5 | 3598 | 10138.5 |  |  |  | Network Operation Division
21:00 | 204 | 6587 | 3644 | 10231
21:30 | 147 | 6619.5 | 3578.5 | 10198
22:00 | 90 | 6652 | 3513 | 10165 |  |  |  |  | Page 6 of 7
22:30 | 125 | 6595.5 | 3503 | 10098.5
23:00 | 160 | 6539 | 3493 | 10032
23:30 | 140 | 6410.5 | 3449.5 | 9860
24:00 | 120 | 6282 | 3406 | 9688
10231 MW (21:00 )
9061 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2023-04-24 |  | Energy |  | 213510886
[13 empty] | 2023-04-24 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 4492 | 882 | 2013 | 0 | 794 | 1205 | 0 | 0 | 156 | 146 | 0 | 0
0:30 | 4362.5 | 789 | 1811.5 | 0 | 599.5 | 1267 | 0 | 0 | 135 | 139 | 0 | 0 |  | Date: | 43578
1:00 | 4233 | 696 | 1610 | 0 | 405 | 1329 | 0 | 0 | 114 | 132 | 0 | 0
1:30 | 4203 | 687 | 1559.5 | 0 | 370 | 1294 | 0 | 0 | 114 | 129 | 0 | 0 | [8 empty] | Total Energy | 213.5109 | Total Energy Gen MKWHr Energy Not Served MKWHr Energy Requirement MKWHr | Total Energy Gen 213.511 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 213.511 MKWHr
2:00 | 4173 | 678 | 1509 | 0 | 335 | 1259 | 0 | 0 | 114 | 126 | 0 | 0 | [8 empty] | Energy not Served | 0
2:30 | 4074 | 678 | 1522.5 | 0 | 306.5 | 1259 | 0 | 0 | 114 | 125 | 0 | 0 | [8 empty] | Energy Requirement | 213.5109
3:00 | 3975 | 678 | 1536 | 0 | 278 | 1259 | 0 | 0 | 114 | 124 | 0 | 0
3:30 | 3922.5 | 678 | 1479.5 | 0 | 256.5 | 1250.5 | 0 | 0 | 114 | 121 | 0 | 0 | [7 empty] | Shortage
4:00 | 3870 | 678 | 1423 | 0 | 235 | 1242 | 0 | 0 | 114 | 118 | 0 | 0
4:30 | 3799 | 708 | 1422 | 0 | 226.5 | 1199.5 | 0 | 0 | 90.5 | 116.5 | 0 | 0
5:00 | 3728 | 738 | 1421 | 0 | 218 | 1157 | 0 | 0 | 67 | 115 | 0 | 0
5:30 | 3637 | 738 | 1369 | 0 | 200.5 | 1157.5 | 0 | 0 | 35.5 | 109.5 | 4.5 | 0
6:00 | 3546 | 738 | 1317 | 0 | 183 | 1158 | 0 | 0 | 4 | 104 | 9 | 0
6:30 | 3573.5 | 737.5 | 1336 | 0 | 207.5 | 1158.5 | 0 | 0 | 2 | 100 | 50 | 0 | [6 empty] | Coal
7:00 | 3601 | 737 | 1355 | 0 | 232 | 1159 | 0 | 0 | 0 | 96 | 91 | 0
7:30 | 3642 | 737 | 1400.5 | 0 | 233 | 1166.5 | 0 | 0 | 0 | 94 | 137.5 | 0 | [5 empty] | Oil
8:00 | 3683 | 737 | 1446 | 0 | 234 | 1174 | 0 | 0 | 0 | 92 | 184 | 0
8:30 | 3684.5 | 737.5 | 1453 | 0 | 241.5 | 1217 | 0 | 0 | 0 | 96 | 224.5 | 0
9:00 | 3686 | 738 | 1460 | 0 | 249 | 1260 | 0 | 0 | 0 | 100 | 265 | 0
9:30 | 3726 | 832 | 1469 | 0 | 249.5 | 1262 | 0 | 0 | 0 | 102 | 315.5 | 0
10:00 | 3766 | 926 | 1478 | 0 | 250 | 1264 | 0 | 0 | 0 | 104 | 366 | 0
10:30 | 3830 | 926 | 1471 | 0 | 383 | 1254.5 | 0 | 0 | 0 | 110 | 387 | 0
11:00 | 3894 | 926 | 1464 | 0 | 516 | 1245 | 0 | 0 | 0 | 116 | 408 | 0
11:30 | 4001 | 927 | 1533 | 0 | 531 | 1284.5 | 0 | 0 | 8 | 116 | 414.5 | 0
12:00 | 4108 | 928 | 1602 | 0 | 546 | 1324 | 0 | 0 | 16 | 116 | 421 | 0
12:30 | 4236 | 928 | 1671 | 0 | 578 | 1368.5 | 0 | 0 | 16 | 120 | 381 | 0
13:00 | 4364 | 928 | 1740 | 0 | 610 | 1413 | 0 | 0 | 16 | 124 | 341 | 0
13:30 | 4364 | 928 | 1740 | 0 | 610 | 1413 | 0 | 0 | 16 | 124 | 341 | 0
14:00 | 4364 | 928 | 1740 | 0 | 610 | 1413 | 0 | 0 | 16 | 124 | 341 | 0
14:30 | 4417.5 | 926 | 1747 | 0 | 665 | 1411.5 | 0 | 0 | 16 | 128 | 271 | 0
15:00 | 4471 | 924 | 1754 | 0 | 720 | 1410 | 0 | 0 | 16 | 132 | 201 | 0
15:30 | 4316.5 | 923 | 1665 | 0 | 676 | 1293.5 | 0 | 0 | 16 | 130 | 176.5 | 0
16:00 | 4162 | 922 | 1576 | 0 | 632 | 1177 | 0 | 0 | 16 | 128 | 152 | 0
16:30 | 4037.5 | 922.5 | 1492 | 0 | 590 | 1172.5 | 0 | 0 | 16.5 | 125 | 116 | 0
17:00 | 3913 | 923 | 1408 | 0 | 548 | 1168 | 0 | 0 | 17 | 122 | 80 | 0
17:30 | 3794.5 | 908 | 1363.5 | 0 | 532 | 1164 | 0 | 0 | 17 | 121 | 45.5 | 0
18:00 | 3676 | 893 | 1319 | 0 | 516 | 1160 | 0 | 0 | 17 | 120 | 11 | 0
18:30 | 3942 | 907.5 | 1613.5 | 0 | 796.5 | 1198 | 12.5 | 0 | 58.5 | 132 | 5.5 | 0
19:00 | 4208 | 922 | 1908 | 0 | 1077 | 1236 | 25 | 0 | 100 | 144 | 0 | 0
19:30 | 4299 | 856 | 1939 | 0 | 1225 | 1351 | 25 | 0 | 152 | 142 | 0 | 0
20:00 | 4389 | 857 | 1927 | 0 | 1180 | 1365 | 25 | 1 | 160 | 142 | 0 | 0
20:30 | 4486 | 856.5 | 1993 | 0 | 1100 | 1375 | 25 | 1 | 160 | 142 | 0 | 0
21:00 | 4583 | 856 | 2059 | 0 | 1020 | 1385 | 25 | 1 | 160 | 142 | 0 | 0
21:30 | 4635 | 847.5 | 2006 | 0 | 1010 | 1370 | 25 | 0.5 | 160 | 144 | 0 | 0
22:00 | 4687 | 839 | 1953 | 0 | 1000 | 1355 | 25 | 0 | 160 | 146 | 0 | 0
22:30 | 4663.5 | 839 | 1952.5 | 0 | 958.5 | 1355 | 25 | 0 | 158 | 147 | 0 | 0
23:00 | 4640 | 839 | 1952 | 0 | 917 | 1355 | 25 | 0 | 156 | 148 | 0 | 0
23:30 | 4566 | 860.5 | 1982.5 | 0 | 855.5 | 1280 | 12.5 | 0 | 156 | 147 | 0 | 0 |  | Max Temp. in Dhaka |  | 35.1° C
24:00 | 4492 | 882 | 2013 | 0 | 794 | 1205 | 0 | 0 | 156 | 146 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 213.511 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 213.511 MKWHr
Note on W13: Author:

## Generation
g | 2023-04-24
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | [19 empty] | 25 | 25 | 25 | 25 | 25 | 25 | 0 | 127920
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2800000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [25 empty] | 0 | 0
| Teknaf 20MW PP (Solartech) | [5 empty] | 1 | 5 | 9 | 11 | 11 | 15 | 18 | 14 | 16 | 10 | 8 | 3 | 0 | [8 empty] | 127170
6 | Sikalbaha 225MW CCPP (Gas) | 228 | 227 | 227 | 227 | 227 | 180 | 181 | 181 | 201 | 223 | 219 | 217 | 219 | 221 | 220 | 220 | 221 | 221 |  | 225 | 224 | 225 | 224 | 226 | 228 | 228 | 5126173
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 67 | 67 | 67 | 67 | 67 | 4 | [5 empty] | 16 | 16 | 16 | 16 | 16 | 17 | 17 |  | 73 | 84 | 84 | 84 | 84 | 84 | 84 | 939305
12 | Hathazari 100 MW peaking PP | [20 empty] | 25 | 28 | 28 | 28 | 24 | 24 | 120864
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [19 empty] | 6 | 17 | 17 | 17 | 17 | 17 | 17 | 100364
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP | 47 | 47 | 47 | 47 | [15 empty] | 27 | 43 | 48 | 48 | 48 | 48 | 48 | 475504
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 37 | 37 | 40 | 38 | 40 | 40 | 42 | 39 | 40 | 60 | 62 | 62 | 62 | 50 | 38 | 37 | 37 |  |  |  |  | 37 | 39 | 37 | 37 | 40 | 1069000
17 | Siddhirganj 335 MW CCPP | 90 | 90 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 100 | 100 | 170 | 208 | 140 | 140 | 140 | 60 |  | 100 | 150 | 150 | 208 | 209 | 206 | 206 | 2754147
18 | Kodda 300 MW PP Unit-2 (Summit) | [25 empty] | 0 | 0
19 | Ashuganj 195MW PP (APSCL-United) | [25 empty] | 0 | 0
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4268250
24
25 | Ghorasal 365 MW CCPP Unit-7 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 160 | 160 | 130 | 130 | 130 |  | 160 | 160 | 160 | 160 | 160 | 160 | 0 | 3121400
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 36 | 10 | 10 | 10 | 10 | 10 | 10 | 35 | 10 | 10 | 10 | 10 | 33 | 31 | 34 | 34 | 37 | 37 |  | 38 | 38 | 38 | 39 | 40 | 40 | 40 | 606024
33 | Ashuganj 225 MW CCPP | 183 | 183 | 183 | 151 | 151 | 130 | 131 | 181 | 151 | 152 | 152 | 206 | 206 | 209 | 209 | 208 | 208 | 195 |  | 210 | 208 | 212 | 210 | 212 | 213 | 213 | 4493000
34 | Ashuganj 450 MW CCPP(South) | 275 | 275 | 275 | 275 | 280 | 250 | 250 | 250 | 250 | 250 | 250 | 290 | 290 | 290 | 290 | 290 | 270 | 270 |  | 280 | 280 | 280 | 300 | 300 | 300 | 300 | 6805000
| Ashuganj 450 MW CCPP(North) | 290 | 290 | 290 | 290 | 290 | 280 | 280 | 290 | 290 | 290 | 325 | 345 | 300 | 290 | 290 | 290 | 290 | 290 |  | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 7411100
| Ashuganj 420 MW CCPP(East) | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 290 | 290 | 320 | 320 | 320 | 270 | 250 | 250 |  | 250 | 250 | 250 | 300 | 300 | 270 | 270 | 6582600
35 | Ashuganj 55 MW PP (Precision)
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 386 | 386 | 337 | 316 | 286 | 278 | 278 | 269 | 275 | 342 | 344 | 344 | 381 | 401 | 396 | 367 | 326 | 304 |  | 361 | 390 | 392 | 398 | 394 | 393 | 396 | 8480770
40 | Meghnaghat 450 MW CCPP(MPL) | 320 | 320 | 320 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 320 | 350 | 350 | 350 | 320 | 300 | 300 |  | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 8215500
41 | Haripur 360MW CCPP(HPL) | 305 | 265 | 265 | 265 | 241 | 243 | 246 | 246 | 254 | 254 | 254 | 275 | 308 | 328 | 329 | 304 | 252 | 254 |  | 343 | 305 | 304 | 334 | 343 | 344 | 344 | 6898000
42 | RPCL 210MW CCPP | 215 | 216 | 216 | 216 | 187 | 149 | 214 | 213 | 210 | 205 | 204 | 199 | 197 | 202 | 201 | 201 | 203 | 146 |  | 207 | 205 | 207 | 208 | 209 | 210 | 210 | 4788480
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 1 | 11 | 27 | 40 | 49 | 53 | 53 | 51 | 46 | 37 | 20 | 5 | 1 | [8 empty] | 389310
44 | Fenchugonj CCPP Phase-1 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 785000
45 | Fenchugonj CCPP Phase-2 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 634560
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 59 | 60 | 60 | 60 | 40 | 40 |  | 61 | 61 | 61 | 61 | 62 | 62 | 63 | 1182528
48 | Shahjibazar 86MW PP (Shahjibazar) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 30 | 30 | 30 | 30 | 30 | 10 |  | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 739200
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | [23 empty] | 100 | 119 | 120 | 291710
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 17 | 18 | 18 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 18 | 18 | 407000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | [13 empty] | 8 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 100620
54 | Hobiganj 11MW PP Cofidence-E | 2 | 8 | 8 | 8 | 8 | 8 | 5 | 5 | 5 | 5 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 175008
55 | Fenchugonj 51 MW PP (Barakatullah) | 22 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 45 | 52 | 52 | 24 | 6 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 600600
56 | Shahjahanulla 25 MW PP | [19 empty] | 5 | 11 | 12 | 12 | 14 | 14 | 15 | 62016
57 | Bibiana-II 341 MW CCPP (Summit) | 270 | 270 | 275 | 245 | 275 | 190 | 230 | 285 | 280 | 300 | 285 | 280 | 275 | 270 | 280 | 275 | 265 | 250 |  | 290 | 290 | 275 | 290 | 275 | 270 | 290 | 6619000
| Bibiyana South 400 MW | 400 | 400 | 400 | 360 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 370 | 400 | 395 | 395 | 340 | 320 | 320 |  | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 8697200
58 | Nababganj 55 MW PP (Southern power ) | [25 empty] | 0 | 0
59 | Tangail Palli Power Gen 22 MW | [7 empty] | 3 | 18 | 19 | 19 | 19 | 18 | 18 | [5 empty] | 1 | 22 | 21 |  |  |  | 0 | 163200
60 | Barabkunda 22 MW PP (Regent) | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 |  | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 295824
61 | Narshingdi 22 MW PP (Doreen) | [16 empty] | 14 | 14 |  | 14 | 14 | 14 | 14 | 13 | 13 | 13 | 112392
62 | Tangail 22 MW PP (Doreen) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 19 | 16 | 16 | 16 | 377640
63 | Impoprt (Tripura) | 132 | 126 | 124 | 118 | 115 | 104 | 96 | 92 | 100 | 104 | 116 | 116 | 124 | 132 | 132 | 128 | 122 | 120 |  | 144 | 142 | 142 | 142 | 146 | 148 | 146 | 2952960
64 | Malancha, Ctg. EPZ (United) | 42 | 34 | 34 | 34 | 34 | 34 | 36 | 36 | 33 | 20 | 20 | 18 | 18 | 19 | 20 | 20 | 20 | 20 |  | 26 | 34 | 34 | 34 | 35 | 35 | 36 | 726720
65 | Feni 22MW PP (Doreen) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 16 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 411480
66 | Feni 11 MW PP (Doreen) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 9 | 9 | 211680
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 20 | 21 | 25 | 25 | 25 | 25 | 25 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 726900
68 | Cumilla 25 MW PP (Summit) | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 12 | 18 | 20 | 20 | 20 | 20 | 15 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 455550
69 | Summit Ashulia | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 |  | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 552000
70 | Summit Madhabdi | 6 | 10 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29160
71 | Maona 33 MW PP(Summit) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 418740
72 | Rupganj 33 MW PP(Summit) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  |  |  |  | 6 | 11 | 11 | 11 | 0 | 0 | 266200
73 | Ghorashal 108MW PP (Regent) | [12 empty] | 13 | 13 | 13 | 13 |  |  |  | 12 | 12 | 12 | 12 | 11 | 11 | 12 | 116045
| Feni Lanka Power | [13 empty] | 34 | 34 | 34 | 17 | 17 |  | 70 | 34 | 34 | 34 | 52 | 52 | 52 | 389880
| Chowmuhani 113 MW | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  |  |  | 27 | 26 | 28 | 28 | 28 | 28 | 28 | 28 |  | 94 | 57 | 55 | 55 | 55 | 22 | 9 | 551880
| Manikgonj 162MW PP(MPGL) | [25 empty] | 0 | 0
77 | Siddhirganj 100 PP(Dutch Bangla) | [25 empty] | 0 | 0
78 | Gazipur 52 MW PP | [19 empty] | 2 | 16 |  |  |  |  | 0 | 11040
79 | Kodda 150 MW PP | [25 empty] | 0 | 0
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 34 | 8 | 8 | [7 empty] | 1 | 16 | 34 | 41 | 52 | 52 | 52 | 16 |  | 26 | 25 | 25 | 25 | 43 | 52 | 52 | 561782
| Gazipur 100 MW PP | [19 empty] | 4 | 35 | 17 |  |  |  | 0 | 28877
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 1 | 3 | 4 | 5 | 5 | 4 | 4 | 3 | 2 | 0 | [9 empty] | 31559
| Jodiac Power | [25 empty] | 0 | 0
| Karnaphuli Power Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 19 | 51 | 34 | 34 | 34 |  | 40 | 51 | 51 | 51 | 51 | 54 | 54 | 735160
82 | Madanganj 102 PP(Summit) | [25 empty] | 0 | 0
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP ( Summit) | 273 | 271 | 277 | 271 | 274 | 281 | 277 | 282 | 296 | 307 | 305 | 301 | 299 | 272 | 281 | 233 | 231 | 230 |  | 275 | 298 | 300 | 298 | 281 | 277 | 299 | 6735069
87 | Meghnaghat 100 MW(IEL) | [19 empty] | 7 | 9 | 9 |  |  |  | 0 | 17280
| Meghnaghat 104 MW PP (OPCL) | [19 empty] | 30 | 30 | 17 | 17 | 20 | 34 | 34 | 142080
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [19 empty] | 44 | 44 | 44 | 10 | 10 |  | 0 | 100920
92 | Fenchuganj 44MW (Energyprima) | 41 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 37 | 37 | 36 | 41 | 20 | 5 |  | 25 | 47 | 47 | 49 | 49 | 49 | 49 | 641664
93 | Ashuganj 51 MW PP (Midland) | [21 empty] | 11 | 14 | 14 | 14 | 14 | 290494
94 | Gagnagar 102 MW PP (Digital Power) | [25 empty] | 0 | 0
95 | Patenga 50MW PP (Baraka) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 10 | 16 | 16 | 18 | 18 | 12 | 6 |  | 9 | 25 | 30 | 33 | 33 | 33 | 11 | 322080
96 | Chattogram 108 MW PP (ECPV) | [19 empty] | 7 | 21 |  |  |  |  | 0 | 14400
97 | katpotti 52 MW
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [25 empty] | 0 | 0
100 | Manikganj 55 MW PP (Northern) | [25 empty] | 0 | 0
101 | Kushiara 163 MW CCPP (KP)
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 0 | 0 | [8 empty] | 14950
103 | Kamalaghat 54 MW PP(Banco Energy) | [25 empty] | 0 | 0
104 | Keranigonj 300 MW PP (APR) | [25 empty] | 0
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 8 | 8 | 8 | 8 | 8 | 8 | 26 | 46 | 46 | 46 | 139 | 141 | 152 | 153 | 85 | 70 | 45 | 55 |  | 67 | 146 | 150 | 150 | 95 | 75 | 55 | 1740000
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit)
115 | Juldah 100 MW PP Unit-3 (Acorn) | 50 | 12 | 12 | 12 | 12 | 12 | 12 | [5 empty] | 12 | 30 | 50 | 30 | 12 | 12 |  | 60 | 100 | 70 | 70 | 70 | 70 | 70 | 755520
116 | Chandpur 200MW (Desh energy) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 430560
117 | Ashuganj 150MW PP (Midland) | [25 empty] | 0 | 0
118 | Bibiyana-III 400 MW CCPP | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 247 | 240 | 240 | 247 |  | 241 | 241 | 241 | 241 | 241 | 241 | 241 | 5776000
| Jamalpur 115 MW PP (United) | 35 | 35 | 35 | 16 | 16 | 16 | 47 | 47 | 47 | 47 | 94 | 94 | 94 | 94 | 89 | 75 | 75 | 75 |  | 115 | 115 | 118 | 115 | 115 | 115 | 115 | 1718400
| Anwara 300 MW PP (United) | 105 | 100 | 65 | 65 | 65 | 30 | 30 | 30 | 30 | 30 | 100 | 100 | 100 | 139 | 139 | 141 | 142 | 142 |  | 225 | 190 | 190 | 175 | 175 | 155 | 87 | 2627018
| Juldah unit-2 (Acorn) | [13 empty] | 12 | 12 | 12 | 12 | 12 |  | 90 | 50 | 50 | 50 | 50 | 25 | 25 | 343680
| Anlima Energy Ltd. | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 |  | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 839291
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 25 | 31 | 35 | 35 | 35 | 35 | 530280
| Spectra Solar Plant Ltd. | [5 empty] | 1 | 7 | 15 | 23 | 28 | 30 | 33 | 32 | 21 | 10 | 0 | 1 | [9 empty] | 205777
| Chandpur 115(Doreen) | 73 | 72 | 50 | 34 | 17 | 17 | 17 | 17 | 17 | 17 | 45 | 55 | 71 | 84 | 94 | 70 | 51 | 51 |  | 72 | 93 | 94 | 93 | 94 | 93 | 93 | 1470720
| Kanchan Purbachal Power Generation Ltd. | [25 empty] | 0
| Mirsharai 150 MW (Oil) | [20 empty] | 0 | 1 | 1 |  |  | 0 | 6690
Mirsharai 150 MW (Gas)
120 | Eastern Zone Total | 5267 | 5083 | 4949 | 4729 | 4579 | 4235 | 4400 | 4536 | 4579 | 4733 | 5133 | 5381 | 5729 | 5960 | 5870 | 5478 | 5108 | 4797 | 0 | 6248 | 6518 | 6494 | 6587 | 6652 | 6539 | 6282 | 130843865
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | [25 empty] | 0 | 0
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | [25 empty] | 0 | 0
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 1 | 22 | 43 | 66 | 90 | 94 | 95 | 31 | 6 | 5 | 40 | 26 | 3 | [8 empty] | 497520
131 | Rampal 1320 MW (BIFPCL)
132 | United Payra Power Ltd. | [25 empty] | 0
133 | Bhola Nutan Biddut BD LTD (GAS)
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [25 empty] | 0 | 0
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 171 | 168 | 171 | 171 | 171 | 171 | 160 | 160 | 160 | 160 | 160 | 160 | 166 | 171 | 160 | 171 | 153 | 158 |  | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 4018518
140 | Bhola 33 MW PP (Venture) | 27 | 26 | 25 | 22 | 21 | 17 | 16 | 18 | 17 | 18 | 20 | 22 | 24 | 25 | 23 | 23 | 22 | 21 |  | 28 | 28 | 28 | 30 | 30 | 32 | 31 | 569561
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 696 | 678 | 678 | 678 | 738 | 738 | 737 | 737 | 738 | 926 | 926 | 928 | 928 | 927 | 924 | 922 | 923 | 893 |  | 922 | 856 | 857 | 856 | 839 | 839 | 882 | 20043636
147 | Bheramara 410 MW CCPP | 355 | 355 | 250 | 250 | 200 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 220 | 355 | 355 | 300 | 200 | 200 |  | 355 | 355 | 355 | 355 | 350 | 355 | 355 | 6815520
148 | Payra 1320 MW | 570 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 560 | 650 | 710 | 650 | 510 | 500 | 500 |  | 550 | 650 | 650 | 680 | 650 | 650 | 500 | 15178400
149
150 | Barapukuria TPP Unit-1 | 75 | 75 | 75 | 76 | 76 | 75 | 76 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 76 | 76 |  | 75 | 76 | 75 | 76 | 76 | 76 | 75 | 1786473
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 |  | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 4173600
153 | Baghabari 71 MW GTPP | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 70 | 70 | 70 | 65 | 65 | 65 | 65 | 40 | 40 |  |  |  |  | 40 | 70 | 70 | 70 | 70 | 1285000
156 | Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 0 | 2 | 3 | 4 | 4 | 4 | 4 | 3 | 2 | 0 | 0 | 0 | [8 empty] | 29760
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 155 | 130 | 130 | 130 | 130 | 130 | 130 | 145 | 140 | 130 | 130 | 130 | 158 | 170 | 167 | 140 | 130 | 130 |  | 162 | 155 | 153 | 167 | 170 | 155 | 157 | 3781409
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 156 | 140 | 130 | 130 | 130 | 130 | 130 | 148 | 156 | 130 | 130 | 193 | 212 | 195 | 177 | 130 | 130 | 130 |  | 145 | 157 | 157 | 169 | 175 | 158 | 159 | 3966845
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 305 | 297 | 314 | 270 | 260 | 236 | 234 | 263 | 264 | 263 | 264 | 360 | 355 | 307 | 313 | 237 | 234 | 213 |  | 294 | 309 | 300 | 381 | 299 | 303 | 322 | 7063927
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 17 | 17 | 18 |  |  |  | 20 | 21 | 21 | 22 | 21 | 22 | 21 | 173040
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | [9 empty] | 0 | 131778
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | [26 empty] | 0
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP | [26 empty] | 0
169 | Natore 52 MW PP (Rajlanka) | [25 empty] | 0 | 0
170 | Chapainawabganj 100 MW Peaking PP | [25 empty] | 0
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [25 empty] | 0 | 0
172 | Confidence Power Bogura Unit-1 113 MW | [25 empty] | 0 | 0
173 | Rangpur 20 MW GTPP | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | [19 empty] | 34 | 34 | 34 | 39 | 34 | 34 | 34 | 192662
177 | Sympa Solar Power 8MW | [6 empty] | 1 | 3 | 5 | 7 | 7 | 7 | 7 | 7 | 3 | 4 | 2 | 1 | [8 empty] | 48884
178 | Energypac Power Venture Thakurgaon Ltd. | [19 empty] | 6 | 35 | 72 |  |  |  | 0 | 109056
| Intraco Solar 30 MW | [5 empty] | 1 | 7 | 15 | 26 | 28 | 35 | 36 | 34 | 31 | 15 | 13 | 9 | 1 | [8 empty] | 247014
| Adani Power Jharkhanda Ltd | 514 | 514 | 514 | 496 | 411 | 413 | 413 | 429 | 515 | 519 | 500 | 519 | 518 | 513 | 515 | 422 | 422 | 414 |  | 441 | 455 | 470 | 459 | 459 | 459 | 460 | 11361818
178 | Teesta Solar Limited | [5 empty] | 4 | 37 | 68 | 86 | 143 | 163 | 168 | 162 | 140 | 114 | 64 | 34 | 5 | [8 empty] | 1192600