## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2023-04-28 | Friday
|  | Date (day): | 2023-04-28 |  | Friday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11724.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14443 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2023-04-27 | 2023-04-28 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 150 | 0 | 0 | 0 | 180 |  | Gas shortage
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 28 | 12 | 16 | 76 |  | 32 | Engine problem
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 405 | 379 | 400 | 400 | 12 |  | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 324 | 303 | 300 | 330 | 30 |  | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 330 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 42 | 0 | 16 | 50 | 50 |  | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 300 | 285 | 300 | 300 |  |  | FGMO
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 0 | 0 | 90 | 90 |  | 12 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 15 | 0 | 15 | 15 | 40 |  | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 13 | 0 | 10 | 18 |  | 4 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 60 | 0 | 90 | 100 |  | 110 | GT-1 Under maint
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 95 | 0 | 90 | 90 |  | 10 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 130 | 0 | 0 | 150 |  | 185 | ST under S/D
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 24 | 0 | 48 | 92 |  | 10 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 0 | 35 | 35 | 19 |  | Fuel shortage
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 0 | 130 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 0 | 37 | 37 | 18 |  | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 0 | 35 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 41 | 26 | 41 | 41 |  | 39 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 0 | 25 | 25 |  | 8 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 0 | 16 | 32 | 32
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 8 | 0 | 48 | 50
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 30 | 0 | 300 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 300 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 0 | 0 | 50 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 80 |  | 20 | Engine problem
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 0 | 0 | 0 | 70 | 79 |  | Fuel shortage
36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 34 | 0 | 105 | 105
37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 72 | 0 | 54 | 70 |  | 34 | Engine problem
38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 17 | 0 | 108 | 162
39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 31 | 0 | 30 | 0
40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 17 | 17 | 35 | 20 |  | Fuel shortage
| Dhaka area Total |  |  |  |  | 6263 | 5847 | 2543 | 1548 | 3352 | 3987 | 499 | 1329
41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 120 | 120 | 120 | 120 | 60 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 8 | 0 | 25 | 25
43 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 18 | 0 | 20 | 0
44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 6 | 38 | 26 | 35 | 15 |  | Fuel shortage
45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 25 | 25 | 25 | 25 | 205 |  | Low Water Level
46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 218 | 220 | 225 | 225
47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 51 | 17 | 105 | 105
49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 45 | 60 |  | 38 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 66 | 84 |  | 18 | Engine problem
51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 44 | 0 | 50 | 70 |  | 30 | Engine problem
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 50 | 74 | 50 | 74 |  | 26 | Engine problem
53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 13 | 0 | 13 | 13 | 9 |  | Gas shortage
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 23 | 26 | 10 | 35
54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 0 | 50 | 58 |  | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5 | 0 | 5 | 0
56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 103 | 170 | 120 | 300
57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 17 | 0 | 17 | 54
58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 52 | 17 | 17 | 51 | 59 |  | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 38 | 12 | 63 | 90 |  | 10 | Engine problem
60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 34 | 34 | 34 | 34 | 82 |  | Fuel shortage
| Mirsharai 150 MW |  | Gas/HSD | BPDB-RPCL | 18.5*9 | 0 | 0 | 163 | 163 | 162 | 162
| Chattogram area Total |  |  |  |  | 2442 | 2382 | 988 | 967 | 1198 | 1612 | 668 | 272
61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 204 | 189 | 210 | 210 |  |  | FGMO
63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 290 | 285 | 300 | 305 |  |  | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 305 | 275 | 310 | 310 |  |  | FGMO
65 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 0 | 0 | 0 | 0
66 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 34 | 40 | 40 | 40
67 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 55 | 0 | 0 | 0 | 0 |  |  | Contract Expired
68 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 108 | 8 | 63 | 63
69 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 10 | 10 | 51 | 51
70 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 16 | 5 | 80 | 150
71 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 42 | 0 | 31 | 46
72 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under Maint.
73 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 51 | 17 | 17 | 34 | 166 |  | Fuel shortage
74 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 18 | 18 |  | 4 | Engine problem
75 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 0 | 8 | 8 |  | 3 | Engine problem
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 128 | 50 | 143 | 165
76 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 0 | 21 | 33
77 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 25 | 52
78 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 21 | 0 | 21 | 21 |  | 4 | Engine problem
79 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 0 |  |  | Contract Expired
80 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 0 | 17 | 106 |  | 8
81 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 36 | 8 | 9 | 113
82 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 0 | 35 | 35 |  | 19 | Engine problem
83 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 72 | 17 | 94 | 94 | 21 |  | Fuel shortage
| Cumilla Area Total |  |  |  |  | 3159 | 3151 | 1392 | 904 | 1493 | 1854 | 187 | 201
84 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 150 | 119 | 162 | 162
85 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 14 | 0 | 16 | 19 | 3 |  | Gas shortage
86 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0
87 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
88 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 153 | 163 | 160 | 170 |  | 30 | Engine prolem
89 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 98 | 115 | 75 | 115
90 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 41 | 0 | 50 | 0
91 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 11 | 12 | 12 | 10 |  | Fuel shortage
| Mymensingh Area Total |  |  |  |  | 717 | 614 | 470 | 408 | 476.6 | 478 | 3 | 30
92 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 32 | 32 | 33 | 33 |  | 37 | Machine problem.
93 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 28 | 28 | 28 | 28 |  | 62 | Machine problem
94 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under maint
95 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
96 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 48 | 20 | 51 | 51
97 | Fenchuganj 44MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 36 | 20 | 44 | 45
98 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 0 | 8 | 8 |  | 3 | Engine problem
99 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 58 | 61 | 61 | 61
100 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 79 | 30 | 85 | 84
101 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
102 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 202 | 0 | 190 | 202 |  | 29 | Machine problem
103 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 17 | 18 | 18
104 | Sylhet 50MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
105 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 8 | 16 | 16 | 9 |  | Gas shortage
106 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 290 | 280 | 300 | 310 |  |  | FGMO
107 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 368 | 377 | 400 | 400 |  |  | FGMO
108 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 0 | 10 | 10
109 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 385 | 274 | 50 | 50 |  | 335 | Machine Problem
| Sylhet Area Total |  |  |  |  | 2472 | 2427 | 1560 | 1147 | 1294 | 1316 | 9 | 1059
110 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 490 | 491 | 509 | 509
111 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 24 | 0 | 85 | 98 |  | 17 | Engine problem
112 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 22 | 35 |  | 19 | Engine problem
113 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
114 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 55 | 74 |  | 35 | Engine problem
115 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 400 | 200 | 90 | 410
116 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 0 | 0 | 40
117 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Fuel shortage
118 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 17 | 17 | 88 |  | Fuel shortage
119 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 15 | 0 | 0 | 100
120 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 94 | 0 | 100 | 0
| Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 0 | 0 | 97 | 0 | 0 | 0 |  |  | On test.
| Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 660*2 | 617 | 617 | 0 | 0 | 0 | 0 |  |  | Coal Shortage.
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3005 | 3001 | 1120 | 691 | 878 | 1283 | 434 | 71
121 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 32 | 0 | 16 | 64
122 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 27 | 6 | 25 | 31 |  | 9 | Engine problem
123 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 59 | 62 | 60 | 60 |  | 134 | machine problem
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
124 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 1120 | 250 | 750 | 1244
125 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 0 | 0 | 0 | 0 |  | 220 | Under maintenance
126 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 17 | 150
127 | Barisal 307 MW |  | Coal | BCPCL | 307*1 | 307 | 307 | 0 | 0 | 0 | 0 | 307 |  | Coal Shortage.
| Barisal Area Total |  |  |  |  | 2265 | 2265 | 1238 | 318 | 868 | 1549 | 307 | 363
128 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 60 | 0 | 0 | 0
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
129 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 26 | 26 |  | 26 | Engine problem
130 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 34 |  | 37 | Engine problem
131 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 14
132 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 34 | 42 |  | 8 | Engine problem
133 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 24 | 42 |  | 8 | Engine problem
134 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 178 | 149 | 190 | 190 |  |  | FGMO
135 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
136 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 184 | 159 | 160 | 200 |  |  | FGMO
137 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 380 | 424 | 380 | 380 |  |  | FGMO
138 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 35 | 35 |  | 15 | Engine problem
139 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 16 | 21 | 22 | 22
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
140 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 0 | 8 | 8 |  | 3 | Engine problem
141 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 8 | 44 |  | Fuel shortage
142 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 80 | 80 |  | 24 | Enginr problem
143 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel shortage
144 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 35 | 57 | 35 | 113
145 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 35 | 35 | 95 | 113
146 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 4 | 0 | 6 | 0
| Adani Power Jharkhanda Ltd |  | Coal | Import | 0 | 0 | 0 | 510 | 425 | 500 | 500 |  |  | On test.
| Rajshahi Area Total |  |  |  |  | 2179 | 2129 | 1410 | 1270 | 1595 | 1807 | 564 | 121
147 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 75 | 74 | 75 | 75 | 10 |  | Coal Shortage.
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
148 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 260 | 200 | 250 | 260 | 14 |  | Coal Shortage.
149 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 15 | 0 | 0 | 0 | 20 |  | Fuel conservation
150 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
151 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 34 | 111 | 42 | 107
152 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 7 | 0 | 8 | 0
153 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 35 | 115 | 35 | 115
154 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 33 | 0 | 30 | 0
| Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 0 | 0 | 155 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 830 | 750 | 614 | 500 | 570 | 557 | 64 | 85
| Total |  |  |  |  | 23332 | 22566 | 11335 | 7753 | 11724.6 | 14443 | 2735 | 3531
A. |  | 2023-04-27 | (Yesterday) |  |  |  |  | Thursday
1 | Highest Generation : |  |  | 11551 | MW at | 14:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 20:00 | hrs.
2 | Minimum Generation : |  |  | 9512 | MW at | 6:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 7753 | MW
3 | Day peak Generation : |  |  | 11335 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 7487.61 | MW
4 | Evening peak Generation : |  |  | 7753 | MW at | 20:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 241.0772 | MKWHr | By Solar | 2.5963 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Gas : | 147.003 | MKWHr |  | By Oil: | 36.2102 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 38.9229 | MKWHr |  | By Hydro: | 0.28866 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2735 | MW | Dhaka | 2433.61 | 2433.61 |  | 0 |  | 18:00 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 3531 | MW | Chittagong | 1164.6 | 1164.6 |  | 0 |  | 19:00 |  | 0
|  |  | Total = |  |  | 6266 | MW | Khulna | 465.8 | 465.8 |  | 0 |  | 19:30 |  | 0
7 | Total Gas Supplied : |  |  | 1076.18 | MMCFD |  |  | Rajshahi | 1105.2 | 1105.2 |  | 0 |  | 20:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 170873824.204 | ii) Oil : | Taka | 419639339.82 | Comilla | 196 | 196 |  | 0 |  | 21:00 |  | 0
|  | iii) Coal : | Taka | 257435735.45 | Total | Taka | 847948899.474 | Mymensingh | 898 | 898 |  | 0 |  | 22:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0.165 | MKWHr. | Sylhet | 200 | 200 |  | 0 |  | 23:00 |  | 0
| ii) During Peak Demand : |  |  | 150 | MW (E to W) at | 20:00 | hrs | Barisal | 140.4 | 140.4 |  | 0 |  | 24:00 |  | 0
| iii) Maximum : |  |  | -40 | MW at | 6:00 | hrs | Rangpur | 884 | 884 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 37.3° C |  |  | Total | 7487.61 | 7487.61 |  | 0
B. |  | 2023-04-28 | (Today) |  |  |  | Friday |  |  | Probable max. temperature in Dhaka |  |  | 38.9° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 11000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 14443 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 9000 | MW
4 | Reserve(Generation end) |  |  |  | 3443 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 229.5774 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 7561 | MW at | 6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 13.5084 | MKWHr. | ii) HVDC Flow at Peak Time |  | 491 | MW at | 20:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.5478 | MKWHr. | iii) Maximum HVDC Flow : |  | 911 | MW at | 4:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 75.22 |  | (b) Today: | 75.19 |  | (c) Rule Curve: |  | 82.6
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2023-04-27 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 150 | 180 | 0 | 77 | 0 | 360 | 335 |  | 0 | 450 | 260 | 9 | 0 | 0 | 145 | 0 | 40 | 40 | 8 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 13 | 23 | 18 | 25 | 0 | 50 | 0 | 0 | 0 | 120 | 0 | 0 | 224 | 0 | 0 | 0 |  | 10 | 0 | 84 | 56 | 0 | 6 | 13 | 40 | 0 | 0 | 0 | 300 | 300 | 211 | 197 | 0 | 42 | 0 | 0 | 51 | 0 | 46 | 52 | 18 | 8 | 33 | 21 | 142 | 192 | 0 | 19 | 0 | 33 | 28 | 53 | 46 | 0 | 0 | 61 | 80 | 0 | 201 | 18 | 0 | 10 | 285 | 16 | 8 | 0 | 0 | 0 | 0 | 47 | 0 | 17 | 0 | 38 | 34 | 0 | 409 | 48 | 105 | 51 | 0 | 88 | 17 | 52 | 106 | 9 | 38 | 400 | 72 | 0 | 72 | 34 | 0 | 35 | 0 | 75 | 17 | 0 | 163 | 0 |  | 863 | 0 | 410 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 32 | 64 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 75 | 0 | 260 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 362 | 0 | 0 | 35 | 0 | 107 | 0 | 0 | 35 | 1244 | 0 | 0 | 72 | 0 | 0 | 114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 7233 | 4261 | 11494 | 4538 | 863 | 2300 | 0 | 1697 | 1579 | 0 | 0 | 375 | 142 | 0 | 262.625 | 75.22
2:00 | 0 | 0 | 150 | 180 | 0 | 77 | 0 | 359 | 335 |  | 0 | 450 | 263 | 9 | 0 | 0 | 145 | 0 | 40 | 24 | 8 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 13 | 23 | 18 | 25 | 0 | 50 | 0 | 0 | 0 | 120 | 0 | 0 | 229 | 0 | 0 | 0 |  | 11 | 0 | 84 | 56 | 0 | 6 | 13 | 40 | 0 | 0 | 0 | 300 | 300 | 211 | 197 | 0 | 42 | 0 | 0 | 51 | 0 | 47 | 52 | 18 | 8 | 33 | 21 | 136 | 192 | 0 | 19 | 0 | 33 | 28 | 53 | 46 | 0 | 0 | 61 | 80 | 0 | 201 | 18 | 0 | 10 | 265 | 16 | 8 | 0 | 0 | 0 | 0 | 47 | 0 | 17 | 0 | 38 | 34 | 0 | 409 | 48 | 105 | 51 | 0 | 88 | 17 | 52 | 106 | 9 | 38 | 360 | 55 | 0 | 72 | 34 | 0 | 35 | 0 | 56 | 17 | 0 | 163 | 0 |  | 864 | 0 | 410 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 32 | 32 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 74 | 0 | 260 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 360 | 0 | 0 | 35 | 0 | 55 | 0 | 0 | 35 | 1182 | 0 | 0 | 35 | 0 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 7074 | 4051 | 11125 | 4502 | 864 | 2281 | 0 | 1500 | 1516 | 0 | 0 | 326 | 136 | 0 | 131.79 | 75.22
3:00 | 0 | 0 | 150 | 180 | 0 | 77 | 0 | 359 | 333 |  | 0 | 450 | 270 | 8 | 0 | 0 | 145 | 0 | 40 | 8 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 13 | 23 | 18 | 25 | 0 | 50 | 0 | 0 | 0 | 120 | 0 | 0 | 228 | 0 | 0 | 0 |  | 12 | 0 | 84 | 56 | 0 | 6 | 13 | 40 | 0 | 0 | 0 | 300 | 300 | 211 | 158 | 0 | 42 | 0 | 0 | 10 | 0 | 43 | 52 | 18 | 8 | 33 | 21 | 132 | 191 | 0 | 19 | 0 | 33 | 28 | 11 | 10 | 0 | 0 | 61 | 80 | 0 | 201 | 18 | 0 | 10 | 270 | 16 | 8 | 0 | 0 | 0 | 0 | 47 | 0 | 17 | 0 | 38 | 34 | 0 | 409 | 49 | 105 | 51 | 0 | 88 | 17 | 52 | 106 | 9 | 38 | 360 | 35 | 0 | 35 | 34 | 0 | 35 | 0 | 49 | 17 | 0 | 163 | 0 |  | 863 | 0 | 410 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 29 | 32 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 74 | 0 | 260 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 361 | 0 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 1162 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6821 | 3883 | 10704 | 4500 | 863 | 2131 | 0 | 1276 | 1496 | 0 | 0 | 306 | 132 | 0 | 142.295 | 75.22
4:00 | 0 | 0 | 150 | 180 | 0 | 22 | 0 | 359 | 334 |  | 0 | 450 | 260 | 9 | 0 | 0 | 140 | 0 | 39 | 8 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 13 | 23 | 18 | 25 | 0 | 41 | 0 | 0 | 0 | 120 | 0 | 0 | 229 | 0 | 0 | 0 |  | 12 | 0 | 84 | 56 | 0 | 6 | 13 | 40 | 0 | 0 | 0 | 300 | 300 | 212 | 108 | 0 | 42 | 0 | 0 | 10 | 0 | 46 | 0 | 18 | 8 | 33 | 21 | 130 | 193 | 0 | 19 | 0 | 33 | 28 | 11 | 10 | 0 | 0 | 61 | 80 | 0 | 201 | 18 | 0 | 10 | 265 | 16 | 8 | 0 | 0 | 0 | 0 | 47 | 0 | 17 | 0 | 38 | 34 | 0 | 340 | 49 | 105 | 51 | 0 | 88 | 17 | 52 | 106 | 9 | 38 | 360 | 35 | 0 | 31 | 34 | 0 | 35 | 0 | 36 | 17 | 0 | 163 | 0 |  | 911 | 0 | 410 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 28 | 16 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 75 | 0 | 260 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 359 | 0 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 1100 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6555 | 3850 | 10405 | 4428 | 911 | 2009 | 0 | 1183 | 1435 | 0 | 0 | 309 | 130 | 0 | 114.6 | 75.22
5:00 | 0 | 0 | 149 | 180 | 0 | 22 | 0 | 360 | 333 |  | 0 | 450 | 297 | 8 | 0 | 0 | 140 | 0 | 40 | 8 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 13 | 23 | 18 | 25 | 0 | 41 | 0 | 0 | 0 | 120 | 0 | 0 | 227 | 0 | 0 | 0 |  | 12 | 0 | 84 | 56 | 0 | 6 | 13 | 39 | 0 | 0 | 0 | 300 | 300 | 211 | 108 | 0 | 43 | 0 | 0 | 10 | 0 | 46 | 0 | 18 | 8 | 33 | 21 | 126 | 192 | 0 | 19 | 0 | 33 | 28 | 11 | 10 | 0 | 0 | 63 | 80 | 0 | 201 | 18 | 0 | 10 | 275 | 16 | 8 | 0 | 0 | 0 | 0 | 48 | 0 | 17 | 0 | 38 | 34 | 0 | 345 | 49 | 105 | 51 | 0 | 88 | 17 | 54 | 106 | 9 | 38 | 360 | 35 | 0 | 17 | 34 | 0 | 35 | 0 | 35 | 17 | 0 | 163 | 0 |  | 484 | 0 | 410 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 27 | 16 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 74 | 0 | 260 | 0 | 0 | 177 | 0 | 0 | 0 | 0 | 0 | 164 | 0 | 419 | 0 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 1100 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6588 | 3462 | 10050 | 4414 | 484 | 2113 | 0 | 1170 | 1434 | 0 | 0 | 309 | 126 | 0 | 114.6 | 75.22
6:00 | 0 | 0 | 148 | 180 | 0 | 22 | 0 | 359 | 292 |  | 0 | 450 | 270 | 9 | 0 | 0 | 130 | 0 | 40 | 8 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 13 | 23 | 18 | 25 | 0 | 8 | 0 | 0 | 0 | 120 | 0 | 0 | 228 | 0 | 0 | 0 |  | 12 | 0 | 84 | 10 | 0 | 6 | 13 | 40 | 0 | 0 | 0 | 300 | 300 | 200 | 108 | 0 | 43 | 0 | 0 | 10 | 0 | 46 | 0 | 18 | 8 | 25 | 21 | 116 | 193 | 0 | 19 | 0 | 33 | 28 | 11 | 10 | 0 | 0 | 40 | 80 | 0 | 201 | 18 | 0 | 10 | 260 | 16 | 8 | 0 | 0 | 0 | 0 | 48 | 0 | 17 | 1 | 38 | 34 | 0 | 346 | 49 | 34 | 51 | 0 | 88 | 17 | 54 | 106 | 9 | 38 | 360 | 35 | 2 | 17 | 34 | 0 | 35 | 1 | 36 | 17 | 0 | 163 | 0 |  | 482 | 0 | 340 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 24 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 73 | 0 | 260 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 157 | 0 | 296 | 0 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 1090 | 0 | 0 | 0 | 0 | 3 | 35 | 0 | 0 | 0 | 1 | 0 | 9 | 6 | 0 |  | 6301 | 3211 | 9512 | 4264 | 482 | 1905 | 0 | 990 | 1432 | 0 | 0 | 309 | 116 | 14 | 49.66 | 75.22
7:00 | 0 | 0 | 150 | 180 | 0 | 22 | 0 | 359 | 295 |  | 0 | 450 | 290 | 9 | 0 | 0 | 130 | 0 | 41 | 24 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 23 | 18 | 0 | 0 | 8 | 0 | 0 | 0 | 120 | 0 | 0 | 230 | 0 | 0 | 0 |  | 12 | 0 | 84 | 10 | 0 | 6 | 13 | 40 | 0 | 0 | 0 | 300 | 300 | 182 | 108 | 0 | 43 | 0 | 0 | 10 | 0 | 46 | 0 | 18 | 8 | 33 | 21 | 98 | 190 | 0 | 19 | 0 | 33 | 28 | 11 | 10 | 0 | 0 | 40 | 80 | 0 | 201 | 18 | 0 | 10 | 280 | 16 | 8 | 0 | 0 | 0 | 0 | 46 | 0 | 17 | 5 | 38 | 34 | 0 | 347 | 49 | 34 | 17 | 1 | 88 | 17 | 17 | 70 | 9 | 38 | 360 | 17 | 10 | 17 | 34 | 0 | 35 | 7 | 35 | 17 | 0 | 163 | 0 |  | 482 | 0 | 340 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 22 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 74 | 0 | 260 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 157 | 0 | 343 | 0 | 0 | 35 | 0 | 34 | 0 | 1 | 35 | 1110 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 6 | 0 | 85 | 34 | 0 |  | 6184 | 3370 | 9554 | 4232 | 482 | 1993 | 0 | 826 | 1529 | 0 | 0 | 309 | 98 | 85 | 0 | 75.21
8:00 | 0 | 0 | 150 | 180 | 0 | 22 | 0 | 361 | 295 |  | 0 | 450 | 299 | 8 | 0 | 0 | 130 | 0 | 41 | 85 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 23 | 18 | 20 | 0 | 8 | 0 | 0 | 0 | 120 | 0 | 0 | 230 | 0 | 0 | 0 |  | 12 | 0 | 84 | 10 | 0 | 6 | 13 | 40 | 0 | 0 | 0 | 290 | 305 | 183 | 108 | 0 | 42 | 0 | 0 | 10 | 0 | 47 | 0 | 18 | 8 | 33 | 21 | 104 | 173 | 0 | 19 | 1 | 33 | 28 | 11 | 10 | 0 | 0 | 40 | 80 | 0 | 204 | 18 | 0 | 10 | 295 | 16 | 8 | 0 | 0 | 0 | 0 | 48 | 0 | 17 | 10 | 38 | 34 | 0 | 346 | 49 | 34 | 17 | 2 | 88 | 17 | 17 | 17 | 9 | 38 | 360 | 17 | 21 | 17 | 34 | 0 | 17 | 14 | 36 | 17 | 0 | 163 | 0 |  | 462 | 0 | 340 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 24 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 75 | 0 | 260 | 0 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 158 | 0 | 347 | 0 | 0 | 35 | 0 | 34 | 0 | 2 | 35 | 1080 | 0 | 0 | 0 | 1 | 43 | 0 | 0 | 0 | 0 | 14 | 0 | 144 | 65 | 0 |  | 6234 | 3451 | 9685 | 4236 | 462 | 2023 | 0 | 818 | 1559 | 0 | 0 | 310 | 104 | 173 | 20.055 | 75.21
9:00 | 0 | 0 | 150 | 180 | 0 | 22 | 0 | 388 | 292 |  | 0 | 450 | 300 | 9 | 0 | 0 | 132 | 0 | 40 | 95 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 13 | 23 | 18 | 25 | 0 | 8 | 0 | 0 | 0 | 120 | 0 | 0 | 224 | 0 | 0 | 0 |  | 12 | 0 | 20 | 10 | 0 | 6 | 13 | 25 | 0 | 0 | 0 | 310 | 320 | 195 | 108 | 0 | 40 | 0 | 0 | 10 | 0 | 46 | 0 | 0 | 8 | 33 | 21 | 106 | 158 | 0 | 15 | 1 | 31 | 28 | 11 | 10 | 0 | 0 | 40 | 80 | 0 | 206 | 17 | 0 | 10 | 300 | 16 | 8 | 0 | 0 | 0 | 0 | 48 | 0 | 17 | 15 | 38 | 38 | 0 | 383 | 49 | 34 | 17 | 3 | 88 | 17 | 17 | 17 | 9 | 38 | 391 | 17 | 33 | 17 | 34 | 0 | 17 | 22 | 36 | 17 | 0 | 163 | 0 |  | 490 | 0 | 340 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 23 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 75 | 0 | 260 | 0 | 0 | 188 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 371 | 0 | 0 | 35 | 0 | 34 | 0 | 5 | 35 | 1080 | 0 | 0 | 0 | 3 | 66 | 0 | 0 | 0 | 0 | 22 | 0 | 278 | 104 | 0 |  | 6319 | 3729 | 10048 | 4357 | 490 | 2033 | 0 | 850 | 1693 | 0 | 0 | 245 | 106 | 274 | 64.94 | 75.21
10:00 | 0 | 0 | 149 | 180 | 0 | 22 | 0 | 395 | 294 |  | 0 | 450 | 300 | 16 | 0 | 0 | 130 | 0 | 97 | 95 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 13 | 23 | 18 | 25 | 0 | 8 | 0 | 0 | 0 | 120 | 0 | 0 | 223 | 0 | 0 | 0 |  | 12 | 0 | 17 | 22 | 0 | 6 | 13 | 25 | 0 | 0 | 0 | 320 | 330 | 204 | 108 | 0 | 34 | 0 | 0 | 10 | 0 | 46 | 0 | 0 | 8 | 33 | 21 | 106 | 152 | 0 | 14 | 2 | 32 | 28 | 11 | 10 | 0 | 0 | 55 | 80 | 0 | 206 | 17 | 0 | 10 | 290 | 16 | 8 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 18 | 38 | 51 | 0 | 380 | 49 | 34 | 27 | 4 | 88 | 17 | 26 | 17 | 9 | 38 | 386 | 32 | 41 | 17 | 34 | 0 | 17 | 27 | 35 | 17 | 0 | 163 | 0 |  | 490 | 0 | 340 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 25 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 8 | 75 | 0 | 260 | 0 | 0 | 194 | 0 | 0 | 0 | 0 | 0 | 197 | 0 | 416 | 0 | 0 | 35 | 0 | 34 | 0 | 7 | 55 | 1080 | 0 | 0 | 0 | 3 | 81 | 0 | 22 | 0 | 0 | 28 | 0 | 391 | 132 | 0 |  | 6476 | 4013 | 10489 | 4474 | 490 | 2070 | 0 | 936 | 1806 | 0 | 22 | 242 | 106 | 343 | 60.165 | 75.21
11:00 | 0 | 0 | 150 | 180 | 0 | 22 | 0 | 395 | 293 |  | 0 | 450 | 288 | 18 | 0 | 2 | 130 | 0 | 40 | 95 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 10 | 13 | 23 | 18 | 25 | 0 | 8 | 0 | 25 | 0 | 120 | 0 | 3 | 224 | 0 | 0 | 0 |  | 12 | 0 | 0 | 44 | 0 | 6 | 13 | 23 | 0 | 0 | 0 | 290 | 305 | 206 | 108 | 0 | 33 | 0 | 0 | 10 | 0 | 42 | 0 | 0 | 8 | 33 | 21 | 124 | 150 | 0 | 14 | 2 | 31 | 28 | 31 | 30 | 0 | 0 | 59 | 80 | 0 | 206 | 0 | 0 | 10 | 290 | 16 | 8 | 0 | 4 | 0 | 0 | 123 | 0 | 0 | 19 | 38 | 51 | 6 | 369 | 97 | 34 | 50 | 5 | 122 | 17 | 48 | 17 | 9 | 38 | 393 | 60 | 44 | 17 | 34 | 0 | 17 | 31 | 52 | 17 | 0 | 163 | 0 |  | 490 | 0 | 380 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 26 | 4 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 8 | 76 | 0 | 260 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 346 | 0 | 0 | 50 | 15 | 34 | 0 | 7 | 55 | 1100 | 0 | 0 | 0 | 4 | 91 | 35 | 23 | 0 | 0 | 32 | 0 | 449 | 151 | 0 |  | 6691 | 4143 | 10834 | 4359 | 490 | 2025 | 0 | 1312 | 1885 | 25 | 23 | 205 | 124 | 386 | 0 | 75.21
12:00 | 0 | 0 | 150 | 180 | 0 | 28 | 0 | 405 | 324 |  | 0 | 450 | 300 | 42 | 0 | 15 | 130 | 0 | 60 | 95 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 13 | 23 | 18 | 25 | 0 | 8 | 0 | 25 | 0 | 120 | 0 | 8 | 218 | 0 | 0 | 0 |  | 12 | 0 | 0 | 44 | 0 | 6 | 13 | 23 | 0 | 0 | 0 | 290 | 305 | 204 | 108 | 0 | 34 | 0 | 0 | 10 | 0 | 42 | 0 | 0 | 8 | 33 | 21 | 128 | 150 | 0 | 14 | 2 | 32 | 28 | 48 | 36 | 0 | 0 | 58 | 79 | 0 | 202 | 0 | 0 | 10 | 290 | 16 | 8 | 0 | 30 | 0 | 0 | 153 | 0 | 0 | 18 | 50 | 51 | 16 | 368 | 98 | 34 | 51 | 5 | 103 | 17 | 52 | 17 | 36 | 38 | 385 | 72 | 41 | 17 | 34 | 0 | 17 | 31 | 72 | 17 | 0 | 163 | 0 |  | 490 | 0 | 400 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 59 | 27 | 32 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 8 | 75 | 0 | 260 | 15 | 0 | 178 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 380 | 0 | 0 | 35 | 15 | 34 | 0 | 7 | 35 | 1120 | 0 | 0 | 0 | 4 | 94 | 35 | 97 | 0 | 0 | 33 | 0 | 510 | 155 | 0 |  | 6953 | 4382 | 11335 | 4400 | 490 | 2129 | 0 | 1491 | 1965 | 25 | 112 | 205 | 128 | 390 | 0 | 75.21
13:00 | 0 | 0 | 150 | 180 | 0 | 75 | 0 | 399 | 324 |  | 0 | 450 | 305 | 66 | 0 | 15 | 130 | 0 | 95 | 95 | 33 | 32 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 13 | 23 | 14 | 25 | 14 | 11 | 0 | 25 | 0 | 120 | 0 | 8 | 218 | 0 | 0 | 0 |  | 10 | 0 | 0 | 44 | 0 | 6 | 13 | 24 | 0 | 0 | 0 | 290 | 305 | 203 | 125 | 0 | 35 | 0 | 0 | 10 | 0 | 41 | 0 | 0 | 5 | 33 | 21 | 126 | 135 | 0 | 14 | 2 | 32 | 28 | 50 | 40 | 0 | 0 | 54 | 78 | 0 | 0 | 17 | 0 | 10 | 285 | 16 | 8 | 0 | 40 | 0 | 0 | 153 | 0 | 0 | 18 | 49 | 51 | 20 | 397 | 88 | 45 | 51 | 4 | 123 | 17 | 54 | 17 | 37 | 38 | 382 | 71 | 34 | 17 | 34 | 0 | 17 | 31 | 90 | 17 | 0 | 163 | 0 |  | 490 | 0 | 400 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 59 | 30 | 32 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 8 | 75 | 0 | 260 | 15 | 0 | 188 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 409 | 0 | 0 | 40 | 50 | 32 | 0 | 6 | 35 | 1160 | 0 | 0 | 0 | 4 | 91 | 35 | 100 | 0 | 0 | 12 | 0 | 512 | 150 | 0 |  | 7007 | 4479 | 11486 | 4274 | 490 | 2231 | 0 | 1630 | 2007 | 25 | 115 | 236 | 126 | 352 | 100.275 | 75.21
14:00 | 0 | 0 | 200 | 180 | 0 | 75 | 0 | 397 | 277 |  | 0 | 450 | 290 | 60 | 0 | 15 | 127 | 0 | 40 | 95 | 50 | 80 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 16 | 23 | 14 | 25 | 28 | 20 | 0 | 25 | 0 | 120 | 0 | 16 | 219 | 0 | 0 | 0 |  | 6 | 0 | 0 | 44 | 0 | 6 | 13 | 24 | 0 | 0 | 0 | 290 | 305 | 203 | 125 | 0 | 35 | 0 | 0 | 25 | 0 | 40 | 0 | 0 | 5 | 33 | 21 | 116 | 120 | 0 | 14 | 1 | 32 | 28 | 50 | 39 | 0 | 0 | 55 | 78 | 0 | 0 | 17 | 0 | 10 | 280 | 16 | 8 | 0 | 110 | 0 | 0 | 153 | 0 | 0 | 17 | 49 | 51 | 20 | 369 | 88 | 70 | 51 | 4 | 123 | 17 | 54 | 17 | 37 | 38 | 385 | 71 | 40 | 17 | 34 | 0 | 17 | 24 | 93 | 17 | 0 | 163 | 0 |  | 490 | 0 | 350 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 24 | 60 | 31 | 32 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 8 | 72 | 0 | 260 | 15 | 0 | 183 | 0 | 0 | 0 | 0 | 0 | 189 | 0 | 370 | 0 | 0 | 50 | 105 | 49 | 0 | 6 | 55 | 1162 | 0 | 0 | 0 | 2 | 81 | 50 | 80 | 0 | 0 | 14 | 0 | 513 | 89 | 0 |  | 7079 | 4472 | 11551 | 4188 | 490 | 2139 | 0 | 1930 | 2007 | 25 | 95 | 283 | 116 | 278 | 364.81 | 75.21
15:00 | 0 | 0 | 200 | 180 | 0 | 75 | 0 | 404 | 274 |  | 0 | 350 | 290 | 66 | 0 | 15 | 97 | 0 | 0 | 95 | 50 | 80 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 16 | 23 | 14 | 25 | 28 | 34 | 0 | 25 | 0 | 120 | 0 | 25 | 219 | 0 | 0 | 0 |  | 6 | 6 | 0 | 43 | 0 | 6 | 13 | 24 | 0 | 0 | 0 | 290 | 270 | 204 | 125 | 0 | 37 | 0 | 0 | 51 | 0 | 34 | 0 | 0 | 5 | 33 | 15 | 120 | 118 | 0 | 14 | 0 | 32 | 28 | 52 | 42 | 0 | 0 | 57 | 77 | 0 | 0 | 17 | 0 | 10 | 280 | 16 | 8 | 0 | 145 | 0 | 0 | 153 | 0 | 0 | 11 | 49 | 51 | 20 | 318 | 88 | 70 | 51 | 3 | 124 | 17 | 54 | 20 | 37 | 38 | 386 | 71 | 14 | 17 | 34 | 0 | 32 | 4 | 93 | 17 | 0 | 163 | 0 |  | 490 | 0 | 300 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 16 | 60 | 31 | 32 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 17 | 0 | 8 | 74 | 0 | 260 | 0 | 0 | 171 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 409 | 0 | 0 | 50 | 67 | 34 | 0 | 6 | 35 | 1110 | 0 | 0 | 24 | 0 | 65 | 35 | 63 | 0 | 0 | 22 | 0 | 514 | 34 | 0 |  | 6887 | 4234 | 11121 | 3960 | 490 | 2107 | 0 | 1956 | 1958 | 25 | 63 | 283 | 120 | 159 | 376.27 | 75.2
16:00 | 0 | 0 | 200 | 180 | 0 | 75 | 0 | 398 | 272 |  | 0 | 350 | 270 | 66 | 0 | 15 | 95 | 0 | 0 | 72 | 16 | 80 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 16 | 23 | 14 | 25 | 28 | 34 | 0 | 25 | 0 | 120 | 0 | 8 | 221 | 0 | 0 | 0 |  | 11 | 42 | 0 | 43 | 12 | 6 | 13 | 25 | 0 | 0 | 0 | 290 | 270 | 205 | 125 | 0 | 36 | 0 | 0 | 10 | 0 | 37 | 0 | 8 | 5 | 32 | 20 | 132 | 120 | 0 | 14 | 0 | 32 | 28 | 53 | 40 | 0 | 0 | 58 | 77 | 0 | 0 | 17 | 0 | 10 | 285 | 16 | 8 | 0 | 45 | 0 | 0 | 116 | 0 | 0 | 7 | 38 | 51 | 10 | 319 | 49 | 70 | 51 | 2 | 124 | 17 | 54 | 17 | 37 | 38 | 390 | 72 | 5 | 54 | 34 | 0 | 0 | 0 | 93 | 17 | 0 | 163 | 0 |  | 490 | 0 | 250 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 31 | 32 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 75 | 0 | 260 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 422 | 0 | 0 | 0 | 21 | 34 | 0 | 3 | 0 | 1030 | 0 | 0 | 17 | 0 | 22 | 35 | 25 | 0 | 0 | 14 | 0 | 512 | 23 | 0 |  | 6625 | 3699 | 10324 | 3821 | 490 | 2062 | 0 | 1494 | 1877 | 25 | 25 | 322 | 132 | 76 | 0 | 75.2
17:00 | 0 | 0 | 120 | 180 | 0 | 22 | 0 | 328 | 233 |  | 0 | 320 | 245 | 66 | 0 | 15 | 50 | 0 | 38 | 13 | 8 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 0 | 23 | 0 | 25 | 30 | 36 | 0 | 25 | 0 | 120 | 0 | 8 | 223 | 0 | 0 | 0 |  | 0 | 42 | 0 | 43 | 24 | 6 | 13 | 29 | 0 | 0 | 0 | 290 | 270 | 207 | 75 | 0 | 37 | 0 | 0 | 10 | 0 | 40 | 0 | 15 | 5 | 32 | 15 | 130 | 120 | 0 | 15 | 0 | 32 | 28 | 53 | 43 | 0 | 0 | 59 | 77 | 0 | 80 | 17 | 0 | 10 | 275 | 16 | 8 | 0 | 15 | 0 | 0 | 116 | 0 | 0 | 3 | 38 | 51 | 5 | 319 | 49 | 80 | 51 | 1 | 124 | 17 | 54 | 17 | 37 | 38 | 280 | 71 | 2 | 17 | 34 | 0 | 8 | 0 | 93 | 17 | 0 | 163 | 0 |  | 490 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 30 | 32 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 74 | 0 | 245 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 426 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 600 | 0 | 0 | 0 | 0 | 2 | 0 | 25 | 0 | 0 | 5 | 0 | 514 | 20 | 0 |  | 5995 | 3072 | 9067 | 3585 | 490 | 1865 | 0 | 1234 | 1433 | 25 | 25 | 245 | 130 | 35 | 94.545 | 75.2
18:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 272 | 233 |  | 0 | 300 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 5 | 0 | 0 | 25 | 0 | 120 | 0 | 0 | 194 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 16 | 17 | 13 | 26 | 0 | 0 | 0 | 280 | 230 | 179 | 0 | 0 | 37 | 0 | 0 | 0 | 0 | 46 | 0 | 15 | 5 | 31 | 0 | 108 | 119 | 0 | 0 | 0 | 32 | 28 | 5 | 20 | 0 | 0 | 40 | 10 | 0 | 80 | 17 | 0 | 10 | 250 | 16 | 8 | 0 | 0 | 0 | 0 | 125 | 0 | 0 | 0 | 40 | 51 | 5 | 319 | 49 | 0 | 51 | 0 | 124 | 0 | 17 | 17 | 16 | 12 | 320 | 71 | 0 | 0 | 34 | 0 | 0 | 0 | 92 | 0 | 0 | 163 | 0 |  | 250 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 26 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 170 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 426 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 415 | 8 | 0 |  | 4766 | 2403 | 7169 | 3083 | 250 | 1576 | 0 | 753 | 1155 | 25 | 0 | 209 | 108 | 10 | 0 | 75.2
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 292 | 303 |  | 0 | 350 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 120 | 0 | 0 | 225 | 0 | 0 | 0 |  | 1 | 0 | 32 | 0 | 0 | 36 | 13 | 26 | 0 | 0 | 0 | 280 | 287 | 180 | 8 | 0 | 33 | 0 | 0 | 10 | 0 | 48 | 0 | 15 | 5 | 0 | 0 | 0 | 118 | 0 | 0 | 0 | 32 | 28 | 5 | 5 | 0 | 0 | 40 | 30 | 0 | 135 | 17 | 0 | 10 | 280 | 16 | 0 | 0 | 0 | 0 | 0 | 127 | 0 | 0 | 0 | 74 | 37 | 5 | 375 | 54 | 0 | 17 | 0 | 170 | 0 | 17 | 17 | 42 | 12 | 395 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 40 | 3 | 0 | 163 | 0 |  | 490 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 1 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 200 | 0 | 0 | 144 | 0 | 0 | 0 | 0 | 0 | 146 | 0 | 425 | 0 | 0 | 4 | 0 | 65 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 420 | 0 | 0 |  | 5019 | 2513 | 7532 | 3336 | 490 | 1705 | 0 | 788 | 945 | 25 | 0 | 243 | 0 | 0 | 0 | 75.2
19:30 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 398 | 303 |  | 0 | 300 | 275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 16 | 0 | 0 | 25 | 0 | 120 | 0 | 0 | 223 | 0 | 0 | 0 |  | 12 | 0 | 51 | 0 | 0 | 36 | 13 | 27 | 0 | 0 | 0 | 280 | 270 | 180 | 8 | 0 | 38 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 118 | 0 | 0 | 0 | 32 | 28 | 5 | 5 | 0 | 0 | 51 | 5 | 0 | 0 | 17 | 0 | 10 | 290 | 16 | 0 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 | 74 | 17 | 6 | 377 | 115 | 0 | 17 | 0 | 170 | 0 | 17 | 0 | 8 | 12 | 370 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 17 | 17 | 0 | 163 | 0 |  | 490 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 75 | 0 | 200 | 0 | 0 | 144 | 0 | 0 | 0 | 0 | 0 | 157 | 0 | 425 | 0 | 0 | 26 | 0 | 100 | 0 | 0 | 35 | 260 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 422 | 0 | 0 |  | 4978 | 2673 | 7651 | 3313 | 490 | 1699 | 0 | 929 | 957 | 25 | 0 | 214 | 24 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 379 | 303 |  | 0 | 330 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 3 | 0 | 16 | 0 | 0 | 25 | 0 | 120 | 0 | 0 | 220 | 0 | 0 | 0 |  | 11 | 0 | 51 | 0 | 0 | 38 | 0 | 26 | 0 | 0 | 0 | 285 | 275 | 189 | 8 | 0 | 40 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 119 | 0 | 0 | 0 | 32 | 28 | 20 | 20 | 0 | 0 | 61 | 30 | 0 | 0 | 17 | 0 | 0 | 280 | 8 | 0 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 | 74 | 17 | 5 | 377 | 115 | 0 | 17 | 0 | 170 | 0 | 17 | 0 | 8 | 12 | 274 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 17 | 17 | 0 | 163 | 0 |  | 491 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 74 | 0 | 200 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 159 | 0 | 424 | 0 | 0 | 57 | 0 | 111 | 0 | 0 | 35 | 250 | 0 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 425 | 0 | 0 |  | 4974 | 2779 | 7753 | 3216 | 491 | 1775 | 0 | 1033 | 949 | 25 | 0 | 214 | 50 | 0 | 0 | 75.2
21:00 | 0 | 0 | 0 | 180 | 0 | 52 | 0 | 381 | 354 |  | 0 | 330 | 305 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 23 | 15 | 0 | 33 | 0 | 0 | 25 | 0 | 120 | 0 | 0 | 225 | 0 | 0 | 0 |  | 12 | 0 | 34 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 300 | 270 | 181 | 8 | 0 | 40 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 125 | 0 | 0 | 0 | 32 | 30 | 22 | 20 | 0 | 0 | 61 | 80 | 0 | 0 | 18 | 0 | 10 | 270 | 16 | 5 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 74 | 17 | 5 | 400 | 108 | 0 | 17 | 0 | 170 | 0 | 17 | 0 | 8 | 12 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 17 | 17 | 0 | 163 | 0 |  | 490 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 74 | 0 | 200 | 0 | 0 | 151 | 0 | 0 | 0 | 0 | 0 | 157 | 0 | 428 | 0 | 0 | 70 | 0 | 70 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 415 | 0 | 0 |  | 4905 | 2815 | 7720 | 3051 | 490 | 1947 | 0 | 875 | 1089 | 25 | 0 | 197 | 46 | 0 | 0 | 75.2
22:00 | 0 | 0 | 0 | 180 | 0 | 75 | 0 | 400 | 344 |  | 0 | 370 | 315 | 0 | 0 | 0 | 110 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 23 | 15 | 10 | 33 | 0 | 0 | 25 | 0 | 120 | 0 | 0 | 225 | 0 | 0 | 0 |  | 12 | 0 | 0 | 0 | 0 | 6 | 11 | 39 | 0 | 0 | 0 | 350 | 315 | 206 | 45 | 0 | 42 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 64 | 128 | 0 | 0 | 0 | 32 | 30 | 22 | 30 | 0 | 0 | 61 | 80 | 0 | 0 | 17 | 0 | 10 | 300 | 16 | 8 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 74 | 17 | 5 | 402 | 108 | 2 | 17 | 0 | 140 | 0 | 17 | 0 | 9 | 12 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 17 | 17 | 0 | 163 | 0 |  | 495 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 75 | 0 | 200 | 0 | 0 | 161 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 427 | 0 | 0 | 70 | 0 | 70 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 411 | 0 | 0 |  | 5360 | 2944 | 8304 | 3397 | 495 | 2120 | 0 | 854 | 1186 | 25 | 0 | 163 | 64 | 0 | 0 | 75.2
23:00 | 0 | 0 | 0 | 180 | 0 | 76 | 0 | 402 | 344 |  | 0 | 450 | 310 | 0 | 0 | 0 | 160 | 0 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 23 | 19 | 25 | 33 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 227 | 0 | 0 | 0 |  | 12 | 0 | 0 | 0 | 0 | 6 | 0 | 30 | 0 | 0 | 0 | 340 | 305 | 196 | 45 | 0 | 45 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 74 | 141 | 0 | 0 | 0 | 31 | 30 | 51 | 48 | 0 | 0 | 61 | 80 | 0 | 0 | 18 | 0 | 10 | 315 | 16 | 8 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 74 | 17 | 5 | 402 | 108 | 17 | 17 | 0 | 140 | 0 | 17 | 0 | 8 | 12 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 17 | 17 | 0 | 163 | 0 |  | 495 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 75 | 0 | 200 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 430 | 0 | 0 | 70 | 0 | 70 | 0 | 0 | 0 | 520 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 467 | 0 | 0 |  | 5623 | 3102 | 8725 | 3583 | 495 | 2280 | 0 | 868 | 1262 | 0 | 0 | 163 | 74 | 0 | 0 | 75.2
24:00 | 0 | 0 | 0 | 180 | 0 | 76 | 0 | 397 | 343 |  | 0 | 450 | 297 | 0 | 0 | 0 | 155 | 0 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 23 | 19 | 25 | 33 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 226 | 0 | 0 | 0 |  | 12 | 0 | 0 | 0 | 0 | 6 | 12 | 38 | 0 | 0 | 0 | 310 | 270 | 215 | 45 | 0 | 45 | 0 | 0 | 51 | 0 | 0 | 0 | 18 | 0 | 33 | 14 | 82 | 147 | 0 | 0 | 0 | 31 | 30 | 51 | 45 | 0 | 0 | 61 | 80 | 0 | 0 | 17 | 0 | 10 | 290 | 16 | 8 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 38 | 17 | 5 | 413 | 48 | 25 | 17 | 0 | 88 | 0 | 17 | 0 | 8 | 12 | 0 | 0 | 0 | 0 | 34 | 0 | 2 | 0 | 17 | 17 | 0 | 163 | 0 |  | 495 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 75 | 0 | 200 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 422 | 0 | 0 | 35 | 0 | 66 | 0 | 0 | 0 | 750 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 0 | 529 | 0 | 0 |  | 5369 | 3479 | 8848 | 3748 | 495 | 2241 | 0 | 565 | 1554 | 0 | 0 | 163 | 82 | 0 | 0 | 75.2
KWH | 0 | 0 | 2770281 | 4284000 | 0 | 1095636 | 0 | 9035770 | 7416000 |  | 0 | 9609250 | 6857513 | 502080 | 0 | 105728 | 2660056 | 0 | 1038000 | 927360 | 272880 | 491040 | 0 | 0 | 0 | 0 | 160560 | 278038 | 224653 | 201960 | 552000 | 338580 | 469700 | 270300 | 451200 | 0 | 288660 | 0 | 2800000 | 0 | 89778 | 5187923 | 0 | 0 | 0 |  | 253920 | 101520 | 867452 | 692400 | 53760 | 223680 | 266112 | 763200 | 0 | 0 | 0 | 7577600 | 7168000 | 4855000 | 2325090 | 0 | 931968 | 0 | 0 | 693286 | 0 | 843524 | 161155 | 197244 | 151560 | 683300 | 364510 | 2547840 | 3565440 | 0 | 255132 | 10400 | 754000 | 619560 | 733200 | 702280 | 0 | 0 | 1317408 | 1725120 | 0 | 2652380 | 366000 | 0 | 226620 | 6907000 | 367488 | 173368 | 0 | 444109 | 0 | 0 | 2385600 | 0 | 173950 | 143100 | 1140480 | 908640 | 217454 | 8846000 | 1645200 | 1284979 | 945927 | 33242 | 2719855 | 332057 | 936726 | 976980 | 442680 | 756480 | 7389000 | 904320 | 289170 | 496800 | 840545 | 0 | 480600 | 189429 | 1291200 | 407160 | 0 | 3910836 | 0 |  | 13508363 | 0 | 8214336 | 0 | 553920 | 0 | 0 | 0 | 0 | 0 | 34500 | 1366000 | 561609 | 424512 | 0 | 0 | 1045000 | 0 | 0 | 0 | 0 | 0 | 0 | 12485 | 0 | 436560 | 0 | 133902 | 1806545 | 0 | 5878800 | 19000 | 0 | 4283100 | 0 | 0 | 0 | 0 | 0 | 4316764 | 0 | 9481854 | 6240 | 0 | 1063968 | 272880 | 1165814 | 0 | 47292 | 694944 | 23955700 | 0 | 0 | 189600 | 25920 | 662400 | 1101888 | 327102 | 0 | 0 | 194098 | 0 | 7281818 | 1001270 | 0 |  | 151008982 | 90068184 | 241077166 | 97468742 | 13508363 | 49534218 | 0 | 29649685 | 38922863 | 288660 | 346102 | 6214372 | 2547840 | 2596321 | 0
Fuel Cost | 0 | 0 | 4044610.26 | 6383160 | 0 | 1457195.88 | 0 | 9487558.5 | 8009280 |  | 0 | 10474082.5 | 7611839.43 | 5613254.4 | 0 | 1400896 | 2979262.72 | 0 | 1816500 | 13558003.2 | 3839421.6 | 7959758.4 | 0 | 0 | 0 | 0 | 2042323.2 | 3753513 | 3012596.73 | 151470 | 414000 | 0 | 0 | 0 | 7674912 | 0 | 77938.2 | 0 | 5292000 | 0 | 1467870.3 | 5395439.92 | 0 | 0 | 0 |  | 3313656 | 1693353.6 | 14764033.04 | 9354324 | 681676.8 | 2587977.6 | 337962.24 | 2541456 | 0 | 0 | 0 | 8411136 | 7813120 | 5631800 | 2999366.1 | 0 | 1053123.84 | 0 | 0 | 1157787.62 | 0 | 14567659.48 | 2167534.75 | 270224.28 | 113670 | 1195775 | 273382.5 | 18293491.2 | 3886329.6 | 0 | 346979.52 | 165776 | 1032980 | 817819.2 | 1275768 | 1214944.4 | 0 | 0 | 2555771.52 | 3933273.6 | 0 | 2678903.8 | 786900 | 0 | 448707.6 | 6907000 | 275616 | 131759.68 | 0 | 6062087.85 | 0 | 0 | 32157888 | 0 | 2409207.5 | 1672839 | 11769753.6 | 12412022.4 | 2885614.58 | 8138320 | 20005632 | 18580796.34 | 11965976.55 | 0 | 31931097.7 | 3616100.73 | 9957397.38 | 13257618.6 | 5706145.2 | 8911334.4 | 6797880 | 11710944 | 4178506.5 | 6304392 | 9565402.1 | 0 | 6276636 | 2263676.55 | 19329264 | 5362297.2 | 0 | 0 | 0 |  | 40525089 | 0 | 9200056.32 | 0 | 5766307.2 | 0 | 0 | 0 | 0 | 0 | 495765 | 1529920 | 1089521.46 | 4627180.8 | 0 | 0 | 2142250 | 0 | 0 | 0 | 0 | 0 | 0 | 170170.55 | 0 | 903679.2 | 0 | 101363.814 | 10496026.45 | 0 | 31098852 | 798380 | 0 | 4968396 | 0 | 0 | 0 | 0 | 0 | 5007446.24 | 0 | 9387035.46 | 83865.6 | 0 | 12586741.44 | 3943116 | 14805837.8 | 0 | 522576.6 | 8436620.16 | 215840857 | 0 | 0 | 1403040 | 293155.2 | 7769952 | 16891943.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 512826755.39 | 410885144.334 | 923711899.724 | 111462886.954 | 40525089 | 59410937.25 | 0 | 379856155.3 | 257435735.45 | 77938.2 | 798380 | 38984804.52 | 18293491.2 | 16866481.85 | 0
Yesterday Day Peak | 0 | 0 | 150 | 180 | 0 | 28 | 0 | 405 | 324 |  | 0 | 450 | 300 | 42 | 0 | 15 | 130 | 0 | 60 | 95 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 13 | 23 | 18 | 25 | 0 | 8 | 0 | 25 | 0 | 120 | 0 | 8 | 218 | 0 | 0 | 0 |  | 12 | 0 | 0 | 44 | 0 | 6 | 13 | 23 | 0 | 0 | 0 | 290 | 305 | 204 | 108 | 0 | 34 | 0 | 0 | 10 | 0 | 42 | 0 | 0 | 8 | 33 | 21 | 128 | 150 | 0 | 14 | 2 | 32 | 28 | 48 | 36 | 0 | 0 | 58 | 79 | 0 | 202 | 0 | 0 | 10 | 290 | 16 | 8 | 0 | 30 | 0 | 0 | 153 | 0 | 0 | 18 | 50 | 51 | 16 | 368 | 98 | 34 | 51 | 5 | 103 | 17 | 52 | 17 | 36 | 38 | 385 | 72 | 41 | 17 | 34 | 0 | 17 | 31 | 72 | 17 | 0 | 163 | 0 |  | 490 | 0 | 400 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 59 | 27 | 32 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 8 | 75 | 0 | 260 | 15 | 0 | 178 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 380 | 0 | 0 | 35 | 15 | 34 | 0 | 7 | 35 | 1120 | 0 | 0 | 0 | 4 | 94 | 35 | 97 | 0 | 0 | 33 | 0 | 510 | 155 | 0 |  | 11335 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 379 | 303 | 0 | 0 | 330 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 3 | 0 | 16 | 0 | 0 | 25 | 0 | 120 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 11 | 0 | 51 | 0 | 0 | 38 | 0 | 26 | 0 | 0 | 0 | 285 | 275 | 189 | 8 | 0 | 40 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 119 | 0 | 0 | 0 | 32 | 28 | 20 | 20 | 0 | 0 | 61 | 30 | 0 | 0 | 17 | 0 | 0 | 280 | 8 | 0 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 | 74 | 17 | 5 | 377 | 115 | 0 | 17 | 0 | 170 | 0 | 17 | 0 | 8 | 12 | 274 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 17 | 17 | 0 | 163 | 0 |  | 491 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 74 | 0 | 200 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 159 | 0 | 424 | 0 | 0 | 57 | 0 | 111 | 0 | 0 | 35 | 250 | 0 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 425 | 0 | 0 |  | 7753 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 0 | 76 | 0 | 400 | 330 | 0 | 0 | 450 | 300 | 50 | 90 | 15 | 150 | 0 | 100 | 90 | 92 | 149 | 0 | 0 | 0 | 0 | 35 | 37 | 55 | 18 | 23 | 18 | 25 | 32 | 50 | 0 | 25 | 0 | 120 | 0 | 25 | 225 | 0 | 0 | 0 | 0 | 12 | 60 | 84 | 70 | 50 | 35 | 13 | 35 | 0 | 0 | 0 | 305 | 310 | 210 | 63 | 0 | 40 | 0 | 0 | 51 | 0 | 46 | 52 | 18 | 8 | 33 | 21 | 165 | 162 | 0 | 19 | 0 | 33 | 28 | 51 | 45 | 0 | 0 | 61 | 84 | 0 | 202 | 18 | 0 | 10 | 310 | 16 | 8 | 0 | 300 | 300 | 100 | 170 | 80 | 70 | 0 | 74 | 34 | 150 | 400 | 115 | 105 | 105 | 0 | 300 | 54 | 51 | 106 | 113 | 90 | 50 | 70 | 0 | 162 | 34 | 0 | 35 |  | 94 | 35 | 0 | 162 |  |  | 509 | 0 | 410 |  | 98 | 0 | 0 | 0 | 35 | 74 | 40 | 60 | 31 | 64 | 0 | 0 | 0 | 26 | 34 | 80 | 14 | 42 | 42 | 8 | 35 | 22 | 0 | 8 | 75 | 0 | 260 | 0 | 0 | 190 |  | 0 | 0 | 0 | 0 | 200 | 0 | 380 | 17 | 0 | 113 | 100 | 107 | 0 | 0 | 113 | 1244 | 0 |  | 150 |  |  | 115 | 0 |  | 0 |  | 0 | 500 |  | 0
Forecast for Day | 0 | 0 | 0 | 180 | 0 | 16 | 0 | 400 | 300 | 0 | 0 | 450 | 300 | 16 | 90 | 15 | 0 | 0 | 90 | 90 | 48 | 130 | 0 | 0 | 0 | 0 | 35 | 37 | 35 | 10 | 23 | 18 | 25 | 32 | 48 | 0 | 25 | 0 | 120 | 0 | 25 | 225 | 0 | 0 | 0 | 0 | 12 | 45 | 66 | 50 | 0 | 26 | 13 | 10 | 0 | 0 | 0 | 300 | 310 | 210 | 63 | 0 | 40 | 0 | 0 | 51 | 0 | 31 | 25 | 18 | 8 | 21 | 21 | 143 | 162 | 0 | 16 | 1.6 | 33 | 28 | 51 | 44 | 0 | 0 | 61 | 85 | 0 | 190 | 18 | 0 | 10 | 300 | 16 | 8 | 0 | 300 | 300 | 50 | 160 | 0 | 0 | 20 | 50 | 17 | 80 | 400 | 75 | 105 | 105 | 5 | 120 | 17 | 17 | 17 | 9 | 63 | 50 | 54 | 50 | 108 | 34 | 0 | 35 | 30 | 94 | 17 | 0 | 162 |  |  | 509 | 0 | 90 | 0 | 85 | 0 | 0 | 0 | 22 | 55 | 0 | 60 | 25 | 16 | 0 | 0 | 0 | 26 | 0 | 80 | 0 | 34 | 24 | 0 | 35 | 22 | 0 | 8 | 75 | 0 | 250 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 380 | 17 | 0 | 35 | 0 | 42 | 0 | 8 | 95 | 750 | 0 |  | 17 | 6 | 100 | 35 | 0 |  | 0 | 30 | 0 | 500 | 130 | 0 |  |  |  |  | g | h | o | c | h | t | s
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 0 | 76 | 0 | 396 | 303 | 0 | 0 | 400 | 312 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 23 | 15 | 25 | 33 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 39 | 0 | 0 | 0 | 325 | 310 | 212 | 63 | 0 | 44 | 0 | 0 | 51 | 0 | 0 | 0 | 18 | 0 | 33 | 18 | 74 | 162 | 0 | 19 | 1 | 33 | 30 | 51 | 49 | 0 | 0 | 61 | 80 | 0 | 120 | 17 | 0 | 10 | 300 | 16 | 8 | 0 | 0 | 0 | 0 | 47 | 0 | 0 | 9 | 20 | 0 | 0 | 367 | 47 | 0 | 0 | 2 | 30 | 0 | 0 | 0 | 0 | 0 | 76 | 0 | 26 | 0 | 34 | 0 | 17 | 15 | 0 | 0 | 0 | 163 | 0 | 0 | 495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 75 | 0 | 170 | 0 | 0 | 167 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 418 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 600 | 0 | 0 | 0 | 2 | 40 | 0 | 0 | 0 | 0 | 12 | 0 | 511 | 67 | 0 | 0 |  |  |  | 147.003 | 13.5084 | 36.2102 | 38.9229 | 0.28866 | 2.5478 | 2.5963
241.0772
| Minimum Generation |  | 9512 | 6:00
| Highest Generation |  | 11551 | 14:00
| Day Peak Generation |  | 11335 | 12:00
| Evening Peak Generation |  | 7753 | 20:00
| HVDC Max Flow |  | 911 | 4:00
| HVDC EvPeak Flow |  | 491 | 20:00
| Load factor L.F |  | 86.96% | [161 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2023-04-28
Till now the maximum generation is : - |  |  |  | 15648 | 21:00 | Hrs on | 2023-04-19
The Summary of Yesterday's |  |  | 2023-04-27 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 11335 | MW Hour : | 12:00 | Min. Gen. at | 6:00 | 7561
Evening Peak Generation : |  |  | 7753 | MW Hour : | 20:00 | Available Max Generation : |  | 14443
E.P. Demand (at gen end) : |  |  | 7753 | MW Hour : | 20:00 | Max Demand (Evening) : |  | 11000
Maximum Generation : |  |  | 11551 | MW Hour : | 14:00 | Reserve(Generation end) |  | 3443
Total Gen. (MKWH) : |  |  | 241.0772 | System Load Factor : | 86.96% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | -40 | MW at | 6:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2023-04-28
Actual : |  | 75.19 | Ft.(MSL) , | Rule curve : | 82.6 | Ft.( MSL )
Gas Consumed : |  | Total = | 1076.18 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 170873824.204
: |  |  | Coal : | 257435735.45 | Oil : | 419639339.82 | Total : | 847948899.474
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 0 | 0:00 | 3784.5363 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 1043.9353 |  |  | 0 | 0%
Khulna Area |  | 0 | 0:00 | 1371.5095 |  |  | 0 | 0%
Rajshahi Area |  | 0 | 0:00 | 1209.1255 |  |  | 0 | 0%
Cumilla Area |  | 0 | 0:00 | 1032.782 |  |  | 0 | 0%
Mymensingh Area |  | 0 | 0:00 | 848.3185 |  |  | 0 | 0%
Sylhet Area |  | 0 | 0:00 | 383.9267 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 309.2613 |  |  | 0 | 0%
Rangpur Area |  | 0 | 0:00 | 669.8549 |  |  | 0 | 0%
Total |  | 0 |  | 10653.25 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 2
2) Ghorasal-3,7
3) Bhula Nuton Biddut
4) Baghabari-100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
7) Shajibazar 330 MW
8) Sirajganj- 2
9) Barishal 307 MW
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
8:15 | 14:16 | Agargaon 230/132kV S/S 132kV Transformer-1 (405T1) LT Scheduled S/D Due to Detected & Removed oil Leakage of 132/33kV Tr-1.
8:20 | 12:57 | Savar 132/33kV S/S T-2 LT Scheduled S/D Due to Red hot maintenance.
8:20 | 12:57 | Savar 132/33kV S/S T-2 HT Scheduled S/D Due to Red hot maintenance.
8:20 | 17:25 | Madanganj 132/33kV S/S 132KV Main Bus Scheduled S/D.
8:26 | 14:11 | Agargaon 230/132kV S/S 132kV Transformer-1 (405T1) HT Scheduled S/D Due to Detected & Removed oil Leakage of 132/33kV Tr-1.
8:41 | 16:26 | Aminbazar-Mirpur 132kV Ckt-1 Scheduled S/D from Mirpur 132/33kV end Due to By pass DS Maintenance work.
- | 9:01 | Khulna 330 MW P/S Synchronize.
9:08 | 16:25 | Mirpur 132/33kV S/S Reserve Bus Scheduled S/D Due to By pass Ds Maintenance work.
9:17 | 14:52 | HVDC Bheramera- Ishwardi 230kV Ckt-3 Scheduled S/D from Ishurdi 230/132kV end Due to A/M.
9:31 | 14:52 | HVDC Bheramera- Ishwardi 230kV Ckt-3 Scheduled S/D from BIPTC end Due to Annual maintenance.
9:45 | - | ICT-1 Shutdown at Rampal P/S due to preventive Maintenance.
9:52 | 18:40 | BIPTC S/S 230kV Bus-2 Scheduled S/D Due to Annual maintenance.
10:13 | - | Ashuganj 132/33kV T-4 both sides tripped showing differential relay at HT side. | [5 empty] | 17MW load interrup.
10:53 | 12:10 | Saidpur 132/33kV S/S TR-4 (414T) LT Forced S/D Due to Due to red hot happen at 33KV BUS under T4 transformer. | [5 empty] | 25.0MW load interrup.
10:53 | 12:06 | Saidpur 132/33kV S/S TR-4 (414T) HT Forced S/D Due to Due to red hot happen at 33KV BUS under T4 transformer. | [5 empty] | 25.0MW load interrup.
10:57 | 12:11 | Shahjadpur 132/33kV S/S T-2(415T) HT Forced S/D Due to Red-hot maintenance (33kV incoming DS (b-phase).
11:20 | 12:20 | Madanganj 132/33kV S/S Madanganj -DPDC Char sayedpur 132k Ckt-1 Scheduled S/D.
12:08 | - | Sylhet CCPP 225 MW tripped.
12:31 | 12:48 | Rampura-Mogbazar 132kV ckt-1 tripped from Mogbazar end showing bus protection relay. | [5 empty] | 103MW load interrup.
12:31 | - | Rampura-Mogbazar 132kV ckt-2 tripped from Mogbazar end showing bus protection relay. | [5 empty] | 103MW load interrup.
13:03 | 14:23 | Savar 132/33kV S/S T-1 LT Scheduled S/D Due to Red hot maintenance.
13:04 | 14:23 | Savar 132/33kV S/S T-1 HT Scheduled S/D Due to Red hot maintenance.
- | 13:20 | Rampura-Mogbazar 132kV ckt-2 was switched on.
14:15 | - | Siddhirganj GT:Unit- 2 was shutdown due to filter change.
- | 14:18 | Pabna- Shahjadpur 132kV Ckt-1 is restored.
14:24 | - | Savar 132/33kV S/S T-3 LT Scheduled S/D Due to Piling work of blast wall of 132/33KV T-4 transformer and also Red hot maintenance work.
14:24 | - | Savar 132/33kV S/S T-3 HT Scheduled S/D Due to Piling work of blast wall of 132/33KV T-4 transformer and also Red hot maintenance work.
- | 15:31 | Bogura West 400KV Reactor ON.
- | 16:03 | Madanganj 132/33kV S/S Madanganj -Summit 102 MW 132 kv Ckt is restored.
- | 16:13 | Sylhet CCPP 225 MW GT was sync.
16:42 | - | Ghorasal-Narsingdi 132 kV Ckt-2 Tripped from Narshingdi 132/33kV end showing Relay Operated from Ghurashal end. relays.
16:44 | - | Pabna 132/33kV S/S T-2 HT Tripped showing -SF6 GAS CB OPEN PHASE ALARM -SF6 GAS CB Reclosing Lockout -O/C, E/F -Differential
Trip -Lock out RY Trip -Oil Temp Alarm -B.H Relay Alarm -Trip circuit Supervisition RY relays Due to SKY Wire problem ( Disconnect) of 33 kV
sujanagar and University line under ( PBS-2).
16:44 | - | Pabna 132/33kV S/S T-2 LT Tripped showing Lockout RY trip relays.
16:46 | 18:48 | Daudkandi-Sonargaon 132 kV Ckt-2 Tripped from Daudkandi 132/33kV end showing Distance Relay (P442) relays Due to Heavy storm and
from Sonargaon 132/33kV end showing General trip, Zone-1 trip, B-phase fault, Carrier send relays Due to Trip for thunderstorm.
16:51 | - | Khulna (S)-Satkhira 132kV Ckt-2 Tripped from Satkhira 132/33kV end showing Distance relay relays.
17:00 | - | Gopalganj(N)-Madaripur 132kV Ckt-1 Tripped from Gopalganj 400/132kV end showing Zone-1 relays Due to Zone-1, Phase AC, Distance 2km.
17:40 | 18:10 | Matuail-Siddhirganj 132kV Ckt-1 Tripped from Siddhirganj 132/33kV end showing 1) O/C 2) E/F relays Due to Trip from Matuail End | [5 empty] | 32.0MW load interrup.
|  | (Siddhirganj end CB on). | [5 empty] | Siddhirganj 132/33kV end.
17:40 | 20:15 | Matuail-Maniknagar 132 kV ckt tripped from Matuail end showing O/C, E/F relay.
17:41 | - | Ghorasal GT-4 was shutdown due to bad weather.
17:41 | 18:21 | Siddhirganj-Siddhirganj (Orion)132kV Ckt-1 Tripped from Siddhirganj 132/33kV end showing 1)Simense SIPROTEC i.General Trip
ii) O/C iii) E/F iv) DEF 2) Lock out relays Due to Storm.
17:41 | 19:07 | Siddhirganj 132/33kV S/S 120MW EGCB GT1 Tripped showing 1) LBB Initiation in ABB RED 670 Relay 2)86 relays Due to Storm.
17:45 | 18:49 | Khulna(C )-Noapara 132kV Ckt-1 Forced S/D from Khulna (C) end Due to Due to over voltage control by order to NLDC. and from
Noapara 132/33kV end Due to Instructed By ALDC Khulna.
17:46 | 18:52 | Sonargaon 132/33kV S/S OPSL(IEL-2) Tripped showing General trip, OV trip/ ALM relays Due to Line trip.
17:47 | 18:50 | Jashore-Noapara 132kV Ckt-1 Forced S/D from Noapara 132/33kV end Due to Instructed By ALDC Khulna.
17:50 | 18:58 | Goalpara- Khulna (C) 132kV Ckt-2 Forced S/D from Khulna (C) end Due to Due to over voltage control by order to NLDC.
17:56 | 19:29 | Candpur- Kachua 132kV Ckt-2 Tripped from Kachua 132/33kV end showing REC650 REL670 relays. and from Chandpur 132/33kV
end showing Distance relay R=0.07 ohm, Distance =2.1 KM, Zone = Z1, Phase = B relays.
17:57 | - | Chandpur 132/33kV S/S 50MW(ST) Power Plant Incomer(T3) Tripped showing Trip Auxiliary relay relays.
18:05 | 19:11 | Aminbazar 400/230/132kV S/S ATR-02 LT Tripped showing 86-1 operated 86-2 operated relays Due to Storm.
18:05 | 20:48 | Aminbazar 400/230/132kV S/S Gopalganj-1 Tripped showing - 86 2.1 Operated - 86 2.2 Operated - 3 ph 86 - R ph Trip - Y ph Trip - B ph Trip relays Due to Storm.
18:05 | 21:36 | Gopalganj 400/132kV S/S 400kV Payra Ckt-2 Tripped showing AR Block relays Due to Over Voltage.
18:05 | 21:14 | Gopalganj 400/132kV S/S 400kV Aminbazar Ckt-1 Tripped showing Ar Block relays Due to Over Voltage.
18:05 | 21:56 | Gopalganj 400/132kV S/S 400kV Aminbazar Ckt-2 Tripped showing AR block relays Due to Over Voltage.
18:05 | 21:55 | Aminbazar 400/230/132kV S/S Gopalganj-2 Tripped showing - 86 2.1 Operated - 86 2.2 Operated - 3 ph 86 - R ph Trip - Y ph Trip - B ph Trip relays Due to Storm.
18:05 | 22:02 | Aminbazar 400/230/132kV S/S ATR-03 HT Tripped showing R ph Int Y ph Int B ph Int 3 ph IN (OHL) relays Due to Storm.
18:05 | 22:04 | Aminbazar 400/230/132kV S/S ATR-03 LT Tripped showing 86-1 operated 86-2 operated relays.
18:05 | 21:55 | Gopalganj 400/132kV S/S 400kV Rampal Ckt-1 Tripped showing O/V, DTT relays.
18:05 | 19:17 | Aminbazar 400/230/132kV S/S ATR-02 HT Tripped showing R ph Int Y ph Int B ph Int 3 ph IN (OHL) relays Due to Storm.
18:11 | - | Bagerhat-Mongla 132 kV Ckt-2 Tripped from Bagerhat 132/33kV end showing Distance Relay. relays. and from Mongla 132/33kV end
showing Distance Relay, relays Due to Distance Relay Zone-2.
18:11 | - | Mongla SS-Orion solar ckt tripped from Mongla SS end .
18:25 | - | Pabna 132/33kV S/S T-2 HT Forced S/D Due to 132/33 kV T-2 HT Tripped showing -SF6 GAS CB OPEN PHASE ALARM -SF6 GAS CB
Reclosing Lockout -O/C, E/F -Differential Trip -Lock out RY Trip -Oil Temp Alarm -B.H Relay Alarm -Trip circuit Supervisition RY relays due
to SKY Wire problem ( Disconnect) of 33 kV sujanagar and University line under ( PBS-2).
18:25 | - | Pabna 132/33kV S/S T-2 LT Forced S/D Due to 132/33 kV T-2 LT Tripped showing Lockout RY trip relays.
19:12 | 19:53 | Chauddagram-Feni 132 kV Ckt-2 Tripped from Feni 132/33kV end showing Auto reclose Relay relays.
19:14 | - | Sylhet CCPP 225 MW GT tripped due to booster trip. | [5 empty] | 150MW generation interrup.
19:37 | 19:51 | Jhenaidah-Magura 132 kV Ckt-2 Tripped from Jhenaidah 132/33kV end showing Trip A, B,C Distance trip Zone-1 trip relays.
- | 19:57 | Rampal 400/230 kV ICT-1 was switched on.
20:15 | - | Bibiyana South 400 MW was forced shutdown due to fire at GBC vent. | [5 empty] | 400MW generation interrup.
23:38 | - | Bhola CCPP 225 MW GT2 was sync. at 23:38 hrs & GT1 was shutdown at 23:50 hrs.
- | 0:13 | Sylhet CCPP 225 MW GT was sync.
2:11 | - | Bheramara 410MW tripped at 02:11 hrs. due to GBC trip. | [5 empty] | 390MW generation interrup.
2:20 | - | Siddirganj CCPP 335MW tripped. | [5 empty] | 180MW generation interrup.
- | 3:00 | Bibiyana South 400 MW GT was sync.
- | 3:09 | Siddirganj CCPP 335MW GT was sync.
6:00 | - | Kushtia 132/33kV S/S T-1 HT Forced S/D Due to Red hot maintenance. | [5 empty] | 22.0MW load interrup.
6:09 | - | Siddirganj 335 MW CCPP GT was shut down for air filter cleaning.
7:25 | - | Faridpur 132/33kV S/S Transformer-1 LT Scheduled S/D Due to Hot spot maintenance work.
7:25 | - | Faridpur 132/33kV S/S Transformer-1 HT Scheduled S/D Due to Hot spot maintenance work.
7:33 | - | Bogura 132/33kV S/S Transformer-2 HT Forced S/D Due to Red Hot. | [5 empty] | 15.0MW load interrup.
7:33 | - | Bogura 132/33kV S/S Transformer-2 LT Forced S/D Due to Red Hot. | [5 empty] | 15.0MW load interrup.
- | 7:33 | Bibiyana South 400 MW ST was sync.
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2023-04-27 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 2770281
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4284000
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 12 | 1095636 | Bad weather
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 379 | 9035770 | Bad weather
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 303 | 7416000 | Bad weather
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 330 | 9609250 | Bad weather
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 0 | 502080 | Reserve
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 285 | 6857513 | FGMO
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 0 | 0 | Reserve
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 0 | 105728 | Reserve
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 201960
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 1038000 | Bad weather
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 0 | 927360
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 2660056 | Bad weather
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 272880 | Reserve
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 0 | 160560 | Reserve
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 0 | 491040 | Reserve
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 0 | 278038 | Reserve
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 0 | 224653 | Reserve
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 26 | 890580 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 0 | 469700
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 16 | 270300 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 0 | 451200 | Reserve
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 0 | 444109 | Reserve
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 0 | 0 | Reserve
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 0 | 173950 | Reserve
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 0 | 1284979
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 0 | 904320 | Reserve
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 0 | 496800 | Reserve
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 189429
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 407160 | Low Demand
| Dhaka area Total |  |  |  | 5847 | 1548 | 53913332
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 120 | 2800000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 0 | 89778 | Reserve
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 143100
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 38 | 223680 | Engine problem
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 25 | 288660 | Low Water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 220 | 5187923
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 17 | 945927 | Low Demand
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 101520 | Reserve
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 867452 | Low Demand
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 0 | 692400 | Reserve
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 74 | 1140480 | Low Demand
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 266112 | Bad weather
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 26 | 763200
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 53760 | Reserve
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 33242
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 170 | 2719855 | Low Demand
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 332057 | Reserve
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 17 | 936726 | Low Demand
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 756480 | Reserve
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 34 | 840545 | Fuel shortage
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 0 | 163 | 3910836 | On test.
| Chattogram area Total |  |  |  | 2382 | 967 | 23093733
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 189 | 4855000 | FGMO
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 285 | 7577600 | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 275 | 7168000 | FGMO
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 0 | 0 | Under maint.
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 40 | 931968 | Engine problem
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 0 | 0 | Contract Expired
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 2325090 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 10 | 693286 | Low Demand
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 5 | 217454 | Low Demand
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 843524 | Reserve
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 17 | 908640 | Low Demand
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 197244 | Bad weather
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 0 | 151560 | Bad weather
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 50 | 2547840
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 0 | 683300 | Bad weather
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 161155 | Reserve
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 0 | 364510 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 976980 | Reserve
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 8 | 442680 | Low Demand
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 0 | 480600 | Reserve
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 17 | 1291200 | Low Demand
| Cumilla Area Total |  |  |  | 3151 | 904 | 32817631
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 119 | 3565440
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 255132 | Engine problem
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 10400
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 163 | 2385600 | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 115 | 1645200
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 289170
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 11 | 253920 | Engine problem
| Mymensingh Area Total |  |  |  | 614 | 408 | 8404862
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 32 | 754000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 28 | 619560 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Under maint.
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 20 | 733200 | Low Demand
| Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 20 | 702280 | Low Demand
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 0 | 173368 | Engine problem
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 61 | 1317408
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 30 | 1725120 | Bad weather
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 0 | 2652380 | Machine problem
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 366000
| Sylhet 50MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 8 | 367488 | Engine problem
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 280 | 6907000 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 377 | 8846000 | FGMO
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 0 | 226620
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 274 | 7389000 | Bad weather
| Sylhet Area Total |  |  |  | 2427 | 1147 | 32779424
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Fuel shortage
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 491 | 13508363
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 0 | 553920 | Reserve
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel conservation
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 200 | 8214336 | Bad weather
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 0 | 34500 | Reserve
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 6240 | Reserve
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 272880 | Reserve
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 662400
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 0 | 0 | 327102 | On test.
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 660*2 | 617 | 0 | 0 | On test.
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3001 | 691 | 23579741
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 424512
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 6 | 561609 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 62 | 1366000 | Machine problem
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 250 | 23955700 | Bad weather
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 0 | 0 | Under maint.
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 189600 | Reserve
| Barisal 307 MW |  | BCPCL | 307*1 | 307 | 0 | 0 | Coal shortage
| Barisal Area Total |  |  |  | 2265 | 318 | 26497421
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 1045000 | Bad weather
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Reserve
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 149 | 4283100 | FGMO
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 159 | 4316764 | FGMO
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 424 | 9481854 | DCT
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 21 | 436560
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 0 | 133902 | Engine problem
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 12485 | Reserve
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Reserve
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Reserve
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 57 | 1063968 | Low Demand
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 35 | 694944 | Low Demand
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 25920
| Adani Power Jharkhanda Ltd |  | Import | 0 | 0 | 425 | 7281818 | On test.
| Rajshahi Area Total |  |  |  | 2129 | 1270 | 28776315
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 74 | 1806545 | Coal shortage
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 200 | 5878800 | Bad weather
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 19000
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 111 | 1165814
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 47292
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 115 | 1101888
| Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 194098
| Teesta Solar Limited |  | BPCL | 16*12.5 | 0 | 0 | 1001270
| Rangpur Area Total |  |  |  | 750 | 500 | 11214707
| Total |  |  |  | 22566 | 7753 | 241077166
| Eastern Grid Total |  |  |  | 14421 | 4974 | 151008982
| Western Grid Total |  |  |  | 8145 | 2779 | 90068184
| National Grid Total |  |  |  | 22566 | 7753 | 241077166
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2023-04-27
| (a) ENTIRE EASTERN GRID : |  | 4892.21 | MW | (b) ENTIRE WESTERN GRID : |  | 2595.4 | MW
| i) Dhaka area |  | 2433.61 | MW | i) Khulna area |  | 465.8 | MW
| ii) Chittagong area |  | 1164.6 | MW | ii) Rajshahi area |  | 1105.2 | MW
| iii) Comilla area |  | 196 | MW | iii) Barisal area |  | 140.4 | MW
| iv) Mymensingh area |  | 898 | MW | iv) Rangpur area |  | 884 | MW
| v) Sylhet area |  | 200 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 7487.61 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | Chhatak | 27 | 00:00 | Kamrangirchar | 29 | 13:00 | Natore | 122 | 19:30 | Shitalakhya | 82 | 16:00
2 | AKSML | 94 | 03:00 | Chowmuhani | 196 | 00:00 | Kaptai | 4 | 18:00 | Nawabganj | 53.5 | 00:00 | Sholosohor | 27 | 19:00
3 | Aftabnagar | 30 | 00:00 | Chuadanga | 87 | 13:00 | Kazla | 46 | 15:00 | Netrakona | 130 | 00:00 | Shyampur | 86 | 06:00
4 | Agargaon | 78 | 13:00 | Coxsbazar | 135 | 20:00 | Keranigonj | 50 | 00:00 | New | 44 | 13:00 | Siddhirganj | 74 | 00:00
5 | Agrabad | 68 | 15:00 | Cumilla(N) | 145 | 00:00 | Khagrachori | 30 | 19:00 | Niamatpur | 93 | 12:00 | Sirajganj | 88 | 14:00
6 | Amnura | 49 | 12:00 | Cumilla(S) | 146 | 00:00 | Khulna | 81 | 13:00 | Noapara | 37 | 00:00 | Sonargaon | 56 | 00:00
7 | Ashuganj | 68 | 00:00 | Daudkandi | 134 | 00:00 | Khulshi | 141 | 19:00 | PHP | 9 | 11:00 | Sreemongol | 64 | 18:30
8 | BIPTC | N/A | N/A | Dhaka | 24 | 11:00 | Kishoreganj | 140 | 00:00 | Pabna | 89 | 14:00 | Sreepur | 42.6 | 15:00
9 | BSRM | 108 | 22:00 | Dhamrai | 110 | 15:00 | Kodda | 183 | 16:00 | Palashbari | 120 | 14:00 | Srinagar | 40.25 | 00:00
10 | Bagerhat | 74 | 00:00 | Dhanmondi | 134 | 14:00 | Kulaura | 48 | 18:30 | Panchagarh | 54 | 19:00 | Sunamganj | 50 | 00:00
11 | Bakulia | 85 | 19:00 | Dohazari | 96 | 20:00 | Kurigram | 70 | 19:30 | Patuakhali | 102 | 00:00 | Sylhet | 147 | 18:30
12 | Banani | 43 | 13:00 | Faridpur | 132 | 00:00 | Kushtia | 116 | 14:00 | Payra | 21.4 | 00:00 | TK | 30 | 20:00
13 | Bangabhaban | 25 | 10:00 | Fatullah | 38 | 14:00 | Lalbag | 24 | 11:00 | Postogola | 43 | 00:00 | Tangail | 215 | 14:00
14 | Barapukuria | 62 | 20:00 | Fenchuganj | 47 | 18:30 | Lalmonirhat | 52 | 19:30 | Purbachal | 15 | 01:00 | Thakurgaon | 92 | 19:30
15 | Barguna | 20 | 00:00 | Feni | 114 | 18:30 | Madanganj | 22 | 13:00 | Purbasadipur | 119 | 19:30 | Tongi | 98 | 15:00
16 | Barishal | 105 | 15:00 | GPH | 75 | 19:00 | Madaripur | 92 | 01:00 | Rahanpur_I | 0 | 00:00 | Ullon | 36 | 00:00
17 | Barishal-230 | 82 | 00:00 | Ghorashal | 74 | 01:00 | Madartek | 70 | 00:00 | Rahim | 0 | 00:00 | Uttara | 59 | 15:00
18 | Baroaulia | 59 | 00:00 | Goalpara | 38 | 00:00 | Madunaghat | 49 | 19:00 | Rajbari | 56 | 01:00 | UttaraNew | 42 | 13:00
19 | Baroirhat | 59 | 19:00 | Gollamari | 46 | 13:00 | Magura | 52 | 00:00 | Rajendrapur | 88 | 15:00 | Zigatola | 62 | 17:00
20 | Bashundhara | 141 | 15:00 | Gopalganj | 92 | 00:00 | Mahasthangarh | 76 | 00:00 | Rajshahi | 120 | 13:00
21 | BashundharaCement | 0 | 00:00 | Gulshan | 116 | 13:00 | Manikganj | 92 | 13:00 | Rajshahi-230 | 27 | 21:00
22 | Beanibazar | 69 | 19:00 | Halishahar | 73 | 18:30 | Maniknagar | 76 | 13:00 | Ramganj | 108 | 01:00
23 | Benapole | 52 | 00:00 | HaripurSBU | 84 | 13:00 | Matarbari | 47 | 20:00 | Rampur | 28 | 00:00
24 | Bhaluka | 124 | 00:00 | Hasnabad | 61 | 14:00 | Matuail | 34 | 00:00 | Rangamati | 16 | 18:30
25 | Bhandaria | 46 | 00:00 | Hathazari | 76 | 19:00 | Millgate | 48 | 12:00 | Rangpur | 137 | 19:30
26 | Bhangura | 38 | 14:00 | Ishurdi | 49 | 12:00 | Mirpur | 107 | 15:00 | Ruppur | 6.2 | 11:00
27 | Bheramara(GK) | 49 | 13:00 | Jaldhaka | 76 | 19:00 | Mirsorai | 3 | 00:00 | SSM | 0 | 00:00
28 | Bhulta | 159 | 15:00 | Jamalpur | 166 | 00:00 | Mithapukur | 40 | 19:30 | Saidpur | 113 | 19:00
29 | Bog-Sherpur | 58 | 13:00 | Jashore | 121 | 14:00 | Modern | 0 | 00:00 | Satkhira | 124 | 00:00
30 | Bogura | 150 | 01:00 | Jhenaidah | 102 | 14:00 | Mogbazar | 108 | 14:00 | Satmasjid | 99 | 15:00
31 | Borhanuddin | 59 | 00:00 | Joydebpur | 102 | 15:00 | Mongla | 34 | 00:00 | Savar | 88 | 13:00
32 | Brahmanbaria | 167 | 00:00 | Joypurhat | 65 | 00:00 | Motijheel | 34 | 13:00 | Shahjadpur | 91 | 13:00
33 | Cantonment | 120 | 14:00 | Juldah | 26 | 00:00 | Munshiganj | 100 | 01:00 | Shahjibazar | 113 | 00:00
34 | Chandpur | 62 | 16:00 | KSRM | 53 | 00:00 | Mymensingh | 178 | 14:00 | Shahmirpur | 45.1 | 00:00
35 | Chandraghona | 30 | 19:00 | Kabirpur | 187 | 16:00 | Naogaon | 113 | 20:00 | Shariatpur | 75 | 00:00
36 | Chapai | 52 | 21:00 | Kachua | 68 | 00:00 | Narail | 48 | 01:00 | Sherpur | 156 | 00:00
37 | Charsaidpur | 30.5 | 12:00 | Kallyanpur | 84 | 15:00 | Narinda | 42 | 13:00 | Shikalbaha | 35 | 19:30
38 | Chauddagram | 62 | 18:30 | Kalurghat | 24 | 00:00 | Narshingdi | 141 | 00:00 | Shikalbaha-230 | N/A | N/A
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2023-04-27 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 415 | 06:00 | 405 | 10:00 | Kaliakoir | N/A | N/A | N/A | N/A
| Bhulta | 401 | 17:00 | 391 | 10:00 | Madunaghat_I | 402 | 06:00 | 383 | 10:00
| Bibiana | 413 | 17:00 | 400 | 13:00 | Payra | 431 | 18:00 | 415 | 12:00
| BIPTC | 408 | 18:00 | 394 | 00:00 | Rahanpur_I | 421 | 05:00 | 409 | 00:00
| Gopalganj | 416 | 06:00 | 393 | 00:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 245 | 18:00 | 232 | 12:00 | Hathazari | 233 | 06:00 | 230 | 03:00
| AKSML | 233 | 21:00 | 225 | 10:00 | Ishurdi | 244 | 18:00 | 228 | 12:00
| Aminbazar | 243 | 17:00 | 235 | 12:00 | Jhenaidah | 243 | 18:00 | 217 | 13:00
| Ashuganj | 245 | 18:00 | 237 | 10:00 | Kaliakoir | N/A | N/A | N/A | N/A
| Baghabari | 238 | 16:00 | 227 | 12:00 | Keranigonj | 245 | 18:00 | 232 | 10:00
| Barapukuria | 221 | 00:00 | 212 | 18:30 | Khulna(S) | 244 | 18:00 | 223 | 13:00
| Barishal | 248 | 19:00 | 216 | 00:00 | Madunaghat_I | 232 | 18:00 | 223 | 10:00
| Bheramara | 242 | 18:00 | 226 | 12:00 | Maniknagar | 243 | 18:00 | 232 | 12:00
| Bhulta | 241 | 18:00 | 234 | 10:00 | Meghnaghat | 250 | 18:00 | 239 | 11:00
| Bibiana | 241 | 18:00 | 234 | 13:00 | Mirsorai | 240 | 06:00 | 231 | 09:00
| BIPTC | 240 | 18:00 | 230 | 10:00 | Rajshahi | 238 | 17:00 | 224 | 13:00
| Bogura | 227 | 06:00 | 220 | 12:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 250 | 18:30 | 215 | 00:00 | Rampura | 243 | 18:00 | 226 | 08:00
| BSRM | 239 | 06:00 | 230 | 10:00 | Shikalbaha | 232 | 21:00 | 223 | 10:00
| Cumilla(N) | 240 | 18:00 | 230 | 10:00 | Shyampur | 245 | 18:00 | 232 | 10:00
| Fenchuganj | 244 | 21:00 | 237 | 12:00 | Siddhirganj | 242 | 17:00 | 231 | 06:00
| Ghorashal | N/A | N/A | N/A | N/A | Sirajgonj | 246 | 18:00 | 235 | 07:00
| GPH | 236 | 21:00 | 225 | 10:00 | Sreepur | 243 | 18:00 | 233 | 10:00
| Haripur | 243 | 18:00 | 233 | 10:00 | Tongi | 235 | 18:00 | 230 | 09:00
| Hasnabad | 248 | 18:00 | 232 | 12:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 139 | 06:00 | 133 | 09:00 | Lalbag | 139 | 18:00 | 131 | 21:00
| Agargaon | 141 | 18:00 | 133 | 10:00 | Lalmonirhat | 129 | 00:00 | 119 | 18:30
| Agrabad | 138 | 21:00 | 129 | 10:00 | Madanganj | 143 | 18:00 | 134 | 10:00
| AKS | 135 | 06:00 | 128 | 08:00 | Madaripur | 141 | 19:00 | 122 | 00:00
| Aminbazar | 141 | 17:00 | 132 | 12:00 | Madartek | 140 | 18:00 | 132 | 10:00
| Amnura | 135 | 17:00 | 128 | 12:00 | Madunaghat | 138 | 21:00 | 130 | 18:30
| Ashuganj | 147 | 17:00 | 138 | 00:00 | Magura | 145 | 17:00 | 126 | 13:00
| Bagerhat | 146 | 18:00 | 123 | 13:00 | Mahasthangarh | 132 | 17:00 | 125 | 12:00
| Bakulia | 137 | 21:00 | 129 | 18:30 | Manikganj | 135 | 17:00 | 125 | 10:00
| Banani | 142 | 18:00 | 138 | 18:30 | Maniknagar | 144 | 18:00 | 135 | 12:00
| Bangabhaban | 142 | 18:00 | 135 | 12:00 | Matarbari | 126 | 22:00 | 110 | 18:30
| Barapukuria | 137 | 20:00 | 129 | 18:30 | Matuail | 139 | 17:00 | 136 | 10:00
| Barguna | 143 | 19:00 | 131 | 02:00 | Millgate | 140 | 17:00 | 131 | 12:00
| Barishal | 143 | 19:30 | 127 | 00:00 | Mirpur | 141 | 18:00 | 130 | 12:00
| Barishal-230 | 141 | 19:00 | 127 | 00:00 | Mithapukur | 132 | 05:00 | 122 | 13:00
| Baroaulia | 138 | 21:00 | 130 | 00:00 | Modern | 137 | 06:00 | 129 | 19:00
| Baroirhat | 138 | 18:30 | 124 | 10:00 | Mogbazar | 142 | 18:00 | 133 | 15:00
| Bashundhara | 140 | 18:00 | 131 | 11:00 | Mongla | 144 | 18:00 | 124 | 13:00
| BashundharaCement | 143 | 18:00 | 134 | 10:00 | Motijheel | 142 | 18:00 | 135 | 12:00
| Beanibazar | 140 | 21:00 | 125 | 14:00 | Munshiganj | 143 | 18:00 | 134 | 13:00
| Benapole | 142 | 17:00 | 122 | 13:00 | Mymensingh | 130 | 19:30 | 115 | 10:00
| Bhaluka | 128 | 19:30 | 112 | 10:00 | Naogaon | 129 | 15:00 | 115 | 12:00
| Bhandaria | 144 | 19:00 | 124 | 03:00 | Narail | 143 | 17:00 | 126 | 13:00
| Bhangura | 141 | 16:00 | 133 | 12:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bheramara | 138 | 18:00 | 131 | 12:00 | Narshingdi | 142 | 18:00 | 131 | 12:00
| Bheramara(GK) | 138 | 06:00 | 133 | 12:00 | Natore | 134 | 16:00 | 131 | 02:00
| Bhulta | 135 | 18:00 | 129 | 10:00 | Nawabganj | 135 | 05:00 | 131 | 10:00
| Bog-Sherpur | 135 | 17:00 | 128 | 12:00 | Netrakona | 130 | 19:30 | 115 | 10:00
| Bogura | 134 | 02:00 | 128 | 12:00 | New | 140 | 18:00 | 132 | 12:00
| Bogura-230 | 134 | 01:00 | 128 | 12:00 | Niamatpur | 128 | 15:00 | 109 | 13:00
| Brahmanbaria | 139 | 19:00 | 132 | 00:00 | Noapara | 144 | 17:00 | 126 | 13:00
| Cantonment | 141 | 18:00 | 132 | 12:00 | Pabna | 139 | 16:00 | 127 | 13:00
| Chandpur | 143 | 19:30 | 121 | 02:00 | Palashbari | 129 | 06:00 | 121 | 13:00
| Chandraghona | 139 | 21:00 | 129 | 18:30 | Panchagarh | 139 | 01:00 | 120 | 18:30
| Chapai | 134 | 01:00 | 129 | 12:00 | Patuakhali | 143 | 19:00 | 132 | 06:00
| Charsaidpur | 141 | 18:00 | 135 | 10:00 | Payra | 143 | 19:00 | 136 | 02:00
| Chauddagram | 140 | 19:30 | 124 | 10:00 | PHP | 139 | 21:00 | 122 | 10:00
| Chhatak | 140 | 20:00 | 123 | 13:00 | Postogola | 142 | 18:00 | 134 | 10:00
| Chowmuhani | 143 | 19:00 | 118 | 10:00 | Purbachal | 140 | 06:00 | 133 | 10:00
| Chuadanga | 143 | 17:00 | 120 | 13:00 | Purbasadipur | 134 | 01:00 | 117 | 07:00
| Coxsbazar | 120 | 06:00 | 107 | 18:30 | Rahim | 144 | 18:00 | 137 | 00:00
| Cumilla(N) | 142 | 19:00 | 130 | 10:00 | Rajbari | 141 | 18:00 | 126 | 01:00
| Cumilla(S) | 142 | 19:00 | 128 | 16:00 | Rajendrapur | 137 | 18:00 | 124 | 12:00
| Daudkandi | 143 | 19:00 | 131 | 00:00 | Rajshahi | 134 | 18:00 | 127 | 12:00
| Dhaka | 141 | 18:00 | 133 | 12:00 | Rajshahi-230 | 134 | 17:00 | 126 | 13:00
| Dhamrai | 140 | 18:00 | 128 | 10:00 | Ramganj | 142 | 19:00 | 116 | 02:00
| Dhanmondi | 140 | 18:00 | 135.5 | 12:00 | Rampur | 136 | 21:00 | 129 | 13:00
| Dohazari | 134 | 07:00 | 124 | 13:00 | Rampura | 140 | 18:00 | 133 | 10:00
| Faridpur | 140 | 18:00 | 126 | 00:00 | Rangamati | 138 | 21:00 | 128 | 18:30
| Fatullah | 144 | 18:00 | 135 | 10:00 | Rangpur | 131 | 01:00 | 122 | 08:00
| Fenchuganj | 141 | 21:00 | 132 | 12:00 | Ruppur | 140 | 16:00 | 131 | 12:00
| Feni | 140 | 19:00 | 124 | 10:00 | Saidpur | 132 | 03:00 | 121 | 12:00
| Ghorashal | 143 | 17:00 | 139 | 12:00 | Satkhira | 145 | 18:00 | 123 | 13:00
| Goalpara | 144 | 17:00 | 128 | 13:00 | Satmasjid | 142 | 18:00 | 132 | 12:00
| Gollamari | 139 | 18:00 | 123 | 01:00 | Savar | 140 | 18:00 | 129 | 20:00
| Gopalganj | 141 | 18:00 | 124 | 00:00 | Shahjadpur | 143 | 16:00 | 135 | 12:00
| Gopalganj-400 | 137 | 16:00 | 128 | 00:00 | Shahjibazar | 139 | 19:30 | 132 | 00:00
| Gulshan | 140 | 18:00 | 132 | 10:00 | Shahmirpur | 137 | 21:00 | 129 | 18:30
| Halishahar | 135 | 06:00 | 128 | 23:00 | Shariatpur | 140 | 18:00 | 125 | 00:00
| Haripur | 144 | 18:00 | 137 | 00:00 | Sherpur | 129 | 19:30 | 106 | 10:00
| HaripurSBU | 144 | 18:00 | 137 | 00:00 | Shikalbaha | 139 | 21:00 | 130 | 18:30
| Hasnabad | 142 | 18:00 | 135 | 00:00 | Shikalbaha-230 | 138 | 22:00 | 131 | 14:00
| Hathazari | 138 | 21:00 | 131 | 23:00 | Shitalakhya | 143 | 18:00 | 134 | 10:00
| Ishurdi | 140 | 18:00 | 131 | 13:00 | Sholosohor | 137 | 06:00 | 129 | 18:30
| Jaldhaka | 131 | 01:00 | 118 | 18:30 | Shyampur | 140 | 18:00 | 134 | 10:00
| Jamalpur | 134 | 19:30 | 110 | 10:00 | Shyampur-230 | 143 | 18:00 | 134 | 10:00
| Jashore | 144 | 17:00 | 123 | 13:00 | Siddhirganj | 140 | 18:00 | 137 | 00:00
| Jhenaidah | 144 | 17:00 | 128 | 13:00 | Sirajganj | 138 | 17:00 | 130 | 12:00
| Jhenaidah-230 | 144 | 17:00 | 128 | 13:00 | Sonargaon | 141 | 18:00 | 133 | 05:00
| Joydebpur | 144 | 00:00 | 138 | 21:00 | Sreemongol | 138 | 21:00 | 131 | 13:00
| Joypurhat | 127 | 15:00 | 111 | 12:00 | Sreepur | 138 | 18:00 | 132 | 10:00
| Juldah | 137 | 22:00 | 131 | 13:00 | Srinagar | 139 | 18:00 | 131 | 10:00
| Kabirpur | 138 | 18:00 | 127 | 12:00 | SSM | 140 | 05:00 | 132 | 00:00
| Kachua | 141 | 19:00 | 124 | 01:00 | Sunamganj | 138 | 21:00 | 120 | 13:00
| Kaliakoir | N/A | N/A | N/A | N/A | Sylhet | 139 | 21:00 | 126 | 13:00
| Kallyanpur | 141 | 18:00 | 132 | 10:00 | Tangail | 133 | 17:00 | 121 | 10:00
| Kalurghat | 138 | 06:00 | 130 | 18:30 | Thakurgaon | 138 | 01:00 | 117 | 10:00
| Kamrangirchar | 136 | 07:00 | 131 | 13:00 | TK | 138 | 21:00 | 130 | 18:30
| Kaptai | 134 | 07:00 | 130 | 00:00 | Tongi | 140 | 18:00 | 133 | 13:00
| Kazla | 141 | 18:00 | 136 | 11:00 | Ullon | 140 | 18:00 | 132 | 12:00
| Keranigonj | 138 | 18:00 | 131 | 20:00 | Uttara | 140 | 18:00 | 131 | 10:00
| Khagrachori | 139 | 21:00 | 128 | 18:30 | UttaraNew | 140 | 18:00 | 130 | 21:00
| Khulna | 143 | 17:00 | 127 | 13:00 | Zigatola | 138 | 18:00 | 132 | 12:00
| Khulna(S) | 144 | 17:00 | 129 | 13:00
| Khulshi | 135 | 21:00 | 128 | 10:00
| Kishoreganj | 134 | 19:00 | 124 | 10:00
| Kodda | 142 | 17:00 | 125 | 12:00
| KSRM | 138 | 21:00 | 130 | 00:00
| Kulaura | 140 | 21:00 | 131 | 13:00
| Kurigram | 129 | 20:00 | 115 | 18:30
| Kushtia | 141 | 17:00 | 129 | 12:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2023-04-27
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 280 | 5369 | 3479 | 8848 |  |  |  | QF-LDC-11
0:30 | 147 | 6301 | 3870 | 10171 | Date: | 2023-04-27
1:00 | 14 | 7233 | 4261 | 11494
1:30 | 27 | 7153.5 | 4156 | 11309.5
2:00 | 40 | 7074 | 4051 | 11125
2:30 | 45 | 6947.5 | 3967 | 10914.5 | [5 empty] | Gen. at Eve. Peak | 7753 | 7753 MW (20:00 )
3:00 | 50 | 6821 | 3883 | 10704 | [6 empty] | 20:00
3:30 | 75 | 6688 | 3866.5 | 10554.5 | [5 empty] | Gen. at Day Peak | 11335 | 11335 MW (12:00 )
4:00 | 100 | 6555 | 3850 | 10405 | [6 empty] | 12:00
4:30 | 60 | 6571.5 | 3656 | 10227.5 | [5 empty] | Highest Generation | 11551
5:00 | 20 | 6588 | 3462 | 10050 | [6 empty] | 14:00
5:30 | 30 | 6444.5 | 3336.5 | 9781
6:00 | 40 | 6301 | 3211 | 9512
6:30 | 35 | 6242.5 | 3290.5 | 9533
7:00 | 30 | 6184 | 3370 | 9554
7:30 | 45 | 6209 | 3410.5 | 9619.5
8:00 | 60 | 6234 | 3451 | 9685
8:30 | 100 | 6276.5 | 3590 | 9866.5
9:00 | 140 | 6319 | 3729 | 10048
9:30 | 248 | 6397.5 | 3871 | 10268.5
10:00 | 356 | 6476 | 4013 | 10489
10:30 | 375 | 6583.5 | 4078 | 10661.5
11:00 | 394 | 6691 | 4143 | 10834
11:30 | 405 | 6822 | 4262.5 | 11084.5
12:00 | 416 | 6953 | 4382 | 11335
12:30 | 409 | 6980 | 4430.5 | 11410.5
13:00 | 402 | 7007 | 4479 | 11486
13:30 | 411 | 7043 | 4475.5 | 11518.5
14:00 | 420 | 7079 | 4472 | 11551
14:30 | 683 | 6983 | 4353 | 11336
15:00 | 946 | 6887 | 4234 | 11121
15:30 | 1026 | 6756 | 3966.5 | 10722.5
16:00 | 1106 | 6625 | 3699 | 10324
16:30 | 1108 | 6310 | 3385.5 | 9695.5
17:00 | 1110 | 5995 | 3072 | 9067
17:30 | 621 | 5380.5 | 2737.5 | 8118
18:00 | 132 | 4766 | 2403 | 7169
18:30 | 77 | 4892.5 | 2458 | 7350.5
19:00 | 22 | 5019 | 2513 | 7532
19:30 | 120 | 4978 | 2673 | 7651
20:00 | 150 | 4974 | 2779 | 7753 |  |  |  | Executive Engineer
20:30 | 183 | 4939.5 | 2797 | 7736.5 |  |  |  | Network Operation Division
21:00 | 216 | 4905 | 2815 | 7720
21:30 | 157 | 5132.5 | 2879.5 | 8012
22:00 | 98 | 5360 | 2944 | 8304 |  |  |  |  | Page 6 of 7
22:30 | 139 | 5491.5 | 3023 | 8514.5
23:00 | 180 | 5623 | 3102 | 8725
23:30 | 230 | 5496 | 3290.5 | 8786.5
24:00 | 280 | 5369 | 3479 | 8848
7753 MW (20:00 )
11335 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2023-04-27 |  | Energy |  | 241077166
[13 empty] | 2023-04-27 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 3748 | 495 | 2241 | 0 | 565 | 1554 | 0 | 0 | 163 | 82 | 0 | 0
0:30 | 4143 | 679 | 2270.5 | 0 | 1131 | 1566.5 | 0 | 0 | 269 | 112 | 0 | 131.3125 |  | Date: | 43581
1:00 | 4538 | 863 | 2300 | 0 | 1697 | 1579 | 0 | 0 | 375 | 142 | 0 | 262.625
1:30 | 4520 | 863.5 | 2290.5 | 0 | 1598.5 | 1547.5 | 0 | 0 | 350.5 | 139 | 0 | 197.2075 | [8 empty] | Total Energy | 241.0772 |  | Total Energy Gen MKWHr Energy Not Served MKWHr Energy Requirement MKWHr | Total Energy Gen 241.077 MKWHr Energy Not Served 2.075 MKWHr Energy Requirement 243.152 MKWHr
2:00 | 4502 | 864 | 2281 | 0 | 1500 | 1516 | 0 | 0 | 326 | 136 | 0 | 131.79 | [8 empty] | Energy not Served | 2.0747
2:30 | 4501 | 863.5 | 2206 | 0 | 1388 | 1506 | 0 | 0 | 316 | 134 | 0 | 137.0425 | [8 empty] | Energy Requirement | 243.1519
3:00 | 4500 | 863 | 2131 | 0 | 1276 | 1496 | 0 | 0 | 306 | 132 | 0 | 142.295
3:30 | 4464 | 887 | 2070 | 0 | 1229.5 | 1465.5 | 0 | 0 | 307.5 | 131 | 0 | 128.4475 | [7 empty] | Shortage
4:00 | 4428 | 911 | 2009 | 0 | 1183 | 1435 | 0 | 0 | 309 | 130 | 0 | 114.6
4:30 | 4421 | 697.5 | 2061 | 0 | 1176.5 | 1434.5 | 0 | 0 | 309 | 128 | 0 | 114.6
5:00 | 4414 | 484 | 2113 | 0 | 1170 | 1434 | 0 | 0 | 309 | 126 | 0 | 114.6
5:30 | 4339 | 483 | 2009 | 0 | 1080 | 1433 | 0 | 0 | 309 | 121 | 7 | 82.13
6:00 | 4264 | 482 | 1905 | 0 | 990 | 1432 | 0 | 0 | 309 | 116 | 14 | 49.66
6:30 | 4248 | 482 | 1949 | 0 | 908 | 1480.5 | 0 | 0 | 309 | 107 | 49.5 | 24.83 | [6 empty] | Coal
7:00 | 4232 | 482 | 1993 | 0 | 826 | 1529 | 0 | 0 | 309 | 98 | 85 | 0
7:30 | 4234 | 472 | 2008 | 0 | 822 | 1544 | 0 | 0 | 309.5 | 101 | 129 | 10.0275 | [5 empty] | Oil
8:00 | 4236 | 462 | 2023 | 0 | 818 | 1559 | 0 | 0 | 310 | 104 | 173 | 20.055
8:30 | 4296.5 | 476 | 2028 | 0 | 834 | 1626 | 0 | 0 | 277.5 | 105 | 223.5 | 42.4975
9:00 | 4357 | 490 | 2033 | 0 | 850 | 1693 | 0 | 0 | 245 | 106 | 274 | 64.94
9:30 | 4415.5 | 490 | 2051.5 | 0 | 893 | 1749.5 | 0 | 11 | 243.5 | 106 | 308.5 | 62.5525
10:00 | 4474 | 490 | 2070 | 0 | 936 | 1806 | 0 | 22 | 242 | 106 | 343 | 60.165
10:30 | 4416.5 | 490 | 2047.5 | 0 | 1124 | 1845.5 | 12.5 | 22.5 | 223.5 | 115 | 364.5 | 30.0825
11:00 | 4359 | 490 | 2025 | 0 | 1312 | 1885 | 25 | 23 | 205 | 124 | 386 | 0
11:30 | 4379.5 | 490 | 2077 | 0 | 1401.5 | 1925 | 25 | 67.5 | 205 | 126 | 388 | 0
12:00 | 4400 | 490 | 2129 | 0 | 1491 | 1965 | 25 | 112 | 205 | 128 | 390 | 0
12:30 | 4337 | 490 | 2180 | 0 | 1560.5 | 1986 | 25 | 113.5 | 220.5 | 127 | 371 | 182.405
13:00 | 4274 | 490 | 2231 | 0 | 1630 | 2007 | 25 | 115 | 236 | 126 | 352 | 364.81
13:30 | 4274 | 490 | 2231 | 0 | 1630 | 2007 | 25 | 115 | 236 | 126 | 352 | 364.81
14:00 | 4274 | 490 | 2231 | 0 | 1630 | 2007 | 25 | 115 | 236 | 126 | 352 | 364.81
14:30 | 4117 | 490 | 2169 | 0 | 1793 | 1982.5 | 25 | 89 | 259.5 | 123 | 255.5 | 370.54
15:00 | 3960 | 490 | 2107 | 0 | 1956 | 1958 | 25 | 63 | 283 | 120 | 159 | 376.27
15:30 | 3890.5 | 490 | 2084.5 | 0 | 1725 | 1917.5 | 25 | 44 | 302.5 | 126 | 117.5 | 188.135
16:00 | 3821 | 490 | 2062 | 0 | 1494 | 1877 | 25 | 25 | 322 | 132 | 76 | 0
16:30 | 3703 | 490 | 1963.5 | 0 | 1364 | 1655 | 25 | 25 | 283.5 | 131 | 55.5 | 47.2725
17:00 | 3585 | 490 | 1865 | 0 | 1234 | 1433 | 25 | 25 | 245 | 130 | 35 | 94.545 | [10 empty] | 472
17:30 | 3334 | 370 | 1720.5 | 0 | 993.5 | 1294 | 25 | 12.5 | 227 | 119 | 22.5 | 47.2725 | [10 empty] | 100
18:00 | 3083 | 250 | 1576 | 0 | 753 | 1155 | 25 | 0 | 209 | 108 | 10 | 0 | [10 empty] | 20
18:30 | 3209.5 | 370 | 1640.5 | 0 | 770.5 | 1050 | 25 | 0 | 226 | 54 | 5 | 0 | [10 empty] | 592
19:00 | 3336 | 490 | 1705 | 0 | 788 | 945 | 25 | 0 | 243 | 0 | 0 | 0
19:30 | 3313 | 490 | 1699 | 0 | 929 | 957 | 25 | 0 | 214 | 24 | 0 | 0
20:00 | 3216 | 491 | 1775 | 0 | 1033 | 949 | 25 | 0 | 214 | 50 | 0 | 0
20:30 | 3133.5 | 490.5 | 1861 | 0 | 954 | 1019 | 25 | 0 | 205.5 | 48 | 0 | 0
21:00 | 3051 | 490 | 1947 | 0 | 875 | 1089 | 25 | 0 | 197 | 46 | 0 | 0
21:30 | 3224 | 492.5 | 2033.5 | 0 | 864.5 | 1137.5 | 25 | 0 | 180 | 55 | 0 | 0
22:00 | 3397 | 495 | 2120 | 0 | 854 | 1186 | 25 | 0 | 163 | 64 | 0 | 0
22:30 | 3490 | 495 | 2200 | 0 | 861 | 1224 | 12.5 | 0 | 163 | 69 | 0 | 0
23:00 | 3583 | 495 | 2280 | 0 | 868 | 1262 | 0 | 0 | 163 | 74 | 0 | 0
23:30 | 3665.5 | 495 | 2260.5 | 0 | 716.5 | 1408 | 0 | 0 | 163 | 78 | 0 | 0 |  | Max Temp. in Dhaka |  | 37.3° C
24:00 | 3748 | 495 | 2241 | 0 | 565 | 1554 | 0 | 0 | 163 | 82 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 241.077 MKWHr Energy Not Served 2.075 MKWHr Energy Requirement 243.152 MKWHr
Shortage
Note on W13: Author:

## Generation
g | 2023-04-27
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | [10 empty] | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 0 |  | 288660
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2800000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [10 empty] | 3 | 8 | 8 | 16 | 25 | 8 | 8 | [8 empty] | 0 | 89778
| Teknaf 20MW PP (Solartech) | [5 empty] | 1 | 5 | 10 | 15 | 18 | 19 | 18 | 18 | 17 | 11 | 7 | 3 | 0 | [8 empty] | 143100
6 | Sikalbaha 225MW CCPP (Gas) | 224 | 229 | 228 | 229 | 227 | 228 | 230 | 230 | 224 | 223 | 224 | 218 | 218 | 219 | 219 | 221 | 223 | 194 |  | 225 | 223 | 220 | 225 | 225 | 227 | 226 | 5187923
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 20 | 17 | 0 | [8 empty] | 32 | 51 | 51 | 34 |  |  | 0 | 867452
12 | Hathazari 100 MW peaking PP | [14 empty] | 6 | 42 | 42 | [9 empty] | 101520
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 51 | 51 | 51 | 51 | 51 | 51 | 17 | 17 | 17 | 27 | 50 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 945927
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | 46 | 47 | 43 | 46 | 46 | 46 | 46 | 47 | 46 | 46 | 42 | 42 | 41 | 40 | 34 | 37 | 40 | 46 |  | 48 | [5 empty] | 0 | 843524
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 40 | 40 | 40 | 39 | 40 | 40 | 41 | 41 | 40 | 97 | 40 | 60 | 95 | 40 |  |  | 38 | [6 empty] | 40 | 103 | 102 | 1038000
17 | Siddhirganj 335 MW CCPP | 145 | 145 | 145 | 140 | 140 | 130 | 130 | 130 | 132 | 130 | 130 | 130 | 130 | 127 | 97 | 95 | 50 | [5 empty] | 26 | 110 | 160 | 155 | 2660056
18 | Kodda 300 MW PP Unit-2 (Summit) | [10 empty] | 4 | 30 | 40 | 110 | 145 | 45 | 15 | [8 empty] | 0 | 444109
19 | Ashuganj 195MW PP (APSCL-United) | 197 | 197 | 158 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 125 | 125 | 125 | 125 | 75 | 0 |  | 8 | 8 | 8 | 8 | 45 | 45 | 45 | 2325090
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4 | 150 | 150 | 150 | 150 | 149 | 148 | 150 | 150 | 150 | 149 | 150 | 150 | 150 | 200 | 200 | 200 | 120 | [8 empty] | 0 | 2770281
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4284000
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 42 | 42 | 42 | 42 | 43 | 43 | 43 | 42 | 40 | 34 | 33 | 34 | 35 | 35 | 37 | 36 | 37 | 37 |  | 33 | 38 | 40 | 40 | 42 | 45 | 45 | 931968
33 | Ashuganj 225 MW CCPP | 211 | 211 | 211 | 212 | 211 | 200 | 182 | 183 | 195 | 204 | 206 | 204 | 203 | 203 | 204 | 205 | 207 | 179 |  | 180 | 180 | 189 | 181 | 206 | 196 | 215 | 4855000
34 | Ashuganj 450 MW CCPP(South) | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 305 | 320 | 330 | 305 | 305 | 305 | 305 | 270 | 270 | 270 | 230 |  | 287 | 270 | 275 | 270 | 315 | 305 | 270 | 7168000
| Ashuganj 450 MW CCPP(North) | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 290 | 310 | 320 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 280 |  | 280 | 280 | 285 | 300 | 350 | 340 | 310 | 7577600
Ashuganj 420 MW CCPP(East)
35 | Ashuganj 55 MW PP (Precision)
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 360 | 359 | 359 | 359 | 360 | 359 | 359 | 361 | 388 | 395 | 395 | 405 | 399 | 397 | 404 | 398 | 328 | 272 |  | 292 | 398 | 379 | 381 | 400 | 402 | 397 | 9035770
40 | Meghnaghat 450 MW CCPP(MPL) | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 350 | 350 | 320 | 300 |  | 350 | 300 | 330 | 330 | 370 | 450 | 450 | 9609250
41 | Haripur 360MW CCPP(HPL) | 335 | 335 | 333 | 334 | 333 | 292 | 295 | 295 | 292 | 294 | 293 | 324 | 324 | 277 | 274 | 272 | 233 | 233 |  | 303 | 303 | 303 | 354 | 344 | 344 | 343 | 7416000
42 | RPCL 210MW CCPP | 192 | 192 | 191 | 193 | 192 | 193 | 190 | 173 | 158 | 152 | 150 | 150 | 135 | 120 | 118 | 120 | 120 | 119 |  | 118 | 118 | 119 | 125 | 128 | 141 | 147 | 3565440
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 2 | 10 | 21 | 33 | 41 | 44 | 41 | 34 | 40 | 14 | 5 | 2 | 0 | [8 empty] | 289170
44 | Fenchugonj CCPP Phase-1 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 31 | 32 | 31 | 32 | 32 | 32 | 32 | 32 | 32 | 32 |  | 32 | 32 | 32 | 32 | 32 | 31 | 31 | 754000
45 | Fenchugonj CCPP Phase-2 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 28 | 28 | 28 | 30 | 30 | 30 | 30 | 619560
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 61 | 61 | 61 | 61 | 63 | 40 | 40 | 40 | 40 | 55 | 59 | 58 | 54 | 55 | 57 | 58 | 59 | 40 |  | 40 | 51 | 61 | 61 | 61 | 61 | 61 | 1317408
48 | Shahjibazar 86MW PP (Shahjibazar) | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 79 | 78 | 78 | 77 | 77 | 77 | 10 |  | 30 | 5 | 30 | 80 | 80 | 80 | 80 | 1725120
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 201 | 201 | 201 | 201 | 201 | 201 | 201 | 204 | 206 | 206 | 206 | 202 |  |  |  |  | 80 | 80 |  | 135 | [5 empty] | 0 | 2652380
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 17 | 17 | 0 |  | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 18 | 17 | 18 | 17 | 366000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 |  | 10 | 10 | 10 | 10 | 226620
54 | Hobiganj 11MW PP Cofidence-E | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  |  |  |  | 5 | 8 | 8 | 8 | 173368
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 53 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 31 | 48 | 50 | 50 | 52 | 53 | 53 | 5 |  | 5 | 5 | 20 | 22 | 22 | 51 | 51 | 733200
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 8 | 16 | 16 | 16 | 16 | 367488
57 | Bibiana-II 341 MW CCPP (Summit) | 285 | 265 | 270 | 265 | 275 | 260 | 280 | 295 | 300 | 290 | 290 | 290 | 285 | 280 | 280 | 285 | 275 | 250 |  | 280 | 290 | 280 | 270 | 300 | 315 | 290 | 6907000
| Bibiyana South 400 MW | 400 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 391 | 386 | 393 | 385 | 382 | 385 | 386 | 390 | 280 | 320 |  | 395 | 370 | 274 |  |  |  |  | 7389000
58 | Nababganj 55 MW PP (Southern power ) | 17 | 17 | 17 | 17 | 17 | 17 |  |  |  |  | 10 | 17 | 17 | 17 | 17 | 17 | 17 | [8 empty] | 0 | 224653
59 | Tangail Palli Power Gen 22 MW | 10 | 11 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 10 | 6 | 6 | 11 |  |  |  | 1 | 12 | 11 | 12 | 12 | 12 | 12 | 253920
60 | Barabkunda 22 MW PP (Regent) | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 |  | 13 | 13 |  |  | 11 | 0 | 12 | 266112
61 | Narshingdi 22 MW PP (Doreen) | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 16 | 16 | 16 | [9 empty] | 0 | 201960
62 | Tangail 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 15 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 15 | [8 empty] | 0 | 255132
63 | Impoprt (Tripura) | 142 | 136 | 132 | 130 | 126 | 116 | 98 | 104 | 106 | 106 | 124 | 128 | 126 | 116 | 120 | 132 | 130 | 108 |  | 0 | 24 | 50 | 46 | 64 | 74 | 82 | 2547840
64 | Malancha, Ctg. EPZ (United) | 40 | 40 | 40 | 40 | 39 | 40 | 40 | 40 | 25 | 25 | 23 | 23 | 24 | 24 | 24 | 25 | 29 | 26 |  | 26 | 27 | 26 | 30 | 39 | 30 | 38 | 763200
65 | Feni 22MW PP (Doreen) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | [7 empty] | 8 | 15 | 15 |  | 15 | [5 empty] | 18 | 197244
66 | Feni 11 MW PP (Doreen) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | [5 empty] | 0 | 151560
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 25 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 32 | 32 | 31 | [5 empty] | 33 | 33 | 33 | 683300
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15 | 20 | 15 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 364510
69 | Summit Ashulia | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 |  | 0 | 23 | 23 | 23 | 23 | 23 | 23 | 552000
70 | Summit Madhabdi | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 14 | 14 | 14 | 14 | 0 | 0 |  | 0 | 0 | 3 | 15 | 15 | 19 | 19 | 338580
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 0 | 20 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 0 |  |  |  |  | 0 | 10 | 25 | 25 | 469700
72 | Rupganj 33 MW PP(Summit) | [12 empty] | 14 | 28 | 28 | 28 | 30 | 5 |  | 0 | 16 | 16 | 33 | 33 | 33 | 33 | 270300
73 | Ghorashal 108MW PP (Regent) | 77 | 77 | 77 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 28 | 75 | 75 | 75 | 75 | 22 |  |  | 12 | 12 | 12 | 52 | 75 | 76 | 76 | 1095636
| Feni Lanka Power | 106 | 106 | 106 | 106 | 106 | 106 | 70 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 20 | 17 | 17 | 17 |  | 17 | [5 empty] | 0 | 976980
| Chowmuhani 113 MW | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 36 | 37 | 37 | 37 | 37 | 37 | 16 |  | 42 | 8 | 8 | 8 | 9 | 8 | 8 | 442680
| Manikgonj 162MW PP(MPGL) | 72 | 72 | 35 | 31 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 54 | 17 | [8 empty] | 0 | 496800
77 | Siddhirganj 100 PP(Dutch Bangla) | 40 | 24 | 8 | 8 | 8 | 8 | 24 | 85 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 72 | 13 | [8 empty] | 0 | 927360
78 | Gazipur 52 MW PP | 50 | 50 | 50 | 41 | 41 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 20 | 34 | 34 | 36 | [8 empty] | 0 | 451200
79 | Kodda 150 MW PP | 82 | 32 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 0 |  | 32 | 80 | 80 | 80 | [9 empty] | 0 | 491040
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 52 | 52 | 52 | [23 empty] | 161155
| Gazipur 100 MW PP | 105 | 105 | 105 | 105 | 105 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 45 | 70 | 70 | 70 | 80 | [6 empty] | 2 | 17 | 25 | 1284979
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 2 | 3 | 4 | 5 | 5 | 4 | 4 | 3 | 2 | 1 | [9 empty] | 33242
| Jodiac Power | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | [8 empty] | 0 | 332057
| Karnaphuli Power Ltd. | 52 | 52 | 52 | 52 | 54 | 54 | 17 | 17 | 17 | 26 | 48 | 52 | 54 | 54 | 54 | 54 | 54 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 936726
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP ( Summit) | 260 | 263 | 270 | 260 | 297 | 270 | 290 | 299 | 300 | 300 | 288 | 300 | 305 | 290 | 290 | 270 | 245 | 270 |  | 240 | 275 | 285 | 305 | 315 | 310 | 297 | 6857513
87 | Meghnaghat 100 MW(IEL) | 9 | 9 | 8 | 9 | 8 | 9 | 9 | 8 | 9 | 16 | 18 | 42 | 66 | 60 | 66 | 66 | 66 | [8 empty] | 0 | 502080
| Meghnaghat 104 MW PP (OPCL) | 72 | 55 | 35 | 35 | 35 | 35 | 17 | 17 | 17 | 32 | 60 | 72 | 71 | 71 | 71 | 72 | 71 | 71 |  |  | 0 |  |  |  |  | 0 | 904320
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 56 | 56 | 56 | 56 | 56 | 10 | 10 | 10 | 10 | 22 | 44 | 44 | 44 | 44 | 43 | 43 | 43 | [8 empty] | 0 | 692400
92 | Fenchuganj 44MW (Energyprima) | 46 | 46 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 30 | 36 | 40 | 39 | 42 | 40 | 43 | 20 |  | 5 | 5 | 20 | 20 | 30 | 48 | 45 | 702280
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 25 | 51 | 10 | 10 | 0 |  | 10 | 10 | 10 | 10 | 27 | 51 | 51 | 693286
94 | Gagnagar 102 MW PP (Digital Power) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 16 | 24 | 33 | 50 | 50 | 16 | 8 | [8 empty] | 0 | 272880
95 | Patenga 50MW PP (Baraka) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 17 |  | 36 | 36 | 38 |  | 6 | 6 | 6 | 223680
96 | Chattogram 108 MW PP (ECPV) | [15 empty] | 12 | 24 | 16 | [7 empty] | 0 | 53760
97 | katpotti 52 MW
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [10 empty] | 2 | 15 | 15 | 15 | 15 | 15 | 15 | [8 empty] | 0 | 105728
100 | Manikganj 55 MW PP (Northern) | [8 empty] | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 17 | [8 empty] | 0 | 278038
101 | Kushiara 163 MW CCPP (KP)
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 1 | 1 | 2 | 2 | 2 | 2 | 1 | 0 | 0 | 0 | [9 empty] | 10400
103 | Kamalaghat 54 MW PP(Banco Energy) | [12 empty] | 17 | 17 | 17 | 17 | 17 | [5 empty] | 17 | 17 | 17 | 17 | 160560
104 | Keranigonj 300 MW PP (APR) | [25 empty] | 0
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 47 | 47 | 47 | 47 | 48 | 48 | 46 | 48 | 48 | 48 | 123 | 153 | 153 | 153 | 153 | 116 | 116 | 125 |  | 127 | 163 | 163 | 140 | 140 | 140 | 48 | 2385600
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | [16 empty] | 0 | 173950
115 | Juldah 100 MW PP Unit-3 (Acorn) | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 50 | 49 | 49 | 49 | 38 | 38 | 40 |  | 74 | 74 | 74 | 74 | 74 | 74 | 38 | 1140480
116 | Chandpur 200MW (Desh energy) | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 38 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 37 | 17 | 17 | 17 | 17 | 17 | 17 | 908640
117 | Ashuganj 150MW PP (Midland) | [10 empty] | 6 | 16 | 20 | 20 | 20 | 10 | 5 | 5 |  | 5 | 6 | 5 | 5 | 5 | 5 | 5 | 217454
118 | Bibiyana-III 400 MW CCPP | 409 | 409 | 409 | 340 | 345 | 346 | 347 | 346 | 383 | 380 | 369 | 368 | 397 | 369 | 318 | 319 | 319 | 319 |  | 375 | 377 | 377 | 400 | 402 | 402 | 413 | 8846000
| Jamalpur 115 MW PP (United) | 48 | 48 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 97 | 98 | 88 | 88 | 88 | 49 | 49 | 49 |  | 54 | 115 | 115 | 108 | 108 | 108 | 48 | 1645200
| Anwara 300 MW PP (United) | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 122 | 103 | 123 | 123 | 124 | 124 | 124 | 124 |  | 170 | 170 | 170 | 170 | 140 | 140 | 88 | 2719855
| Juldah unit-2 (Acorn) | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 756480
| Anlima Energy Ltd. | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 |  | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 840545
| Bhairob 54.5 MW | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 32 |  | 8 | [8 empty] | 2 | 480600
| Spectra Solar Plant Ltd. | [5 empty] | 1 | 7 | 14 | 22 | 27 | 31 | 31 | 31 | 24 | 4 | 0 |  | 0 | [8 empty] | 189429
| Chandpur 115(Doreen) | 75 | 56 | 49 | 36 | 35 | 36 | 35 | 36 | 36 | 35 | 52 | 72 | 90 | 93 | 93 | 93 | 93 | 92 |  | 40 | 17 | 17 | 17 | 17 | 17 | 17 | 1291200
| Kanchan Purbachal Power Generation Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  |  | 3 | 17 | 17 | 17 | 17 | 17 | 17 | 407160
| Mirsharai 150 MW (Oil) | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 |  | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 3910836
Mirsharai 150 MW (Gas)
120 | Eastern Zone Total | 7233 | 7074 | 6821 | 6555 | 6588 | 6301 | 6184 | 6234 | 6319 | 6476 | 6691 | 6953 | 7007 | 7079 | 6887 | 6625 | 5995 | 4766 | 0 | 5019 | 4978 | 4974 | 4905 | 5360 | 5623 | 5369 | 151008982
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | 67 | 66 | 32 | 32 | 32 | 16 | 16 | 16 | 16 | 16 | 19 | 24 | 20 | 57 | 65 | 16 | [9 empty] | 0 | 553920
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL) | [9 empty] | 22 | 23 | 97 | 100 | 80 | 63 | 25 | 25 | [9 empty] | 327102
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | [25 empty] | 0 | 6240
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 3 | 21 | 43 | 66 | 81 | 91 | 94 | 91 | 81 | 65 | 22 | 2 | [8 empty] | 0 | 662400
131 | Rampal 1320 MW (BIFPCL)
132 | United Payra Power Ltd. | 72 | 35 | [12 empty] | 24 | 17 | [9 empty] | 0 | 189600
133 | Bhola Nutan Biddut BD LTD (GAS)
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 64 | 32 | 32 | 16 | 16 | 0 |  |  |  |  | 4 | 32 | 32 | 32 | 32 | 32 | 32 | 16 |  | 16 | [5 empty] | 0 | 424512
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 40 | 40 | 40 | 59 | 59 | 60 | 60 | 60 | 60 | 60 |  | 60 | 62 | 62 | 62 | 62 | 40 | 70 | 1366000
140 | Bhola 33 MW PP (Venture) | 32 | 32 | 29 | 28 | 27 | 24 | 22 | 24 | 23 | 25 | 26 | 27 | 30 | 31 | 31 | 31 | 30 | 26 |  | 1 | 3 | 6 | 6 | 14 | 18 | 21 | 561609
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali) | [13 empty] | 24 | 16 | [10 empty] | 0 | 34500
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | [10 empty] | 15 | 15 | 50 | 105 | 67 | 21 | [9 empty] | 0 | 272880
146 | Bheramara HVDC | 863 | 864 | 863 | 911 | 484 | 482 | 482 | 462 | 490 | 490 | 490 | 490 | 490 | 490 | 490 | 490 | 490 | 250 |  | 490 | 490 | 491 | 490 | 495 | 495 | 495 | 13508363
147 | Bheramara 410 MW CCPP | 410 | 410 | 410 | 410 | 410 | 340 | 340 | 340 | 340 | 340 | 380 | 400 | 400 | 350 | 300 | 250 | 220 | 200 |  | 200 | 200 | 200 | 200 | 200 | 280 | 400 | 8214336
148 | Payra 1320 MW | 1244 | 1182 | 1162 | 1100 | 1100 | 1090 | 1110 | 1080 | 1080 | 1080 | 1100 | 1120 | 1160 | 1162 | 1110 | 1030 | 600 | 500 |  | 250 | 260 | 250 | 400 | 500 | 520 | 750 | 23955700
149
150 | Barapukuria TPP Unit-1 | 75 | 74 | 74 | 75 | 74 | 73 | 74 | 75 | 75 | 75 | 76 | 75 | 75 | 72 | 74 | 75 | 74 | 70 |  | 75 | 75 | 74 | 74 | 75 | 75 | 75 | 1806545
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 245 | 170 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 5878800
153 | Baghabari 71 MW GTPP | 70 | 70 | 70 | 70 | 70 | 50 | 50 | 50 | 65 | 65 | 65 | 60 | 60 | 60 | 60 | 50 | 50 | [9 empty] | 1045000
156 | Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 0 | 1 | 3 | 3 | 4 | 4 | 4 | 2 | 0 | 0 | 0 | 0 | [8 empty] | 25920
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 175 | 175 | 175 | 174 | 177 | 175 | 175 | 176 | 188 | 194 | 180 | 178 | 188 | 183 | 171 | 130 | 130 | 130 |  | 144 | 144 | 149 | 151 | 161 | 170 | 180 | 4283100
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 186 | 186 | 186 | 186 | 164 | 157 | 157 | 158 | 170 | 197 | 185 | 184 | 190 | 189 | 174 | 130 | 130 | 130 |  | 146 | 157 | 159 | 157 | 167 | 175 | 170 | 4316764
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 362 | 360 | 361 | 359 | 419 | 296 | 343 | 347 | 371 | 416 | 346 | 380 | 409 | 370 | 409 | 422 | 426 | 426 |  | 425 | 425 | 424 | 428 | 427 | 430 | 422 | 9481854
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 19 | 18 | 16 | 16 | 15 | 17 | 17 | 17 |  |  | 0 | 21 | 21 | 22 | 22 | 22 | 22 | 436560
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | [10 empty] | 8 | 133902
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | [25 empty] | 0 | 0
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka) | [14 empty] | 8 | [10 empty] | 0 | 12485
170 | Chapainawabganj 100 MW Peaking PP
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 50 | 35 | 40 | 50 | 50 |  |  |  |  | 4 | 26 | 57 | 70 | 70 | 70 | 35 | 1063968
172 | Confidence Power Bogura Unit-1 113 MW | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 55 | 55 | 35 | 35 | 55 | 35 | [5 empty] | 35 | 35 |  |  |  | 0 | 694944
173 | Rangpur 20 MW GTPP | [10 empty] | 0 | 15 | 15 | 15 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19000
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 107 | 55 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 32 | 49 | 34 | 34 |  |  |  | 65 | 100 | 111 | 70 | 70 | 70 | 66 | 1165814
177 | Sympa Solar Power 8MW | [6 empty] | 1 | 2 | 5 | 7 | 7 | 7 | 6 | 6 | 6 | 3 | 2 | 1 | [8 empty] | 47292
178 | Energypac Power Venture Thakurgaon Ltd. | 114 | 90 | 35 | 35 | 35 | 35 |  |  |  |  | 35 | 35 | 35 | 50 | 35 | 35 |  |  |  | 17 | 53 | 115 | 70 | 70 | 70 | 36 | 1101888
| Intraco Solar 30 MW | [5 empty] | 1 | 6 | 14 | 22 | 28 | 32 | 33 | 12 | 14 | 22 | 14 | 5 | 1 | [8 empty] | 194098
| Adani Power Jharkhanda Ltd | [5 empty] | 9 | 85 | 144 | 278 | 391 | 449 | 510 | 512 | 513 | 514 | 512 | 514 | 415 |  | 420 | 422 | 425 | 415 | 411 | 467 | 529 | 7281818
178 | Teesta Solar Limited | [5 empty] | 6 | 34 | 65 | 104 | 132 | 151 | 155 | 150 | 89 | 34 | 23 | 20 | 8 | [8 empty] | 1001270