## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2023-04-29 | Saturday
|  | Date (day): | 2023-04-29 |  | Saturday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 12727.6 | MW |  |  | (b) At Evening Peak Hour : |  | 15228 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2023-04-28 | 2023-04-29 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 220 | 150 | 150 | 30 |  | Gas shortage
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 75 | 78 | 16 | 76 |  | 32 | Engine problem
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 403 | 393 | 400 | 400 | 12 |  | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 328 | 334 | 300 | 330 | 30 |  | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 0 | 8 | 16 | 50 | 50 |  | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 285 | 275 | 300 | 300 |  |  | FGMO
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 0 | 0 | 90 | 90 |  | 12 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 0 | 15 | 15 | 15 | 40 |  | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 10 | 10 | 10 | 18 |  | 4 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 99 | 100 | 90 | 100 |  | 110 | GT-1 Under maint
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 0 | 0 | 90 | 90 |  | 10 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 220 | 220 | 220 |  | 115 | ST under S/D
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 8 | 48 | 92 |  | 10 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 54 | 35 | 54 |  |  | Fuel shortage
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 150 | 149 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 17 | 17 | 55 |  |  | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 17 | 35 | 35
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 36 | 43 | 43 | 43 |  | 37 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25 |  | 8 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 32 | 30 | 32 | 32
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 0 | 41 | 41 | 41
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 0 | 300 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 300 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 0 | 0 | 50 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 80 |  | 20 | Engine problem
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 15 | 70 | 17 | 70 | 79 |  | Fuel shortage
36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 105 | 105 | 105
37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 0 | 17 | 54 | 70 |  | 34 | Engine problem
38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 5 | 126 | 126 | 162
39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 33 | 0 | 30 | 0
40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 8 | 34 | 17 | 35 | 20 |  | Fuel shortage
| Dhaka area Total |  |  |  |  | 6263 | 5847 | 1984 | 3020 | 3751 | 4217 | 312 | 1257
41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 120 | 120 | 120 | 120 | 60 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
43 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 19 | 0 | 20 | 0
44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 1 | 25 | 26 | 35 | 15 |  | Fuel shortage
45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 25 | 25 | 25 | 25 | 205 |  | Low Water Level
46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 224 | 226 | 225 | 225
47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 17 | 17 | 17
49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 45 | 60 |  | 38 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 34 | 66 | 84 |  | 18 | Engine problem
51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 0 | 78 | 50 | 70 |  | 30 | Engine problem
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 38 | 76 | 38 | 76 |  | 24 | Engine problem
53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 12 | 12 | 13 | 13 | 9 |  | Gas shortage
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 33 | 38 | 15 | 35
54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 12 | 0 | 50 | 58 |  | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 80 | 200 | 120 | 300
57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 17 | 17 | 54
58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 9 | 51 | 17 | 51 | 59 |  | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 76 | 63 | 90 |  | 10 | Engine problem
60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 34 | 34 | 34 | 34 | 82 |  | Fuel shortage
| Mirsharai 150 MW |  | Gas/HSD | BPDB-RPCL | 18.5*9 | 0 | 0 | 163 | 163 | 162 | 162
| Chattogram area Total |  |  |  |  | 2442 | 2382 | 774 | 1204 | 1103 | 1526 | 668 | 270
61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 210 | 211 | 210 | 210 |  |  | FGMO
63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 310 | 310 | 310 | 310 |  |  | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 310 | 300 | 310 | 310 |  |  | FGMO
65 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 0 | 0 | 0 | 0
66 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 40 | 41 | 40 | 40
67 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 55 | 0 | 0 | 0 | 0 |  |  | Contract Expired
68 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 157 | 118 | 118 | 118
69 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
70 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 52 | 80 | 150
71 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 31 | 46
72 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under Maint.
73 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 150 | 17 | 150 | 50 |  | Fuel shortage
74 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 18 | 18 | 18 |  | 4 | Engine problem
75 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 5 | 8 | 8 |  | 3 | Engine problem
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 88 | 144 | 143 | 165
76 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 25 | 25 | 33
77 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 43 | 43 | 43
78 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 19 | 20 | 20 | 20 |  | 5 | Engine problem
79 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 0 |  |  | Contract Expired
80 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 17 | 106 |  | 8
81 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 7 | 113 | 9 | 113
82 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 16 | 17 | 35 | 35 |  | 19 | Engine problem
83 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 31 | 93 | 94 | 94 | 21 |  | Fuel shortage
| Cumilla Area Total |  |  |  |  | 3159 | 3151 | 1295 | 1711 | 1579 | 2020 | 71 | 202
84 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 157 | 160 | 162 | 162
85 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 16 | 19 | 3 |  | Gas shortage
86 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0
87 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
88 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 144 | 173 | 160 | 170 |  | 30 | Engine prolem
89 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 75 | 88 | 75 | 115
90 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 40 | 0 | 50 | 0
91 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 12 | 12 | 12 | 10 |  | Fuel shortage
| Mymensingh Area Total |  |  |  |  | 717 | 614 | 443 | 452 | 476.6 | 478 | 3 | 30
92 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 0 | 0 | 0 | 0 |  | 70 | Machine problem.
93 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 29 | 29 | 29 | 29 |  | 61 | Machine problem
94 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under maint
95 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
96 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 53 | 53 | 51 | 51
97 | Fenchuganj 44MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 43 | 47 | 44 | 45
98 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 8 | 8 |  | 3 | Engine problem
99 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 60 | 62 | 61 | 61
100 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 80 | 80 | 85 | 85
101 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
102 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 130 | 133 | 133 | 133 |  | 98 | ST Under S/D
103 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 16 | 18 | 18 | 18
104 | Sylhet 50MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
105 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 16 | 16 | 16 | 9 |  | Gas shortage
106 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 280 | 285 | 300 | 310 |  |  | FGMO
107 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 369 | 415 | 400 | 400 |  |  | FGMO
108 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
109 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 120 | 400 | 400 | 400
| Sylhet Area Total |  |  |  |  | 2472 | 2427 | 1214 | 1556 | 1555 | 1566 | 9 | 825
110 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 497 | 493 | 508 | 942
111 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 0 | 33 | 85 | 98 |  | 17 | Engine problem
112 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 22 | 35 |  | 19 | Engine problem
113 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
114 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 55 | 74 |  | 35 | Engine problem
115 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 350 | 340 | 350 | 350
116 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 0 | 0 | 40
117 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Fuel shortage
118 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 17 | 17 | 17 | 88 |  | Fuel shortage
119 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 100
120 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 95 | 0 | 100 | 0
| Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 0 | 0 | 152 | 0 | 0 | 0 |  |  | On test.
| Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 660*2 | 617 | 617 | 0 | 0 | 0 | 0 |  |  | Coal Shortage.
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3005 | 3001 | 1094 | 883 | 1137 | 1656 | 434 | 71
121 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 16 | 64
122 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 23 | 28 | 25 | 31 |  | 9 | Engine problem
123 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 70 | 70 | 70 | 70 |  | 124 | machine problem
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
124 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 890 | 1112 | 900 | 1244
125 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 0 | 0 | 0 | 0 |  | 220 | Under maintenance
126 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 17 | 150
127 | Barisal 307 MW |  | Coal | BCPCL | 307*1 | 307 | 307 | 0 | 0 | 0 | 0 | 307 |  | Coal Shortage.
| Barisal Area Total |  |  |  |  | 2265 | 2265 | 983 | 1210 | 1028 | 1559 | 307 | 353
128 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 70 | 70 | 70
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
129 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 26 | 26 |  | 26 | Engine problem
130 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 34 |  | 37 | Engine problem
131 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 14
132 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 8 | 34 | 42 |  | 8 | Engine problem
133 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 24 | 42 |  | 8 | Engine problem
134 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 174 | 174 | 190 | 190 |  |  | FGMO
135 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
136 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 184 | 180 | 160 | 200 |  |  | FGMO
137 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 373 | 376 | 380 | 380 |  |  | FGMO
138 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 35 | 35 |  | 15 | Engine problem
139 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 18 | 21 | 22 | 22
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
140 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 8 | 8 | 8 |  | 3 | Engine problem
141 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 34 | 0 | 34 | 18 |  | Fuel shortage
142 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 47 | 80 | 80 |  | 24 | Enginr problem
143 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel shortage
144 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 12 | 113 | 95 | 113
145 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 113 | 95 | 113
146 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 4 | 0 | 6 | 0
| Adani Power Jharkhanda Ltd |  | Coal | Import | 0 | 0 | 0 | 508 | 522 | 500 | 500 |  |  | On test.
| Rajshahi Area Total |  |  |  |  | 2179 | 2129 | 1278 | 1666 | 1725 | 1903 | 538 | 121
147 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 75 | 76 | 75 | 75 | 10 |  | Coal Shortage.
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
148 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 250 | 0 | 0 | 0 |  | 250 | Under maint
149 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
150 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
151 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 113 | 95 | 113
152 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 6 | 0 | 8 | 0
153 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 35 | 115 | 35 | 115
154 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 28 | 0 | 30 | 0
| Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 0 | 0 | 80 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 830 | 750 | 474 | 304 | 373 | 303 | 50 | 335
| Total |  |  |  |  | 23332 | 22566 | 9539 | 12006 | 12727.6 | 15228 | 2392 | 3464
A. |  | 2023-04-28 | (Yesterday) |  |  |  |  | Friday
1 | Highest Generation : |  |  | 12006 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 7561 | MW at | 6:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 12100 | MW
3 | Day peak Generation : |  |  | 9539 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 11554.89 | MW
4 | Evening peak Generation : |  |  | 12006 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 90 | MW
5 | Total Energy Generation : |  | 233.5115 | MKWHr | By Solar | 2.6635 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Gas : | 145.0018 | MKWHr |  | By Oil: | 29.7352 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 41.518 | MKWHr |  | By Hydro: | 0.3 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2392 | MW | Dhaka | 3593.65 | 3593.65 |  | 0 |  | 18:00 |  | 66.85
|  |  | For Plants S/D or M/C prob = |  |  | 3464 | MW | Chittagong | 1251.2 | 1251.2 |  | 0 |  | 19:00 |  | 146.115
|  |  | Total = |  |  | 5856 | MW | Khulna | 1316.8 | 1316.8 |  | 0 |  | 19:30 |  | 169.035
7 | Total Gas Supplied : |  |  | 1164.67 | MMCFD |  |  | Rajshahi | 1393 | 1393 |  | 0 |  | 20:00 |  | 143.25
8 | Fuel Cost : | i) Gas : | Taka | 169701787.724 | ii) Oil : | Taka | 317655397.09 | Comilla | 1232 | 1207 |  | 25 |  | 21:00 |  | 93
|  | iii) Coal : | Taka | 242345113.13 | Total | Taka | 729702297.944 | Mymensingh | 1159 | 1094 |  | 65 |  | 22:00 |  | 50
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0.1485 | MKWHr. | Sylhet | 503 | 503 |  | 0 |  | 23:00 |  | 92
| ii) During Peak Demand : |  |  | -150 | MW (E to W) at | 21:00 | hrs | Barisal | 266.24 | 266.24 |  | 0 |  | 24:00 |  | 298
| iii) Maximum : |  |  | -150 | MW at | 20:00 | hrs | Rangpur | 840 | 840 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 34.8° C |  |  | Total | 11554.89 | 11464.89 |  | 90
B. |  | 2023-04-29 | (Today) |  |  |  | Saturday |  |  | Probable max. temperature in Dhaka |  |  | 35.3° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 12500 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 15228 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 11000 | MW
4 | Reserve(Generation end) |  |  |  | 2728 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 243.1196 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 9111 | MW at | 6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 11.9564 | MKWHr. | ii) HVDC Flow at Peak Time |  | 493 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.3366 | MKWHr. | iii) Maximum HVDC Flow : |  | 497 | MW at | 12:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 75.19 |  | (b) Today: | 75.16 |  | (c) Rule Curve: |  | 80.4
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2023-04-28 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 0 | 76 | 0 | 395 | 343 |  | 0 | 450 | 321 | 0 | 0 | 0 | 150 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 16 | 25 | 33 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 228 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 6 | 12 | 39 | 0 | 0 | 0 | 315 | 270 | 212 | 45 | 0 | 45 | 0 | 0 | 51 | 0 | 0 | 0 | 18 | 0 | 33 | 15 | 84 | 162 | 0 | 0 | 0 | 31 | 29 | 51 | 49 | 0 | 0 | 62 | 81 | 0 | 80 | 18 | 0 | 10 | 280 | 16 | 8 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 38 | 17 | 0 | 414 | 48 | 52 | 17 | 0 | 88 | 0 | 17 | 0 | 8 | 12 | 0 | 0 | 0 | 0 | 34 | 0 | 17 | 0 | 17 | 17 | 0 | 163 | 0 |  | 495 | 0 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 77 | 0 | 200 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 700 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 520 | 0 | 0 |  | 5435 | 3263 | 8698 | 3752 | 495 | 2265 | 0 | 442 | 1497 | 0 | 0 | 163 | 84 | 0 | 0 | 75.19
2:00 | 0 | 0 | 0 | 180 | 0 | 76 | 0 | 395 | 343 |  | 0 | 450 | 319 | 0 | 0 | 0 | 150 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 16 | 25 | 33 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 228 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 6 | 12 | 40 | 0 | 0 | 0 | 330 | 280 | 212 | 45 | 0 | 45 | 0 | 0 | 51 | 0 | 0 | 0 | 18 | 0 | 33 | 15 | 80 | 164 | 0 | 19 | 0 | 31 | 29 | 51 | 49 | 0 | 0 | 62 | 81 | 0 | 100 | 18 | 0 | 10 | 290 | 16 | 8 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 38 | 17 | 0 | 414 | 48 | 0 | 17 | 0 | 88 | 0 | 17 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 34 | 0 | 17 | 0 | 17 | 0 | 0 | 163 | 0 |  | 496 | 0 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 76 | 0 | 200 | 0 | 0 | 177 | 0 | 0 | 0 | 0 | 0 | 164 | 0 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 507 | 0 | 0 |  | 5423 | 3112 | 8535 | 3822 | 496 | 2232 | 0 | 359 | 1383 | 0 | 0 | 163 | 80 | 0 | 0 | 75.19
3:00 | 0 | 0 | 0 | 180 | 0 | 76 | 0 | 396 | 345 |  | 0 | 450 | 280 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 16 | 25 | 33 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 227 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 6 | 12 | 40 | 0 | 0 | 0 | 310 | 295 | 215 | 63 | 0 | 45 | 0 | 0 | 51 | 0 | 0 | 0 | 18 | 0 | 33 | 15 | 84 | 166 | 0 | 19 | 0 | 31 | 29 | 51 | 49 | 0 | 0 | 62 | 81 | 0 | 120 | 18 | 0 | 10 | 290 | 16 | 8 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 38 | 17 | 0 | 400 | 48 | 0 | 17 | 0 | 88 | 0 | 17 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 34 | 0 | 17 | 0 | 17 | 0 | 0 | 163 | 0 |  | 495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 75 | 0 | 200 | 0 | 0 | 179 | 0 | 0 | 0 | 0 | 0 | 169 | 0 | 403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 740 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 513 | 0 | 0 |  | 5294 | 2894 | 8188 | 3325 | 495 | 2234 | 0 | 359 | 1528 | 0 | 0 | 163 | 84 | 0 | 0 | 75.19
4:00 | 0 | 0 | 0 | 180 | 0 | 76 | 0 | 390 | 343 |  | 0 | 450 | 284 | 0 | 0 | 0 | 80 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 16 | 25 | 33 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 227 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 6 | 12 | 40 | 0 | 0 | 0 | 310 | 305 | 216 | 63 | 0 | 45 | 0 | 0 | 51 | 0 | 0 | 0 | 18 | 0 | 33 | 15 | 80 | 166 | 0 | 19 | 0 | 31 | 29 | 51 | 49 | 0 | 0 | 62 | 81 | 0 | 120 | 18 | 0 | 10 | 275 | 16 | 8 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 38 | 17 | 0 | 401 | 49 | 0 | 17 | 0 | 88 | 0 | 17 | 0 | 0 | 12 | 45 | 0 | 0 | 0 | 34 | 0 | 17 | 0 | 17 | 0 | 0 | 163 | 0 |  | 496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 75 | 0 | 200 | 0 | 0 | 173 | 0 | 0 | 0 | 0 | 0 | 158 | 0 | 303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 750 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 511 | 0 | 0 |  | 5379 | 2781 | 8160 | 3409 | 496 | 2116 | 0 | 360 | 1536 | 0 | 0 | 163 | 80 | 0 | 0 | 75.19
5:00 | 0 | 0 | 0 | 180 | 0 | 76 | 0 | 348 | 344 |  | 0 | 450 | 287 | 0 | 0 | 0 | 80 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 14 | 25 | 33 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 229 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 2 | 12 | 40 | 0 | 0 | 0 | 310 | 305 | 216 | 63 | 0 | 45 | 0 | 0 | 51 | 0 | 0 | 0 | 18 | 0 | 33 | 15 | 74 | 166 | 0 | 19 | 0 | 31 | 30 | 51 | 49 | 0 | 0 | 62 | 81 | 0 | 120 | 18 | 0 | 10 | 290 | 16 | 8 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 20 | 0 | 0 | 402 | 24 | 0 | 0 | 0 | 30 | 0 | 17 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 34 | 0 | 17 | 0 | 0 | 0 | 0 | 163 | 0 |  | 496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 76 | 0 | 180 | 0 | 0 | 162 | 0 | 0 | 0 | 0 | 0 | 156 | 0 | 329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 650 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 503 | 0 | 0 |  | 5185 | 2667 | 7852 | 3381 | 496 | 2161 | 0 | 168 | 1409 | 0 | 0 | 163 | 74 | 0 | 0 | 75.19
6:00 | 0 | 0 | 0 | 180 | 0 | 76 | 0 | 350 | 303 |  | 0 | 350 | 298 | 0 | 0 | 0 | 80 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 15 | 25 | 33 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 228 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 40 | 0 | 0 | 0 | 310 | 305 | 216 | 63 | 0 | 45 | 0 | 0 | 51 | 0 | 0 | 0 | 18 | 0 | 33 | 15 | 72 | 166 | 0 | 19 | 0 | 31 | 30 | 51 | 49 | 0 | 0 | 62 | 40 | 0 | 120 | 18 | 0 | 10 | 275 | 16 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 1 | 20 | 0 | 0 | 365 | 24 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 2 | 0 | 34 | 0 | 17 | 1 | 0 | 0 | 0 | 163 | 0 |  | 495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 75 | 0 | 170 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 0 | 157 | 0 | 329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 2 | 0 | 512 | 7 | 0 |  | 4931 | 2630 | 7561 | 3348 | 495 | 1976 | 0 | 133 | 1357 | 0 | 0 | 163 | 72 | 17 | 0 | 75.19
7:00 | 0 | 0 | 0 | 180 | 0 | 76 | 0 | 358 | 302 |  | 0 | 350 | 314 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 15 | 25 | 33 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 228 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 40 | 0 | 0 | 0 | 335 | 325 | 214 | 63 | 0 | 45 | 0 | 0 | 51 | 0 | 0 | 0 | 18 | 0 | 33 | 18 | 72 | 163 | 0 | 19 | 0 | 33 | 30 | 51 | 49 | 0 | 0 | 61 | 40 | 0 | 120 | 18 | 0 | 10 | 300 | 16 | 8 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 4 | 20 | 0 | 0 | 374 | 40 | 0 | 0 | 1 | 30 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 12 | 0 | 34 | 0 | 17 | 7 | 0 | 0 | 0 | 163 | 0 |  | 495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 74 | 0 | 170 | 0 | 0 | 173 | 0 | 0 | 0 | 0 | 0 | 169 | 0 | 348 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 600 | 0 | 0 | 0 | 1 | 19 | 0 | 0 | 0 | 0 | 5 | 0 | 504 | 35 | 0 |  | 5002 | 2709 | 7711 | 3351 | 495 | 2034 | 0 | 163 | 1348 | 0 | 0 | 163 | 72 | 85 | 0 | 75.18
8:00 | 0 | 0 | 0 | 180 | 0 | 76 | 0 | 396 | 303 |  | 0 | 400 | 312 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 23 | 15 | 25 | 33 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 228 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 39 | 0 | 0 | 0 | 325 | 310 | 212 | 63 | 0 | 44 | 0 | 0 | 51 | 0 | 0 | 0 | 18 | 0 | 33 | 18 | 74 | 162 | 0 | 19 | 1 | 33 | 30 | 51 | 49 | 0 | 0 | 61 | 80 | 0 | 120 | 17 | 0 | 10 | 300 | 16 | 8 | 0 | 0 | 0 | 0 | 47 | 0 | 0 | 9 | 20 | 0 | 0 | 367 | 47 | 0 | 0 | 2 | 30 | 0 | 0 | 0 | 0 | 0 | 76 | 0 | 26 | 0 | 34 | 0 | 17 | 15 | 0 | 0 | 0 | 163 | 0 |  | 495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 75 | 0 | 170 | 0 | 0 | 167 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 418 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 600 | 0 | 0 | 0 | 2 | 40 | 0 | 0 | 0 | 0 | 12 | 0 | 511 | 67 | 0 |  | 5166 | 2842 | 8008 | 3357 | 495 | 2192 | 0 | 195 | 1356 | 0 | 0 | 163 | 74 | 176 | 0 | 75.18
9:00 | 0 | 0 | 0 | 180 | 0 | 74 | 0 | 401 | 345 |  | 0 | 450 | 313 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 23 | 15 | 25 | 33 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 227 | 0 | 0 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 12 | 34 | 0 | 0 | 0 | 325 | 320 | 210 | 63 | 0 | 42 | 0 | 0 | 51 | 0 | 0 | 0 | 18 | 0 | 33 | 18 | 80 | 160 | 0 | 19 | 1 | 32 | 30 | 51 | 47 | 0 | 0 | 61 | 80 | 0 | 130 | 17 | 0 | 10 | 305 | 16 | 8 | 0 | 0 | 0 | 0 | 46 | 0 | 0 | 13 | 20 | 0 | 0 | 397 | 47 | 0 | 0 | 4 | 30 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 21 | 0 | 34 | 0 | 17 | 23 | 0 | 0 | 0 | 163 | 0 |  | 496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 75 | 0 | 170 | 0 | 0 | 164 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 421 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 600 | 0 | 0 | 0 | 3 | 61 | 0 | 0 | 0 | 0 | 20 | 0 | 507 | 108 | 0 |  | 5387 | 2908 | 8295 | 3436 | 496 | 2284 | 0 | 195 | 1352 | 0 | 0 | 195 | 80 | 257 | 0 | 75.18
10:00 | 0 | 0 | 0 | 180 | 0 | 74 | 0 | 400 | 329 |  | 0 | 450 | 301 | 0 | 0 | 0 | 0 | 0 | 99 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 23 | 15 | 25 | 33 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 226 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 12 | 27 | 0 | 0 | 0 | 345 | 340 | 209 | 63 | 0 | 42 | 0 | 0 | 51 | 0 | 0 | 0 | 18 | 0 | 33 | 18 | 72 | 157 | 0 | 19 | 2 | 10 | 29 | 53 | 47 | 0 | 0 | 60 | 80 | 0 | 130 | 17 | 0 | 9 | 310 | 16 | 8 | 0 | 0 | 0 | 0 | 46 | 0 | 13 | 16 | 20 | 0 | 0 | 376 | 47 | 0 | 0 | 4 | 30 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 45 | 0 | 34 | 0 | 17 | 30 | 0 | 0 | 0 | 163 | 0 |  | 496 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 5 | 75 | 0 | 184 | 0 | 0 | 179 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 422 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 620 | 0 | 0 | 0 | 4 | 70 | 0 | 28 | 0 | 0 | 26 | 0 | 498 | 102 | 0 |  | 5417 | 3069 | 8486 | 3532 | 496 | 2254 | 0 | 213 | 1377 | 0 | 28 | 211 | 72 | 303 | 0 | 75.18
11:00 | 0 | 0 | 0 | 180 | 0 | 75 | 0 | 402 | 329 |  | 0 | 450 | 306 | 0 | 0 | 0 | 0 | 0 | 98 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 23 | 13 | 25 | 32 | 0 | 0 | 0 | 25 | 120 | 0 | 0 | 220 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 12 | 33 | 0 | 0 | 0 | 320 | 310 | 208 | 120 | 0 | 41 | 0 | 0 | 51 | 0 | 0 | 0 | 18 | 5 | 33 | 18 | 84 | 157 | 0 | 19 | 2 | 0 | 29 | 53 | 46 | 0 | 0 | 60 | 80 | 0 | 130 | 16 | 0 | 9 | 305 | 16 | 8 | 0 | 0 | 0 | 0 | 111 | 0 | 15 | 18 | 22 | 0 | 0 | 382 | 66 | 0 | 0 | 5 | 80 | 0 | 0 | 0 | 0 | 0 | 66 | 0 | 51 | 0 | 34 | 0 | 0 | 29 | 1 | 0 | 0 | 163 | 0 |  | 496 | 0 | 135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 5 | 75 | 0 | 250 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 420 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 730 | 0 | 0 | 0 | 5 | 73 | 0 | 102 | 0 | 0 | 33 | 0 | 504 | 131 | 0 |  | 5572 | 3430 | 9002 | 3540 | 496 | 2314 | 0 | 335 | 1559 | 25 | 102 | 195 | 84 | 352 | 0 | 75.18
12:00 | 0 | 0 | 0 | 180 | 0 | 75 | 0 | 403 | 328 |  | 0 | 450 | 285 | 0 | 0 | 0 | 0 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 23 | 13 | 25 | 32 | 0 | 0 | 0 | 25 | 120 | 0 | 0 | 224 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 1 | 12 | 33 | 0 | 0 | 0 | 310 | 310 | 210 | 157 | 0 | 40 | 0 | 0 | 51 | 0 | 0 | 0 | 18 | 5 | 33 | 19 | 88 | 157 | 0 | 19 | 2 | 0 | 29 | 53 | 43 | 0 | 0 | 60 | 80 | 0 | 130 | 16 | 0 | 10 | 280 | 16 | 8 | 0 | 0 | 0 | 0 | 144 | 0 | 15 | 19 | 38 | 0 | 0 | 369 | 75 | 0 | 0 | 4 | 80 | 0 | 9 | 0 | 7 | 12 | 120 | 0 | 40 | 5 | 34 | 0 | 16 | 33 | 31 | 8 | 0 | 163 | 0 |  | 497 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 5 | 75 | 0 | 250 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 373 | 0 | 0 | 12 | 0 | 0 | 0 | 6 | 0 | 890 | 0 | 0 | 0 | 4 | 95 | 35 | 152 | 0 | 0 | 28 | 0 | 508 | 80 | 0 |  | 5710 | 3829 | 9539 | 3793 | 497 | 2259 | 0 | 528 | 1723 | 25 | 152 | 163 | 88 | 311 | 0 | 75.18
13:00 | 0 | 0 | 26 | 180 | 0 | 75 | 0 | 400 | 328 |  | 0 | 450 | 299 | 0 | 0 | 0 | 45 | 0 | 97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 23 | 13 | 25 | 32 | 0 | 0 | 0 | 25 | 120 | 0 | 0 | 219 | 0 | 0 | 0 |  | 6 | 0 | 0 | 10 | 0 | 5 | 12 | 35 | 0 | 0 | 0 | 330 | 325 | 205 | 157 | 0 | 40 | 0 | 0 | 51 | 0 | 0 | 0 | 18 | 5 | 33 | 19 | 100 | 153 | 0 | 19 | 2 | 0 | 29 | 53 | 46 | 0 | 0 | 59 | 80 | 0 | 132 | 17 | 0 | 10 | 300 | 16 | 8 | 0 | 0 | 0 | 0 | 144 | 0 | 15 | 18 | 38 | 4 | 0 | 376 | 66 | 0 | 1 | 4 | 100 | 0 | 17 | 14 | 9 | 40 | 256 | 0 | 46 | 54 | 34 | 0 | 17 | 33 | 71 | 17 | 0 | 163 | 0 |  | 496 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 24 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 5 | 76 | 0 | 250 | 0 | 0 | 182 | 0 | 0 | 0 | 0 | 0 | 198 | 0 | 413 | 0 | 0 | 35 | 0 | 0 | 0 | 6 | 0 | 1040 | 0 | 0 | 0 | 5 | 94 | 68 | 152 | 0 | 0 | 31 | 0 | 511 | 75 | 0 |  | 6179 | 4162 | 10341 | 4097 | 496 | 2339 | 0 | 778 | 1877 | 25 | 152 | 163 | 100 | 314 | 0 | 75.18
14:00 | 0 | 0 | 120 | 180 | 0 | 75 | 0 | 403 | 328 |  | 0 | 380 | 280 | 12 | 0 | 0 | 214 | 0 | 96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 10 | 23 | 13 | 25 | 32 | 2 | 0 | 0 | 25 | 120 | 0 | 0 | 219 | 0 | 0 | 0 |  | 6 | 0 | 0 | 10 | 1 | 6 | 12 | 27 | 0 | 0 | 0 | 285 | 280 | 206 | 112 | 0 | 36 | 0 | 0 | 5 | 0 | 0 | 0 | 18 | 5 | 33 | 19 | 102 | 153 | 0 | 19 | 1 | 0 | 29 | 53 | 46 | 0 | 0 | 59 | 79 | 0 | 132 | 17 | 0 | 10 | 290 | 16 | 8 | 0 | 0 | 0 | 0 | 144 | 0 | 15 | 16 | 38 | 78 | 0 | 318 | 66 | 4 | 16 | 3 | 100 | 0 | 17 | 17 | 9 | 50 | 160 | 28 | 44 | 90 | 34 | 0 | 17 | 26 | 72 | 17 | 0 | 163 | 0 |  | 496 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 24 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 5 | 75 | 0 | 250 | 0 | 0 | 159 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 347 | 0 | 0 | 70 | 0 | 0 | 0 | 6 | 0 | 1100 | 0 | 0 | 0 | 5 | 67 | 76 | 153 | 0 | 0 | 18 | 0 | 511 | 94 | 0 |  | 6191 | 4043 | 10234 | 3962 | 496 | 2073 | 0 | 1044 | 1936 | 25 | 153 | 163 | 102 | 280 | 0 | 75.18
15:00 | 0 | 0 | 121 | 180 | 0 | 74 | 0 | 402 | 329 |  | 0 | 380 | 289 | 16 | 0 | 0 | 210 | 0 | 96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 10 | 23 | 13 | 25 | 30 | 16 | 0 | 0 | 25 | 120 | 0 | 0 | 219 | 0 | 0 | 0 |  | 6 | 0 | 0 | 55 | 21 | 6 | 12 | 33 | 0 | 0 | 0 | 310 | 290 | 204 | 110 | 0 | 37 | 0 | 0 | 5 | 0 | 0 | 4 | 18 | 5 | 33 | 19 | 102 | 152 | 0 | 19 | 1 | 0 | 29 | 53 | 45 | 0 | 0 | 59 | 79 | 0 | 130 | 17 | 0 | 8 | 290 | 16 | 8 | 0 | 0 | 0 | 0 | 144 | 0 | 17 | 11 | 38 | 148 | 0 | 400 | 66 | 28 | 17 | 3 | 122 | 0 | 17 | 0 | 9 | 50 | 15 | 34 | 32 | 90 | 34 | 0 | 17 | 21 | 72 | 17 | 0 | 163 | 0 |  | 495 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 26 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 5 | 74 | 0 | 250 | 0 | 0 | 155 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 348 | 0 | 0 | 70 | 0 | 0 | 0 | 5 | 0 | 1112 | 0 | 0 | 0 | 4 | 69 | 75 | 205 | 0 | 0 | 10 | 0 | 504 | 41 | 0 |  | 6336 | 4031 | 10367 | 3916 | 495 | 2086 | 0 | 1238 | 1940 | 25 | 205 | 163 | 102 | 197 | 0 | 75.18
16:00 | 0 | 0 | 120 | 180 | 0 | 74 | 0 | 397 | 329 |  | 0 | 380 | 282 | 16 | 0 | 0 | 170 | 0 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 10 | 23 | 14 | 25 | 30 | 16 | 0 | 0 | 25 | 120 | 0 | 0 | 224 | 0 | 0 | 0 |  | 6 | 0 | 0 | 10 | 40 | 6 | 12 | 33 | 0 | 0 | 0 | 280 | 275 | 207 | 112 | 0 | 38 | 0 | 0 | 5 | 0 | 0 | 8 | 16 | 5 | 33 | 19 | 104 | 156 | 0 | 19 | 1 | 0 | 29 | 53 | 45 | 0 | 0 | 60 | 79 | 0 | 130 | 17 | 0 | 9 | 270 | 16 | 8 | 0 | 0 | 0 | 0 | 117 | 0 | 17 | 8 | 38 | 100 | 0 | 369 | 47 | 76 | 17 | 1 | 123 | 0 | 34 | 0 | 9 | 50 | 35 | 32 | 11 | 35 | 34 | 0 | 17 | 6 | 81 | 17 | 0 | 163 | 0 |  | 494 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 23 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 8 | 74 | 0 | 250 | 0 | 0 | 154 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 323 | 0 | 0 | 35 | 0 | 0 | 0 | 3 | 0 | 1102 | 0 | 0 | 0 | 1 | 40 | 75 | 312 | 0 | 0 | 13 | 0 | 508 | 31 | 0 |  | 6067 | 4012 | 10079 | 3809 | 494 | 2034 | 0 | 1089 | 1934 | 25 | 312 | 163 | 104 | 115 | 44.885 | 75.18
17:00 | 0 | 0 | 120 | 180 | 0 | 75 | 0 | 365 | 289 |  | 0 | 320 | 270 | 9 | 0 | 0 | 170 | 0 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 10 | 23 | 14 | 25 | 30 | 16 | 0 | 0 | 25 | 120 | 0 | 0 | 223 | 0 | 0 | 0 |  | 7 | 0 | 0 | 10 | 49 | 6 | 12 | 32 | 0 | 0 | 0 | 280 | 280 | 207 | 118 | 0 | 39 | 0 | 0 | 5 | 0 | 0 | 16 | 16 | 5 | 33 | 20 | 98 | 153 | 0 | 19 | 0 | 0 | 29 | 53 | 42 | 0 | 0 | 60 | 79 | 0 | 130 | 17 | 0 | 9 | 290 | 16 | 8 | 0 | 0 | 0 | 0 | 117 | 0 | 17 | 3 | 38 | 91 | 0 | 369 | 47 | 105 | 17 | 0 | 123 | 0 | 51 | 0 | 9 | 50 | 65 | 17 | 5 | 35 | 34 | 0 | 17 | 3 | 93 | 17 | 0 | 163 | 0 |  | 493 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 21 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 8 | 75 | 0 | 251 | 0 | 0 | 151 | 0 | 0 | 0 | 0 | 0 | 164 | 0 | 312 | 0 | 0 | 35 | 0 | 0 | 0 | 2 | 0 | 1102 | 0 | 0 | 0 | 0 | 11 | 37 | 210 | 0 | 0 | 7 | 0 | 508 | 24 | 0 |  | 6001 | 3812 | 9813 | 3787 | 493 | 1933 | 0 | 1113 | 1936 | 25 | 210 | 163 | 98 | 55 | 57.3 | 75.17
18:00 | 0 | 0 | 120 | 180 | 0 | 74 | 0 | 320 | 259 |  | 0 | 320 | 263 | 9 | 0 | 0 | 140 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 0 | 23 | 14 | 25 | 30 | 16 | 0 | 0 | 25 | 120 | 0 | 0 | 225 | 0 | 0 | 0 |  | 12 | 0 | 0 | 10 | 50 | 17 | 12 | 38 | 0 | 0 | 0 | 280 | 280 | 180 | 118 | 0 | 36 | 0 | 0 | 5 | 0 | 0 | 16 | 17 | 5 | 33 | 20 | 98 | 156 | 0 | 19 | 0 | 0 | 29 | 22 | 20 | 0 | 0 | 61 | 80 | 0 | 132 | 17 | 0 | 10 | 260 | 16 | 8 | 0 | 8 | 0 | 0 | 124 | 0 | 20 | 0 | 50 | 104 | 6 | 319 | 47 | 105 | 17 | 0 | 123 | 0 | 51 | 0 | 55 | 88 | 124 | 17 | 1 | 35 | 34 | 0 | 17 | 1 | 93 | 23 | 0 | 163 | 0 |  | 492 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 8 | 75 | 0 | 250 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 163 | 0 | 298 | 0 | 0 | 35 | 0 | 34 | 0 | 1 | 10 | 1080 | 0 | 0 | 0 | 0 | 4 | 37 | 40 | 0 | 0 | 1 | 0 | 518 | 5 | 0 |  | 5919 | 3562 | 9481 | 3620 | 492 | 1810 | 0 | 1297 | 1923 | 25 | 40 | 163 | 98 | 13 | 66.85 | 75.17
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 200 | 180 | 0 | 77 | 0 | 348 | 348 |  | 0 | 450 | 289 | 8 | 0 | 7 | 217 | 0 | 100 | 2 | 24 | 48 | 0 | 0 | 0 | 0 | 35 | 17 | 3 | 0 | 23 | 14 | 25 | 30 | 16 | 0 | 0 | 25 | 120 | 0 | 0 | 225 | 0 | 0 | 0 |  | 12 | 0 | 34 | 67 | 50 | 25 | 12 | 38 | 0 | 0 | 0 | 300 | 305 | 208 | 118 | 0 | 41 | 0 | 0 | 18 | 0 | 0 | 18 | 18 | 5 | 31 | 20 | 140 | 154 | 0 | 19 | 0 | 0 | 29 | 53 | 47 | 0 | 0 | 60 | 80 | 0 | 133 | 17 | 0 | 10 | 300 | 16 | 8 | 0 | 15 | 0 | 0 | 173 | 0 | 40 | 0 | 76 | 127 | 8 | 366 | 85 | 105 | 17 | 0 | 160 | 4 | 51 | 17 | 113 | 86 | 138 | 24 | 0 | 48 | 34 | 0 | 17 | 0 | 94 | 34 | 0 | 163 | 0 |  | 492 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 8 | 75 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 395 | 0 | 0 | 68 | 0 | 101 | 0 | 0 | 100 | 1030 | 0 | 0 | 0 | 0 | 0 | 85 | 60 | 0 | 0 | 0 | 0 | 509 | 0 | 0 |  | 7212 | 3759 | 10971 | 4125 | 492 | 2260 | 0 | 1966 | 1614 | 25 | 60 | 289 | 140 | 0 | 146.115 | 75.17
19:30 | 0 | 0 | 200 | 180 | 0 | 77 | 0 | 398 | 348 |  | 0 | 450 | 277 | 50 | 15 | 15 | 219 | 0 | 99 | 16 | 16 | 48 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 10 | 23 | 20 | 25 | 30 | 30 | 0 | 0 | 25 | 120 | 0 | 0 | 225 | 0 | 0 | 0 |  | 12 | 0 | 34 | 77 | 45 | 25 | 12 | 38 | 0 | 0 | 0 | 310 | 300 | 208 | 118 | 0 | 41 | 0 | 0 | 51 | 0 | 0 | 38 | 18 | 5 | 28 | 20 | 142 | 158 | 0 | 19 | 0 | 0 | 29 | 53 | 47 | 0 | 0 | 60 | 80 | 0 | 133 | 17 | 0 | 10 | 265 | 16 | 8 | 0 | 15 | 0 | 0 | 173 | 0 | 70 | 0 | 76 | 150 | 50 | 415 | 83 | 105 | 17 | 0 | 200 | 17 | 51 | 17 | 113 | 86 | 192 | 35 | 0 | 126 | 34 | 0 | 17 | 0 | 94 | 34 | 0 | 163 | 0 |  | 493 | 0 | 340 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 27 | 0 | 0 | 0 | 30 | 0 | 0 | 47 | 0 | 0 | 0 | 10 | 0 | 21 | 0 | 8 | 75 | 0 | 0 | 0 | 0 | 177 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 370 | 17 | 0 | 94 | 0 | 113 | 0 | 0 | 113 | 1110 | 0 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 516 | 0 | 0 |  | 7754 | 3936 | 11690 | 4343 | 493 | 2232 | 0 | 2462 | 1701 | 25 | 0 | 292 | 142 | 0 | 169.035 | 0
20:00 | 0 | 0 | 200 | 180 | 0 | 78 | 0 | 393 | 344 |  | 0 | 450 | 288 | 22 | 14 | 15 | 220 | 0 | 100 | 16 | 8 | 82 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 10 | 23 | 20 | 25 | 30 | 41 | 0 | 0 | 25 | 120 | 0 | 0 | 225 | 0 | 0 | 0 |  | 12 | 0 | 34 | 78 | 20 | 25 | 12 | 38 | 0 | 0 | 0 | 310 | 300 | 211 | 118 | 0 | 41 | 0 | 0 | 51 | 0 | 0 | 43 | 18 | 5 | 25 | 20 | 140 | 159 | 0 | 19 | 0 | 0 | 29 | 53 | 47 | 0 | 0 | 61 | 80 | 0 | 133 | 17 | 0 | 10 | 260 | 16 | 8 | 0 | 0 | 0 | 0 | 173 | 0 | 70 | 0 | 76 | 150 | 38 | 416 | 88 | 105 | 17 | 0 | 200 | 17 | 51 | 0 | 113 | 86 | 265 | 37 | 0 | 126 | 34 | 0 | 17 | 0 | 94 | 34 | 0 | 163 | 0 |  | 493 | 0 | 340 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 28 | 0 | 0 | 0 | 65 | 0 | 0 | 47 | 0 | 0 | 0 | 17 | 0 | 21 | 0 | 8 | 75 | 0 | 0 | 0 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 379 | 17 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 1112 | 0 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 519 | 0 | 0 |  | 7780 | 4017 | 11797 | 4450 | 493 | 2245 | 0 | 2412 | 1706 | 25 | 0 | 326 | 140 | 0 | 143.25 | 75.17
21:00 | 0 | 0 | 220 | 180 | 0 | 78 | 0 | 393 | 334 |  | 0 | 450 | 275 | 8 | 0 | 15 | 220 | 0 | 100 | 0 | 8 | 150 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 10 | 23 | 20 | 25 | 30 | 41 | 0 | 0 | 25 | 120 | 0 | 0 | 226 | 0 | 0 | 0 |  | 12 | 0 | 34 | 78 | 12 | 25 | 12 | 38 | 0 | 0 | 0 | 310 | 300 | 211 | 118 | 0 | 41 | 0 | 0 | 51 | 0 | 0 | 43 | 18 | 5 | 25 | 20 | 144 | 160 | 0 | 19 | 0 | 0 | 29 | 53 | 47 | 0 | 0 | 62 | 80 | 0 | 133 | 18 | 0 | 10 | 285 | 16 | 8 | 0 | 0 | 0 | 0 | 173 | 0 | 70 | 0 | 76 | 150 | 52 | 415 | 88 | 105 | 17 | 0 | 200 | 17 | 51 | 0 | 113 | 76 | 400 | 17 | 0 | 126 | 34 | 0 | 17 | 0 | 93 | 34 | 0 | 163 | 0 |  | 493 | 0 | 340 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 28 | 0 | 0 | 0 | 70 | 0 | 0 | 47 | 0 | 8 | 0 | 34 | 0 | 21 | 0 | 8 | 76 | 0 | 0 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 376 | 17 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 1112 | 0 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 522 | 0 | 0 |  | 7943 | 4063 | 12006 | 4611 | 493 | 2244 | 0 | 2385 | 1710 | 25 | 0 | 394 | 144 | 0 | 93 | 75.17
22:00 | 0 | 0 | 220 | 180 | 0 | 78 | 0 | 393 | 331 |  | 0 | 450 | 280 | 9 | 0 | 0 | 218 | 0 | 70 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 54 | 17 | 0 | 10 | 23 | 20 | 25 | 30 | 41 | 0 | 0 | 25 | 120 | 0 | 0 | 225 | 0 | 0 | 0 |  | 12 | 0 | 34 | 66 | 12 | 25 | 12 | 39 | 0 | 0 | 0 | 310 | 300 | 211 | 118 | 0 | 42 | 0 | 0 | 51 | 0 | 0 | 43 | 18 | 5 | 25 | 20 | 148 | 160 | 0 | 19 | 0 | 0 | 29 | 53 | 49 | 0 | 0 | 61 | 80 | 0 | 133 | 17 | 0 | 10 | 265 | 16 | 8 | 0 | 0 | 0 | 0 | 173 | 0 | 70 | 0 | 76 | 150 | 10 | 367 | 88 | 105 | 17 | 0 | 200 | 17 | 51 | 0 | 114 | 76 | 400 | 17 | 0 | 126 | 34 | 0 | 25 | 0 | 93 | 34 | 0 | 163 | 0 |  | 493 | 0 | 340 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 30 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 22 | 0 | 8 | 76 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 371 | 17 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 1112 | 0 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 523 | 0 | 0 |  | 7766 | 4023 | 11789 | 4529 | 493 | 2227 | 0 | 2309 | 1711 | 25 | 0 | 347 | 148 | 0 | 50 | 75.17
23:00 | 0 | 0 | 220 | 180 | 0 | 78 | 0 | 395 | 339 |  | 0 | 450 | 285 | 14 | 0 | 0 | 218 | 0 | 66 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 35 | 17 | 0 | 0 | 23 | 20 | 25 | 30 | 41 | 0 | 0 | 0 | 120 | 0 | 0 | 227 | 0 | 0 | 0 |  | 12 | 0 | 34 | 66 | 8 | 25 | 12 | 39 | 0 | 0 | 0 | 310 | 300 | 211 | 118 | 0 | 42 | 0 | 0 | 51 | 0 | 0 | 43 | 18 | 5 | 25 | 15 | 146 | 161 | 0 | 19 | 0 | 0 | 29 | 53 | 49 | 0 | 0 | 62 | 80 | 0 | 133 | 18 | 0 | 10 | 270 | 16 | 8 | 0 | 0 | 0 | 0 | 173 | 0 | 70 | 0 | 76 | 150 | 10 | 367 | 89 | 105 | 17 | 0 | 200 | 17 | 51 | 0 | 62 | 76 | 400 | 22 | 0 | 126 | 34 | 0 | 35 | 0 | 93 | 34 | 0 | 163 | 0 |  | 493 | 0 | 410 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 30 | 16 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 22 | 0 | 8 | 76 | 0 | 0 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 371 | 17 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 1112 | 0 | 0 | 0 | 0 | 0 | 114 | 0 | 0 | 0 | 0 | 0 | 519 | 0 | 0 |  | 7691 | 4116 | 11807 | 4590 | 493 | 2245 | 0 | 2279 | 1707 | 0 | 0 | 347 | 146 | 0 | 92 | 75.17
24:00 | 0 | 0 | 220 | 180 | 0 | 78 | 0 | 394 | 339 |  | 0 | 450 | 285 | 33 | 0 | 0 | 220 | 0 | 66 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 0 | 23 | 24 | 25 | 32 | 16 | 0 | 0 | 0 | 120 | 0 | 4 | 227 | 0 | 0 | 0 |  | 12 | 0 | 34 | 55 | 3 | 6 | 12 | 40 | 0 | 0 | 0 | 310 | 300 | 211 | 153 | 0 | 43 | 0 | 0 | 51 | 0 | 19 | 43 | 18 | 5 | 25 | 15 | 148 | 162 | 0 | 19 | 0 | 0 | 29 | 53 | 49 | 0 | 0 | 62 | 80 | 0 | 133 | 18 | 0 | 10 | 270 | 16 | 8 | 0 | 0 | 0 | 0 | 49 | 0 | 70 | 0 | 63 | 17 | 10 | 367 | 49 | 105 | 17 | 0 | 87 | 17 | 40 | 0 | 36 | 76 | 400 | 63 | 0 | 126 | 34 | 0 | 35 | 0 | 94 | 17 | 0 | 163 | 0 |  | 493 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 29 | 16 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 22 | 0 | 8 | 76 | 0 | 0 | 0 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 373 | 17 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 1212 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 514 | 0 | 0 |  | 7267 | 4106 | 11373 | 4600 | 493 | 2282 | 0 | 1682 | 1802 | 0 | 0 | 366 | 148 | 0 | 298 | 75.17
KWH | 0 | 0 | 1734781 | 4315500 | 0 | 1794000 | 0 | 9383940 | 7842000 |  | 0 | 9847500 | 7038167 | 150720 | 10930 | 48454 | 2793456 | 0 | 1850000 | 10560 | 39600 | 730224 | 0 | 0 | 0 | 0 | 259920 | 185546 | 48065 | 130968 | 552000 | 371880 | 617000 | 783400 | 256800 | 0 | 0 | 300000 | 2900000 | 0 | 3447 | 5317542 | 0 | 0 | 0 |  | 151920 | 0 | 195653 | 480720 | 272640 | 219360 | 280896 | 904320 | 0 | 0 | 0 | 7800000 | 7354000 | 5088000 | 2325090 | 0 | 1003104 | 0 | 0 | 986034 | 0 | 11728 | 276139 | 418356 | 90720 | 769800 | 422860 | 2336640 | 3741120 | 0 | 400144 | 13750 | 306000 | 656520 | 1222200 | 1114128 | 0 | 0 | 1462560 | 1828800 | 0 | 2945490 | 401000 | 0 | 239220 | 7012000 | 384288 | 192384 | 0 | 55200 | 0 | 0 | 2344800 | 0 | 545616 | 137430 | 1026240 | 1372320 | 276000 | 9071000 | 1398000 | 1062451 | 273490 | 30961 | 2481491 | 96006 | 610542 | 37620 | 609000 | 816000 | 3095500 | 313920 | 357190 | 1064160 | 839291 | 0 | 469440 | 222898 | 1153920 | 358200 | 0 | 3919200 | 0 |  | 11956363 | 0 | 5516064 | 0 | 158400 | 0 | 0 | 0 | 0 | 0 | 0 | 1640000 | 529031 | 131520 | 0 | 0 | 295000 | 0 | 0 | 122512 | 0 | 7634 | 0 | 142800 | 0 | 473520 | 0 | 151632 | 1786473 | 0 | 4031100 | 0 | 0 | 4301455 | 0 | 0 | 0 | 0 | 0 | 4360845 | 0 | 8946581 | 81600 | 0 | 989952 | 0 | 656889 | 0 | 45653 | 621120 | 23378600 | 0 | 0 | 0 | 36240 | 691200 | 1020864 | 1326556 | 0 | 0 | 196331 | 0 | 12321818 | 931850 | 0 |  | 146661870 | 86849603 | 233511473 | 92899205 | 11956363 | 52102591 | 0 | 23429307 | 41517991 | 300000 | 1326556 | 4979317 | 2336640 | 2663503 | 0
Fuel Cost | 0 | 0 | 2532780.26 | 6430095 | 0 | 2386020 | 0 | 9853137 | 8469360 |  | 0 | 10733775 | 7812365.37 | 1685049.6 | 144822.5 | 642015.5 | 3128670.72 | 0 | 3237500 | 154387.2 | 557172 | 11836931.04 | 0 | 0 | 0 | 0 | 3306182.4 | 2504871 | 644551.65 | 98226 | 414000 | 0 | 0 | 0 | 4368168 | 0 | 0 | 81000 | 5481000 | 0 | 56358.45 | 5530243.68 | 0 | 0 | 0 |  | 1982556 | 0 | 3330014.06 | 6494527.2 | 3457075.2 | 2537995.2 | 356737.92 | 3011385.6 | 0 | 0 | 0 | 8658000 | 8015860 | 5902080 | 2999366.1 | 0 | 1133507.52 | 0 | 0 | 1646676.78 | 0 | 202542.56 | 3714069.55 | 573147.72 | 68040 | 1347150 | 317145 | 16777075.2 | 4077820.8 | 0 | 544195.84 | 219175 | 419220 | 866606.4 | 2126628 | 1927441.44 | 0 | 0 | 2837366.4 | 4169664 | 0 | 2974944.9 | 862150 | 0 | 473655.6 | 7012000 | 288216 | 146211.84 | 0 | 753480 | 0 | 0 | 31607904 | 0 | 7556781.6 | 1606556.7 | 10590796.8 | 18745891.2 | 3662520 | 8345320 | 16999680 | 15363041.46 | 3459648.5 | 0 | 29132704.34 | 1045505.34 | 6490061.46 | 510503.4 | 7850010 | 9612480 | 2847860 | 4065264 | 5161395.5 | 13504190.4 | 9551131.58 | 0 | 6130886.4 | 2663631.1 | 17274182.4 | 4717494 | 0 | 0 | 0 |  | 35869089 | 0 | 6177991.68 | 0 | 1648944 | 0 | 0 | 0 | 0 | 0 | 0 | 1836800 | 1026320.14 | 1433568 | 0 | 0 | 604750 | 0 | 0 | 1916087.68 | 0 | 126419.04 | 0 | 1946364 | 0 | 980186.4 | 0 | 114785.424 | 10379408.13 | 0 | 21324519 | 0 | 0 | 4989687.8 | 0 | 0 | 0 | 0 | 0 | 5058580.2 | 0 | 8857115.19 | 1096704 | 0 | 11711132.16 | 0 | 8342490.3 | 0 | 504465.65 | 7540396.8 | 210641186 | 0 | 0 | 0 | 409874.4 | 8107776 | 15649845.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 432807850.38 | 368294486.114 | 801102336.494 | 106069828.104 | 35869089 | 63631959.62 | 0 | 300369821.75 | 242345113.13 | 81000 | 0 | 17285575.34 | 16777075.2 | 18672874.35 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 0 | 75 | 0 | 403 | 328 |  | 0 | 450 | 285 | 0 | 0 | 0 | 0 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 23 | 13 | 25 | 32 | 0 | 0 | 0 | 25 | 120 | 0 | 0 | 224 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 1 | 12 | 33 | 0 | 0 | 0 | 310 | 310 | 210 | 157 | 0 | 40 | 0 | 0 | 51 | 0 | 0 | 0 | 18 | 5 | 33 | 19 | 88 | 157 | 0 | 19 | 2 | 0 | 29 | 53 | 43 | 0 | 0 | 60 | 80 | 0 | 130 | 16 | 0 | 10 | 280 | 16 | 8 | 0 | 0 | 0 | 0 | 144 | 0 | 15 | 19 | 38 | 0 | 0 | 369 | 75 | 0 | 0 | 4 | 80 | 0 | 9 | 0 | 7 | 12 | 120 | 0 | 40 | 5 | 34 | 0 | 16 | 33 | 31 | 8 | 0 | 163 | 0 |  | 497 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 5 | 75 | 0 | 250 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 373 | 0 | 0 | 12 | 0 | 0 | 0 | 6 | 0 | 890 | 0 | 0 | 0 | 4 | 95 | 35 | 152 | 0 | 0 | 28 | 0 | 508 | 80 | 0 |  | 9539 | DayPeak
Yesterday Evening Peak | 0 | 0 | 220 | 180 | 0 | 78 | 0 | 393 | 334 | 0 | 0 | 450 | 275 | 8 | 0 | 15 | 220 | 0 | 100 | 0 | 8 | 150 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 10 | 23 | 20 | 25 | 30 | 41 | 0 | 0 | 25 | 120 | 0 | 0 | 226 | 0 | 0 | 0 | 0 | 12 | 0 | 34 | 78 | 12 | 25 | 12 | 38 | 0 | 0 | 0 | 310 | 300 | 211 | 118 | 0 | 41 | 0 | 0 | 51 | 0 | 0 | 43 | 18 | 5 | 25 | 20 | 144 | 160 | 0 | 19 | 0 | 0 | 29 | 53 | 47 | 0 | 0 | 62 | 80 | 0 | 133 | 18 | 0 | 10 | 285 | 16 | 8 | 0 | 0 | 0 | 0 | 173 | 0 | 70 | 0 | 76 | 150 | 52 | 415 | 88 | 105 | 17 | 0 | 200 | 17 | 51 | 0 | 113 | 76 | 400 | 17 | 0 | 126 | 34 | 0 | 17 | 0 | 93 | 34 | 0 | 163 | 0 |  | 493 | 0 | 340 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 28 | 0 | 0 | 0 | 70 | 0 | 0 | 47 | 0 | 8 | 0 | 34 | 0 | 21 | 0 | 8 | 76 | 0 | 0 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 376 | 17 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 1112 | 0 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 522 | 0 | 0 |  | 12006 | EvPeak
Forecast for Evening | 0 | 0 | 150 | 180 | 0 | 76 | 0 | 400 | 330 | 0 | 0 | 450 | 300 | 50 | 90 | 15 | 220 | 0 | 100 | 90 | 92 | 149 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 18 | 23 | 20 | 25 | 32 | 41 | 0 | 25 | 0 | 120 | 0 | 25 | 225 | 0 | 0 | 0 | 0 | 12 | 60 | 84 | 70 | 50 | 35 | 13 | 35 | 0 | 0 | 0 | 310 | 310 | 210 | 118 | 0 | 40 | 0 | 0 | 51 | 0 | 46 | 43 | 18 | 8 | 33 | 20 | 165 | 162 | 0 | 19 | 0 | 0 | 29 | 51 | 45 | 0 | 0 | 61 | 85 | 0 | 133 | 18 | 0 | 10 | 310 | 16 | 8 | 0 | 300 | 300 | 100 | 170 | 80 | 70 | 0 | 76 | 150 | 150 | 400 | 115 | 105 | 17 | 0 | 300 | 54 | 51 | 106 | 113 | 90 | 400 | 70 | 0 | 162 | 34 | 0 | 35 |  | 94 | 35 | 0 | 162 |  |  | 942 | 0 | 350 |  | 98 | 0 | 0 | 0 | 35 | 74 | 40 | 70 | 31 | 64 | 0 | 0 | 70 | 26 | 34 | 80 | 14 | 42 | 42 | 34 | 35 | 22 | 0 | 8 | 75 | 0 | 0 | 0 | 0 | 190 |  | 0 | 0 | 0 | 0 | 200 | 0 | 380 | 17 | 0 | 113 | 100 | 113 | 0 | 0 | 113 | 1244 | 0 |  | 150 |  |  | 115 | 0 |  | 0 |  | 0 | 500 |  | 0
Forecast for Day | 0 | 0 | 150 | 180 | 0 | 16 | 0 | 400 | 300 | 0 | 0 | 450 | 300 | 16 | 90 | 15 | 220 | 0 | 90 | 90 | 48 | 149 | 0 | 0 | 0 | 0 | 35 | 17 | 35 | 10 | 23 | 20 | 25 | 32 | 41 | 0 | 25 | 0 | 120 | 0 | 25 | 225 | 0 | 0 | 0 | 0 | 12 | 45 | 66 | 50 | 0 | 26 | 13 | 15 | 0 | 0 | 0 | 310 | 310 | 210 | 118 | 0 | 40 | 0 | 0 | 51 | 0 | 31 | 43 | 18 | 8 | 25 | 20 | 143 | 162 | 0 | 16 | 1.6 | 0 | 29 | 51 | 44 | 0 | 0 | 61 | 85 | 0 | 133 | 18 | 0 | 10 | 300 | 16 | 8 | 0 | 300 | 300 | 50 | 160 | 0 | 17 | 20 | 38 | 17 | 80 | 400 | 75 | 105 | 17 | 5 | 120 | 17 | 17 | 17 | 9 | 63 | 400 | 54 | 50 | 126 | 34 | 0 | 35 | 30 | 94 | 17 | 0 | 162 |  |  | 508 | 0 | 350 | 0 | 85 | 0 | 0 | 0 | 22 | 55 | 0 | 70 | 25 | 16 | 0 | 0 | 70 | 26 | 0 | 80 | 0 | 34 | 24 | 0 | 35 | 22 | 0 | 8 | 75 | 0 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 380 | 17 | 0 | 95 | 0 | 95 | 0 | 8 | 95 | 900 | 0 |  | 17 | 6 | 100 | 35 | 0 |  | 0 | 30 | 0 | 500 | 130 | 0 |  |  |  |  | g | h | o | c | h | t | s
Generation at 08:00(Today) | 0 | 0 | 150 | 180 | 0 | 13 | 0 | 351 | 254 | 0 | 0 | 340 | 310 | 34 | 0 | 0 | 140 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 20 | 25 | 33 | 0 | 0 | 0 | 0 | 120 | 0 | 8 | 226 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 44 | 0 | 4 | 12 | 8 | 0 | 0 | 0 | 305 | 285 | 193 | 158 | 0 | 43 | 0 | 0 | 10 | 0 | 0 | 43 | 18 | 5 | 25 | 20 | 118 | 160 | 0 | 19 | 1 | 0 | 29 | 53 | 46 | 0 | 0 | 61 | 81 | 0 | 133 | 17 | 0 | 10 | 290 | 16 | 8 | 0 | 0 | 0 | 0 | 48 | 0 | 17 | 9 | 38 | 17 | 0 | 337 | 59 | 17 | 17 | 2 | 87 | 17 | 17 | 0 | 9 | 38 | 370 | 53 | 22 | 0 | 34 | 0 | 17 | 14 | 36 | 0 | 0 | 0 | 0 | 0 | 496 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 17 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 74 | 0 | 0 | 0 | 0 | 158 | 0 | 0 | 0 | 0 | 0 | 158 | 0 | 330 | 0 | 0 | 15 | 0 | 95 | 0 | 1 | 0 | 900 | 0 | 0 | 0 | 1 | 48 | 64 | 0 | 0 | 0 | 11 | 0 | 509 | 68 | 0 | 0 |  |  |  | 145.0018 | 11.9564 | 29.7352 | 41.518 | 0.3 | 2.3366 | 2.6635
233.5115
| Minimum Generation |  | 7561 | 6:00
| Highest Generation |  | 12006 | 21:00
| Day Peak Generation |  | 9539 | 12:00
| Evening Peak Generation |  | 12006 | 21:00
| HVDC Max Flow |  | 497 | 12:00
| HVDC EvPeak Flow |  | 493 | 21:00
| Load factor L.F |  | 81.04% | [161 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2023-04-29
Till now the maximum generation is : - |  |  |  | 15648 | 21:00 | Hrs on | 2023-04-19
The Summary of Yesterday's |  |  | 2023-04-28 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 9539 | MW Hour : | 12:00 | Min. Gen. at | 6:00 | 9111
Evening Peak Generation : |  |  | 12006 | MW Hour : | 21:00 | Available Max Generation : |  | 15228
E.P. Demand (at gen end) : |  |  | 12100 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 12500
Maximum Generation : |  |  | 12006 | MW Hour : | 21:00 | Reserve(Generation end) |  | 2728
Total Gen. (MKWH) : |  |  | 233.5115 | System Load Factor : | 81.04% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | -150 | MW at | 20:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2023-04-29
Actual : |  | 75.16 | Ft.(MSL) , | Rule curve : | 80.4 | Ft.( MSL )
Gas Consumed : |  | Total = | 1164.67 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 169701787.724
: |  |  | Coal : | 242345113.13 | Oil : | 317655397.09 | Total : | 729702297.944
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 0 | 0:00 | 4277.4276 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 1183.5628 |  |  | 0 | 0%
Khulna Area |  | 0 | 0:00 | 1555.8063 |  |  | 0 | 0%
Rajshahi Area |  | 0 | 0:00 | 1372.6427 |  |  | 0 | 0%
Cumilla Area |  | 25 | 600:00 | 1171.9796 |  |  | 0 | 0%
Mymensingh Area |  | 65 | 1560:00 | 963.3164 |  |  | 0 | 0%
Sylhet Area |  | 0 | 0:00 | 435.3258 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 351.1605 |  |  | 0 | 0%
Rangpur Area |  | 0 | 0:00 | 760.6533 |  |  | 0 | 0%
Total |  | 90 |  | 12071.875 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 2
2) Ghorasal-3,7
3) Bhula Nuton Biddut
4) Baghabari-100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
7) Shajibazar 330 MW
8) Sirajganj- 2
9) Barishal 307 MW
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
- | 8:05 | Kushtia 132/33 kV S/S T-1 HT is restored.
8:22 | - | Bibiyana South 400 MW ST tripped due to high vibration in ST bearing.
9:03 | 15:02 | HVDC Bheramera-Ishwardi 230kV Ckt-4 Scheduled S/D from Ishurdi 230/132kV end Due to Annual Maintenance.
9:20 | 11:39 | Jhenaidah-Khulna 230kV Ckt-1 Scheduled S/D from Khulna(S) 230/132kV end Due to For maintenance Work at Jhenaidah SS end.
and from Jhenaidah 230/132kV end Due to Earth switch alignment rectification work.
9:29 | 15:04 | HVDC Bheramera-Ishwardi 230kV Ckt-4 Scheduled S/D from BIPTC end Due to Shutdown is taken from Ishurdi sub-station end.
9:30 | 17:12 | Bagerhat-Mongla 132 kV Ckt-2 Forced S/D from Bagerhat 132/33kV end Due to R-Phase Lightening Arrester Changing work.
- | 9:46 | Bogura 132/33kV S/S Transformer-2 LT is restored.
- | 9:46 | Bogura 132/33kV S/S Transformer-2 HT is restored.
9:52 | 18:01 | BIPTC S/S 400kV Bus-2 Scheduled S/D Due to Annual maintenance.
10:24 | 10:48 | Maniknagar 132/33kV S/S Kazla Ckt -1 Project Work S/D Due to Outage No-9351 (D/W). RTU and Telecommunication panel installation work by DPDC.
10:50 | 11:21 | Maniknagar 132/33kV S/S Kazla Ckt -2 Project Work S/D Due to Outage No-9351 (D/W). RTU and Telecommunication panel installation work by DPDC.
11:25 | 14:56 | Ghorasal-Narsingdi 132 kV Ckt-1 Scheduled S/D from Narshingdi 132/33kV end Due to For Kite Remove.
11:25 | 15:08 | Ghorasal-Narsingdi 132 kV Ckt-2 Scheduled S/D from Narshingdi 132/33kV end Due to For Kite Remove.
- | 11:35 | Faridpur 132/33kV S/S Transformer-1 HT is restored.
- | 11:36 | Faridpur 132/33kV S/S Transformer-1 LT is restored.
11:48 | 13:32 | Jhenaidah 230/132kV S/S Transformer- 1 LT Project Work S/D Due to D/S connection problem solving.
11:48 | 13:28 | Jhenaidah 230/132kV S/S Transformer- 1 HT Project Work S/D Due to D/S connection problem solving.
- | 11:58 | Ghorasal GT-4 was sync.
- | 12:42 | Siddirganj CCPP 335MW GT was sync.
- | 15:05 | Gopalganj(N)-Madaripur 132kV Ckt-1 is restored.
15:15 | 17:07 | HVDC Bheramera- Jhenaidah 230kV Ckt-1 Project Work S/D from Jhenaidah 230/132kV end Due to D/S connection problem solving and
from BIPTC end Due to Shutdown is taken from Jhenaidah S/S end for DS finger check.
15:16 | 16:54 | Jhenaidah 230/132kV S/S 230 kV Bus Project Work S/D Due to D/S connection problem solving.
15:16 | 16:54 | Jhenaidah 230/132kV S/S 230 kV Bus Project Work S/D Due to D/S connection problem solving.
- | 16:58 | Khulna (S)-Satkhira 132kV Ckt-2 is restored.
- | 17:13 | Bagerhat-Mongla 132 kV Ckt-2 is restored.
- | 17:27 | Bibiyana South 400 MW ST was sync.
17:32 | - | BIPTC S/S 20DF24 Scheduled S/D Due to Tripped for CB pole discrepency.
18:48 | - | Barapukuria-3 was forced shutdown due to excessive steamline leakage.
19:03 | - | Khulna 330 MW CCPP was shutdown due to IP turbine problem.
19:13 | - | Bogura 400/230 KV S/S-Reactor open.
- | 19:26 | Savar 132/33kV S/S Bus-B is restored.
- | 19:29 | Baghabari GT-1 - 71MW was sync.
- | 19:31 | Savar 132/33kV S/S T-3 HT is restored.
- | 19:32 | Savar 132/33kV S/S T-3 LT is restored.
22:42 | 0:17 | Ishurdi 132/33kV S/S 132/33 kV T-2 HT Forced S/D Due to red hot maintenance.
22:42 | 0:17 | Ishurdi 132/33kV S/S 132/33 kV T-2 LT Forced S/D Due to red hot maintenance.
5:28 | - | Bhaluka 132/33kV S/S Transformer- 02 LT Project Work S/D Due to Development work. | [5 empty] | 110.0MW load interrup.
5:28 | - | Bhaluka 132/33kV S/S Transformer- 01 LT Project Work S/D Due to Development work. | [5 empty] | 110.0MW load interrup.
5:30 | - | Bhaluka 132/33kV S/S Transformer- 02 HT Project Work S/D Due to Development work. | [5 empty] | 110.0MW load interrup.
5:30 | - | Bhaluka 132/33kV S/S Transformer- 01 HT Project Work S/D Due to Development work. | [5 empty] | 110.0MW load interrup.
5:32 | - | Bhaluka-Mymensingh 132 kV Ckt-2 Project Work S/D from Bhaluka 132/33kV end Due to Development work. | [5 empty] | 110.0MW load interrup. Bhaluka 132/33kV end
5:32 | - | Bhaluka-Mymensingh 132 kV Ckt-1 Project Work S/D from Bhaluka 132/33kV end Due to Development work. | [5 empty] | 110.0MW load interrup. Bhaluka 132/33kV end
7:05 | - | Kodda 132/33kV S/S Tr-3 (426T) LT Scheduled S/D.
7:06 | - | Kodda 132/33kV S/S Tr-4 (436T) LT Scheduled S/D.
7:07 | - | Kodda 132/33kV S/S Tr-3 (426T) HT Scheduled S/D. | [5 empty] | 25.0MW load interrup.
7:08 | - | Kodda 132/33kV S/S Tr-4 (436T) HT Scheduled S/D. | [5 empty] | 25.0MW load interrup.
7:16 | - | Naogaon 132/33kV S/S T-3 LT Scheduled S/D Due to Loop connection of new 33kv nesco bay with T-3 33kv bus. | [5 empty] | 35.0MW load interrup.
7:17 | - | Naogaon 132/33kV S/S T-3 HT Scheduled S/D Due to Loop connection of new 33kv nesco bay with T-3 33kv bus. | [5 empty] | 35.0MW load interrup.
7:18 | - | Faridpur 132/33kV S/S Transformer-2 LT Scheduled S/D Due to maintenance work. | [5 empty] | 40.0MW load interrup.
7:18 | - | Faridpur 132/33kV S/S Transformer-2 HT Scheduled S/D Due to maintenance work. | [5 empty] | 40.0MW load interrup.
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2023-04-28 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 220 | 1734781
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4315500
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 78 | 1794000 | Engine problem
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 393 | 9383940 | Machine problem
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 334 | 7842000 | Machine problem
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 9847500
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 8 | 150720 | Low Demand
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 275 | 7038167 | FGMO
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 0 | 10930 | Reserve
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 15 | 48454 | Low Demand
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 10 | 130968 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 100 | 1850000 | Frequency control
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 0 | 10560 | Low Demand
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 220 | 2793456 | ST Under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 8 | 39600 | Low Demand
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 259920
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 150 | 730224
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 17 | 185546 | Low Demand
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 17 | 48065 | Low Demand
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 43 | 923880 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 617000 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 30 | 783400
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 41 | 256800 | Engine problem
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 0 | 55200 | Reserve
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 0 | 0 | Reserve
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 70 | 545616 | Low Demand
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 1062451
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 17 | 313920 | Low Demand
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 126 | 1064160 | Low Demand
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 222898
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 34 | 358200 | Low Demand
| Dhaka area Total |  |  |  | 5847 | 3020 | 54417856
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 120 | 2900000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 0 | 3447 | Reserve
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 137430
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 25 | 219360 | Low Demand
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 25 | 300000 | Low Water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 226 | 5317542
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 17 | 273490 | Low Demand
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Reserve
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 34 | 195653 | Low Demand
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 78 | 480720 | Low Demand
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 76 | 1026240 | Low Demand
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 12 | 280896 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 38 | 904320
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 12 | 272640 | Low Demand
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 30961
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 200 | 2481491 | Low Demand
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 17 | 96006 | Low Demand
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 51 | 610542 | Low Demand
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 76 | 816000 | Engine problem
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 34 | 839291 | Fuel shortage
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 0 | 163 | 3919200 | On test.
| Chattogram area Total |  |  |  | 2382 | 1204 | 21105229
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 211 | 5088000 | FGMO
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 310 | 7800000 | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 300 | 7354000 | FGMO
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 0 | 0 | Under maint.
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 41 | 1003104
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 0 | 0 | Contract Expired
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 118 | 2325090 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 986034
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 52 | 276000 | Low Demand
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 11728 | Reserve
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 150 | 1372320 | Low Demand
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 418356 | Engine problem
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 5 | 90720 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 144 | 2336640
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 25 | 769800 | Engine problem
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 43 | 276139 | Engine problem
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 20 | 422860 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 37620 | Reserve
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 113 | 609000
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 469440 | Low Demand
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 93 | 1153920 | Engine problem
| Cumilla Area Total |  |  |  | 3151 | 1711 | 32800771
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 160 | 3741120 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 400144 | Engine problem
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 13750
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 173 | 2344800 | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 88 | 1398000 | Fuel shortage
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 357190
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 151920 | Engine problem
| Mymensingh Area Total |  |  |  | 614 | 452 | 8406924
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 0 | 306000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 29 | 656520 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Under maint.
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 1222200
| Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 47 | 1114128
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 8 | 192384 | Engine problem
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 62 | 1462560
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 80 | 1828800
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 133 | 2945490 | Machine problem
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 401000
| Sylhet 50MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 384288 | Engine problem
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 285 | 7012000 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 415 | 9071000 | FGMO
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 239220
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 400 | 3095500
| Sylhet Area Total |  |  |  | 2427 | 1556 | 29931090
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Fuel shortage
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 493 | 11956363
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 33 | 158400 | Low Demand
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel conservation
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 340 | 5516064 | Frequency control
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 0 | 0 | Reserve
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 81600 | Low Demand
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Reserve
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 691200
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 0 | 0 | 1326556 | On test.
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 660*2 | 617 | 0 | 0 | On test.
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3001 | 883 | 19730183
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 131520
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 28 | 529031 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 70 | 1640000 | Machine problem
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1112 | 23378600 | Low Demand
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 0 | 0 | Under maint.
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Reserve
| Barisal 307 MW |  | BCPCL | 307*1 | 307 | 0 | 0 | Coal shortage
| Barisal Area Total |  |  |  | 2265 | 1210 | 25679151
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 70 | 295000
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Reserve
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 8 | 7634 | Reserve
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 174 | 4301455 | FGMO
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 180 | 4360845 | FGMO
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 376 | 8946581 | FGMO
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 21 | 473520
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 151632 | Engine problem
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 34 | 142800 | Low Demand
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 47 | 122512 | Low Demand
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Reserve
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 989952
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 621120
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 36240
| Adani Power Jharkhanda Ltd |  | Import | 0 | 0 | 522 | 12321818 | On test.
| Rajshahi Area Total |  |  |  | 2129 | 1666 | 32771109
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 76 | 1786473 | Coal shortage
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 4031100 | Under maint.
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 656889
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 45653
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 115 | 1020864
| Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 196331
| Teesta Solar Limited |  | BPCL | 16*12.5 | 0 | 0 | 931850
| Rangpur Area Total |  |  |  | 750 | 304 | 8669160
| Total |  |  |  | 22566 | 12006 | 233511473
| Eastern Grid Total |  |  |  | 14421 | 7943 | 146661870
| Western Grid Total |  |  |  | 8145 | 4063 | 86849603
| National Grid Total |  |  |  | 22566 | 12006 | 233511473
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2023-04-28
| (a) ENTIRE EASTERN GRID : |  | 7648.85 | MW | (b) ENTIRE WESTERN GRID : |  | 3816.04 | MW
| i) Dhaka area |  | 3593.65 | MW | i) Khulna area |  | 1316.8 | MW
| ii) Chittagong area |  | 1251.2 | MW | ii) Rajshahi area |  | 1393 | MW
| iii) Comilla area |  | 1207 | MW | iii) Barisal area |  | 266.24 | MW
| iv) Mymensingh area |  | 1094 | MW | iv) Rangpur area |  | 840 | MW
| v) Sylhet area |  | 503 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 11464.89 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | Chhatak | 29 | 20:00 | Kamrangirchar | 28 | 12:00 | Natore | 137 | 20:00 | Shitalakhya | 73 | 23:00
2 | AKSML | 101 | 02:00 | Chowmuhani | 204 | 22:00 | Kaptai | 4 | 18:00 | Nawabganj | 53.6 | 21:00 | Sholosohor | 26 | 22:00
3 | Aftabnagar | 29 | 19:00 | Chuadanga | 99 | 19:30 | Kazla | 57 | 21:00 | Netrakona | 135 | 21:00 | Shyampur | 88 | 12:00
4 | Agargaon | 59 | 19:30 | Coxsbazar | 128 | 22:00 | Keranigonj | 50 | 22:00 | New | 44 | 21:00 | Siddhirganj | 80 | 20:00
5 | Agrabad | 58 | 20:00 | Cumilla(N) | 169 | 21:00 | Khagrachori | 30 | 19:30 | Niamatpur | 99 | 21:00 | Sirajganj | 104 | 19:30
6 | Amnura | 64 | 21:00 | Cumilla(S) | 148 | 22:00 | Khulna | 76 | 13:00 | Noapara | 33 | 21:00 | Sonargaon | 62 | 21:00
7 | Ashuganj | 70 | 23:00 | Daudkandi | 128 | 22:00 | Khulshi | 168 | 23:00 | PHP | 8 | 06:00 | Sreemongol | 60 | 20:00
8 | BIPTC | N/A | N/A | Dhaka | 14 | 18:30 | Kishoreganj | 132 | 20:00 | Pabna | 87 | 21:00 | Sreepur | 43.7 | 21:00
9 | BSRM | 111 | 05:00 | Dhamrai | 112 | 19:00 | Kodda | 192 | 20:00 | Palashbari | 130 | 19:30 | Srinagar | 42.55 | 20:00
10 | Bagerhat | 65 | 14:00 | Dhanmondi | 97 | 19:00 | Kulaura | 44 | 19:30 | Panchagarh | 55 | 19:00 | Sunamganj | 46 | 20:00
11 | Bakulia | 82 | 23:00 | Dohazari | 102 | 20:00 | Kurigram | 64 | 20:00 | Patuakhali | 89 | 12:00 | Sylhet | 122 | 20:00
12 | Banani | 29 | 19:30 | Faridpur | 126 | 21:00 | Kushtia | 122 | 21:00 | Payra | 17.4 | 13:00 | TK | 12 | 01:00
13 | Bangabhaban | 5 | 16:00 | Fatullah | 40 | 23:00 | Lalbag | 22 | 19:30 | Postogola | 41 | 23:00 | Tangail | 237 | 19:30
14 | Barapukuria | 58 | 22:00 | Fenchuganj | 48 | 18:30 | Lalmonirhat | 50 | 19:00 | Purbachal | 16 | 23:00 | Thakurgaon | 92 | 19:30
15 | Barguna | 16 | 00:00 | Feni | 109 | 19:30 | Madanganj | 22 | 10:00 | Purbasadipur | 121 | 19:30 | Tongi | 90 | 15:00
16 | Barishal | 80 | 15:00 | GPH | 76 | 20:00 | Madaripur | 89 | 23:00 | Rahanpur_I | 0 | 00:00 | Ullon | 35 | 22:00
17 | Barishal-230 | 70 | 15:00 | Ghorashal | 68 | 19:30 | Madartek | 68 | 23:00 | Rahim | 0 | 00:00 | Uttara | 54 | 19:30
18 | Baroaulia | 59 | 00:00 | Goalpara | 36 | 13:00 | Madunaghat | 47 | 19:00 | Rajbari | 58 | 19:30 | UttaraNew | 40 | 22:00
19 | Baroirhat | 58 | 19:30 | Gollamari | 43 | 13:00 | Magura | 52 | 19:00 | Rajendrapur | 92 | 19:30 | Zigatola | 58 | 20:00
20 | Bashundhara | 126 | 19:00 | Gopalganj | 77.4 | 22:00 | Mahasthangarh | 74 | 19:30 | Rajshahi | 138 | 23:00
21 | BashundharaCement | 0 | 00:00 | Gulshan | 80 | 19:30 | Manikganj | 100 | 21:00 | Rajshahi-230 | 33 | 23:00
22 | Beanibazar | 63 | 19:00 | Halishahar | 66.5 | 22:00 | Maniknagar | 60 | 20:00 | Ramganj | 100 | 19:30
23 | Benapole | 48 | 19:00 | HaripurSBU | 78 | 19:00 | Matarbari | 46 | 20:00 | Rampur | 28 | 23:00
24 | Bhaluka | 122 | 15:00 | Hasnabad | 58 | 17:00 | Matuail | 36 | 22:00 | Rangamati | 16 | 19:30
25 | Bhandaria | 35 | 14:00 | Hathazari | 70 | 23:00 | Millgate | 56 | 23:00 | Rangpur | 127 | 19:00
26 | Bhangura | 37 | 19:30 | Ishurdi | 60 | 21:00 | Mirpur | 105 | 19:30 | Ruppur | 4.4 | 11:00
27 | Bheramara(GK) | 55 | 19:30 | Jaldhaka | 70 | 19:00 | Mirsorai | 2 | 00:00 | SSM | 0 | 00:00
28 | Bhulta | 158 | 23:00 | Jamalpur | 169 | 22:00 | Mithapukur | 40 | 18:30 | Saidpur | 103 | 20:00
29 | Bog-Sherpur | 58 | 19:30 | Jashore | 110 | 21:00 | Modern | 0 | 00:00 | Satkhira | 91 | 15:00
30 | Bogura | 159 | 23:00 | Jhenaidah | 114 | 19:30 | Mogbazar | 78 | 20:00 | Satmasjid | 93 | 19:00
31 | Borhanuddin | 48 | 01:00 | Joydebpur | 112 | 21:00 | Mongla | 26 | 11:00 | Savar | 118 | 22:00
32 | Brahmanbaria | 142 | 19:30 | Joypurhat | 65 | 21:00 | Motijheel | 27 | 19:00 | Shahjadpur | 106 | 21:00
33 | Cantonment | 109 | 19:30 | Juldah | 20 | 21:00 | Munshiganj | 101 | 21:00 | Shahjibazar | 113 | 21:00
34 | Chandpur | 65 | 22:00 | KSRM | 32 | 12:00 | Mymensingh | 182 | 19:00 | Shahmirpur | 33 | 23:00
35 | Chandraghona | 30 | 21:00 | Kabirpur | 171 | 21:00 | Naogaon | 124 | 21:00 | Shariatpur | 68 | 21:00
36 | Chapai | 66 | 19:30 | Kachua | 71 | 21:00 | Narail | 41 | 22:00 | Sherpur | 152 | 22:00
37 | Charsaidpur | 32 | 20:00 | Kallyanpur | 84 | 19:00 | Narinda | 36 | 19:00 | Shikalbaha | 35 | 00:00
38 | Chauddagram | 65 | 20:00 | Kalurghat | 24 | 00:00 | Narshingdi | 138 | 21:00 | Shikalbaha-230 | N/A | N/A
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2023-04-28 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 415 | 06:00 | 404 | 13:00 | Kaliakoir | N/A | N/A | N/A | N/A
| Bhulta | 397 | 19:00 | 389 | 13:00 | Madunaghat_I | 406 | 18:00 | 382 | 00:00
| Bibiana | 408 | 04:00 | 401 | 12:00 | Payra | 419 | 11:00 | 413 | 03:00
| BIPTC | 403 | 04:00 | 53 | 18:00 | Rahanpur_I | 414 | 02:00 | 408 | 12:00
| Gopalganj | 417 | 06:00 | 392 | 12:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 238 | 04:00 | 230 | 13:00 | Hathazari | 233 | 18:00 | 221 | 10:00
| AKSML | 233 | 18:00 | 212 | 08:00 | Ishurdi | 235 | 17:00 | 226 | 10:00
| Aminbazar | 240 | 04:00 | 232 | 12:00 | Jhenaidah | 232 | 18:00 | 220 | 13:00
| Ashuganj | 240 | 06:00 | 235 | 13:00 | Kaliakoir | N/A | N/A | N/A | N/A
| Baghabari | 231 | 00:00 | 224 | 12:00 | Keranigonj | 237 | 04:00 | 230 | 13:00
| Barapukuria | 218 | 05:00 | 203 | 19:00 | Khulna(S) | 238 | 18:00 | 223 | 13:00
| Barishal | 236 | 18:30 | 222 | 12:00 | Madunaghat_I | 235 | 19:30 | 221 | 06:00
| Bheramara | 233 | 18:00 | 223 | 10:00 | Maniknagar | 238 | 19:30 | 232 | 12:00
| Bhulta | 238 | 03:00 | 233 | 13:00 | Meghnaghat | 241 | 03:00 | 238 | 12:00
| Bibiana | 241 | 18:00 | 236 | 12:00 | Mirsorai | 238 | 19:00 | 228 | 11:00
| BIPTC | 234 | 17:00 | 223 | 10:00 | Rajshahi | 232 | 17:00 | 222 | 10:00
| Bogura | 222 | 05:00 | 215 | 19:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 236 | 18:30 | 227 | 00:00 | Rampura | 237 | 04:00 | 232 | 11:00
| BSRM | 238 | 18:00 | 228 | 05:00 | Shikalbaha | 231 | 19:30 | 220 | 06:00
| Cumilla(N) | 237 | 18:00 | 229 | 13:00 | Shyampur | 237 | 04:00 | 233 | 13:00
| Fenchuganj | 243 | 06:00 | 237 | 13:00 | Siddhirganj | 240 | 02:00 | 234 | 13:00
| Ghorashal | N/A | N/A | N/A | N/A | Sirajgonj | 237 | 00:00 | 233 | 10:00
| GPH | 235 | 18:00 | 222 | 05:00 | Sreepur | 237 | 18:00 | 233 | 13:00
| Haripur | 236 | 04:00 | 234 | 11:00 | Tongi | 234 | 17:00 | 227 | 13:00
| Hasnabad | 239 | 18:00 | 234 | 13:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 138 | 04:00 | 134 | 13:00 | Lalbag | 133 | 04:00 | 128 | 13:00
| Agargaon | 138 | 04:00 | 133 | 13:00 | Lalmonirhat | 129 | 23:00 | 120 | 19:00
| Agrabad | 137 | 18:00 | 127 | 09:00 | Madanganj | 138 | 19:30 | 133 | 13:00
| AKS | 134 | 18:30 | 127 | 00:00 | Madaripur | 135 | 17:00 | 128 | 12:00
| Aminbazar | 134 | 03:00 | 132 | 00:00 | Madartek | 137 | 04:00 | 132 | 13:00
| Amnura | 132 | 17:00 | 127 | 09:00 | Madunaghat | 138 | 19:00 | 128 | 00:00
| Ashuganj | 140 | 00:00 | 137 | 13:00 | Magura | 134 | 03:00 | 123 | 13:00
| Bagerhat | 139 | 18:00 | 124 | 13:00 | Mahasthangarh | 130 | 05:00 | 124 | 10:00
| Bakulia | 137 | 18:00 | 128 | 05:00 | Manikganj | 137 | 21:00 | 127 | 15:00
| Banani | 138 | 04:00 | 133 | 13:00 | Maniknagar | 139 | 03:00 | 135 | 13:00
| Bangabhaban | 139 | 06:00 | 135 | 13:00 | Matarbari | 122 | 17:00 | 108 | 00:00
| Barapukuria | 134 | 04:00 | 125 | 19:00 | Matuail | 138 | 04:00 | 134 | 13:00
| Barguna | 141 | 18:00 | 131 | 13:00 | Millgate | 137 | 03:00 | 131 | 13:00
| Barishal | 141 | 18:00 | 124 | 12:00 | Mirpur | 134 | 06:00 | 34 | 20:00
| Barishal-230 | 135 | 17:00 | 124 | 12:00 | Mithapukur | 130 | 23:00 | 122 | 10:00
| Baroaulia | 137 | 19:00 | 128 | 10:00 | Modern | 137 | 19:00 | 129 | 00:00
| Baroirhat | 137 | 00:00 | 125 | 13:00 | Mogbazar | 139 | 06:00 | 135 | 12:00
| Bashundhara | 137 | 03:00 | 130 | 12:00 | Mongla | 138 | 18:00 | 123 | 13:00
| BashundharaCement | 138 | 19:30 | 133 | 13:00 | Motijheel | 139 | 06:00 | 135 | 13:00
| Beanibazar | 136 | 04:00 | 127 | 23:00 | Munshiganj | 138 | 19:00 | 133 | 13:00
| Benapole | 135 | 18:00 | 121 | 13:00 | Mymensingh | 127 | 02:00 | 115 | 13:00
| Bhaluka | 124 | 03:00 | 112 | 13:00 | Naogaon | 127 | 05:00 | 119 | 12:00
| Bhandaria | 142 | 18:00 | 126 | 13:00 | Narail | 132 | 00:00 | 122 | 13:00
| Bhangura | 136 | 00:00 | 131 | 13:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bheramara | 134 | 00:00 | 127 | 13:00 | Narshingdi | 137 | 19:30 | 130 | 13:00
| Bheramara(GK) | 136 | 00:00 | 128 | 10:00 | Natore | 131 | 18:00 | 126 | 02:00
| Bhulta | 131 | 00:00 | 129 | 12:00 | Nawabganj | 133 | 04:00 | 127 | 13:00
| Bog-Sherpur | 132 | 04:00 | 128 | 08:00 | Netrakona | 126 | 02:00 | 115 | 06:00
| Bogura | 132 | 18:00 | 127 | 10:00 | New | 138 | 05:00 | 133 | 13:00
| Bogura-230 | 132 | 18:00 | 127 | 10:00 | Niamatpur | 125 | 05:00 | 115 | 19:00
| Brahmanbaria | 136 | 06:00 | 132 | 13:00 | Noapara | 137 | 18:00 | 126 | 12:00
| Cantonment | 137 | 04:00 | 132 | 13:00 | Pabna | 134 | 00:00 | 128 | 13:00
| Chandpur | 140 | 18:00 | 124 | 11:00 | Palashbari | 126 | 18:30 | 120 | 08:00
| Chandraghona | 136 | 18:00 | 129 | 01:00 | Panchagarh | 136 | 23:00 | 113 | 11:00
| Chapai | 132 | 00:00 | 127 | 12:00 | Patuakhali | 140 | 17:00 | 130 | 01:00
| Charsaidpur | 138 | 19:30 | 134 | 13:00 | Payra | 141 | 18:00 | 136 | 12:00
| Chauddagram | 135 | 18:00 | 127 | 10:00 | PHP | 135 | 01:00 | 125 | 10:00
| Chhatak | 135 | 06:00 | 127 | 23:00 | Postogola | 138 | 19:30 | 133 | 13:00
| Chowmuhani | 134 | 19:00 | 123 | 10:00 | Purbachal | 138 | 04:00 | 130 | 13:00
| Chuadanga | 130 | 00:00 | 116 | 13:00 | Purbasadipur | 132 | 18:30 | 117 | 11:00
| Coxsbazar | 123 | 18:00 | 107 | 00:00 | Rahim | 138 | 04:00 | 132 | 12:00
| Cumilla(N) | 139 | 19:30 | 132 | 13:00 | Rajbari | 133 | 00:00 | 126 | 13:00
| Cumilla(S) | 138 | 19:00 | 122 | 19:00 | Rajendrapur | 138 | 23:00 | 127 | 13:00
| Daudkandi | 137 | 07:00 | 130 | 23:00 | Rajshahi | 131 | 18:00 | 125 | 10:00
| Dhaka | 138 | 03:00 | 133 | 13:00 | Rajshahi-230 | 132 | 18:00 | 125 | 10:00
| Dhamrai | 134 | 04:00 | 127 | 13:00 | Ramganj | 136 | 18:00 | 124 | 10:00
| Dhanmondi | 138.5 | 19:30 | 135 | 13:00 | Rampur | 136 | 18:00 | 128 | 01:00
| Dohazari | 134 | 18:00 | 124 | 13:00 | Rampura | 137 | 00:00 | 134 | 12:00
| Faridpur | 134 | 06:00 | 127 | 21:00 | Rangamati | 136 | 18:00 | 128 | 10:00
| Fatullah | 138 | 06:00 | 134 | 13:00 | Rangpur | 129 | 23:00 | 120 | 19:00
| Fenchuganj | 139 | 06:00 | 134 | 18:30 | Ruppur | 134 | 00:00 | 129 | 10:00
| Feni | 134 | 19:00 | 126 | 13:00 | Saidpur | 131 | 04:00 | 120 | 10:00
| Ghorashal | 143 | 00:00 | 139 | 01:00 | Satkhira | 137 | 18:00 | 122 | 13:00
| Goalpara | 140 | 18:00 | 128 | 13:00 | Satmasjid | 137 | 03:00 | 132 | 13:00
| Gollamari | 134 | 18:00 | 127 | 12:00 | Savar | 134 | 18:00 | 129 | 13:00
| Gopalganj | 134 | 18:00 | 126 | 13:00 | Shahjadpur | 137 | 00:00 | 134 | 07:00
| Gopalganj-400 | 136 | 17:00 | 129 | 12:00 | Shahjibazar | 136 | 04:00 | 133 | 13:00
| Gulshan | 137 | 04:00 | 133 | 13:00 | Shahmirpur | 137 | 18:00 | 128 | 00:00
| Halishahar | 138 | 18:00 | 128 | 00:00 | Shariatpur | 135 | 18:00 | 127 | 22:00
| Haripur | 138 | 04:00 | 137 | 00:00 | Sherpur | 127 | 20:00 | 108 | 06:00
| HaripurSBU | 138 | 04:00 | 137 | 00:00 | Shikalbaha | 139 | 19:30 | 128 | 13:00
| Hasnabad | 137 | 19:00 | 135 | 10:00 | Shikalbaha-230 | 137 | 19:30 | 129 | 01:00
| Hathazari | 137 | 18:00 | 129 | 10:00 | Shitalakhya | 138 | 19:30 | 133 | 13:00
| Ishurdi | 135 | 00:00 | 129 | 10:00 | Sholosohor | 137 | 18:00 | 127 | 05:00
| Jaldhaka | 129 | 18:30 | 118 | 11:00 | Shyampur | 138 | 03:00 | 135 | 15:00
| Jamalpur | 131 | 19:00 | 111 | 10:00 | Shyampur-230 | 138 | 18:00 | 134 | 13:00
| Jashore | 135 | 18:00 | 122 | 13:00 | Siddhirganj | 138 | 18:00 | 134 | 13:00
| Jhenaidah | 136 | 04:00 | 123 | 13:00 | Sirajganj | 136 | 04:00 | 128 | 19:00
| Jhenaidah-230 | 135 | 18:00 | 124 | 13:00 | Sonargaon | 137 | 00:00 | 133 | 11:00
| Joydebpur | 142 | 18:00 | 135 | 13:00 | Sreemongol | 135 | 00:00 | 131 | 23:00
| Joypurhat | 125 | 18:00 | 117 | 19:00 | Sreepur | 134 | 06:00 | 131 | 13:00
| Juldah | 137 | 19:00 | 129 | 00:00 | Srinagar | 133 | 04:00 | 127 | 13:00
| Kabirpur | 138 | 21:00 | 129 | 13:00 | SSM | 142 | 18:00 | 130 | 02:00
| Kachua | 138 | 18:00 | 126 | 11:00 | Sunamganj | 134 | 01:00 | 124 | 23:00
| Kaliakoir | N/A | N/A | N/A | N/A | Sylhet | 135 | 00:00 | 130 | 23:00
| Kallyanpur | 134 | 04:00 | 132 | 10:00 | Tangail | 132 | 02:00 | 122 | 13:00
| Kalurghat | 136 | 19:30 | 128 | 13:00 | Thakurgaon | 135 | 23:00 | 113 | 11:00
| Kamrangirchar | 133 | 04:00 | 128 | 13:00 | TK | 131 | 07:00 | 129 | 00:00
| Kaptai | 135 | 16:00 | 130 | 00:00 | Tongi | 138 | 07:00 | 134 | 13:00
| Kazla | 139 | 04:00 | 135 | 14:00 | Ullon | 140 | 04:00 | 133 | 13:00
| Keranigonj | 133 | 08:00 | 128 | 13:00 | Uttara | 134 | 19:30 | 129 | 13:00
| Khagrachori | 135 | 19:30 | 127 | 10:00 | UttaraNew | 134 | 05:00 | 129 | 13:00
| Khulna | 138 | 18:00 | 127 | 13:00 | Zigatola | 133 | 04:00 | 128 | 13:00
| Khulna(S) | 140 | 18:00 | 129 | 13:00
| Khulshi | 135 | 18:00 | 126 | 10:00
| Kishoreganj | 130 | 01:00 | 123 | 13:00
| Kodda | 141 | 19:00 | 127 | 13:00
| KSRM | 136 | 18:00 | 128 | 00:00
| Kulaura | 137 | 06:00 | 133 | 19:00
| Kurigram | 128 | 23:00 | 119 | 18:30
| Kushtia | 135 | 02:00 | 126 | 13:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2023-04-28
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 58 | 7267 | 4106 | 11373 |  |  |  | QF-LDC-11
0:30 | 187 | 6351 | 3684.5 | 10035.5 | Date: | 2023-04-28
1:00 | 316 | 5435 | 3263 | 8698
1:30 | 293 | 5429 | 3187.5 | 8616.5
2:00 | 270 | 5423 | 3112 | 8535
2:30 | 239 | 5358.5 | 3003 | 8361.5 | [5 empty] | Gen. at Eve. Peak | 12006 | 12006 MW (21:00 )
3:00 | 208 | 5294 | 2894 | 8188 | [6 empty] | 21:00
3:30 | 158 | 5336.5 | 2837.5 | 8174 | [5 empty] | Gen. at Day Peak | 9539 | 9539 MW (12:00 )
4:00 | 108 | 5379 | 2781 | 8160 | [6 empty] | 12:00
4:30 | 101 | 5282 | 2724 | 8006 | [5 empty] | Highest Generation | 12006
5:00 | 94 | 5185 | 2667 | 7852 | [6 empty] | 21:00
5:30 | 114 | 5058 | 2648.5 | 7706.5
6:00 | 134 | 4931 | 2630 | 7561
6:30 | 135 | 4966.5 | 2669.5 | 7636
7:00 | 136 | 5002 | 2709 | 7711
7:30 | 150 | 5084 | 2775.5 | 7859.5
8:00 | 164 | 5166 | 2842 | 8008
8:30 | 140 | 5276.5 | 2875 | 8151.5
9:00 | 116 | 5387 | 2908 | 8295
9:30 | 173 | 5402 | 2988.5 | 8390.5
10:00 | 230 | 5417 | 3069 | 8486
10:30 | 220 | 5494.5 | 3249.5 | 8744
11:00 | 210 | 5572 | 3430 | 9002
11:30 | 243 | 5641 | 3629.5 | 9270.5
12:00 | 276 | 5710 | 3829 | 9539
12:30 | 323 | 5944.5 | 3995.5 | 9940
13:00 | 370 | 6179 | 4162 | 10341
13:30 | 414 | 6185 | 4102.5 | 10287.5
14:00 | 458 | 6191 | 4043 | 10234
14:30 | 509 | 6263.5 | 4037 | 10300.5
15:00 | 560 | 6336 | 4031 | 10367
15:30 | 645 | 6201.5 | 4021.5 | 10223
16:00 | 730 | 6067 | 4012 | 10079
16:30 | 700 | 6034 | 3912 | 9946
17:00 | 670 | 6001 | 3812 | 9813
17:30 | 605 | 5960 | 3687 | 9647
18:00 | 540 | 5919 | 3562 | 9481
18:30 | 287 | 6565.5 | 3660.5 | 10226
19:00 | 34 | 7212 | 3759 | 10971
19:30 | 130 | 7754 | 3936 | 11690
20:00 | 150 | 7780 | 4017 | 11797 |  |  |  | Executive Engineer
20:30 | 150 | 7861.5 | 4040 | 11901.5 |  |  |  | Network Operation Division
21:00 | 150 | 7943 | 4063 | 12006
21:30 | 130 | 7854.5 | 4043 | 11897.5
22:00 | 110 | 7766 | 4023 | 11789 |  |  |  |  | Page 6 of 7
22:30 | 100 | 7728.5 | 4069.5 | 11798
23:00 | 90 | 7691 | 4116 | 11807
23:30 | 74 | 7479 | 4111 | 11590
24:00 | 58 | 7267 | 4106 | 11373
12006 MW (21:00 )
9539 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2023-04-28 |  | Energy |  | 233511473
[13 empty] | 2023-04-28 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 4600 | 493 | 2282 | 0 | 1682 | 1802 | 0 | 0 | 366 | 148 | 0 | 0
0:30 | 4176 | 494 | 2273.5 | 0 | 1062 | 1649.5 | 0 | 0 | 264.5 | 116 | 0 | 0 |  | Date: | 43582
1:00 | 3752 | 495 | 2265 | 0 | 442 | 1497 | 0 | 0 | 163 | 84 | 0 | 0
1:30 | 3787 | 495.5 | 2248.5 | 0 | 400.5 | 1440 | 0 | 0 | 163 | 82 | 0 | 0 | [8 empty] | Total Energy | 233.5115 |  | Total Energy Gen MKWHr Energy Not Served MKWHr Energy Requirement MKWHr | Total Energy Gen 233.511 MKWHr Energy Not Served 0.880 MKWHr Energy Requirement 234.392 MKWHr
2:00 | 3822 | 496 | 2232 | 0 | 359 | 1383 | 0 | 0 | 163 | 80 | 0 | 0 | [8 empty] | Energy not Served | 0.88022
2:30 | 3573.5 | 495.5 | 2233 | 0 | 359 | 1455.5 | 0 | 0 | 163 | 82 | 0 | 0 | [8 empty] | Energy Requirement | 234.3917
3:00 | 3325 | 495 | 2234 | 0 | 359 | 1528 | 0 | 0 | 163 | 84 | 0 | 0
3:30 | 3367 | 495.5 | 2175 | 0 | 359.5 | 1532 | 0 | 0 | 163 | 82 | 0 | 0 | [7 empty] | Shortage
4:00 | 3409 | 496 | 2116 | 0 | 360 | 1536 | 0 | 0 | 163 | 80 | 0 | 0
4:30 | 3395 | 496 | 2138.5 | 0 | 264 | 1472.5 | 0 | 0 | 163 | 77 | 0 | 0
5:00 | 3381 | 496 | 2161 | 0 | 168 | 1409 | 0 | 0 | 163 | 74 | 0 | 0
5:30 | 3364.5 | 495.5 | 2068.5 | 0 | 150.5 | 1383 | 0 | 0 | 163 | 73 | 8.5 | 0
6:00 | 3348 | 495 | 1976 | 0 | 133 | 1357 | 0 | 0 | 163 | 72 | 17 | 0
6:30 | 3349.5 | 495 | 2005 | 0 | 148 | 1352.5 | 0 | 0 | 163 | 72 | 51 | 0 | [6 empty] | Coal
7:00 | 3351 | 495 | 2034 | 0 | 163 | 1348 | 0 | 0 | 163 | 72 | 85 | 0
7:30 | 3354 | 495 | 2113 | 0 | 179 | 1352 | 0 | 0 | 163 | 73 | 130.5 | 0 | [5 empty] | Oil
8:00 | 3357 | 495 | 2192 | 0 | 195 | 1356 | 0 | 0 | 163 | 74 | 176 | 0
8:30 | 3396.5 | 495.5 | 2238 | 0 | 195 | 1354 | 0 | 0 | 179 | 77 | 216.5 | 0
9:00 | 3436 | 496 | 2284 | 0 | 195 | 1352 | 0 | 0 | 195 | 80 | 257 | 0
9:30 | 3484 | 496 | 2269 | 0 | 204 | 1364.5 | 0 | 14 | 203 | 76 | 280 | 0
10:00 | 3532 | 496 | 2254 | 0 | 213 | 1377 | 0 | 28 | 211 | 72 | 303 | 0
10:30 | 3536 | 496 | 2284 | 0 | 274 | 1468 | 12.5 | 65 | 203 | 78 | 327.5 | 0
11:00 | 3540 | 496 | 2314 | 0 | 335 | 1559 | 25 | 102 | 195 | 84 | 352 | 0
11:30 | 3666.5 | 496.5 | 2286.5 | 0 | 431.5 | 1641 | 25 | 127 | 179 | 86 | 331.5 | 0
12:00 | 3793 | 497 | 2259 | 0 | 528 | 1723 | 25 | 152 | 163 | 88 | 311 | 0
12:30 | 3945 | 496.5 | 2299 | 0 | 653 | 1800 | 25 | 152 | 163 | 94 | 312.5 | 0
13:00 | 4097 | 496 | 2339 | 0 | 778 | 1877 | 25 | 152 | 163 | 100 | 314 | 0
13:30 | 4097 | 496 | 2339 | 0 | 778 | 1877 | 25 | 152 | 163 | 100 | 314 | 0
14:00 | 4097 | 496 | 2339 | 0 | 778 | 1877 | 25 | 152 | 163 | 100 | 314 | 0
14:30 | 4006.5 | 495.5 | 2212.5 | 0 | 1008 | 1908.5 | 25 | 178.5 | 163 | 101 | 255.5 | 0
15:00 | 3916 | 495 | 2086 | 0 | 1238 | 1940 | 25 | 205 | 163 | 102 | 197 | 0
15:30 | 3862.5 | 494.5 | 2060 | 0 | 1163.5 | 1937 | 25 | 258.5 | 163 | 103 | 156 | 22.4425
16:00 | 3809 | 494 | 2034 | 0 | 1089 | 1934 | 25 | 312 | 163 | 104 | 115 | 44.885
16:30 | 3798 | 493.5 | 1983.5 | 0 | 1101 | 1935 | 25 | 261 | 163 | 101 | 85 | 51.0925
17:00 | 3787 | 493 | 1933 | 0 | 1113 | 1936 | 25 | 210 | 163 | 98 | 55 | 57.3 | [10 empty] | 472
17:30 | 3703.5 | 492.5 | 1871.5 | 0 | 1205 | 1929.5 | 25 | 125 | 163 | 98 | 34 | 62.075 | [10 empty] | 100
18:00 | 3620 | 492 | 1810 | 0 | 1297 | 1923 | 25 | 40 | 163 | 98 | 13 | 66.85 | [10 empty] | 20
18:30 | 3872.5 | 492 | 2035 | 0 | 1631.5 | 1768.5 | 25 | 50 | 226 | 119 | 6.5 | 106.4825 | [10 empty] | 592
19:00 | 4125 | 492 | 2260 | 0 | 1966 | 1614 | 25 | 60 | 289 | 140 | 0 | 146.115
19:30 | 4343 | 493 | 2232 | 0 | 2462 | 1701 | 25 | 0 | 292 | 142 | 0 | 144.6825
20:00 | 4450 | 493 | 2245 | 0 | 2412 | 1706 | 25 | 0 | 326 | 140 | 0 | 143.25
20:30 | 4530.5 | 493 | 2244.5 | 0 | 2398.5 | 1708 | 25 | 0 | 360 | 142 | 0 | 118.125
21:00 | 4611 | 493 | 2244 | 0 | 2385 | 1710 | 25 | 0 | 394 | 144 | 0 | 93
21:30 | 4570 | 493 | 2235.5 | 0 | 2347 | 1710.5 | 25 | 0 | 370.5 | 146 | 0 | 71.5
22:00 | 4529 | 493 | 2227 | 0 | 2309 | 1711 | 25 | 0 | 347 | 148 | 0 | 50
22:30 | 4559.5 | 493 | 2236 | 0 | 2294 | 1709 | 12.5 | 0 | 347 | 147 | 0 | 71
23:00 | 4590 | 493 | 2245 | 0 | 2279 | 1707 | 0 | 0 | 347 | 146 | 0 | 92
23:30 | 4595 | 493 | 2263.5 | 0 | 1980.5 | 1754.5 | 0 | 0 | 356.5 | 147 | 0 | 195 |  | Max Temp. in Dhaka |  | 34.8° C
24:00 | 4600 | 493 | 2282 | 0 | 1682 | 1802 | 0 | 0 | 366 | 148 | 0 | 298
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 233.511 MKWHr Energy Not Served 0.880 MKWHr Energy Requirement 234.392 MKWHr
Shortage
Note on W13: Author:

## Generation
g | 2023-04-28
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3
2 | Karnaphuli Hydro PP Unit-4 & 5 | [10 empty] | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 0 |  | 300000
3 | Chattogram TPP-1 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2900000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [25 empty] | 4 | 3447
| Teknaf 20MW PP (Solartech) |  |  |  |  | 0 | 1 | 4 | 9 | 13 | 16 | 18 | 19 | 18 | 16 | 11 | 8 | 3 | 0 | [8 empty] | 137430
6 | Sikalbaha 225MW CCPP (Gas) | 228 | 228 | 227 | 227 | 229 | 228 | 228 | 228 | 227 | 226 | 220 | 224 | 219 | 219 | 219 | 224 | 223 | 225 |  | 225 | 225 | 225 | 226 | 225 | 227 | 227 | 5317542
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [19 empty] | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 195653
12 | Hathazari 100 MW peaking PP | [26 empty] | 0
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 17 | 17 | 17 | 17 | [8 empty] | 1 | 16 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 273490
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | [25 empty] | 19 | 11728
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 40 | 40 | 70 | 40 | 40 | 40 | 40 | 40 | 100 | 99 | 98 | 99 | 97 | 96 | 96 | 77 | 59 | 40 |  | 100 | 99 | 100 | 100 | 70 | 66 | 66 | 1850000
17 | Siddhirganj 335 MW CCPP | 150 | 150 | 0 | 80 | 80 | 80 | 0 | [5 empty] | 45 | 214 | 210 | 170 | 170 | 140 |  | 217 | 219 | 220 | 220 | 218 | 218 | 220 | 2793456
18 | Kodda 300 MW PP Unit-2 (Summit) | [17 empty] | 8 |  | 15 | 15 | [5 empty] | 55200
19 | Ashuganj 195MW PP (APSCL-United) | 45 | 45 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 120 | 157 | 157 | 112 | 110 | 112 | 118 | 118 |  | 118 | 118 | 118 | 118 | 118 | 118 | 153 | 2325090
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4 | [12 empty] | 26 | 120 | 121 | 120 | 120 | 120 |  | 200 | 200 | 200 | 220 | 220 | 220 | 220 | 1734781
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4315500
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 44 | 42 | 42 | 41 | 40 | 40 | 36 | 37 | 38 | 39 | 36 |  | 41 | 41 | 41 | 41 | 42 | 42 | 43 | 1003104
33 | Ashuganj 225 MW CCPP | 212 | 212 | 215 | 216 | 216 | 216 | 214 | 212 | 210 | 209 | 208 | 210 | 205 | 206 | 204 | 207 | 207 | 180 |  | 208 | 208 | 211 | 211 | 211 | 211 | 211 | 5088000
34 | Ashuganj 450 MW CCPP(South) | 270 | 280 | 295 | 305 | 305 | 305 | 325 | 310 | 320 | 340 | 310 | 310 | 325 | 280 | 290 | 275 | 280 | 280 |  | 305 | 300 | 300 | 300 | 300 | 300 | 300 | 7354000
| Ashuganj 450 MW CCPP(North) | 315 | 330 | 310 | 310 | 310 | 310 | 335 | 325 | 325 | 345 | 320 | 310 | 330 | 285 | 310 | 280 | 280 | 280 |  | 300 | 310 | 310 | 310 | 310 | 310 | 310 | 7800000
Ashuganj 420 MW CCPP(East)
35 | Ashuganj 55 MW PP (Precision)
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 395 | 395 | 396 | 390 | 348 | 350 | 358 | 396 | 401 | 400 | 402 | 403 | 400 | 403 | 402 | 397 | 365 | 320 |  | 348 | 398 | 393 | 393 | 393 | 395 | 394 | 9383940
40 | Meghnaghat 450 MW CCPP(MPL) | 450 | 450 | 450 | 450 | 450 | 350 | 350 | 400 | 450 | 450 | 450 | 450 | 450 | 380 | 380 | 380 | 320 | 320 |  | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 9847500
41 | Haripur 360MW CCPP(HPL) | 343 | 343 | 345 | 343 | 344 | 303 | 302 | 303 | 345 | 329 | 329 | 328 | 328 | 328 | 329 | 329 | 289 | 259 |  | 348 | 348 | 344 | 334 | 331 | 339 | 339 | 7842000
42 | RPCL 210MW CCPP | 162 | 164 | 166 | 166 | 166 | 166 | 163 | 162 | 160 | 157 | 157 | 157 | 153 | 153 | 152 | 156 | 153 | 156 |  | 154 | 158 | 159 | 160 | 160 | 161 | 162 | 3741120
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 2 | 12 | 26 | 21 | 45 | 51 | 40 | 46 | 44 | 32 | 11 | 5 | 1 | [8 empty] | 357190
44 | Fenchugonj CCPP Phase-1 | 31 | 31 | 31 | 31 | 31 | 31 | 33 | 33 | 32 | 10 | 0 | [15 empty] | 306000
45 | Fenchugonj CCPP Phase-2 | 29 | 29 | 29 | 29 | 30 | 30 | 30 | 30 | 30 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 |  | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 656520
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 62 | 62 | 62 | 62 | 62 | 62 | 61 | 61 | 61 | 60 | 60 | 60 | 59 | 59 | 59 | 60 | 60 | 61 |  | 60 | 60 | 61 | 62 | 61 | 62 | 62 | 1462560
48 | Shahjibazar 86MW PP (Shahjibazar) | 81 | 81 | 81 | 81 | 81 | 40 | 40 | 80 | 80 | 80 | 80 | 80 | 80 | 79 | 79 | 79 | 79 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1828800
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 80 | 100 | 120 | 120 | 120 | 120 | 120 | 120 | 130 | 130 | 130 | 130 | 132 | 132 | 130 | 130 | 130 | 132 |  | 133 | 133 | 133 | 133 | 133 | 133 | 133 | 2945490
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 17 | 17 | 17 | 16 | 16 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 18 | 17 | 18 | 18 | 401000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 9 | 9 | 10 | 10 | 10 | 8 | 9 | 9 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 239220
54 | Hobiganj 11MW PP Cofidence-E | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 192384
55 | Fenchugonj 51 MW PP (Barakatullah) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 22 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 1222200
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384288
57 | Bibiana-II 341 MW CCPP (Summit) | 280 | 290 | 290 | 275 | 290 | 275 | 300 | 300 | 305 | 310 | 305 | 280 | 300 | 290 | 290 | 270 | 290 | 260 |  | 300 | 265 | 260 | 285 | 265 | 270 | 270 | 7012000
| Bibiyana South 400 MW |  |  | 0 | 45 | 70 | 70 | 70 | 76 | 50 | 60 | 66 | 120 | 256 | 160 | 15 | 35 | 65 | 124 |  | 138 | 192 | 265 | 400 | 400 | 400 | 400 | 3095500
58 | Nababganj 55 MW PP (Southern power ) | [19 empty] | 3 | 17 | 17 | 17 |  |  |  | 48065
59 | Tangail Palli Power Gen 22 MW | 6 | [7 empty] | 1 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 7 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 151920
60 | Barabkunda 22 MW PP (Regent) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 280896
61 | Narshingdi 22 MW PP (Doreen) | [7 empty] | 6 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  |  |  | 10 | 10 | 10 | 10 |  |  | 130968
62 | Tangail 22 MW PP (Doreen) | 0 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 400144
63 | Impoprt (Tripura) | 84 | 80 | 84 | 80 | 74 | 72 | 72 | 74 | 80 | 72 | 84 | 88 | 100 | 102 | 102 | 104 | 98 | 98 |  | 140 | 142 | 140 | 144 | 148 | 146 | 148 | 2336640
64 | Malancha, Ctg. EPZ (United) | 39 | 40 | 40 | 40 | 40 | 40 | 40 | 39 | 34 | 27 | 33 | 33 | 35 | 27 | 33 | 33 | 32 | 38 |  | 38 | 38 | 38 | 38 | 39 | 39 | 40 | 904320
65 | Feni 22MW PP (Doreen) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 16 | 16 | 17 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 418356
66 | Feni 11 MW PP (Doreen) | [10 empty] | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 90720
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 31 | 28 | 25 | 25 | 25 | 25 | 25 | 769800
68 | Cumilla 25 MW PP (Summit) | 15 | 15 | 15 | 15 | 15 | 15 | 18 | 18 | 18 | 18 | 18 | 19 | 19 | 19 | 19 | 19 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 15 | 15 | 422860
69 | Summit Ashulia | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 |  | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 552000
70 | Summit Madhabdi | 16 | 16 | 16 | 16 | 14 | 15 | 15 | 15 | 15 | 15 | 13 | 13 | 13 | 13 | 13 | 14 | 14 | 14 |  | 14 | 20 | 20 | 20 | 20 | 20 | 24 | 371880
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 617000
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 32 | 32 | 32 | 32 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 32 | 783400
73 | Ghorashal 108MW PP (Regent) | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 74 | 74 | 75 | 75 | 75 | 75 | 74 | 74 | 75 | 74 |  | 77 | 77 | 78 | 78 | 78 | 78 | 78 | 1794000
| Feni Lanka Power | [12 empty] | 14 | 17 | [5 empty] | 17 | 17 | [5 empty] | 37620
| Chowmuhani 113 MW | 8 | [10 empty] | 7 | 9 | 9 | 9 | 9 | 9 | 55 |  | 113 | 113 | 113 | 113 | 114 | 62 | 36 | 609000
| Manikgonj 162MW PP(MPGL) | [11 empty] | 5 | 54 | 90 | 90 | 35 | 35 | 35 |  | 48 | 126 | 126 | 126 | 126 | 126 | 126 | 1064160
77 | Siddhirganj 100 PP(Dutch Bangla) | [19 empty] | 2 | 16 | 16 |  |  |  |  | 10560
78 | Gazipur 52 MW PP | [13 empty] | 2 | 16 | 16 | 16 | 16 |  | 16 | 30 | 41 | 41 | 41 | 41 | 16 | 256800
79 | Kodda 150 MW PP | [8 empty] | 32 | 48 | 32 | [8 empty] | 48 | 48 | 82 | 150 | 150 | 150 | 150 | 730224
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | [14 empty] | 4 | 8 | 16 | 16 |  | 18 | 38 | 43 | 43 | 43 | 43 | 43 | 276139
| Gazipur 100 MW PP | 52 | [12 empty] | 4 | 28 | 76 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 1062451
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 2 | 4 | 4 | 5 | 4 | 4 | 3 | 3 | 1 | 0 | [9 empty] | 30961
| Jodiac Power | [19 empty] | 4 | 17 | 17 | 17 | 17 | 17 | 17 | 96006
| Karnaphuli Power Ltd. | 17 | 17 | 17 | 17 | 17 | [6 empty] | 9 | 17 | 17 | 17 | 34 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 40 | 610542
82 | Madanganj 102 PP(Summit) | [20 empty] | 15 | 14 |  |  |  |  | 10930
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP ( Summit) | 321 | 319 | 280 | 284 | 287 | 298 | 314 | 312 | 313 | 301 | 306 | 285 | 299 | 280 | 289 | 282 | 270 | 263 |  | 289 | 277 | 288 | 275 | 280 | 285 | 285 | 7038167
87 | Meghnaghat 100 MW(IEL) | [13 empty] | 12 | 16 | 16 | 9 | 9 |  | 8 | 50 | 22 | 8 | 9 | 14 | 33 | 150720
| Meghnaghat 104 MW PP (OPCL) | [13 empty] | 28 | 34 | 32 | 17 | 17 |  | 24 | 35 | 37 | 17 | 17 | 22 | 63 | 313920
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [12 empty] | 10 | 10 | 55 | 10 | 10 | 10 |  | 67 | 77 | 78 | 78 | 66 | 66 | 55 | 480720
92 | Fenchuganj 44MW (Energyprima) | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 47 | 47 | 46 | 43 | 46 | 46 | 45 | 45 | 42 | 20 |  | 47 | 47 | 47 | 47 | 49 | 49 | 49 | 1114128
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 5 | 5 | 5 | 5 | 5 |  | 18 | 51 | 51 | 51 | 51 | 51 | 51 | 986034
94 | Gagnagar 102 MW PP (Digital Power) | [19 empty] | 24 | 16 | 8 | 8 |  |  |  | 39600
95 | Patenga 50MW PP (Baraka) | 6 | 6 | 6 | 6 | 2 | [6 empty] | 1 | 5 | 6 | 6 | 6 | 6 | 17 |  | 25 | 25 | 25 | 25 | 25 | 25 | 6 | 219360
96 | Chattogram 108 MW PP (ECPV) | [13 empty] | 1 | 21 | 40 | 49 | 50 |  | 50 | 45 | 20 | 12 | 12 | 8 | 3 | 272640
97 | katpotti 52 MW
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [19 empty] | 7 | 15 | 15 | 15 |  |  |  | 48454
100 | Manikganj 55 MW PP (Northern) | [13 empty] | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 185546
101 | Kushiara 163 MW CCPP (KP)
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 1 | 1 | 2 | 2 | 2 | 2 | 1 | 1 | 1 | 0 | 0 | [8 empty] | 13750
103 | Kamalaghat 54 MW PP(Banco Energy) | [16 empty] | 17 | 17 |  | 35 | 54 | 54 | 54 | 54 | 35 | 17 | 259920
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 48 | 48 | 48 | 48 | 24 | 8 | 22 | 47 | 46 | 46 | 111 | 144 | 144 | 144 | 144 | 117 | 117 | 124 |  | 173 | 173 | 173 | 173 | 173 | 173 | 49 | 2344800
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [9 empty] | 13 | 15 | 15 | 15 | 15 | 17 | 17 | 17 | 20 |  | 40 | 70 | 70 | 70 | 70 | 70 | 70 | 545616
115 | Juldah 100 MW PP Unit-3 (Acorn) | 38 | 38 | 38 | 38 | 20 | 20 | 20 | 20 | 20 | 20 | 22 | 38 | 38 | 38 | 38 | 38 | 38 | 50 |  | 76 | 76 | 76 | 76 | 76 | 76 | 63 | 1026240
116 | Chandpur 200MW (Desh energy) | 17 | 17 | 17 | 17 | [8 empty] | 4 | 78 | 148 | 100 | 91 | 104 |  | 127 | 150 | 150 | 150 | 150 | 150 | 17 | 1372320
117 | Ashuganj 150MW PP (Midland) | [17 empty] | 6 |  | 8 | 50 | 38 | 52 | 10 | 10 | 10 | 276000
118 | Bibiyana-III 400 MW CCPP | 414 | 414 | 400 | 401 | 402 | 365 | 374 | 367 | 397 | 376 | 382 | 369 | 376 | 318 | 400 | 369 | 369 | 319 |  | 366 | 415 | 416 | 415 | 367 | 367 | 367 | 9071000
| Jamalpur 115 MW PP (United) | 48 | 48 | 48 | 49 | 24 | 24 | 40 | 47 | 47 | 47 | 66 | 75 | 66 | 66 | 66 | 47 | 47 | 47 |  | 85 | 83 | 88 | 88 | 88 | 89 | 49 | 1398000
| Anwara 300 MW PP (United) | 88 | 88 | 88 | 88 | 30 | 30 | 30 | 30 | 30 | 30 | 80 | 80 | 100 | 100 | 122 | 123 | 123 | 123 |  | 160 | 200 | 200 | 200 | 200 | 200 | 87 | 2481491
| Juldah unit-2 (Acorn) | 12 | 12 | 12 | 12 | [7 empty] | 12 | 40 | 50 | 50 | 50 | 50 | 88 |  | 86 | 86 | 86 | 76 | 76 | 76 | 76 | 816000
| Anlima Energy Ltd. | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 |  | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 839291
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 16 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 25 | 35 | 35 | 469440
| Spectra Solar Plant Ltd. | [5 empty] | 1 | 7 | 15 | 23 | 30 | 29 | 33 | 33 | 26 | 21 | 6 | 3 | 1 | [8 empty] | 222898
| Chandpur 115(Doreen) | 17 | 17 | 17 | 17 | [6 empty] | 1 | 31 | 71 | 72 | 72 | 81 | 93 | 93 |  | 94 | 94 | 94 | 93 | 93 | 93 | 94 | 1153920
| Kanchan Purbachal Power Generation Ltd. | 17 | [10 empty] | 8 | 17 | 17 | 17 | 17 | 17 | 23 |  | 34 | 34 | 34 | 34 | 34 | 34 | 17 | 358200
| Mirsharai 150 MW (Oil) | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 |  | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 3919200
Mirsharai 150 MW (Gas)
120 | Eastern Zone Total | 5435 | 5423 | 5294 | 5379 | 5185 | 4931 | 5002 | 5166 | 5387 | 5417 | 5572 | 5710 | 6179 | 6191 | 6336 | 6067 | 6001 | 5919 | 0 | 7212 | 7754 | 7780 | 7943 | 7766 | 7691 | 7267 | 146661870
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | [20 empty] | 10 | 16 | 33 | 49 | 49 | 0 | 158400
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL) | [9 empty] | 28 | 102 | 152 | 152 | 153 | 205 | 312 | 210 | 40 |  | 60 | [6 empty] | 1326556
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | [20 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 81600
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 4 | 19 | 40 | 61 | 70 | 73 | 95 | 94 | 67 | 69 | 40 | 11 | 4 | [8 empty] | 691200
131 | Rampal 1320 MW (BIFPCL)
132 | United Payra Power Ltd.
133 | Bhola Nutan Biddut BD LTD (GAS)
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [12 empty] | 13 | 32 | 32 | 16 | 16 | [7 empty] | 16 | 16 | 131520
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 67 | 67 | 67 | 68 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1640000
140 | Bhola 33 MW PP (Venture) | 23 | 22 | 23 | 18 | 18 | 19 | 18 | 18 | 18 | 18 | 19 | 23 | 24 | 24 | 26 | 23 | 21 | 24 |  | 17 | 27 | 28 | 28 | 30 | 30 | 29 | 529031
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 495 | 496 | 495 | 496 | 496 | 495 | 495 | 495 | 496 | 496 | 496 | 497 | 496 | 496 | 495 | 494 | 493 | 492 |  | 492 | 493 | 493 | 493 | 493 | 493 | 493 | 11956363
147 | Bheramara 410 MW CCPP | 390 | 390 | 0 | [6 empty] | 80 | 135 | 350 | 400 | 300 | 300 | 300 | 300 | 250 |  | 340 | 340 | 340 | 340 | 340 | 410 | 410 | 5516064
148 | Payra 1320 MW | 700 | 600 | 740 | 750 | 650 | 600 | 600 | 600 | 600 | 620 | 730 | 890 | 1040 | 1100 | 1112 | 1102 | 1102 | 1080 |  | 1030 | 1110 | 1112 | 1112 | 1112 | 1112 | 1212 | 23378600
149
150 | Barapukuria TPP Unit-1 | 77 | 76 | 75 | 75 | 76 | 75 | 74 | 75 | 75 | 75 | 75 | 75 | 76 | 75 | 74 | 74 | 75 | 75 |  | 75 | 75 | 75 | 76 | 76 | 76 | 76 | 1786473
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 200 | 200 | 200 | 200 | 180 | 170 | 170 | 170 | 170 | 184 | 250 | 250 | 250 | 250 | 250 | 250 | 251 | 250 | [8 empty] | 4031100
153 | Baghabari 71 MW GTPP | [20 empty] | 30 | 65 | 70 | 70 | 70 | 70 | 295000
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [26 empty] | 0
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 1 | 2 | 3 | 4 | 5 | 4 | 5 | 5 | 4 | 1 | 0 | 0 | [8 empty] | 36240
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 175 | 177 | 179 | 173 | 162 | 163 | 173 | 167 | 164 | 179 | 187 | 174 | 182 | 159 | 155 | 154 | 151 | 150 |  | 170 | 177 | 176 | 174 | 173 | 174 | 176 | 4301455
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 162 | 164 | 169 | 158 | 156 | 157 | 169 | 168 | 165 | 168 | 172 | 184 | 198 | 168 | 167 | 166 | 164 | 163 |  | 175 | 180 | 180 | 180 | 181 | 183 | 182 | 4360845
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 424 | 383 | 403 | 303 | 329 | 329 | 348 | 418 | 421 | 422 | 420 | 373 | 413 | 347 | 348 | 323 | 312 | 298 |  | 395 | 370 | 379 | 376 | 371 | 371 | 373 | 8946581
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 18 | 18 | 18 | 17 | 17 | 17 | 18 | 19 |  | 20 | 21 | 21 | 21 | 22 | 22 | 22 | 473520
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 151632
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | [22 empty] | 8 |  |  |  | 7634
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka) | [20 empty] | 10 | 17 | 34 | 34 | 43 | 24 | 142800
170 | Chapainawabganj 100 MW Peaking PP | [19 empty] | 44 | 47 | 47 | 47 |  |  |  | 122512
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [11 empty] | 12 | 35 | 70 | 70 | 35 | 35 | 35 |  | 68 | 94 | 113 | 113 | 113 | 113 | 113 | 989952
172 | Confidence Power Bogura Unit-1 113 MW | [17 empty] | 10 |  | 100 | 113 | 113 | 113 | 113 | 113 | 113 | 621120
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | [17 empty] | 34 |  | 101 | 113 | 113 | 113 | 113 | 113 | 113 | 656889
177 | Sympa Solar Power 8MW | [6 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 6 | 6 | 5 | 3 | 2 | 1 | [8 empty] | 45653
178 | Energypac Power Venture Thakurgaon Ltd. | [11 empty] | 35 | 68 | 76 | 75 | 75 | 37 | 37 |  | 85 | 115 | 115 | 115 | 115 | 114 | 75 | 1020864
| Intraco Solar 30 MW | [5 empty] | 2 | 5 | 12 | 20 | 26 | 33 | 28 | 31 | 18 | 10 | 13 | 7 | 1 | [8 empty] | 196331
| Adani Power Jharkhanda Ltd | 520 | 507 | 513 | 511 | 503 | 512 | 504 | 511 | 507 | 498 | 504 | 508 | 511 | 511 | 504 | 508 | 508 | 518 |  | 509 | 516 | 519 | 522 | 523 | 519 | 514 | 12321818
178 | Teesta Solar Limited | [5 empty] | 7 | 35 | 67 | 108 | 102 | 131 | 80 | 75 | 94 | 41 | 31 | 24 | 5 | [8 empty] | 931850