## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2023-05-10 | Wednesday
|  | Date (day): | 2023-05-10 |  | Wednesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13199.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14761 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2023-05-09 | 2023-05-10 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 120 | 120 | 120 | 120 | 60 |  | Gas shortage
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 170 | 180 | 180 | 180
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 22 | 22 | 22 | 22 | 86 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 394 | 399 | 412 | 412
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 235 | 334 | 330 | 330 | 30 |  | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 68 | 49 | 70 | 70 | 30 |  | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 292 | 293 | 300 | 300 |  |  | FGMO
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 95 | 97 | 97 | 97
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 55 | 15 | 15 | 15 | 40 |  | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 22 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 |  | 210 | GT-1 Under maint
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 72 | 75 | 34 | 75 | 25 |  | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 202 | 200 | 200 | 200 |  | 135 | ST under S/D
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 40 | 92 | 40 | 92 |  | 10 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 17 | 0 | 35 | 19 |  | Fuel shortage
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 98 | 146 | 100 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 0 | 55 | 55 |  |  | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 0 | 35 | 55 |  |  | Fuel shortage
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 43 | 45 | 46 | 51 |  | 29 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 25 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 30 | 39 | 16 | 50
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 190 | 278 | 145 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 303 | 302 | 300 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 76 | 80 | 70 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 75 | 80 | 70 | 80 |  | 20 | Engine problem
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 128 | 144 | 35 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 88 | 105 | 88 | 105
37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 53 | 53 | 54 | 54 | 50 |  | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 72 | 17 | 72 | 162 |  |  | Fuel shortage
39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 29 | 0 | 30 | 0
40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 17 | 34 | 34 | 21 |  | Fuel shortage
| Dhaka area Total |  |  |  |  | 6263 | 5847 | 3658 | 3721 | 3508 | 4130 | 412 | 1269
41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 115 | 115 | 120 | 120 | 60 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 8 | 17 | 25 | 25
43 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 20 | 0 | 20 | 0
44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 8 | 44 | 6 | 39 | 11 |  | Fuel shortage
45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 27 | 27 | 25 | 25 | 205 |  | Low Water Level
46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 212 | 220 | 225 | 225
47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 30 | 87 | 51 | 51 | 54 |  | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 42 | 48 | 56 | 60 |  | 38 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 63 | 84 | 84 | 84 |  | 18 | Engine problem
51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 22 | 33 | 22 | 44 | 56 |  | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 25 | 38 | 25 | 50 | 50 |  | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 8 | 8 | 8 | 8 | 14 |  | Gas shortage
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 26 | 5 | 20
54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 30 | 0 | 50 | 58 |  | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5 | 0 | 5 | 0
56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 82 | 300 | 85 | 300
57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 17 | 17 | 17 | 54
58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 54 | 74 | 54 | 54 | 56 |  | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 38 | 38 | 38 | 62 |  | Fuel shortage
60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 17 | 17 | 17 | 17 | 99 |  | Fuel shortage
| Mirsharai 150 MW |  | Gas/HFO | BPDB-RPCL | 18.5*9 | 0 | 0 | 108 | 163 | 163 | 163 |  |  | On test.
| Chattogram area Total |  |  |  |  | 2442 | 2382 | 890 | 1386 | 1051 | 1427 | 725 | 386
61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 198 | 203 | 200 | 200 |  |  | FGMO
63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 305 | 310 | 310 | 310 |  |  | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 320 | 305 | 310 | 340 |  |  | FGMO
65 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Under maint.
66 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 33 | 33 | 41 | 42
67 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 55 | 0 | 0 | 0 | 0 |  |  | Contract Expired
68 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 177 | 175 | 180 | 180 | 15 |  | Gas shortage
69 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 43 | 40 | 43 |  | 8 | Engine problem
70 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 18 | 137 | 20 | 150 |  |  | Fuel shortage
71 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 35 | 36 | 36 | 34 |  | 18 | Engine problem
72 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under Maint.
73 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 51 | 69 | 34 | 85 | 115 |  | Fuel shortage
74 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 15 | 17 | 18 | 18 |  | 4 | Engine problem
75 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 7 | 7 | 7 | 7 |  | 4 | Engine problem
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 160 | 154 | 150 | 166
76 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
77 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 35 | 52 | 52 | 52
78 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 15 | 20 | 20 | 20 |  | 5 | Engine problem
79 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 0 |  |  | Contract Expired
80 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 0 | 0 |  |  | Fuel shortage
81 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 55 | 57 | 55 | 55 | 58 |  | Fuel shortage
82 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 35 | 17 | 17 | 35 |  | 19 | Engine problem
83 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 95 | 94 | 94 | 94 | 21 |  | Fuel shortage
| Cumilla Area Total |  |  |  |  | 3159 | 3151 | 1622 | 1762 | 1617 | 1864 | 209 | 621
84 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 28 | 68 | 44 | 70 | 132 |  | Gas shortage
85 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 13 | 18 | 16 | 17 | 5 |  | Gas shortage
86 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0
87 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
88 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 75 | 95 | 57 | 98 | 102 |  | Fuel shortage
89 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 78 | 98 | 50 | 98 | 17 |  | Fuel shortage
90 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 46 | 0 | 50 | 0
91 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 12 | 12 | 10 |  | Fuel shortage
| Mymensingh Area Total |  |  |  |  | 717 | 614 | 254 | 291 | 230.6 | 295 | 137 | 0
92 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 0 | 43 | 43 | 43 |  | 27 | Machine problem.
93 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 28 | 28 | 29 | 29 |  | 61 | Machine problem
94 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under maint
95 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
96 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 47 | 53 | 50 | 50
97 | Fenchuganj 44MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 41 | 48 | 44 | 50
98 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 10 | 10
99 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 49 | 56 | 56 | 60
100 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 74 | 80 | 84 | 84
101 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
102 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 201 | 204 | 210 | 210 |  | 21 | Machine problem
103 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 17 | 17 | 17 | 17
104 | Sylhet 50MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
105 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 8 | 16 | 16 | 16 | 9 |  | Gas shortage
106 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 285 | 280 | 300 | 300 |  |  | FGMO
107 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 391 | 369 | 400 | 400 |  |  | FGMO
108 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
109 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 354 | 385 | 400 | 400
| Sylhet Area Total |  |  |  |  | 2472 | 2427 | 1513 | 1597 | 1669 | 1679 | 9 | 702
110 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 911 | 814 | 932 | 932
111 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 60 | 94 | 85 | 98 |  | 17 | Engine problem
112 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 11 | 37 | 19 | 43 |  | 11 | Engine problem
113 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
114 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 22 | 75 | 20 | 76 |  | 33 | Engine problem
115 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 | 410 |  | Gas shortage
116 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 32 | 40 | 32 | 40
117 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Fuel shortage
118 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 36 | 55 | 17 | 53 | 52 |  | Fuel shortage
119 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 50 | 105 | 105 | 105
120 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 75 | 0 | 100 | 0
| Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 0 | 0 | 200 | 0 | 0 | 0 |  |  | On test.
| Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 660*2 | 617 | 617 | 0 | 0 | 0 | 0 |  |  | Coal Shortage.
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3005 | 3001 | 1397 | 1220 | 1310 | 1347 | 808 | 61
121 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 64 | 16 | 16 | 64
122 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 23 | 36 | 22 | 32 |  | 8 | Engine problem
123 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 170 | 175 | 180 | 181
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
124 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 1200 | 1244 | 1244 | 1244
125 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 0 | 0 | 0 | 0 |  | 220 | Under maintenance
126 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 150 | 17 | 150
127 | Barisal 307 MW |  | Coal | BCPCL | 307*1 | 307 | 307 | 0 | 0 | 0 | 0 | 307 |  | Coal Shortage.
| Barisal Area Total |  |  |  |  | 2265 | 2265 | 1474 | 1621 | 1479 | 1671 | 307 | 228
128 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
129 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 21 | 28 | 28 | 28 |  | 24 | Engine problem
130 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 4 | 0 | 0 | 31 |  | 40 | Engine problem
131 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 21 | 21 | 21 | 21
132 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 42 | 42 | 42 |  | 8 | Engine problem
133 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 40 | 40 | 24 | 40 |  | 10 | Engine problem
134 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 159 | 180 | 160 | 164 | 46 |  | Gas shortage
135 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
136 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 133 | 153 | 140 | 142 | 78 |  | Gas shortage
137 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 227 | 345 | 300 | 345 | 69 |  | Gas shortage
138 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 35 | 34 | 34 |  | 16 | Engine problem
139 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 11 | 20 | 22 | 22
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
140 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 8 | 8 |  | 3 | Engine problem
141 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 34 | 8 | 43 | 9 |  | Fuel shortage
142 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 72 | 78 | 80 | 83 |  | 21 | Enginr problem
143 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel shortage
144 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 35 | 50 | 35 | 50 | 63 |  | Fuel shortage
145 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 35 | 55 | 35 | 55 | 58 |  | Fuel shortage
146 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
| Adani Power Jharkhanda Ltd |  | Coal | Import | 0 | 0 | 0 | 742 | 592 | 750 | 750 |  |  | On test.
| Rajshahi Area Total |  |  |  |  | 2179 | 2129 | 1521 | 1681 | 1693 | 1858 | 914 | 122
147 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 75 | 75 | 75 | 75 | 10 |  | Coal Shortage.
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
148 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 200 | 250 | 250 | 250
149 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
150 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
151 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 34 | 34 | 34 | 50
152 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 7 | 0 | 8 | 0
153 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 95 | 114 | 115 | 115
154 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 33 | 0 | 30 | 0
| Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 0 | 0 | 197 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 830 | 750 | 641 | 473 | 642 | 490 | 50 | 85
| Total |  |  |  |  | 23332 | 22566 | 12970 | 13752 | 13199.6 | 14761 | 3571 | 3474
A. |  | 2023-05-09 | (Yesterday) |  |  |  |  | Tuesday
1 | Highest Generation : |  |  | 13908 | MW at | 22:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 11741 | MW at | 6:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 15300 | MW
3 | Day peak Generation : |  |  | 12970 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 14671.81 | MW
4 | Evening peak Generation : |  |  | 13752 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 1478 | MW
5 | Total Energy Generation : |  | 305.3341 | MKWHr | By Solar | 3.1767 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Gas : | 146.5474 | MKWHr |  | By Oil: | 73.9217 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 56.0384 | MKWHr |  | By Hydro: | 0.324 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 3571 | MW | Dhaka | 5232.01 | 5060.01 |  | 172 |  | 18:00 |  | 1050
|  |  | For Plants S/D or M/C prob = |  |  | 3474 | MW | Chittagong | 1447.7 | 1247.7 |  | 200 |  | 19:00 |  | 1444.915
|  |  | Total = |  |  | 7045 | MW | Khulna | 1782.7 | 1490.7 |  | 292 |  | 19:30 |  | 1485.98
7 | Total Gas Supplied : |  |  | 1113.4 | MMCFD |  |  | Rajshahi | 1520.4 | 1370.4 |  | 150 |  | 20:00 |  | 1567.155
8 | Fuel Cost : | i) Gas : | Taka | 167659062.99 | ii) Oil : | Taka | 999616857.34 | Comilla | 1468 | 1247 |  | 221 |  | 21:00 |  | 1478.34
|  | iii) Coal : | Taka | 321969341.87 | Total | Taka | 1489245262.2 | Mymensingh | 1165 | 907 |  | 258 |  | 22:00 |  | 1138.36
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0 | MKWHr. | Sylhet | 625 | 532 |  | 93 |  | 23:00 |  | 1724.73
| ii) During Peak Demand : |  |  | 570 | MW (E to W) at | 21:00 | hrs | Barisal | 478 | 478 |  | 0 |  | 24:00 |  | 1399.075
| iii) Maximum : |  |  | 500 | MW at | 19:30 | hrs | Rangpur | 953 | 861 |  | 92
10 | Maximum Temperature in Dhaka was |  |  |  | 39.8° C |  |  | Total | 14671.81 | 13193.81 |  | 1478
B. |  | 2023-05-10 | (Today) |  |  |  | Wednesday |  |  | Probable max. temperature in Dhaka |  |  | 39.4° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 15600 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 793 | MW
2 | Maximum Generation (Generation end) |  |  |  | 14761 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 13800 | MW
4 | Reserve(Generation end) |  |  |  | - | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 342.48 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 11392 | MW at | 7:00 | 199 | 86 | 120 | 114 | 94 | 83 | 32 | 0 | 65
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.5425 | MKWHr. | ii) HVDC Flow at Peak Time |  | 814 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.7834 | MKWHr. | iii) Maximum HVDC Flow : |  | 913 | MW at | 10:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 74.59 |  | (b) Today: | 74.47 |  | (c) Rule Curve: |  | 80.29
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2023-05-09 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 120 | 180 | 0 | 22 | 0 | 398 | 323 |  | 0 | 450 | 296 | 25 | 97 | 0 | 199 | 0 | 0 | 40 | 32 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 23 | 26 | 33 | 31 | 16 | 0 | 0 | 0 | 120 | 0 | 25 | 224 | 0 | 0 | 0 |  | 6 | 46 | 84 | 33 | 0 | 6 | 8 | 35 | 0 | 0 | 0 | 310 | 305 | 206 | 185 | 0 | 40 | 0 | 0 | 43 | 0 | 35 | 50 | 16 | 7 | 33 | 21 | 172 | 82 | 0 | 16 | 0 | 40 | 29 | 53 | 48 | 0 | 0 | 56 | 81 | 0 | 203 | 17 | 0 | 10 | 290 | 14 | 8 | 0 | 130 | 260 | 80 | 48 | 72 | 25 | 0 | 38 | 17 | 145 | 399 | 49 | 105 | 22 | 0 | 87 | 17 | 54 | 114 | 9 | 25 | 345 | 17 | 0 | 17 | 17 | 0 | 17 | 0 | 45 | 17 | 0 | 163 | 0 |  | 910 | 0 | 120 | 0 | 80 | 0 | 0 | 0 | 25 | 68 | 32 | 178 | 35 | 0 | 0 | 0 | 0 | 21 | 30 | 73 | 21 | 42 | 24 | 8 | 34 | 20 | 0 | 5 | 75 | 0 | 250 | 0 | 0 | 158 | 0 | 0 | 0 | 0 | 0 | 133 | 0 | 229 | 37 | 0 | 35 | 105 | 34 | 0 | 0 | 35 | 1244 | 0 | 0 | 150 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 740 | 0 | 0 |  | 7701 | 5064 | 12765 | 4122 | 910 | 2120 | 412 | 2037 | 2309 | 0 | 0 | 683 | 172 | 0 | 1618 | 74.61
2:00 | 0 | 0 | 120 | 180 | 0 | 22 | 0 | 398 | 322 |  | 0 | 450 | 305 | 24 | 97 | 0 | 189 | 0 | 0 | 33 | 32 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 23 | 26 | 33 | 31 | 16 | 0 | 0 | 0 | 120 | 0 | 25 | 225 | 0 | 0 | 0 |  | 6 | 52 | 84 | 22 | 0 | 6 | 8 | 35 | 0 | 0 | 0 | 310 | 305 | 207 | 185 | 0 | 42 | 0 | 0 | 43 | 0 | 34 | 43 | 17 | 7 | 33 | 0 | 168 | 86 | 0 | 17 | 0 | 40 | 29 | 53 | 49 | 0 | 0 | 56 | 81 | 0 | 204 | 17 | 0 | 10 | 295 | 14 | 8 | 0 | 97 | 220 | 80 | 48 | 75 | 17 | 0 | 38 | 17 | 46 | 401 | 49 | 105 | 17 | 0 | 87 | 17 | 54 | 114 | 9 | 25 | 348 | 17 | 0 | 17 | 17 | 0 | 17 | 0 | 36 | 17 | 0 | 163 | 0 |  | 909 | 0 | 120 | 0 | 80 | 0 | 0 | 0 | 20 | 68 | 32 | 178 | 34 | 0 | 0 | 0 | 0 | 21 | 30 | 73 | 21 | 42 | 24 | 8 | 0 | 20 | 0 | 5 | 72 | 0 | 250 | 0 | 0 | 157 | 0 | 0 | 0 | 0 | 0 | 133 | 0 | 224 | 37 | 0 | 35 | 105 | 34 | 0 | 0 | 35 | 1244 | 0 | 0 | 150 | 0 | 0 | 114 | 0 | 0 | 0 | 0 | 0 | 727 | 0 | 0 |  | 7452 | 5002 | 12454 | 4106 | 909 | 2128 | 375 | 1858 | 2293 | 0 | 0 | 617 | 168 | 0 | 1530.865 | 74.61
3:00 | 0 | 0 | 120 | 180 | 0 | 22 | 0 | 400 | 323 |  | 0 | 450 | 307 | 25 | 97 | 0 | 175 | 0 | 0 | 33 | 32 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 23 | 26 | 33 | 31 | 16 | 0 | 0 | 0 | 120 | 0 | 25 | 225 | 0 | 0 | 0 |  | 6 | 52 | 84 | 22 | 0 | 6 | 8 | 35 | 0 | 0 | 0 | 335 | 330 | 205 | 185 | 0 | 42 | 0 | 0 | 43 | 0 | 34 | 43 | 17 | 7 | 33 | 8 | 166 | 87 | 0 | 17 | 0 | 40 | 29 | 53 | 49 | 0 | 0 | 56 | 81 | 0 | 202 | 17 | 0 | 10 | 300 | 14 | 8 | 0 | 97 | 200 | 80 | 48 | 75 | 17 | 0 | 38 | 17 | 20 | 404 | 49 | 105 | 17 | 0 | 87 | 17 | 54 | 0 | 9 | 25 | 343 | 17 | 0 | 17 | 17 | 0 | 17 | 0 | 36 | 17 | 0 | 163 | 0 |  | 910 | 0 | 120 | 0 | 80 | 0 | 0 | 0 | 20 | 68 | 32 | 178 | 33 | 0 | 0 | 0 | 0 | 21 | 30 | 0 | 21 | 42 | 24 | 8 | 0 | 21 | 0 | 5 | 72 | 0 | 250 | 0 | 0 | 157 | 0 | 0 | 0 | 0 | 0 | 135 | 0 | 248 | 37 | 0 | 0 | 105 | 34 | 0 | 0 | 0 | 1244 | 0 | 0 | 17 | 0 | 0 | 114 | 0 | 0 | 0 | 0 | 0 | 745 | 0 | 0 |  | 7340 | 4771 | 12111 | 4149 | 910 | 2160 | 355 | 1516 | 2311 | 0 | 0 | 544 | 166 | 0 | 1517.495 | 74.6
4:00 | 0 | 0 | 120 | 180 | 0 | 22 | 0 | 402 | 329 |  | 0 | 450 | 307 | 25 | 88 | 0 | 175 | 0 | 0 | 33 | 32 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 23 | 26 | 33 | 31 | 16 | 0 | 0 | 0 | 120 | 0 | 25 | 223 | 0 | 0 | 0 |  | 6 | 52 | 84 | 22 | 0 | 6 | 8 | 36 | 0 | 0 | 0 | 315 | 305 | 207 | 185 | 0 | 42 | 0 | 0 | 43 | 0 | 34 | 43 | 17 | 7 | 33 | 21 | 160 | 87 | 0 | 18 | 0 | 40 | 29 | 53 | 49 | 0 | 0 | 56 | 81 | 0 | 202 | 17 | 0 | 10 | 285 | 14 | 8 | 0 | 97 | 200 | 80 | 48 | 74 | 17 | 0 | 25 | 17 | 20 | 404 | 49 | 105 | 17 | 0 | 87 | 17 | 45 | 0 | 9 | 25 | 343 | 17 | 0 | 17 | 17 | 0 | 17 | 0 | 36 | 17 | 0 | 163 | 0 |  | 909 | 0 | 120 | 0 | 65 | 0 | 0 | 0 | 20 | 68 | 32 | 178 | 32 | 0 | 0 | 0 | 0 | 21 | 28 | 73 | 21 | 42 | 24 | 8 | 0 | 21 | 0 | 5 | 74 | 0 | 250 | 0 | 0 | 157 | 0 | 0 | 0 | 0 | 0 | 135 | 0 | 249 | 37 | 0 | 0 | 105 | 34 | 0 | 0 | 0 | 1244 | 0 | 0 | 17 | 0 | 0 | 114 | 0 | 0 | 0 | 0 | 0 | 742 | 0 | 0 |  | 7265 | 4825 | 12090 | 4120 | 909 | 2152 | 354 | 1470 | 2310 | 0 | 0 | 615 | 160 | 0 | 1381.885 | 74.6
5:00 | 0 | 0 | 120 | 180 | 0 | 22 | 0 | 401 | 332 |  | 0 | 450 | 299 | 25 | 97 | 0 | 170 | 0 | 0 | 33 | 32 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 23 | 26 | 33 | 31 | 16 | 0 | 0 | 0 | 120 | 0 | 25 | 225 | 0 | 0 | 0 |  | 6 | 52 | 84 | 22 | 0 | 6 | 8 | 36 | 0 | 0 | 0 | 315 | 315 | 207 | 180 | 0 | 42 | 0 | 0 | 43 | 0 | 34 | 43 | 17 | 5 | 33 | 20 | 160 | 87 | 0 | 17 | 0 | 40 | 29 | 53 | 49 | 0 | 0 | 56 | 81 | 0 | 203 | 17 | 0 | 10 | 290 | 14 | 8 | 0 | 97 | 70 | 80 | 48 | 75 | 17 | 0 | 25 | 17 | 18 | 404 | 49 | 90 | 17 | 0 | 82 | 17 | 54 | 0 | 9 | 25 | 370 | 17 | 0 | 17 | 17 | 0 | 17 | 0 | 36 | 17 | 0 | 163 | 0 |  | 910 | 0 | 120 | 0 | 65 | 0 | 0 | 0 | 20 | 68 | 32 | 178 | 31 | 0 | 0 | 0 | 0 | 21 | 15 | 73 | 21 | 42 | 24 | 8 | 0 | 21 | 0 | 5 | 74 | 0 | 250 | 0 | 0 | 157 | 0 | 0 | 0 | 0 | 0 | 135 | 0 | 249 | 37 | 0 | 0 | 105 | 34 | 0 | 0 | 0 | 1244 | 0 | 0 | 17 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 741 | 0 | 0 |  | 7157 | 4810 | 11967 | 4150 | 910 | 2146 | 225 | 1465 | 2309 | 0 | 0 | 602 | 160 | 0 | 1258.69 | 74.59
6:00 | 0 | 0 | 120 | 180 | 0 | 22 | 0 | 400 | 334 |  | 0 | 450 | 303 | 24 | 97 | 0 | 170 | 0 | 0 | 33 | 32 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 23 | 26 | 33 | 32 | 16 | 0 | 0 | 0 | 120 | 0 | 25 | 225 | 0 | 0 | 0 |  | 6 | 56 | 84 | 22 | 0 | 6 | 8 | 34 | 0 | 0 | 0 | 320 | 320 | 207 | 180 | 0 | 43 | 0 | 0 | 43 | 0 | 34 | 51 | 17 | 5 | 25 | 20 | 144 | 87 | 0 | 18 | 0 | 40 | 29 | 53 | 49 | 0 | 0 | 56 | 81 | 0 | 203 | 17 | 0 | 10 | 285 | 14 | 8 | 0 | 97 | 0 | 0 | 48 | 0 | 17 | 1 | 25 | 17 | 20 | 404 | 49 | 88 | 17 | 0 | 82 | 17 | 54 | 0 | 9 | 25 | 370 | 17 | 3 | 17 | 17 | 0 | 17 | 2 | 36 | 17 | 0 | 163 | 0 |  | 910 | 0 | 120 | 0 | 65 | 0 | 0 | 0 | 19 | 68 | 32 | 179 | 27 | 0 | 0 | 0 | 0 | 21 | 0 | 73 | 21 | 42 | 24 | 8 | 0 | 20 | 0 | 5 | 74 | 0 | 250 | 0 | 0 | 157 | 0 | 0 | 0 | 0 | 0 | 136 | 0 | 253 | 37 | 0 | 0 | 105 | 34 | 0 | 0 | 0 | 1222 | 0 | 0 | 17 | 0 | 5 | 114 | 0 | 0 | 0 | 1 | 0 | 753 | 10 | 0 |  | 6939 | 4802 | 11741 | 4159 | 910 | 2144 | 0 | 1473 | 2299 | 0 | 0 | 590 | 144 | 22 | 1209.985 | 74.59
7:00 | 0 | 0 | 120 | 180 | 0 | 22 | 0 | 401 | 324 |  | 0 | 450 | 295 | 24 | 97 | 2 | 170 | 0 | 0 | 33 | 32 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 23 | 26 | 33 | 31 | 16 | 0 | 0 | 0 | 120 | 0 | 25 | 226 | 0 | 0 | 0 |  | 6 | 56 | 84 | 22 | 0 | 6 | 8 | 25 | 0 | 0 | 0 | 310 | 305 | 207 | 180 | 0 | 39 | 0 | 0 | 43 | 0 | 37 | 51 | 18 | 5 | 25 | 20 | 146 | 49 | 0 | 18 | 1 | 43 | 29 | 53 | 49 | 0 | 0 | 56 | 81 | 0 | 202 | 17 | 0 | 10 | 285 | 14 | 8 | 0 | 97 | 0 | 0 | 48 | 0 | 17 | 5 | 25 | 17 | 20 | 404 | 49 | 88 | 17 | 1 | 82 | 17 | 47 | 0 | 9 | 25 | 370 | 17 | 11 | 17 | 17 | 0 | 17 | 7 | 35 | 17 | 0 | 163 | 0 |  | 912 | 0 | 120 | 0 | 65 | 0 | 0 | 0 | 19 | 68 | 32 | 179 | 24 | 0 | 0 | 0 | 0 | 21 | 0 | 75 | 21 | 42 | 24 | 8 | 0 | 18 | 0 | 5 | 75 | 0 | 250 | 0 | 0 | 157 | 0 | 0 | 0 | 0 | 0 | 136 | 0 | 248 | 37 | 0 | 11 | 105 | 34 | 0 | 1 | 20 | 1222 | 0 | 0 | 17 | 0 | 28 | 115 | 0 | 0 | 0 | 6 | 0 | 745 | 44 | 0 |  | 6867 | 4884 | 11751 | 4096 | 912 | 2107 | 0 | 1499 | 2292 | 0 | 0 | 595 | 146 | 104 | 715.295 | 74.58
8:00 | 0 | 0 | 120 | 180 | 0 | 22 | 0 | 401 | 304 |  | 0 | 450 | 286 | 25 | 97 | 15 | 170 | 0 | 0 | 33 | 32 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 23 | 26 | 33 | 31 | 16 | 0 | 0 | 0 | 120 | 0 | 25 | 220 | 0 | 0 | 0 |  | 6 | 56 | 84 | 22 | 0 | 6 | 8 | 2 | 0 | 0 | 0 | 315 | 340 | 203 | 180 | 0 | 39 | 0 | 0 | 43 | 0 | 37 | 51 | 15 | 5 | 33 | 20 | 142 | 32 | 0 | 18 | 1 | 43 | 29 | 53 | 49 | 0 | 0 | 55 | 81 | 0 | 204 | 17 | 0 | 10 | 290 | 14 | 8 | 0 | 97 | 0 | 0 | 48 | 0 | 17 | 10 | 25 | 17 | 20 | 404 | 49 | 88 | 17 | 2 | 82 | 17 | 54 | 0 | 9 | 25 | 370 | 20 | 23 | 17 | 17 | 0 | 17 | 8 | 36 | 17 | 0 | 163 | 0 |  | 911 | 0 | 120 | 0 | 63 | 0 | 0 | 0 | 19 | 20 | 32 | 173 | 22 | 0 | 0 | 0 | 0 | 21 | 0 | 75 | 21 | 42 | 24 | 8 | 0 | 15 | 0 | 5 | 76 | 0 | 250 | 0 | 0 | 157 | 0 | 0 | 0 | 0 | 0 | 135 | 0 | 231 | 37 | 0 | 35 | 105 | 34 | 0 | 3 | 35 | 1200 | 0 | 0 | 17 | 2 | 43 | 115 | 0 | 0 | 0 | 15 | 0 | 745 | 91 | 0 |  | 6879 | 4897 | 11776 | 4108 | 911 | 2038 | 0 | 1561 | 2271 | 0 | 0 | 547 | 142 | 198 | 834.67 | 74.58
9:00 | 0 | 0 | 120 | 180 | 0 | 22 | 0 | 401 | 293 |  | 0 | 450 | 295 | 25 | 97 | 15 | 195 | 0 | 0 | 45 | 32 | 48 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 19 | 23 | 26 | 33 | 30 | 16 | 0 | 0 | 0 | 115 | 0 | 16 | 216 | 0 | 0 | 0 |  | 6 | 55 | 80 | 22 | 0 | 6 | 8 | 2 | 0 | 0 | 0 | 340 | 325 | 199 | 180 | 0 | 36 | 0 | 0 | 43 | 0 | 37 | 43 | 15 | 5 | 31 | 20 | 146 | 32 | 0 | 14 | 2 | 36 | 29 | 53 | 48 | 0 | 0 | 55 | 78 | 0 | 204 | 18 | 0 | 10 | 290 | 14 | 8 | 0 | 97 | 0 | 0 | 48 | 0 | 17 | 14 | 25 | 17 | 18 | 389 | 49 | 88 | 17 | 3 | 82 | 17 | 54 | 0 | 8 | 25 | 370 | 30 | 33 | 17 | 17 | 0 | 17 | 13 | 36 | 17 | 0 | 163 | 0 |  | 911 | 0 | 115 | 0 | 63 | 0 | 0 | 0 | 19 | 22 | 32 | 172 | 22 | 0 | 0 | 0 | 0 | 21 | 0 | 75 | 21 | 42 | 24 | 8 | 0 | 15 | 0 | 5 | 75 | 0 | 250 | 0 | 0 | 155 | 0 | 0 | 0 | 0 | 0 | 133 | 0 | 209 | 37 | 0 | 35 | 105 | 34 | 0 | 5 | 35 | 1160 | 0 | 0 | 17 | 3 | 68 | 115 | 75 | 0 | 0 | 23 | 0 | 746 | 139 | 0 |  | 6900 | 4986 | 11886 | 4086 | 911 | 2010 | 0 | 1580 | 2231 | 0 | 75 | 544 | 146 | 303 | 968.37 | 74.57
10:00 | 0 | 0 | 120 | 180 | 0 | 22 | 0 | 402 | 253 |  | 0 | 450 | 296 | 41 | 95 | 15 | 195 | 0 | 0 | 60 | 32 | 82 | 0 | 0 | 0 | 0 | 0 | 35 | 35 | 19 | 20 | 17 | 33 | 28 | 30 | 0 | 0 | 0 | 115 | 0 | 16 | 219 | 0 | 0 | 0 |  | 12 | 47 | 63 | 22 | 0 | 6 | 8 | 2 | 0 | 0 | 0 | 310 | 305 | 203 | 178 | 0 | 35 | 0 | 0 | 43 | 0 | 35 | 42 | 15 | 5 | 25 | 18 | 156 | 30 | 0 | 14 | 1 | 36 | 28 | 50 | 47 | 0 | 0 | 55 | 78 | 0 | 203 | 16 | 0 | 10 | 290 | 8 | 8 | 0 | 100 | 171 | 70 | 68 | 75 | 106 | 17 | 25 | 29 | 20 | 404 | 68 | 88 | 17 | 4 | 82 | 17 | 54 | 0 | 55 | 25 | 370 | 50 | 42 | 72 | 17 | 0 | 20 | 23 | 47 | 17 | 0 | 163 | 0 |  | 913 | 0 | 110 | 0 | 62 | 0 | 0 | 0 | 18 | 22 | 24 | 174 | 23 | 32 | 0 | 0 | 0 | 21 | 0 | 72 | 21 | 42 | 24 | 8 | 0 | 15 | 0 | 5 | 75 | 0 | 250 | 0 | 0 | 155 | 0 | 0 | 0 | 0 | 0 | 133 | 0 | 196 | 36 | 0 | 35 | 105 | 34 | 0 | 7 | 35 | 1080 | 0 | 0 | 17 | 4 | 85 | 115 | 200 | 0 | 0 | 29 | 0 | 753 | 168 | 0 |  | 7530 | 5098 | 12628 | 4021 | 913 | 1953 | 316 | 1984 | 2158 | 0 | 200 | 547 | 156 | 380 | 689.51 | 74.57
11:00 | 0 | 0 | 120 | 180 | 0 | 22 | 0 | 396 | 209 |  | 0 | 450 | 298 | 68 | 95 | 45 | 200 | 0 | 0 | 67 | 40 | 98 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 20 | 23 | 33 | 28 | 37 | 0 | 0 | 27 | 115 | 0 | 8 | 213 | 0 | 0 | 0 |  | 12 | 42 | 63 | 22 | 0 | 6 | 8 | 2 | 0 | 0 | 0 | 315 | 300 | 202 | 177 | 0 | 34 | 0 | 0 | 43 | 0 | 34 | 40 | 15 | 7 | 25 | 12 | 160 | 30 | 0 | 14 | 2 | 36 | 28 | 50 | 43 | 0 | 0 | 54 | 75 | 0 | 200 | 17 | 0 | 9 | 280 | 8 | 8 | 0 | 168 | 300 | 78 | 76 | 75 | 139 | 19 | 25 | 34 | 18 | 398 | 78 | 88 | 17 | 4 | 82 | 17 | 54 | 0 | 55 | 25 | 372 | 53 | 48 | 72 | 17 | 0 | 35 | 25 | 93 | 17 | 0 | 163 | 0 |  | 912 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 16 | 22 | 24 | 171 | 24 | 36 | 0 | 0 | 0 | 17 | 0 | 72 | 21 | 42 | 24 | 8 | 0 | 13 | 0 | 5 | 75 | 0 | 250 | 0 | 0 | 155 | 0 | 0 | 0 | 0 | 0 | 132 | 0 | 203 | 36 | 0 | 35 | 15 | 34 | 0 | 7 | 35 | 1070 | 0 | 0 | 17 | 4 | 73 | 115 | 228 | 0 | 0 | 32 | 0 | 747 | 192 | 0 |  | 7993 | 4924 | 12917 | 3893 | 912 | 1898 | 453 | 2247 | 2142 | 27 | 228 | 551 | 160 | 406 | 652.265 | 74.56
12:00 | 0 | 0 | 120 | 170 | 0 | 22 | 0 | 394 | 235 |  | 0 | 450 | 292 | 68 | 95 | 55 | 202 | 0 | 0 | 72 | 40 | 98 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 20 | 23 | 33 | 25 | 30 | 0 | 0 | 27 | 115 | 0 | 8 | 212 | 0 | 0 | 0 |  | 12 | 42 | 63 | 22 | 0 | 8 | 8 | 2 | 0 | 0 | 0 | 305 | 320 | 198 | 177 | 0 | 33 | 0 | 0 | 43 | 0 | 35 | 35 | 15 | 7 | 25 | 15 | 160 | 28 | 0 | 13 | 2 | 0 | 28 | 47 | 41 | 0 | 0 | 49 | 74 | 0 | 201 | 17 | 0 | 10 | 285 | 8 | 8 | 0 | 190 | 303 | 76 | 75 | 75 | 128 | 20 | 25 | 51 | 18 | 391 | 78 | 88 | 30 | 5 | 82 | 17 | 54 | 0 | 55 | 25 | 354 | 53 | 46 | 72 | 17 | 0 | 35 | 29 | 95 | 17 | 0 | 108 | 0 |  | 911 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 11 | 22 | 32 | 170 | 23 | 64 | 0 | 0 | 0 | 21 | 4 | 72 | 21 | 0 | 40 | 8 | 0 | 11 | 0 | 8 | 75 | 0 | 200 | 0 | 0 | 159 | 0 | 0 | 0 | 0 | 0 | 133 | 0 | 227 | 36 | 0 | 35 | 50 | 34 | 0 | 7 | 35 | 1200 | 0 | 0 | 17 | 5 | 75 | 95 | 200 | 0 | 0 | 33 | 0 | 742 | 197 | 0 |  | 7937 | 5033 | 12970 | 3826 | 911 | 1939 | 454 | 2301 | 2217 | 27 | 200 | 516 | 160 | 419 | 792.65 | 74.56
13:00 | 0 | 0 | 120 | 170 | 0 | 22 | 0 | 390 | 320 |  | 0 | 450 | 288 | 73 | 95 | 55 | 197 | 0 | 0 | 67 | 40 | 98 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 20 | 16 | 25 | 24 | 30 | 0 | 0 | 27 | 115 | 0 | 14 | 216 | 0 | 0 | 0 |  | 12 | 43 | 63 | 22 | 0 | 15 | 8 | 2 | 0 | 0 | 0 | 315 | 305 | 201 | 177 | 0 | 31 | 0 | 0 | 43 | 0 | 31 | 33 | 15 | 7 | 27 | 20 | 156 | 28 | 0 | 13 | 2 | 0 | 28 | 43 | 41 | 0 | 0 | 54 | 74 | 0 | 200 | 17 | 0 | 10 | 290 | 8 | 8 | 0 | 198 | 54 | 75 | 75 | 75 | 126 | 17 | 25 | 51 | 17 | 405 | 76 | 88 | 41 | 4 | 93 | 6 | 54 | 0 | 56 | 25 | 352 | 56 | 48 | 72 | 17 | 0 | 35 | 23 | 95 | 17 | 0 | 108 | 0 |  | 911 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 14 | 19 | 24 | 168 | 25 | 64 | 0 | 0 | 0 | 28 | 4 | 69 | 28 | 42 | 40 | 8 | 0 | 9 | 0 | 8 | 75 | 0 | 222 | 0 | 0 | 167 | 0 | 0 | 0 | 0 | 0 | 138 | 0 | 259 | 36 | 0 | 35 | 105 | 34 | 0 | 7 | 35 | 1244 | 0 | 0 | 17 | 4 | 90 | 95 | 120 | 0 | 0 | 32 | 0 | 744 | 185 | 0 |  | 7762 | 5165 | 12927 | 3835 | 911 | 2053 | 204 | 2407 | 2285 | 27 | 120 | 517 | 156 | 412 | 1024.715 | 74.55
14:00 | 0 | 0 | 120 | 170 | 0 | 22 | 0 | 394 | 317 |  | 0 | 450 | 292 | 73 | 95 | 15 | 150 | 0 | 0 | 64 | 40 | 98 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 20 | 16 | 25 | 24 | 16 | 0 | 0 | 27 | 115 | 0 | 16 | 212 | 0 | 0 | 0 |  | 12 | 45 | 74 | 33 | 0 | 26 | 8 | 2 | 0 | 0 | 0 | 315 | 305 | 197 | 177 | 0 | 30 | 0 | 0 | 43 | 0 | 25 | 37 | 14 | 7 | 18 | 5 | 160 | 25 | 0 | 15 | 2 | 0 | 28 | 48 | 38 | 0 | 0 | 53 | 70 | 0 | 200 | 17 | 0 | 10 | 290 | 8 | 8 | 0 | 173 | 129 | 50 | 45 | 50 | 44 | 12 | 25 | 37 | 18 | 380 | 46 | 88 | 63 | 4 | 82 | 17 | 54 | 0 | 28 | 34 | 345 | 64 | 27 | 72 | 17 | 0 | 17 | 21 | 76 | 17 | 0 | 108 | 0 |  | 908 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 18 | 20 | 24 | 168 | 27 | 16 | 0 | 0 | 0 | 28 | 5 | 68 | 28 | 42 | 40 | 8 | 0 | 9 | 0 | 8 | 75 | 0 | 250 | 0 | 0 | 169 | 0 | 0 | 0 | 0 | 0 | 141 | 0 | 260 | 36 | 0 | 35 | 105 | 33 | 0 | 7 | 35 | 1244 | 0 | 0 | 17 | 4 | 83 | 95 | 40 | 0 | 0 | 29 | 0 | 747 | 173 | 0 |  | 7365 | 5055 | 12420 | 3729 | 908 | 2055 | 229 | 2065 | 2316 | 27 | 40 | 529 | 160 | 362 | 1413.4 | 74.56
15:00 | 0 | 0 | 120 | 170 | 0 | 22 | 0 | 393 | 314 |  | 0 | 450 | 289 | 72 | 95 | 15 | 196 | 0 | 0 | 72 | 58 | 98 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 20 | 22 | 25 | 24 | 16 | 0 | 0 | 27 | 115 | 0 | 16 | 211 | 0 | 0 | 0 |  | 12 | 45 | 74 | 31 | 0 | 32 | 8 | 2 | 0 | 0 | 0 | 320 | 310 | 194 | 175 | 0 | 30 | 0 | 0 | 43 | 0 | 26 | 30 | 14 | 7 | 22 | 15 | 162 | 29 | 0 | 15 | 2 | 29 | 28 | 47 | 39 | 0 | 0 | 53 | 71 | 0 | 200 | 17 | 0 | 10 | 290 | 8 | 8 | 0 | 95 | 300 | 70 | 45 | 75 | 29 | 13 | 25 | 34 | 16 | 370 | 46 | 88 | 87 | 3 | 82 | 17 | 54 | 0 | 27 | 34 | 327 | 53 | 27 | 72 | 17 | 0 | 17 | 22 | 72 | 17 | 0 | 108 | 0 |  | 908 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 18 | 22 | 24 | 168 | 28 | 0 | 0 | 0 | 0 | 28 | 20 | 70 | 28 | 42 | 40 | 8 | 0 | 9 | 0 | 8 | 75 | 0 | 250 | 0 | 0 | 173 | 0 | 0 | 0 | 0 | 0 | 142 | 0 | 271 | 36 | 0 | 35 | 105 | 33 | 0 | 7 | 35 | 1244 | 0 | 0 | 17 | 3 | 59 | 110 | 0 | 0 | 0 | 23 | 0 | 731 | 138 | 0 |  | 7586 | 4968 | 12554 | 3810 | 908 | 2060 | 445 | 1996 | 2300 | 27 | 0 | 549 | 162 | 297 | 1571.93 | 74.54
16:00 | 0 | 0 | 120 | 170 | 0 | 21 | 0 | 389 | 314 |  | 0 | 450 | 263 | 72 | 95 | 15 | 194 | 0 | 0 | 72 | 58 | 98 | 4 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 20 | 22 | 25 | 24 | 16 | 0 | 0 | 27 | 115 | 0 | 16 | 220 | 0 | 0 | 0 |  | 12 | 39 | 74 | 31 | 0 | 34 | 8 | 2 | 0 | 0 | 0 | 320 | 305 | 199 | 175 | 0 | 29 | 0 | 0 | 43 | 0 | 25 | 30 | 15 | 7 | 15 | 15 | 158 | 31 | 0 | 12 | 1 | 10 | 28 | 47 | 43 | 0 | 0 | 50 | 71 | 0 | 198 | 17 | 0 | 10 | 285 | 14 | 8 | 0 | 97 | 129 | 70 | 46 | 75 | 30 | 8 | 25 | 35 | 21 | 400 | 46 | 88 | 87 | 2 | 82 | 17 | 60 | 0 | 28 | 34 | 355 | 53 | 21 | 72 | 17 | 0 | 17 | 14 | 72 | 17 | 0 | 108 | 0 |  | 908 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 21 | 22 | 24 | 168 | 28 | 0 | 0 | 0 | 0 | 28 | 26 | 69 | 28 | 42 | 24 | 8 | 0 | 9 | 0 | 8 | 74 | 0 | 250 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 144 | 0 | 290 | 36 | 0 | 35 | 105 | 33 | 0 | 5 | 35 | 1244 | 0 | 0 | 17 | 2 | 41 | 104 | 0 | 0 | 0 | 14 | 0 | 719 | 90 | 0 |  | 7413 | 4886 | 12299 | 3849 | 908 | 2051 | 274 | 2013 | 2287 | 27 | 0 | 534 | 158 | 198 | 1719.955 | 74.54
17:00 | 0 | 0 | 120 | 170 | 0 | 21 | 0 | 393 | 314 |  | 0 | 450 | 291 | 53 | 95 | 15 | 194 | 0 | 0 | 70 | 58 | 98 | 4 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 20 | 22 | 25 | 14 | 16 | 0 | 0 | 27 | 115 | 0 | 16 | 221 | 0 | 0 | 0 |  | 12 | 34 | 74 | 31 | 0 | 0 | 8 | 2 | 0 | 0 | 0 | 310 | 305 | 200 | 175 | 0 | 30 | 0 | 0 | 43 | 0 | 25 | 38 | 15 | 7 | 22 | 10 | 152 | 31 | 0 | 12 | 1 | 15 | 28 | 49 | 44 | 0 | 0 | 45 | 74 | 0 | 199 | 17 | 0 | 10 | 290 | 16 | 8 | 0 | 95 | 172 | 25 | 47 | 40 | 32 | 3 | 25 | 40 | 30 | 382 | 47 | 105 | 87 | 1 | 99 | 17 | 54 | 0 | 56 | 34 | 370 | 53 | 10 | 72 | 17 | 0 | 17 | 6 | 73 | 17 | 0 | 108 | 0 |  | 909 | 0 | 0 | 0 | 44 | 0 | 0 | 0 | 22 | 40 | 24 | 168 | 26 | 0 | 0 | 0 | 0 | 28 | 28 | 69 | 21 | 42 | 24 | 8 | 0 | 12 | 0 | 8 | 75 | 0 | 250 | 0 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 144 | 0 | 303 | 36 | 0 | 35 | 105 | 34 | 0 | 4 | 35 | 1244 | 0 | 0 | 17 | 1 | 17 | 104 | 0 | 0 | 0 | 6 | 0 | 743 | 40 | 0 |  | 7394 | 4842 | 12236 | 3839 | 909 | 2104 | 237 | 2017 | 2312 | 27 | 0 | 550 | 152 | 89 | 1684.62 | 74.53
18:00 | 0 | 0 | 120 | 170 | 0 | 21 | 0 | 403 | 313 |  | 0 | 450 | 300 | 48 | 95 | 15 | 196 | 0 | 0 | 72 | 58 | 106 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 20 | 23 | 33 | 26 | 16 | 0 | 0 | 27 | 115 | 0 | 16 | 221 | 0 | 0 | 0 |  | 12 | 44 | 82 | 33 | 30 | 7 | 8 | 5 | 0 | 0 | 0 | 310 | 305 | 198 | 175 | 0 | 14 | 0 | 0 | 43 | 0 | 26 | 38 | 15 | 7 | 32 | 10 | 154 | 31 | 0 | 17 | 0 | 43 | 28 | 50 | 45 | 0 | 0 | 50 | 76 | 0 | 200 | 16 | 0 | 9 | 270 | 16 | 8 | 0 | 112 | 11 | 25 | 58 | 25 | 56 | 0 | 25 | 68 | 46 | 390 | 49 | 105 | 87 | 0 | 120 | 17 | 67 | 0 | 56 | 38 | 360 | 53 | 2 | 72 | 0 | 0 | 17 | 1 | 82 | 17 | 0 | 126 | 0 |  | 909 | 0 | 0 | 0 | 64 | 0 | 0 | 0 | 22 | 65 | 24 | 161 | 26 | 0 | 0 | 0 | 0 | 28 | 28 | 69 | 21 | 42 | 40 | 8 | 32 | 16 | 0 | 8 | 75 | 0 | 250 | 0 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 315 | 36 | 0 | 35 | 105 | 34 | 0 | 1 | 35 | 1244 | 0 | 0 | 150 | 0 | 3 | 109 | 0 | 0 | 0 | 1 | 0 | 752 | 7 | 0 |  | 7462 | 5039 | 12501 | 3897 | 909 | 2114 | 61 | 2335 | 2321 | 27 | 0 | 668 | 154 | 15 | 1050 | 74.53
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 120 | 170 | 0 | 21 | 0 | 392 | 334 |  | 0 | 450 | 242 | 49 | 95 | 15 | 201 | 0 | 0 | 72 | 92 | 145 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 20 | 24 | 33 | 26 | 35 | 0 | 0 | 27 | 115 | 0 | 17 | 224 | 0 | 0 | 0 |  | 12 | 28 | 84 | 33 | 30 | 36 | 8 | 5 | 0 | 0 | 0 | 310 | 305 | 206 | 175 | 0 | 15 | 0 | 0 | 43 | 0 | 29 | 40 | 16 | 7 | 32 | 18 | 156 | 46 | 0 | 17 | 0 | 43 | 28 | 50 | 43 | 0 | 0 | 56 | 78 | 0 | 198 | 16 | 0 | 10 | 280 | 16 | 8 | 0 | 245 | 292 | 72 | 94 | 78 | 130 | 0 | 38 | 69 | 73 | 367 | 97 | 105 | 87 | 0 | 290 | 17 | 74 | 0 | 56 | 38 | 320 | 53 | 0 | 162 | 10 | 0 | 17 | 0 | 86 | 17 | 0 | 163 | 0 |  | 909 | 0 | 0 | 0 | 77 | 0 | 0 | 0 | 32 | 70 | 40 | 157 | 34 | 16 | 0 | 0 | 0 | 28 | 28 | 75 | 21 | 42 | 40 | 35 | 35 | 19 | 0 | 8 | 76 | 0 | 250 | 0 | 0 | 177 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 310 | 36 | 0 | 37 | 105 | 34 | 0 | 0 | 55 | 1230 | 0 | 0 | 150 | 0 | 0 | 114 | 0 | 0 | 0 | 0 | 0 | 647 | 0 | 0 |  | 8552 | 5035 | 13587 | 3866 | 909 | 2094 | 442 | 3133 | 2203 | 27 | 0 | 757 | 156 | 0 | 1444.915 | 74.51
19:30 | 0 | 0 | 120 | 180 | 0 | 21 | 0 | 397 | 334 |  | 0 | 450 | 268 | 50 | 95 | 15 | 204 | 0 | 0 | 72 | 92 | 145 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 20 | 24 | 33 | 24 | 39 | 0 | 0 | 27 | 115 | 0 | 17 | 225 | 0 | 0 | 0 |  | 12 | 24 | 84 | 33 | 30 | 44 | 8 | 10 | 0 | 0 | 0 | 310 | 305 | 206 | 175 | 0 | 20 | 0 | 0 | 43 | 0 | 32 | 52 | 16 | 7 | 32 | 18 | 152 | 47 | 0 | 18 | 0 | 44 | 28 | 50 | 46 | 0 | 0 | 56 | 78 | 0 | 198 | 17 | 0 | 10 | 270 | 16 | 8 | 0 | 265 | 156 | 73 | 95 | 51 | 140 | 0 | 38 | 69 | 92 | 369 | 97 | 105 | 87 | 0 | 290 | 17 | 74 | 0 | 56 | 38 | 330 | 53 | 0 | 162 | 17 | 0 | 17 | 0 | 94 | 17 | 0 | 163 | 0 |  | 908 | 0 | 0 | 0 | 79 | 0 | 0 | 0 | 36 | 82 | 40 | 159 | 34 | 16 | 0 | 0 | 0 | 28 | 28 | 75 | 21 | 42 | 40 | 35 | 35 | 19 | 0 | 8 | 76 | 0 | 250 | 0 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 153 | 0 | 336 | 36 | 0 | 50 | 105 | 34 | 0 | 0 | 55 | 1244 | 0 | 0 | 150 | 0 | 0 | 114 | 0 | 0 | 0 | 0 | 0 | 643 | 0 | 0 |  | 8537 | 5107 | 13644 | 3910 | 908 | 2144 | 280 | 3238 | 2213 | 27 | 0 | 772 | 152 | 0 | 1485.98 | 0
20:00 | 0 | 0 | 120 | 180 | 0 | 21 | 0 | 398 | 334 |  | 0 | 450 | 280 | 48 | 97 | 15 | 205 | 0 | 0 | 72 | 92 | 146 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 20 | 24 | 33 | 25 | 39 | 0 | 0 | 27 | 115 | 0 | 17 | 225 | 0 | 0 | 0 |  | 12 | 30 | 84 | 33 | 29 | 44 | 8 | 14 | 0 | 0 | 0 | 310 | 305 | 205 | 175 | 0 | 28 | 0 | 0 | 43 | 0 | 34 | 52 | 17 | 7 | 33 | 18 | 152 | 48 | 0 | 18 | 0 | 44 | 28 | 50 | 47 | 0 | 0 | 56 | 80 | 0 | 196 | 17 | 0 | 10 | 260 | 16 | 8 | 0 | 278 | 106 | 80 | 95 | 50 | 141 | 0 | 38 | 69 | 102 | 369 | 97 | 105 | 87 | 0 | 296 | 17 | 74 | 0 | 57 | 38 | 355 | 53 | 0 | 162 | 17 | 0 | 17 | 0 | 92 | 17 | 0 | 163 | 0 |  | 814 | 0 | 0 | 0 | 79 | 0 | 0 | 0 | 44 | 80 | 40 | 175 | 35 | 16 | 0 | 0 | 0 | 28 | 8 | 75 | 21 | 42 | 40 | 43 | 35 | 20 | 0 | 8 | 76 | 0 | 250 | 0 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 153 | 0 | 341 | 44 | 0 | 50 | 105 | 34 | 0 | 0 | 55 | 1244 | 0 | 0 | 150 | 0 | 0 | 114 | 0 | 0 | 0 | 0 | 0 | 639 | 0 | 0 |  | 8575 | 5034 | 13609 | 3962 | 814 | 2160 | 236 | 3282 | 2209 | 27 | 0 | 767 | 152 | 0 | 1567.155 | 74.52
21:00 | 0 | 0 | 120 | 180 | 0 | 22 | 0 | 399 | 334 |  | 0 | 450 | 293 | 49 | 97 | 15 | 200 | 0 | 0 | 75 | 92 | 146 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 20 | 25 | 25 | 25 | 39 | 0 | 0 | 27 | 115 | 0 | 17 | 220 | 0 | 0 | 0 |  | 12 | 48 | 84 | 33 | 30 | 44 | 8 | 26 | 0 | 0 | 0 | 310 | 305 | 203 | 175 | 0 | 33 | 0 | 0 | 43 | 0 | 36 | 52 | 17 | 7 | 33 | 20 | 154 | 68 | 0 | 18 | 0 | 43 | 28 | 53 | 48 | 0 | 0 | 56 | 80 | 0 | 204 | 17 | 0 | 10 | 280 | 16 | 8 | 0 | 278 | 302 | 80 | 95 | 80 | 144 | 0 | 38 | 69 | 137 | 369 | 98 | 105 | 87 | 0 | 300 | 17 | 74 | 0 | 57 | 38 | 385 | 53 | 0 | 17 | 17 | 0 | 17 | 0 | 94 | 17 | 0 | 163 | 0 |  | 814 | 0 | 0 | 0 | 94 | 0 | 0 | 0 | 37 | 75 | 40 | 175 | 36 | 16 | 0 | 0 | 0 | 28 | 0 | 78 | 21 | 42 | 40 | 34 | 35 | 20 | 0 | 8 | 75 | 0 | 250 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 153 | 0 | 345 | 55 | 0 | 50 | 105 | 34 | 0 | 0 | 55 | 1244 | 0 | 0 | 150 | 0 | 0 | 114 | 0 | 0 | 0 | 0 | 0 | 592 | 0 | 0 |  | 8757 | 4995 | 13752 | 4015 | 814 | 2215 | 462 | 3134 | 2161 | 27 | 0 | 770 | 154 | 0 | 1478.34 | 74.51
22:00 | 0 | 0 | 120 | 180 | 0 | 22 | 0 | 398 | 334 |  | 0 | 450 | 303 | 63 | 97 | 15 | 200 | 0 | 0 | 72 | 92 | 146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 20 | 26 | 25 | 25 | 39 | 0 | 0 | 27 | 115 | 0 | 17 | 222 | 0 | 0 | 0 |  | 12 | 56 | 84 | 33 | 30 | 44 | 8 | 34 | 0 | 0 | 0 | 310 | 305 | 204 | 187 | 0 | 36 | 0 | 0 | 43 | 0 | 35 | 52 | 17 | 7 | 33 | 20 | 164 | 82 | 0 | 18 | 0 | 43 | 28 | 53 | 49 | 0 | 0 | 59 | 80 | 0 | 204 | 18 | 0 | 10 | 285 | 16 | 11 | 0 | 278 | 303 | 80 | 97 | 80 | 145 | 0 | 38 | 69 | 143 | 367 | 98 | 105 | 87 | 0 | 286 | 17 | 97 | 0 | 57 | 38 | 390 | 50 | 0 | 17 | 17 | 0 | 17 | 0 | 95 | 17 | 0 | 163 | 0 |  | 813 | 0 | 0 | 0 | 93 | 0 | 0 | 0 | 37 | 75 | 40 | 175 | 37 | 16 | 0 | 0 | 0 | 28 | 0 | 78 | 21 | 42 | 40 | 34 | 35 | 20 | 0 | 8 | 76 | 0 | 250 | 0 | 0 | 184 | 0 | 0 | 0 | 0 | 0 | 156 | 0 | 354 | 55 | 0 | 50 | 105 | 34 | 0 | 0 | 55 | 1244 | 0 | 0 | 150 | 0 | 0 | 114 | 0 | 0 | 0 | 0 | 0 | 638 | 0 | 0 |  | 8851 | 5057 | 13908 | 4052 | 813 | 2261 | 463 | 3143 | 2208 | 27 | 0 | 777 | 164 | 0 | 1138.36 | 74.51
23:00 | 0 | 0 | 120 | 180 | 0 | 22 | 0 | 396 | 305 |  | 0 | 450 | 254 | 53 | 97 | 15 | 160 | 0 | 0 | 72 | 50 | 146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 20 | 26 | 25 | 20 | 39 | 0 | 0 | 0 | 115 | 0 | 17 | 226 | 0 | 0 | 0 |  | 12 | 56 | 84 | 33 | 21 | 40 | 8 | 16 | 0 | 0 | 0 | 310 | 305 | 207 | 195 | 0 | 33 | 0 | 0 | 43 | 0 | 35 | 50 | 18 | 7 | 33 | 20 | 176 | 72 | 0 | 18 | 0 | 43 | 28 | 53 | 49 | 0 | 0 | 60 | 81 | 0 | 194 | 17 | 0 | 10 | 285 | 16 | 11 | 0 | 278 | 58 | 25 | 97 | 27 | 144 | 0 | 38 | 92 | 143 | 319 | 98 | 105 | 87 | 0 | 208 | 17 | 104 | 0 | 75 | 38 | 340 | 35 | 0 | 17 | 17 | 0 | 17 | 0 | 85 | 17 | 0 | 163 | 0 |  | 771 | 0 | 0 | 0 | 94 | 0 | 0 | 0 | 37 | 75 | 40 | 170 | 37 | 16 | 0 | 0 | 0 | 28 | 0 | 78 | 21 | 42 | 40 | 0 | 35 | 20 | 0 | 8 | 76 | 0 | 250 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 309 | 55 | 0 | 35 | 105 | 60 | 0 | 0 | 35 | 1200 | 0 | 0 | 150 | 0 | 0 | 114 | 0 | 0 | 0 | 0 | 0 | 643 | 0 | 0 |  | 8113 | 4881 | 12994 | 3884 | 771 | 2129 | 110 | 2978 | 2169 | 0 | 0 | 777 | 176 | 0 | 1724.73 | 74.5
24:00 | 0 | 0 | 120 | 180 | 0 | 22 | 0 | 379 | 336 |  | 0 | 450 | 293 | 32 | 88 | 15 | 190 | 0 | 0 | 72 | 50 | 146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 26 | 25 | 25 | 16 | 0 | 0 | 0 | 115 | 0 | 17 | 225 | 0 | 0 | 0 |  | 12 | 56 | 84 | 22 | 0 | 11 | 8 | 32 | 0 | 0 | 0 | 310 | 305 | 207 | 197 | 0 | 34 | 0 | 0 | 43 | 0 | 35 | 48 | 18 | 7 | 33 | 20 | 170 | 72 | 0 | 18 | 0 | 43 | 28 | 53 | 49 | 0 | 0 | 59 | 81 | 0 | 202 | 17 | 0 | 10 | 290 | 16 | 8 | 0 | 278 | 12 | 25 | 88 | 25 | 144 | 0 | 38 | 120 | 150 | 368 | 98 | 105 | 81 | 0 | 87 | 17 | 66 | 0 | 75 | 38 | 390 | 34 | 0 | 17 | 47 | 0 | 17 | 0 | 94 | 17 | 0 | 163 | 0 |  | 813 | 0 | 0 | 0 | 95 | 0 | 0 | 0 | 33 | 75 | 40 | 170 | 37 | 0 | 0 | 0 | 0 | 28 | 0 | 78 | 21 | 42 | 40 | 0 | 35 | 20 | 0 | 8 | 75 | 0 | 250 | 0 | 0 | 183 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 372 | 55 | 0 | 35 | 105 | 63 | 0 | 0 | 35 | 1140 | 0 | 0 | 150 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 645 | 0 | 0 |  | 8034 | 4901 | 12935 | 3974 | 813 | 2285 | 62 | 2748 | 2110 | 0 | 0 | 773 | 170 | 0 | 1399.075 | 74.5
KWH | 0 | 0 | 2787406 | 4183200 | 0 | 516454 | 0 | 9650170 | 7444000 |  | 0 | 10012500 | 7096378 | 1079040 | 2170958 | 386968 | 4588293 | 0 | 0 | 1318915 | 1171008 | 2176320 | 8746 | 0 | 0 | 0 | 276480 | 443525 | 443193 | 425592 | 552000 | 541800 | 757300 | 661700 | 560640 | 0 | 0 | 324000 | 2700000 | 0 | 456975 | 5248249 | 0 | 0 | 0 |  | 239040 | 1115820 | 1886967 | 641640 | 171840 | 44352 | 191472 | 387360 | 0 | 0 | 0 | 8021500 | 7665000 | 4882000 | 4315636 | 0 | 807624 | 0 | 0 | 939772 | 0 | 799008 | 1023672 | 378324 | 156240 | 698400 | 379740 | 3783360 | 1200960 | 0 | 359064 | 14900 | 745000 | 640080 | 1218000 | 1099008 | 0 | 0 | 1287648 | 1865280 | 0 | 5081260 | 386000 | 0 | 242460 | 6985500 | 311304 | 220416 | 0 | 3788725 | 4059373 | 1320586 | 1509600 | 1296796 | 1712736 | 136215 | 707520 | 1029600 | 1286327 | 9277000 | 1536000 | 2322029 | 1211054 | 33242 | 2948182 | 437970 | 1502102 | 296400 | 813120 | 730560 | 8616000 | 947520 | 345340 | 1144800 | 434073 | 0 | 495000 | 209228 | 1593600 | 432720 | 0 | 3529454 | 0 |  | 21542545 | 0 | 1299744 | 0 | 1635840 | 0 | 0 | 0 | 507360 | 1203840 | 736500 | 4191611 | 704800 | 289824 | 0 | 0 | 0 | 583584 | 230961 | 1733908 | 524560 | 880579 | 655300 | 273845 | 231400 | 371520 | 0 | 148860 | 1746327 | 0 | 5939900 | 0 | 0 | 4233600 | 0 | 0 | 0 | 0 | 0 | 3639182 | 0 | 6434981 | 936960 | 0 | 814944 | 2404224 | 853795 | 0 | 60616 | 817632 | 31121100 | 0 | 0 | 1617600 | 35520 | 619200 | 2644416 | 843640 | 0 | 0 | 246983 | 0 | 17231080 | 1475480 | 0 |  | 183870329 | 121463761 | 305334090 | 96913739 | 21542545 | 49633649 | 6676755 | 51747349 | 56038407 | 324000 | 843640 | 14653922 | 3783360 | 3176724 | 0
Fuel Cost | 0 | 0 | 4069612.76 | 6232968 | 0 | 686883.82 | 0 | 10132678.5 | 8039520 |  | 0 | 10913625 | 7876979.58 | 12063667.2 | 28765193.5 | 5127326 | 5138888.16 | 0 | 0 | 19282537.3 | 16476082.56 | 35278147.2 | 80638.12 | 0 | 0 | 0 | 3516825.6 | 5987587.5 | 5943218.13 | 319194 | 414000 | 0 | 0 | 0 | 9536486.4 | 0 | 0 | 87480 | 5103000 | 0 | 7471541.25 | 5458178.96 | 0 | 0 | 0 |  | 3119472 | 18611877.6 | 32116178.34 | 8668556.4 | 2178931.2 | 513152.64 | 243169.44 | 1289908.8 | 0 | 0 | 0 | 8903865 | 8354850 | 5663120 | 5567170.44 | 0 | 912615.12 | 0 | 0 | 1569419.24 | 0 | 13798868.16 | 13768388.4 | 518303.88 | 117180 | 1222200 | 284805 | 27164524.8 | 1309046.4 | 0 | 488327.04 | 237506 | 1020650 | 844905.6 | 2119320 | 1901283.84 | 0 | 0 | 2498037.12 | 4252838.4 | 0 | 5132072.6 | 829900 | 0 | 480070.8 | 6985500 | 233478 | 167516.16 | 0 | 51716096.25 | 85084458.08 | 27296512.62 | 20349408 | 26804773.32 | 23721393.6 | 1592353.35 | 7301606.4 | 14064336 | 17069559.29 | 8534840 | 18677760 | 33576539.34 | 15319833.1 | 0 | 34611656.68 | 4769493.3 | 15967344.26 | 4022148 | 10481116.8 | 8605996.8 | 7926720 | 12270384 | 4990163 | 14527512 | 4939750.74 | 0 | 6464700 | 2500274.6 | 23856192 | 5698922.4 | 0 | 0 | 0 |  | 64627635 | 0 | 1455713.28 | 0 | 17029094.4 | 0 | 0 | 0 | 9137553.6 | 21669120 | 10583505 | 4694604.32 | 1367312 | 3159081.6 | 0 | 0 | 0 | 9786703.68 | 4039507.89 | 27118321.12 | 4039112 | 14582388.24 | 11081123 | 3732507.35 | 3903718 | 769046.4 | 0 | 112687.02 | 10146159.87 | 0 | 31422071 | 0 | 0 | 4910976 | 0 | 0 | 0 | 0 | 0 | 4221451.12 | 0 | 6370631.19 | 12592742.4 | 0 | 9640787.52 | 34741036.8 | 10843196.5 | 0 | 669806.8 | 9926052.48 | 280401111 | 0 | 0 | 11970240 | 401731.2 | 7263216 | 40538897.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 909831111.89 | 688948841.06 | 1598779952.95 | 107469553.48 | 64627635 | 60189509.51 | 139185744.02 | 673889994.73 | 321969341.87 | 87480 | 0 | 186541118.59 | 27164524.8 | 17655050.95 | 0
Yesterday Day Peak | 0 | 0 | 120 | 170 | 0 | 22 | 0 | 394 | 235 |  | 0 | 450 | 292 | 68 | 95 | 55 | 202 | 0 | 0 | 72 | 40 | 98 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 20 | 23 | 33 | 25 | 30 | 0 | 0 | 27 | 115 | 0 | 8 | 212 | 0 | 0 | 0 |  | 12 | 42 | 63 | 22 | 0 | 8 | 8 | 2 | 0 | 0 | 0 | 305 | 320 | 198 | 177 | 0 | 33 | 0 | 0 | 43 | 0 | 35 | 35 | 15 | 7 | 25 | 15 | 160 | 28 | 0 | 13 | 2 | 0 | 28 | 47 | 41 | 0 | 0 | 49 | 74 | 0 | 201 | 17 | 0 | 10 | 285 | 8 | 8 | 0 | 190 | 303 | 76 | 75 | 75 | 128 | 20 | 25 | 51 | 18 | 391 | 78 | 88 | 30 | 5 | 82 | 17 | 54 | 0 | 55 | 25 | 354 | 53 | 46 | 72 | 17 | 0 | 35 | 29 | 95 | 17 | 0 | 108 | 0 |  | 911 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 11 | 22 | 32 | 170 | 23 | 64 | 0 | 0 | 0 | 21 | 4 | 72 | 21 | 0 | 40 | 8 | 0 | 11 | 0 | 8 | 75 | 0 | 200 | 0 | 0 | 159 | 0 | 0 | 0 | 0 | 0 | 133 | 0 | 227 | 36 | 0 | 35 | 50 | 34 | 0 | 7 | 35 | 1200 | 0 | 0 | 17 | 5 | 75 | 95 | 200 | 0 | 0 | 33 | 0 | 742 | 197 | 0 |  | 12970 | DayPeak
Yesterday Evening Peak | 0 | 0 | 120 | 180 | 0 | 22 | 0 | 399 | 334 | 0 | 0 | 450 | 293 | 49 | 97 | 15 | 200 | 0 | 0 | 75 | 92 | 146 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 20 | 25 | 25 | 25 | 39 | 0 | 0 | 27 | 115 | 0 | 17 | 220 | 0 | 0 | 0 | 0 | 12 | 48 | 84 | 33 | 30 | 44 | 8 | 26 | 0 | 0 | 0 | 310 | 305 | 203 | 175 | 0 | 33 | 0 | 0 | 43 | 0 | 36 | 52 | 17 | 7 | 33 | 20 | 154 | 68 | 0 | 18 | 0 | 43 | 28 | 53 | 48 | 0 | 0 | 56 | 80 | 0 | 204 | 17 | 0 | 10 | 280 | 16 | 8 | 0 | 278 | 302 | 80 | 95 | 80 | 144 | 0 | 38 | 69 | 137 | 369 | 98 | 105 | 87 | 0 | 300 | 17 | 74 | 0 | 57 | 38 | 385 | 53 | 0 | 17 | 17 | 0 | 17 | 0 | 94 | 17 | 0 | 163 | 0 |  | 814 | 0 | 0 | 0 | 94 | 0 | 0 | 0 | 37 | 75 | 40 | 175 | 36 | 16 | 0 | 0 | 0 | 28 | 0 | 78 | 21 | 42 | 40 | 34 | 35 | 20 | 0 | 8 | 75 | 0 | 250 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 153 | 0 | 345 | 55 | 0 | 50 | 105 | 34 | 0 | 0 | 55 | 1244 | 0 | 0 | 150 | 0 | 0 | 114 | 0 | 0 | 0 | 0 | 0 | 592 | 0 | 0 |  | 13752 | EvPeak
Forecast for Evening | 0 | 0 | 120 | 180 | 0 | 22 | 0 | 412 | 330 | 0 | 0 | 450 | 300 | 70 | 97 | 15 | 200 | 0 | 0 | 75 | 92 | 149 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 23 | 28 | 33 | 33 | 50 | 0 | 0 | 25 | 120 | 0 | 25 | 225 | 0 | 0 | 0 | 0 | 12 | 60 | 84 | 44 | 50 | 39 | 8 | 20 | 0 | 0 | 0 | 310 | 340 | 200 | 180 | 0 | 42 | 0 | 0 | 43 | 0 | 34 | 52 | 18 | 7 | 33 | 20 | 166 | 70 | 0 | 17 | 0 | 43 | 29 | 50 | 50 | 0 | 0 | 60 | 84 | 0 | 210 | 17 | 0 | 10 | 300 | 16 | 10 | 0 | 300 | 300 | 100 | 98 | 80 | 149 | 0 | 50 | 85 | 150 | 400 | 98 | 105 | 51 | 0 | 300 | 54 | 54 | 0 | 55 | 38 | 400 | 54 | 0 | 162 | 17 | 0 | 35 |  | 94 | 34 | 0 | 163 |  |  | 932 | 0 | 0 |  | 98 | 0 | 0 | 0 | 43 | 76 | 40 | 181 | 32 | 64 | 0 | 0 | 0 | 28 | 31 | 83 | 21 | 42 | 40 | 43 | 34 | 22 | 0 | 8 | 75 | 0 | 250 | 0 | 0 | 164 |  | 0 | 0 | 0 | 0 | 142 | 0 | 345 | 53 | 0 | 50 | 105 | 50 | 0 | 0 | 55 | 1244 | 0 |  | 150 |  |  | 115 | 0 |  | 0 |  | 0 | 750 |  | 0
Forecast for Day | 0 | 0 | 120 | 180 | 0 | 22 | 0 | 412 | 330 | 0 | 0 | 450 | 300 | 70 | 97 | 15 | 200 | 0 | 0 | 34 | 40 | 100 | 0 | 0 | 0 | 0 | 0 | 55 | 35 | 22 | 23 | 23 | 33 | 33 | 16 | 0 | 0 | 25 | 120 | 0 | 25 | 225 | 0 | 0 | 0 | 0 | 12 | 56 | 84 | 22 | 0 | 6 | 8 | 5 | 0 | 0 | 0 | 310 | 310 | 200 | 180 | 0 | 41 | 0 | 0 | 40 | 0 | 36 | 52 | 18 | 7 | 33 | 20 | 150 | 44 | 0 | 16 | 1.6 | 43 | 29 | 50 | 44 | 0 | 0 | 56 | 84 | 0 | 210 | 17 | 0 | 10 | 300 | 16 | 10 | 0 | 145 | 300 | 70 | 57 | 70 | 35 | 20 | 25 | 34 | 20 | 400 | 50 | 88 | 51 | 5 | 85 | 17 | 54 | 0 | 55 | 38 | 400 | 54 | 50 | 72 | 17 | 0 | 17 | 30 | 94 | 34 | 0 | 163 |  |  | 932 | 0 | 0 | 0 | 85 | 0 | 0 | 0 | 19 | 20 | 32 | 180 | 22 | 16 | 0 | 0 | 0 | 28 | 0 | 80 | 21 | 42 | 24 | 8 | 34 | 22 | 0 | 8 | 75 | 0 | 250 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 300 | 17 | 0 | 35 | 105 | 34 | 0 | 8 | 35 | 1244 | 0 |  | 17 | 6 | 100 | 115 | 0 |  | 0 | 30 | 0 | 750 | 130 | 0 |  |  |  |  | g | h | o | c | h | t | s
Generation at 08:00(Today) | 0 | 0 | 120 | 180 | 0 | 22 | 0 | 399 | 305 | 0 | 0 | 450 | 305 | 24 | 99 | 15 | 150 | 0 | 0 | 34 | 33 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 23 | 26 | 33 | 16 | 16 | 0 | 0 | 0 | 115 | 0 | 25 | 223 | 0 | 0 | 0 | 0 | 6 | 55 | 84 | 10 | 0 | 6 | 8 | 2 | 0 | 0 | 0 | 300 | 310 | 205 | 199 | 0 | 33 | 0 | 0 | 43 | 0 | 36 | 52 | 18 | 7 | 33 | 20 | 150 | 27 | 0 | 18 | 1 | 43 | 29 | 53 | 48 | 0 | 0 | 40 | 81 | 0 | 203 | 17 | 0 | 10 | 285 | 16 | 5 | 0 | 97 | 0 | 0 | 48 | 0 | 17 | 10 | 12 | 17 | 20 | 368 | 49 | 88 | 17 | 2 | 88 | 17 | 54 | 0 | 9 | 12 | 360 | 24 | 22 | 17 | 17 | 0 | 17 | 15 | 18 | 17 | 0 | 108 | 0 | 0 | 917 | 0 | 0 | 0 | 81 | 0 | 0 | 0 | 23 | 72 | 8 | 173 | 22 | 0 | 0 | 0 | 0 | 28 | 0 | 52 | 21 | 42 | 24 | 8 | 28 | 20 | 0 | 8 | 75 | 0 | 250 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 159 | 0 | 309 | 36 | 0 | 35 | 105 | 12 | 0 | 3 | 35 | 1160 | 0 | 0 | 17 | 2 | 50 | 115 | 0 | 0 | 0 | 14 | 0 | 747 | 89 | 0 | 0 |  |  |  | 146.5474 | 21.5425 | 73.9217 | 56.0384 | 0.324 | 3.7834 | 3.1767
305.3341
| Minimum Generation |  | 11741 | 6:00
| Highest Generation |  | 13908 | 22:00
| Day Peak Generation |  | 12970 | 12:00
| Evening Peak Generation |  | 13752 | 21:00
| HVDC Max Flow |  | 913 | 10:00
| HVDC EvPeak Flow |  | 814 | 21:00
| Load factor L.F |  | 91.47% | [161 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2023-05-10
Till now the maximum generation is : - |  |  |  | 15648 | 21:00 | Hrs on | 2023-04-19
The Summary of Yesterday's |  |  | 2023-05-09 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 12970 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 11392
Evening Peak Generation : |  |  | 13752 | MW Hour : | 21:00 | Available Max Generation : |  | 14761
E.P. Demand (at gen end) : |  |  | 15300 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 15600
Maximum Generation : |  |  | 13908 | MW Hour : | 22:00 | Reserve(Generation end) |  | -
Total Gen. (MKWH) : |  |  | 305.3341 | System Load Factor : | 91.47% | Load Shed : |  | 793
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 500 | MW at | 19:30 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2023-05-10
Actual : |  | 74.47 | Ft.(MSL) , | Rule curve : | 80.29 | Ft.( MSL )
Gas Consumed : |  | Total = | 1113.4 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 167659062.99
: |  |  | Coal : | 321969341.87 | Oil : | 999616857.34 | Total : | 1489245262.2
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 172 | 4128:00 | 5098.9131 |  |  | 199 | 3.903%
Chittagong Area |  | 200 | 4800:00 | 1416.2754 |  |  | 86 | 6.072%
Khulna Area |  | 292 | 7008:00 | 1862.9675 |  |  | 120 | 6.441%
Rajshahi Area |  | 150 | 3600:00 | 1645.1712 |  |  | 114 | 6.929%
Cumilla Area |  | 221 | 5304:00 | 1403.9755 |  |  | 94 | 6.695%
Mymensingh Area |  | 258 | 6192:00 | 1154.9797 |  |  | 83 | 7.186%
Sylhet Area |  | 93 | 2232:00 | 520.9909 |  |  | 32 | 6.142%
Barisal Area |  | 0 | 0:00 | 420.9926 |  |  | 0 | 0%
Rangpur Area |  | 92 | 2208:00 | 911.984 |  |  | 65 | 7.127%
Total |  | 1478 |  | 14436.25 |  |  | 793
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 2
2) Ghorasal-3,7
3) Bhula Nuton Biddut
4) Baghabari-100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
7) Shajibazar 330 MW
8) Sirajganj- 2
9) Barishal 307 MW
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
| 08:12 | Goalpara 132/33kV S/S T-6 HT is restored.
| 08:13 | Bhandaria 132/33kV S/S Transformer-1 HT is restored.
08:42 |  | Khulna 330 MW CCPP GT was sync.
09:06 |  | Matarbari 400/11KV SUT1 SD for project work by P/S
| 09:28 | Joydebpur 132/33kV S/S GT-2 HT is restored.
10:05 | 11:03 | Hathazari-Kaptai 132kV Ckt-1 Forced S/D from Hathazari 230/132/33kV end Due to gantry structure clean.
10:29 |  | Bheramara 410MW tripped
10:36 | 10:36 | Aminbazar 400/230/132kV S/S 132 kv Bus 02 Forced S/D Due to Bus Separated Load Distribution : 230/132 kv Tr 1,2 & 3 + Mirpur 1 & 2 + MPP 1 & 2
10:36 | 10:36 | Aminbazar 400/230/132kV S/S 132 kv Bus 01 Forced S/D Due to Bus Separated Load Distribution : 400/132kv Tr + Kalyanpur 1 & 2
10:41 |  | Madunaghat-TKCL 132kV Ckt-1 Forced S/D from Madunaghat 132/33kV end Due to Over current flow through the Hathazari ckt.
10:42 |  | Madunaghat-Sikalbaha 132kV Ckt-2 Forced S/D from Madunaghat end Due to Over current flow through the Hathazari ckt.
14:19 | 15:25 | Joydebpur 132/33kV S/S GT-3 HT Scheduled S/D Due to Bushing Hot - Spot Maintenance.
16:04 | 17:59 | Niamatpur 132/33kV S/S 407T HT Forced S/D Due to 33 kV bus Red hot. | [5 empty] | 24 MW Power interrupt.
| 18:14 | Tongi 230/132/33kV S/S T-1 HT is restored.
18:38 | 18:56 | Coxsbazar 132/33kV S/S 405T-T1 HT Tripped showing ABB (model RET670) relays Due to Over Load (Over Current). | [5 empty] | 70 MW Power interrupt.
22:57 | 01:02 | Kaliakoir 400/230/132kV S/S 400/132kV TR1 LT Forced S/D Due to Red Hot.
05:38 | 07:36 | Brahmanbaria-Shahjibazar 132 kV Ckt-2 S/D due to Hot spot maintenance work at Shahjibazar end
05:41 | 07:36 | Shahjibazar 132/33kV S/S BPDB 60 MW Scheduled S/D Due to Red hot maintenance at CB: 852 D/S loop jont .
06:49 |  | Nawabganj 132/33kV S/S TR-2 LT Forced S/D Due to Due to red hot maintenance Bay 105.
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2023-05-09 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 120 | 2787406 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4183200
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 22 | 516454 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 399 | 9650170
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 334 | 7444000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 10012500
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 49 | 1079040 | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 293 | 7096378 | FGMO
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 97 | 2170958 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 15 | 386968 | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 8746 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 425592
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 75 | 1318915 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 200 | 4588293 | ST under maint
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 92 | 1171008 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 17 | 276480 | Fuel shortage
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 146 | 2176320
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 0 | 443525 | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 0 | 443193 | Fuel shortage
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 45 | 1093800 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 757300
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 661700 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 39 | 560640 | 0:00
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 278 | 3788725 | Machine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 302 | 4059373
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 80 | 1320586 | Fuel shortage
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 80 | 1296796 | Engine problem
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 144 | 1712736 | Engine problem
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 2322029
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 53 | 947520 | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 17 | 1144800 | Fuel shortage
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 209228
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 432720 | Fuel shortage
| Dhaka area Total |  |  |  | 5847 | 3721 | 76487099
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 115 | 2700000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 17 | 456975
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 136215
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 44 | 44352 | Engine problem
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 27 | 324000 | Low Water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 220 | 5248249
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 87 | 1211054 | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 48 | 1115820 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 84 | 1886967 | Engine problem
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 33 | 641640 | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 38 | 707520 | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 8 | 191472 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 26 | 387360
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 30 | 171840 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 33242
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 300 | 2948182
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 17 | 437970 | Fuel shortage
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 74 | 1502102 | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 38 | 730560
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 17 | 434073 | Fuel shortage
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 0 | 163 | 3529454
| Chattogram area Total |  |  |  | 2382 | 1386 | 24839047
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 203 | 4882000 | FGMO
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 310 | 8021500 | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 305 | 7665000 | FGMO
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 0 | 0 | Under maint.
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 33 | 807624 | Gas shortage
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 0 | 0 | Contract Expired
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 175 | 4315636 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 939772 | Machine problem
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 137 | 1286327 | Fuel shortage
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 36 | 799008 | Engine problem
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 69 | 1029600 | Fuel shortage
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 17 | 378324 | Engine problem
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 7 | 156240 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 154 | 3783360
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 698400
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 1023672
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 20 | 379740 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Contract Expired
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 296400 | Fuel shortage
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 57 | 813120 | Fuel shortage
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 495000 | Engine problem
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 94 | 1593600 | Engine problem
| Cumilla Area Total |  |  |  | 3151 | 1762 | 39364323
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 68 | 1200960 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 359064 | Engine problem
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 14900
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 95 | 1509600 | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 98 | 1536000 | Fuel shortage
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 345340
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 239040 | Engine problem
| Mymensingh Area Total |  |  |  | 614 | 291 | 5204904
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 745000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 28 | 640080 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Under maint.
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 1218000
| Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 48 | 1099008
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 8 | 220416
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 56 | 1287648
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 80 | 1865280
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 204 | 5081260 | Machine problem
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 386000
| Sylhet 50MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 311304 | Engine problem
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 280 | 6985500 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 369 | 9277000 | FGMO
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 242460
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 385 | 8616000
| Sylhet Area Total |  |  |  | 2427 | 1597 | 37974956
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Fuel shortage
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 814 | 21542545
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 94 | 1635840 | Engine problem
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 37 | 507360
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel conservation
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 75 | 1203840 | Engine problem
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 0 | 1299744 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 40 | 736500
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Contract Expired
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 55 | 936960 | Fuel shortage
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 105 | 2404224
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 619200
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 0 | 0 | 843640 | On test.
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 660*2 | 617 | 0 | 0 | On test.
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3001 | 1220 | 31729853
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 16 | 289824 | Fuel shortage
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 36 | 704800 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 175 | 4191611 | Machine problem
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1244 | 31121100
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 0 | 0 | Under maint.
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 150 | 1617600
| Barisal 307 MW |  | BCPCL | 307*1 | 307 | 0 | 0 | Coal shortage
| Barisal Area Total |  |  |  | 2265 | 1621 | 37924935
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 28 | 583584 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 230961 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 21 | 524560 | Engine problem
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 42 | 880579 | Engine problem
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 40 | 655300 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 180 | 4233600 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 153 | 3639182 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 345 | 6434981 | Gas shortage
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 35 | 231400 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 20 | 371520
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 148860 | Engine problem
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 34 | 273845 | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 78 | 1733908 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Fuel shortage
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 50 | 814944 | Fuel shortage
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 55 | 817632 | Fuel shortage
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 35520
| Adani Power Jharkhanda Ltd |  | Import | 0 | 0 | 592 | 17231080 | On test.
| Rajshahi Area Total |  |  |  | 2129 | 1681 | 38841456
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 75 | 1746327
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 250 | 5939900
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 34 | 853795 | Fuel shortage
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 60616
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 114 | 2644416
| Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 246983
| Teesta Solar Limited |  | BPCL | 16*12.5 | 0 | 0 | 1475480
| Rangpur Area Total |  |  |  | 750 | 473 | 12967517
| Total |  |  |  | 22566 | 13752 | 305334090
| Eastern Grid Total |  |  |  | 14421 | 8757 | 183870329
| Western Grid Total |  |  |  | 8145 | 4995 | 121463761
| National Grid Total |  |  |  | 22566 | 13752 | 305334090
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2023-05-09
| (a) ENTIRE EASTERN GRID : |  | 8993.71 | MW | (b) ENTIRE WESTERN GRID : |  | 4200.1 | MW
| i) Dhaka area |  | 5060.01 | MW | i) Khulna area |  | 1490.7 | MW
| ii) Chittagong area |  | 1247.7 | MW | ii) Rajshahi area |  | 1370.4 | MW
| iii) Comilla area |  | 1247 | MW | iii) Barisal area |  | 478 | MW
| iv) Mymensingh area |  | 907 | MW | iv) Rangpur area |  | 861 | MW
| v) Sylhet area |  | 532 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 13193.81 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | Chhatak | 34 | 19:00 | Kamrangirchar | 55 | 16:00 | Natore | 132 | 22:00 | Shitalakhya | 127 | 16:00
2 | AKSML | 6.7 | 18:00 | Chowmuhani | 205 | 19:30 | Kaptai | 5 | 19:00 | Nawabganj | 52.9 | 21:00 | Sholosohor | 35 | 09:00
3 | Aftabnagar | 62 | 13:00 | Chuadanga | 89 | 00:00 | Kazla | 96 | 13:00 | Netrakona | 114 | 22:00 | Shyampur | 156 | 23:00
4 | Agargaon | 97 | 13:00 | Coxsbazar | 128 | 18:30 | Keranigonj | 60 | 16:00 | New | 90 | 15:00 | Siddhirganj | 120 | 11:00
5 | Agrabad | 78 | 10:00 | Cumilla(N) | 174 | 21:00 | Khagrachori | 30 | 21:00 | Niamatpur | 97 | 21:00 | Sirajganj | 112 | 19:30
6 | Amnura | 62 | 22:00 | Cumilla(S) | 176 | 23:00 | Khulna | 102 | 13:00 | Noapara | 40 | 13:00 | Sonargaon | 90 | 11:00
7 | Ashuganj | 67 | 13:00 | Daudkandi | 131 | 21:00 | Khulshi | 180 | 18:00 | PHP | 5 | 13:00 | Sreemongol | 70 | 19:00
8 | BIPTC | N/A | N/A | Dhaka | 38 | 11:00 | Kishoreganj | 128 | 10:00 | Pabna | 99 | 22:00 | Sreepur | 63.92 | 10:00
9 | BSRM | 112 | 19:00 | Dhamrai | 124 | 20:00 | Kodda | 304 | 18:30 | Palashbari | 142 | 19:30 | Srinagar | 50.11 | 21:00
10 | Bagerhat | 83 | 22:00 | Dhanmondi | 148 | 13:00 | Kulaura | 48 | 18:30 | Panchagarh | 48 | 19:30 | Sunamganj | 52 | 18:30
11 | Bakulia | 103 | 00:00 | Dohazari | 96 | 18:30 | Kurigram | 62 | 21:00 | Patuakhali | 124 | 23:00 | Sylhet | 168 | 19:00
12 | Banani | 88 | 13:00 | Faridpur | 134 | 00:00 | Kushtia | 124 | 18:00 | Payra | 24 | 23:00 | TK | 33.5 | 21:00
13 | Bangabhaban | 28 | 10:00 | Fatullah | 72 | 16:00 | Lalbag | 80 | 17:00 | Postogola | 47 | 00:00 | Tangail | 216 | 19:30
14 | Barapukuria | 59 | 21:00 | Fenchuganj | 48 | 18:00 | Lalmonirhat | 46 | 21:00 | Purbachal | 23 | 23:00 | Thakurgaon | 89 | 20:00
15 | Barguna | 24 | 23:00 | Feni | 109 | 22:00 | Madanganj | 42 | 00:00 | Purbasadipur | 119 | 07:00 | Tongi | 107 | 11:00
16 | Barishal | 115 | 21:00 | GPH | 83 | 15:00 | Madaripur | 95 | 22:00 | Rahanpur_I | 0 | 00:00 | Ullon | 46 | 00:00
17 | Barishal-230 | 104 | 19:00 | Ghorashal | 71 | 11:00 | Madartek | 100 | 23:00 | Rahim | 44 | 15:00 | Uttara | 79 | 16:00
18 | Baroaulia | 66 | 23:00 | Goalpara | 36 | 18:30 | Madunaghat | 52 | 21:00 | Rajbari | 64 | 19:00 | UttaraNew | 56 | 15:00
19 | Baroirhat | 59 | 00:00 | Gollamari | 61 | 00:00 | Magura | 52 | 13:00 | Rajendrapur | 96 | 13:00 | Zigatola | 86 | 22:00
20 | Bashundhara | 202 | 16:00 | Gopalganj | 96.4 | 00:00 | Mahasthangarh | 78 | 19:30 | Rajshahi | 162 | 21:00
21 | BashundharaCement | 11 | 11:00 | Gulshan | 86 | 12:00 | Manikganj | 105 | 21:00 | Rajshahi-230 | 38 | 21:00
22 | Beanibazar | 80 | 19:00 | Halishahar | 93 | 07:00 | Maniknagar | 100 | 13:00 | Ramganj | 98 | 21:00
23 | Benapole | 58 | 21:00 | HaripurSBU | 155 | 11:00 | Matarbari | 48 | 00:00 | Rampur | 35 | 22:00
24 | Bhaluka | 128 | 22:00 | Hasnabad | 103 | 18:00 | Matuail | 70 | 10:00 | Rangamati | 14 | 11:00
25 | Bhandaria | 50 | 22:00 | Hathazari | 74 | 19:00 | Millgate | 104 | 12:00 | Rangpur | 125 | 21:00
26 | Bhangura | 38 | 18:30 | Ishurdi | 58 | 19:30 | Mirpur | 166 | 19:00 | Ruppur | 4.4 | 10:00
27 | Bheramara(GK) | 63 | 19:30 | Jaldhaka | 62 | 19:00 | Mirsorai | 4 | 19:30 | SSM | 15 | 10:00
28 | Bhulta | 238 | 18:00 | Jamalpur | 140 | 22:00 | Mithapukur | 38 | 22:00 | Saidpur | 104 | 21:00
29 | Bog-Sherpur | 70 | 19:00 | Jashore | 128 | 00:00 | Modern | 0 | 00:00 | Satkhira | 129 | 22:00
30 | Bogura | 151 | 22:00 | Jhenaidah | 118 | 18:30 | Mogbazar | 144 | 11:00 | Satmasjid | 131 | 23:00
31 | Borhanuddin | 69 | 22:00 | Joydebpur | 157 | 18:00 | Mongla | 32 | 10:00 | Savar | 198 | 18:00
32 | Brahmanbaria | 143 | 00:00 | Joypurhat | 65 | 19:00 | Motijheel | 48 | 13:00 | Shahjadpur | 106 | 09:00
33 | Cantonment | 148 | 16:00 | Juldah | 28 | 00:00 | Munshiganj | 114 | 23:00 | Shahjibazar | 111 | 18:00
34 | Chandpur | 68 | 22:00 | KSRM | 28 | 16:00 | Mymensingh | 174 | 21:00 | Shahmirpur | 42 | 04:00
35 | Chandraghona | 27 | 20:00 | Kabirpur | 276 | 22:00 | Naogaon | 125 | 20:00 | Shariatpur | 73 | 18:30
36 | Chapai | 62 | 21:00 | Kachua | 67 | 22:00 | Narail | 52 | 19:00 | Sherpur | 110 | 19:00
37 | Charsaidpur | 49 | 01:00 | Kallyanpur | 114 | 20:00 | Narinda | 77 | 13:00 | Shikalbaha | 34 | 18:30
38 | Chauddagram | 59 | 18:30 | Kalurghat | 36 | 09:00 | Narshingdi | 169 | 23:00 | Shikalbaha-230 | N/A | N/A
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2023-05-09 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 403 | 19:30 | 391 | 12:00 | Kaliakoir | 390 | 21:00 | 378 | 14:00
| Bhulta | 389 | 19:00 | 374 | 12:00 | Madunaghat_I | 416 | 19:00 | 379 | 10:00
| Bibiana | 406 | 20:00 | 396 | 17:00 | Payra | 413 | 10:00 | 408 | 12:00
| BIPTC | 397 | 07:00 | 390 | 00:00 | Rahanpur_I | 417 | 23:00 | 412 | 14:00
| Gopalganj | 407 | 19:00 | 396 | 12:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 232 | 19:00 | 223 | 09:00 | Hathazari | 240 | 23:00 | 221 | 08:00
| AKSML | 233 | 23:00 | 207 | 01:00 | Ishurdi | 234 | 16:00 | 227 | 12:00
| Aminbazar | 234 | 18:30 | 225 | 16:00 | Jhenaidah | 227 | 19:30 | 221 | 12:00
| Ashuganj | 237 | 19:00 | 232 | 00:00 | Kaliakoir | 231 | 19:00 | 222 | 14:00
| Baghabari | 229 | 00:00 | 225 | 10:00 | Keranigonj | 231 | 19:00 | 225 | 20:00
| Barapukuria | 223 | 16:00 | 216 | 18:30 | Khulna(S) | 233 | 10:00 | 225 | 15:00
| Barishal | 240 | 10:00 | 231 | 22:00 | Madunaghat_I | 241 | 19:00 | 219 | 10:00
| Bheramara | 233 | 20:00 | 225 | 11:00 | Maniknagar | 230 | 19:00 | 223 | 12:00
| Bhulta | 233 | 19:00 | 224 | 12:00 | Meghnaghat | 235 | 19:30 | 230 | 08:00
| Bibiana | 239 | 20:00 | 233 | 02:00 | Mirsorai | 242 | 23:00 | 225 | 12:00
| BIPTC | 233 | 16:00 | 225 | 11:00 | Rajshahi | 233 | 16:00 | 224 | 11:00
| Bogura | 225 | 16:00 | 219 | 11:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 241 | 00:00 | 236 | 21:00 | Rampura | 229 | 03:00 | 223 | 11:00
| BSRM | 239 | 23:00 | 226 | 12:00 | Shikalbaha | 234 | 23:00 | 220 | 00:00
| Cumilla(N) | 233 | 19:00 | 224 | 12:00 | Shyampur | 232 | 19:00 | 225 | 09:00
| Fenchuganj | 240 | 16:00 | 235 | 09:00 | Siddhirganj | 232 | 02:00 | 226 | 12:00
| Ghorashal | N/A | N/A | N/A | N/A | Sirajgonj | 236 | 00:00 | 230 | 06:00
| GPH | 238 | 23:00 | 222 | 10:00 | Sreepur | 235 | 20:00 | 227 | 18:30
| Haripur | 228 | 00:00 | 223 | 11:00 | Tongi | 228 | 18:30 | 220 | 09:00
| Hasnabad | 230 | 17:00 | 225 | 09:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 137 | 04:00 | 129 | 14:00 | Lalbag | 138 | 04:00 | 132 | 09:00
| Agargaon | 132 | 04:00 | 127 | 09:00 | Lalmonirhat | 130 | 00:00 | 122 | 19:00
| Agrabad | 138 | 18:30 | 125 | 10:00 | Madanganj | 135 | 19:00 | 128 | 9:00
| AKS | 135 | 18:30 | 126 | 11:00 | Madaripur | 130 | 03:00 | 126 | 11:00
| Aminbazar | 133 | 18:30 | 124 | 12:00 | Madartek | 136 | 03:00 | 129 | 15:00
| Amnura | 137 | 13:00 | 131 | 22:00 | Madunaghat | 138 | 23:00 | 128 | 11:00
| Ashuganj | 136 | 00:00 | 134 | 12:00 | Magura | 134 | 23:00 | 128 | 11:00
| Bagerhat | 134 | 10:00 | 128 | 12:00 | Mahasthangarh | 132 | 13:00 | 126 | 22:00
| Bakulia | 139 | 19:00 | 128 | 10:00 | Manikganj | 136 | 23:00 | 128 | 02:00
| Banani | 136 | 02:00 | 129 | 11:00 | Maniknagar | 133 | 03:00 | 126 | 12:00
| Bangabhaban | 132 | 03:00 | 126 | 12:00 | Matarbari | 138 | 19:00 | 110 | 00:00
| Barapukuria | 137 | 13:00 | 132 | 21:00 | Matuail | 133 | 19:00 | 129 | 09:00
| Barguna | 138 | 18:00 | 132 | 05:00 | Millgate | 135 | 19:30 | 122 | 14:00
| Barishal | 138 | 19:00 | 126 | 00:00 | Mirpur | 130 | 19:00 | 122 | 09:00
| Barishal-230 | 133 | 10:00 | 127 | 18:30 | Mithapukur | 132 | 16:00 | 124 | 22:00
| Baroaulia | 140 | 19:00 | 128 | 07:00 | Modern | 140 | 19:00 | 128 | 11:00
| Baroirhat | 133 | 23:00 | 123 | 04:00 | Mogbazar | 138 | 04:00 | 130 | 12:00
| Bashundhara | 130 | 19:30 | 121 | 12:00 | Mongla | 134 | 08:00 | 128 | 12:00
| BashundharaCement | 135 | 19:00 | 128 | 09:00 | Motijheel | 132 | 03:00 | 126 | 12:00
| Beanibazar | 129 | 06:00 | 124 | 18:30 | Munshiganj | 134 | 19:00 | 130 | 10:00
| Benapole | 132 | 23:00 | 124 | 15:00 | Mymensingh | 132 | 00:00 | 108 | 12:00
| Bhaluka | 131 | 02:00 | 111 | 12:00 | Naogaon | 128 | 16:00 | 120 | 11:00
| Bhandaria | 135 | 19:00 | 127 | 13:00 | Narail | 133 | 10:00 | 127 | 12:00
| Bhangura | 136 | 16:00 | 131 | 11:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bheramara | 133 | 06:00 | 127 | 12:00 | Narshingdi | 127 | 01:00 | 122 | 11:00
| Bheramara(GK) | 133 | 02:00 | 127 | 11:00 | Natore | 132 | 16:00 | 126 | 11:00
| Bhulta | 124 | 03:00 | 120 | 09:00 | Nawabganj | 139 | 19:00 | 132 | 09:00
| Bog-Sherpur | 134 | 16:00 | 128 | 22:00 | Netrakona | 135 | 23:00 | 112 | 13:00
| Bogura | 135 | 16:00 | 129 | 22:00 | New | 130 | 04:00 | 123 | 14:00
| Bogura-230 | 134 | 23:00 | 128 | 11:00 | Niamatpur | 126 | 17:00 | 115 | 22:00
| Brahmanbaria | 133 | 19:00 | 128 | 12:00 | Noapara | 136 | 23:00 | 130 | 15:00
| Cantonment | 131 | 04:00 | 126 | 12:00 | Pabna | 132 | 01:00 | 127 | 11:00
| Chandpur | 139 | 23:00 | 120 | 06:00 | Palashbari | 129 | 16:00 | 121 | 22:00
| Chandraghona | 140 | 23:00 | 129 | 08:00 | Panchagarh | 138 | 23:00 | 128 | 12:00
| Chapai | 134 | 13:00 | 132 | 01:00 | Patuakhali | 139 | 18:00 | 135 | 03:00
| Charsaidpur | 135 | 19:30 | 129 | 09:00 | Payra | 140 | 19:00 | 136 | 12:00
| Chauddagram | 134 | 23:00 | 123 | 06:00 | PHP | 129 | 01:00 | 122 | 04:00
| Chhatak | 130 | 06:00 | 127 | 13:00 | Postogola | 134 | 19:00 | 128 | 09:00
| Chowmuhani | 134 | 23:00 | 118 | 06:00 | Purbachal | 136 | 21:00 | 121 | 12:00
| Chuadanga | 129 | 19:30 | 120 | 18:30 | Purbasadipur | 134 | 23:00 | 124 | 11:00
| Coxsbazar | 131 | 23:00 | 110 | 00:00 | Rahim | 134 | 19:30 | 131 | 07:00
| Cumilla(N) | 136 | 23:00 | 129 | 08:00 | Rajbari | 129 | 06:00 | 123 | 12:00
| Cumilla(S) | 136 | 23:00 | 126 | 01:00 | Rajendrapur | 138 | 22:00 | 129 | 08:00
| Daudkandi | 132 | 13:00 | 127 | 09:00 | Rajshahi | 132 | 10:00 | 127 | 11:00
| Dhaka | 137 | 06:00 | 130 | 11:00 | Rajshahi-230 | 133 | 16:00 | 126 | 11:00
| Dhamrai | 132 | 19:00 | 127 | 09:00 | Ramganj | 135 | 23:00 | 119 | 06:00
| Dhanmondi | 133 | 02:00 | 129 | 09:00 | Rampur | 139 | 23:00 | 126 | 11:00
| Dohazari | 140 | 23:00 | 124 | 00:00 | Rampura | 137 | 03:00 | 130 | 10:00
| Faridpur | 129 | 03:00 | 125 | 11:00 | Rangamati | 139 | 23:00 | 127 | 11:00
| Fatullah | 135 | 19:00 | 129 | 09:00 | Rangpur | 133 | 15:00 | 123 | 21:00
| Fenchuganj | 136 | 16:00 | 133 | 12:00 | Ruppur | 134 | 10:00 | 128 | 11:00
| Feni | 131 | 23:00 | 123 | 07:00 | Saidpur | 135 | 23:00 | 125 | 22:00
| Ghorashal | 139 | 18:30 | 134 | 11:00 | Satkhira | 133 | 10:00 | 126 | 15:00
| Goalpara | 139 | 23:00 | 132 | 12:00 | Satmasjid | 131 | 04:00 | 126 | 12:00
| Gollamari | 135 | 02:00 | 123 | 11:00 | Savar | 133 | 19:30 | 124 | 00:00
| Gopalganj | 135 | 19:30 | 124 | 11:00 | Shahjadpur | 139 | 15:00 | 135 | 07:00
| Gopalganj-400 | 131 | 03:00 | 128 | 14:00 | Shahjibazar | 135 | 20:00 | 131 | 02:00
| Gulshan | 136 | 03:00 | 129 | 11:00 | Shahmirpur | 140 | 22:00 | 129 | 00:00
| Halishahar | 141 | 19:00 | 126 | 10:00 | Shariatpur | 129 | 05:00 | 125 | 11:00
| Haripur | 134 | 19:30 | 131 | 07:00 | Sherpur | 139 | 23:00 | 115 | 12:00
| HaripurSBU | 134 | 19:30 | 131 | 07:00 | Shikalbaha | 143 | 19:00 | 129 | 00:00
| Hasnabad | 135 | 18:30 | 128 | 09:00 | Shikalbaha-230 | 139 | 23:00 | 129 | 00:00
| Hathazari | 140 | 22:00 | 129 | 08:00 | Shitalakhya | 135 | 19:00 | 128 | 09:00
| Ishurdi | 134 | 01:00 | 129 | 12:00 | Sholosohor | 139 | 23:00 | 127 | 11:00
| Jaldhaka | 133 | 23:00 | 124 | 21:00 | Shyampur | 134 | 19:00 | 128 | 09:00
| Jamalpur | 139 | 23:00 | 118 | 12:00 | Shyampur-230 | 135 | 19:00 | 129 | 09:00
| Jashore | 132 | 23:00 | 125 | 15:00 | Siddhirganj | 135 | 19:00 | 130 | 09:00
| Jhenaidah | 134 | 19:00 | 128 | 15:00 | Sirajganj | 133 | 03:00 | 128 | 11:00
| Jhenaidah-230 | 134 | 10:00 | 129 | 12:00 | Sonargaon | 134 | 17:00 | 129 | 05:00
| Joydebpur | 138 | 19:00 | 133 | 11:00 | Sreemongol | 132 | 00:00 | 130 | 11:00
| Joypurhat | 125 | 01:00 | 117 | 11:00 | Sreepur | 132 | 21:00 | 129 | 09:00
| Juldah | 141 | 23:00 | 124 | 01:00 | Srinagar | 138 | 19:00 | 132 | 09:00
| Kabirpur | 139 | 23:00 | 121 | 09:00 | SSM | 142 | 23:00 | 130 | 07:00
| Kachua | 135 | 23:00 | 122 | 08:00 | Sunamganj | 127 | 05:00 | 121 | 18:30
| Kaliakoir | 140 | 21:00 | 130 | 08:00 | Sylhet | 132 | 23:00 | 129 | 15:00
| Kallyanpur | 129 | 23:00 | 124 | 09:00 | Tangail | 136 | 23:00 | 121 | 12:00
| Kalurghat | 139 | 19:00 | 128 | 10:00 | Thakurgaon | 137 | 04:00 | 126 | 22:00
| Kamrangirchar | 127 | 19:00 | 122 | 09:00 | TK | 142 | 23:00 | 126 | 03:00
| Kaptai | 135 | 16:00 | 128 | 00:00 | Tongi | 132 | 19:30 | 126 | 09:00
| Kazla | 132 | 03:00 | 126 | 13:00 | Ullon | 137 | 21:00 | 129 | 14:00
| Keranigonj | 139 | 19:00 | 132 | 09:00 | Uttara | 130 | 19:00 | 122 | 09:00
| Khagrachori | 136 | 19:00 | 126 | 23:00 | UttaraNew | 130 | 19:00 | 122 | 09:00
| Khulna | 137 | 23:00 | 131 | 15:00 | Zigatola | 138 | 04:00 | 132 | 09:00
| Khulna(S) | 138 | 23:00 | 131 | 15:00
| Khulshi | 138 | 19:00 | 126 | 02:00
| Kishoreganj | 126 | 19:00 | 119 | 12:00
| Kodda | 139 | 21:00 | 130 | 02:00
| KSRM | 136 | 20:00 | 128 | 10:00
| Kulaura | 135 | 22:00 | 132 | 11:00
| Kurigram | 131 | 23:00 | 121 | 21:00
| Kushtia | 131 | 03:00 | 125 | 11:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2023-05-09
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 710 | 8034 | 4901 | 12935 |  |  |  | QF-LDC-11
0:30 | 650 | 7867.5 | 4982.5 | 12850 | Date: | 2023-05-09
1:00 | 590 | 7701 | 5064 | 12765
1:30 | 599 | 7576.5 | 5033 | 12609.5
2:00 | 608 | 7452 | 5002 | 12454
2:30 | 619 | 7396 | 4886.5 | 12282.5 | [5 empty] | Gen. at Eve. Peak | 13752 | 13752 MW (21:00 )
3:00 | 630 | 7340 | 4771 | 12111 | [6 empty] | 21:00
3:30 | 700 | 7302.5 | 4798 | 12100.5 | [5 empty] | Gen. at Day Peak | 12970 | 12970 MW (12:00 )
4:00 | 770 | 7265 | 4825 | 12090 | [6 empty] | 12:00
4:30 | 805 | 7211 | 4817.5 | 12028.5 | [5 empty] | Highest Generation | 13908
5:00 | 840 | 7157 | 4810 | 11967 | [6 empty] | 22:00
5:30 | 870 | 7048 | 4806 | 11854
6:00 | 900 | 6939 | 4802 | 11741
6:30 | 910 | 6903 | 4843 | 11746
7:00 | 920 | 6867 | 4884 | 11751
7:30 | 990 | 6873 | 4890.5 | 11763.5
8:00 | 1060 | 6879 | 4897 | 11776
8:30 | 1130 | 6889.5 | 4941.5 | 11831
9:00 | 1200 | 6900 | 4986 | 11886
9:30 | 1125 | 7215 | 5042 | 12257
10:00 | 1050 | 7530 | 5098 | 12628
10:30 | 1035 | 7761.5 | 5011 | 12772.5
11:00 | 1020 | 7993 | 4924 | 12917
11:30 | 1035 | 7965 | 4978.5 | 12943.5
12:00 | 1050 | 7937 | 5033 | 12970
12:30 | 1090 | 7849.5 | 5099 | 12948.5
13:00 | 1130 | 7762 | 5165 | 12927
13:30 | 1115 | 7563.5 | 5110 | 12673.5
14:00 | 1100 | 7365 | 5055 | 12420
14:30 | 1075 | 7475.5 | 5011.5 | 12487
15:00 | 1050 | 7586 | 4968 | 12554
15:30 | 1025 | 7499.5 | 4927 | 12426.5
16:00 | 1000 | 7413 | 4886 | 12299
16:30 | 1010 | 7403.5 | 4864 | 12267.5
17:00 | 1020 | 7394 | 4842 | 12236
17:30 | 1010 | 7428 | 4940.5 | 12368.5
18:00 | 1000 | 7462 | 5039 | 12501
18:30 | 890 | 8007 | 5037 | 13044
19:00 | 780 | 8552 | 5035 | 13587
19:30 | 500 | 8537 | 5107 | 13644
20:00 | 640 | 8575 | 5034 | 13609 |  |  |  | Executive Engineer
20:30 | 605 | 8666 | 5014.5 | 13680.5 |  |  |  | Network Operation Division
21:00 | 570 | 8757 | 4995 | 13752
21:30 | 590 | 8804 | 5026 | 13830
22:00 | 610 | 8851 | 5057 | 13908 |  |  |  |  | Page 6 of 7
22:30 | 625 | 8482 | 4969 | 13451
23:00 | 640 | 8113 | 4881 | 12994
23:30 | 675 | 8073.5 | 4891 | 12964.5
24:00 | 710 | 8034 | 4901 | 12935
13752 MW (21:00 )
12970 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2023-05-09 |  | Energy |  | 305334090
[13 empty] | 2023-05-09 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 3974 | 813 | 2285 | 62 | 2748 | 2110 | 0 | 0 | 773 | 170 | 0 | 0
0:30 | 4048 | 861.5 | 2202.5 | 237 | 2392.5 | 2209.5 | 0 | 0 | 728 | 171 | 0 | 809 |  | Date: | 43593
1:00 | 4122 | 910 | 2120 | 412 | 2037 | 2309 | 0 | 0 | 683 | 172 | 0 | 1618
1:30 | 4114 | 909.5 | 2124 | 393.5 | 1947.5 | 2301 | 0 | 0 | 650 | 170 | 0 | 1574.4325 | [8 empty] | Total Energy | 305.3341 |  | Total Energy Gen MKWHr Energy Not Served MKWHr Energy Requirement MKWHr | Total Energy Gen 305.334 MKWHr Energy Not Served 29.209 MKWHr Energy Requirement 334.543 MKWHr
2:00 | 4106 | 909 | 2128 | 375 | 1858 | 2293 | 0 | 0 | 617 | 168 | 0 | 1530.865 | [8 empty] | Energy not Served | 29.2088
2:30 | 4127.5 | 909.5 | 2144 | 365 | 1687 | 2302 | 0 | 0 | 580.5 | 167 | 0 | 1524.18 | [8 empty] | Energy Requirement | 334.5428
3:00 | 4149 | 910 | 2160 | 355 | 1516 | 2311 | 0 | 0 | 544 | 166 | 0 | 1517.495
3:30 | 4134.5 | 909.5 | 2156 | 354.5 | 1493 | 2310.5 | 0 | 0 | 579.5 | 163 | 0 | 1449.69 | [7 empty] | Shortage
4:00 | 4120 | 909 | 2152 | 354 | 1470 | 2310 | 0 | 0 | 615 | 160 | 0 | 1381.885
4:30 | 4135 | 909.5 | 2149 | 289.5 | 1467.5 | 2309.5 | 0 | 0 | 608.5 | 160 | 0 | 1320.2875
5:00 | 4150 | 910 | 2146 | 225 | 1465 | 2309 | 0 | 0 | 602 | 160 | 0 | 1258.69
5:30 | 4154.5 | 910 | 2145 | 112.5 | 1469 | 2304 | 0 | 0 | 596 | 152 | 11 | 1234.3375
6:00 | 4159 | 910 | 2144 | 0 | 1473 | 2299 | 0 | 0 | 590 | 144 | 22 | 1209.985
6:30 | 4127.5 | 911 | 2125.5 | 0 | 1486 | 2295.5 | 0 | 0 | 592.5 | 145 | 63 | 962.64 | [6 empty] | Coal
7:00 | 4096 | 912 | 2107 | 0 | 1499 | 2292 | 0 | 0 | 595 | 146 | 104 | 715.295
7:30 | 4102 | 911.5 | 2072.5 | 0 | 1530 | 2281.5 | 0 | 0 | 571 | 144 | 151 | 774.9825 | [5 empty] | Oil
8:00 | 4108 | 911 | 2038 | 0 | 1561 | 2271 | 0 | 0 | 547 | 142 | 198 | 834.67
8:30 | 4097 | 911 | 2024 | 0 | 1570.5 | 2251 | 0 | 37.5 | 545.5 | 144 | 250.5 | 901.52
9:00 | 4086 | 911 | 2010 | 0 | 1580 | 2231 | 0 | 75 | 544 | 146 | 303 | 968.37
9:30 | 4053.5 | 912 | 1981.5 | 158 | 1782 | 2194.5 | 0 | 137.5 | 545.5 | 151 | 341.5 | 828.94
10:00 | 4021 | 913 | 1953 | 316 | 1984 | 2158 | 0 | 200 | 547 | 156 | 380 | 689.51
10:30 | 3957 | 912.5 | 1925.5 | 384.5 | 2115.5 | 2150 | 13.5 | 214 | 549 | 158 | 393 | 670.8875
11:00 | 3893 | 912 | 1898 | 453 | 2247 | 2142 | 27 | 228 | 551 | 160 | 406 | 652.265
11:30 | 3859.5 | 911.5 | 1918.5 | 453.5 | 2274 | 2179.5 | 27 | 214 | 533.5 | 160 | 412.5 | 722.4575
12:00 | 3826 | 911 | 1939 | 454 | 2301 | 2217 | 27 | 200 | 516 | 160 | 419 | 792.65
12:30 | 3830.5 | 911 | 1996 | 329 | 2354 | 2251 | 27 | 160 | 516.5 | 158 | 415.5 | 1103.025
13:00 | 3835 | 911 | 2053 | 204 | 2407 | 2285 | 27 | 120 | 517 | 156 | 412 | 1413.4
13:30 | 3835 | 911 | 2053 | 204 | 2407 | 2285 | 27 | 120 | 517 | 156 | 412 | 1413.4
14:00 | 3835 | 911 | 2053 | 204 | 2407 | 2285 | 27 | 120 | 517 | 156 | 412 | 1413.4
14:30 | 3822.5 | 909.5 | 2056.5 | 324.5 | 2201.5 | 2292.5 | 27 | 60 | 533 | 159 | 354.5 | 1492.665
15:00 | 3810 | 908 | 2060 | 445 | 1996 | 2300 | 27 | 0 | 549 | 162 | 297 | 1571.93
15:30 | 3829.5 | 908 | 2055.5 | 359.5 | 2004.5 | 2293.5 | 27 | 0 | 541.5 | 160 | 247.5 | 1645.9425
16:00 | 3849 | 908 | 2051 | 274 | 2013 | 2287 | 27 | 0 | 534 | 158 | 198 | 1719.955
16:30 | 3844 | 908.5 | 2077.5 | 255.5 | 2015 | 2299.5 | 27 | 0 | 542 | 155 | 143.5 | 1702.2875
17:00 | 3839 | 909 | 2104 | 237 | 2017 | 2312 | 27 | 0 | 550 | 152 | 89 | 1684.62 | [10 empty] | 472
17:30 | 3868 | 909 | 2109 | 149 | 2176 | 2316.5 | 27 | 0 | 609 | 153 | 52 | 1367.31 | [10 empty] | 100
18:00 | 3897 | 909 | 2114 | 61 | 2335 | 2321 | 27 | 0 | 668 | 154 | 15 | 1050 | [10 empty] | 20
18:30 | 3881.5 | 909 | 2104 | 251.5 | 2734 | 2262 | 27 | 0 | 712.5 | 155 | 7.5 | 1247.4575 | [10 empty] | 592
19:00 | 3866 | 909 | 2094 | 442 | 3133 | 2203 | 27 | 0 | 757 | 156 | 0 | 1444.915
19:30 | 3910 | 908 | 2144 | 280 | 3238 | 2213 | 27 | 0 | 772 | 152 | 0 | 1506.035
20:00 | 3962 | 814 | 2160 | 236 | 3282 | 2209 | 27 | 0 | 767 | 152 | 0 | 1567.155
20:30 | 3988.5 | 814 | 2187.5 | 349 | 3208 | 2185 | 27 | 0 | 768.5 | 153 | 0 | 1522.7475
21:00 | 4015 | 814 | 2215 | 462 | 3134 | 2161 | 27 | 0 | 770 | 154 | 0 | 1478.34
21:30 | 4033.5 | 813.5 | 2238 | 462.5 | 3138.5 | 2184.5 | 27 | 0 | 773.5 | 159 | 0 | 1308.35
22:00 | 4052 | 813 | 2261 | 463 | 3143 | 2208 | 27 | 0 | 777 | 164 | 0 | 1138.36
22:30 | 3968 | 792 | 2195 | 286.5 | 3060.5 | 2188.5 | 13.5 | 0 | 777 | 170 | 0 | 1431.545
23:00 | 3884 | 771 | 2129 | 110 | 2978 | 2169 | 0 | 0 | 777 | 176 | 0 | 1724.73
23:30 | 3929 | 792 | 2207 | 86 | 2863 | 2139.5 | 0 | 0 | 775 | 173 | 0 | 1561.9025 |  | Max Temp. in Dhaka |  | 39.8° C
24:00 | 3974 | 813 | 2285 | 62 | 2748 | 2110 | 0 | 0 | 773 | 170 | 0 | 1399.075
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 305.334 MKWHr Energy Not Served 29.209 MKWHr Energy Requirement 334.543 MKWHr
Shortage
Note on W13: Author:

## Generation
g | 2023-05-09
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3
2 | Karnaphuli Hydro PP Unit-4 & 5 | [10 empty] | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 |  | 27 | 27 | 27 | 27 | 27 | 0 |  | 324000
3 | Chattogram TPP-1 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2700000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 16 | 16 | 8 | 8 | 14 | 16 | 16 | 16 | 16 | 16 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 456975
| Teknaf 20MW PP (Solartech) | [5 empty] | 1 | 5 | 10 | 14 | 17 | 19 | 20 | 17 | 12 | 13 | 8 | 3 | [9 empty] | 136215
6 | Sikalbaha 225MW CCPP (Gas) | 224 | 225 | 225 | 223 | 225 | 225 | 226 | 220 | 216 | 219 | 213 | 212 | 216 | 212 | 211 | 220 | 221 | 221 |  | 224 | 225 | 225 | 220 | 222 | 226 | 225 | 5248249
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 80 | 63 | 63 | 63 | 63 | 74 | 74 | 74 | 74 | 82 |  | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 1886967
12 | Hathazari 100 MW peaking PP | 46 | 52 | 52 | 52 | 52 | 56 | 56 | 56 | 55 | 47 | 42 | 42 | 43 | 45 | 45 | 39 | 34 | 44 |  | 28 | 24 | 30 | 48 | 56 | 56 | 56 | 1115820
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 22 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 30 | 41 | 63 | 87 | 87 | 87 | 87 |  | 87 | 87 | 87 | 87 | 87 | 87 | 81 | 1211054
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | 35 | 34 | 34 | 34 | 34 | 34 | 37 | 37 | 37 | 35 | 34 | 35 | 31 | 25 | 26 | 25 | 25 | 26 |  | 29 | 32 | 34 | 36 | 35 | 35 | 35 | 799008
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 199 | 189 | 175 | 175 | 170 | 170 | 170 | 170 | 195 | 195 | 200 | 202 | 197 | 150 | 196 | 194 | 194 | 196 |  | 201 | 204 | 205 | 200 | 200 | 160 | 190 | 4588293
18 | Kodda 300 MW PP Unit-2 (Summit) | 130 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 100 | 168 | 190 | 198 | 173 | 95 | 97 | 95 | 112 |  | 245 | 265 | 278 | 278 | 278 | 278 | 278 | 3788725
19 | Ashuganj 195MW PP (APSCL-United) | 185 | 185 | 185 | 185 | 180 | 180 | 180 | 180 | 180 | 178 | 177 | 177 | 177 | 177 | 175 | 175 | 175 | 175 |  | 175 | 175 | 175 | 175 | 187 | 195 | 197 | 4315636
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2787406
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 170 | 170 | 170 | 170 | 170 | 170 | 170 |  | 170 | 180 | 180 | 180 | 180 | 180 | 180 | 4183200
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 40 | 42 | 42 | 42 | 42 | 43 | 39 | 39 | 36 | 35 | 34 | 33 | 31 | 30 | 30 | 29 | 30 | 14 |  | 15 | 20 | 28 | 33 | 36 | 33 | 34 | 807624
33 | Ashuganj 225 MW CCPP | 206 | 207 | 205 | 207 | 207 | 207 | 207 | 203 | 199 | 203 | 202 | 198 | 201 | 197 | 194 | 199 | 200 | 198 |  | 206 | 206 | 205 | 203 | 204 | 207 | 207 | 4882000
34 | Ashuganj 450 MW CCPP(South) | 305 | 305 | 330 | 305 | 315 | 320 | 305 | 340 | 325 | 305 | 300 | 320 | 305 | 305 | 310 | 305 | 305 | 305 |  | 305 | 305 | 305 | 305 | 305 | 305 | 305 | 7665000
| Ashuganj 450 MW CCPP(North) | 310 | 310 | 335 | 315 | 315 | 320 | 310 | 315 | 340 | 310 | 315 | 305 | 315 | 315 | 320 | 320 | 310 | 310 |  | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 8021500
Ashuganj 420 MW CCPP(East)
35 | Ashuganj 55 MW PP (Precision)
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 398 | 398 | 400 | 402 | 401 | 400 | 401 | 401 | 401 | 402 | 396 | 394 | 390 | 394 | 393 | 389 | 393 | 403 |  | 392 | 397 | 398 | 399 | 398 | 396 | 379 | 9650170
40 | Meghnaghat 450 MW CCPP(MPL) | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 |  | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 10012500
41 | Haripur 360MW CCPP(HPL) | 323 | 322 | 323 | 329 | 332 | 334 | 324 | 304 | 293 | 253 | 209 | 235 | 320 | 317 | 314 | 314 | 314 | 313 |  | 334 | 334 | 334 | 334 | 334 | 305 | 336 | 7444000
42 | RPCL 210MW CCPP | 82 | 86 | 87 | 87 | 87 | 87 | 49 | 32 | 32 | 30 | 30 | 28 | 28 | 25 | 29 | 31 | 31 | 31 |  | 46 | 47 | 48 | 68 | 82 | 72 | 72 | 1200960
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 3 | 11 | 23 | 33 | 42 | 48 | 46 | 48 | 27 | 27 | 21 | 10 | 2 | [8 empty] | 345340
44 | Fenchugonj CCPP Phase-1 | 40 | 40 | 40 | 40 | 40 | 40 | 43 | 43 | 36 | 36 | 36 |  |  |  | 29 | 10 | 15 | 43 |  | 43 | 44 | 44 | 43 | 43 | 43 | 43 | 745000
45 | Fenchugonj CCPP Phase-2 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 640080
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 55 | 55 | 55 | 54 | 49 | 54 | 53 | 53 | 50 | 45 | 50 |  | 56 | 56 | 56 | 56 | 59 | 60 | 59 | 1287648
48 | Shahjibazar 86MW PP (Shahjibazar) | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 78 | 78 | 75 | 74 | 74 | 70 | 71 | 71 | 74 | 76 |  | 78 | 78 | 80 | 80 | 80 | 81 | 81 | 1865280
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 203 | 204 | 202 | 202 | 203 | 203 | 202 | 204 | 204 | 203 | 200 | 201 | 200 | 200 | 200 | 198 | 199 | 200 |  | 198 | 198 | 196 | 204 | 204 | 194 | 202 | 5081260
51 | Sylhet 20 MW GTPP | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 18 | 16 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 16 |  | 16 | 17 | 17 | 17 | 18 | 17 | 17 | 386000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 9 | 10 | 10 | 10 | 10 | 10 | 10 | 9 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 242460
54 | Hobiganj 11MW PP Cofidence-E | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 11 | 11 | 8 | 220416
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 50 | 50 | 47 | 43 | 48 | 47 | 47 | 49 | 50 |  | 50 | 50 | 50 | 53 | 53 | 53 | 53 | 1218000
56 | Shahjahanulla 25 MW PP | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 8 | 8 | 8 | 8 | 8 | 8 | 14 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 311304
57 | Bibiana-II 341 MW CCPP (Summit) | 290 | 295 | 300 | 285 | 290 | 285 | 285 | 290 | 290 | 290 | 280 | 285 | 290 | 290 | 290 | 285 | 290 | 270 |  | 280 | 270 | 260 | 280 | 285 | 285 | 290 | 6985500
| Bibiyana South 400 MW | 345 | 348 | 343 | 343 | 370 | 370 | 370 | 370 | 370 | 370 | 372 | 354 | 352 | 345 | 327 | 355 | 370 | 360 |  | 320 | 330 | 355 | 385 | 390 | 340 | 390 | 8616000
58 | Nababganj 55 MW PP (Southern power ) | [9 empty] | 35 | 55 | 55 | 55 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 |  |  |  |  | 443193
59 | Tangail Palli Power Gen 22 MW | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 239040
60 | Barabkunda 22 MW PP (Regent) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 191472
61 | Narshingdi 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 22 | 22 | 22 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 22 | 22 | 22 |  | 425592
62 | Tangail 22 MW PP (Doreen) | 16 | 17 | 17 | 18 | 17 | 18 | 18 | 18 | 14 | 14 | 14 | 13 | 13 | 15 | 15 | 12 | 12 | 17 |  | 17 | 18 | 18 | 18 | 18 | 18 | 18 | 359064
63 | Impoprt (Tripura) | 172 | 168 | 166 | 160 | 160 | 144 | 146 | 142 | 146 | 156 | 160 | 160 | 156 | 160 | 162 | 158 | 152 | 154 |  | 156 | 152 | 152 | 154 | 164 | 176 | 170 | 3783360
64 | Malancha, Ctg. EPZ (United) | 35 | 35 | 35 | 36 | 36 | 34 | 25 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 5 |  | 5 | 10 | 14 | 26 | 34 | 16 | 32 | 387360
65 | Feni 22MW PP (Doreen) | 16 | 17 | 17 | 17 | 17 | 17 | 18 | 15 | 15 | 15 | 15 | 15 | 15 | 14 | 14 | 15 | 15 | 15 |  | 16 | 16 | 17 | 17 | 17 | 18 | 18 | 378324
66 | Feni 11 MW PP (Doreen) | 7 | 7 | 7 | 7 | 5 | 5 | 5 | 5 | 5 | 5 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 |  | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 156240
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 33 | 31 | 25 | 25 | 25 | 27 | 18 | 22 | 15 | 22 | 32 |  | 32 | 32 | 33 | 33 | 33 | 33 | 33 | 698400
68 | Cumilla 25 MW PP (Summit) | 21 | 0 | 8 | 21 | 20 | 20 | 20 | 20 | 20 | 18 | 12 | 15 | 20 | 5 | 15 | 15 | 10 | 10 |  | 18 | 18 | 18 | 20 | 20 | 20 | 20 | 379740
69 | Summit Ashulia | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 552000
70 | Summit Madhabdi | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 17 | 23 | 23 | 16 | 16 | 22 | 22 | 22 | 23 |  | 24 | 24 | 24 | 25 | 26 | 26 | 26 | 541800
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 25 | 25 | 25 | 33 |  | 33 | 33 | 33 | 25 | 25 | 25 | 25 | 757300
72 | Rupganj 33 MW PP(Summit) | 31 | 31 | 31 | 31 | 31 | 32 | 31 | 31 | 30 | 28 | 28 | 25 | 24 | 24 | 24 | 24 | 14 | 26 |  | 26 | 24 | 25 | 25 | 25 | 20 | 25 | 661700
73 | Ghorashal 108MW PP (Regent) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 21 | 21 |  | 21 | 21 | 21 | 22 | 22 | 22 | 22 | 516454
| Feni Lanka Power | 114 | 114 | [24 empty] | 296400
| Chowmuhani 113 MW | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 8 | 55 | 55 | 55 | 56 | 28 | 27 | 28 | 56 | 56 |  | 56 | 56 | 57 | 57 | 57 | 75 | 75 | 813120
| Manikgonj 162MW PP(MPGL) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 |  | 162 | 162 | 162 | 17 | 17 | 17 | 17 | 1144800
77 | Siddhirganj 100 PP(Dutch Bangla) | 40 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 45 | 60 | 67 | 72 | 67 | 64 | 72 | 72 | 70 | 72 |  | 72 | 72 | 72 | 75 | 72 | 72 | 72 | 1318915
78 | Gazipur 52 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 30 | 37 | 30 | 30 | 16 | 16 | 16 | 16 | 16 |  | 35 | 39 | 39 | 39 | 39 | 39 | 16 | 560640
79 | Kodda 150 MW PP | 80 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 82 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 106 |  | 145 | 145 | 146 | 146 | 146 | 146 | 146 | 2176320
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 50 | 43 | 43 | 43 | 43 | 51 | 51 | 51 | 43 | 42 | 40 | 35 | 33 | 37 | 30 | 30 | 38 | 38 |  | 40 | 52 | 52 | 52 | 52 | 50 | 48 | 1023672
| Gazipur 100 MW PP | 105 | 105 | 105 | 105 | 90 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2322029
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 2 | 3 | 4 | 4 | 5 | 4 | 4 | 3 | 2 | 1 | [9 empty] | 33242
| Jodiac Power | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 6 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 437970
| Karnaphuli Power Ltd. | 54 | 54 | 54 | 45 | 54 | 54 | 47 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 60 | 54 | 67 |  | 74 | 74 | 74 | 74 | 97 | 104 | 66 | 1502102
82 | Madanganj 102 PP(Summit) | 97 | 97 | 97 | 88 | 97 | 97 | 97 | 97 | 97 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 |  | 95 | 95 | 97 | 97 | 97 | 97 | 88 | 2170958
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [15 empty] | 4 | 4 | [9 empty] | 8746
86 | Meghnaghat CCPP ( Summit) | 296 | 305 | 307 | 307 | 299 | 303 | 295 | 286 | 295 | 296 | 298 | 292 | 288 | 292 | 289 | 263 | 291 | 300 |  | 242 | 268 | 280 | 293 | 303 | 254 | 293 | 7096378
87 | Meghnaghat 100 MW(IEL) | 25 | 24 | 25 | 25 | 25 | 24 | 24 | 25 | 25 | 41 | 68 | 68 | 73 | 73 | 72 | 72 | 53 | 48 |  | 49 | 50 | 48 | 49 | 63 | 53 | 32 | 1079040
| Meghnaghat 104 MW PP (OPCL) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 20 | 30 | 50 | 53 | 53 | 56 | 64 | 53 | 53 | 53 | 53 |  | 53 | 53 | 53 | 53 | 50 | 35 | 34 | 947520
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 33 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 33 | 31 | 31 | 31 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 22 | 641640
92 | Fenchuganj 44MW (Energyprima) | 48 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 48 | 47 | 43 | 41 | 41 | 38 | 39 | 43 | 44 | 45 |  | 43 | 46 | 47 | 48 | 49 | 49 | 49 | 1099008
93 | Ashuganj 51 MW PP (Midland) | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 939772
94 | Gagnagar 102 MW PP (Digital Power) | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 40 | 40 | 40 | 40 | 58 | 58 | 58 | 58 |  | 92 | 92 | 92 | 92 | 92 | 50 | 50 | 1171008
95 | Patenga 50MW PP (Baraka) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 8 | 15 | 26 | 32 | 34 |  | 7 |  | 36 | 44 | 44 | 44 | 44 | 40 | 11 | 44352
96 | Chattogram 108 MW PP (ECPV) | [17 empty] | 30 |  | 30 | 30 | 29 | 30 | 30 | 21 |  | 171840
97 | katpotti 52 MW
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [6 empty] | 2 | 15 | 15 | 15 | 45 | 55 | 55 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 386968
100 | Manikganj 55 MW PP (Northern) | [8 empty] | 17 | 35 | 55 | 55 | 55 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 |  |  |  |  | 443525
101 | Kushiara 163 MW CCPP (KP)
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 1 | 1 | 2 | 1 | 2 | 2 | 2 | 2 | 2 | 1 | 1 | 0 | [8 empty] | 14900
103 | Kamalaghat 54 MW PP(Banco Energy) | [10 empty] | 54 | 54 | 35 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 |  |  |  | 276480
104 | Keranigonj 300 MW PP (APR) | 260 | 220 | 200 | 200 | 70 |  |  |  |  | 171 | 300 | 303 | 54 | 129 | 300 | 129 | 172 | 11 |  | 292 | 156 | 106 | 302 | 303 | 58 | 12 | 4059373
105 | Bramhangoan 100 MW PP (Aggreko) | 80 | 80 | 80 | 80 | 80 |  |  |  |  | 70 | 78 | 76 | 75 | 50 | 70 | 70 | 25 | 25 |  | 72 | 73 | 80 | 80 | 80 | 25 | 25 | 1320586
106 | Mymensingh 200 MW PP (United) | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 68 | 76 | 75 | 75 | 45 | 45 | 46 | 47 | 58 |  | 94 | 95 | 95 | 95 | 97 | 97 | 88 | 1509600
112 | Aurahati 100MW PP (Aggreko) | 72 | 75 | 75 | 74 | 75 |  |  |  |  | 75 | 75 | 75 | 75 | 50 | 75 | 75 | 40 | 25 |  | 78 | 51 | 50 | 80 | 80 | 27 | 25 | 1296796
114 | Kodda 149 MW PP Unit-1 (Summit) | 25 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 106 | 139 | 128 | 126 | 44 | 29 | 30 | 32 | 56 |  | 130 | 140 | 141 | 144 | 145 | 144 | 144 | 1712736
115 | Juldah 100 MW PP Unit-3 (Acorn) | 38 | 38 | 38 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 707520
116 | Chandpur 200MW (Desh energy) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 29 | 34 | 51 | 51 | 37 | 34 | 35 | 40 | 68 |  | 69 | 69 | 69 | 69 | 69 | 92 | 120 | 1029600
117 | Ashuganj 150MW PP (Midland) | 145 | 46 | 20 | 20 | 18 | 20 | 20 | 20 | 18 | 20 | 18 | 18 | 17 | 18 | 16 | 21 | 30 | 46 |  | 73 | 92 | 102 | 137 | 143 | 143 | 150 | 1286327
118 | Bibiyana-III 400 MW CCPP | 399 | 401 | 404 | 404 | 404 | 404 | 404 | 404 | 389 | 404 | 398 | 391 | 405 | 380 | 370 | 400 | 382 | 390 |  | 367 | 369 | 369 | 369 | 367 | 319 | 368 | 9277000
| Jamalpur 115 MW PP (United) | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 68 | 78 | 78 | 76 | 46 | 46 | 46 | 47 | 49 |  | 97 | 97 | 97 | 98 | 98 | 98 | 98 | 1536000
| Anwara 300 MW PP (United) | 87 | 87 | 87 | 87 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 93 | 82 | 82 | 82 | 99 | 120 |  | 290 | 290 | 296 | 300 | 286 | 208 | 87 | 2948182
| Juldah unit-2 (Acorn) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 34 | 34 | 34 | 34 | 38 |  | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 730560
| Anlima Energy Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  |  | 10 | 17 | 17 | 17 | 17 | 17 | 47 | 434073
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 20 | 35 | 35 | 35 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 495000
| Spectra Solar Plant Ltd. | [5 empty] | 2 | 7 | 8 | 13 | 23 | 25 | 29 | 23 | 21 | 22 | 14 | 6 | 1 | [8 empty] | 209228
| Chandpur 115(Doreen) | 45 | 36 | 36 | 36 | 36 | 36 | 35 | 36 | 36 | 47 | 93 | 95 | 95 | 76 | 72 | 72 | 73 | 82 |  | 86 | 94 | 92 | 94 | 95 | 85 | 94 | 1593600
| Kanchan Purbachal Power Generation Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 432720
| Mirsharai 150 MW (Oil) | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 108 | 108 | 108 | 108 | 108 | 108 | 126 |  | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 3529454
Mirsharai 150 MW (Gas)
120 | Eastern Zone Total | 7701 | 7452 | 7340 | 7265 | 7157 | 6939 | 6867 | 6879 | 6900 | 7530 | 7993 | 7937 | 7762 | 7365 | 7586 | 7413 | 7394 | 7462 |  | 8552 | 8537 | 8575 | 8757 | 8851 | 8113 | 8034 | 183870329
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | 80 | 80 | 80 | 65 | 65 | 65 | 65 | 63 | 63 | 62 | 62 | 60 | 60 | 60 | 60 | 60 | 44 | 64 |  | 77 | 79 | 79 | 94 | 93 | 94 | 95 | 1635840
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL) | [8 empty] | 75 | 200 | 228 | 200 | 120 | 40 | [12 empty] | 843640
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 25 | 20 | 20 | 20 | 20 | 19 | 19 | 19 | 19 | 18 | 16 | 11 | 14 | 18 | 18 | 21 | 22 | 22 |  | 32 | 36 | 44 | 37 | 37 | 37 | 33 | 507360
Khulna 225 MW CCPP
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 |  | 36 | 36 | 44 | 55 | 55 | 55 | 55 | 936960
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 5 | 28 | 43 | 68 | 85 | 73 | 75 | 90 | 83 | 59 | 41 | 17 | 3 | [8 empty] | 619200
131 | Rampal 1320 MW (BIFPCL)
132 | United Payra Power Ltd. | 150 | 150 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 1617600
133 | Bhola Nutan Biddut BD LTD (GAS)
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [9 empty] | 32 | 36 | 64 | 64 | 16 | [5 empty] | 16 | 16 | 16 | 16 | 16 | 16 |  | 289824
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 178 | 178 | 178 | 178 | 178 | 179 | 179 | 173 | 172 | 174 | 171 | 170 | 168 | 168 | 168 | 168 | 168 | 161 |  | 157 | 159 | 175 | 175 | 175 | 170 | 170 | 4191611
140 | Bhola 33 MW PP (Venture) | 35 | 34 | 33 | 32 | 31 | 27 | 24 | 22 | 22 | 23 | 24 | 23 | 25 | 27 | 28 | 28 | 26 | 26 |  | 34 | 34 | 35 | 36 | 37 | 37 | 37 | 704800
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali) | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 24 | 24 | 32 | 24 | 24 | 24 | 24 | 24 | 24 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 736500
143 | Gopalganj 100 MW Peaking PP | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 20 | 22 | 22 | 22 | 22 | 19 | 20 | 22 | 22 | 40 | 65 |  | 70 | 82 | 80 | 75 | 75 | 75 | 75 | 1203840
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 15 | 50 | 105 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2404224
146 | Bheramara HVDC | 910 | 909 | 910 | 909 | 910 | 910 | 912 | 911 | 911 | 913 | 912 | 911 | 911 | 908 | 908 | 908 | 909 | 909 |  | 909 | 908 | 814 | 814 | 813 | 771 | 813 | 21542545
147 | Bheramara 410 MW CCPP | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 115 | 110 | [16 empty] | 1299744
148 | Payra 1320 MW | 1244 | 1244 | 1244 | 1244 | 1244 | 1222 | 1222 | 1200 | 1160 | 1080 | 1070 | 1200 | 1244 | 1244 | 1244 | 1244 | 1244 | 1244 |  | 1230 | 1244 | 1244 | 1244 | 1244 | 1200 | 1140 | 31121100
149
150 | Barapukuria TPP Unit-1 | 75 | 72 | 72 | 74 | 74 | 74 | 75 | 76 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 74 | 75 | 75 |  | 76 | 76 | 76 | 75 | 76 | 76 | 75 | 1746327
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 200 | 222 | 250 | 250 | 250 | 250 | 250 |  | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 5939900
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 17 | 21 | 28 | 28 | 28 | 28 | 28 | 28 |  | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 583584
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 0 | 2 | 3 | 4 | 4 | 5 | 4 | 4 | 3 | 2 | 1 | 0 | [8 empty] | 35520
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 158 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 155 | 155 | 155 | 159 | 167 | 169 | 173 | 175 | 176 | 176 |  | 177 | 176 | 176 | 180 | 184 | 187 | 183 | 4233600
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 133 | 133 | 135 | 135 | 135 | 136 | 136 | 135 | 133 | 133 | 132 | 133 | 138 | 141 | 142 | 144 | 144 | 148 |  | 148 | 153 | 153 | 153 | 156 | 150 | 145 | 3639182
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 229 | 224 | 248 | 249 | 249 | 253 | 248 | 231 | 209 | 196 | 203 | 227 | 259 | 260 | 271 | 290 | 303 | 315 |  | 310 | 336 | 341 | 345 | 354 | 309 | 372 | 6434981
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | 30 | 30 | 30 | 28 | 15 | [6 empty] | 4 | 4 | 5 | 20 | 26 | 28 | 28 |  | 28 | 28 | 8 |  |  |  |  | 230961
162 | Bogra 22 MW PP (GBB) | 20 | 20 | 21 | 21 | 21 | 20 | 18 | 15 | 15 | 15 | 13 | 11 | 9 | 9 | 9 | 9 | 12 | 16 |  | 19 | 19 | 20 | 20 | 20 | 20 | 20 | 371520
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 148860
165 | Amnura 50 MW PP(Sinha) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 28 | 28 | 28 | 28 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 524560
166 | Katakhali 50 MW PP (Northern) | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 880579
167 | Katakhali 50 MW Peaking PP | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 40 | 40 | 40 | 40 | 24 | 24 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 655300
168 | Santahar 50 MW Peaking PP | 34 | [16 empty] | 32 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 231400
169 | Natore 52 MW PP (Rajlanka) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 35 | 35 | 43 | 34 | 34 |  |  | 273845
170 | Chapainawabganj 100 MW Peaking PP | 73 | 73 |  | 73 | 73 | 73 | 75 | 75 | 75 | 72 | 72 | 72 | 69 | 68 | 70 | 69 | 69 | 69 |  | 75 | 75 | 75 | 78 | 78 | 78 | 78 | 1733908
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 35 | 35 |  |  |  |  | 11 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 37 | 50 | 50 | 50 | 50 | 35 | 35 | 814944
172 | Confidence Power Bogura Unit-1 113 MW | 35 | 35 |  |  |  |  | 20 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 55 | 55 | 55 | 55 | 55 | 35 | 35 | 817632
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 33 | 33 | 33 | 34 | 34 |  | 34 | 34 | 34 | 34 | 34 | 60 | 63 | 853795
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1 | 3 | 5 | 7 | 7 | 7 | 7 | 7 | 7 | 5 | 4 | 1 | [8 empty] | 60616
178 | Energypac Power Venture Thakurgaon Ltd. | 113 | 114 | 114 | 114 | 113 | 114 | 115 | 115 | 115 | 115 | 115 | 95 | 95 | 95 | 110 | 104 | 104 | 109 |  | 114 | 114 | 114 | 114 | 114 | 114 | 113 | 2644416
| Intraco Solar 30 MW | [5 empty] | 1 | 6 | 15 | 23 | 29 | 32 | 33 | 32 | 29 | 23 | 14 | 6 | 1 | [8 empty] | 246983
| Adani Power Jharkhanda Ltd | 740 | 727 | 745 | 742 | 741 | 753 | 745 | 745 | 746 | 753 | 747 | 742 | 744 | 747 | 731 | 719 | 743 | 752 |  | 647 | 643 | 639 | 592 | 638 | 643 | 645 | 17231080
178 | Teesta Solar Limited | [5 empty] | 10 | 44 | 91 | 139 | 168 | 192 | 197 | 185 | 173 | 138 | 90 | 40 | 7 | [8 empty] | 1475480